## 250812_eval_set_sample
id | doc_title | chunk | metadata
8a6ad2b0-e571-4704-815a-5662e14ebf0f | KSCIEC61643-12_KR | KS C IEC 61643-12 KSKSKSKS KSKSKSK KSKSKS KSKSK KSKS KSK K KS 저압 서지보호장치 - 제 12 부: 저압 전력 시스템 보호용 서지보호장치 선정 및 적용지침 KS C IEC 61643-12:2020 산 업 표 준 심 의 회 2023 년 3 월 17 일 개정 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
56486011-7db1-4410-9d82-cec9532a5ab7 | KSCIEC61643-12_KR | KS CIEC 61643-12:2020 심 의 : 전력기기 기술심의 회 성 명 근 무 처 직 위 (회 장) 홍 순 찬 단국대학교 교 수 (위 원) 김 재 철 숭실대학교 교 수 서 호 선 KR 지식재산법률사무소 대 표 심 대 섭 (주)정인시스템 기술연구소장 이 주 철 (주)건일이엔지 연 구 소 장 전 기 중 (주)피디엔에스 전 무 박 현 주 한국전력공사 전력연구원 책임연구원 안 상 필 한국전기연구원 실 장 채 경 수 한국스마트의 료기기산업진흥재단 연 구 위 원 (간 사) 조 형 민 국가기술표준원 표준정책국 전기전자정보표준과 주 무 관 원안작성협력 : 서지보호기 전문위원회 성 명 근 무 처 직 위 (대표전문위원) 손 석 금 오산대학교 교 수 (위 원) 강 무 성 인곡엔지니어링 부 장 허 재 완 한국전기안전공사 부 장 박 춘 현 (주)에이치엠 부 장 유 덕 선 한국오토와 전기(주) 이 사 이 기 홍 한국토지주택공사 토지주택연구원 연 구 위 원 신 성 수 대한전기협회 팀 장 최 길 한국기계전기전자시험연구원 책임연구원 고 병 찬 한국전기안전공사 지 사 장 이 정 희 제룡전기(주) 상 무 홍 장 수 비츠로이엠 팀 장 박 철 배 한국전력공사 차 장 엄 주 홍 한국전력공사 전력연구원 책임연구원 이 영 준 (주)성진테크윈연구소 이 사 (간 사) 김 용 성 한국전기연구원 팀 장 (간 사) 이 유 기 한국전기연구원 선임기술원 표준열람 : e 나라표준인증(http://www.srandiand.go.kr) 제 정 자 : 산업표준심의 회 위원장 담당부처 : 산업통상자원부 국가기술표준원 제 정 : 2003 년 8 월 30 일 개 정 : 2023 년 3 월 17 일 심 의 : 산업표준심의 회 전력기기 기술심의 회 원안작성협력 : 서지보호기 전문위원회 이 표준에 대한 의견 또는 질문은 e 나라표준인증 웹사이트를 이용하여 주십시오. 이 표준은 산업표준화법 제 10 조의 규정에 따라 매 5 년마다 산업표준심의 회에서 심의 되어 확인, 개정 또는 폐지됩니다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
0273366c-1337-49ee-9d47-ed552c6721a0 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 목 차 머 리 말 .................................... 개 요 ...................................... V 0.1 일반사항 ··················· ..................... V 0.2 이 표준의 구조를 이해하기 위한 중요사항................. vi 1 적용범위 ................................ 1 2 인용표준 .................................. 1 3 용어, 정의 및 약어 ................... 3.1 용어와 정의 .............. 2 3.2 이 표준에서 사용되는 약어 및 약어 목록 .................................... 16 4 보호의 필요성 ························ 18 5 보호해야 하는 저압 전력 시스템과 장비 ...................... 18 5.1 일반사항. ---- 18 5.2 저압 전력 시스템 ······ 19 5.3 보호 기기의 특성 ...... 22 6 서지보호장치 ············ 22 6.1 SPD 의 기본 ************* 22 6.2 추가 요구사항. ········· 23 6.3 SPD 의 등급 분류 ------ 23 6.4 SPD 의 특성 ___ ___ 6.5 SPD 의 특성에 대한 부가 정보 ----------⌀ 7 저압 전력 시스템에서의 SPD ※ = = = = = = 33 7.1 일반사항 __________/ 7.2 시험 등급에 따른 SPD 위치 고려 ................ 7.3 SPD 보호 가능 모드와 설치 ........... 34 7.4 추가 보호의 필요성 ....... 7.5 SPD 특성 선정 ......... 43 7.6 보조 장치의 특성 ······· 54 부속서 A (참고) SPD 를 선정하기 전에 필요한 기본적인 정보 및 시험 절차.................................. 56 A.1 SPD 를 선정하기 전에 필요한 기본적인 정보 ........................................56 A.2 KSCIEC 61643-11 에서 사용된 시험 절차 설명 ................................................... 58 부속서 B (참고) Uc 와 공칭 시스템 전압 간의 관계 및 금속 산화 배리스터(MOV)의 Up 와 Uc 간의 관계에 대한 예 .................................... 66 B.1 Uc 와 시스템의 공칭 전압 간의 관계 ................................................... 66 B.2 금속 산화 배리스터(MOV)의 Up 과 Uc 간의 관계................................. 66 부속서 C (참고) 환경 -LV 시스템의 서지 전압 ............................... 68 C.1 일반사항. ................. 68 C.2 낙뢰 과전압 ............... 68 C.3 스위칭 ..................... 71 -i- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및무단배포를 금합니다. | {}
85aa7d41-ff31-40f6-974e-9284554b97cb | KSCIEC61643-12_KR | KS CIEC 61643-12:2020 부속서 D(참고) 부분적인 뇌전류의 계산 ........ ................................................... 74 부속서 E(참고) 고압 시스템과 접지 사이의 고장으로 인한 저압 시스템의 TOV.............................. 77 E.1 일반사항 ··············· ......................................... 77 E.2 205 번................................ 78 E.3 기호 ·························· 78 E.4 고압 접지 고장 시 LV 시스템의 과전압 ................................................... 78 E.5 TT 시스템 예 - 가능한 일시적인 과전압의 계산 .... 80 E.6 다양한 LV 시스템 및 다양한 종류의 접지 구성에 따른 일시적 전력 주파수 과전압.......... 81 E.7 북미 TN C 시스템의 일시적인 과전압 값 ................................................... 88 E.8 설명과 함께 KS C IEC 61643-11 에 사용된 일시적 과전압 값 ··················································· 89 부속서 F (참고) 협조 규칙과 원칙 ··········· 100 F.1 일반사항 ............ 100 F.2 에너지 협조 .... ............................. 100 F.3 협조 시험: 에너지 및 전압 보호 협조 ................................................... 109 ························ 부속서 G (참고) 응용 예 ................................................ ················ 113 G.1 가정에서의 응용 ................................................... ················· ......................... 113 G.2 산업에서의 응용 - 115 G.3 뇌 보호 시스템의 존재 ......... 119 G.4 풍력 터빈 ······· ............... 120 부속서 H (참고) 위험성 평가 방법 및 응용 사례 ................................ 125 H.1 일반사항 ············ ················· 125 H.2 KS C IEC 60364-4-44 에 명시된 저전압 위험 평가를 위해 제안된 단순화된 방법 ............ 125 H.3 위험 평가 시 고려해야 할 요소 ........................... ................................................... 131 부속서 I (참고) 시스템 스트레스 ........ 134 I.1 낙뢰 과전압과 전류[5.2.2] ........... 134 1.2 스위칭 과전압[5.2.3] ........... 135 I.3 일시적인 과전압 UTOV[5.2.4] ..................... ················· 135 부속서 J (참고) SPD 의 응용 ................ 137 137 J.1 위치와 SPD 에 의한 보험법」 J.2 SPD 의 선정 ·················· 147 J.3 LPS 로 보호되는 건물의 경우 I 등급 시험된 SPD 에 대한 limp 의 간단한 계산.................. 150 부속서 K(참고) 내성 대 정격 임펄스 전압 내력 ......... -------------- 154 부속서 L (참고) 일부 국가에서 배전반에 SPD 설치 이..................................... 160 부속서 M(참고) 장비에 신호 및 전원 단자가 모두 있는 경우의 협조 10000000000000000000000000000mm 165 부속서 N (참고) 단락 후비 보호 및 서지 내력 ··················································· 171 N.1 일반사항 ................................................... 171 N.2 서지 8/20 및 10/350 파형의 1 회에 대한 퓨즈 내력 정보 . ··················································· 171 N.3 사전시험 및 동작 책무 시험에 대한 퓨즈 영향 요인(감소) ....... 172 N.4 실험 데이터를 기반으로 하고 IEC 60269 시리즈에 지정된 매개변수 및 한계를 기반으로 한 계산으로 확인된 퓨즈의 동작 책무 내성 ······· ·········· 172 N.5 외부 분리기 기술 모드 ............ 174 N.6 일부 국가에서 사용되는 SPD 외부 분리기에 대한 추가 요구사항 및 시험 값 ................. 174 -ii- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단배포를 금합니다. | {}
cbf1a267-86bc-441e-8c34-fff685c0a42f | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 부속서 O (참고) 뇌방전 조건에서 시스템 레벨 내성을 시험하기 위한 실용적인 방법 ····················· 178 0.1 일반사항 .......................... 178 O.2 정상적인 서비스 조건에서 SPD 방전 전류 시험 ··············· ................................................... 178 O.3 뇌전류에 의한 유도 시험 100000000000000000000000000000000000001100000000000 178 0.4 시스템 레벨 내성 시험의 권고 시험 분류(IEC 61000-4-5 에 따름)................................. 178 부속서 P (참고) 여러 부품이 포함된 SPD 시험 지침 --------------------------------------------------- 180 P.1 일반사항 ......................................... 180 P.2 저항/용량 트리거 제어와 직렬로 연결된 다중 스파크 갭의 예 180 P.3 용량성 트리거 제어 및 GDT + MOV 의 병렬 연결된 직렬 연결과 직렬로 연결된 2 개의 스파크 갭의 예 181 P.4 병렬 MOV 바이패스/트리거 제어를 사용하는 3 전극 GDT 의 예 ................................................... 181 P.5 GDT + MOV 트리거 제어가 있는 4 전극 간격의 예 ............................... ...................... 182 P.6 직렬 연결된 GDT 및 MOV 와 병렬인 스파크 갭의 예 ................... ................... 183 P.7 트리거 변압기가 있는 3 전극 간격의 예 ························ ................. 183 부속서 Q (참고) I 등급 시험된 SPD 와 관련된 미국의 예외 ................ ··············· 185 참고문헌 ............... ----------- 186 KS C IEC 61643-12:2020 해 설 ---- 188 -iii- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
43cc3c5e-ec11-4f6f-9b09-07947fc68142 | KSCIEC61643-12_KR | KS CIEC 61643-12:2020 머 리 말 이 표준은 산업표준화법 관련 규정에 따라 산업표준심의 회의 심의 를 거쳐 개정한 한국산업표준이다. 이에 따라 KS C IEC 61643-12:2002(2007 년 발행)는 개정되어 이 표준으로 바뀌었다. 이 표준은 저작권법의 보호 대상이 되는 저작물이다. 이 표준의 일부가 기술적 성질을 가진 특허권, 출원공개 이후의 특허출원, 실용신안권 또는 출원공개 후의 실용신안등록출원에 저촉될 가능성이 있다는 것에 주의 를 환기한다. 관계 중앙행정기관의 장과 산업표준심의 회는 이러한 기술적 성질을 가진 특허권, 출원공개 이후의 특허출원, 실용신안권 또는 출원공개 후의 실용신안등록출원에 관계되는 확인에 대하여 책임을 지지 않는다. IEC 61643 시리즈는 "저압 서지보호장치"라는 공통제목을 가지며, 모든 부의 목록은 IEC 웹사이트에 서 찾을 수 있다. -iv- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
15c8be57-67f0-49b9-b21d-67f73f3f776d | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 개 요 이 표준은 2020 년 제 3 판으로 발행된 IEC 61643-12, Low-voltage surge protective devices - Part 12: Surge protective devices connected to low-voltage power systems - Selection and application principles 를 기초로 기술적 내용 및 대응국제표준의 구성을 변경하지 않고 작성한 한국산업표준이다. 이 제 3 판은 2007 년 발행된 제 2 판을 취소, 대체하며 기술적으로 개정되었다. 비고 비영속적인 특성에 관하여 다음과 같은 상이한 실행 관행이 미국에 존재한다. 미국에서는 I 등 급 시험에 따라 시험된 SPD 가 필요하지 않다. 이러한 예외는 전체 표준에 적용된다. 이 판에는 이전 판과 관련하여 다음과 같은 중요한 기술적 변경사항을 포함한다. a) 적용범위: 1 500 V DC 삭제 b) 일부 정의 의 추가 또는 수정 c) 보호 필요성에 대한 4 절을 새롭게 추가 d) 분리기에 대한 새로운 정보 추가 e) SPD 의 특성 수정 f) SPD 선정 시 매개변수 목록 수정 g) 측정된 제한 전압에 대한 새로운 정보 추가 h) 일부 부속서 추가 또는 개정 0.1 일반사항 서지보호장치(Surge protective devices, 이하 SPD)는 명시된 조건에서 뇌 서지 및 스위칭 서지와 같 은 다양한 과전압 및 임펄스 전류로부터 전기 시스템과 장비를 보호하는 데 사용된다. SPD 는 환경 조건과 장비 및 SPD 의 허용 고장률에 따라 선정해야 한다. 이 표준은 SPD 선정에 유용한 특성에 대한 정보를 사용자에게 제공한다. 이 표준은 KS C IEC 62305(모든 부) 및 IEC 60364 시리즈를 참조하여 저압 시스템에서 SPD 의 사용 필요성을 평가하기 위한 정보를 제공한다. 또한 SPD 가 적용되는 전체 환경을 고려하며 SPD 의 선정 및 협조에 대한 정보를 제공한다. 예를 들면 보호 기기 및 시스템 특성, 절연 수준, 과전압, 설치 방 법, SPD 위치, SPD 협조, SPD 폐기 및 장비 고장 결과 가 있다. KS C IEC 62305-2 는 서지 및 낙뢰로 인한 위험을 평가하는 일반적인 방법을 제공한다. KS C IEC 60364-4-44 는 전기 설비에 가해지는 위험을 평가하는 간략한 방법을 제공한다. 제품의 절연 협조 요구사항에 대한 지침은 IEC 60664 시리즈가 제공한다. 안전(화재, 과전류 및 전기 적 충격) 및 설치에 대한 요구사항은 IEC 60364 시리즈가 제공한다. IEC 60364 시리즈는 계약자에게 SPD 설치에 대한 직접적인 정보를 제공한다. IEC TR 62066 에는 서 지 보호의 과학적 배경에 대한 자세한 정보가 포함되어 있다. -V- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
da3d5c3d-81d4-4a77-91e4-368c1c442675 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 0.2 이 표준의 구조를 이해하기 위한 중요사항 다음 목록은 이 표준의 구조를 요약하고 각 절과 부속서에서 다루는 정보의 개요를 제공한다. 주요 절은 SPD 선정 시 사용하는 요인에 대한 기본 정보를 제공한다. 4 절부터 7 절까지 제공한 정보의 더 자세한 사항을 얻고자 하는 독자는 관련 부속서를 참조하는 것이 좋다. 1 절은 이 표준의 범위를 설명한다. 2 절은 인용 표준을 나열하였으며 여기에서 추가 정보를 찾아도 된다. 3 절은 이 표준을 이해하는 데 유용한 정의 를 제공한다. 4 절은 서지 위험(SPD 의 사용이 이로운 경우 고려사항)에 대한 소개다. 5 절은 SPD 선정에 중요한 시스템 및 장비의 매개변수를 다룬다. 낙뢰에 의해 발생하는 스트레스 외 에도, 네트워크 자체에 의해 생성되는 스트레스, 즉 일시적인 과전압 및 스위칭 서지를 설명한다. 6 절은 SPD 선정을 위한 전기적 매개변수를 나열하고 해당 매개변수에 관해 설명한다. 이는 KS C IEC 61643-11 에서 제시한 매개변수와 관련이 있다. 7 절은 이 표준의 핵심이다. 이 절은(5 절에서 논의 한 바와 같이) 네트워크에서 오는 스트레스와(6 절에 서 논의 한 바와 같이) SPD 의 특성을 연관시킨다. 또한 SPD 가 제공하는 보호가 어떻게 SPD 설치의 영향을 받을 수 있는지 간략히 설명한다. SPD 선정을 위한 여러 단계가 제시되어 있으며, 설비에서 둘 이상의 SPD 를 사용할 때의 협조도 포함된다(SPD 협조에 대한 세부사항은 부속서 F 에서 확인할 수 있다). 부속서 A 는 연구와 함께 제공된 정보를 다루고 KS C IEC 61643-11 에서 사용한 시험 절차를 설명한다. 부속서 B 는 특정한 금속 산화 배리스터(MOV)의 경우에서 SPD 의 두 가지 중요한 매개 변수인 Uc 와 Up 사이의 관계에 대한 예시를 제공하며, Uc 와 네트워크의 공칭 전압 사이의 관계에 대한 예시도 제 공한다. 부속서 C 는 저압 시스템의 서지 전압에 관해 5 절에서 제시한 정보를 보충한다. 부속서 D 는 직접 뇌 전류가 발생할 경우 SPD 정격을 결정하는 데 사용하는 다양한 접지 시스템 간 의 뇌 전류 분배를 다룬다. 부속서 E 는 고압 시스템의 고장으로 인한 일시적인 과전압을 다룬다. 부속서 F 는 시스템에 둘 이상의 SPD 를 사용하는 경우 협조 규칙에 관한 7 절에서 제시한 정보를 보 충한다. 부속서 G 는 이 표준의 구체적인 사용 예를 제공한다. 부속서 H 는 4 절에서 제시한 위험 분석의 구체적인 사용 예를 제공한다. 부속서 I 는 시스템 스트레스에 관해 5 절에서 제시한 정보를 보충한다. 부속서 J 는 다양한 SPD 선정용 저압 시스템 기준에서의 SPD 적용에 관해 7 절에서 제시한 정보를 -vi- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
9cdcbb93-44b1-4a04-ac71-f4aeb79a0be8 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 보충한다. 부속서 K 는 전기 장비의 내성 수준과 절연 내력 간의 차이를 논의 한다. 부속서 L 은 일부 국가에서 사용하는 SPD 설치의 실제 예를 제공한다. 부속서 M 은 신호 및 전원 단자를 모두 갖춘 장비와 의 협조 문제를 논의 한다. 부속서 N 은 서지 조건에서의 퓨즈 내력에 대한 정보를 제공한다. 부속서 O 는 시스템 수준 내성을 시험하기 위한 실용적인 방법을 제공한다. 부속서 P 는 여러 부품이 있는 SPD 에의 시험 적용을 제공한다. - vii - 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
8a145d52-40a1-4f5f-b68c-52f6488d0fea | KSCIEC61643-12_KR | 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
4f8c01eb-d315-4954-a077-b7ac225224bf | KSCIEC61643-12_KR | 한국산업표준 KS C IEC 61643-12:2020 저압 서지보호장치 - 제 12 부: 저압 전력 시스템 보호용 서지보호장치 선정 및 적용지침 Low-voltage surge protective devices - Part 12: Surge protective devices connected to low-voltage power systems Selection and application principles 1 적용범위 이 표준은 50/60 Hz AC 전원 회로 및 최대 1 000 V RMS 정격 장비에 연결하는 SPD 의 선정, 운전, 위치, 협조에 대한 원칙에 대하여 기술한다. 해당 장치는 적어도 하나의 비선형 부품을 포함하고 있으며, 서지 전압을 제한하고 서지 전류를 분 산시키기 위한 것이다. 비고 1 필요한 경우 특수한 용도에 대한 추가 요구사항도 적용할 수 있다. 비고 2 IEC 60364 및 KS C IEC 62305-4 도 적용 가능하다. 비고 3 이 표준은 SPD 만 다루고 장비 내부에 통합된 서지보호부품(Surge protection components, 이 하 SPC)은 다루지 않는다. 2 인용표준 다음의 인용표준은 전체 또는 부분적으로 이 표준의 적용을 위해 필수적이다. 발행연도가 표기된 인 용표준은 인용된 판만을 적용한다. 발행연도가 표기되지 않은 인용표준은 최신판(모든 추록을 포함) 을 적용한다. KS C 9610-4-5, 전자파적합성(EMC) - 제 4-5 부: 시험 및 측정기술 - 서지 내성시험 KS C IEC 60364-4-44:2018, 저압전기설비 - 제 4-44 부: 안전을 위한 보호 - 전압 및 전기자기 장애 에 대한 보호 KS C IEC 60364-5-53, 저압전기설비 - 제 5-53 부: 전기기기의 선정 및 설치 - 안전, 절연, 개폐, 제 어 및 감시를 위한 보호장치 KS C IEC 60529, 외함의 밀폐 보호등급 구분(IP 코드) KS C IEC 60664-1:2007, 저압기기의 절연협조 - 제 1 부: 원칙, 요구사항, 시험 KS C IEC 61643-11:2011, 저전압 서지보호장치 - 제 11 부: 저전압 계통의 저압 서지보호장치 - 요구 사항 및 시험방법 1 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
7e02e6f1-8239-414e-92f6-b0e0bb2e196e | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 KS C IEC 62305-1:2010, 피뢰시스템 - 제 1 부: 일반원칙 KS C IEC 62305-2, 피뢰시스템 - 제 2 부: 리스크 관리 KS C IEC 62305-4, 피뢰시스템 - 제 4 부: 구조물 내부의 전기전자시스템 KS C IEC 62475:2010, 대전류 시험방법 - 시험 전류 및 측정 시스템의 정의 와 요구사항 IEC 61643-32, Low-voltage surge protective devices - Part 32: Surge protective devices connected to the d.c. side of photovoltaic installations - Selection and application principles 3 용어, 정의 및 약어 이 표준의 목적을 위하여 다음의 용어와 정의 를 적용한다. 참고 이 표준과 관련된 ISO 및 IEC 의 용어 데이터베이스는 다음과 같다. ISO 온라인 브라우징 (browsing) 플랫폼: https://www.iso.org/obp IEC 일렉트로피디아(Electropedia): http://www.electropedia.org 3.1 용어와 정의 3.1.1 서지보호장치(surge protective device) SPD 서지 전압을 제한하고 서지 전류를 분산시키기 위한 장치로 최소 하나 이상의 비선형 부품을 포함한다. 비고 SPD 는 적적할 연결 수단을 가지고 있는 완전한 부속품이다. [출처: KS C IEC 61643-11:2011, 3.1.1] 3.1.2 연속 동작 전류(continuous operating current) lc 각 모드에 최대연속 사용전압(Uc)을 가하였을 때, SPD 의 각 보호 모드를 통해 흐르는 전류 3.1.3 최대 연속 사용 전압(maximum continuous operating voltage) Uc SPD 의 보호 모드에 지속적으로 적용되는 최대 RMS 전압 비고 이 표준에서 정의 한 Uc 는 1 000 V 를 초과 할 수도 있다. [출처: KS C IEC 61643-11:2011, 3.1.11] 3.1.4 전압 보호 레벨(voltage protection level) Up 규정된 전압 급준도를 갖는 임펄스 스트레스와 주어진 진폭 및 파형의 방전 전류를 갖는 임펄스 스 트레스로 인해 SPD 단자에서 예상되는 최대 전압 비고 전압 보호 레벨은 제조자가 명시하며 다음과 같거나 커야 한다. · 스파크오버전압(적용되는 제품에 따라) 파두로부터 결정된 제한 전압. II 및/또는 I 등급 시험 의 경우, 각각 최대 In 및/또는 /imp 진폭에서의 잔류 전압에서 결정된 측정 제한 전압 2 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
da98d8aa-fa31-4c1b-82c3-9e816bdb9937 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 · III 등급 시험에서 조합파 발생기에 대해 결정된 최대 Uoc 까지의 측정 제한 전압 [출처: KS C IEC 61643-11:2011, 3.1.14, 수정됨 - 비고] 3.1.5 측정된 제한 전압(measured limiting voltage) 규정된 파형과 진폭의 임펄스 적용 시 SPD 의 단자에서 측정한 전압의 최대 크기 [출처 : KS C IEC 61643-11:2011, 3.1.15] 3.1.6 잔류 전압(residual voltage) Ures 방전 전류의 통과 로 인해 SPD 의 단자 간에 나타나는 전압의 파고값 [출처: KS C IEC 61643-11:2011, 3.1.16] 3.1.7 일시적 과전압 시험 값(temporary overvoltage test value) UT 일시적 과전압(TOV) 조건에서 스트레스를 시뮬레이션하기 위해 특정 지속 시간 IT 동안 SPD 에 인가 되는 시험 전압 비고 특정 지속 시간 IT 동안 Uc 보다 높은 전압 UT 로 스트레스를 가할 때 SPD 의 작용에 대한 정보 를 제공하는 제조자가 선언한 SPD 의 특성이다. 이러한 작용은 일시적 과전압을 인가한 후에도 성능에 변화가 없거나 고장이 나더라도 사람, 장비 혹은 시설에 아무런 해도 입히지 않는다. [출처 : KS C IEC 61643-11:2011, 3.1.17, 수정됨 - 비고를 추가] 3.1.8 전력 시스템의 일시적 과전압 값(temporary overvoltage value of the power system) UTOV 일정 위치에서 상대적으로 오랫동안 네트워크에 발생하는 전원 주파수 과전압 비고 1 TOV 는 LV 시스템(UTOV(LV)) 또는 HV 시스템(UTOV(HV)) 내부 결함으로 인해 발생할 수 있다. 비고 2 시스템의 특징이다. 일반적으로 최대 몇 초까지 지속되는 일시적 과전압은 일반적으로 스위 칭 동작 또는 결함(예를 들면 급작스런 부하 차단, 단상 결함 등) 및/또는 비선형성(철 공명 효과, 고조파 등)으로 인해 발생한다. 3.1.9 II 등급 시험을 위한 공칭 방전 전류(nominal discharge current for class II test) In 전류 파형이 8/20 인 SPD 를 통과 하는 전류의 파고 값 [출처: KS C IEC 61643-11:2011, 3.1.9] 3 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
73cf0774-e477-47b9-b8d7-8d566167767e | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 3.1.10 I 등급 시험을 위한 임펄스 방전 전류(impulse discharge current for class I test) /imp 명시된 시간 내에 명시된 전하 이동 Q 와 명시된 에너지 WIR 로 SPD 를 통하여 흐르는 방전 전류의 파고 값 [출처 : KS C IEC 61643-11:2011, 정의 3.1.10] 3.1.11 조합파(combination wave) 개방 회로 조건에서는 정의 된 전압 진폭(Uoc)과 파형을 특징으로 하고, 단락 조건에서는 정의 된 전류 진폭(lcw)과 파형을 특징으로 하는 파장 비고 SPD 에 적용되는 전압 진폭, 전류 진폭 및 파형은 2 옴의 조합파 발생기(CWG) 가상 임피던스 Z 와 DUT 의 임피던스에 의해 결정된다. [출처: KS C IEC 61643-11:2011, 3.1.22, 수정됨 - 비고에 "2 옴의"를 추가] 3.1.12 8/20 전류 임펄스(8/20 current impulse) 규약 파두 시간이 8 �s 이고 반값 도달 시간이 20 �s 인 전류 임펄스 비고 KS C IEC 62475:2010 의 10 절에서는 전류 임펄스의 규약 파두 시간, 반값 도달 시간 및 파형 허용 오차를 정의 한다. [출처 : IEC 61643-11:2011, 3.1.21, 수정됨 - 정의 에서 "공칭"을 삭제] 3.1.13 1.2/50 전압 임펄스(1.2/50 voltage impulse) 규약 파두 시간이 1.2 �s 이고 반값 도달 시간이 50 �s 인 전압 임펄스 비고 KS C IEC 60060-1(2010)의 7 절에서는 전압 임펄스의 규약 파두 시간, 반값 도달 시간 및 파형 허용 오차를 정의 한다. [출처 : KS C IEC 61643-11:2011, 3.1.20, 수정됨 - 정의 에서 "공칭"을 삭제] 3.1.14 열적 안정성(thermal stability) 온도상승을 일으키는 동작 책무 시험 이후, 규정된 주위 온도 조건에서 최대 연속 사용 전압을 SPD 에 인가할 때 시간이 지남에 따라 SPD 의 온도가 감소하는 상태 [출처: KS C IEC 61643-11:2011, 3.1.25, 수정됨 - "의 상태" 추가 및 "열적으로 안정적이다"를 삭제] 3.1.15 SPD 분리기(분리기)[SPD disconnector (disconnector)] 전원 시스템에서 SPD 또는 SPD 의 부품을 차단하기 위한 장치 비고 이 차단 장치는 안전용 절연 기능이 필요하지 않다. 이는 시스템의 지속적인 오동작을 방지하 기 위한 것으로 SPD 의 오동작을 표시하는 데 사용된다. 분리기는 내장형 또는 외장형(제조사 4 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
d749911d-1d29-4124-8a74-32e0a5a6a466 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 가 요구)일 수 있다. 예를 들어 과전류 보호 기능 및 열 보호 기능과 같은 두 가지 이상의 분 리기 기능이 있을 수도 있다. 해당 기능은 서로 다른 장치에 있을 수도 있다. [출처: KS C IEC 61643-11:2011, 3.1.28] 3.1.16 형식 시험(type tests) 제품을 대표하는 하나 이상의 품목에 하는 적합성 시험 [출처: KS C IEC 60050-151:2001, 151-16-16] 3.1.17 외함의 방진 및 방수 보호등급(degree of protection provided of enclosure) IP 위험한 부품에 대한 접근, 고형 이물질의 유입 및 유해한 물 유입에 대한 수납 보호 범위를 나타내 는 기호 IP 앞에 있는 분류 [출처: KS C IEC 61643-11:2011, 3.1.29]] 3.1.18 전압 강하[voltage drop(단위: %)] AU= [(Uin - Uout) / Uin ] x 100 % 여기에서 Uin 은 입력 전압이고 Uout 은 전체 정격 저항 부하가 연결된 상태에서 동시에 측정한 출력 전압이다. 이 파라미터는 2 포트 SPD 에만 사용된다. 3.1.19 2 포트 SPD 의 부하측 서지 내력(load-side surge withstand capability for a two-port SPD) SPD 의 회로 하부에서 발생하는 출력 단자의 서지를 견딜 수 있는 2 포트 SPD 의 성능 [출처: KS C IEC 61643-11:2011, 정의 3.1.18] 3.1.20 정격 단락 전류(short-circuit current rating) ISCCR 지정된 분리기와 함께 SPD 가 정격인 전력 시스템의 최대 예상 단락 전류 비고 별도의 입력 및 출력 단자가 있는 2 포트 SPD 또는 1 포트 SPD 의 경우 2 개의 정격 단락 전류 를 정의 해도 된다. 하나는 내부 단락(내부 작동부 단락)에 해당하고 다른 하나는 출력 단자에 서 직접적으로 외부 단락(부하 측 단락)에 해당한다(부하에서 오류가 발생한 경우). [출처: KS C IEC 61643-11:2011, 3.1.27, 수정됨 - 비고를 추가] 3.1.21 1 포트 SPD(one-port SPD) 특정 직렬 임피던스가 없는 SPD 비고 1 1 포트 SPD 에는 분리된 입출력 단자가 있을 수도 있다. 비고 2 그림 1 은 대표적인 1 포트 SPD 와 1 포트 SPD 의 일반적 구성도(그림 1c)를 나타낸다. 1 포트 SPD 는 병렬 연결(그림 1) 또는 전원 선로에 직렬(그림 1b)로 연결된다. 병렬 연결의 경우, 부 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. 5 | {}
cdb5826f-35f8-49ee-8432-ad4d52dea68d | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 하 전류는 SPD 의 입출력 단자를 통해 흐르지 않는다. 직렬 연결의 경우, 부하 전류는 SPD 의 입출력 단자를 통해 흐르며 부하 전류에 의해 온도가 상승하고 2 포트 SPD 처럼 최대 허 용 부하 전류가 정해져야 한다. 그림 3b ~ 그림 3d 는 조합파 발생기를 통해 8/20 임펄스가 적 용된 1 포트 SPD 의 다양한 반응을 나타낸다. 3.1.22 2 포트 SPD(two-port SPD) 분리된 입출력 단자 사이에 연결된 특정 직렬 임피던스를 갖는 SPD 비고 측정된 제한 전압은 출력 단자에서보다 입력 단자에서 더 높다. 따라서 보호 기기는 출력 단자 에 연결되어야 한다. 그림 2 는 대표적인 2 포트 SPD 를 나타낸다. 그림 3e 와 그림 3f 는 2 포트 SPD 가 조합파 발생기를 통해 적용된 8/20 임펄스에 응답하는 과정을 나타낸다. [출처: KS C IEC 61643-11:2011, 3.1.3, 수정됨 - 비고를 추가] 6 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
9cb62618-14e8-4532-9056-ed20240c0f22 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) a ▼ ▲ b C SPD 식별부호 a 1 포트 SPD b 입출력 단자가 분리된 1 포트 SPD C 1 포트 SPD 의 일반적 표시 그림 1 - 1 포트 SPD 예 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 7 | {}
c7ceb1a6-526e-46df-9ac2-7d44119b7477 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) Z a ▼ ▲ Z U b ▼ ▲ Z C SPD 식별부호 a 3 단자 2 포트 SPD b 4 단자 2 포트 SPD C 2 포트 SPD 의 일반적 표시 Z 입출력 단자 사이의 직렬 임피던스 그림 2 - 2 포트 SPD 예 8 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f73940f3-6252-4e81-90b7-2d1b156fa3ba | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) Ip a 0 (us) / 0 U b 0 t U 0 / U d 0 T U Z 0 1 U 식별부호 ¦ a ¦ 적용된 전류 파형 ¦ d 1 포트 조합형 SPD 출력 전압 파형 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ b ¦ 전압 제한형 SPD 출력 전압 파형 ¦ e 2 포트 조합형 SPD 출력 전압 파형 ¦ ¦ C ¦ 전압 스위칭형 SPD 출력 전압 파형 ¦ ¦ ¦ f ¦ 필터링 기능이 있는 2 포트 전압 제한형 ¦ SPD 출력 전압 파형 ¦ 비고 전압 레벨은 대표적인 것일 뿐 실제 값을 표시한 것은 아니다. 그림 오른쪽의 U 는 SPD 의 출 력 전압을 의미하며 왼쪽의 U 는 배리스터 기호다. 그림 3 - 조합파 발생기 임펄스에 대한 1 포트와 2 포트 SPD 의 출력 전압 응답 [출처: KS C IEC 61643-11:2011, 3.1.2, 수정됨 비고 2 및 그림 1 부터 그림 3 을 추가] 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 9 | {}
b9c3d6fb-a130-4006-87cd-36c6e4c32e3e | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 3.1.23 전압 스위칭형 SPD(Voltage-switching SPD) 서지가 없을 때에는 고 임피던스를 나타내지만 전압 서지에 반응하여 임피던스가 급격하게 낮아질 수 있는 SPD 비고 1 전압 스위칭형 SPD 에 사용되는 부품의 일반적인 예로는 스파크 갭, 가스 방전 튜브 및 실리콘 기반 부품(예를 들면 사이리스터)가 있다. 이러한 부품을 "크로바형" 부품이라 부르기도 한다. 비고 2 전압 스위칭형 장치는 U 에 대한 I 가 불연속적인 특징이 있다. 그림 3c 는 대표적인 전압 스위 칭형 SPD 가 조합파 발생기를 통해 적용된 임펄스에 응답하는 과정을 나타낸다. [출처: KS C IEC 61643-11:2011, 3.1.4, 수정됨 - 비고 2 를 추가] 3.1.24 전압 제한형 SPD(Voltage-limiting SPD) 서지가 없는 경우 고 임피던스를 나타내지만 서지 전류와 전압이 상승하면 임피던스가 연속적으로 감소하는 SPD 비고 1 전압 제한형 SPD 에 사용되는 부품의 일반적인 예로는 금속 산화 배리스터와 애벌런치 항복 다이오드가 있다. 이러한 부품을 "클램핑형" 부품이라 부르기도 한다. 비고 2 전압 제한형 장치는 U 에 대한 I 가 연속적인 특징이 있다. 그림 3b 는 대표적인 전압 제한형 SPD 가 조합파 발생기를 통해 적용된 임펄스에 응답하는 과정을 나타낸다. [출처 : KS C IEC 61643-11:2011, 3.1.5, 수정됨 - 비고 2 를 추가)] 3.1.25 조합형 SPD(combination SPD) 전압 스위칭형 부품과 전압 제한형 부품 모두를 포함하는 SPD 비고 1 SPD 는 전압 스위칭형, 전압 제한형 또는 둘 다를 나타낸다. 비고 2 그림 3d 와 그림 3e 는 다양한 일반적 조합형의 SPD 가 조합파 발생기를 통해 적용된 임펄스 에 응답하는 과정을 나타낸다. [출처: KS C IEC 61643-11:2011, 3.1.6, 수정됨 - 비고를 추가] 3.1.26 보호 모드(mode of protection) 보호 부품을 포함하는 단자 사이의 의도된 전류 경로(예를 들면 선과 선, 선과 접지, 선과 중성선, 중 성선과 접지) [출처: KS C IEC 61643-11:2011, 3.1.8] 3.1.27 속류(follow current) If 전원 시스템에 의해 공급되어 방전 전류 임펄스에 이어서 SPD 를 통해 흐르는 순간 최대 전류 [출처: KS C IEC 61643-11:2011, 3.1.12] 10 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
10f15459-e5f0-494e-9f91-55823926e346 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 3.1.28 최대 방전 전류(maximum discharge current) Imax 제조사의 사양에 따라 8/20 파형과 크기를 가지며 SPD 에 흐르는 전류의 최댓값 비고 Imax 는 In 보다 크거나 같다. [출처: KS C IEC 61643-11:2011, 3.1.48] 3.1.29 (성능의) 감소[degradation (of performance)] 요구되는 성능으로부터 장치 또는 시스템의 동작 성능이 원치 않게 영구적으로 상실되는 현상 비고 내구성은 SPD 가 유효 수명 동안 설계된 조건을 견딜 수 있는 능력을 나타내는 척도다. 성능 감소에 대한 신뢰도를 제공하기 위해 두 가지 유형의 시험을 한다. 첫 번째는 동작 책무 시험 이고 두 번째는 열화 시험이다. 그러나 이 두 가지 시험을 혼용하여 사용해도 된다. 동작 책무 시험은 정의 된 전류 파형을 규정된 횟수만큼 SPD 에 인가하여 수행한다. SPD 특성의 허용 변 경은 KS C IEC 61643-11 에 명시되어 있다. 열화 시험은 SPD 에 규정된 크기의 전압을 규정된 시간 동안 인가한 상태로 규정된 온도에서 진행한다. SPD 특성의 허용 변경은 KS C IEC 61643-11 에 명시되어 있다(이 시험은 현재 검토 중). 이러한 시험은 SPD 기대 수명을 결정하 는 데 사용할 수 있으며 다음과 같은 사항도 고려하는 것이 좋다. · 교체 정책 · 위치 및 접근 가능성 · 허용 고장률 · 동작 실행 [출처: KS C IEC 61643-11:2011, 3.1.26, 수정됨 - 비고를 추가] 3.1.30 누전 차단기(residual current device) RCD 정상적인 사용 조건에서 전류를 투입, 전달, 차단하고 지정된 조건에서 누설 전류가 주어진 값에 도 달할 때 접점을 개방하기 위해 설계된 기계적 스위칭 장치 비고 누전 차단기는 누설 전류를 감지 및 평가하고 전류를 투입 및 차단하도록 설계된 다양한 개별 요소의 조합일 수 있다. [출처 : IEC 60050-442:1998, 442-05-02] 3.1.31 시스템의 공칭 전압(nominal voltage of the system) 시스템 또는 기기를 설계하고 특정 동작 특성이 나타나도록 적용되는 전압(예를 들면 230/400 V) 비고 1 정상적인 시스템 조건하에서 공급 단자의 전압은 공급 시스템의 허용 오차만큼 공칭 전압과 다를 수 있다. 이 표준에서 허용 오차는 ±10 %를 적용한다. 비고 2 접지에서 시스템 상의 공칭 전압을 Un 이라 한다(IEC 60038 참조). 비고 3 시스템의 선 대 중성선 전압을 U0 라 한다. 11 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
0650a07b-bf8f-48c7-ab52-6cc3d1ca6be3 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 비고 4 시스템의 선 대 선 전압을 U 라 한다. 3.1.32 임펄스 시험 분류(impulse test classification) 3.1.32.1 I 등급 시험(Class I tests) I 등급 시험용 방전전류 /imp, /imp 와 동등한 크기의 파고값을 갖는 8/20 전류파형, 1.2/50 전압파형으로 수행하는 시험 [출처 : KS C IEC 61643-11:2011, 3.1.34.1, 수정됨 - "관련된 경우"를 추가)] 3.1.32.2 II 등급 시험(class II tests) 1.2/50 파형의 전압과 함께 공칭방전전류 In 으로 수행하는 시험 [출처: KS C IEC 61643-11:2011, 3.1.34.2, 수정됨 - "관련된 경우"를 추가] 3.1.32.3 III 등급 시험(class III tests) 1.2/50 전압파형 및 8/20 전류파형의 조합파 발생기로 수행하는 시험 [출처 : KS C IEC 61643-11:2011, 3.1.34.3] 3.1.33 정격 부하 전류(rated load current) 儿 SPD 의 출력측에 연결된 저항상 부하에 공급되는 최대 연속 정격 실효 전류 비고 이는 분리된 입출력 단자의 SPD 에 한에서만 적용된다. [출처: KS C IEC 61643-11:2011, 3.1.13, 수정됨(비고 추가)] 3.1.34 SPD 위치에 있는 전력 시스템의 최대 연속 사용 전압(maximum continuous operating voltage of the power system at the SPD location) Ucs SPD 설치 지점에서 SPD 에 영구적으로 인가되는 최대 RMS 전압 비고 1 이는 전압 변동률 및/혹은 전압 강하와 상승만을 감안한다. 실제 최대 시스템 전압이라고도 하며 Uo 에 직접적으로 연관되어 있다. 비고 2 이 전압은 고조파, 고장, TOV 또는 과도 현상 등을 포함하지 않는다. 3.1.35 전압 스위칭형 SPD 의 트리거 전압(trigger voltage of a voltage switching SPD) 전압 스위칭 SPD 가 높은 임피던스에서 낮은 임피던스로 급격하게 바뀌는 시점의 최대 전압 값 비고 전압 스위칭 SPD 는 갭 이외의 부품(예를 들면 실리콘 기반 부품)에 기반을 두어도 된다. 12 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
668ff931-6953-488e-a2b6-500c8daf2676 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 [출처 : KS C IEC 61643-11:2011, 3.1.36, 수정됨 - 비고를 추가)] 3.1.36 뇌 보호 시스템(lightning protection system) LPS 낙뢰로 인한 구조물의 물리적 손상을 줄이기 위해 사용되는 전체 시스템 비고 이는 외부 피뢰 시스템과 내부 피뢰 시스템으로 구성된다. [출처: KS C IEC 62305-3:2010, 3.1] 3.1.37 멀티서비스형 SPD(multiservice SPD) 서비스 간에 기준 본드가 제공되는 단일 외함에서 전원, 통신, 신호 등 둘 이상의 서비스를 보호하는 서지보호장치 3.1.38 누설 전류(residual current) /PE 제조자의 사용설명서에 따라 설치되고 기준 시험 전압(UREF)으로 전압이 가해질 때 SPD 의 PE 단자 를 통해 흐르는 전류 비고 예를 들면 전기적 충격으로부터 보호하기 위해(IEV 195-02-09 에 따라) 안전 목적으로 보호 도 체(PE)를 제공한다. [출처 : KS C IEC 61643-11:2011, 3.1.40, 수정됨 - 비고를 추가] 3.1.39 예상 단락 전류(prospective short-circuit current of a power supply) /p 매우 작은 임피던스로 회로가 단락이 된 경우, 정해진 회로부에 흐르는 전류 비고 이 대칭분 예상전류는 RMS 값으로 표현한다. [출처: KS C IEC 61643-11:2011, 3.1.38] 3.1.40 속류 차단 정격(follow current interrupt rating) /fi 분리기의 작동 없이 SPD 가 차단할 수 있는 예상 단락 전류 [출처: IEC 61643-11:2011, 3.1.39] 3.1.41 I 등급 시험에 대한 특성 에너지(specific energy for class I test) W/R 임펄스 방전 전류 /imp 에 의해 단위 저항 1 �에서 소모되는 에너지 비고 이는 전류의 제곱을 시간으로 적분한 W/R = fi2dt 와 동일하다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. 13 | {}
dc9deb06-4caa-4c61-974c-f24ba9747dd7 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 [출처: KS C IEC 61643-11:2011, 3.1.37] 3.1.42 정격 임펄스 전압(rated impulse voltage) Uw 과도 과전압에 대해 절연체의 규정된 내절연능력을 특징으로 하는 기기나 그 부품에 제조자가 지정 한 임펄스 내전압 값 비고 이 표준에서는 상도체와 접지 사이의 내전압만 고려한다. [출처: KS C IEC 60664-1:2007, 3.9.2, 수정됨 - 비고를 추가] 3.1.43 임펄스 내전압(impulse withstand voltage) 규정 조건하에서 절연 파괴를 일으키지 않으며 규정된 형태와 극성의 임펄스 전압의 최대 파고 값 [출처: KS C IEC 60664-1:2007, 3.8.1] 3.1.44 과전압 범주(overvoltage category) 과도 과전압 조건을 정의 하는 숫자 [출처 : KS C IEC 60664-1:2007:3.10, 수정됨] 3.1.45 과전류 보호 장치(overcurrent protective device) OCPD 전기 회로의 도체 전류가 지정된 시간 동안 미리 정해진 값을 초과 할 경우 전기 회로를 차단하기 위 해 제공되는 장치 [출처: KS C IEC 60050-826:2004, 826-14-14] 3.1.46 유효 전압 보호 레벨(effective voltage protection level) Up/f SPD 의 전압 보호 레벨로 인해 발생한 SPD 어셈블리의 접속점에서의 전압, 그리고 존재하는 경우 분리기 및 연결 도선의 전압 강하 3.1.47 단락형 SPD(short-circuiting SPD) 공칭 방전 전류 In 을 초과 하는 서지 전류가 부과 되면 의도적으로 내부 회로가 단락하는 특성으로 변 경하는 II 등급 시험에 따라 검사 받은 SPD [출처: KS C IEC 61643-11:2011, 3.1.7] 3.1.48 상태 표시기(status indicator) SPD 또는 SPD 부품의 동작 상태를 나타내는 장치 비고 이러한 표시기는 시각표시장치 및/또는 가청 경보와 가까이 위치해 있을 수 있으며, 원격 신호 14 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
9a1d4ce2-8fd3-422d-928d-78ff4dba85ac | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 및/또는 출력 접점 성능을 가질 수 있다. [출처 : KS C IEC 61643-11:2011, 3.1.41] 3.1.49 개방 회로 전압(open circuit voltage) Uoc 시험품의 접속점에서 걸리는 조합파 발생기의 개방 회로 전압 [출처: KS C IEC 61643-11:2011, 3.1.23] 3.1.50 조합파 발생기 단락 전류(combination wave generator short-circuit current) /cw 조합파 발생기와 시험품의 접속점으로 흐르는 예상 단락전류 비고 SPD 가 조합파 발생기에 연결되면 장치에 흐르는 전류는 일반적으로 /cw 보다 작다. [출처: KS C IEC 61643-11:2011, 3.1.24] 3.1.51 출력 접점(output contact) SPD 의 주회로와 분리된 회로에 포함되어 있으며 분리기 또는 상태 표시기에 결합되는 접점 [출처: KS C IEC 61643-11:2011, 3.1.42] 3.1.52 멀티모드형 SPD(multimode SPD) 하나 이상의 보호 모드를 가지는 SPD 형식 또는 하나의 장치로 제공되는 전기적으로 상호 결합된 SPD 의 조합 [출처: KS C IEC 61643-11:2011, 3.1.43, 수정됨] 3.1.53 전체 방전 전류(total discharge current) /Total 전체 방전 전류시험에서 멀티모드형 SPD 의 PE 또는 PEN 도체를 통해 흐르는 전류 비고 1 이 시험은 멀티모드형 SPD 의 여러 보호모드가 동시에 작동할 때 발생하는 누적 효과 를 검사 하기 위해 사용한다. 비고 2 ITotal 은 특히 시험등급 I 에 따라 시험된 SPD 와 관련이 있으며, IEC 62305 시리즈에 따라 피뢰 용 등전위본딩을 위해 사용된다. 비고 3 PEN 도체는 보호용 접지 도체와 중성점 도체의 기능을 결합한 도체이다(IEV 195-02-12 를 따 른다). [출처 : KS C IEC 61643-11:2011, 3.1.44, 수정됨(비고 3 항목 추가)] 15 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
ce6baac4-cad9-4446-a2dd-c6c34dc10597 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 3.1.54 기준 시험 전압(reference test voltage) UREF SPD 의 보호모드, 전력 시스템의 공칭 전압, 전력 시스템 내 구조 및 전압 조절에 의해 결정되는 시 험용 RMS 전압 값 [출처: KS C IEC 61643-11:2011, 3.1.45] 3.1.55 단락형 SPD 의 단락 전환 서지 전류(transition surge current rating for short-circuiting SPD) Itrans 단락형 SPD 를 단락상태로 변환시키는 공칭 방전 전류 /n 보다 큰 8/20 파형의 전류 값 [출처: KS C IEC 61643-11:2011, 3.1.46] 3.1.56 공간 거리 결정 전압(voltage for clearance determination) Umax 공간 거리 결정을 위해 서지 인가 시 측정된 최대 전압 [출처: KS C IEC 61643-11:2011, 3.1.47, 수정됨] 3.1.57 배리스터 전압(Varistor voltage) Vv 규정된 시간 동안 규정된 전류(일반적으로 1 mA)에서 측정된 MOV 양단의 전압 [출처: KS C IEC 61643-331, 3.2.3] 3.2 이 표준에서 사용되는 약어 및 약어 목록 ¦ 약어 목록 ¦ 약어 목록 ¦ ¦ --- ¦ --- ¦ ¦ Emax ¦ 최대 에너지 내력 ¦ ¦ /c ¦ 연속 동작 전류 ¦ ¦ /cw ¦ 조합파 발생기 단락 전류 ¦ ¦ If ¦ 속류 ¦ ¦ /fi ¦ 속류 차단 정격 ¦ ¦ /imp ¦ I 등급 시험용 임펄스 방전 전류 ¦ ¦ /L ¦ 정격 부하 전류 ¦ ¦ Imax ¦ 최대 방전 전류 ¦ ¦ /n ¦ II 등급 시험용 공칭 방전 전류 ¦ ¦ /p ¦ 전원의 예상 단락 전류 ¦ ¦ /PE ¦ UREF 에서의 누설 전류 ¦ ¦ /sc ¦ CWG 단락 전류 ¦ ¦ ISCCR ¦ 정격 단락 전류 ¦ ¦ /Total ¦ 멀티모드형 SPD 의 전체 방전 전류 ¦ 16 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
87b623b8-1c7a-42b3-8d60-717621612b2d | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ¦ 약어 목록 ¦ 약어 목록 ¦ ¦ --- ¦ --- ¦ ¦ Itrans ¦ 단락형 SPD 의 단락 전환 서지 전류 ¦ ¦ L ¦ 인덕턴스 ¦ ¦ NG ¦ 대지 뇌방전 밀도 ¦ ¦ Nk ¦ 커라우닉 수치 ¦ ¦ PSPD ¦ 협조된 SPD 시스템이 보호함에도 불구하고 장치가 손상될 확률 ¦ ¦ Q ¦ (임펄스 전류의) 전하 ¦ ¦ IT ¦ 시험용 TOV 인가 시간 ¦ ¦ Ucs ¦ 전력 시스템의 최대 연속 사용 전압 ¦ ¦ Umax ¦ 공간거리결정전압 ¦ ¦ Un ¦ 시스템 상 대 접지의 공칭 전압 ¦ ¦ Uo ¦ 시스템의 선 대 중성점 전압 ¦ ¦ Uoc ¦ 조합파 발생기의 개방 회로 전압 ¦ ¦ Up ¦ 전압 보호 레벨 ¦ ¦ UREF ¦ 기준 시험 전압 ¦ ¦ Ures ¦ 잔류 전압 ¦ ¦ UT ¦ 일시적 과전압 시험 값 ¦ ¦ UTov ¦ 전력 시스템의 일시적 과전압 값 ¦ ¦ UTOV(HV) ¦ 고압 시스템 내부 네트워크의 일시적 과전압 값 ¦ ¦ UTOV(LV) ¦ 저압 시스템 내부 네트워크의 일시적 과전압 값 ¦ ¦ Uw ¦ 정격 임펄스 전압 ¦ ¦ VV ¦ 배리스터 전압 ¦ ¦ W/R ¦ 특성에너지 ¦ ¦ Zf ¦ (조합파 발생기의) 가상 임피던스 ¦ ¦ △U ¦ 전압 강하(in %) ¦ ¦ ABD ¦ 애벌런치 부품 ¦ ¦ dB ¦ 데시벨 ¦ ¦ CWG ¦ 조합파 발생기 ¦ ¦ DFIG ¦ 이중 공급 유도 발전기 ¦ ¦ DUT ¦ 시료 ¦ ¦ EB ¦ 등전위 본딩 바 ¦ ¦ EMC ¦ 전자기 호환성 ¦ ¦ GDT ¦ 가스 방전관 ¦ ¦ HV ¦ 고전압 ¦ ¦ IGBT ¦ 절연 게이트 양극성 트랜지스터 ¦ ¦ IP ¦ 외함의 보호 등급 ¦ ¦ LEMP ¦ 낙뢰 전자기 펄스 ¦ ¦ LPS ¦ 뇌 보호 시스템 ¦ ¦ LPZ ¦ 뇌 보호 영역 ¦ ¦ LTE ¦ 통과 에너지 ¦ ¦ LV ¦ 저전압 ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 17 | {}
34bd497e-6dbc-42d1-8119-476129a3b0fe | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ¦ 약어 목록 ¦ 약어 목록 ¦ ¦ --- ¦ --- ¦ ¦ MEB ¦ 주 등전위 본딩 ¦ ¦ MOV ¦ 금속 산화 배리스터 ¦ ¦ HVA ¦ 고전압 A (중전압, < 50 kV) ¦ ¦ MV ¦ 중전압 ¦ ¦ OCPD ¦ 과전류 보호 장치 ¦ ¦ PDS ¦ 배전 시스템 ¦ ¦ PE ¦ 보호 접지 ¦ ¦ PV ¦ 태양광 발전 ¦ ¦ PWM ¦ 펄스 폭 변조 ¦ ¦ RCD ¦ 누전 차단기 ¦ ¦ TOV ¦ 일시적 과전압 ¦ ¦ SPC ¦ 서지 보호 부품 ¦ ¦ SPD ¦ 서지보호장치 ¦ 4 보호의 필요성 SPD 의 사용 여부는 사용자가 중시하는 광범위한 매개변수에 따라 결정된다. 고려하면 좋은 매개변 수는 H.2 에 나열되어 있다. 위험 분석 수행에 대한 자세한 내용은 다음의 두 표준에서 확인할 수 있다. KS C IEC 62305-2(전체 분석용) KS C IEC 60364-4-44(선로에 또는 선로 근처로의 뇌방전에 대해서만 보호가 필요한 구조). 이 방 법의 사용법에 대한 예는 H.1 에 설명되어 있다. SPD 가 주어진 서지 조건(KS C IEC 62305-2 에 정의 된 PSPD)에서 수명 말기에 도달할 확률은 LPS 가 있는 경우에 대해 KS C IEC 62305-2 에 나타낸다. SPD 의 서지 내력이 증가하면 PSPD 가 감소한다. 비고 관할 기관이 위험 평가 요구 없이 특정 인가에 대한 서지 보호의 필요성을 지정하는 경우 이 기관은 필요성 및 보호 등급에 대한 결정을 명시한다. 경우에 따라 SPD 의 필요성이 아닌, SPD 의 시험 등급을 정의 하기 위해 위험 평가를 추가로 수행할 수 있다. 5 보호해야 하는 저압 전력 시스템과 장비 5.1 일반사항 SPD 의 필요성 때문에 설치를 검토하는 경우, 두 가지 요인을 고려해야 한다. · 예상되는 과전압, 전류 형태와 레벨을 포함하여 SPD 가 설치될 저압 전력 배전 시스템의 특성 · 보호 대상 기기에 대한 특성 18 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
45d27b39-1105-4e39-81b0-918f0e7fee6b | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 5.2 저압 전력 시스템 5.2.1 일반사항 저압 전력 시스템은 기본적으로 시스템의 접지(TN-C, TN-S, TN-C-S, TT, IT)형태와 공칭 전압, 과전압 및 서지 전류 형태로 특징지을 수 있다. 이 표준에서 과전압 및 서지 전류는 다음과 같이 3 그룹으로 분류된다. · 뇌 · 스위칭 · 일시적 과전압 5.2.2 뇌 과전압과 서지 전류 대부분의 경우 뇌의 스트레스는 SPD 의 등급 시험과 KS C IEC 61643-11 에 정의 된 관련 전류 또는 전 압 값(limp, In or Uoc)을 선정할 때 고려해야 할 주요 요소다. 뇌 스트레스(파형, 전류 또는 전압의 크기에 기반함)의 평가는 SPD 를 적절하게 선정하기 위해 필요하 다. SPD 의 전압 보호 레벨이 이러한 조건에서 기기를 보호하는 데 적합할지를 확인하는 것도 중요하다. 뇌 보호 시스템(LPS)이 있는 경우, 설비의 인입구에 있는 SPD 가 필수이며 I 등급 시험에 따라 검사한 SPD 를 선정해야 한다. 뇌 보호 시스템(LPS)을 갖춘 건물의 경우, KS C IEC 62305-1 에서 뇌의 스트레 스에 대한 추가 정보를 확인할 수 있다. /imp 의 선정에 관해서는, 부속서 J.3 에서 더 많은 정보를 찾을 수도 있다. 많은 경우, 구조물의 외부에 설치된 전기 설비에서 더 높은 스트레스가 발생한다(예를 들면 구조물에 연결된 외부 전기 선로에 직격뢰가 떨어지거나 서지가 유도되는 경우). 구조물 내부에서의 스트레스 는 회로 구성, SPD 상호작용, 임피던스의 변화로 인해 시설의 인입구에서 내부 회로로 이동하면서 감소한다. 위험 분석은 KS C IEC 60364-4-44(H.2 참조)에서 설명한 단순화된 방법을 적용하거나 KS C IEC 62305-2 에서 설명한 상세한 위험 분석을 적용하여 수행한다. 위험 분석을 수행하려면 사용자는 최소 한 다음 사항을 알아야 한다. 국부 대지 뇌방전 밀도 NG(구조물이 위치한 지역을 고려한 연평균 대지 뇌방전 밀도, 연평균 km2 당 뇌방전). 최근의 뇌 위치 시스템(LLS)은 합리적인 정확도로 NG 에 대한 정보를 제공한다. · 전기 설비의 노출 지하 매설 케이블을 통해 전원이 공급될 때 서지 보호의 필요성 여부를 결정하려면 다음과 같은 사 항을 고려하는 것이 좋다. - 설비 주변에 LPS 가 있다. 지하 케이블의 길이가 적절한 서지 감쇠를 제공하기에 충분한가?(IEC 62305 시리즈에 따르면, 서 지가 허용 가능한 수준으로 감소한다고 간주하기 위해서는 최소 1 000 m 의 길이가 필요하다.) 토양의 저항이 큰 곳에서 지하 케이블이 직격뢰로 인한 영향을 받을 수 있다(케이블이 차폐되거나 금속 도관 안에 있는 경우 제외) 설비와 연결된 변압기의 HV(고전압) 측을 공급하는 가공선에서 대기 중에서 발생한 높은 서지가 19 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
a9e66c2e-af8e-4027-a35f-b64c67f37c7d | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 나타날 수도 있다. 지하 케이블로 구동되는 건물의 크기 또는 높이가 건물에 가해지는 직격뢰의 위험을 크게 증가시 킬 만큼 충분히 높다. 전원 시스템과 기기에 영향을 미칠 수 있는 기타 가공선 설비(전화선, 안테나 시스템 등)가 있다. 많은 건물이 단일 전력 공급 시스템에 연결되어 있으며, SPD 가 설치되지 않은 이러한 건물은 전기 시스템에 심한 스트레스를 받을 수 있다. 뇌격/사고 근접(즉, 구조물에 직접 또는 가까이, 전력선에 직접 또는 근처)에 따른 파형의 형태와 전 류 크기의 평가는 KS C IEC 62305-1:2010 의 부속서 E 에 나와 있다. 이러한 각 손상 발생원에 대한 위 험 평가는 KS C IEC 62305-2 에 설명하는 방법을 사용하여 수행할 수 있다. 부속서 C 와 부속서 I 는 뇌 스트레스에 대한 보다 자세한 정보를 명시하고 있다. SPD 진입부에 있는 전기 시설 내의 장비는 설비의 서지 내력에 영향을 미칠 수도 있으므로 서지 내 력을 측정하는 것이 좋다. 5.2.3 스위칭 과전압 피크 전류와 전압으로 표시되는 이러한 스트레스는 일반적으로 뇌 스트레스에 비해 낮지만, 지속 시 간이 훨씬 길거나(예를 들면 결함 및 퓨즈 동작으로 인한 과도 현상) 에너지가 낮지만 훨씬 더 자주 발생한다(예를 들면 접촉기 작동, 역률 보정을 위한 커패시터 뱅크, IGBT 등). 그러나 경우에 따라 특 히 구조물 내부 또는 스위칭 전압 소스와 인접한 곳의 스위칭 스트레스는 뇌로 인해 발생된 스트레 스보다 더 높을 수 있다. 적합한 SPD 를 선정하기 위해서는 이러한 스위칭 서지와 관련된 에너지를 결정하는 것이 필요하다. 일반적으로 SPD 의 서지 정격 선정은 낙뢰로 인한 스트레스를 기반으로 한다. 설비 안의 배전 시스템 내에서 발생하는 서지에 대한 추가 정보는 IEEE 표준 C62.41.1-2002 의 하위 절 4.3 및 C62.72-2016 의 하위 절 5.2.2 를 참조한다. 이러한 유형의 서지는 배전 시스템이나 연결된 장비에 항상 즉각적인 손상을 입히는 것은 아니지만 종종 시스템 작동을 중단하고 방해한다. 이러한 서지는 배전 시스템 외부의 소스에서 예상되는 것과 크게 다른 파형 및 진폭을 가지며 이렇게 내부 적으로 생성된 서지의 영향을 특별히 완화하도록 설계된 SPD 가 필요할 수도 있다. 이러한 서지를 대표하는 추가 권고 파형 및 시험 진폭은 IEEE 표준 C62.41.2-2002 에 정의 되어 있다. 해당 서지에 대한 추가 정보는 IEC TR 62066:2002, Surge overvoltages and surge protection in low-voltage AC power systems General basic information 에서 찾을 수 있다. 부속서 C 와 부속서 I 는 스위칭 스트레스에 대한 자세한 정보를 제공한다. 스위칭 서지에 대한 추가 정보는 IEC TR 62066 에서 확인할 수 있다. 5.2.4 일시적 과전압 UTOV 5.2.4.1 일반사항 모든 SPD 는 그 수명 동안 전력 시스템의 정상 전압을 초과 하는 일시적 과전압 UTOV 에 노출될 수 있다. 일시적 과전압의 범위는 진폭과 시간 2 변수로 나타낸다. 과전압의 지속 시간은 일차적으로 전원 시 20 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
2c408a4f-ce26-4190-b75e-c71b095b6de4 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 스템(고압 시스템과 SPD 가 연결된 저압 시스템이 포함된다)의 접지에 의해 좌우된다. 시스템의 일시 적 과전압을 결정할 때, 시스템의 선-중성선 및 선-선 전압을 고려해야 한다(표 E.3 참조). TOV 는 저압 시스템에 장애가 있는 경우 L-N 혹은 L-PEN 사이의 저압 시스템에서 발생할 수도 있다. 단락 상태의 경우 OCPD 가 작동할 때까지 정의 되지 않은 시간 동안 중성선 손실의 경우 무제한적인 시간 동안 TOV 는 고압 시스템과 저압 시스템의 접지 구성 또는 두 시스템 간의 가능한 상호 작용에 따라 고압 시스템에서 접지 결함이 발생할 경우 N-PE 또는 L-PE 간 제한된 시간 동안 저압 시스템에서 발생할 수 있다. SPD 는 시스템 TOV 를 보호하기 위한 것이 아니다. SPD 는 KS C IEC 61643-11 에 설명한 대로 안전한 방법으로 견디거나 견디지 못할 수도 있다. 중성선 손실로 인한 TOV 는 매우 오랜 시간(최대 몇 시간) 동안 선-중성선 과전압을 초래하며, 이러 한 과전압은 전원 시스템의 선-선 전압까지 전압 값에 도달할 수도 있다. SPD 는 이러한 TOV 로부터 보호될 수 없다. 이러한 경우 POP(상용주파 과전압 보호 장치)를 사용할 수 있다. 비고 POP 는 IEC 63052 에서 정의 하고 있다. 부속서 E 와 부속서 I 은 일시적 과전압에 대한 자세한 정보를 제공한다. 5.2.4.2 표준값 KS C IEC 60364-4-44 는 저압 전력 시스템에서 예상되는 UTOV 의 최댓값을 제시하고 있다(이 값에 대 한 보다 상세한 산출 내용은 부속서 E 참조). 낮은 값은 SPD 의 설치 위치, 전력 시스템의 형태 등과 같은 다양한 요인에 의해 좌우될 수 있다. 전기 소비 설비에서의 최대 일시적 과전압 값은 표 1 에 나타낸다. SPD 시험에서 사용한 값은 부속서 E 에 나와 있다. 21 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
366d9b2b-13e1-4fa1-a298-9b44bc08e782 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 표 1 - KS C IEC 60364-4-44:2018 에 명시된 최대 TOV 값 ¦ UTOV 발생 ¦ 시스템 ¦ UTOV(HV) 최댓값 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 상과 접지 사이 ¦ TT,IT ¦ Uo + 250 V 지속 시간 > 5s ¦ ¦ 상과 접지 사이 ¦ TT,IT ¦ Uo + 1 200 V 지속 시간 5s 까지 ¦ ¦ 중성선과 접지 사이 ¦ TT,IT ¦ 250 V 지속 시간 > 5s ¦ ¦ 중성선과 접지 사이 ¦ TT,IT ¦ 1 200 V 지속 시간 5s 까지 ¦ ¦ 위의 값은 고압 전력 시스템 고장과 연관된 극한값이며 부속서 E 에 명시된 전력 시스템 형태에 의 해 산출된 것이다. ¦ 위의 값은 고압 전력 시스템 고장과 연관된 극한값이며 부속서 E 에 명시된 전력 시스템 형태에 의 해 산출된 것이다. ¦ 위의 값은 고압 전력 시스템 고장과 연관된 극한값이며 부속서 E 에 명시된 전력 시스템 형태에 의 해 산출된 것이다. ¦ ¦ UTOV 발생 ¦ 시스템 ¦ UTOV(LV) 최댓값 ¦ ¦ 상과 중성선 사이 ¦ TT 와 TN ¦ V3 x Uo ¦ ¦ 위의 값은 저압 시스템에서의 중성선 도체의 손실과 관련이 있다. ¦ 위의 값은 저압 시스템에서의 중성선 도체의 손실과 관련이 있다. ¦ 위의 값은 저압 시스템에서의 중성선 도체의 손실과 관련이 있다. ¦ ¦ 상과 접지 사이 ¦ IT 시스템(TT 시스 템: 비고 1 참조) ¦ V3 x Uo ¦ ¦ 위의 값은 저압 시스템에서 상도체의 우발적 접지와 관련이 있다. ¦ 위의 값은 저압 시스템에서 상도체의 우발적 접지와 관련이 있다. ¦ 위의 값은 저압 시스템에서 상도체의 우발적 접지와 관련이 있다. ¦ ¦ 상과 중성선 사이 ¦ TT, IT 와 TN ¦ 1.45 x Uo5s 까지의 지속 시간 ¦ ¦ 위의 값은 선도체와 중성선 도체 사이의 단락과 관련이 있다. ¦ 위의 값은 선도체와 중성선 도체 사이의 단락과 관련이 있다. ¦ 위의 값은 선도체와 중성선 도체 사이의 단락과 관련이 있다. ¦ ¦ 비고 1 이 정도로 높은 TOV 가 TT 시스템에서도 역시 최대 5 초 동안 발생할 수 있다는 것이 밝혀 졌다. 자세한 사항은 부속서 E 참조. 이 조건은 KS C IEC 60364-4-44 에서 다루지 않는다. 비고 2 변압기 위치에서의 최대 TOV 값은 위의 표와 다를 수 있다(높거나 낮음). 자세한 사항은 부 속서 E 참조 U0 은 저압 시스템의 선-중성선 전압이다. ¦ 비고 1 이 정도로 높은 TOV 가 TT 시스템에서도 역시 최대 5 초 동안 발생할 수 있다는 것이 밝혀 졌다. 자세한 사항은 부속서 E 참조. 이 조건은 KS C IEC 60364-4-44 에서 다루지 않는다. 비고 2 변압기 위치에서의 최대 TOV 값은 위의 표와 다를 수 있다(높거나 낮음). 자세한 사항은 부 속서 E 참조 U0 은 저압 시스템의 선-중성선 전압이다. ¦ 비고 1 이 정도로 높은 TOV 가 TT 시스템에서도 역시 최대 5 초 동안 발생할 수 있다는 것이 밝혀 졌다. 자세한 사항은 부속서 E 참조. 이 조건은 KS C IEC 60364-4-44 에서 다루지 않는다. 비고 2 변압기 위치에서의 최대 TOV 값은 위의 표와 다를 수 있다(높거나 낮음). 자세한 사항은 부 속서 E 참조 U0 은 저압 시스템의 선-중성선 전압이다. ¦ 5.3 보호 기기의 특성 과도 현상에서 보호해야 할 기기의 특성은 다음과 같은 두 가지 시험방법에 의해 결정된다. KS C IEC 60664-1 에 따른 기기 시험의 임펄스 내력. 이는 절연 협조 시험일 뿐이다. 시험 중에는 기기의 전원이 차단된다. KS C IEC 61000-4-5 따른 기기 시험의 임펄스 내성. 이 시험은 기기의 동작 내력을 평가한다. 시험 은 주로 서로 다른 레벨에서 조합파 발생기(1.2/50, 8/20)를 사용하여 수행한다. 전원이 공급되는 작동 중에 오작동, 오류 또는 고장이 발생할 수 있는 위치를 결정한다. 기기를 사용하는 과도 환경과 관련하여 임펄스 내력 및 임펄스 내성 수준을 비교하여 SPD 의 잠재적 필요성을 결정한다. 자세한 사항은 부속서 O 를 참조한다. 비고 선정된 SPD 는 보호 기기의 임펄스 내력 Uw 보다 낮은 유효 보호 레벨 Up/f 를 제공할 수 있다. 기기의 연속 작동이 임계 상태에 도달하였고 기기의 임펄스 내력보다 Up/f 가 낮은 경우, 7.4.5 를 참조한다. Up 은 7.5.2 및 7.5.6 에 따라 선정할 수 있다. 6 서지보호장치 6.1 SPD 의 기본 기능 이 표준에서 고려하는 SPD 는 보호 기기 외부 또는 내부에 설치된 SPD 다. 22 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
5638ca50-0a2e-4603-9f1c-9bc06b0d44a0 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 비고 전기 및 전자 장비는 여기에서 고려하지 않은 과전압 부품(예를 들면 KS C IEC 61643-331 에 준수하는 MOV)으로 보호되곤 한다. 이 표준에서는 IEC 61643-11 을 준수하는 장치(SPD)와 함 께 제공되는 과전압 보호만 고려한다. 전력 시스템에서 이들의 기능은 다음과 같다. · 서지가 없는 경우: SPD 는 SPD 가 사용되는 시스템의 동작 특성에 별다른 영향을 주지 않아야 한다. · 서지 발생 시간 동안: SPD 는 전압(대부분의 경우 보호 레벨 Up 보다 훨씬 낮음)을 제한하기 위해 임피던스를 낮추고 서지 전류를 전환하여 서지 전압에 반응한다. 서지는 SPD 설계에 따라 SPD 에 전력이 실린 속류가 흐르게 할 수도 있다(전력이 실린 속류를 갖는 SPD). · 서지 발생 이후: SPD 는 서지 발생 이후 높은 임피던스 상태로 회복되며, 속류가 흐르지 못하게 한다. SPD 의 특성은 정상적인 운전 조건하에서 위의 기능을 발휘한다. 정상 운전 조건은 전력 시스템 전 압의 주파수, 부하 전류, 고도(예를 들면 기압), 습도 및 주위 온도 등으로 규정된다. 6.2 추가 요구사항 SPD 의 적용 환경에 따라 다음과 같은 사항이 추가로 필요하다. · 직접 접촉(KS C IEC 60364-4-41 에 의거)에 대한 SPD 보호 · SPD 고장 시 안전성 SPD 는 서지가 설계된 최대 에너지와 방전 전류 능력보다 클 경우, 고장이 발생하거나 파손될 수 있 다. 이 표준에 따라 SPD 의 고장 모드는 개방 회로 또는 단락 회로로 구분된다(6.5.4 참조). 비고 이 조항에서는 SPD 의 특정 기술과 관련된 KS C IEC 61643-11(SPD 고장 작동)의 SPD 분류 개념을 다루지 않는다. 그러나 단락형 SPD 로 분류되는 SPD 는 정의 상 수명이 다하면 단락이 된다. 일반적으로 시스템에 거의 영향을 끼치지 않으므로 SPD 의 고장을 감지하기 어렵다. 그러나 시스템 은 더 이상 보호되지 않는다. 다음 서지 발생 이전에 고장난 SPD 가 교체되도록 하기 위해서 고장 표시 기능이 필요하다(7.6.3 참조). 단락 전류는 전원에서 고장난 SPD 를 통해 흐르게 된다. KS C IEC 61643-11 의 단락 내력 시험은 단락 전류가 흐르는 동안 소모되는 에너지로 인해 화재 위험이 발생하지 않는지 확인하기 위해 수행된다. KS C IEC 61643-11 에 따라 선언된 SPD 고장 작동(개방 회로 또는 단락 회로 작동)과 관계없이 과부 하 시 SPD 를 보호하기 위해 적합한 차단 장치가 필요할 수도 있다(7.5.2.4 참조). 6.3 SPD 의 등급 분류 6.3.1 SPD: 등급 분류 서지보호장치는 KS C IEC 61643-11 에 따라 다음과 같이 분류된다. ¦ 포트 수: ¦ 1 개 또는 2 개 ¦ ¦ --- ¦ --- ¦ ¦ 설계 기술: ¦ 전압 스위칭, 전압 제한 또는 혼용 ¦ 23 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
ee7d377f-a72f-4504-bc6a-d87e0135ac4e | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ¦ SPD 시험 등급: ¦ I,II, III ¦ ¦ --- ¦ --- ¦ ¦ 위치: ¦ 옥내 또는 옥외 ¦ ¦ 접근성: ¦ 접근 가능, 접근 불가능(손이 닿지 않음) ¦ ¦ 부착 방식: ¦ 고정식 또는 이동식 ¦ ¦ 분리기: ¦ 위치(외부, 내부, 외부와 내부 모두, 없음) 및 기능(열, 누설 전류, 과전류) ¦ ¦ 백업 과전류 보호: ¦ 명시되었거나 없음 ¦ ¦ 보호 등급: ¦ SPD 외함(IP)에서 제공 ¦ ¦ 온도 범위: ¦ 정상 혹은 확장 ¦ 비고 정의 에서 실외라 함은 밀폐된 저장소의 외부를 의미한다. 따라서 이러한 SPD 는 모든 외부 조 건에서 적용되어야 한다. 내부라 함은 밀폐된 저장소의 내부를 의미한다. 따라서 이러한 SPD 는 내부 환경 조건에서 적용되어야 한다. 손이 닿지 않는 범위라 함은 도구나 기타 장비를 사 용하지 않고는 충전부에 접근할 수 없음을 의미한다. 상기사항의 일부는 적용된 기술과 연계되어 있으며, 제조자에 의해 정의 되어 있다. 6.3.2 대표적 설계 방식과 구성 형태 SPD 에서 사용되는 주요 보호 부품은 다음과 같이 두 가지 형태로 분류된다. 전압 제한 부품: 금속 산화 배리스터(MOV, KS C IEC 61643-331 참조), 애벌런치 항복 다이오드 (ABD, KS C IEC 61643-321 참조) 또는 서프레서 다이오드(KSCIEC 61643-321 참조) 등 전압 스위칭 부품: 에어 갭, 가스 방전관(GDT, KS C IEC 61643-311 참조), 사이리스터, 서지 서프 레서(TSS, KS C IEC 61643-341 참조), 트라이액(KS C IEC 61643-341 참조) 등 이러한 부품을 기반으로 한 대표적인 SPD 의 설계는 그림 4 에 나타낸다. 단일 전압 제한 부품(그림 4a): 전압 제한형 SPD 단일 전압 스위칭 부품(그림 4b): 전압 스위칭형 SPD 전압 제한과 스위칭 부품 조합(그림 4c 및 그림 4d): 조합형 SPD 24 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
822289f0-9de5-4877-87c0-74efcc931429 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 a b ![image](/image/placeholder) ※ U C d 식별부호 a 전압 제한 부품 b 전압 전환 부품 C 전압 스위칭 부품과 직렬 연결된 전압 제한 부품 d 전압 스위칭 부품과 병렬 연결된 전압 제한 부품 그림 4 - 부품과 부품 조합의 예 SPD 는 간단한 서지 보호 부품으로 구성해도 되지만, 표시기, 분리기, 퓨즈, 인덕터, 커패시터, 열 차 단 및 정온도 계수 서미스터, 그리고 기타 부품을 포함해도 된다. SPD 는 일반적으로 1 포트 SPD (3.1.21 참조)와 2 포트 SPD(3.1.22 참조)로 분류된다. 다중 부품이 있는 SPD 에 적용하는 시험에 대한 자세한 내용은 부속서 P 를 참조한다. 6.4 SPD 의 특성 6.4.1 KS C IEC 61643-11 에 명시된 운전 조건 6.4.1.1 표준 운전 조건 · 주 전원의 주파수는 47 Hz ~ 63 Hz AC 이다. · 고도는 2 000 m 를 초과 하지 않아야 한다. · 동작 온도: 표준 범위 -5 °C ~ +40 °C, 확장 범위 -40 °C ~ +70 °C · 실내 온도 조건의 상대 습도는 표준 범위의 경우 5 % ~ 95 %, 확장 범위의 경우 5 % ~ 100 %이어 25 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
560224dd-291f-4c1f-9731-d953a14d35f1 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 야 한다. 표준 범위는 온도나 습도를 조절하지 않은 내후성 위치에서 실내용 SPD 를 다룬다. 확장 범위는 비 내후성 위치에서 실외용 SPD 를 다룬다. 비고 1 사용자는 SPD 를 적용하는 위치(실외, 실내 등)를 설정하며, 주변 온도 조건이 표준 또는 확 장 범위 이내에 있는지 결정한다. 비고 2 일반적으로 보관 온도 범위는 동작 온도 범위보다 크다. 6.4.1.2 비표준 운전 조건 SPD 가 비표준 운전 조건에 노출되면 SPD 의 설계 또는 적용 시 특별하게 고려해도 되며 제조자의 주의 를 환기시키는 것이 좋다. 태양 복사: 대부분의 SPD 는 태양 복사에 노출되지 않는다. 일반적으로 태양 복사는 형식 시험 중에 고려되지 않는다. SPD 가 태양 복사에 노출되는 경우 이를 고려하고 그에 따른 시험을 하는 것이 좋다. 비고 일반적으로 SPD 외함의 보호 레벨은 IP2X 보다 크다. 경우에 따라 다른 값이 사용될 수 있다 (예를 들면 실외용 SPD 의 경우). 6.4.2 SPD 선정 시 매개변수 목록 다음 사항은 사용자가 SPD 를 적합하게 선정하는 데 필요한 통상 매개변수 목록이다. 비고 이러한 매개변수 중 일부는 보호 모드별로 정의 되었다. a) Uc 최대 연속 사용 전압 b) UT 일시적 과전압 시험 값 및/또는 SPD 를 설계할 때 전력 시스템의 종류 c) I 등급 시험의 /imp d) In 11 등급 시험용 공칭 방전 전류 e) III 등급 시험의 Uoc f) Up 전압 보호 레벨 g) 고장 모드(제조자가 선언한 경우) h) ISCCR 정격 단락 전류 i) /fi 속류 차단 정격(전압 제한형 SPD 의 경우 제외) j) /L 정격 부하 전류(입출력 단자가 분리된 2 포트 SPD 또는 1 포트 SPD 의 경우) k) 전압 강하(2 포트 SPD 의 경우) 1) /PE 누설 전류(보호 도체용 단자가 있는 SPD 의 경우) m) Itrans 단락 전환 서지 전류(단락 SPD 의 경우) n) 필요한 경우, 외부 분리기의 정격 및 특성 o) /max 최대 방전 전류(선택사항) 26 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
1391c397-0150-42de-8456-dd44bc3dbb39 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 p) /Total 멀티모드형 SPD 의 총 방전 전류(제조사가 선언한 경우) q) 2 포트 SPD 에 대한 부하 측 서지 내력(제조사가 선언한 경우) r) 보호 모드(보호 모드가 두 개 이상인 SPD 의 경우) s) du/dt 전압 상승률(제조사가 선언한 경우) 6.5 SPD 의 특성에 대한 부가 정보 6.5.1 상용 주파수 전압과 관련된 정보 6.5.1.1 Uc 최대 연속 사용 전압, lc 연속 동작 전류 및 누설 전류 /PE Uc 는 표준 조건에서 SPD 특성(노화, 열 폭주 등)에 대한 변화를 최소화할 수 있을 정도로 높아야 한다. lc 는 Uc 가 인가될 때 SPD 를 통해 흐르는 전류의 값이다. 접지(PE) 단자를 통해 흐르는 전류가 있다 면 이를 누설 전류 /PE 라 한다. 이 전류 /PE 는 과전류 장치 또는 이 밖의 다른 보호 장치(예를 들면 RCD) (KS C IEC 60364-5-53:2001 의 531.2.1.2 참조)의 불필요한 동작을 방지하기 위해 SPD 를 선정하 는 데 사용된다. 비고 lc 는 KS C IEC 61643-11 에서 측정하지 않으며 선택적 매개변수다. 6.5.1.2 일시적 과전압 특성 SPD 의 일시적인 과전압 특성은 일반적으로 전압(전력 주파수에서) 대 시간(최대 몇 초)의 곡선에서 몇 개의 점(전압/시간)으로 나타낸다. KS C IEC 61643-11 에 의해 정의 되는 TOV 의 지속 시간은 다음과 같이 3 가지로 한정된다. · HV 측 결함으로 인한 TOV 200 ms · LV 시스템의 결함으로 인한 TOV 5 초 · 중성선 손실로 인한 TOV 120 분 그리고 관련 시험 전압 값을 UT(일시적 과전압 시험 값)라 한다. SPD 의 성능에 허용할 수 없는 변화가 일어나지 않고 TOV 시험을 견디거나 안전하게 고장이 나도 된다. KS C IEC 60364-5-53 에 따라 설치된 SPD 는 저압 전력 시스템의 결함으로 인한 TOV 에 견뎌도 된다(표 E.3 의 5 초에 대한 TOV 값 참조). 제조자가 설치 지침서에 주 RCD 의 상부인 중성선과 PE 사이의 TT 시스템에 설치해도 된다고 선언 한 SPD 도 고압 전력 시스템의 결함으로 인한 TOV 에 견뎌야 한다(표 E.3 의 200 ms 에 대한 TOV 값 참조). 일시적 과전압 시험 값은 KS C IEC 61643-11 에 따라 제조자가 선언해야 한다. 비고 높은 일시적 과전압 내력 및 낮은 전압 보호 레벨을 모두 갖춘 SPD 를 선정하기는 어려울 수 있다. 27 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
317c48b2-d4b7-4d4b-ba0f-46d8b0a55152 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 사용자는 SPD 의 일시적 과전압 시험 값과 전력 시스템에서 발생하는 일시적 과전압(UTov)을 비교하 여 가장 적합한 SPD 를 선정할 수 있다. SPD 시험에 사용된 표준 값은 표 E.3 에 제시되어 있다. 제조자의 데이터 시트는 UT(일시적 과전압 시험 값) 또는 SPD 가 설계한 전력 시스템의 형태를 제공 하여야 한다. SPD 에 적합한 시스템의 형태가 제공된 경우, 필요한 모든 시험이 요구된 UT 값으로 수 행되었으므로 KS CIEC 60364-4-44 에 정의 된 TOV 를 준수하는 시스템에 대해 UT 와 UTOV 를 비교할 필 요가 없다. 이제 SPD 가 설계한 전력 시스템의 형태는 사용자의 작업을 단순화하기 위해 데이터 시 트에서 제공되는 것이 일반적이다. 6.5.2 서지 전류 관련 정보 6.5.2.1 일반사항 다음은 서지 파형의 전압, 전류와 시간적 특성과 관련된 사항이다. SPD 가 노출될 것으로 예상되는 스트레스에 따라 다양한 서지 파형과 레벨이 시험에 사용된다. SPD 에 적합한 시험 등급을 선정하는 지침은 KS C IEC 61643-11 의 개요에 명시되어 있으며 다음과 같다. 시험에는 세 가지 등급이 있다. I 등급 시험은 부분적으로 흐르는 뇌 전류에 대한 시뮬레이션을 목적으로 한다. I 등급 시험을 받는 SPD 는 일반적으로 뇌 보호 시스템으로 보호된 건물의 인입 선로 등과 같이 노출 정도가 높은 지 점에 설치할 것을 권고한다. II 등급 또는 III 등급 시험을 받는 SPD 는 지속시간이 짧은 임펄스에 적용한다. SPD 를 선정 시 시험 등급과 SPD 가 정격되는 임펄스의 크기를 모두 고려하는 것이 필요하다. II 등급 시험 또는 III 등급 시험을 받는 SPD 는 대부분 직접적인 임펄스에 노출 정도가 낮은 지점에 설치할 것을 권고한다. III 등급 시험을 받은 SPD 는 인입 및 하위 배전반에서 사용할 수 있으며, III 등급 시험을 받은 SPD 는 장비와 가까운 위치에서 사용하는 것이 좋다. 비고 1 II 등급 시험은 SPD 에 전류를 주입한다. III 등급 시험은 SPD 에 전압을 인가하는데, 전류는 SPD 의 특성에 따라 좌우된다. SPD 에 있는 표시는 시험 중 SPD 를 통해 흐른 실제 전류가 아니라 사용한 발전기와 관련이 있다. 비고 2 SPD 가 받은 시험 등급은 정사각형에 T 로 표기하는 형식을 사용하여 명판에 제공한다. T1 는 I 등급 시험, 'T2" 는 II 등급 시험, "T3"는 III 등급 시험, 또는 "시험 등급"을 단어로 작성한다. 6.5.2.2 In: 공칭 방전 전류(8/20) II 등급 시험을 만족하는 SPD 의 경우, 이는 측정된 제한 전압을 결정하기 위한 하나의 시험 매개변수 로 사용되는 전류이다(다른 시험은 전압 스위칭 및 조합형 SPD 에 대한 파두 스파크오버 전압 시험 이다). 이 전류는 동작 책무 시험에도 사용된다(15 회 인가). In 는 현장에서 자주 발생할 것으로 예상되는 전류에 해당한다. In 의 우선 값은 다음과 같다. 0.05; 0.1; 0.25; 0.5; 1.0; 1.5; 2.0;2.5; 3.0; 5.0; 10; 15 및 20kA 28 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
6e8bd294-aabb-4a33-aa4c-5aa2737bad7b | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 KS C IEC 60364-5-53 은 설치 인입에서 최소 5kA 를 요구한다. 6.5.2.3 /imp: 전류 임펄스 방전(e.g.10/350) I 등급 시험을 만족하는 SPD 의 경우, /imp 는 I 등급 시험의 추가 동작 책무 시험에 사용되는 시험 매개 변수다. 시스템의 SPD 위치에서 발생할 수 있는 최대 방전 전류와 연관된다. 비고 파형 8/20 과 크기 limp 를 갖는 임펄스는 측정된 제한 전압을 결정하기 위해 사용된다(다른 시험 은 전압 스위칭 및 조합형 SPD 에 대한 파두 스파크오버 전압 시험이다). 이는 동작 책무 시험 에 사용된다(15 회 인가). KS C IEC 61643-11 에 따른 /imp (Q, W/R)의 우선 값은 표 2 에 나타낸다. 표 2 - /imp 의 우선 값 ¦ /imp kA ¦ Q C ¦ W/R kJ/� ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 25 ¦ 12.5 ¦ 156 ¦ ¦ 20 ¦ 10 ¦ 100 ¦ ¦ 12.5 ¦ 6.25 ¦ 39 ¦ ¦ 10 ¦ 5 ¦ 25 ¦ ¦ 5 ¦ 2.5 ¦ 6.25 ¦ ¦ 2 ¦ 1 ¦ 1 ¦ ¦ 1 ¦ ¦ ¦ ¦ ¦ 0.5 ¦ 0.25 ¦ ¦ 비고 10/350 파형은 표 2 의 요구사항을 만족하는 대표적인 파형이다. ¦ 비고 10/350 파형은 표 2 의 요구사항을 만족하는 대표적인 파형이다. ¦ 비고 10/350 파형은 표 2 의 요구사항을 만족하는 대표적인 파형이다. ¦ 6.5.2.4 Imax: 최대 방전 전류 Imax 는 선택적 시험 매개변수다. 동작 책무 시험에서 Imax 에는 임펄스가 없다. 시스템의 SPD 위치에서 거의 발생하지 않을 것으로 예상되는 최대 방전 전류와 연관된다. 제조자가 Imax 를 선언할 때 파고값 Imax 를 갖는 8/20 전류 임펄스를 추가로 인가하고 잔류 전압을 측 정하여 기록하여야 한다. 제한 부품을 기반으로 하는 SPD 의 경우 전압 Umax 는 In 에서의 잔류 전압과 같거나 더 크다. 6.5.2.5 Itrans: 단락 전환 서지 전류(단락 SPD 의 경우) Itrans 는 In 보다 큰 8/20 임펄스로 단락 SPD 를 단락시키는 전류에 해당한다. 이 전류는 단락 전류 동작 시험을 위한 사전 조정 시에도 사용된다. Itrans 의 값은 In 의 우선 값 중 선정된다. 6.5.3 SPD 가 제공하는 전압 보호 수준 관련 정보 6.5.3.1 측정된 제한 전압 a) I 등급과 II 등급 시험 29 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
0773de32-9b9e-4cb1-a23d-7e3a5d830184 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 측정된 제한 전압은 다음 2 종류의 시험을 수행함으로써 결정된다. 다양한 8/20 파 전류에서의 잔류 전압의 측정 1.2/50 에서의 파두 스파크오버 전압의 측정(전압 스위칭 및 조합형 SPD 에만 해당) 다음 전압 가운데 제일 큰 것을 측정된 제한 전압으로 한다. 8/20 파 전류 임펄스 범위에 대한 잔류 전압, 파두 및 파고값이 I 등급 시험에서는 /imp 크기의 0.1 배부터 1 배까지, II 등급 시험에서는 In 의 0.1 배부터 1 배까지 또는 1.2/50 파동을 사용하는 파두 스파크오버 전압 예를 들어, 전압 제한 부품이 있는 SPD 의 경우, 그림 5 는 금속 산화 배리스터(MOV)의 대표적인 잔류 전압 곡선(Ures 대 1)을 나타낸다. 이는 Imax 에서의 전류에 대한 SPD 의 잔류 전압이 In 에서의 잔류 전압과 Imax 가 선언되었을 때의 잔류 전압보다 크다는 것을 보여준다. /max 에서 이 전압이 전 압 보호 레벨보다 높고, 특히 보호 대상 기기의 임펄스 내전압보다 높다면, 이러한 스트레스에서 SPD 가 견뎌 내더라도 기기는 보호되지 않을 수 있다. 따라서 SPD 전압 보호 레벨과 서지 전류 내력은 이러한 사항을 고려하여 선정되어야 한다. ![image](/image/placeholder) MOV Chart Type: line 1 mA In Imax item_01 0.4Ures 0.8Ures 2.0Ures 식별부호 U1 In 에서의 잔류전압 U2 /max 에서의 잔류전압 R 몇 kA 의 범위 그림 5 - 금속 산화 배리스터(MOV)에 대한 Ures 대 /의 일반적인 곡선 전압 스위칭 부품(예를 들면 스파크 갭 장치, 가스 방전관 등)이 있는 SPD 의 경우 임펄스 스파크오 버 전압은 인가된 과도 전압의 상승률(du/dr)에 따라 좌우된다. 일반적으로 과도 전압 상승률(dv/dr)이 증가하면 임펄스 스파크오버 전압이 상승한다. 임펄스 스파크오버 전압은 정의 된 du/dt 에서의 통계적 인 값이므로 측정된 값에는 확산이 있을 수 있다(그림 6 참조). 30 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
bee5470a-6a8b-4633-a3bf-e39061c04e57 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 Chart Type: line Si B T item_01 50kV 25kV 25kV 식별부호 a 높은 상승률 10 kV/�s b 낮은 상승률 1 kV/�s St 스파크오버 시간의 확산 SU 스파크오버 전압의 확산 그림 6 - 스파크 갭의 일반적 곡선 b) III 등급 시험 SPD 의 III 등급 시험에는 조합파 발생기가 사용된다. 0.1 x Uoc 에서 Uoc 까지 조합파 발생기 임펄스 로 시험하는 동안 측정된 최댓값이 측정된 제한 전압으로 사용된다. 6.5.3.2 전압 보호 레벨 Up Up 는 제조자에 의해 명시된다. 정의 에 따라서, 이는 제한 전압의 가장 높은 값과 같거나 더 크다. 제 조자가 이 값을 선정할 때 제조 오차를 고려해야 한다. 실제로 SPD 가 제공하는 보호 수준이 선언된 Up 보다 더 나은 경우가 드물지 않다. 몇몇 경우에만, 제조자는 데이터 시트에 곡선 U 또는 Ures 대 / 또는 1 의 몇 가지 값에 대한 U 또는 Ures 의 표를 발행한다. 설치 위치에서 SPD 를 통해 흐르는 전류 가 Up 를 결정하기 위해 사용되는 전류보다 낮으면, 더 나은 보호를 위해 이 전압 값(U 또는 Ures)을 사용할 수 있다. 우선 전압 보호 레벨은 다음과 같다. 과전압 범주와 보호 대상 기기의 공칭 전압에 따라 (0.08, 0.09, 0.10, 0.12, 0.15, 0.22, 0.33, 0.4, 0.5, 0.6, 0.7, 0.8, 0.9, 1.0, 1.2, 1.5, 1.8, 2.0,2.5, 3.0, 4.0, 5.0, 6.0,8.0, 10) kV. 부속서 B 는 금속 산화 배리스터(MOV)를 기반으로 한 전압 제한 SPD 에 대한 Uc 와 Up 간의 관계 예 를 제공한다. 6.5.4 SPD 고장 시 SPD 의 상태와 관련된 정보 SPD 의 고장 모드는 서지 전류 및 전압의 크기, 횟수, 파형의 형태, 전원 시스템의 단락 용량 및 고 장 시 SPD 에 적용된 전압값 등에 의해 좌우된다. 이 표준에서는 2 개의 SPD 를 제시하고 있다. 단락 회로(또는 낮은 임피던스) 31 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
9be6b30c-4028-4f15-b89c-3f91c338bcb9 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 - 개방 회로(또는 높은 임피던스) 비고 1 이 절의 맥락에서, 이는 SPD 의 특정 기술과 관련된 KS C IEC 61643-11:2011, 5.12 항(SPD 고 장 모드)의 SPD 분류 개념을 다루지 않는다. 그러나 5.12.2(단락형 SPD)에 따라 분류된 SPD 는 수명이 다하면(정의 에 의해) 단락이 된다. 가끔 SPD 는 일정 시간 동안 중간 상태로 진입하기도 한다. 이러한 상태는 에너지 흡수를 수반하며, 최종적으로 개방 회로(자체적으로 또는 분리기나 상부 과전류 보호 장치와 함께) 또는 단락 상태를 유도한다. 이 표준에서는 이러한 상태를 일시적인 것으로 간주하므로 다루지 않는다. 비고 2 중간 상태 - 제조자가 지정한 것보다 매개변수 수준이 낮지만(나쁨) SPD 는 고장이 난 상태 가 아니다. SPD 특성의 변화가 반드시 고장으로 간주되는 것은 아니다. 이 주제는 6.5.7 에서 다룬다. 6.5.5 ISCCR: 정격 단락 전류와 /fi: 속류 차단 정격 SPD 는 단독으로 또는 분리기 및/또는 과전류 보호와 함께 제조자가 선언한 정격 단락 전류 ISCCR 을 견뎌야 한다. 이 값은 제조자가 선언한 분리기 및/또는 과전류 보호와 관련하여 KS C IEC 61643-11 에 서 정의 하고 시험된다. SPD 는 용해된 물질을 태우거나, 탄화하거나, 배출하지 않고, 또는 외함에 개 구부를 만들어 시험을 통과 하여야 한다. SPD 는 전원 lp 의 예상 단락 전류가 내단락 전류보다 큰 곳에 서 사용하지 않아야 할 필요가 있다. 또한 제조자가 권고하는 적합한 분리기 및/또는 과전류 보호 장 치가 구비되어 정상적으로 동작되는지 확인할 필요가 있다. ISCCR 값은 규정된 분리기 및/또는 과전류 보호 장치와 함께 사용할 때의 SPD 정격 값이다. 이 값은 필요한 경우 외부 분리기의 정격 및 특성 뿐만 아니라 제품이 납품될 때 제조자 설명서에 제공된다. 전압 제한형이 아닌 SPD 의 경우, 속류는 전력 시스템이 공급하는 파고 전류이며 방전 전류 임펄스 가 인가된 후 SPD 를 통해 흐른다. 속류 차단 정격 ln 는 SPD 가 분리기의 동작 없이 차단할 수 있는 예상 단락 전류다. 전압 제한형이 아닌 SPD 를 선정할 때는 속류 차단 정격(ki)을 고려해야 한다. 이 정보는 납품될 제품과 함께 제조사 설명서에 제공된다. 설치 규칙에 따라 SPD 보호를 위해 사용되 는 외부 분리기 또는 과전류 보호 장치는 과전류 보호 장치에 대한 관련 IEC 표준 또는 해당하는 경 우 현지 국가 표준을 준수해야 한다. 6.5.6 IL: 정격 부하 전류와 △U: 전압 강하(2 포트 SPD 또는 입출력 단자가 분리된 1 포트 SPD) 전력선에 연결된 2 포트 또는 1 포트 SPD 의 경우 장비 부하 전류가 정격 부하 전류 IL 을 초과 하지 않 도록 하는 것이 필요하다. 비고 부하의 형태도 고려해야 한다. 예를 들어 어떤 부하에는 RMS 값의 3 배에 달하는 돌입 전류가 흐 를 수도 있다. 이러한 파고 전류는 2 포트 SPD 의 직렬 소자 내부에 추가로 열을 발생시킬 수 있다. 또한 2 포트 SPD 를 설치 시 하부에 있는 기기의 허용 한계를 벗어나는 전압 강하가 발생하지 않는지 확인해야 한다. 이는 선택적 매개변수 전압 강하 △U 를 특징으로 한다. 6.5.7 SPD 의 특성변화와 관련된 정보 표준 시험에서 정의 된 것보다 높은 스트레스에 이르면 일부 SPD 의 상태가 중간 상태로 진입한다. 이러한 경우, Up, In, /c 등과 같은 특성 중 일부는 설계된 값에서 변화하게 된다. 특히, 이것은 SPD 에 능동 병렬 부품이 있으면서, 이 가운데 어느 하나가 서지에 의해 차단될 경우에 발생한다. 이때에 사 32 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
6cb61c13-e4d3-4aa4-b4ed-2540f652f851 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 용자는 이러한 특성 변화를 인식하지 못한다. 이러한 모든 중간 상태는 발생 시 이를 명확하게 알려 주는 표시가 없는 한 SPD 설계 단계에서 방지해야 한다. 7 저압 전력 시스템에서의 SPD 적용 7.1 일반사항 SPD 의 필요성을 정의 하기 위해 위험 분석을 수행하는 경우(4 절 참조), 그리고 시스템에서 발생할 수 있는 스트레스가 알려진 경우(5 절에서 식별됨), 장비를 보호하기 위한 SPD 의 특성(6 절에 나열됨)은 그림 7 에 나와 있는 절차를 사용하여 규정할 수 있다. 배전 시스템의 SPD 는 7.1 에 나열된 원칙과 7.2 에 설명된 절차에 따라 선택된 특성을 사용하여 선정 해도 된다. SPD 선택 ![image](/image/placeholder) 1, II, III 등급 시험된 SPD 는 인입구에서 사용해 도 되며 II 및 III 등급 시험된 SPD 는 기기와 가 까운 위치에서 사용해도 된다. 낙뢰의 영향과 스위칭 과전압으로부터 보호하 기 위해, II 등급 시험된 SPD 를 사용하여야 한 다. 구조물에 LPS 장착 시, I 등급 시험된 SPD 를 사용하여야 한다. 구조물에 LPS 가 장착되지 않았을 시, 그리고 마지막 극과 설비 인입구 사이의 가공 선로에 대한 직격뢰 발생을 고려해야 하는 경우, 전기 7.2 시험 등급 선택 설비의 인입구 또는 가까운 위치에 있는 I 등급 시험된 SPD 를 선정해도 된다. 7.3 필요한 보호 모드 결정 7.4 추가 보호 필요 SPD 는 가능한 한 인입구에 가깝게 설치되어야 진동 현상 하며, 필요한 경우 보호 대상 기기 근처에 설치되 설치 시 유도된 전압 어야 한다. SPD 의 연결 리드 길이 전압 보호 레벨의 영향 이러한 모든 SPD 는 조정 작업하는 것이 좋다 낙뢰 보호 구역(LPZ) 개념 참조). SPD 는 일반적으로 보호 거리가 제한 (7.5.7 되어 있으므로 진동을 고려할 필요가 있다. 일반적으로 설치 시 유도되는 전압은 무시할 수 있다(7.4.3 참조). SPD 를 위한 연결 도체는 가능한 짧아야 한다. LPZ(낙뢰 보호 구역) 개념을 사용하 는 경우, SPD 는 구역 경계에 설치되어야 한다. 그림 7 - SPD 적용 흐름도 33 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
4bc5925e-3704-4641-9fc3-cb312e8ff1df | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 SPD 의 적용 예는 부속서 G 에 나타낸다. SPD 의 실제 설치 예는 부속서 L 에 나타낸다. 7.2 시험 등급에 따른 SPD 위치 고려 인입 지점에서는 유입되는 스트레스에 따라 I 등급 또는 II 등급으로 시험된 SPD 를 위험 분석 결과 에 따라 사용해도 된다(4 절 참조). SPD 를 설치 인입구에 최대한 가깝게 설치하면 하부 설치 장치(예를 들면 미터기, 단자, 보호 장치, 스위치 등)를 통해 흐르는 서지 전류가 감소한다. 서지에 관련된 전기 적 스트레스를 고려하는 것은 올바른 SPD 를 선정하는 데 있어 핵심 요소다. 설비 내에서 발생하는 스위칭 과전압 또는 전화선, 인터넷 연결 또는 다른 구조물에 공급하는 다른 운전에서의 과전압과 같은 다른 유입 서비스의 과전압인 경우 SPD 는 그러한 위협 원천에 가능한 한 가깝게 위치하는 것 이 좋다. LPS 가 있는 경우 IEC 62305 시리즈 표준에서 추가 정보를 찾을 수 있다. II 등급과 III 등급 시 험된 SPD 는 보호 대상 기기에 가까운 위치에도 적합하다. 7.3 SPD 보호 가능 모드와 설치 보호 대상 기기가 충분한 내전압 성능이 있거나 주 배전반에 인접한 곳에 있는 경우, 하나의 SPD 로 충분하며, 인입구에 최대한 가깝게 설치되어야 한다. SPD 는 이러한 위치에서 충분한 서지 내력을 가 져야 한다. 그림 L.1 ~ 그림 L.5 는 다양한 형태의 시스템에서 전력 인입구에 설치된 대표적인 SPD 의 연결을 나타낸다. 그림 L.5 는 TN C-S 시스템의 특수한 경우를 제시한다. 설비 인입구 또는 근처에 있는 SPD 는 적어도 다음과 같은 지점 사이에 연결되어야 한다. a) 설비 인입구 또는 가까운 곳에 중성 도체와 PE 사이가 직결된 경우 또는 각 선도체와 주 접지 단 자나 주 보호 도체 사이에 중성 도체가 없는 경우 어느 쪽이든 경로가 더 짧은 경우, 또는 비고 1 IT 시스템에서 중성선을 PE 에 연결하는 임피던스는 연결로 간주하지 않는다. b) 설비 인입구 또는 근처에 있는 중성 도체와 PE 사이가 직결되지 않은 경우 각 선도체와 주 접지 단자 또는 주 보호 도체 사이, 그리고 중성 도체와 주 접지 단자 또는 보호 도체 사이 어느 쪽이든 경로가 더 짧은 경우 - 연결 유형 1 (CT 1), 그림 8 참조 또는 각 선도체와 중성 도체 사이, 그리고 중성 도체와 주 접지 단자 또는 보호 도체 사이 어느 쪽이든 경로가 더 짧은 경우 - 연결 유형 2 (CT2), 그림 9 참조 비고 2 선도체가 접지된 경우, 이 항을 적용하기 위해 중성 도체와 동등한 것으로 간주한다. 34 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
70c3140a-878b-437d-a70e-8af1d53837dd | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 Chart Type: line PE SPD MET item_01 2 2 1 식별부호 MET: 주 등전위 단자 비고 (1) 및/또는 (2) 서지보호장치의 접지 연결은 최단 경로인 것이 좋다. 국가 규정에 따라 1, 2 또 는 둘 다를 의무적으로 사용해도 된다. 그림 8 - 연결 유형의 예 1 (CT1) Chart Type: line L L2 L3 N PE item_01 1 2 3 1 2 식별부호 MET: 주 등전위 단자 비고 (1) 및/또는 (2) 서지보호장치의 접지 연결은 최단 경로인 것이 좋다. 국가 규정에 따라 1, 2 또 는 둘 다를 의무적으로 사용해도 된다. 그림 9 - 연결 유형의 예 2 (CT2) 표 3 은 다양한 LV 시스템에 필요한 보호 모드를 나타낸다. 비고 3 동일한 도체에 둘 이상의 SPD 가 연결되는 경우 이들 사이의 조정 작업이 필요하다(7.5.7 참 조). 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 35 | {}
15e0ec56-c75a-4cf5-bd20-4ed5dc4cf21c | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 비고 4 보호 모드의 수는 보호 대상인 기기의 형태(예를 들면 기기가 접지에 연결되어 있지 않으면 선- 또는 중성선-접지 보호 모드는 설치하지 않아도 된다), 보호 모드별 기기의 내력, 전기 시 스템 구조 및 접지와 인입되는 서지의 특성 등에 의해 좌우된다, 예를 들면 상/중성선과 PE 도체 사이 또는 상/중성선 사이의 보호가 일반적으로 적용되며, 상과 상 간의 보호는 일반적 으로 사용되지 않는다. 비고 5 전기 계량기 이전에 설치되는 SPD 는 전지 공급자와 협의 해야 한다. 표 3 - 다양한 LV 시스템의 보호 가능 모드 ¦ SPD 설치 위치 ¦ SPD 설치 위치의 시스템 구성 ¦ SPD 설치 위치의 시스템 구성 ¦ SPD 설치 위치의 시스템 구성 ¦ SPD 설치 위치의 시스템 구성 ¦ SPD 설치 위치의 시스템 구성 ¦ SPD 설치 위치의 시스템 구성 ¦ SPD 설치 위치의 시스템 구성 ¦ SPD 설치 위치의 시스템 구성 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ SPD 설치 위치 ¦ TT ¦ TT ¦ TN-C ¦ TN-S ¦ TN-S ¦ 배전된 중성선을 가지는 IT ¦ 배전된 중성선을 가지는 IT ¦ 배전된 중성선이 없는 IT ¦ ¦ ¦ 에 따른 설치 ¦ 에 따른 설치 ¦ ¦ 에 따른 설치 ¦ 에 따른 설치 ¦ 에 따른 설치 ¦ 에 따른 설치 ¦ ¦ ¦ CT 1 C ¦ CT2 ¦ CT 1 ¦ CT2 ¦ CT 1 ¦ CT2 ¦ ¦ ¦ ¦ ¦ 각 선도체와 중성 도체 ¦ + ¦ · ¦ NA ¦ + ¦ · ¦ + ¦ · ¦ NA ¦ ¦ 각 선도체와 PE 도체 ¦ · ¦ NA ¦ NA ¦ · ¦ NA ¦ · ¦ NA ¦ · ¦ ¦ 중성 도체와 PE 도체 ¦ · ¦ · b,d ¦ NA ¦ · a ¦ · a,b ¦ · ¦ · b ¦ NA ¦ ¦ 각 선도체와 PEN 도체 ¦ NA ¦ NA ¦ · ¦ NA ¦ NA ¦ NA ¦ NA ¦ NA ¦ ¦ 선도체 ¦ + ¦ + ¦ + ¦ + ¦ + ¦ + ¦ + ¦ + ¦ ¦ · 필수 NA : 해당 없음 + : 추가적으로 요구되는 SPD 외에 선택사항 CT: 연결 형태 ¦ · 필수 NA : 해당 없음 + : 추가적으로 요구되는 SPD 외에 선택사항 CT: 연결 형태 ¦ · 필수 NA : 해당 없음 + : 추가적으로 요구되는 SPD 외에 선택사항 CT: 연결 형태 ¦ · 필수 NA : 해당 없음 + : 추가적으로 요구되는 SPD 외에 선택사항 CT: 연결 형태 ¦ · 필수 NA : 해당 없음 + : 추가적으로 요구되는 SPD 외에 선택사항 CT: 연결 형태 ¦ · 필수 NA : 해당 없음 + : 추가적으로 요구되는 SPD 외에 선택사항 CT: 연결 형태 ¦ · 필수 NA : 해당 없음 + : 추가적으로 요구되는 SPD 외에 선택사항 CT: 연결 형태 ¦ · 필수 NA : 해당 없음 + : 추가적으로 요구되는 SPD 외에 선택사항 CT: 연결 형태 ¦ · 필수 NA : 해당 없음 + : 추가적으로 요구되는 SPD 외에 선택사항 CT: 연결 형태 ¦ ¦ a TN-S 또는 TN-C-S 시스템에서는 PE 에서 N 까지의 분리 지점과 설치된 SPD 의 위치 사이의 거 리가 0.5m 이하이거나 분리 지점과 SPD 가 동일한 배전반에 위치하는 경우 중성선과 PE 사이 의 SPD 를 생략해도 된다. b CT2 를 사용할 때 기기의 내전압 Uw 을 직렬 연결된(L-N 및 N-PE) 두 SPD 의 결과 로 얻은 보호 레벨과 비교하는 것이 좋다. 이는 단순히 두 SPD 의 Up 를 추가하는 것과 는 다른 결과 를 제공할 수도 있다. C RCD 의 하부만 해당된다. d 주 RCD 상부에서 사용하려면 SPD 가 TOV 를 견뎌야 한다(6.5.1.2 참조). ¦ a TN-S 또는 TN-C-S 시스템에서는 PE 에서 N 까지의 분리 지점과 설치된 SPD 의 위치 사이의 거 리가 0.5m 이하이거나 분리 지점과 SPD 가 동일한 배전반에 위치하는 경우 중성선과 PE 사이 의 SPD 를 생략해도 된다. b CT2 를 사용할 때 기기의 내전압 Uw 을 직렬 연결된(L-N 및 N-PE) 두 SPD 의 결과 로 얻은 보호 레벨과 비교하는 것이 좋다. 이는 단순히 두 SPD 의 Up 를 추가하는 것과 는 다른 결과 를 제공할 수도 있다. C RCD 의 하부만 해당된다. d 주 RCD 상부에서 사용하려면 SPD 가 TOV 를 견뎌야 한다(6.5.1.2 참조). ¦ a TN-S 또는 TN-C-S 시스템에서는 PE 에서 N 까지의 분리 지점과 설치된 SPD 의 위치 사이의 거 리가 0.5m 이하이거나 분리 지점과 SPD 가 동일한 배전반에 위치하는 경우 중성선과 PE 사이 의 SPD 를 생략해도 된다. b CT2 를 사용할 때 기기의 내전압 Uw 을 직렬 연결된(L-N 및 N-PE) 두 SPD 의 결과 로 얻은 보호 레벨과 비교하는 것이 좋다. 이는 단순히 두 SPD 의 Up 를 추가하는 것과 는 다른 결과 를 제공할 수도 있다. C RCD 의 하부만 해당된다. d 주 RCD 상부에서 사용하려면 SPD 가 TOV 를 견뎌야 한다(6.5.1.2 참조). ¦ a TN-S 또는 TN-C-S 시스템에서는 PE 에서 N 까지의 분리 지점과 설치된 SPD 의 위치 사이의 거 리가 0.5m 이하이거나 분리 지점과 SPD 가 동일한 배전반에 위치하는 경우 중성선과 PE 사이 의 SPD 를 생략해도 된다. b CT2 를 사용할 때 기기의 내전압 Uw 을 직렬 연결된(L-N 및 N-PE) 두 SPD 의 결과 로 얻은 보호 레벨과 비교하는 것이 좋다. 이는 단순히 두 SPD 의 Up 를 추가하는 것과 는 다른 결과 를 제공할 수도 있다. C RCD 의 하부만 해당된다. d 주 RCD 상부에서 사용하려면 SPD 가 TOV 를 견뎌야 한다(6.5.1.2 참조). ¦ a TN-S 또는 TN-C-S 시스템에서는 PE 에서 N 까지의 분리 지점과 설치된 SPD 의 위치 사이의 거 리가 0.5m 이하이거나 분리 지점과 SPD 가 동일한 배전반에 위치하는 경우 중성선과 PE 사이 의 SPD 를 생략해도 된다. b CT2 를 사용할 때 기기의 내전압 Uw 을 직렬 연결된(L-N 및 N-PE) 두 SPD 의 결과 로 얻은 보호 레벨과 비교하는 것이 좋다. 이는 단순히 두 SPD 의 Up 를 추가하는 것과 는 다른 결과 를 제공할 수도 있다. C RCD 의 하부만 해당된다. d 주 RCD 상부에서 사용하려면 SPD 가 TOV 를 견뎌야 한다(6.5.1.2 참조). ¦ a TN-S 또는 TN-C-S 시스템에서는 PE 에서 N 까지의 분리 지점과 설치된 SPD 의 위치 사이의 거 리가 0.5m 이하이거나 분리 지점과 SPD 가 동일한 배전반에 위치하는 경우 중성선과 PE 사이 의 SPD 를 생략해도 된다. b CT2 를 사용할 때 기기의 내전압 Uw 을 직렬 연결된(L-N 및 N-PE) 두 SPD 의 결과 로 얻은 보호 레벨과 비교하는 것이 좋다. 이는 단순히 두 SPD 의 Up 를 추가하는 것과 는 다른 결과 를 제공할 수도 있다. C RCD 의 하부만 해당된다. d 주 RCD 상부에서 사용하려면 SPD 가 TOV 를 견뎌야 한다(6.5.1.2 참조). ¦ a TN-S 또는 TN-C-S 시스템에서는 PE 에서 N 까지의 분리 지점과 설치된 SPD 의 위치 사이의 거 리가 0.5m 이하이거나 분리 지점과 SPD 가 동일한 배전반에 위치하는 경우 중성선과 PE 사이 의 SPD 를 생략해도 된다. b CT2 를 사용할 때 기기의 내전압 Uw 을 직렬 연결된(L-N 및 N-PE) 두 SPD 의 결과 로 얻은 보호 레벨과 비교하는 것이 좋다. 이는 단순히 두 SPD 의 Up 를 추가하는 것과 는 다른 결과 를 제공할 수도 있다. C RCD 의 하부만 해당된다. d 주 RCD 상부에서 사용하려면 SPD 가 TOV 를 견뎌야 한다(6.5.1.2 참조). ¦ a TN-S 또는 TN-C-S 시스템에서는 PE 에서 N 까지의 분리 지점과 설치된 SPD 의 위치 사이의 거 리가 0.5m 이하이거나 분리 지점과 SPD 가 동일한 배전반에 위치하는 경우 중성선과 PE 사이 의 SPD 를 생략해도 된다. b CT2 를 사용할 때 기기의 내전압 Uw 을 직렬 연결된(L-N 및 N-PE) 두 SPD 의 결과 로 얻은 보호 레벨과 비교하는 것이 좋다. 이는 단순히 두 SPD 의 Up 를 추가하는 것과 는 다른 결과 를 제공할 수도 있다. C RCD 의 하부만 해당된다. d 주 RCD 상부에서 사용하려면 SPD 가 TOV 를 견뎌야 한다(6.5.1.2 참조). ¦ a TN-S 또는 TN-C-S 시스템에서는 PE 에서 N 까지의 분리 지점과 설치된 SPD 의 위치 사이의 거 리가 0.5m 이하이거나 분리 지점과 SPD 가 동일한 배전반에 위치하는 경우 중성선과 PE 사이 의 SPD 를 생략해도 된다. b CT2 를 사용할 때 기기의 내전압 Uw 을 직렬 연결된(L-N 및 N-PE) 두 SPD 의 결과 로 얻은 보호 레벨과 비교하는 것이 좋다. 이는 단순히 두 SPD 의 Up 를 추가하는 것과 는 다른 결과 를 제공할 수도 있다. C RCD 의 하부만 해당된다. d 주 RCD 상부에서 사용하려면 SPD 가 TOV 를 견뎌야 한다(6.5.1.2 참조). ¦ 상세한 사항은 부속서 J 를 참조한다. 7.4 추가 보호의 필요성 7.4.1 일반사항 SPD 가 필요한 경우 첫 번째 SPD 를 설비 인입구 가까이에 설치하여야 한다. 이 SPD 의 목적은 설비 외부에서 발생하는 서지의 영향을 완화하는 것이다. 일부 조건에서는 예를 들어 구조물의 인입구에 서 스트레스가 낮거나 기기의 서지 내력 및/또는 SPD 의 Up 이 낮으면 하나의 SPD 로도 충분하다. 예를 들어 다음과 같은 경우, 배전반 또는 장비(예를 들면 콘센트)에 대한 추가적인 보호가 필요할 수도 있다. 36 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
1b0266d1-d2a9-4e68-8bf2-2f1578f55cce | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 · SPD 와 보호 대상 기기 간의 거리가 너무 길다. · 뇌방전에 의해 구조물 내부에 자계가 생성된다. · 인입구에 설치된 SPD 의 리드 길이가 너무 길어 해당 위치에 제공되는 보호 효과 가 감소했다. · 민감한 기기(전자 기기, 컴퓨터)가 있다. SPD 의 Up 보다 낮은 서지 내력 다음과 같은 다른 원인으로 발생하는 위협에 대해 일시적인 과전압 보호를 제공하기 위해 추가 SPD 가 필요할 수도 있다. · 설비 내에 위치한 기기에서 발생하는 스위칭 과전압 · 전화선, 인터넷 연결과 같은 다른 수신 서비스의 과전압 · 2 차 건물, 외부 설비/조명, 외부 센서에 전원을 공급하는 전력선 등 다른 구조물에 전력을 공급하 는 다른 서비스의 과전압 PV 설치가 있는 경우 추가 보호가 필요할 수도 있다. 이 경우 IEC 61643-32 가 더 많은 정보를 제공 한다. 7.4.2 보호 거리에서의 진동 현상 영향 비고 일부 국가에서는 보호 거리를 분리 거리라고도 부른다. 특정 장비를 보호하기 위해 SPD 를 사용하는 경우 SPD 는 보호 대상 기기에 최대한 가깝게 설치해야 한다. SPD 와 보호 대상 기기와 의 거리가 너무 멀리 떨어져 있는 경우 진동은 기기 단자에서 Up 보다 최대 2 배까지, 어떤 경우에는 이 수준을 훨씬 웃도는 전압을 유도하게 된다. 이는 SPD 가 설치되어 있다고 해도(그림 J.8 ~ 그림 J.10 참조) 보호 대상 기기의 고장 원인이 된다. 허용 거리(보호 거리라 고 함)는 SPD 형태, 시스템 형태, 인입 서지의 급준도(du/df)와 파형, 연결된 부하 등에 따라 달라진 다. 특히, 전압의 증배는 기기가 고임피던스에 해당하거나 커패시터 역할을 하고 있거나, 기기가 내 부적으로 차단된 경우 발생 가능하다. 그림 J.10 은 이 같은 조건하에서 발생하는 전압의 증배에 대한 현상을 예시로 설명하고 있다. 일반적으로 10m 미만의 거리에서는 진동이 무시될 수 있다. 일부의 경우 기기에 내부 보호 부품(예 를 들면 배리스터)이 장착되어 있어서 먼 거리임에도 불구하고 진동을 상당 수준 감소시킨다. 이 마 지막 경우에는 SPD 와 기기 내부의 보호 부품 간의 협조 문제를 피하기 위해 특별한 주의 가 필요하 다(7.5.7 참조). 7.4.3 설치 시 유도 전압 특히 구조물에 LPS 가 있고 구조물이 차폐되지 않은 경우, SPD 와 보호 대상 기기 사이에 존재하는 회로 루프에서 뇌전류가 직접 유도하는 전압으로 인해 보호 거리가 더욱 줄어들 수도 있다. 이는 다음 조건에서는 무시할 수 있다. · 내부 케이블을 차폐하거나 금속 덕트 내부에 배선된다(보호 장치 또는 금속 덕트는 양쪽 끝에서 접지되어야 한다). · PE 도체는 동일한 상도체 케이블로 배선된다. LPS 가 설치된 경우 유도 루프의 길이는 10 m 로 제 한하는 것이 좋다. 37 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
4bc04b16-4d59-4e79-9ef1-8fcd1432f05a | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 · PE 도체는 상도체의 동일한 덕트에 배치되며, 유도 루프의 길이는 10 m 로 제한하고 손상 원인 S1 은 무시한다. · SPD 는 기기 인입구에 설치된다. 대부분의 경우 철근 콘크리트 구조물은 유도 전압을 고려하지 않을 만큼 충분히 감쇠시킨다. 유도 전압은 주로 루프의 크기에 기인하며 일반적인 기기에서는 활성 도체와 PE 가 벽 또는 파이프에서 함께 작동하므로 루프 표면은 무시해도 될 정도다. 무시할 수 없는 경우 SPD 보호 레벨을 선정할 때 유도 전압을 고려한다(KS C IEC 62305-4 참조). 상세한 사항은 부속서 J 를 참조한다. 7.4.4 연결 리드 길이 영향 최적의 과전압 보호를 위해서 SPD 의 연결 도체는 가능한 한 짧아야 한다. 길이가 긴 리드는 SPD 의 보호 기능을 감소시킨다. 따라서 효율적인 보호 기능을 적용하기 위해 보호 레벨이 낮은 SPD 를 선 정해야 한다. 기기로 전달되는 잔류 전압은 최악의 경우 연결 리드를 따라 SPD 의 잔류 전압과 유도 전압 강하의 합이 된다. 이 전압을 Up/f 라고 한다. 2 개의 전압은 같은 순간에 정확하게 피크에 도달하 지는 않지만, 일반적으로 실용적인 목적을 위해 단순히 합한다. 그림 10 은 임펄스 방전 전류가 발생 하는 동안 SPD 의 연결 지점 사이에서 측정된 전압의 연결 리드 인덕턴스 효과 에 대해 설명하고 있다. 전압 강하 △U 는 다음 식으로 추산할 수 있다. △U=0.1 X ISPD xAl(kV) 여기에서 ISPD : SPD(kA)를 통해 흐르는 전류 AI : 연결 리드의 길이(m)(일반적으로 ≤0.5 m) 구조물 근처에서 뇌방전에 의해 유도된 전류만 SPD 를 통해 흐를 경우 이 전압 강하는 무시할 수 있 다. 가능한 한, 그림 10(때로는 V 연결이라고도 함)에 나타낸 이 인덕턴스 영향을 상당히 감소시키는 방식 b)를 사용하면 좋다. 방식 b)를 사용할 수 없을 때는 연선을 사용하는 방식 c)가 사용될 수 있 다. 이는 일반적으로 동일한 리드 길이의 2 배만큼 감소시킨다. 가능한 한 방식 a)를 피해야 한다. SPD 의 연결 도체의 길이를 늘리면 과전압 보호 효과 가 감소하기 때문에, 방식 a)에서는 SPD 의 모 든 연결 도체가 가능한 한 짧을 때(가급적 전체 리드 길이로 0.5 m 를 초과 하지 않는다) 루프 없이 최 적으로 과전압을 보호한다. 0.5m 의 리드 길이는 내전압 Uw 의 20 % 여유를 따른다. 리드 길이가 0.5m 보다 크면 Up 대신 Up/f 를 사용하여야 하며, 그러면 20 % 여유가 더 이상 필요하지 않다. SPD 가 보호 대상 금속 캐비닛 내부에 밀폐되어 있을 때 리드 길이를 줄이는 좋은 방법은 SPD 를 짧 은 리드로 금속 캐비닛 프레임(플레이트)에 직접 연결하는 것이다. 이것은 금속 캐비닛이 IEC 60439 를 준수하는 경우에만 적용된다. 또한 SPD 접지 도체가 금속 캐비닛에 접합되는 연결 지점 역시 동 일한 크기의 도체를 가진 캐비닛/배전 시스템의 접지 모선에 접합하는 것을 권고한다(그러면 SPD 의 접지 단자에 연결된 2 개의 도체가 있다. 하나는 금속 프레임에 연결되고 다른 하나는 접지 모선에 연결된다. 마지막 하나는 SPD 가 손상된 경우 단락 전류가 안전하게 흐르도록 사용하는 반면 금속판 은 주로 서지의 고주파 부분을 전환하는 데 사용한다). 비고 도체를 가까이 배치하여 유입되는 전류 도체에 귀선 전류 경로를 자기적으로 결합하면 인덕턴 스가 감소한다(그림 10c 참조). 38 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
53a517b8-141f-4c1b-a319-7f086d0ec098 | KSCIEC61643-12_KR | KS CIEC 61643-12:2020 ![image](/image/placeholder) A U VAB L1 a SPD VSPD L2 Isurge B t A A B SPD b C B SPD 식별부호 a) ¦ L1, L2 리드 길이 21, 2 에 해당하는 인덕턴스 Isurge ¦ ¦ --- ¦ ¦ 서지 전류 대 시간 파형 VSPD 서지 지속 시간 동안의 SPD 단자 전압 VAB 전압 제한형 또는 전압 스위칭형 SPD 의 경우 서지 지속 시간 동안 A 지점과 B 지점 사이 의 전압 = Up/f = VSPD + △U. 조합형 SPD 에는 다른 공식을 적용해도 된다. 이 방식은 가능한 한 특히 L1 또는 L2 가 클 경우 사용하지 않는다. ¦ b) 이 방식을 사용할 것을 권고한다. c) 이 방식은 방식 b)가 적용 불가능한 경우 사용한다. 그림 10 - SPD 연결 리드 길이의 영향 총 배선 길이가 0.5 m 를 초과 하는 경우 다음 중 하나 이상을 선택하여야 한다. 낮은 전압 보호 레벨 Up(10kA(8/20)의 방전 전류를 전달하는 1m 길이의 직선 케이블에 약 1 000 V 의 전압 강하가 추가됨)인 SPD 를 선정한다. 보호 대상 기기의 정격 임펄스 전압까지 전압 보호 레벨을 조정하기 위해 두 번째 협조된 SPD 를 보호 대상 기기에 가깝게 설치한다. · 그림 11 에 설명된 설치 방식을 사용한다. · 금속 외함으로 만들어진 대형 배전반에 설치된 SPD 의 경우, SPD 를 금속 부품, 예를 들어 어셈블 리의 금속 외함(KS C IEC 60364-5-54 의 543.4.2 참조)을 통해 주 접지 단자 또는 보호 도체에 연결 해도 된다. PE 에 연결되고 KS CIEC 60364-5-54 에 따른 보호 도체 요구사항을 충족한다면. 금속 외 함에 SPD 를 연결할 지점은 그림 11 에 정의 된 중간 접지 단자이며, 이 경우 길이 4(주 접지 단자 에서 중간 접지 단자까지)는 전체 길이 산출에 고려되지 않아야 한다. 그림 11(b)를 참조한다. 39 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
68fff7fd-9bbe-49ae-a159-7d5cc7e61ccc | KSCIEC61643-12_KR | KS CIEC 61643-12:2020 ![image](/image/placeholder) OCPD E/I PE SPD 5 B 3 ●96 2 1 의 4 (a) 식별부호 ¦ 1 ¦ 주 접지 바 ¦ ¦ --- ¦ --- ¦ ¦ 2 ¦ 중간 접지 바 ¦ ¦ 3 ¦ SPD 접지 리드 ¦ ¦ 4 ¦ 중간 접지 바를 주 접지 바에 연결하기 위한 추가 도체 ¦ ¦ 5 ¦ 중간 접지 바에서 PE 를 분류하는 추가 도체 ¦ ![image](/image/placeholder) 금속 배전판 ○○○ ○○○ d1 る O D 오 오 d2 S P D 패널 접지 바 중간 패널 접지 바 d3 (1) (2) 주 보호 접지 도체 사용자 방향 주 접지 바 (b) 식별부호 D 분리기 (1) 권고되는 추가 등전위 도체 (2) 주 등전위 도체 비고 중간 패널 접지 바는 설계 또는 설치함으로써 제작한 커넥터와 함께 배전반의 금속 구조물에 연결된다. 그림 11 - 리드 길이가 50 cm 를 초과 하는 경우 중간 접지 바를 사용하여 가능한 설치 방법 상세한 사항은 부속서 J 를 참조한다. 40 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c5a1e7fa-54a7-46c3-8db3-210fd5c1e79e | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 7.4.5 전압 보호 레벨 영향 SPD 서지 보호 레벨을 선정하려면 시스템 안에서 보호받아야 할 가장 민감한 기기의 내전압 Uw (KS C IEC 60664-1 참조) 또는 지속적으로 작동하는 것이 중요한 기기의 임펄스 내력 수준을 고려해야 한다. 다음 예에서(그림 12 참조) 기기는 중요하지 않으며 Uw 만 고려된다. 이러한 기기에 가장 가까이 설치된 SPD 는 리드 길이가 50 cm 를 초과 하지 않을 때 이 기기의 내전압 Uw 보다 최소 20 % 낮은 전압 보호 레벨(Up2)로 선정해야 한다. 리드 길이가 50 cm 를 초과 하는 경우 Up2 대신 Up/f2 를 사용하는 것이 좋다. Uw 보다 낮은 Up/f2 를 사용하는 것이 좋다. 보호 대상 기기의 전 압은 그 기기의 형태와 선로 길이에 따라 k 가 1 과 2 사이인 Up 의 k 배와 같다. k 는 측정 또는 시뮬레 이션에서 얻을 수 있다. 잠재적으로 피해 위험이 있는 스위칭 서지는 건물 내부에서 발생될 수 있다(5.2.3 및 부속서 C 참조). 이 경우 SPD 가 추가로 필요하다. 2 개의 SPD 가 동일한 회로에서 사용될 때, 협조가 필요하다(7.5.7 참조). 유도 전압 Ui 가 무시해도 될 정도이면, 다음과 같은 경우 추가 SPD 가 필요하지 않아도 된다. · SPD 를 연결하는 리드 길이가 50 cm 를 초과 하지 않으며 SPD 와 기기 사이의 거리가 10 m 보다 크 고 Up 가 0.8 x Uw 보다 작다. · SPD 를 연결하는 리드 길이가 50 cm 를 초과 하지 않으며, SPD 와 기기 사이의 거리가 10 m 보다 크 고 2 x Up 가 0.8 x Uw 보다 낮게 유지된다. · SPD 를 연결하는 리드 길이가 50 cm 를 초과 하고, SPD 와 기기 사이의 거리가 10 m 보다 작으며 Up/f 가 Uw 보다 작다. · SPD 를 연결하는 리드 길이가 50 cm 를 초과 하고, SPD 와 기기 사이의 거리가 10 m 보다 크지만 2 x Up/f 가 Uw 보다 낮게 유지된다. 비고 1 IEC 61000-4-5 의 기기 내성은 KS C IEC 60664-1(Uw)에 정의 된 내전압과 다를 수 있다. 그 이 유는 IEC 61000-4-5 의 시험은 조합파 발생기를 사용하며, 특히 저 임피던스인 경우 서지 전 류의 일부가 기기로 유입될 수 있기 때문이다. 이 경우, 적절한 협조가 요구된다(7.5.7 참조). 내성과 절연 내력 비교에 대한 추가 정보는 부속서 K 에 나타낸다. KS C IEC 60664-1 에서 Uw 를 구하는방법을 설명했음에도 불구하고, 실제로 모든 형태의 기기에 대해 Uw 값을 얻는 것 은 어려울 수 있다는 점에 주목한다. 비고 2 미국에서는 전압 보호 레벨을 6 인치 리드 도체로 시험한다. 이것은 이 절에서 설명하는 50cm 규칙이 설비와 관련되었다면, 설비와 관련이 없다. 상세한 사항은 J.1.2 과 그림 J.9 를 참조한다. 41 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
0a827100-915f-4d78-98d0-d7b77860d8c4 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) s Eq SPD Up1 I Up2 IP No. 1 D I No.2 Uw I 식별부호 Up1 x k < 0.8 x Uw 인 경우, SPD 와 기기 사이의 루프에서 발생하는 전압이 높고 근처에서 낙뢰가 발생 하지 않는 한 (인입구에 설치된) SPD No.1 만 필요하다(예를 들면: 구조물에 있는 LPS 의 경우). Up1 x k> 0.8 x Uw 인 경우, SPD No.1 에 추가하여 SPD No.2 (Up2 < 0.8 Uw))를 설치하고 이에 맞춰 협조 하여야 한다. Eq 는 KS C IEC 60664-1 에 정의 된 바에 따라 내전압 Uw 인 보호 대상 기기다. k 는 가능한 진동을 감안한 계수(1 <k<2, 7.1.3 참조)다. 그림 12 - 연결된 리드의 길이가 50 cm 미만일 때 추가 SPD 의 필요성 예 7.4.6 뇌 보호 구역(LPZ) 개념 적합한 서지 보호를 설계하고 적용하기 위해 KS C IEC 62305-4 에 설명된 보호 구역의 계층 구성을 고려하면 유용할 수도 있다. 뇌 보호 구역(LPZ)은 적어도 전도성 서지를 줄이기 위한 구역 인입구의 SPD 와 구역 내부의 전자기 스트레스(구역 내부에 직접 유도된 서지)를 줄이기 위한 잠재적인 추가 차폐 조치로 정의 된다. 이러한 계획 개념은 전력 시스템의 스위칭과 직/간접 뇌격에 의해 생성된 유도 서지가 보호되지 않 은 환경에서 보호된 민감한 기기에 이르는 단계(단계 간의 거리는 7.5.3 에 명시된 내용에 의거한다) 별로 감소된다는 가정을 전제로 한다. 건물의 전력 시스템을 보호 구역으로 재분할하고 SPD 의 위치를 지정하는 예는 그림 J.11 에 나타 낸다. 구조물에 인입되는 전력 및 신호 네트워크는 서로 가까워야 하며, 공통 본딩 바에 함께 결합되어야 한다. 이는 특히 비차폐 자재(나무벽돌, 콘크리트 등)로 만들어진 구조물인 경우 더욱 중요한 사항이 다. 그 목적은 두 네트워크의 도체로 이루어진 루프에 과전압이 발생하지 않도록 하기 위함이다. 42 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
a19ca04d-b38a-4ddc-99d3-03d33e209da6 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 7.5 SPD 특성 선정 7.5.1 일반사항 SPD 는 그림 13 에 나타낸 것처럼 7.5.2 ~ 7.5.7 에 명시된 다음 6 단계 방식에 따라 선정된다. ![image](/image/placeholder) 7.5.2 SPD 의 Uc, UT, In, /imp, Imax, ISCCR, /fi, Uoc 선정 SPD 의 일시적 과전압(U+)은 네트워크의 일시적 과전압(UTOV(LV)) 보다 크거나 같다. 제조자의 선언 및 설비의 예상 단락에 따른 SPD 의 ISCCR 와 /fi 선정 7.5.3 보호 거리 SPD 의 위치 사용자/설계자가 수용 가능한가? 7.5.4 기대 수명 7.5.5 SPD 와 다른 장치 간의 상호 작용 SPD 와 과전류 보호 장치 정상 조건 간의 서지 조정 SPD 가 인명의 안전을 위협 SPD 의 과전류 보호 장치는 SPD 의 지정된 서지 정격에서 동작하지 하거나 다른 기기의 교란을 않도록 시험한다. 상부에 있는 다른 과전류 보호 장치는 SPD 서지 일으키지 않는다. 정격과 조정되지 않을 수도 있다. SPD 는 제조자가 지정한 외부 차단기(있는 경우)를 제외하고 RCD 또는 회로 차단기와 같은 다른 부품을 간섭하지 않아야 한다. 7.5.2.4 참조 7.5.6 전압 보호 레벨 Up 선택 다음 사항을 감안한다. 보호 대상 기기의 서지 내력 또는 내성 시스템의 공칭 전압 동일한 도체에서 2 개의 SPD 가 사용되는 경우 7.5.7 선정된 SPD 와 다른 SPD 간의 조정 그림 13 - SPD 선정을 위한 공정도 43 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
53bfceb8-ce2e-495f-829a-6687accd1977 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 7.5.2 SPD 의 Uc, UT, In, limp, Imax, ISCCR, Ifi, Uoc 선정 7.5.2.1 Uc SPD 의 최대 연속 사용 전압 SPD 의 Uc 값은 다음 기준을 충족하여야 한다. Uc 는 전력 시스템의 최대 연속 사용 전압 Ucs(= k x Uo)과 같거나 커야 한다(부속서 J 및 부속서 B 에 제시된 값을 참조). U。≥ Ucs 비고 Uc 는 IT 시스템을 외에도 첫 번째 고장 조건을 포함할 수 있을 만큼 충분히 높다(1.1 Uo x V3). 이것은 표 4 에 제시된 값들을 포함한다. 실제로, 이는 표 4 에 제시된 요구사항으로 이어진다(KS C IEC 60364-5-53 참조). 표 4 - 다양한 전력 시스템에 대한 SPD 의 최소 권고 Uc ¦ SPD 연결 위치 (해당하는 경우) ¦ 배전 네트워크의 시스템 구성 ¦ 배전 네트워크의 시스템 구성 ¦ 배전 네트워크의 시스템 구성 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ SPD 연결 위치 (해당하는 경우) ¦ TN 시스템 ¦ TT 시스템 ¦ IT 시스템 ¦ ¦ 선도체와 중성 도체 사이 ¦ 1.1 U/V3 또는 (0.64 x U) ¦ 1.1 U/V3 또는 (0.64 x U) ¦ 1.1 U/V3 또는 (0.64 x U) ¦ ¦ 선도체와 PE 도체 사이 ¦ 1. 1 U/V3 또는 (0.64 x U) ¦ 1.1 U/V3 또는 (0.64 x U) ¦ 1.1 U ¦ ¦ 선도체와 PEN 도체 사이 ¦ 1.1 U/V3 또는 (0.64 x U) ¦ 없음 ¦ 없음 ¦ ¦ 중성 도체와 PE 도체 사이 ¦ 1.1 U/V3 a ¦ 1.1 U/V3a ¦ 1.1 U/V3 또는 (0.64 x U) ¦ ¦ 선도체 사이 ¦ 1.1 U ¦ 1.1 U ¦ 1.1 U ¦ ¦ 비고 1 해당 없음 비고 2 U 는 저압 시스템의 선 대 선 전압이다. ¦ 비고 1 해당 없음 비고 2 U 는 저압 시스템의 선 대 선 전압이다. ¦ 비고 1 해당 없음 비고 2 U 는 저압 시스템의 선 대 선 전압이다. ¦ 비고 1 해당 없음 비고 2 U 는 저압 시스템의 선 대 선 전압이다. ¦ ¦ a 이러한 값은 최악의 고장 조건과 관련이 있으므로 10 %의 공차는 고려되지 않는다. ¦ a 이러한 값은 최악의 고장 조건과 관련이 있으므로 10 %의 공차는 고려되지 않는다. ¦ a 이러한 값은 최악의 고장 조건과 관련이 있으므로 10 %의 공차는 고려되지 않는다. ¦ a 이러한 값은 최악의 고장 조건과 관련이 있으므로 10 %의 공차는 고려되지 않는다. ¦ 7.5.2.2 UT SPD 의 일시적 과전압 정격 UT 의 값은 그림 14 에서와 같이 저압 시스템에서의 사고로 인하여 시스템에서 발생할 것으로 예상되 는 일시적 과전압(TOV)과 같거나 높아야 한다. UT≥ UTOV(LV) 비고 5 초를 초과 해서 지속되는 UTOV(LV)는 최대 연속 운전 전압(Uc)으로 간주된다. 예를 들면 IT 시스템 에서 상과 접지 간에 연결된 SPD 의 Uc 값은 상당히 오랜 시간(몇 시간) 동안 발생할 수 있는 접 지 고장으로 인해 최소한 상간 시스템 전압의 최댓값(1.1 Uo xV3)과 같은 값이 된다. 대표적인 TOV 시험 값은 부속서 E 에 나타낸다. TOV 의 진폭이 지나치게 높은 경우, 허용 서지 보호 기능이 가능한 SPD 를 찾기는 힘들다. 발생 확률 이 충분히 낮은 경우에 TOV 스트레스에 견딜 수 없는 SPD 를 사용할 수 있다. 이런 경우, 적당한 차 단 장치를 사용해야 한다. 44 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c5f544fa-76eb-4f94-93f2-b8df4a7b0fa7 | KSCIEC61643-12_KR | KS CIEC 61643-12:2020 Chart Type: line 1.1 x U0 + 1200 V U0 + 250 V <3 x 1.1 U0 1.45 x U0 item_01 50 20 15 10 식별부호 a LV 설비에서의 사고(단락)에 대한 TT, TN, IT 시스템의 상과 중성선 간의 UTOV(LV) 영역 b LV 설비에서의 사고(우발적 접지)에 대한 IT(TT) 시스템의 상과 접지 간의 UTOV(LV) 영역, 그리고 LV 설비에서의 사고(중성선 단선)에 대한 TT, TN 시스템의 상과 중성선 간의 UTOV(LV) 영역 C HV 시스템에서 고장이 발생한 경우, TT 와 IT 시스템의 상과 접지 간의 수용가에서의 UTOV(HV)의 최댓값 d 정의 되지 않은 영역 비고 1 3W + G(3 전선 + 접지), 단상, 120/240 V 시스템에서 사용되는 SPD 에 필요한 UTOV(LV) 및 4W + G(4 전선 + 접지), 3 상, 120/208 V, 277/480 V, 347/600 V 시스템에서 사용되는 SPD 에 필요 한 UTOV(LV)는 북미에서 사용되는 다른 값이다. SPD 의 UT 값 비고 2 그림에 나타난 바와 같이, 다음과 같은 특성의 SPD 선정이 가능하다. UT = U。≥ UTOV(LV) max 이것은 특히 IT 시스템인 경우에 해당된다. 그림 14 - UT 와 UTOV 원하는 보호 레벨을 가진 SPD 를 선정할 때 예상되는 TOV 의 요구 작동(내력 특성 또는 고장)을 고 려하여야 한다. 발생 확률이 충분히 낮은 경우에는 TOV 스트레스를 견딜 수 없지만 KS C IEC 61643-11 에 따라 허용 가능한 수준이면 SPD 를 원하는 보호 레벨에 도달하기 위해 사용할 수 있다. 수명 종료 동작을 허용하지 않는 경우, 허용 보호 레벨의 SPD 를 적용하기 전에 TOV 를 제한하기 위 해 추가 조치를 취해야 한다. 7.5.2.3 In, limp, Uoc 및 Imax In, /imp, Uoc, /max (선언된 경우)는 적합한 에너지 내력 선정을 위해 필요하다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 45 | {}
73e6e3ad-c0e0-4df4-8c83-f10d20950ad3 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 SPD 의 에너지 내력(시험 등급에 따라 /imp, In 또는 Uoc 를 선택) 선정은 서지의 발생 확률과 허용 고 장률을 비교하는 위험 분석(4 절 참조)에 기초하여야 한다. 둘 이상의 SPD 가 포함될 때에는 협조 분 석도 고려해야 한다. 비고 1 /imp 는 I 등급 시험과 연관되고 In 은 II 등급 시험과 연관되며 Uoc 는 III 등급 시험과 연관되고 Imax 는 선택적 8/20 전류 임펄스이다. 비고 2 필요한 경우, 6.5.2.2 및 6.5.2.3 의 우선 값보다 큰 것을 사용할 수 있다. 대기 중에서 발생한 서지에 대한 보호로 SPD 가 필요한 경우, 설비 인입구의 공칭 방전 전류 In 은 필 요한 보호 모드별로 5 kA 8/20 이상이어야 한다. 연결형 2(CT2, 그림 9 참조)에 따른 설비의 경우, 중성 도체와 PE 사이에 연결된 서지보호장치의 설 치 입구에서 공칭 방전 전류 In 은 3 상 시스템의 경우 20kA8/20, 단상 시스템의 경우 10kA 8/20 이상 이어야 한다. 비고 3 In 은 선언된 Itrans 가 동일한 연결 사례(예를 들면 상 또는 PE 에 대한 중성선)의 /n 보다 높은 경 우 단락 유형 SPD 에 대한 위의 값보다 낮을 수 있다(A.2.2.9 참조). 직격뢰가 발생할 가능성이 있는 LPS 가 있어서 SPD 가 필요한 경우, 뇌 임펄스 전류 /imp 를 평가하여 야 한다(부속서 I 참조). SPD 의 상부에 설치된 부품(퓨즈, 배선 단면 등)은 전체 시스템의 최대 서지 기능을 제한할 수 있으므로 SPD 에 대한 최대 스트레스를 고려해도 된다. 이러한 평가가 가능하지 않은 경우 /imp 값은 필요한 보호 모드별로 12.5 kA 이상이어야 한다. 연결 유형 2(CT2)에 따라 배선된 설비의 경우, 중성 도체와 PE 사이에 연결된 서지보호장치에 대한 뇌 임펄스 전류 limp 는 KS C IEC 62305-4 와 유사하게 산출되어야 한다. 전류 값을 설정할 수 없는 경 우, /imp 값은 3 상 시스템일 때 50kA, 단상 시스템일 때 25 kA 이상이어야 한다. 비고 4 상세한 사항은 KS C IEC 62305-1:2010, 부속서 E 에 나타낸다. 단일 SPD 를 대기 중에서 발생하는 서지로부터 보호하고 직격뢰의 영향으로부터 보호하기 위해 사용 하는 경우, In 와 /imp 의 정격은 위의 값과 일치해야 한다. 추가 SPD 에 대한 In 및 Imax (선언된 경우)의 선택은 7.5.2.4 에 설명된 협조 규칙에 기초한다. 비고 5 Imax 는 특별한 경우에만 사용되며, 일반적으로 In 은 II 등급 시험된 SPD 의 특성을 나타내기에 충분하다. /max 는 에너지 내력 및 결과 적으로 특정 위치에서의 기대 수명을 보여준다. 7.5.2.4 설치 지점에서 네트워크의 예상 단락 전류에 대한 SPD 의 협조 SPD 에는 RCD, 퓨즈 또는 분리기 등과 같은 다른 보호 장치에 간섭되지 않도록 필요한 차단 장치를 장착해도 된다. 지정된 관련(내부 또는 외부) 과전류 보호 장치와 함께 SPD 의 단락 전류 내력(SPD 고장의 경우)은 설치 지점에서 예상되는 최대 단락 전류 이상이어야 하며 SPD 제조자가 지정한 최대 과전류 보호 장치를 고려하여야 한다. IEC 60364 에 따라 SPD 보호에 사용하는 외부 분리기 또는 과전류 보호 장 치는 관련 IEC 표준(예를 들면 IEC 60898 시리즈, KS C IEC 60947-2 또는 IEC 60269 시리즈 또는 해 당하는 경우 현지 국가 표준)을 준수하여야 한다. 46 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
664d0adb-3456-41f0-a1cd-dbabf8396725 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 a) 정격 단락 전류 ISCCR SPD 는 정격 단락 전류(/SCCR)에 따라 선정 및 설치하여야 한다. ISCCR 값은 제품과 함께 시험한 정 격 값이며 해당 제품과 함께 제공된 제조자 설명서에 선언되어 있다. 제조자가 명시한 대로 SPD 의 분리기 및/또는 과전류 보호장치와 함께 SPD 의 정격 단락 전류 (/SCCR)는 설치 지점에서 네트워크의 예상 단락 전류 이상이어야 한다. SPD 는 SPD 와 함께 제공된 문서에서 제조자가 선언한 분리기와 함께 설치하여야 한다. 분리기는 SPD 제조자의 결정대로 SPD 에 결합되거나 별도의 장치(예를 들면 분리기 또는 퓨즈)이어도 된다. IT 시스템에서 중성선과 PE 사이에 연결된 SPD 의 정격 단락 전류(/SCCR)는 (KS C IEC 60364-4- 43:2008 의 431.2.2 에 따라) 상과 중성선 사이에 연결된 SPD 의 경우와 동일하여야 한다. b) 속류 차단 정격(ki) 제조자가 속류 차단 정격(lf)을 선언한 경우, 이는 설치 지점에서 예상되는 예상 단락 전류 이상이 어야 한다. TT 또는 TN 시스템에서 중성선 도체와 PE 사이에 연결된 SPD 의 경우 속류 차단 정 격은 100 A 이상이어야 한다. 드 시스템에서 중성선과 PE 사이에 연결된 SPD 의 경우 속류 차단 정격은 상과 중성선 사이에 연결된 SPD 의 경우와 동일하여야 한다. 비고 1 속류(KS C IEC 61643-11:2011, 3.1.12 참조)는 방전 전류 임펄스 후에 전력 시스템에 의해 공급되고 SPD 를 통해 흐르는 파고 전류다. 실제로 속류를 허용하는 장치는 전압 스위칭 장치(예를 들면 스파크 갭)이다. 비고 2 100 A 는 TT 또는 TN 시스템의 고장 조건에서 N 과 PE 사이에 흐를 것으로 예상되는 최대 전류다. 이 값은 KS C IEC 61643-11 에서 시험용으로 사용한 값이다. c) SPD 와 분리기의 협조(D) SPD 를 보호하기 위해 사용하는 분리기 및/또는 과전류 보호 장치의 위치는 설비 공급의 연속과 설비 내 유효 전압 보호 레벨에 영향을 미친다. SPD 와 분리기 및/또는 과전류 보호 장치의 두 가 지 배치를 사용해도 된다. 사례 1: 외부 분리기 D(또는 과전류 보호 장치 - OCPD)는 그림 15 와 같이 SPD 회로에 설치해도 된다. 이 경우 SPD 고장이 발생하면 분리기가 작동하여 SPD 를 보호하고 연속적으로 전원을 공급하지 만(비고 3 참조), 추가 과전압으로부터 설비를 보호하지 않는다. 이러한 배치에서 SPD 와 직렬로 연결된 분리기의 전압 강하로 인해 설비 내 유효 전압 보호 레벨(Up/f)이 증가한다. 따라서 Up/f 값 이 증가한다(Up 및 Up/f 에 대한 자세한 사항은 7.5.6 참조). 분리기가 독립형 장치로 SPD 외함 내 에 결합된 경우 유효 전압 보호 레벨(Up/f)은 변경되지 않은 상태로 유지된다. 비고 3 추가적으로 SPD 와 RCD 사이의 배선 구성도 공급의 연속에 영향을 줄 수 있다. 47 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
cee384b6-69d2-456d-b3b0-3df483822c58 | KSCIEC61643-12_KR | KS CIEC 61643-12:2020 ![image](/image/placeholder) D 설비 또는 기기 SPD 식별부호 ¦ D: ¦ SPD 와의 협조용으로 SPD 제조자가 선언한 외부 분리기(또는 과전류 보호 장치 - OCPD) ¦ ¦ --- ¦ --- ¦ ¦ ・・・・・・・・・ --------- ¦ SPD 및 분리기로 구성된 SPD 어셈블리 ¦ 그림 15 - 공급의 연속을 위한 SPD 및 외부 분리기 배치 사례 2: 분리기(또는 OCPD)는 그림 16 과 같이 주 회로와 직렬로 설치해도 된다. 이 경우 SPD 고장이 발 생하면 분리기가 걸려 SPD 가 보호되지만 공급의 연속성은 유지되지 않는다. 이러한 배치에서는, 설비 내의 유효 전압 보호 레벨(Up/f)이 증가하지 않는다. ![image](/image/placeholder) D 설비 또는 SPD 기기 식별부호 D: SPD 와의 협조용으로 SPD 제조자가 선언한 외부 분리기(또는 과전류 보호 장치 - OCPD) 비고 4 SPD 용 상부의 비-전용 분리기가 동작할 시, 정확한 동작 원인을 파악한다. SPD 가 고장 조 건에 도달하면 시스템에서 SPD 를 제거하여 시스템에 전원을 다시 공급하기 전에 교체한 다. 고장난 SPD 가 연결된 회로에 다시 전원을 공급하면 위험한 상황이 발생할 수 있다. 그림 16 - 보호의 연속성을 위한 SPD 및 외부 분리기 배치 연속적으로 운전해야 할 경우에는 이 장치를 사용하지 않는다. 그 이유는 SPD 의 고장 시, SPD 를 교체해야 공급이 복구되기 때문이다. 차단기가 전력선에 대한 과전류 보호를 위해 사용되는 경우 과전류 보호에 대한 KS C IEC 60364-4- 43 및 KS C IEC 60947-2, KS C IEC 60898-1 또는 IEC 60269 시리즈의 요구사항을 준수하여야 한다. 48 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
63c0e8f2-4f41-40c4-95c0-51997748bc4a | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 d) 단락 시 설비 과전류 보호 장치가 있는 SPD 분리기의 선택성 필요 시 설비의 과전류 보호 장치가 있는 SPD 분리기(D) 간의 선택성을 단락의 경우 주의 깊게 조사하여야 한다. 그림 17 과 같이, 단락 발생 시, 설치 지점의 단락 전류, OCPD 및 분리기 D 의 선택에 따라 공급의 연속이 확보된다. 공급 연속성을 위해 OCPD 는 분리기 D 가 결함을 처리할 때까지 트립되지 않도 록 선택하는 것이 좋다. 연속적으로 운전해야 할 경우, OCPD 제조자가 제공하는 선택성 표에 따 라 OCPD 및 분리기 D 를 선택하는 것이 좋다. ![image](/image/placeholder) OCPD D 설비 또는 기기 SPD 식별부호 D: SPD 와의 협조용으로 SPD 제조자가 선언한 외부 분리기(또는 과전류 보호 장치 - OCPD) OCPD: 전기 설비의 과전류 보호 장치 그림 17 - 단락 시 OCPD 와 분리기 사이의 선택성 e) 서지 발생 시 SPD 외부 분리기와 설비 과전류 보호 장치의 협조 필요한 경우 서지 발생 시 OCPD 와 분리기 사이의 협조를 고려하는 것이 좋다. 서지 발생 시 II 등 급 시험된 SPD 의 경우 분리기 D 가 최대 In 까지, I 등급 시험된 SPD 의 경우 /imp 까지 서지를 견딜 수 있도록 SPD 제품 표준(KS C IEC 61643-11)이 보장한다. 그러나 OCPD 는 이러한 서지에 견딜 수 있도록 선택하는 것이 좋다. 이 표준의 부속서 N 은 서지 발생 시 트립되지 않는 OCPD 를 결정 하기 위해 서지 내력 관련 OCPD 선택을 위한 정보를 제공한다. 비고 일부 국가에서는 시험 등급 n(n = 1, II 또는 III)에 따라 검사 받은 SPD 를 SPD 유형 n(각각 n= 1.2 또는 3)이라고 한다. 서지 발생 시, 통제되지 않는 상황을 피하기 위해서는 위의 단락에 따라 OCPD 를 올바르게 선택 해야 한다는 사실을 독자들은 주목한다. 적절한 추가 조치는 설비의 주 OCPD 상류에 SPD 를 설 치하는 것이다(현지 국가 설치 규칙 또는 기타 현지 규정에서 허용하는 경우). 이 경우 SPD 를 보 호하기 위해 분리기 D 가 필요하다. SPD 설치 지점까지 선 측 상부에 절연 수단이 없는 경우 차단 기 D 도 절연 기능을 갖거나(KS C IEC 60664-1 참조) 추가 상부 절연 스위칭 장치와 연결되어야 한다. 7.5.3 보호 거리 SPD 의 위치(인입구, 기기와 인접한 위치 등)를 결정하기 위해 보호 거리, 즉 SPD 가 충분한 보호 성 능을 발휘할 수 있는 SPD 와 보호 대상기기 간의 허용 거리를 알아야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 49 | {}
29210f5b-e374-4010-bcdb-63f2739b4032 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 이 거리는 SPD 의 특성(Up 등), 구조물 내부의 설치(리드 길이 등), 시스템 특성(도체의 형태 및 길이 등), 그리고 기기의 특성(내전압, 내성 등)에 따라 좌우된다. 상세한 사항은 관련된 현상이 설명되어 있는 7.3 및 7.4 를 참조한다. 비고 보호 구역의 기획자는 SPD 에서 보호 대상 기기까지의 보호 거리를 숙지해야 한다. 7.5.4 기대 수명 SPD 의 기대 수명은 주로 SPD 의 최대 방전 용량을 초과 하는 서지 발생 확률에 따라 좌우된다. 실제 로 SPD 는 실제 발생 빈도에 따라 더 오래 또는 더 짧게 지속될 수 있다. 예를 들어, 적합한 위험 분석에 의해 사전에 결정된 주어진 임펄스 전류 /imp 값을 가진 SPD 가 해당 하는 /imp 값을 초과 하는 예외적인 서지 전류에 노출되면 SPD 가 고장 날 가능성이 높다. 이러한 극단 적인 경우는 모든 기대 수명이 실제적인 수명을 결코 보장할 수 없는 통계적 값일 뿐임을 의미한다. 단지 기대(예상) 수명을 고려하는 것만 가능할 뿐이다. 예외적인 서지 전류가 발생하면 이 서지 전류 보다 낮은 /imp 정격을 가진 SPD 는 설치 후 몇 초 안에 파괴되어 버릴 수 있다. 이러한 경우 /imp 가 예외적인 서지 전류보다 10 배 낮든 2 배 낮든 상관없다. 그러나 특정 애플리케이션의 경우 SPD 내력 한계를 초과 하지 않는 한, 높은 /imp 가 지정된 SPD 의 기대 수명은 항상 낮은 /imp 를 갖는 유사한 SPD 의 수명보다 길다. 예상 서지 및 다른 SPD 와의 필요한 협조를 고려하고 고장 시 화재 또는 감전과 같은 위험을 유발하 지 않는 SPD 를 선택해야 한다. 전원 공급 중단 또는 방해를 방지하려면 SPD 와 모든 상부 백업 보호 간의 협조도 필요하다. 7.5.5 SPD 와 다른 장치 간의 상호 작용 7.5.5.1 일반사항 이 주제와 관련하여 상세한 사항은 IEC 60364 시리즈를 참조한다. 7.5.5.2 정상 조건 누설 전류(IPE)는 다른 기기(예를 들면 RCD)에 인명에 대한 위험(간접적 접촉 등)이나 교란을 발생시 키지 않아야 한다. 비고 1 누설 전류 IPE 는 RCD 의 경우 정격 누설 전류(< /An/3)의 1/3 미만이어야 한다. 다양한 SPD 와 다른 장치의 누적 효과 가 바람직하게 고려해야 할 사항이다. 비고 2 SPD 가 RCD, 퓨즈 또는 분리기의 부하 측에 위치하는 경우 서지로 인한 불필요한 트립, 오 동작 또는 손상으로부터 보호할 수 없다. 7.5.5.3 SPD 와 RCD, 퓨즈 또는 분리기 등과 같은 과전류 보호 장치와 의 서지 협조 네트워크에서 사용되는 과전류 보호 장치와 누설 전류 장치(RCDs)의 정의 된 내력은 자체적인 표준 (KS C IEC 61008-1 및 KS C IEC 61009-1)에 의거하는 S 타입 RCD 를 제외하고는 정의 되어 있지 않으 며, S 타임 RCD 는 트립되지 않고 3kA 8/20 을 견딜 수 있다. 50 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
203b9c8d-8f77-4d50-84f4-952edccad59e | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 SPD 와 과전류 보호 장치 또는 RCD 와의 협조 시, 과전류 보호 장치 또는 RCD 는 공칭 방전 전류 /n 및/또는 임펄스 전류 /imp 에서 동작하지 않는 것이 좋다. 그러나 일반적으로 In 및/또는 /imp 보다 높은 전류에서는 과전류 보호 장치가 동작하는 것이 받아들여 진다. 회로 분리기와 같이 리셋 가능한 과전류 보호 장치의 경우 서지에 의해 손상되지 않아야 한다. 이러한 경우, 과전류 보호 장치의 응답 시간으로 인해 과전류 보호 장치가 동작해도 전체 서지는 SPD 를 통해 흐르게 된다. 따라서 SPD 는 충분한 에너지 내력을 가져야 한다. 이러한 현상으로 인해 RCD 또는 과전류 보호 장치가 동작해도 전기 설비가 보호되어 있는 상태이므로 SPD 의 고장으로 간 주되지 않는다. 전원 공급 중단이 사용자에게 허용되지 않을 경우에는 특수한 구성 또는 과전류 보 호 장치가 사용된다. 비고 1 SPD 는 KS C IEC 61643-11 및 기타 표준에 따라 분리기로 시험된다. 그러나 SPD 의 상부에 있는 다른 과전류 보호 장치가 존재하기도 하여 이러한 분리기와 SPD 의 서지 정격을 협조하 는 것을 더 복잡하게 만들 수 있다(부속서 N 참조). 비고 2 LPS 또는 가공선 등과 같이 높은 전류가 노출되는 상황에서 과전류 보호 장치의 동작은 /n 및/또는 In 및/또는 /imp 가 설비에서 사용된 과전류 보호 장치의 실제 내력을 웃돌면 /imp 미만 에서도 과전류 보호 장치의 동작이 허용된다. 이 경우 SPD 의 공칭 방전 전류는 서지 용량만 을 근거로 하여 선정된 것이다. 비고 3 전압 스위칭형 SPD 의 스파크오버가 발생하면 전기 공급 품질이 나빠진다. 일반적으로 전압 스위칭형 SPD 가 자가 소화하지 않으면, 전력을 동반한 속류가 과전류 보호 장치 동작의 원 인이 된다. 이때 SPD 의 상부 측 과전류 보호 장치와 의 협조가 필요하다. 비고 4 간접 접촉에 대한 보호를 위해 KS C IEC 60364-5-53 이 적용된다. 7.5.6 전압 보호 레벨 선택 Up 선정 SPD 의 적합한 전압 보호 레벨값 선정 시 보호 대상 기기의 서지 내력(또는 중요 기기의 임펄 스 내성)과 시스템의 공칭 전압이 고려되어야 한다. 값이 낮을 수록 보호 성능은 더 우수하다. 이는 Uc 와 UT, SPD 의 성능 감소와 다른 SPD 와의 협조에 대한 사항으로 제한된다. 7.5.2 및 7.5.3 도 참조 한다. 전압 제한 SPD 에 대한 전압 보호 레벨은 I 등급 시험의 경우 정해진 값 /imp, II 등급 시험의 경우 In 과 관련된다. III 등급 시험에 대한 전압 보호 레벨 선택은 조합파 발생기 시험(Uoc)에 의해 선정된다. 전압 스위칭 SPD 또는 조합형 SPD 에 대한 전압 보호 레벨은 스파크오버 전압과 관련이 있다. 7.5.7 선정된 SPD 와 다른 SPD 간의 협조 7.5.7.1 일반사항 앞서 언급한 바와 같이, SPD 적용 시 일부 경우에는 보호 대상 기기에서의 전기 스트레스를 허용값 (낮은 전압 보호 레벨)으로 감소시키고 구조물 내부의 과도 전류를 감소시키기 위해 2 개(또는 그 이 상)의 SPD 를 사용할 수도 있다. 많은 SPD 를 협조할 때 두 가지 측면을 다루어야 한다(부속서 F 참조). 51 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
64344b70-61aa-4bfd-b158-09eeff6db271 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 에너지 협조: 과도한 에너지로 파괴되지 않도록 두 SPD 간의 에너지 내력에 따라 적합하게 스트 레스를 분담한다. 보호 레벨 협조: 하부 전압 제한형 SPD 의 전압 보호 레벨이 하부 전압 제한형 SPD 를 통해 더 낮은 전류가 흐르도록 함으로써 하부 SPD 의 잔류 전압을 Up 아래로 감소시킨다. 보기는 그림 18 에 나타낸다. ![image](/image/placeholder) d 1 2 O/c Eq SPD 1 SPD 2 Z 1 2 O/c Eq U14 U2 ▲ SPD 1 SPD 2 i1 12 식별부호 ¦ Eq ¦ 정상 동작 하에서의 보호 대상 기기 ¦ ¦ --- ¦ --- ¦ ¦ O/c ¦ 개방 회로(전원에서 차단된 기기) ¦ ¦ i ¦ 인입 서지 ¦ 그림 18 - 2 개의 SPD 를 사용한 대표적인 예 - 회로도 2 개의 SPD 간의 임피던스 Z(일반적으로 인덕턴스)는 물리적 하나(2 개의 SPD 간 에너지 공유를 쉽 게 하기 위해 선로에 삽입된 특정 부품) 또는 2 개의 SPD 간의 케이블 길이에 따른 인덕턴스를 의미 한다(일반적으로 1 �H/m). Z 가 물리적 임피던스를 나타내는 경우, 선로의 인덕턴스는 Z 와 비교해서 작으므로 무시된다. Z 는 위의 두 가지 경우, 모두 그림 18 의 회로도로 나타난다. 비고 1 그림 18 은 기기가 연결되지 않은 가장 심각한 경우를 나타낸다. 전류는 전혀 이 기기를 통해 흐르지 않게 되며 전체 스트레스는 2 개의 SPD 에 부담된다. 서지가 SPD 단자와 부하 간에 52 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
55c9a47c-982b-4f08-8011-780ba147ac71 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 발생되는 경우 추가사항을 감안해야 한다. 비고 2 이 예에서 연결 리드는 무시된다. 실제로 이들은 2 개의 SPD 간에 스트레스를 나누는 데 영 향을 주게 된다. 비고 3 진행 도체와 귀환 도체가 가깝게 결합되어 있으면 루프가 작으며, 특성 인덕턴스가 1 �H/m 미만이다. 그 후 인덕턴스가 0.5 �H/m 까지 작아질 수도 있다. 비고 4 1 �H/m 의 값은 이미 진행 도체와 귀환 도체의 인덕턴스와 결합되었다. 7.5.7.2 협조 문제 협조 문제는 다음 질문에 의해 일차적 접근으로 정리될 수 있다. 인입 서지 i 의 경우 이 전류 i 의 어 떤 부분이 SPD1(h)을 통해 흐르고 어떤 부분이 SPD2(i2)를 통해 흐르게 되는가? 혹은 2 개의 SPD 가 이러한 스트레스를 견딜 수 있는가? 2 개의 SPD 간의 거리가 서지의 지속 시간에 비해 짧으면 인덕턴스의 결과 는 무시될 수 있으며 SPD2 는 과스트레스를 받게 된다. 올바른 협조는 2 개의 SPD 간 임피던스를 고려하여 12 값을 허용 레벨까지 감소시키는 데 적합한 SPD 를 선정함으로써 얻을 수 있다. 이러한 과정은 또한 두 번째 SPD 의 잔류 전압을 원하는 값까지 끌어내려 감소시킨다. 이러한 협조는 SPD2 의 과도 설계와 i2 가 너무 높은 경우 건물에 문제를 발생시킬 수 있는 일부 EMC 동요를 방지하기 위해 필요하다. 그러나 전류 측면에서의 협조를 다루는 것만으로는 충분하지 않다. 에너지에 관한 협조 역시 논의 되 어야 할 필요가 있다. 2 개의 SPD 가 적절히 협조한다는 것을 확실히 하기 위해 에너지 기준으로 알려진 다음 요구사항을 충족시켜야 한다. 0 과 /n1 간의 모든 서지 전류 값에 대해 /imp1 및 /max1(선언된 경우)이 SPD2 를 통해 방산된 에너지의 일부분이 최대 에너지 내력(Emax2)보다 낮거나 같으면 에너지 협조가 이뤄진 것이다. SPD2 의 잔류 전압도 점검하여야 한다. 자세한 사항은 부속서 F 및 부속서 J 를 참조한다. 7.5.7.3 협조 절차 협조에 관한 연구는 복잡하다고 할 수 있다. 모든 SPD 가 동일한 제조자에 의해 제공되었다고 하면 선정된 SPD 간의 거리 또는 임피던스에 관련된 사항이나 적합한 협조 방식 등 모든 시방을 그 제조 자에게 문의 하면 문제는 간단하게 해결될 것이다. 그렇지 않은 경우 협조에 관한 연구를 수행해야 한다. 에너지 및 전압 보호 협조를 위해 3 가지 가능 성이 제시된다. · 부품의 허용 편차가 결과 에 중대한 영향을 끼치게 된다는 것을 숙지하고 0 에서 Emax1 에 해당하는 전류까지 긴 파형과 짧은 파형으로 서지 전류를 주입하여 시험한다(부속서 J 참조). 53 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
aa5e40c3-990e-4c71-b3a0-4ad5477eab04 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 · SPD 의 특성에 정확한 데이터가 필요하다는 것을 염두에 두고, 설치 시 실제 적용되는 방식의 특 성을 감안하여 시뮬레이션을 수행한다. · 2 개의 SPD 가 전압 제한형이면 U-I 곡선을 비교하여 분석 연구를 수행한다. 에너지 협조에만 관련된 경우, 통과 에너지(LTE: Let-Through Energy)라는 또 다른 방식을 사용하여 시험한다. 부속서 F 와 부속서 J 는 이러한 현상과 분석 연구, LTE 방식에 대해 자세한 정보를 제공하고 있다. 7.6 보조 장치의 특성 7.6.1 분리기 3 개의 기본 분리기 기능이 있다. · 열 보호 · 단락 보호 · 간접 접촉 보호 비고 또는 분리된 입출력 단자가 있는 2 포트 SPD 와 1 포트 SPD 는 과전류 보호라는 또 다른 기능이 필요한 경우가 있다. 이러한 기능은 단일 분리기로 수행되어야 하며 최대 3 개의 분리기까지 사용해야 할 수도 있다. 이러한 분리기는 SPD 자체의 내부에 장착되거나 SPD 와 결합하여 사용할 수 있다. 일부 분리기 기 능은 시스템의 백업 보호로 간주할 수 있어 SPD 에서 일정 거리에 떨어진 곳에 위치할 수 있다. 전용 분리기가 SPD 회로 내부에 있거나 전원과 직렬로 연결되는 것은 전원 공급의 연속성과 보호의 연속성을 비교한 것, 그리고 과전류 보호 장치 사이의 협조에 따른다(부속서 JJ.2 참조). 예를 들어 매우 높은 일시적 과전압의 경우에는 분리기의 다른 기능이 필요할 수도 있다. 열 분리기는 일반적으로 필요 시 SPD 에 포함된다. 과전류 차단기는 SPD 또는 SPD 의 상부에 포함된다. 과전류 차단기는 퓨즈나 회로 분리기 또는 이 애플리케이션 전용 장치일 수 있다. 때로는 RCBO(과전류 보호 기능이 있는 RCD, KS C IEC 61009-1 참조)일 수도 있다. 간접 접촉 분리기는 일반적으로 설치 시 제공된다(예를 들면 RCD 의 SPD 하부 설치 시). 설비가 충 분한 보호를 제공하지 않으면 SPD 제조자가 추가 조치를 제공하여야 한다. 7.6.2 서지 계수기 서지 계수기는 일반적으로 감지된 서지의 숫자에 관한 정보를 제공하고, 어떤 경우에는 진폭과 파형 등에 대한 정보를 제공한다. 서지 계수기는 해당 위치의 낙뢰 밀도를 결정하거나 교체 정책을 결정 하는 데 사용해도 된다. 일부 정교한 계수기는 발생 빈도, 날짜와 시각, 관련 에너지 등에 대한 통계 데이터를 제공한다. 서지 계수기는 KS C IEC 62561-6 을 준수하여야 한다. 54 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
58500468-e3fa-43fe-a661-082adeae5e17 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 SPD 어셈블리의 일부인 계수기는 일반적으로 감지된 과도 과전압 숫자에 관한 정보만 제공한다. 이 러한 경우 KS C IEC 62561-6 을 준수할 필요가 없다. 비고 사용자는 임계 레벨이 너무 낮을 경우, 계수기가 제공한 정보가 혼동을 일으킬 수 있다는 것을 알아야 한다. 7.6.3 상태 표시기 분리기가 제공된 경우(SPD 내장형 또는 외부형) 상태 표시기는 필수사항이다. 이 장치는 분리기와 연결되어 사용자에게 SPD 가 설계된 대로 동작하는가 또는 동작하지 않는가에 관한 정보를 제공한다. SPD 를 교체하도록 알려주는 데 이용될 수도 있다. 상태 표시기 중 일부는 현장에서, 일부는 원거리 에서 동작한다. 전기적, 시각적 또는 청각적 경보를 제공할 수도 있다. 상태 표시기의 중간 단계 또는 기타 유사한 기능이 예를 들어 고장이 발생하기 전에 예방 유지보수 를 위해 제공될 수도 있다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 55 | {}
8746a4f3-e1e3-49a3-a951-fd1da96a63fc | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 부속서 A (참고) SPD 를 선정하기 전에 필요한 기본적인 정보 및 시험 절차 A.1 SPD 를 선정하기 전에 필요한 기본적인 정보 A.1.1 시스템 자료 · Uo · 전력 시스템의 최대 전압 조정 · 주파수 · 일시적 과전압 UTOV · 보호 대상 기기의 정격 임펄스 전압 레벨(또는 주요 장비의 임펄스 내성) 비고 사용자는 절연 내력 강도가 전압의 상승률과 지속 시간에 따라 다양하게 나타날 수 있다는 사실을 인식해야 한다. 예를 들어 4 kV 1.2/50 의 내력을 갖는 장치가 파장이 긴 1 kV 밖에 못 견딜 수도 있다. · SPD 가 설치되는 곳의 시스템 단락 전류 · 배전 시스템의 형태(IT, TT, TN 등) A.1.2 SPD 적용 시 고려사항 a) 연결 상과 접지 중성선과 접지 상과 중성선 상과 상 b) 보호 대상 기기의 형태 변압기 전기 기계 전자 기기를 포함한 장치 기타 기기 케이블(종류와 길이) 등 c) SPD 와 보호 대상 기기 간의 도체 최대 길이(보호 거리) 비고 이 거리는 가능한 한 짧아야 한다. d) SPD 와 모든 도체(상, 중성선, 접지선) 간의 연결을 모두 고려한 SPD 단자에서부터의 도체 최대 56 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
2039828e-1447-45dc-81fc-e84d2aba4993 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 길이(리드 길이) A.1.3 SPD 특성 · 최대 연속 사용 전압 Uc (각 보호 모드 별로 하나의 값) · 공칭 AC 시스템 전압 및 SPD 가 설계된 최대 허용 전압 조절을 포함한 LV 시스템 형태(TN 시스 템, TT 시스템, IT 시스템) · 연결 대상(선과 중성선, 선과 접지, 중성선과 접지, 선과 선) · 시험 분류 및 방전 매개변수는 제조자가 선언한 각 보호 모드별로 나란히 인쇄되어야 한다. I 등급 시험의 경우: "I 등급 시험" 및 "/imp" 및 kA 값, 및/또는 "T1" (정사각형 안에 T1) 및 "/imp" 및 kA 값 II 등급 시험의 경우: "II 등급 시험" 및 "In" 및 kA 값, 및/또는 "T2"(정사각형 안에 T2) 및 "In" 및 kA 값 III 등급 시험의 경우: "III 등급 시험" 및 "Uoc" 및 kV 값, 및/또는 "T3" (정사각형 안에 T3) 및 "Uoc" 및 kV 값 · /max (선택사항) · 멀티모드형 SPD 에 대한 총 방전 전류 /Total (제조자가 선언한 경우) 및 해당 시험 등급 · 전압 보호 레벨 Up (각 보호 모드 별로 하나의 값) 비고 SPD 는 둘 이상의 시험 등급[예를 들면 I 등급 시험(T1) 및 II 등급 시험(T2)]에 따라 분류해도 된다. 이 경우 제조자는 하나의 보호 레벨만 선언하고 가장 높은 보호 레벨을 표기하여야 한다. · 2 포트 SPD 및 분리된 입출력 단자가 있는 1 포트 SPD 의 정격 부하 전류 儿 · 2 포트 SPD 의 부하 측 서지 내력(선택사항) · 포트 수 · 정격 단락 전류 ISCCR · 단락형 SPD/trans 의 단락 전환 서지 전류 정격 · 일시적 과전압 정격 UT 및/또는 SPD 를 사용하도록 설계된 전력 시스템 형태 · 2 포트 SPD 의 전압 강하 · 고장 모드(선언된 경우) · 누설 전류 /PE · 속류 차단 정격 또 (전압 제한형 SPD 의 경우 제외) A.1.4 추가 기기와 부속품 · 설치 지침 · 장착 방법 · SPD 설치 위치(실외, 실내 등) · 일반 설치 방향(중요한 경우) 57 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
3a41031a-7846-48c7-9c02-ce5df7976033 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 · SPD 가 설치될 수 있는 접지 전도성 표면과 의 최소 거리 · 외함에서 제공하는 보호 레벨(IP 코드) · 온도 및 습도 범위 · 외부 분리기의 정격 및 특성(필요한 경우) · 교체 가능한 부품에 대한 정보(해당되는 경우 표시기, 퓨즈 등) · 연결 리드 단면 A.2 KS C IEC 61643-11 에서 사용된 시험 절차 설명 A.2.1 일반 원칙 KS C IEC 61643-11 에 대한 적합성을 요구할 때 SPD 의 대표 시료는 모든 필수 시험 순서를 통과 해야 한다. 시험 순서는 3 개의 시료 집합이 통과 해야 하는 일련의 시험이다. SPD 분류에 따라 전체적인 형식 시험을 수행하기 위해 최대 8 개의 시험 순서가 필요할 수도 있다. 각 시험은 제품 표준 KS C IEC 61643-11 에 자세히 설명되어 있다. 다음의 항은 시험과 합격 기준을 요약하지만 KS C IEC 61643-11 을 대체하여 사용할 수는 없다. 의심스러운 경우 KS C IEC 61643-11 이 우선한다. A.2.2 시험 순서 및 시험 설명 A.2.2.1 일반사항 아래의 시험 순서 설명에서 수행되는 시험은 제품 표준과 동일한 방식으로 수행되며 아래 괄호 안의 항 번호는 KS C IEC 61643-11:2011 의 해당 항을 나타낸다. A.2.2.2 시험 순서 1 A.2.2.2.1 식별 및 마킹(7.1.1/7.1.2/8.2) SPD 는 요청된 특성 또는 정보와 함께 제공되는데 그 정보는 제품 자체 또는 설치 설명서에 있을 수 있다. 제품 본체에 정보가 있는 경우 표기의 내구성을 확인하기 위한 시험을 수행한다. A.2.2.2.2 설치(7.3.1) SPD 의 장착 방식과 불량 접속을 방지하는 SPD 부품의 기계적 코딩/접속을 육안 검사로 확인한다. A.2.2.2.3 나사, 전류통전부 및 접속부(7.3.2/7.3.3/8.4.2) 나사, 전류통전부 및 접속부의 신뢰성은 육안 검사와 일련의 시험을 통해 점검한다. 제시한 토크로 도체에 나사를 여러 번 조이고 풀어야 하며 나사 연결은 느슨하지 않아야 하며 제품 (외함, 커버 및 연결부 포함)이 손상되지 않아야 한다. 연결된 와이어에 당기는 힘을 가하는 인장 시험은 각 접속부에서 수행된다. 접속 특성(예를 들면 최 대 및 최소 허용 와이어 단면적)과 접속 유형(예를 들면 나사, 나사 없는, 절연 관통형, 평판 퀵 접속 또는 돼지꼬리 접속)에 따라 특정 설정(당기는 힘)이 필요하다. 이 시험이 끝나면 도체가 제품 안에 58 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
7ee2c0c9-0316-4304-b41a-40cadf08ad0d | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 서 움직이지 않아야 한다. A.2.2.2.4 직접 접촉에 대한 보호 시험(7.2.1/8.3.1) SPD 가 충전부에 접촉되지 않는지 확인한다. SPD 는 SPD 가 설치될 때 가능한 모든 위치에서 충전부 에 시험 핑거(KS C IEC 60529 에 따라)가 접촉할 수 없도록 설계되어야 한다. A.2.2.2.5 환경, IP 코드(7.4.1/8.5.1) 고체 물체 및 물의 침투로부터 보호하기 위한 SPD 의 외함은 KS C IEC 60529 에서 설명한 대로 선언 된 IP 코드에 따라 시험된다. A.2.2.2.6 누설 전류(7.2.2/8.3.2) SPD 가 허용 가능한 변화를 포함하는 공칭 전압으로 전원이 공급될 때 측정된 누설 전류를 선언된 누설 전류 IPE 와 비교한다. A.2.2.2.7 동작 책무 시험(7.2.4/8.3.4) 이 시험은 다음과 같은 두 부분으로 구성된다. "동작 책무 시험 1, II, ■등급(8.3.4.2/8.3.4.3/8.3.4.5)" 및 "추가 동작 책무 시험 I 등급(8.3.4.4)" 시험 설비 설치는 그림 A.1 에 나타낸다. ![image](/image/placeholder) 임펄스 UC Surge DUT (SPD) 식별부호 ¦ Uc ¦ KS C IEC 61643-11 에 따른 전원 ¦ ¦ --- ¦ --- ¦ ¦ D ¦ 제조자가 제시한 SPD 분리기 ¦ ¦ DUT ¦ 시료(SPD) ¦ ¦ 임펄스: ¦ I 등급 및 II 등급 동작 책무 시험의 8/20 서지 전류 추가 동작 책무 시험의 임펄스 방전 전류 /imp III 등급의 동작 책무 시험의 조합파 발생기 ¦ 그림 A.1 - 동작 책무 시험 설비 설치 운전 조건은 다음을 적용하여 시뮬레이션한다. I 등급(/imp), II 등급(In), III 등급(Uoc) 시험 SPD 에 대한 15 회의 임펄스, 그리고 I 등급 시험 SPD 에 대한 /imp 시간: 0.1, 0.25, 0.5, 0.75, 그리고 1 에서의 5 회의 추가 임펄스 I 등급 및 II 등급 시험 SPD 에 대한 15 회의 시험 임펄스는 /imp 의 선언 값 또는 In 의 선언 값에 해당하 59 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
ed65b09c-ef5e-42cf-83be-deb79b716520 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 는 파고 전류를 시험 표본에 전달할 수 있도록 설정된 8/20 파형 발생기에 의해 생성된다. III 등급 시 험 SPD 에 대한 15 회의 시험 임펄스는 선언된 Uoc 와 동일한 개방 회로 전압으로 설정된 조합파 서지 발생기(2 옴의 내부 임피던스)에 의해 생성된다. 15 회의 임펄스는 그룹 사이에 30 분 ~ 35 분 간격으로 50 초 ~ 60 초마다 5 회의 임펄스를 3 개 그룹으로 사용한다(그림 A.2 참조). I 등급 및 II 등급 시험의 15 회 임펄스에 대해 각 임펄스는 정극성이며 30°씩 증가하는 동기화 위상각 은 0°에서 시작하여 전원 주파수와 동기화한다. III 등급 시험의 15 회 임펄스에 대해 첫 번째 및 마지막 임펄스 그룹은 정극성이고 두 번째 그룹은 부 극성이다. 각 임펄스는 첫 번째 및 마지막 그룹은 정극성 파고값에서, 두 번째 그룹은 부극성 파고값 에서 전원 주파수와 동기화한다. ![image](/image/placeholder) 서지 임펄스 동작 책무 시험 전류 Uc 15 min 35 min 35 min 조합파 임펄스 I 등급 및 II 등급 시험 ![image](/image/placeholder) Uc 30 min 30 min III 등급 시험 그림 A.2 - 최초 15 회 임펄스에 대한 시험 시간 흐름도 I 등급 시험 SPD 에 적용할 추가 임펄스의 경우, 임펄스 전류 발생기는 SPD 에서 (맹점을 찾기 위해) 0.1 /imp, 0.25 /imp, 0.5 /imp, 0.75 /imp 및 /imp 의 전류를 생성하도록 설정되어 있다. 그림 A.3 을 참조한다. 임펄스는 정극성 피크값에서 적용된다. 각 임펄스 사이에는 열 냉각이 있다. 비고 맹점은 SPD 가 /imp 에서 올바르게 기능하는 동안 SPD 의 고장을 일으킬 수 있는 /imp 보다 낮은 전류 값에 해당한다. 대표적인 예로 스파크 갭과 병렬로 연결된 금속 산화 배리스터(MOV)가 있다. 간격이 트리거되지 않으면 전체 서지가 배리스터에 인가된다. 이 배리스터는 갭과 동일 한 스트레스를 견디지 못하고 고장날 수 있다. I 등급 시험을 위한 추가 동작책무시험 각 임펄스 전류 통전 동안과 이후에 Uc 에서 전원 공급 Chart Type: line Uc 5 A item_01 1.0 그림 A.3 - 추가 5 회의 임펄스에 대한 시험 시간 흐름도 15 회의 임펄스가 인가되는 동안 SPD 는 Uc 에서 전원을 공급받아야 한다. AC 전원의 기능은 속류를 생성하거나 생성하지 않는 SPD 동작에 따라 선택해야 한다(예를 들면 전압 스위칭 부품이 있는 경 우). 스위칭(크로바형) 부품의 존재를 확인하고 속류의 크기를 결정하기 위한 시험은 다음과 같은 이 60 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
8033bb86-0330-44ab-88d6-e2da222de9e8 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 유로 수행되어야 한다. 속류가 없거나 500 A 이하의 속류: AC 전원의 임피던스 또는 용량은 속류가 흐르는 동안 전원 주 파수 전압의 피크값이 Uc 의 피크값 이하로 10 % 이상 떨어지지 않도록 하여야 한다. 속류가 500 A 초과: AC 전원의 예상 단락 전류는 제조자가 선언한 정격 차단 속류 /fi 또는 500 A 중 더 큰 값과 동일하다. 예상 단락 전류는 TN 및/또는 TT 시스템에서 N 과 PE 사이에 연결된 SPD 의 경우 최소 100 A 여야 한다. 5 회의 추가 임펄스가 인가되는 동안 SPD 는 최소 5A 를 전달할 수 있는 AC 전원에 의해 Uc 에서 전 원 공급된다. 이 시험 후, 잔류 전압이 선언된 보호 레벨보다 여전히 낮은지 확인하기 위해 2 회의 최종 임펄스가 인가된다. SPD 는 눈에 보이는 손상 없이 동작 상태를 유지해야 한다. A.2.2.2.8 열 안정성(7.2.5.2/8.3.5.2) SPD 는 성능 저하 또는 과도한 스트레스로 인한 과열로부터 보호된다. 이 시험은 전압 제한형 SPD 및 전압 제한 부품과 전압 전환 부품이 직렬로 있는 조합형 SPD 에서만 수행된다. 이 경우 전압 전 환 부품을 단락 시켜야 한다. SPD 는 전류가 흐르도록 충분히 높은 AC 전압으로 스트레스를 받는다. 이 전류는 모니터링되고 시작 값이 2mA 로 설정된다. 각각의 열 안정성 기간 후 전류는 2mA 단계 씩 증가한다. 시험 대상 SPD 의 외부 온도를 모니터링한다. 전류가 분리기(내부 또는 외부)에 의해 차단되면 시험이 중지된다. SPD 에 인가되는 전압이 Uc 보다 낮아지면 상당한 단락전류 용량을 가진 Uref 로 설정된 전원이 인가되 어 외부 분리기의 동작으로 이어질 수 있다. SPD 는 무결성을 확인하기 위해 점검되며, 시험 중과 시 험 후 온도 상승을 최댓값과 비교한다(5 분 동안 120 K 및 5 분 후 80 K). A.2.2.2.9 공간 거리 및 연면 거리(7.3.4/8.4.3) 공간 거리와 연면 거리는 표본에서 확인 및 측정되며 KS C IEC 61643-11 에서 제공한 표와 비교된다. 주어진 공간 거리는 SPD 에서 수행한 모든 서지 시험 동안 측정된 최대 피크 전압에 따라 달라진다. 거리는 분석되는 부품에 따라 다르다(예를 들면 충전부와 SPD 의 고정 표면 또는 본체 사이의 여유 공간에 대한 요구사항이 다름). 연면 거리는 공칭 전압과 전도성 부품을 절연하는 표면의 능력(오염 등급 포함)에 따라 다르다. 공간 거리는 주어진 고도에 따라 정의 된다. A.2.2.2.10 볼 프레셔 시험(7.4.2/8.5.3) SPD 는 다양한 온도(외함 부품의 기능에 따라 70 °C 및 125 °C)에서 1 시간 동안 20 N 으로 설정된 2.5 mm 반경 볼 프레셔를 받는다. 변형을 측정하며 이는 2 mm 를 초과 해서는 안 된다. A.2.2.2.11 비정상적인 열 및 화재에 대한 내성(7.4.3/8.5.4) SPD 는 외함 부품의 기능에 따라 650 °C ~ 850 °C 의 온도를 갖는 글로와 이어로 스트레스를 받는다. 61 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
6255fea8-3386-4088-a42f-fd66e8baf14a | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 물질은 타지 않거나 30 초 이내에 자체적으로 소화되어야 한다. A.2.2.2.12 내트래킹성(7.4.4/8.5.5) 2 개의 전극이 절연 재료 표면 위에 4 mm 거리에 배치되고 (100~600) V AC 로 전원이 공급된다. 시험 된 표면에 용액을 떨어뜨려서 전류가 증가하거나 재료가 변질되면 시험을 중지한다. 그런 다음 트래 킹 지수를 결정하고 제조자 선언과 비교한다. A.2.2.3 시험 순서 2 A.2.2.3.1 전압 보호레벨(7.2.3/8.3.3) 이 시험은 "잔류 전압(8.3.3.1)", "파두 스파크오버 전압(8.3.3.2)" 및 "조합파 발생기로 전압 제한 (8.3.3.3)"의 세 부분으로 구성된다. I 등급 및 II 등급 시험의 경우 잔류 전압을 8/20 파동 발생기를 사용하여 두 극성 모두에서 0.1, 0.2, 0.5, 1.0 배의 In 또는 /imp 에서 측정한다. 또한 스위칭 부품 동작을 나타내는 SPD(1.2/50 전압 임펄스 발생기는 500 옴의 내부 임피던스와 6 kV 의 개방 회로 전압으로 설정됨)의 경우 1.2/50 파형의 추가 5 개의 정극성 및 5 개의 부극성 임펄스가 SPD 에 인가된다. III 종 시험의 경우, 선언된 Uoc 의 0.1, 0.2, 0.5, 1.0 배로 설정된 조합파 발생기에서 생성된 임펄스를 인 가할 때 잔류 전압을 측정한다. 측정된 제한 전압을 결정하는 데 사용되는 잔류 전압은 SPD 시험 등급에 따라 해당하는 In, /imp 또는 Uoc 에서 측정된 가장 높은 전압이다. 잔류 전압은 선언된 전압 보호 레벨 Up 보다 낮거나 같아야 한다. Imax 를 선언하면 Imax 에서 추가 8/20 임펄스가 SPD 에 인가하여 잔류 전압을 측정한다. Umax 를 결정하기 위한 값은 SPD 시험 등급에 따라 해당 In, Imax(선언된 경우) 또는 /imp 에서 측정된 가 장 높은 잔류 전압이다. A.2.2.3.2 제조자가 선언한 경우 부하측 서지 내성(7.6.2.2/8.7.3) 기본적으로 II 등급 또는 III 등급 시험을 위한 임펄스 시험은 2 포트 SPD 의 부하측에서 반복된다. III 등 급 시험을 제외하고 임펄스는 항상 정극성이며 II 등급 시험에 대해 A.2.2.2.7 에서 설명한 바와 같은 방식으로 동기화된다. SPD 는 외부 또는 내부 변경 없이 기능을 유지해야 하며 잔류 전압은 선언된 전압 보호 레벨 아래로 유지된다. A.2.2.3.3 분리된 입력/출력 단자가 있는 2 포트 SPD 및 1 포트 SPD 에 대한 부하측 단락 전류 모드- SPD(7.5.1.3/8.6.1.3) SPD 는 우선 예상 단락 전류가 ISCCR 로 설정된 후 선언된 상부 보호 최대 정격의 5 배 값으로 Uc 에서 전원에 연결된다. 출력은 단락된다. SPD 는 자체 또는 내부 또는 외부 분리기에 의해 분리될 때까지 전류 손상 없이 견딜 수 있어야 한다. 62 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
27f9644e-38f6-40eb-9374-4ce500476b3d | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 A.2.2.4 시험 순서 3 A.2.2.4.1 절연저항(7.2.6/8.3.6) 48 시간동안 습도에 노출된 후 접근 가능한 모든 전도성 부품 사이의 절연 저항을 측정한다. 저항 측 정값이 제품 표준에서 요청한 최솟값보다 높은지 확인한다. A.2.2.4.2 절연내력(7.2.7/8.3.7) SPD 의 작동 전압에 따라 시험 전압으로 설정된 AC 고압 전원은 접근 가능한 모든 전도성 부품 사 이에 1 분동안 인가된다. 시험 중에는 스파크오버가 허용되지 않는다. 실외 SPD 의 경우 이 시험은 젖 은 상태(살수)에서 추가로 수행된다. A.2.2.4.3 분리된 회로가 있는 SPD 를 위한 보조회로 간 분리(7.5.3/8.3.6, 8.3.7) 내부 보조 회로와 전원 회로 사이에 절연저항 및 절연내력 시험이 반복된다. A.2.2.4.4 기계적 강도(7.3.5/8.4.4) 시료는 다양한 높이에서 던져진 관절형 레버에 부착된 질량에 의한 충격 스트레스로 시험된다. 이 시험은 다양한 부분(전면, 측면, 후면 등)에서 다양한 레벨의 에너지로 시료를 망치로 두드리는 해머 시험과 비교할 수 있다. 시료에 심각한 손상이 발견되지 않으면 이 시험은 통과 한다. A.2.2.4.5 온도 내성(7.2.5/8.3.5.1) SPD 는 24 시간동안 온도 80 °C 에 노출된다. 그 어떤 외부적 또는 내부적 손상이 일어나지 않아야 한 다. 분리기가 동작하지 않아야 한다. 제조자가 선언한 경우 전압 강화(7.6.2.1/8.7.2) 전압 강하(SPD 의 입력과 출력 전압을 비교하는 전압 손실)는 SPD 가 전원 공급될 때 SPD 를 측정하 고, 최대 부하 전류에 이르는 값으로 부하를 조정한다. 이 측정값은 선언된 값과 비교된다. A.2.2.5 시험 순서 4 A.2.2.5.1 내열성(7.4.2/8.5.2) SPD 는 100 °C 의 온도에서 1 시간 동안 캐비닛에 넣은 후 내부 분리기의 동작이 허용되더라도 눈에 띄는 주요한 열화나 성능에 문제를 일으킬 수 있는 열화를 보이지 않아야 한다. A.2.2.5.2 TOV 시험(7.2.8 8.3.8) 이 시험은 두 부분으로 구성된다. 저압 시스템의 결함 또는 교란으로 인한 TOV: (7.2.8.1/8.3.8.1), "고 (중)압 시스템(7.2.8.2/8.3.8.2)의 결함으로 인한 TOV". 시료에는 다양한 시간 동안 다양한 전압과 다양한 단락 전류를 가한다. 이러한 특정 스트레스는 세 가지 가능한 임시 과전압 상황을 시뮬레이션해야 한다. 다양한 상황은 LV 시스템 형태 및 접지 구성 에 따라 다양한 보호 모드에 다양한 스트레스 전압을 생성한다. 63 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
f0a4b756-de03-4290-8aa8-741d21285cc1 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 HV/LV 변압기의 고전압 측 접지 결함으로 인한 TOV 는 N-PE 와 L-PE 사이의 전압을 증가시킬 수 있다. 시험은 200 ms 동안 제한된 300 A 전원으로 수행된다. TOV 는 TT 시스템의 접지 오류 또는 TN 시스템의 PEN 오류 또는 TT 와 IT 시스템의 중성선 오류 로 인해 전원 시스템의 LV 측에서 발생한다. 시험은 5s 동안 무제한 전원으로 수행된다. 부하측에 따라 2 상/3 상 LV 시스템 모두에서 중성선 단선으로 인해 LV 측에서 TOV 가 발생한다. 시험은 120 분 동안 10 A 의 제한된 전류와 전체 상간 전압으로 수행된다. 시험 후 SPD 의 요구된 상태는 TOV 고장 형태와 이러한 조건에서 SPD 의 선언된 동작에 따라 다를 수 있다. 각 TOV 스트레스 후 전원 시스템이 정상 동작으로 돌아가고 SPD 의 상태를 점검하여 안전 문제(폭 발, 균열 또는 기타 잠재적으로 위험한 사고)가 없는지 확인한다. TOV 내력 모드는 SPD 제조자가 선언해야 한다(표 E.3 참조). A.2.2.6 시험 순서 5 A.2.2.6.1 단락전류특성(7.2.5.3/8.3.5.3) 예상 단락 전류로 전원 장치에 연결하려는 보호 모드의 경우 SPD 는 각 설정에 대해 준비된 별도의 시료 세트를 사용하여 두 가지 다른 시험 설정에서 검사한다. 준비는 구리 블록 막대로 서로 다른 각 전류 경로의 능동 기기를 교체하는 것으로 구성된다. 이 시 험의 목적은 화재, 폭발 또는 감전과 같은 위험을 일으키지 않고 SPD 의 단락에 의해 생성된 스트레 스를 견딜 수 있는 내부 전류 경로의 능력을 확인하는 것이다. 시험 중 예상 단락 전류는 먼저 ISCCR 로 설정한 다음 상부 최대 보호 정격의 5 배로 설정한다(선언되 지 않은 경우 300 A 로 설정됨). 이 전류는 ISCCR 에 대해 두 번 인가되고 더 낮은 전류에 대해 한 번 인가된다. 전압의 영점 교차 후 45 위상각에서 개시된다. 내부 또는 외부 분리기에 의해 전류가 분리되거나 낮은 예상 단락 전류가 인가된 후 시간이 5 초에 이르면 시험이 중지된다. 5 초를 선택하여 최대 고장 분리 시간을 대표한다. /fi 를 선언하고 ISCCR 이 /fi 보다 높을 때 /SCCR 로 설정한 시험을 반복하지만 시료 준비는 따르지 않는다. SPD 의 전압 스위칭 부품은 속류를 개시하기에 충분히 높은 서지 전류로 트리거된다. 이 시험은 외 부 분리기의 동작으로 이어진다. A.2.2.7 시험 순서 6 A.2.2.7.1 멀티모드형 SPD 에 대한 전체 방전 전류 시험(7.6.1.1/8.7.1) 멀티모드형 SPD 는 각 극의 서지 내력과 다를 수 있는 전체 서지 내력을 나타낼 수 있다. 이 시험은 SPD 가 모든 활성 단자를 통해 동시에 PE 단자(또는 전선)로 흐르는 서지 전류를 견디는 능력을 확인하고자 한다. 그런 다음 모든 활성 단자가 함께 결합되고 서지 발생기가 이 공통 지점 및 PE 단자에 연결된다. 시험은 서지 전류가 PE 에 대한 모든 보호 모드에서 동일하게 공유되는 방 64 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
b2251822-cd8b-4717-ad0a-037e840874e6 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 식으로 이루어진다. 서지는 선언된 /Total 전류에서 한 번만 인가되며 SPD 는 어떠한 손상도 보이지 않아야 한다. ITotal 는 명 시된 I 등급 또는 II 등급 시험의 SPD 등급과 일치하도록 8/20 또는 10/350 파형이 될 수 있다. A.2.2.8 시험 순서 7 A.2.2.8.1 옥외용으로 분류된 SPD(7.5.2/8.6.2) 옥외용으로 선언된 SPD 의 경우 추가 시험을 수행해야 한다. UV 방사선을 이용한 가속 노화 시험 물 침수 시험 절연 시험 온도 사이클 시험 침식에 대한 내성 시험 이러한 시험은 KS C IEC 61643-11:2011 의 부속서 F 에 기술되어 있다. A.2.2.9 시험 순서 8 - 단락형 SPD(7.5.4/8.6.4) 이 시험은 다음의 세 부분으로 구성된다. "특성 절차 변화(단락 조건으로 사전 조정)(8.6.4.1)", "서지 내성 시험(내부 단락 상태)(8.6.4.2)" 및 "단락 전류 특성 시험(내부 단락 상태) (8.6.4.3)" 이 시험은 외부 손상 없이 시료를 단락 상태로 전환하기 위해 선언된 조정 임펄스 Itrans 를 인가하여 수행한다. 그런 다음 A.2.2.6.1 에 설명된 단락 전류 특성 시험이 시료에 수행된다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. 65 | {}
d37107fb-c512-4978-ac2a-9605a15339d1 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 부속서 B (참고) Uc 와 공칭 시스템 전압 간의 관계 및 금속 산화 배리스터(MOV)의 Up 와 Uc 간의 관계에 대한 예 B.1 Uc 와 시스템의 공칭 전압 간의 관계 KS C IEC 60364-5-53 에 주어진 값에 기초한 Uc 와 KS C IEC 60664-1 에 따른 시스템의 공칭 전압 간의 관계는 표 B.1 에 나타낸다. 표 B.1 - Uc 와 시스템의 공칭 전압 간의 관계 ¦ KS C IEC 60664-1 에 따른 시스템의 공칭 전압 ¦ KS C IEC 60664-1 에 따른 시스템의 공칭 전압 ¦ KS C IEC 60364-5-53 에서 제시된 값을 근거로 한 Uc 의 예 ¦ KS C IEC 60364-5-53 에서 제시된 값을 근거로 한 Uc 의 예 ¦ KS C IEC 60364-5-53 에서 제시된 값을 근거로 한 Uc 의 예 ¦ KS C IEC 60364-5-53 에서 제시된 값을 근거로 한 Uc 의 예 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 3 상 4 선식 중성점 접지 시스템 ¦ 3 상 3 선식 또는 4 선식 비접지 게통 ¦ TN 시스템 a 에서 상과 PE 또는 PEN 간에 설치 된 SPD 또는 TT 시스템 a 에서 상과 중성선 간에 설치된 SPD 의 Uc 최솟값 ¦ TT 시스템 a 에서 상과 접지 또는 중성선과 접지 간 에 설치된 SPD 의 Uc 최솟값 ¦ IT 시스템에서 상과 접지 또는 중성선과 접지 간 에 설치된 SPD 의 Uc 최솟값 ¦ TT, TN 또는 IT 시스템에서 상과 상 사이에 설치 된 SPD 의 Uc 최솟값 ¦ ¦ TT 및 TN 시스템 ¦ IT 시스템 ¦ 전압 변동이 10 %와 동일한 경우 ¦ 1.5 x Uo 값을 사용한 경우 ¦ V3 x Uo 값을 사용한 경우 ¦ 전압 변동이 10 %와 동일한 경우 ¦ ¦ V ¦ V ¦ V ¦ V ¦ V ¦ V ¦ ¦ 120/208 ¦ ¦ 132 ¦ 180 ¦ ¦ 229 ¦ ¦ 127/220 ¦ 220 ¦ 140 ¦ 191 ¦ 220 ¦ 242 ¦ ¦ ¦ 230, 240 ¦ ¦ ¦ 240 ¦ 264 ¦ ¦ ¦ 260, 277, 347 ¦ ¦ ¦ 347 ¦ 382 ¦ ¦ 220/380, 230/400 ¦ 380,400 ¦ 253 ¦ 345 ¦ 400 ¦ 440 ¦ ¦ 240/415, 260/440 ¦ 415 ¦ 286 ¦ 390 ¦ 415 ¦ 484 ¦ ¦ 277/480 ¦ 440, 480 ¦ 305 ¦ 416 ¦ 480 ¦ 528 ¦ ¦ a 일부 조건하에서 상위값이 필요할 수도 있다(예를 들면 TT 시스템에서 중성선 단선). ¦ a 일부 조건하에서 상위값이 필요할 수도 있다(예를 들면 TT 시스템에서 중성선 단선). ¦ a 일부 조건하에서 상위값이 필요할 수도 있다(예를 들면 TT 시스템에서 중성선 단선). ¦ a 일부 조건하에서 상위값이 필요할 수도 있다(예를 들면 TT 시스템에서 중성선 단선). ¦ a 일부 조건하에서 상위값이 필요할 수도 있다(예를 들면 TT 시스템에서 중성선 단선). ¦ a 일부 조건하에서 상위값이 필요할 수도 있다(예를 들면 TT 시스템에서 중성선 단선). ¦ B.2 금속 산화 배리스터(MOV)의 Up 과 Uc 간의 관계 Up/Uc 비율은 SPD 를 특징짓는 데 중요한 매개변수다. 이 비율은 사용된 부품에 따라 좌우된다. 다음 표 B.2 는 부속품 크기와 적용된 전류 In 에 따라 변하는 금속 산화 배리스터(MOV)의 Up/Uc 일반적 비 율값을 제시하고 있다. 66 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
d3200fa2-bc2e-47f4-948f-bd9d1e14e4af | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 표 B.2 - 금속 산화 배리스터(MOV)의 Up/Uc 값의 예 ¦ In (8/20) kA ¦ 지름 mm ¦ 금속 산화 배리스터 (MOV)의 Up/Uc ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ 14 ¦ 3.3 ¦ ¦ 2.5 ¦ 20 ¦ 3.8 ¦ ¦ 5 ¦ 32 ¦ 4.1 ¦ ¦ 10 ¦ 40 ¦ 4.6 ¦ ¦ 20 ¦ 60 ¦ 4.6 ¦ 기술에 따라 기기에서 더 낮은 비율이나 더 높은 비율을 모두 얻을 수 있다. 비고 서지 내력과 같은 다른 매개변수도 기술에 따라 달라진다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 67 | {}
dc3a945f-6480-4a1f-bbb0-914879e2ac73 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 부속서 C (참고) 환경 - LV 시스템의 서지 전압 C.1 일반사항 서지 과전압은 세 가지 유형의 사건 결과 로 저압 시스템에서 발생한다. 전력 시스템을 직접 뇌격하거나 가까이 있는 다른 물체를 뇌격하여 과전압을 유도시킬 수 있는 낙 뢰와 같은 자연 현상 전력 회사 또는 최종 수용가 작업에 의해 저압 시스템 또는 송전 또는 배전 시스템에서 일어나는 부하나 캐패시터 스위칭과 같은 전력 시스템에 대한 의도적인 행동 전력 시스템의 고장과 그 고장의 제거 또는 전력 시스템과 신호/통신 시스템 간의 상호 작용과 같 은 다른 시스템 간의 결합 등의 의도되지 않은 사건 이 표준에서 고려하는 서지 과전압은 피크 동작 전압의 2 배(단위당 2 개 또는 2p.u.)를 초과 하고 지속 시간이 마이크로초에서 밀리초까지인 전압이다 여기에서 단위당 2 미만의 과전압은 고려되지 않고, 전력 장치의 동작과 고장 모드에서 생기는, 지속시간이 긴 과도 현상도 고려하지 않는다. 작은 진폭 과 장기간의 서지는 일반적으로 통상적인 서지보호장치로 억제할 수 없기 때문에 이 표준에서 의논 되고 있는 것과 는 다른 보호 기술이 필요하다. 이 부속서는 이 표준의 사용을 용이하게 하기 위해 IEC TR 62066 의 저압 시스템의 서지 전압에 대한 중요한 정보를 제시하고 요약한다. C.2 낙뢰 과전압 C.2.1 일반사항 낙뢰는 여러 메커니즘을 통해 저압 시스템(전력 시스템 및 신호/통신 시스템)에 영향을 미치는 피할 수 없는 사건이다. 시스템에 영향을 주는 분명한 상호 작용은 직격뢰이지만, 다른 결합 메커니즘도 시스템의 과전압을 초래할 수 있다. 저압 시스템에 과전압을 일으킬 수 있는 세 가지 결합 메커니즘 을 논의 한다. 이 논의 에서는 "과전압"을 언급하지만, 과전압과 관련된 전류 또는 애초에 과전압을 일 으킨 전류를 고려하는 것이 이번 논의 의 중요한 주제다. 세 가지 범주는 다음과 같다. a) MV/LV 배전용 변압기의 1 차측과 LV 배전 시스템(가공 및 지중) 및 각각의 건물에 대한 가공 인 입선에 발생할 수 있는 전력 시스템에 대한 직격뢰 b) 간접뢰: 가까이에 있는 물체에 떨어진 낙뢰로, 유도 결합 또는 동일 경로 작용에 의해여 LV 배전 시스템에 과전압을 일으킨다. 이런 낙뢰로 인한 과전압 및 서지 전류는 직격뢰로 인한 것보다 정 도가 약할 수 있으나 발생 빈도는 훨씬 더 많다. c) LPS 또는 최종 사용자 건물의 외부 부품(철 구조물, 수도관, 난방 및 공조 덕트, 엘리베이터 샤프 트 등의 비전기 부품)에 대한 직격뢰. 이런 뇌격에는 두 가지 영향력이 있다. 건물 외부 부품에 흐르는 뇌전류의 유도 결합과 주입되는 낙뢰 전류는 LV 시스템 도체와 접지 사이에 SPD 를 설치 68 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
e0c270da-d636-45f6-a711-b2e1a3e2f9e3 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 하는, 이른바 설비의 등전위 본딩으로도 막을 수 없다. 어떤 낙뢰가 있을 때, 사용자 설비에 나타 나는 과전압의 심각도는 뇌격점과 사용자 설비 사이의 거리와 시스템 특성, 접지 방식과 접지 임 피던스, 경로를 따라 SPD 가 있는가, 배전 시스템의 분기 등과 같은 결함 경로의 특성에 따라 달 라진다. C.2.2 MV 에서 LV 시스템으로 전달된 뇌 서지 낙뢰에 의해 MV 시스템에서 생성된 과전압 서지는 두 가지 다른 방식으로 LV 배전 시스템으로 전달 된다. MV/LV 변압기를 통한 용량 및 유도 결합에 의해 접지 결합에 의해 전달된 뇌 서지 크기는 다음과 같은 여러 매개 변수에 따라 달라진다. LV 접지 시스템(TT, TN,IT) LV 선로 및 LV 부하의 특성 LV 과전압 보호 장치 MV 와 LV 접지 사이의 결합 조건 변압기 설계 MV 선로에 직격뢰가 발생하는 경우, 서지 피뢰기 동작 또는 절연체 스파크오버가 접지 시스템을 통 해 서지 전류를 전환하고 MV 와 LV 시스템 사이에 저항성 접지 결합을 생성할 수 있으며 과전압이 LV 시스템으로 전달된다. 접지 임피던스 값에 따라 이 접지 결합 과전압은 변압기를 통한 용량 결합 보다 훨씬 높을 수 있다. TN 시스템에서 중성선 역시 고객 설비에서 접지되면 더 작은 과전압이 발생한다. 또한 이러한 종류 의 저항성 결합은 변압기의 LV 부분에 별도의 접지 시스템을 사용하여 피할 수 있다. MV/LV 변압기 측의 2 차측으로 용량 및 유도 결합에 의해 전달되는 과전압의 일반적인 값은 상 도체 와 중성 도체 사이의 MV 상 대 접지 전압의 2 %이고 상 도체와 접지 사이의 8 %다. 이 값은 부하된 LV 회로에서 일반적이다. 변압기의 LV 측이 열려 있거나 매우 가벼운 부하가 있는 경우 LV 시스템 에 따라 값이 훨씬 더 높을 수 있다. MV 시스템에서 유도된 뇌 서지는 직격뢰보다 훨씬 작은 서지 전류(일반적으로 1 kA 미만)를 생성하 며, 과전압은 실제로 용량 결합에 의해서만 LV 시스템으로 전달되고 몇 킬로볼트를 초과 하지 않는다. 이러한 경우 LV 시스템에서 직접 유도되는 과전압(적어도 직격뢰 지점에서 멀지 않은 부분)은 일반 적으로 MV 측에서 전달되는 과전압보다 높다. SPD 가 동작하거나 스파크오버가 발생할 경우 전류는 작고 저항성 결합은 무시할 수 있다. C.2.3 LV 전력 시스템에 대한 직격뢰로 인한 과전압 뇌 경로의 유효 임피던스가 높아서 낙뢰 전류는 이상적인 전류원으로 간주될 수 있다. 따라서 생성 된 과전압은 뇌 전류에 의해 나타나는 일시적인 유효 임피던스에 의해 결정된다. 뇌가 선로에 떨어지면 전압은 순간적으로 그 선로의 특성 임피던스(서지 임피던스)에 의해 결정된다. 69 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
19e067b1-eb17-4782-93d1-ff747bcbf717 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 그 전류(1)는 처음에 두 부분으로 나뉘며 생성된 전압 서지(U)는 다음과 같다. U=ZxI/2 여기에서 U : 서지 전압(kV) Z : 선로의 서지 임피턴스(�) I : 서지 전류(KA) 중간 정도의 서지 전류 10 kA 와 400 �의 서지 임피던스를 가정하면, 예상되는 전압 서지는 2 000 kV 이다. 따라서 저압선의 경우 방전은 일반적으로 모든 선로 도체 사이에서 일어나며 대부분의 경우에 땅으로도 방전이 일어난다. 방전이 일어난 다음에 유효 임피던스는 관련된 접지 저항에 따라 줄어든 다. 그러나 예를 들어 10 �과 같이 다소 낮은 유효 임피던스의 경우에도 전압은 앞의 예에서 가정한 10 kA 뇌전류에 대해 그 선로의 전압은 100 kV 가 된다. 가공선/케이블이 결합된 시스템에서는 가공선에 비해 케이블의 서지 임피던스가 낮아 과전압이 다소 감소한다. 감소량은 전류의 지속 시간과 시스템 접지에 대한 전체 커패시턴스에 따라 달라진다. 그러 나 일반적으로 이 감소량은 저압 시스템에서 일반적인 절연 수준을 초과 하는 과전압을 방지하기에 충분하지 않다. 따라서 대부분의 경우 직격뢰는 이러한 시스템에 손상을 일으키는 것으로 보아야 한다. C.2.4 LV 배전 시스템의 유도 과전압 낙뢰가 일어나는 중 전자기장의 변화로 인해, 모든 종류의 가공선에 낙뢰로부터 상당히 멀리 떨어진 곳의 선로에도 서지가 발생하게 된다. 대강 어림잡아, 선로의 예상 과전압(U)은 다음 식에서 추산할 수 있다. U= 30 xkx(h/d)xI 여기에서 U : 예상 과전압(kV) I : 뇌전류(KA) h : 땅에서 도체까지의 높이(m) k : 낙뢰 경로의 귀환 스트로크의 속도에 관한 인자 d : 낙뢰에서 떨어진 거리(m) 매개변수 k 의 변동은 작다(1.0 ~ 1.3). 뇌전류를 중간값인 30 kA 로 하고 지면에서부터 선로의 높이를 5m 로 할 때, 1 km 거리에 떨어진 낙뢰 로 인한 전압은 5 kV 를 초과 한다. 이런 경우, 100 kA 의 전류는 10 km 의 거리에서도 1.8 kV 의 예상 과 전압을 발생시킨다. C.2.5 뇌 보호 시스템 또는 근접한 구조물에 떨어진 낙뢰로 인한 과전압 LV 전력 시스템에 의해 병렬로 공급되는 여러 구조물 중 하나에 낙뢰가 부딪힐 때 대지로 흐르는 뇌 전류는 다양한 유효 경로로 나뉜다. 여기에는 국부 접지(건물 접지)와 모든 금속 경로(주로 전원 공 급 케이블)를 통한 원거리 접지 지점이 포함된다. 주입된 서지 전류는 LPS 의 피뢰침전극에서 인하도선을 통해 접지 종단 시스템으로 흐른다. 그 지점 에서 뇌전류는 적어도 두 가지 부품으로 나뉜다. 하나는 건물의 국부 접지로 흐르고 다른 하나는 전 70 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
608b87e3-5ad9-46ca-9594-a418bbc029fa | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 원 공급 케이블을 통해 원거리 접지로 흐른다(전류는 금속 파이프 및 기타 전도성 서비스와 같은 다 른 경로를 따를 수도 있다.). 이 전류는 임피던스의 역비례에 따라 나뉜다. 임펄스 전류의 초기 단계 에서 전류 분산은 인덕턴스의 비율에 의해 결정된다. 전류의 변화률이 작은 끝 부분에서는 분산이 저항률에 의해 결정된다. 여러 건물이 전기적으로 연결되면 유효 저항이 감소한다. 이는 더 많은 건물이 스트링에 연결될 때 타격을 받은 건물에서 LV 시스템으로 흐르는 뇌전류의 양이 증가한다는 것을 의미한다. 중성 접지에 대한 방식은 국가마다 다르므로 유효 경로 간에 뇌전류가 분산되는 방식에 약간의 차이 가 예상될 수 있다. 시스템 설계자는 이러한 차이점을 고려해야 한다. 유효 경로 간의 전류 분산은 주로 도체와 국부 접지 사이에 과전압을 발생시킨다. LV 설비의 구성과 SPD 의 유무에 따라 이러한 과전압은 크거나 중간일 수 있다. 경험은 서비스 인입구에서 개선된 중 성 접지의 유익한 효과 와 저항, 유도 및 상호 결합 효과 를 고려하는 것의 중요성을 보여준다. 건물이나 구조물에 대한 직격뢰로 인한 접지 전위 상승은 일반적으로 저압 설비의 절연 수준을 초과 하며, 등전위 본딩 SPD 가 장착되지 않은 경우. 결과 적으로 동일한 저압 배전 네트워크에 연결된 인 접 건물(설비)로 전파되는 뇌방전과 과전압을 발생시킨다는 점에 유의 해야 한다. 결과 적으로 낙뢰가 치지 않은 건물이라도 배전 네트워크를 따라 전파되기 때문에 과전압에 노출될 수 있다. 더욱이 해당 지역의 주어진 낙뢰 밀도의 경우, 고층 건물이 있으면 주변의 작은 건물에 직 격뢰가 떨어질 확률은 감소하지만 과전압이 전도될 가능성은 높아진다. 도체 사이의 과전압과 국부 접지는 연결된 장비의 절연에 스트레스를 가하며 일반적으로 KS C IEC 60664-1 권고사항에 따라 충분한 내력 수준을 갖는 반면 전력 장비의 작동 부품은 도체 사이에 나타 나는 과전압에 의해 스트레스를 받는다. 언뜻 보기에 가장 위협적인 상황은 전력 장비의 작동 부품 에 가해지는 과전압일 수 있다. 그러나 접지에 대한 과전압은 전력 장비 절연에 대한 문제가 아니라 장비에 연결될 수도 있는 전력 시스템과 통신 시스템 간의 기준 전위 이동의 결과 로 문제가 될 수 있다. C.3 스위칭 과전압 C.3.1 일반사항 LV 발전기가 설비에 전원을 공급하거나 유도 또는 용량 부하(예를 들면 모터, 변압기, 커패시터 뱅크 등), 저장 장치 또는 고전류 부하가 설치된 곳과 같은 설비의 과전압 범주에 따라 스위칭 과전압 또 는 그 값을 초과 하는 교란을 생성할 가능성이 있는 기기의 경우 스위칭 과전압에 대한 보호를 고려 해야 한다. 이 경우 그러한 위협의 원인과 가능한 한 가까운 곳에 SPD 를 설치하는 것을 고려하는 것이 좋다. 전류, 전압, 지속 시간으로 나타나는 이러한 스트레스는 일반적으로 낙뢰 스트레스보다 작다. 그러나 어떤 경우에는 특히 구조물 내부 깊숙이 또는 스위칭 과전압 전원 근처에서 스위칭 스트레스가 낙뢰 스트레스보다 클 수도 있다. 적절한 SPD 를 선택하기 위해서는 이러한 스위칭 서지의 에너지를 알 필요가 있다. 고장과 퓨즈 동작에 따른 과도 현상까지 포함하는 스위칭 서지의 지속 시간은 낙뢰 서 지 기간보다 훨씬 더 길 수도 있다. 일반적으로 전기 시스템에서 모든 스위칭 작용, 고장 개시, 차단 뒤에는 과전압이 발생하는 과도 현 상이 따라온다. 시스템의 급격한 변화는 그 시스템이 다시 새로운 정상 상태로 안정될 때까지(전력 71 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f7c63df4-ecfe-46e7-9309-1c9ce652db7f | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 시스템의 공진 주파수에 의하여 결정되는) 고주파수를 가진 감쇄 진동을 일으킬 수 있다. 스위칭 과전압의 크기는 예를 들어 회로의 종류, 스위칭 조작의 종류(닫힘, 열림, 재충격), 부하, 회로 차단기 또는 퓨즈 등 많은 매개변수에 따라 달라진다. 스위칭 조작이 일어나는 동안 진동의 주파수는 시스템의 특성에 따라 결정되며, 때때로 공진 현상이 발생할 수도 있다. 이런 경우에는 매우 높은 과전압이 발생할 수도 있다. 일반적으로 시스템의 전원 주파수의 고조파와 공진을 일으킬 가능성은 낮다. 그러나 시스템의 스위칭 부분의 특성 주파수가 시 스템의 나머지 부분의 공진 주파수와 근접한다면 과도 공진 현상이 일어날 수도 있다. C.3.2 일반적 설명 스위칭 서지의 대표적인 형태는 저압 시스템의 응답에 의해 결정된다. 대부분의 경우에 이것은 감쇄 하는 진동파가 된다. 주파수는 일반적으로 마이크로초당 수백 킬로헤르츠 정도다. 최고 상승률은 일 반적으로 마이크로초당 몇 킬로볼트 정도다. 서지 지속 시간은 훨씬 더 넓은 시간대에 걸쳐 분포한 다. 퓨즈의 동작에 의하여 발생한 스위칭 과전압을 제외하면, 대표적인 지속 시간(크기가 반으로 줄 어드는 시간)은 1 sm ~ 50 us 다. 통계 자료를 보면 크기도 작고 지속 시간이 긴(100 sm 이상) 서지가 발생할 가능성은 매우 낮다. C.3.3 차단기와 스위치 작용 C.3.3.1 일반사항 차단기와 스위치는 과부하 또는 단락 시 전원을 꺼서 전기 설비를 보호하거나 전원 켜기와 전원 끄 기를 통해 장비의 동작을 제어하기 위해 모든 설비에 널리 사용된다. 스위칭 동작 발생률은 그 응용 영역에 의존하게 되는데, 산업 환경에서 그 비율이 높고 가정용에서는 비율이 상대적으로 낮다. 저항 부하의 경우 스위칭 전류는 그 장치의 정격 전류 범위 안에 있다. 그러나 스위칭 모드 전원 공 급 장치가 있는 경우 그 스위칭 전류가 정격 전류보다 훨씬 높다. 예를 들어, 100 W 텔레비전 수상기 의 경우 정격 전류는 0.4A 인 반면 유입 전류는 약 20 A 로 50 배 더 높다. 수동 또는 전기 기계 동작으로 움직이는 기계적 스위치 기어는 각 스위칭 과정에서 전기 아크를 생 성하게 된다. 고주파 진동은 스위치에서 일어나는 갑작스러운 전압 변화와 스위치 주변의 인덕턴스 및 커패시턴스의 상호 작용에 의해 일어난다. 이 진동은 선도체 사이 및 선도체와 접지 사이의 전압 에 중첩되며, 전체 전압은 노출된 도체와 기타 회로에 대해 전기 장치의 절연에 스트레스를 준다. 공 공 배전 시스템을 통해 고객 설비로 전달되는 과도 전압과 달리 차단기와 스위치에 의해 고객 설비 내에서 생성된 스위칭 과도 전압은 별로 감쇠되지 않은 상태로 전기 장치에 영향을 준다. 따라서 이 런 과도 전압의 크기는 상대적으로 큰 편이다. C.3.3.2 수용가 내에서 차단기와 스위치의 동작 일반적으로 장치의 스위치를 켤 때보다 끌 때, 더 높은 진폭이 발생한다. 스위치를 끄는 동안 부하 측의 스위칭 서지가 선로 측보다 진폭과 에너지가 더 크다. 그러나 이것은 주로 이러한 종류의 장치 에 국한된 문제, 특히 절연일 뿐이다. 다른 장비가 병렬로 연결된 경우에도 스트레스가 발생한다. 전 체 시스템과 그 시스템에 연결된 장치에는 선로 측의 과전압이 부하 측보다 더 중요하다. C.3.3.3 전력 시스템(LV 및 HV)에서 차단기와 스위치의 동작 모든 전력 시스템에서 전기 장치에 스트레스를 주는 과도 과전압이 발견될 수 있다. 지중 전력 시스 72 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b290c75f-97af-47a4-9b04-d43f9216fddf | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 템에서 거의 모든 과도현상은 유사한 전원의 전기 기계적 스위치 기어에 의하여 발생한다. 고압 및 저압 설비에서 변압기, 임피던스 코일, 접촉자 코일, 계전기와 같은 인덕턴스의 스위칭은 전 원과 병렬로 설치되어 진폭이 수 킬로볼트에 이르는 스위칭 과전압을 발생시킬 수 있다. 루프 도체 와 같은 직렬 인덕턴스가 있거나 또는 선로의 자체 인덕턴스로 인해 전력 시스템이 차단될 때에도 동일한 현상이 발생한다. 전원 측에서 스위칭 과전압은 게이트 제어, 슬립 링 모터의 브러시 아크, 전기 기계 또는 변압기의 급격한 부하 감소, 그리고 역률을 조정하기 위해 사용하는 커패시터의 스위치 동작에 의해 발생할 수 있다. 그러한 과전압의 빈도와 에너지는 저압 설비에 대한 영향에 관한 한 아주 드물긴 하지만 낙뢰보다 상당히 높을 수 있다. 저압 전력 시스템이 동작할 때 특정 조건으로 인해 최댓값이 제한된다고 가정하더라도 저압 전원에 서 스위칭으로 인한 과도 과전압은 수 킬로볼트의 진폭에 도달할 수 있다. 보호 장치에 의한 과전압 제어가 이루어지는 배전 시스템의 경우에는 저압 수용가 설비에 나타나는 과전압의 최댓값은 6 kV 를 초과 하지 않는다고 볼 수 있다. 스위칭 과전압과 유사한 또 다른 현상은 고압 시스템의 단락 및 접지 고장에서 발생한다. 접지 고장 으로 인해 선 간 전압 범위 내에서 선로와 대지 사이에 과전압을 일으킬 수 있다. 또한 그런 경우에 도 과도 과전압도 발생할 수 있다. 이러한 과도 전압은 고압 시스템에서 저압 시스템으로 전달된다. C.3.4 퓨즈의 동작(한류 퓨즈) 퓨즈는 과전류 보호와 단락 회로의 차단을 위해 배전 시스템 및 전기 설비에 널리 사용된다. 예를 들어 배전 시스템에서 단락을 제거하기 위해 퓨즈가 동작하면 이 동작으로 인해 대략 삼각파 과전압 이 발생하며 이는 상대적으로 빈도가 낮은 현상이다. 과전압은 접지된 중성선 또는 IT 시스템인 경우 대지 커패시턴스로 인해 시스템의 선 도체 사이, 그리고 선 도체와 보호 접지 도체 사이에서 발생한 다. 따라서 이 과전압은 노출된 도체와 다른 회로에 대해 절연재에 스트레스를 준. 물론 이 과전압은 동작 전류의 스위칭에 의하여 발생하는 과전압에 비해 드물게 발생한다. 이 과전압은 버스 바를 통 해 동일한 배전 시스템에서 전력을 공급받아 운전 중인 다른 장치에 전달된다. 스위칭 동작에 의하여 생기는 다른 서지에 비해 퓨즈 동작에 의한 서지는 그 발생 빈도가 적다. 그 러나 단락 회로를 차단하는 경우에는 매우 심한 과전압 서지가 발생할 수도 있다. 이는 주로 단락 회로 전류의 상승률, 퓨즈의 특성, 퓨즈의 전류 정격, 회로의 인덕턴스에 의해 영향을 받는다. 퓨즈의 스위칭에 의해 발생하는 과전압이 동일한 버스 바에 접속되어 운전 중인 다른 장비에 영향을 미치기 때문에, 버스 바 근처에 설치된 퓨즈로 배전 시스템 간선의 단락 사고를 제거하는 것은 중요 한 일이다. 통계에 따르면 공공 저압 공급 장치에서 이런 사고가 매우 드물다. 그러나 이러한 종류의 사고는 단락 사고가 드문 경우가 아닌 산업 분야의 배전 시스템에서는 중요한 의미를 가진다. 73 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
175df9d7-4a4f-4b6f-bf3b-0cd1f7e32a6c | KSCIEC61643-12_KR | KS CIEC 61643-12:2020 부속서 D (참고) 부분적인 뇌전류의 계산 그림 D.1 을 보면 LPS 시스템이 있는 건물이 낙뢰를 맞았다. 뇌전류 IL 은 피뢰침을 따라 타격 받은 건물의 접지 시스템으로 흐를 것이다. 이것은 잠재적인 상승을 일으키고 결과 적으로 설비에서 뇌방 전 및/또는 SPD 의 동작으로 이어져 뇌전류 IL 이 시스템의 4 개 전선에 부분적으로 분산된다. ![image](/image/placeholder) 6 a RN RE,G RE,1 RE,2 RE,n b I 6 RN RE,G RE,1 RE,2 RE,n C IL 1 RE,E 6 1 RN � RE,i RE,G RE,E II IM RE,E 1 + RE,G 식별부호 ¦ RN ¦ 중성점 접지 저항 ¦ ¦ --- ¦ --- ¦ ¦ RE,G ¦ 뇌격된 건물의 접지 저항 ¦ ¦ RE,i ¦ i 번째 건물의 접지 저항 ¦ ¦ RE,E ¦ 뇌격된 건물을 제외한 모든 접지의 총 저항 ¦ ¦ 儿 ¦ 뇌격된 건물의 뇌전류 ¦ ¦ /M ¦ 주 전원에 흐르는 전류 ¦ 그림 D.1 - 전력 배전 시스템에 흐르는 부분적인 뇌전류의 합을 구하는 간단한 계산법 이 계산에서 이웃한 건물의 접지 저항 RE,E 가 뇌격을 당한 건물의 접지 저항 RE,G 와 같거나 더 작아 야 한다. 74 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
5946ba33-bb6b-4ff3-86ba-3b104e054c5e | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 분산된 부분 전류 IM 은 시스템 및 설비에 과전압을 생성하여 절연체 및 연결된 장치에 스트레스를 준다. 따라서 타격을 입은 건물뿐만 아니라 인근 건물 및 시설물도 위험하다. 단순화된 네트워크(그림 D.1 b) 및 c))를 통해 배전 시스템에 대한 부분 전류 IM 을 단순화할 수 있다. 비고 이 계산은 에너지 공유(뇌전류 파동의 끝부분)에만 유효하다. SPD 가 서지 조건에서 받게 되는 스트레스는 복잡하고 상호 관련된 많은 매개변수의 함수다. 여기에 는 다음이 포함된다. 구조물 내 SPD 의 위치: 주 배전반에 위치하는가? 또는 보조반의 시설 내부에 위치하는가? 또는 최종 사용자 장비 앞에 위치하는가? SPD 의 업스트림에 설치된 구성요소. 예를 들어 퓨즈, 배선 단면적이 전체 시스템의 서지 처리 능 력을 제한할 수 있으므로 SPD 가 받는 최대 스트레스가 제한될 수 있다. 낙뢰를 설비에 연관시키는 방식: 예를 들어, 이것은 구조물의 LPS 에 직격하는가, 또는 근처의 타 격으로 인한 건물 배선의 유도를 통한 것인가? 구조물 내 뇌전류 분산: 예를 들어, 낙뢰 전류의 어떤 부분이 접지 시스템으로 들어가고, 어떤 부 분이 배전 시스템 및 등전위 본딩 SPD 를 통해 원격 접지로 가는가? 배전 시스템의 형태: 전력 배전 시스템에서 뇌전류의 분산은 중성 도체에 대한 접지 관행에 많이 영향을 받는다. 예를 들어, 다중 접지 중성선이 있는 TN-C 시스템에서는 TT 시스템보다 뇌전류에 대해 더 직접적이고 낮은 임피던스 경로가 제공된다. 설비에 연결된 추가 전도성 서비스: 이들은 직접 뇌전류의 일부를 전달하므로 낙뢰 등전위 본딩 SPD 를 통해 배전 시스템을 통해 흐르는 부분을 줄인다. 비전도성 부품으로 교체할 수 있으므로 이러한 서비스의 영구성에 주의 를 기울여야 한다. 고려 중인 파형의 형태: SPD 가 서지 조건에서 수행해야 하는 피크 전류를 단순히 고려하기란 불가 능하며 이 서지의 파형도 고려해야 한다. SPD 가 설비 내 여러 위치에서 경험하게 될 "위협 수준"과 전기적 환경을 정량화하려는 많은 시도가 있었다. KS C IEC 62305-4 는 고려 중인 낙뢰 보호 레벨(LPL)을 기반으로 SPD 에 표시될 수 있는 가장 높은 서지 크기를 고려하여 이 문제를 해결하려고 했다. 예를 들어, 이 표준은 LPL I 에서 구조물의 LPS 에 대한 직격뢰의 크기가 200 kA 10/350 만큼 높을 수 있다고 가정한다. 이러한 레벨은 가능하지 만 통계적 발생 확률은 1 %에 불과 하다. 즉, 뇌방전의 99 %는 이렇게 가정된 200 kA 피크 전류 레벨 보다 작을 것이다. 또한 이 전류의 50 %는 건물의 접지 시스템을 통해 전도되고 50 %는 3 선 + 중성 배전 시스템에 연 결된 등전위 본딩 SPD 를 통해 귀환된다고 가정한다. 또한 추가 전도성 서비스가 존재하지 않는다고 가정한다. 이것은 초기 200 kA 뇌방전 부분 중 각 SPD 가 경험하는 부분이 25kA 임을 의미한다. 전류 분산에 대한 단순화된 가정은 SPD 가 경험할 수 있는 위협 레벨을 고려하는 데 유용하지만 가 정이 만들어지는 맥락을 유지하는 것이 중요하다. 위의 예에서는 200 kA 의 뇌방전이 고려되었다. 따 라서 등전위 본딩 SPD 에 대한 위협 수준은 99 % 동안 25 kA 미만이 된다. 또한 SPD 를 통한 이 전 류 부품의 파형이 초기 방전과 동일한 파형 형태일 것으로 가정하고 있지만, 실제로는 건물 배선 등 의 임피던스에 의해 파형이 변경되었을 수 있다. 많은 표준은 운전 중에 SPD 가 경험할 수 있는 위협 수준에 기초하여 시간 경과 에 따라 수집된 현장 경험을 바탕으로 고려하고자 한다. 예를 들어 IEEE 환경 지침 C62.41.1 및 권고 사례 C62.41.2 는 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 75 | {}
813298f0-b1a7-419d-9303-2e9c3f1787df | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 SPD 가 설치된 위치에 따라 이러한 각 조건에서 서로 다른 노출 수준을 제시한다. 위 내용에서 SPD 의 적절한 limp, In 또는 /max(선언된 경우)의 선택은 복잡하고 상호 연결된 많은 매개 변수에 따라 달라진다. 사용자는 주입 전류가 구조물 및 전력 배전 시스템 내에서 어떻게 분산될 지 고려할 필요가 있을 뿐만 아니라 이 방전의 크기 및 관련된 파형과 관련된 통계적 확률도 고려해야 한다. 전원, 전화 및 데이터 회선을 통해 유입되는 서지 현상으로 인한 건물 내 전자 시스템의 손상 확률 은 건물 자체에 대한 직격뢰로 인한 확률보다 훨씬 크다는 점을 명심해야 한다. 많은 건물에는 LPS 가 없거나 필요하지 않을 수 있으므로 고전류 I 등급 시험 SPD 는 낮은 보호 레벨 Up 의 올바르게 설계된 II 등급 시험 SPD 시스템만큼 필요하지 않을 수 있다. 이러한 복잡함을 해결하려면, SPD 를 선정할 때 가장 중요한 측면은 예상되는 서지 사고 동안의 제한 전압 성능이지 SPD 가 처리할 수 있는 에너지 내력(/imp, In, Uoc 또는 Imax)이 아니라는 점을 명심해야 한다. 제한 전압이 낮은 SPD 는 장비의 적절한 보호를 보장하는 반면 에너지 내력이 높은 SPD 는 운 전 수명을 연장할 수 있다. 76 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b3237608-b7f2-42f5-bf2d-d8fc6d971804 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 부속서 E (참고) 고압 시스템과 접지 사이의 고장으로 인한 저압 시스템의 TOV E.1 일반사항 다음 고장은 IEC 60050-614-03-13 에 정의 되고 KS C IEC 60364-4-44 에서 제안한 대로 가장 심각한 일 시적 과전압을 야기한다. 고압 시스템의 접지 고장과 저압 시스템의 결함으로 인한 일시적 과전압을 고려하는 것이 좋다. 다음 조건을 고려해야 한다. 서로 다른 LV 시스템(TN, TT, IT) 및 HV 시스템과 LV 시스템 간의 서로 다른 접지 구성에 따라 저압 배전 시스템을 공급하는 변전소의 고압 시스템과 접지 사이의 고장 저압 시스템 또는 설비에서 중성선의 단선 - 저압 시스템 또는 설비의 단락 - 저압 IT 시스템 선도체의 우발적 접지(접지 고장) 1 kV 이상의 변전소에서의 접지 배열 요구사항은 KS C IEC 61936-1 에 제시되어 있다. IT 시스템에서 충전부는 접지로부터 절연되거나 충분히 높은 임피던스를 통해 접지에 연결되어야 한 다. 우발적인 접지(첫 번째 고장인 접지 고장) 중에는 분리할 필요가 없으므로 첫 번째 고장 조건에 서도 공급의 연속성을 보장하기 위해 IT 시스템이 점점 더 많이 사용된다. 다음 조건을 충족해야 한다: U+≤RA x ld≤50 V 절연 감시 장치는 첫 번째 고장 발생을 표시하기 위해 제공된다. 가능한 가장 짧은 시간 안에 첫 번 째 고장을 제거하는 것이 좋다. TT/TN 과 IT LV 시스템 간의 상황이 다른 이유는 IT 시스템에서 고압 시스템의 접지 고장은 저압 시스템의 접지 고장과 정의 되지 않은 시간 동안 동시에 발생할 수 있기 때문이다. IT 저압 설비에서 선과 접지(PE) 사이에 연결된 SPD 의 경우 정의 되지 않은 시간 동안 지속되는 첫 번째 LV 고장을 처리하려면 Uc 가 최대 선로 간 시스템 전압과 같거나 더 높아야 한다. 이 부속서의 지침은 저압 분배를 공급하는 변전소에서 고압 시스템과 접지 사이에 고장이 발생할 경 우 저압 설비 기기 내부의 서지보호장치(SPD)의 올바른 선정을 위한 특별한 정보를 제공한다. 저압 분배기에 연결된 SPD 는 변전소의 고압 측 접지 중 전력 주파수 스트레스 전압의 영향을 받을 수 있다. 가능한 전력 주파수 스트레스 전류는 선정한 SPD 의 고장 동작에 중요하다. 저압 시스템에 서는 다양한 형태의 접지 연결이 알려져 있으며 접지 연결 형태에 따라 다양한 스트레스 전압(U1 및 U2)과 다양한 스트레스 전류를 일으킬 수 있다. 접지 연결 형태에 따라 U1 과 U2 가 다를 수 있으므로 변전소의 저압 측 내부와 소비자(부하) 측 저압 설비에서 서로 다른 전력 주파수 스트레스 전압이 발 생할 수 있다. IT 시스템의 경우 첫 번째 LV 접지 고장이 변전소 또는 소비자의 LV 설비에 존재한다 는 점을 고려해야 한다. 다음 절은 일시적 과전압 UTOV(HV)에 대한 관련 정보 및 산출 방법을 제공 한다. 77 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
de081ebf-003b-4d77-95b0-58086a9307b2 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 E.2 참고문헌 KS C IEC 60364-5-53 KS C IEC 60364-4-44 KS C IEC 60364-1 KS C IEC 61936-1 E.3 기호 다음 기호가 사용된다. /E 변전소의 접지 장치를 통해 흐르는 고압 시스템의 접지 전류의 일부 RE 변전소의 접지 배열 저항 RA 저압 설비 장비의 노출 도전부의 접지 배열 저항 RB 변전소와 저압 시스템 중성선의 접지 배열이 전기적으로 독립된 저압 시스템의 경우 저압 시스템 중성선의 접지 배열 저항 Uo TN 및 TT 시스템 내: 접지에 대한 공칭 AC r.m.s 선 전압 비고 1 IT 시스템 내: 선도체와 중성 도체 또는 중성 도체 사이의 공칭 AC 전압. 중성선이 없는 IT 시스템에서는 일반적으로 기호 U 가 사용되며 기준은 선 간 전압이다. Uf 고장 시 노출 도전부와 접지 사이의 저압 시스템에 나타나는 전력 주파수 고장 전압 U1 고장 시 변전소 저압 장비의 노출 도전부와 선도체 사이의 전력 주파수 스트레스 전압 U2 고장 시 저압 설비 저압 기기의 노출 도전부와 선도체 사이의 전력 주파수 스트레스 전압 비고 2 전력 주파수 스트레스 전압(U1 및 U2)은 저압 시스템에 연결된 활성 와이어와 PE 사이의 저압 기기 절연 및 서지보호장치 전반에 걸쳐 나타나는 전압이다. 다음과 같은 추가적인 기호는 저압 설비의 노출 도전부가 변전소의 접지 배열과 전기적으로 독립적 인 접지 배열에 연결되는 IT 시스템에 사용된다. /h 저압 설비에 고압 고장 및 첫 번째 고장이 발생한 기간 동안 저압 설비 기기의 노출 도전부 의 접지 배열을 통해 흐르는 고장 전류 /d 저압 시스템에서 첫 번째 고장이 발생하는 동안 저압 설비의 노출 도전부 접지 배열을 통해 흐르는 고장 전류 Z 저압 시스템과 접지 장치 사이의 임피던스(예를 들면 IMD 내부 임피던스, 인공 중성 임피던 스). 중성선 및 IT-델타 시스템이 없는 IT 시스템에서 기준 도체는 선도체다. E.4 고압 접지 고장 시 LV 시스템의 과전압 변전소의 HV 측에서 접지 고장이 발생할 경우 다음과 같은 유형의 과전압이 LV 설비에 영향을 줄 수 있다. 전력 주파수 고장 전압(U+) 전력 주파수 스트레스-전압(U+ 및 U2) 78 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
44e6f090-2e6b-4c58-9817-fa9fde51b619 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 기기 및 SPD 에 대해 가능한 전력 주파수 스트레스 전압은 표 E.1 에 나타낸다. 표 E.1 - KS C IEC 60364-4-44 에 따른 허용 전력 주파수 스트레스 전압 ¦ 고압 시스템의 접지 지속시간 t ¦ 저압 설비 기기의 허용 전력 주파수 스트레스 전압 U ¦ ¦ --- ¦ --- ¦ ¦ > 5 s ≤5 s ¦ U。 + 250 V U。 + 1200 V ¦ ¦ 중성선이 없는 시스템에서 U。는 선 대 선 전압이어야 한다. 비고 1 표의 첫 줄은 분리 시간이 긴 고압 시스템(예를 들면 절연 중성선 및 공진 접지된 고압 시 스템)에 관한 것이다. 두 번째 줄은 분리 시간이 짧은 고압 시스템, 예를 들어 저임피던스 접지된 고압 시스템에 관한 것이다. 두 줄 모두 일시적 전력 주파수 과전압과 관련하여 저 압 기기의 절연을 위한 관련 설계 기준이다(KS C IEC 60664-1 참조). 비고 2 중성선이 변전소의 접지 배열에 연결된 시스템에서 기기가 건물 외부에 있을 때 접지된 외 함에 있지 않은 절연체 전반에 걸쳐 이러한 일시적 전력 주파수 과전압이 예상된다. ¦ 중성선이 없는 시스템에서 U。는 선 대 선 전압이어야 한다. 비고 1 표의 첫 줄은 분리 시간이 긴 고압 시스템(예를 들면 절연 중성선 및 공진 접지된 고압 시 스템)에 관한 것이다. 두 번째 줄은 분리 시간이 짧은 고압 시스템, 예를 들어 저임피던스 접지된 고압 시스템에 관한 것이다. 두 줄 모두 일시적 전력 주파수 과전압과 관련하여 저 압 기기의 절연을 위한 관련 설계 기준이다(KS C IEC 60664-1 참조). 비고 2 중성선이 변전소의 접지 배열에 연결된 시스템에서 기기가 건물 외부에 있을 때 접지된 외 함에 있지 않은 절연체 전반에 걸쳐 이러한 일시적 전력 주파수 과전압이 예상된다. ¦ ![image](/image/placeholder) 변전소 LV 설치 HV LV L1 L2 L3 or Nor PEN Z /E RE RB RA Ut 그림 E.1 - 변전소 및 LV 설치의 가능한 접지 연결 및 고장 발생 시 과전압에 대한 대표적인 회로도 여기에서 별도의 고압 및 저압 접지 시스템이 서로 가깝게 존재하는 경우 현재 두 가지 방식이 사용 된다. TN/TT 시스템의 모든 고압(RE) 및 저압(RB) 접지 시스템의 상호 연결 IT 시스템의 모든 고압(RE) 및 저압(Z 및 RA) 접지 시스템의 상호 연결 TN/TT 시스템의 고압(RE) 및 저압(RB) 접지 시스템의 분리 IT 시스템에서 고압(RE) 및 저압(Z 및 RA) 접지 시스템의 분리 일반적으로 사용되는 방법은 상호 연결이다. 고압 및 저압 접지 시스템은 저압 시스템이 고압 접지 시스템에 의해 적용되는 영역 내에서 완전히 제한되는 경우 상호 연결되어야 한다(KS C IEC 61936-1 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 79 | {}
e4325392-a907-4426-9d44-f5c8d415005c | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 참조). 비고 시스템 접지 유형별 세부 정보(TN, TT, IT 는 KS C IEC 60364-1 에 나타낸다.) E.5 TT 시스템 예 - 가능한 일시적인 과전압의 계산 E.5.1 고압 시스템의 접지 고장으로 인하여 저압 설비에 발생할 수 있는 스트레스 ![image](/image/placeholder) HV LV Z ZLV L1 L2 L3 N ZN SPD SPD SPD SPD PE ZEHV RE (RB) RA 식별부호 P: HV 시스템; S:LV 시스템; T: 변압기; ZEHV: 고압 시스템의 접지 배열 임피던스(고압에서 중성점의 처리에 의존) ZLV, ZN: 선로 임피던스 및 중성선의 임피던스 그림 E.2 - LV-중간점 접지(접지된 중성선) RB 가 있는 변전소 RE 의 결합 접지를 갖춘 TT 시스템의 예 저압 측 변압기의 중성점이 접지된 경우 HV 시스템의 접지 고장은 LV 시스템의 전압에 영향을 미친 다(그림 E.2). 변압기의 두 중성점을 연결하는 공통 접지 도체가 존재하지 않는 경우 접지 고장(예를 들면 변압기의 부싱, 스파크 갭의 고장 또는 변압기 내부의 고장)은 LV 시스템의 중성점의 전압 상 승을 일으킨다. 임피던스 RE 을 통해 흐르는 HV 시스템의 접지 전류는 변압기의 중성점 전압 상승의 원인이 된다. 따라서 RE 값과 접지 전류 값이 LV 시스템에서 일시적 전력 주파수 과전압 값을 결정 한다. E.5.2 고압 시스템의 특성 E.5.2.1 접지 전류가 제한되는 고압 시스템 피터슨 코일로 HV 시스템을 접지함으로써 아크가 확실히 자체 소화되도록 전류를 /E = 50 A ~ 60 A 로 제한한다. 따라서 HV 시스템의 잔류 접지 임피던스는 ZEHV = 100 � ~ 500 � 범위에 있으며 접지 전류는 ZEHV 에 의해서만 결정된다. 단락 회로 전력과 접지 저항 RE (RB) 및 RA 는 눈에 띄는 영향을 미치지 않는다. 80 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
e2e89a64-6524-4b55-afe4-58a728bc8abd | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 접지 전류가 제한된 HV 시스템에서 공급되는 LV 시스템의 경우, 변전소에서 접지 배열의 임피던스 는 RE = 2.5 � ~ 5 � 범위에 있어야 한다. 접지 전류 /E = 50 A 에서 중성선과 접지 사이의 전압은 UTOV(HV) = 125 V ~ 250 V 까지 상승한다. TT 시스템에서 이러한 TOV 는 설치된 경우 절연 및 과전압 보 호 소자에 스트레스를 가한다. 중성선과 접지 사이에 설치된 과전압 보호 소자를 통해 UTOV(HV)가 구 동하는 최대 전류는 50 A 보다 확실히 작다. 따라서 중성선과 접지 사이의 스파크 갭은 작은 AC 전류 를 차단할 수 있어야 한다. 비고 일부 국가에서는 접지 저항 RE 가 10 �만큼 높을 수 있으므로 UTOV(HV) 값이 500 V 만큼 높은 경 우가 있다. E.5.2.2 중성점 접지 저항이 낮은 고압 시스템 완전한 지중 시스템의 경우 접지 전류 제한으로는 더 이상 접지 전류를 자체 소화시킬 수 없다(케이 블의 절연 고장으로 인해 절연체가 손상됨). 이러한 이유로 점점 더 많은 수의 HV 시스템이 중성점 접지 저항이 낮은 방향으로 작동한다. 일반적으로 접지 저항 ZEHV 는 접지 단락 전류 /E = 2 kA 를 제한 하는 것이 좋다. 정격 전압 Un = 20 KV 인 HV 시스템의 경우 접지 저항 ZEHV = 5 �이 이 요구사항을 충족시킨다. 소형 소내 변압기에는 값비싼 과전류 보호 기능이 없는 경우가 종종 있다. 따라서 퓨즈는 단락 전류를 차 단하는 데 사용된다. 차단 시간은 퓨즈 정격 전류에 따라 약 100 ms 정도다. 대표적인 20 KV 시스템에 다음 매개변수가 주어졌다고 가정한다. ZEHV = 5 요; Pshort circuit = 100 MVA; Un = 20 kV (L-L); 그리고 LV-시스템은 다음과 같은 특성을 가지고 있다. RE = 1 � Un = 230 V RA = 5 � ZLV = ZN = 150 m� RE 에서 UTOV(HV) = 1 200 V 의 TOV 가 발생한다. 중성선과 접지 사이에 설치된 과전압 보호 소자를 통해 흐르는 최대 전류는 RA 와 ZN 의 합에 대한 RE 의 비에 따라 달라진다. TT 시스템의 이 예에서는 전류 = 200 A 로 계산된다. E.6 다양한 LV 시스템 및 다양한 종류의 접지 구성에 따른 일시적 전력 주파수 과 전압 E.6.1 일반사항 고압 접지 고장 시 저압 시스템의 전력 주파수 스트레스 전압 및 전력 주파수 고장 전압이 표 E.2 에 나타낸다. 81 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
33e1e26e-2cd4-4968-84b7-8e87da931dcf | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 표 E.2 - 고압 접지 고장 시 저압 시스템의 전력 주파수 스트레스 전압 및 전력 주파수 고장 전압 ¦ 시스템 접지 형태 ¦ 접지 연결 형태 ¦ 첫 번째 LV 접 지 고장 위치 ¦ U1 ¦ U2 ¦ Uf ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ TT ¦ 구성 1 그림 E.4a: RE 및 RB 연결됨 RE= RB, 분리된 RA ¦ N.A. ¦ Uo ¦ RE x /E + Uo ¦ 0 ¦ ¦ TT ¦ 구성 2 그림 E.4b: RE 및 RB 분리됨 그리고 분리된 RA ¦ N.A ¦ RE x /E + Uo ¦ Uo ¦ 0 ¦ ¦ TN ¦ 구성 3 그림 E.3a: RE 및 RB 연결됨 RE = RB=RA ¦ N.A. ¦ Uo ¦ Uo ¦ RExIE ¦ ¦ TN ¦ 구성 4 그림 E.3b: RE 및 RB 분리됨 RB = RA ¦ N.A. ¦ RE x /E + U。 ¦ Uo ¦ 0 ¦ ¦ IT ¦ 구성 5 그림 E.6: ¦ LV 고장 없이 ¦ Uo ¦ RE x /E + UO***** ¦ 0 *** ¦ ¦ IT ¦ RE 및 Z 연결됨 ¦ 변압기 측 ¦ Uo xV3 * ¦ RE x /E + Uo x V3 ¦ 0 *** ¦ ¦ IT ¦ RE = RB 및 RA 분리됨 1 ¦ 소비자 측 ¦ RE x /E + Uo x V3 ¦ Uo xV3* ¦ x RE/ RA x /E Z*** ¦ ¦ IT ¦ 구성 6 그림 E.5: ¦ LV 고장 없이 ¦ U。 ¦ Uo ¦ RE x /E ¦ ¦ IT ¦ RE 및 Z 연결됨 RE = RB 및 RA 상호 연결됨 2 ¦ 변압기 측 ¦ * Uo xV3 ¦ Uo xV3 * ¦ REx /E ¦ ¦ IT ¦ RE 및 Z 연결됨 RE = RB 및 RA 상호 연결됨 2 ¦ 소비자 측 ¦ Uo xV3* ¦ Uo xV3 * ¦ RE x /E ¦ ¦ IT ¦ 구성 7 그림 E.7: ¦ LV 고장 없이 ¦ RE x /E + Uo **) ***) ¦ Uo ¦ 0 *** ¦ ¦ IT ¦ RE 및 Z 분리됨 RE 및 RA 분리됨 ¦ 변압기 측 ¦ Uo x V3 * ¦ RE x /E + Uo x V3 ¦ 0 *** ¦ ¦ IT ¦ RE 및 Z 분리됨 RE 및 RA 분리됨 ¦ 소비자 측 ¦ RE x /E + Uo x V3 ¦ Uo x V3 * ¦ RA x /E x RE/ Z*** ¦ ¦ 비고 1 IT 시스템의 경우 첫 하는 것으로 간주된다. 비고 2 ¦ 번째 LV 동시 고장은 변전소 LV 측 또는 소비자 측의 LV 설비에 존재 TT 및 TN 시스템에서 "연결됨" 및 "분리됨"이라는 문구는 RE 와 RB 간의 전기적 연결을 나 타낸다. IT 시스템의 경우 RE 와 Z 간의 전기적 연결과 RE 와 RA 간의 연결을 나타낸다. ¦ ¦ --- ¦ --- ¦ ¦ * ** ¦ SPD Uc 는 IT 시스템에서 사용하기 위해서는 선 대 선 전압과 같거나 더 높도록 선택해야 하기 때문에 고려할 필요가 없다. HV-접지 고장 조건에서는 최대 스트레스 전압이 나타날 수 있지만, 스트레스 전류는 임피던스 Z 에 의해 제한된다. ¦ ¦ *** ¦ SPD 가 양단에 설치된 경우, 한 위치에서 SPD 전압 제한 동작은 다른 위치에서 LV 설비의 SPD 에 대해 유사한 스트레스를 즉시 발생시킨다는 점을 고려해야 한다. IT LV 전력 시스템에서 대표적이고 선호되는 접지 배열 유형 산업용 IT LV 전력 시스템에서 대표적이고 선호되는 접지 배열 유형 ¦ E.6.2 결론 - SPD HV-TOV 모드에 대한 최악의 SPD 스트레스 전류. 변전소의 HV 측에서 접지 고장이 발생한 경우, 위 표에 따라 서로 다른 전력 시스템 및 다른 접지 배열로 접지(N-PE, L-PE)에 연결된 경우 다음 전류 값이 서지보호장치에 영향을 미칠 수 있다. 82 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
c4381c0d-7d57-4881-8b15-2dff6db4fbbd | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 IT 시스템의 경우: HV-접지(RE)와 LV-접지(RA) 사이가 분리되고 첫 번째 LV 접지 고장이 일어난 모든 시스템에서 최 대 300 A 이다. 첫 번째 LV 접지 고장이 발생한 경우에도 HV- 및 LV-접지 배열이 상호 연결된 IT 시스템에서 스 트레스 전압과 전류 스트레스가 나타나지 않는다. HV-접지와 LV-접지 사이가 분리되어 있는 IT 시스템에서는 첫 번째 LV 접지 고장이 없는 한 임 피던스 Z 에 의해 스트레스 전류가 제한되지만 이러한 이상적인 상황은 변압기 측에서 발생하든 소비자 측에서 발생하든 SPD 의 전력 제한 조치에 의해 영향을 받는다. LV 설비에서 HV-TOV 스 트레스 전류는 최대 300 A 까지 증가할 수 있다. TT 시스템의 경우: 최대 300 A 의 변압기 측에서만 HV-접지(RE)와 LV-접지(RB) 배열 사이가 분리된다. 최대 300 A 의 소비자 측에서만 HV-접지(RE)와 LV-접지(RB) 배열 사이가 연결된다. TN 시스템의 경우: - 최대 300 A 의 변압기 측에서만 HV-접지(RE)와 LV-접지(RB) 배열 사이가 분리된다. 스트레스 전압 및 전류 스트레스는 HV- 및 LV-접지 배열이 연결된(상호 연결) TN 시스템에 나타 나지 않는다. E.6.3 결론 - SPD 가 N-PE 및/또는 L-PE 사이의 접지에 연결된 경우 SPD HV-TOV 모드에 대한 최 악의 시험원: 구성 1,5, 7 의 경우: 1 200 V AC (N-PE); U。 + 1 200 V AC (L-PE)/300 Afor 200 ms (SPD 가 LV 소비자 측 에서 사용되는 경우 또는 알 수 없는 경우) 구성 2, 4 의 경우: 1 200 V AC (N-PE); U。 + 1 200 V AC (L-PE)/300 Afor 200 ms (SPD 가 LV 변압기 측에 서 사용되는 경우 또는 알 수 없는 경우) 구성 3, 6 의 경우: SPD 가 HV 및 LV-접지 배열이 상호 연결된 TN 및 IT 시스템에서만 사용되는 경우 에는 시험이 필요하지 않다. 비고 1 중성 도체가 없는 시스템에서 U。는 선 대 선 전압이다. SPD 는 제조자 설치 지침(KS C IEC 61643-11)에서 제공한 애플리케이션 및 시스템 구성에 대해 내력 모드 또는 안전한 고장 동작 시험에서 통과 해야 한다. SPD 의 선정 및 설치를 위해 합격 기준은 KS C IEC 60364-5-53 에 따라야 한다. 비고 2 제조자가 설치 지침에서 중성선과 PE 상부 RCD 사이의 TT 시스템에 설치되었다고 선언한 SPD 는 TOV 내력 모드 기준을 고려해야 한다. 여기에는 KS C IEC 60364-5-53:2001 의 534.2.3.3 에 설명된 애플리케이션이 포함된다. 83 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
e87906b4-41cc-4484-8c98-3e18388ad070 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 E.6.4 다양한 LV 시스템 및 가능한 접지 구성의 예 변전소 LV 설치 ![image](/image/placeholder) U2 U1 LV HV L1 L2 L3 PEN U1 = Uo Uf U2 = U1 = Uo IE RE U+ = REx /E TN - a U2 U1 LV HV L1 L2 L3 PEN Uf /E RB RE U1 = RE x 1E + Uo U2 = Uo U+ = 0 TN - b 그림 E.3 - TN 시스템(KS C IEC 60364-4-44:2018, 그림 44B) 84 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
18a03adc-825d-4034-8e7d-b94b04562351 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) LV 설치 변전소 U2 U1 LV HV L1 L2 L3 N U1 = Uo U2= RE x /E + Uo Uf U, = 0 RA /E RE TT- a U2 U1 LV HV L1 L2 L3 N Uf RA /E RB RE U1 = REx /E + U。 U2 = Uo Uf = 0 TT - b 그림 E.4 - TT 시스템(KS C IEC 60364-4-44:2018, 그림 44C) 85 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
1edc48a0-0c9e-4a02-83d0-89d46c9ad621 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) U2 U1 LV HV Z Uf U1 = U。 /E RE U2 = U1 = Uo U+= REx /E 1. LV 시스템에 고장이 없다. ![image](/image/placeholder) U2 U1 LV HV Z U1 = U。 V3 Uf IE RE U2 = U1 = U。 V3 U+= RExIE 2. LV 시스템에 첫 번째 고장이 있다. 그림 E.5 - IT 시스템, 예 a (KS C IEC 60364-4-44:2018, 그림 44D) 86 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
226edd47-7ae3-4490-8ee4-626f27a96a57 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) U2 U1 LV HV Z Uf U1 = Uo /E U2 = RE x IE + Uo RA RE Uf = 0 1. LV 시스템에 고장이 없다. U2 U1 LV HV Z U1 = Uo V3 Uf IE U2 = RE x /E + Uo V3 Id RA RE Uf = RA x Id S UL 2. LV 시스템에 첫 번째 고장이 있다. 그림 E.6 - IT 시스템, 예 b (KS C IEC 60364-4-44:2018, 그림 44F) 87 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
ae8f2bc9-0391-4bdf-82ec-796b5b1d76ee | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) U1 U2 LV HV U1 = RE x 1E + U。 Uf U2 = Uo IE RE Z RA U+=0 1. LV 시스템에 고장이 없다. ![image](/image/placeholder) U1 U2 HV LV U1 =RExIE+U0 V3 U2 = Uo V3 Uf U+= RA x ld⌀ UL IE ld RA RE Z 2. LV 시스템에 첫 번째 고장이 있다. 그림 E.7 - IT 시스템, 예 c1 (KS C IEC 60364-4-44:2018, 그림 44E) E.7 북미 TN C 시스템의 일시적인 과전압 값 그림 E.8 은 배전 변압기의 고압 측 고장에 대한 고장 전류 분배의 예다. 이 예에서는 변압기와 운전 인입구 모두의 접지 저항을 15 �이라고 가정한다. U1 = Uo 여기에서 Uo 는 이차적인 운전의 최대 사용 전압이다. ZL 는 변압기와 서비스 패널 사이의 선도체 임피던스다. 88 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
531dda3a-b98a-4d13-abde-9a538381a72a | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) U1 U2 변전소 LV 설치 HV LV L1 L2 L3 PEN ZL, 61 m lE3 0.2 le /E U1 = Uo IE2 0.2lE U2 = Uo + ZLx /E3 0.6lE Uf RE (RB) Uf = RAX /E3 IE1 RA 0.2lE TN - system 그림 E.8 - 북미 방식에 따른 배전용 변압기의 일차적 고장(4 선 MV 시스템 - 직접 접지)으로 인한 일시적 과전압 이 예의 목적에 맞는 대표적인 예는 최대 고장 전류(IE)가 10 kA 인 북미의 23 kV/13.2 kV Y 배전 선로 이다. 3 kVA ~ 25 kVA 단상 가공 배전 변압기를 3 상으로 설치할 때 쓰이기도 하는 3 중 2 차 도체의 일 반적인 임피던스(ZL)는 0.041 �이다. 계산하기 위해 약 60 m 의 4/0 AWG(IEC 60999-1 의 25 mm2 에 해 당) 구리를 사용하였다. 사고 전류의 분배에 대한 가정은 다중 접지 배전 회로에서 고장을 일으킨 상 황에서 측정된 값과 계산값을 토대로 하고 있다. ¦ 이러한 예로는 ¦ Uo = 132 v U1 = Uo = 132 v ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ + ¦ U2 = Uo 0.2 IE x ZL = 132 + 0.2 x ¦ x ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 214 v ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 10 000 x 0.04 = ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 이것은 공칭 시스템 전압의 1.78 배(1.78 p.u.)의 과전압을 나타내지만, RE >> RA 라고 가정하면 같은 상 황에서 U2 = 294 V 또는 공칭 시스템 전압의 2.45 배(2.45 p.u.)가 나올 수 있다는 것을 보여주고 있다. 이런 일시적 과전압(TOV)은 퓨즈 또는 상부 회로 차단기 또는 리클로저가 개방되어 고장이 제거될 때까지 지속된다. 이러한 장치의 동작에 걸리는 시간은 고장 분리 장치 특성에 따라 0.016 초에서 1.5 초에 이른다. 도체의 길이가 짧고 고장 전류가 적을 수록 상황은 좀 덜 심각해진다. 이 예에서는 1 차 쪽 고장이 공칭 시스템 전압의 단위당 최대 2.45 의 TOV 를 일으키는 것을 보여주지 만 이는 극히 드문 경우다. 배전 회로의 고장 전류가 실제로 10kA 가 된다는 것은 매우 드물다. 배전 회로의 대부분의 고장 전류는 4kA 미만이다. 따라서 TOV 는 크게 줄어들게 된다. 2 차 선로가 긴 것 은 일반적인 상황이 아니다. 선로 길이가 짧을 수록 과전압도 낮아진다. 일반적으로 2 차의 선로는 30 m 를 초과 하지 않는다. 따라서 고장 전류가 4 kA 이고 2 차 선로 길이가 30 m 미만이면 TOV 는 공칭 시 스템 전압 단위당 약 1.24 배, 즉 148.4 V 가 된다. E.8 설명과 함께 KS C IEC 61643-11 에 사용된 일시적 과전압 값 E.8.1 일반사항 시험 절차는 제조자가 제공한 설치 지침에 따라 저압 배전 시스템에 SPD 설치방법을 따른다. 89 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
944b0329-f02f-4f2d-94dd-abd12454bd64 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 IEC 60364 시리즈에 정의 된 시스템의 경우 전압 조절을 고려한 최대 시스템 전압은 표 E.4 에 제공되 고 그에 따른 TOV 값은 표 E.3 에 제공된다. 표 E.3 은 IEC 60364 에 따라 LV-시스템의 소비자 측에서 SPD 위치에 대한 최악의 시험 값을 제공한 다. HV-와 LV-소비자 측 사이의 접지 구성이 상호 연결된 IT LV 시스템에서는 HV-TOV 시험이 필요 하지 않다. 이러한 상호 연결된 IT 시스템에 대한 자세한 사항은 E.6 에 나타낸다. 표 E.3 - IEC 60364 시리즈를 준수하는 시스템에 대한 TOV 시험값 ¦ 애플리케이션 ¦ TOV 시험 매개변수 ¦ TOV 시험 매개변수 ¦ TOV 시험 매개변수 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ SPD 접속 ¦ tt=5s 의 경우 (소비자 설치의 LV 시스템 사고) ¦ t= 120 min 의 경우 (배전 시스템에서 LV 시스템 사고 및 중성선 단선) ¦ IT = 200 ms 의 경우 (HV 시스템 사고) ¦ ¦ SPD 접속 ¦ 내력 모드 필요 ¦ 내력 또는 안전 실패 모드 만족 ¦ 내력 또는 안전 실패 모드 만족 ¦ ¦ ¦ TOV 시험값 UT(V) ¦ TOV 시험값 UT(V) ¦ TOV 시험값 UT(V) ¦ ¦ TN-시스템 ¦ ¦ ¦ ¦ ¦ L-(PE)N 또는 L-N 접속 ¦ 1.32 x UREF ¦ V3 x UREF ¦ ¦ ¦ N-PE 접속 ¦ ¦ ¦ ¦ ¦ L-L 접속 ¦ ¦ ¦ ¦ ¦ TT-시스템 ¦ ¦ ¦ ¦ ¦ L-PE 접속 ¦ V3 x UREF ¦ 1.32 x UREF ¦ 1 200 + UREF ¦ ¦ L-N 접속 ¦ 1.32 x UREF ¦ V3 x UREF ¦ ¦ ¦ N-PE 접속 ¦ ¦ ¦ 1 200 ¦ ¦ L-L 접속 ¦ ¦ ¦ ¦ ¦ IT-시스템 ¦ ¦ ¦ ¦ ¦ L-PE 접속 ¦ ¦ ¦ 1 200 + UREF ¦ ¦ L-N 접속 ¦ 1.32 x UREF ¦ V3 x UREF ¦ ¦ ¦ N-PE 접속 ¦ ¦ ¦ 1 200 + UREF ¦ ¦ L-L 접속 ¦ ¦ ¦ ¦ ¦ UREF ¦ 시험 및 전력 시스템의 최고 조정 전압을 고려하기 위해 사용되는 기준 시험 전압(부속서 A 참조) ¦ ¦ --- ¦ --- ¦ ¦ U。 ¦ TN 및 TT 시스템: 접지에 대한 공칭 AC RMS 선 전압; IT 시스템: 선도체와 중성 도체 또는 적정한 중간점 사이의 공칭 AC 전압(KS C IEC 60364-4-44 의 442.1.2 참조) ¦ ¦ 1.32 x ¦ 전압 조정이 +10 %를 초과 하지 않는 경우 UREF 는 1.45 x U。와 같다(KS C IEC 60364-4-44 의 442.5 참조). ¦ ¦ 비고 ¦ 전압 조정 범위가 10 %를 초과 하는 국가는 UREF 만 이 표준에서 일반적으로 적용한다. 전압 조정에 대한 추가 정보는 IEC 60038 을 참조한다. ¦ 표 E.3 의 값은 KS C IEC 61643-11 에서의 요구대로 시험되고 선언되어야 하는 모든 SPD 에 적용된다. 표 E.1 에 주어진 조건과 다르며 아래에 주어진 특정 배전 시스템 요구사항과 다른 조건을 가진 특정 애플리케이션의 경우, 실제 네트워크 구성과 조건에 따라 제조자와 사용자 간의 합의 로 추가 TOV 시험 값 UT 와 시험 기간을 정의 해도 된다. 이러한 UT 값과 해당 지속 시간은 표 E.3 에 요청값을 추 가하여 SPD 데이터 시트에 선언해야 한다. 일부 국가에서는 다음과 같이 추가 TOV 시험 값과 시험 지속 기간이 필요하다(E.8.1 및 E.8.2 참조). 90 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b1aaf6c2-40cb-4cbd-bd19-a26fe1d285bc | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 표 E.4 - IEC 60364 시리즈를 준수하는 시스템에 대한 기준 시험 전압 값 ¦ 전력 배전 시스템 ¦ 전력 배전 시스템 ¦ AC 시스템 공칭 전압 L-PE / L-L V ¦ 배전 시스템 의 예상 조정 전압 max +(%) ¦ 기준 시험 전압 UREF (보호 모드에 따라) V ¦ 기준 시험 전압 UREF (보호 모드에 따라) V ¦ 기준 시험 전압 UREF (보호 모드에 따라) V ¦ 기준 시험 전압 UREF (보호 모드에 따라) V ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 전력 배전 시스템 ¦ 전력 배전 시스템 ¦ AC 시스템 공칭 전압 L-PE / L-L V ¦ 배전 시스템 의 예상 조정 전압 max +(%) ¦ L- N (PEN ¦ L - PE ¦ L-L ¦ N - PE ¦ ¦ PE 및 중성선 분산이 없는 3 상 TT- 시스템 ¦ 3 선 ¦ 230 / 400 ¦ 10 ¦ ¦ 255 ¦ 440 ¦ ¦ ¦ 중성선 분산이 있는 3 상 TT 시스템 ¦ 4 선 N ¦ 230 / 400 ¦ 10 ¦ 255 ¦ 255 ¦ 440 ¦ 255 ¦ ¦ PEN 분산이 있는 3 상 TN-C 시스템 ¦ 4 선 PEN ¦ 230 / 400 ¦ 10 ¦ 255 ¦ 255 ¦ 440 ¦ ¦ ¦ PE 및 중성선 분산이 있는 3 상 TN-S 시스템 ¦ 5 선 N PE ¦ 230 / 400 ¦ 10 ¦ 255 ¦ 255 ¦ 440 ¦ 255 ¦ ¦ PE 및 중성선 분산이 있는 3 상 TN-S 시스템 ¦ 5 선 N PE ¦ 240 / 415 ¦ 6 ¦ 255 ¦ 255 ¦ 440 ¦ 255 ¦ ¦ PE 및 중성선 분산이 있는 3 상 TN-S 시스템 ¦ 5 선 N PE ¦ 120 / 208 ¦ 10 ¦ 132 ¦ 132 ¦ 230 ¦ 132 a ¦ ¦ PE 및 중성선 분산이 있는 3 상 TN-S 시스템 ¦ 5 선 N PE ¦ / 480 277 ¦ 10 ¦ 305 ¦ 305 ¦ 530 ¦ 305 a ¦ ¦ 중성선 분산이 있는 3 상 IT 시스템 ¦ 4 선 N ¦ 230 / 400 ¦ 10 ¦ 255 ¦ 440 ¦ 440 ¦ 255 ¦ ¦ 중성선 분산이 없는 3 상 IT 시스템 ¦ 3 선 ¦ 230 ¦ 10 ¦ ¦ 255 ¦ 255 ¦ ¦ ¦ 단상 TN-S 시스템 ¦ 3 선 ¦ 230 ¦ 10 ¦ 255 ¦ 255 ¦ --- ¦ 255 ¦ ¦ 단상 TN-S 시스템 ¦ N PE ¦ 120 ¦ 10 ¦ 132 ¦ 132 ¦ ¦ 132 ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 91 | {}
f5647e7c-66e0-4d1c-b135-f615750392e4 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 표 E.4 - IEC 60364 시리즈를 준수하는 시스템에 대한 기준 시험 전압 값(계속) ¦ 전력 배전 시스템 ¦ 전력 배전 시스템 ¦ AC 시스템 공칭 전압 L-PE /L-L V ¦ 배전 시스템 의 예상 조정 전압 max +(%) ¦ 기준 시험 전압 UREF (보호 모드에 따라) V ¦ 기준 시험 전압 UREF (보호 모드에 따라) V ¦ 기준 시험 전압 UREF (보호 모드에 따라) V ¦ 기준 시험 전압 UREF (보호 모드에 따라) V ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 전력 배전 시스템 ¦ 전력 배전 시스템 ¦ AC 시스템 공칭 전압 L-PE /L-L V ¦ 배전 시스템 의 예상 조정 전압 max +(%) ¦ L-N (PEN ¦ L- PE ¦ L-L ¦ N-PE ¦ ¦ 3 상(델타) 코너 접지 TN 시스템 또는 TT 또는 IT 시스템 ¦ 3 선 or 3 선 + PE (G) ¦ 230 ¦ 10 ¦ --- ¦ 264 ¦ 264 ¦ --- ¦ ¦ 3 상(델타) 코너 접지 TN 시스템 또는 TT 또는 IT 시스템 ¦ ¦ 200 (202) ¦ 10 ¦ ¦ 222 ¦ 222 ¦ ¦ ¦ 3 상(델타) 코너 접지 TN 시스템 또는 TT 또는 IT 시스템 ¦ (델타) 코너 접지, 선택적 ¦ 460 ¦ 10 ¦ ¦ 528 ¦ 528 ¦ ¦ ¦ 3 상(델타) 중앙 탭 접지 TN 시스템 또는 TT 시스템 ¦ 3 선 + PEN ¦ 230 ¦ 10 ¦ 132 ¦ 264 ¦ 264 ¦ ¦ ¦ 3 상(델타) 중앙 탭 접지 TN 시스템 또는 TT 시스템 ¦ ¦ 200 (202) ¦ 10 ¦ --- ¦ 129 192 ¦ 222 ¦ ¦ ¦ 3 상(델타) 중앙 탭 접지 TN 시스템 또는 TT 시스템 ¦ PEN (델타) 센터 와인딩 그리드 ¦ 460 ¦ 10 ¦ ¦ 528 ¦ 528 ¦ ¦ ¦ 분산 TN 시스템 ¦ L N L PE ¦ 120 / 240 ¦ 10 ¦ 132 ¦ 132 ¦ 264 ¦ 132 ¦ ¦ 비고 특정 적용에 더 높은 전압 규정이 필요한 경우(예를 들면 +15 %), 제조자와 사용자 사이의 특별한 합의 에 따른다. ¦ 비고 특정 적용에 더 높은 전압 규정이 필요한 경우(예를 들면 +15 %), 제조자와 사용자 사이의 특별한 합의 에 따른다. ¦ 비고 특정 적용에 더 높은 전압 규정이 필요한 경우(예를 들면 +15 %), 제조자와 사용자 사이의 특별한 합의 에 따른다. ¦ 비고 특정 적용에 더 높은 전압 규정이 필요한 경우(예를 들면 +15 %), 제조자와 사용자 사이의 특별한 합의 에 따른다. ¦ 비고 특정 적용에 더 높은 전압 규정이 필요한 경우(예를 들면 +15 %), 제조자와 사용자 사이의 특별한 합의 에 따른다. ¦ 비고 특정 적용에 더 높은 전압 규정이 필요한 경우(예를 들면 +15 %), 제조자와 사용자 사이의 특별한 합의 에 따른다. ¦ 비고 특정 적용에 더 높은 전압 규정이 필요한 경우(예를 들면 +15 %), 제조자와 사용자 사이의 특별한 합의 에 따른다. ¦ 비고 특정 적용에 더 높은 전압 규정이 필요한 경우(예를 들면 +15 %), 제조자와 사용자 사이의 특별한 합의 에 따른다. ¦ a 이 값은 KS C IEC 61643-11:2011, 표 A.1(편집 수정)에서 수정되었다. E.8.2 미국 시스템의 일시적 과전압 값 미국의 경우, IEEE 1159 에 따라 표 E.5 에 네트워크 값이 나와 있다. 92 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
4ddc4282-78a6-487d-9fd0-9a835d610c6f | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 표 E.5 - 미국 시스템의 TOV 매개변수 ¦ IEEE 1159-2009 표 2 의 항목 번호 및 범주 ¦ 일반적인 최대 지 속 시간 S ¦ 일반적인 최대 RMS 전압 V ¦ 일반적인 피크 전압 V ¦ SPD TOV 내력- +5 % ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 2.0 단기 변화 - 2.1 즉각적- 2.1.2 순간전압상승 ¦ 0.5 ¦ 1.8*Uo ¦ 2.55*Uo ¦ 1.89 ¦ ¦ 2.0 단기 변화 - 2.2 순간적- 2.2.2 순간전압상승 ¦ 3.0 ¦ 1.4*Uo ¦ 1.98*Uo ¦ 1.47 ¦ ¦ 2.0 단기 변화 - 2.3 일시적- 2.3.3 순간전압상승 ¦ 60.0 ¦ 1.2*Uo ¦ 1.70*Uo ¦ 1.26 ¦ 그림 E.9 에서, 단위당(p.u.)은 U0 의 곱셈 계수다. 표 E.5 와 다른 형식으로 미국의 TOV 를 보여준다. Chart Type: bar 0. 1.0 10.0 100.0 item_01 1.8Volts (V) 1.6Volts (V) 1.4Volts (V) 1.2Volts (V) 그림 E.9 - 일반적인 TOV 최대 p.u. RMS 전압(V) 표 2, IEEE 1159-2009 그러나 미국에서 SPD 용 UL 1449 는 표 E.6 에 표시된 위의 값보다 더 많은 값을 요구한다. 비고 북미에서는 UL 1449 를 TOV SPD 시험에 적용한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 93 | {}
dd864241-174b-473d-8dd4-e19245c8c1a7 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 표 E.6 - 미국 시스템에서 SPD 를 시험하는 데 사용되는 UL TOV 값 ¦ 정격 전압 ¦ 상 ¦ 시험 전압 a ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 0 V ~ 109 V ¦ Single ¦ 2 배 정격 전압 ¦ ¦ 110 V ~ 219 V ¦ Single ¦ 240 ¦ ¦ 220 V ~ 229 V ¦ Single ¦ 380 ¦ ¦ 230 V ~ 239 V ¦ Single ¦ 400 ¦ ¦ 240 V ~ 345 V ¦ Single ¦ 480 ¦ ¦ 346 V ~ 399 V ¦ Single ¦ 600 ¦ ¦ 400 V ~ 499 V ¦ Single ¦ 690 ¦ ¦ 500 V ~ 1 000 V ¦ Single ¦ 최대 1 000 V 까지 2 배 정격 전압 ¦ ¦ 110 V ~ 120 V/220 V ~240 V ¦ Split ¦ 240 ¦ ¦ 120/208 V ¦ 3-WYE ¦ 208 ¦ ¦ 220/380 V ¦ 3-WYE ¦ 380 ¦ ¦ 230/400 V ¦ 3-WYE ¦ 400 ¦ ¦ 220 V ~ 240 V/380 V ~ 415 V ¦ 3-WYE ¦ 415 ¦ ¦ 240/415 V ¦ 3-WYE ¦ 415 ¦ ¦ 254 V ~ 277 V/440 V ~ 480 V ¦ 3-WYE ¦ 480 ¦ ¦ 346/600 V ¦ 3-WYE ¦ 600 ¦ ¦ 400/690 V ¦ 3-WYE ¦ 690 ¦ ¦ 120/240 V ¦ High leg delta ¦ 240 ¦ ¦ 240/480 V ¦ High leg delta ¦ 480 ¦ ¦ 240 V ¦ Delta ¦ C ¦ ¦ 480 V ¦ Delta ¦ C ¦ ¦ 600 V ¦ Delta ¦ b ¦ a 이 표에 규정되지 않은 장치 정격의 경우 시험 전압은 최대 상 전압(사용 가능한 경우) 또는 최 대 1 000 Vmax 까지 도체 쌍형 전압 정격의 2 배여야 한다. b 600 V 델타 정격 장치에 비정상적인 과전압 시험을 수행할 필요는 없지만 단락 시험은 수행하 여야 한다. C 단락 및 중간 전류 시험은 전체 상 전압에서 수행된다. E.8.3 일본 시스템의 일시적 과전압 값 일본 시스템의 공칭 전압과 기준 시험 전압은 표 E.7 에 나타낸다. 일본 시스템 TOV 시험 매개변수는 표 E.8 에 나타낸다. 94 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
ab0eecce-baa0-4367-934d-5a12e49fdc41 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 표 E.7 - 일본 시스템의 공칭 전압 및 기준 시험 전압 ¦ 전력 배전 시스템 ¦ 전력 배전 시스템 ¦ 전력 배전 시스템 ¦ 공칭 전압 V ¦ 공칭 전압 V ¦ 기준 시험 전압 UREF V ¦ 기준 시험 전압 UREF V ¦ 기준 시험 전압 UREF V ¦ 기준 시험 전압 UREF V ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 전력 배전 시스템 ¦ 전력 배전 시스템 ¦ 전력 배전 시스템 ¦ 공칭 전압 V ¦ 공칭 전압 V ¦ L-N ¦ L- PE ¦ L-L ¦ N - PE ¦ ¦ 단상 중간 탭 접지 100 / 200 V TT- 시스템(IT- 시스템) ¦ 단상 중간 탭 접지 100 / 200 V TT- 시스템(IT- 시스템) ¦ L1 N L2 ¦ L1-N L2-N ¦ 100 ¦ 110 ¦ 110 ¦ 220 ¦ 110 ¦ ¦ 단상 중간 탭 접지 100 / 200 V TT- 시스템(IT- 시스템) ¦ 단상 중간 탭 접지 100 / 200 V TT- 시스템(IT- 시스템) ¦ L1 N L2 ¦ L1-L2 ¦ 200 ¦ 110 ¦ 110 ¦ 220 ¦ 110 ¦ ¦ 단상 100 V TT- 시스템(IT- 시스템) ¦ 단상 100 V TT- 시스템(IT- 시스템) ¦ L1 N ¦ 100 ¦ 100 ¦ 110 ¦ 110 ¦ ¦ 110 ¦ ¦ 단상 200 V TT- 시스템(IT- 시스템) ¦ 단상 200 V TT- 시스템(IT- 시스템) ¦ ¦ 200 ¦ 200 ¦ 220 ¦ 220 ¦ - ¦ 220 ¦ ¦ 단상 중간 탭 접지 200 V TT- 시스템 ¦ 단상 중간 탭 접지 200 V TT- 시스템 ¦ L1 L2 ¦ 200 ¦ 200 ¦ - ¦ 110 ¦ 220 ¦ - ¦ ¦ 3 상(델타) 코너 접지 200 V TT- 시스템(IT- 시스템) ¦ 3 상(델타) 코너 접지 200 V TT- 시스템(IT- 시스템) ¦ L1 L2 N ¦ 200 ¦ 200 ¦ 220 ¦ 220 ¦ 220 ¦ 220 ¦ ¦ 단상 및 3 상 공유 ¦ 단상 L1, N, L2 ¦ N L2 L3 ¦ L1-N L2-N L1-L2 ¦ 100 200 ¦ 110 ¦ 110 ¦ 220 ¦ 110 ¦ ¦ 중앙 탭 접지 TT 시스템 ¦ 3 상 L1, L2,L3 ¦ N L2 L3 ¦ 200 ¦ 200 ¦ - ¦ 110 (L1) 110 (L2) 191 (L3) ¦ 220 ¦ 191 ¦ ¦ 중성선이 있는 3 상 100 / 173 V TT- 시스템 ¦ 중성선이 있는 3 상 100 / 173 V TT- 시스템 ¦ L1 L2 N L3 ¦ L1-N L2-N L3-N ¦ 100 ¦ 110 ¦ 110 ¦ 191 ¦ 110 ¦ ¦ 중성선 분산이 없는 3 상 400 V TT- 시스템 (IT- 시스템) ¦ 중성선 분산이 없는 3 상 400 V TT- 시스템 (IT- 시스템) ¦ L1 L2 L3 ¦ 400 ¦ 400 ¦ ¦ 255 ¦ 440 ¦ ¦ ¦ 중성선 분산이 있는 3 상 230 / 400 V TT- 시스템 (IT- 시스템) ¦ 중성선 분산이 있는 3 상 230 / 400 V TT- 시스템 (IT- 시스템) ¦ L1 L2 N L3 ¦ 400 ¦ 400 ¦ 255 ¦ 255 ¦ 440 ¦ 255 ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 95 | {}
d14a135a-22ea-4a6a-998f-0361f7dea869 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 표 E.8 - 일본 시스템에 대한 TOV 시험 매개변수 ¦ 애플리케이션 ¦ TOV 시험 매개변수 ¦ TOV 시험 매개변수 ¦ TOV 시험 매개변수 ¦ TOV 시험 매개변수 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ SPD 접속 ¦ For tT = 120 min (배전 시스템의 LV 시스템 사고 및 중성선 단선) ¦ For tT = 120 min (배전 시스템의 LV 시스템 사고 및 중성선 단선) ¦ For IT = 1 s (HV- 시스템 사고) ¦ For IT = 1 s (HV- 시스템 사고) ¦ ¦ SPD 접속 ¦ 내력 또는 안전 실패 모드 만족 ¦ 내력 또는 안전 실패 모드 만족 ¦ 내력 또는 안전 실패 모드 만족 ¦ 내력 또는 안전 실패 모드 만족 ¦ ¦ ¦ TOV 시험값 UT V ¦ 예상 단락 전류 A ¦ TOV 시험값 UT V ¦ 예상 단락 전류 A ¦ ¦ AC 시스템 공칭 전압 100 V ¦ ¦ ¦ ¦ ¦ ¦ L-PE 접속 ¦ 330 ¦ 20 ¦ 710 ¦ 30 ¦ ¦ L-N 접속 ¦ 330 ¦ 20 ¦ ¦ ¦ ¦ N-PE 접속 ¦ ¦ ¦ 600 ¦ 30 ¦ ¦ L-L 접속 ¦ ¦ ¦ ¦ ¦ ¦ AC 시스템 공칭 전압 200 V ¦ ¦ ¦ ¦ ¦ ¦ L-PE 접속 ¦ 330 ¦ 20 ¦ 820 ¦ 30 ¦ ¦ L-N 접속 ¦ 330 ¦ 20 ¦ ¦ ¦ ¦ N-PE 접속 ¦ ¦ ¦ 600 ¦ 30 ¦ ¦ L-L 접속 ¦ ¦ ¦ ¦ ¦ ¦ AC 시스템 공칭 전압 400 V ¦ ¦ ¦ ¦ ¦ ¦ L-PE 접속 ¦ 440 ¦ 20 ¦ 855 ¦ 300 ¦ ¦ L-N 접속 ¦ 440 ¦ 20 ¦ ¦ ¦ ¦ N-PE 접속 ¦ ¦ ¦ 600 ¦ 300 ¦ ¦ L-L 접속 ¦ ¦ ¦ ¦ ¦ ¦ 비고 이러한 값은 전기 설비에 대하여 장관 법령에 의거한 기술 표준에 의해 요구된 수치이다. ¦ 비고 이러한 값은 전기 설비에 대하여 장관 법령에 의거한 기술 표준에 의해 요구된 수치이다. ¦ 비고 이러한 값은 전기 설비에 대하여 장관 법령에 의거한 기술 표준에 의해 요구된 수치이다. ¦ 비고 이러한 값은 전기 설비에 대하여 장관 법령에 의거한 기술 표준에 의해 요구된 수치이다. ¦ 비고 이러한 값은 전기 설비에 대하여 장관 법령에 의거한 기술 표준에 의해 요구된 수치이다. ¦ 일본의 저압 시스템 사고에 의한 TOV 전압 UT 는 다음과 같다. 그림 E.11 은 일본의 저압 시스템의 사고에 의한 특정 TOV 전압값을 보여준다. 일본에서는 단상 중 간 탭 접지 100/200 V 시스템과 3 상(델타) 코너 접지 200 V 시스템의 접지를 공유하는 경우가 많다. 이 경우, 예를 들어, 3 상(델타) 코너 접지 200 V 시스템 중 한 선로가 접지 고장(그림 E.10 의 접지 고 장 지점(d))일 때, 단상 중간 탭 접지 100/200V 시스템(그림 E.10 의 t)과 PE 사이의 전압은 300 V AC 다. 이와 유사한 방법으로, 100/200 V 접지 시스템의 한 선로가 접지 고장인 경우(그림 E.10 의 접지 고장 지점(a)), 3 상(델타) 코너 접지 200 V 시스템(그림 E.10 의 u)과 PE 사이의 전압은 300 V AC 다 표 E.7 의 공칭 전압 100 V, 200 V 에서 TOV 전압 330 V 는 표 E.8 의 300 V 에 배전 시스템 최대 10 %의 예상 조정 전압을 추가하여 얻은 값이다. 96 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
672ac9a4-4cbe-4930-bed6-d49d7e2cee84 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) u iu (d) IW v W W V 도(C ) IV iv W S 6 (b) N t 6 (a ) Chart Type: line u(d) c(d) item_01 173 200 그림 E.10 - 단상 중간 탭 접지 100/200 V 시스템 및 3 상(델타) 코너 접지 200V 시스템의 접지 공유 예 표 E.9 - 다른 접지의 고장 지점에서 TOV 전압 최댓값 ¦ 접지 고장 지점 ¦ 3 상(Delta) 코너 접지 200 V ¦ 3 상(Delta) 코너 접지 200 V ¦ 3 상(Delta) 코너 접지 200 V ¦ 단상 중간 탭 접지 100/200 V ¦ 단상 중간 탭 접지 100/200 V ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 접지 고장 지점 ¦ u ¦ V ¦ W ¦ s ¦ t ¦ ¦ (a) ¦ 300 V ¦ 265 V ¦ 100 V ¦ 200 V ¦ 0V ¦ ¦ (b) ¦ 100 V ¦ 173 V ¦ 100 V ¦ 0V ¦ 200 V ¦ ¦ (c) ¦ 200 V ¦ 0V ¦ 200 V ¦ 173 V ¦ 265 V ¦ ¦ (d) ¦ 0V ¦ 200 V ¦ 200 V ¦ 100 V ¦ 300 V ¦ 일본의 고압 시스템에서 고장에 의한 TOV 는 접지 고장과 전력 시스템 고장(고압 시스템과 저압 시 스템 간의 사고)으로 인해 발생한다. 이 경우 TOV(접지 고장 전류 또는 전력 시스템 고장 전류)로 인한 전류는 다음과 같다. 모든 100 V AC 및 200 V AC 배전 시스템은 일본의 6.6 kV 고압 비접지 시스템에서 공급된다. 따라서 고압 시스템의 고장 시 TOV 로 인한 전류는 6.6 kV 고압선과 접지 사이의 커패시턴스를 통해 흐른다. 그러면 고압 시스템의 고장 시 TOV 에 의해 발생하는 전류는 일본의 100 V AC 및 200 V AC 배전 시 스템에서 최대 30 A 다. 400 V AC 배전 시스템의 90 %는 일본의 6.6 kV 고압 비접지 시스템에서 공급된다. 그러나 400 V AC 배전 시스템의 10 %는 6.6 kV 를 초과 하는 고압 접지 시스템에서 공급된다. 이는 유럽(IEC) 시스템과 동일하다. 따라서 고압 시스템의 고장 시 TOV 로 인해 발생하는 전류는 일본의 400 V AC 배전 시스 템에서 300 A(KS C IEC 61643-11:2011, 8.3.8.2 와 동일)다. 그림 E.11 는 일본의 단상 중간 탭 접지 100/200 V 시스템의 일반적인 배전 네트워크를 보여준다. 그림 E.12 는 일본의 일반적인 전력 시스템 구성을 나타낸다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 97 | {}
1c37c179-e2fb-48a1-93a3-ba0988400568 | KSCIEC61643-12_KR | KS CIEC 61643-12:2020 Chart Type: line 시스 접지 A 등급 시스템 접지 B 등급 item_01 6.6kV 6.6kV 200kV 100kV 그림 E.11 - 일본 100/200 V 접지 단상 중간 탭 접지의 일반적인 전력 배전 네트워크 일본 규정에 따른 접지 전극에 대한 4 가지 등급은 표 E.10 에 나타낸다. 표 E.10 - 접지 전극 등급 및 접지 저항의 최댓값 ¦ 등급 ¦ 접지 저항의 최댓값 요 ¦ 참조 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ A ¦ 10 ¦ 고압 적용 기기 ¦ ¦ B ¦ 150// ¦ 접지 고장 및 전력 시스템 고장으로부터 보호 ¦ ¦ C ¦ 10 ¦ 300 V AC 이상에서 사용되는 기기의 애플리케이션 ¦ ¦ D ¦ 100 ¦ 300 V AC 이하에서 사용되는 기기의 애플리케이션 ¦ B 등급 시스템 접지(R)의 최대 접지 저항값은 표 E.10 에 있는 일본 규정에서 다음 공식으로 계산하여 결정하여야 한다. R = 150/I B 등급 접지 전극의 전위가 150 V 이상 증가하면 진공 차단기는 그림 E.13 에 있는 시간-전류 특성 내 에서 차단되어야 한다. 98 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
a0ccca09-9eb8-41a0-84be-933629622775 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) 배전 변압기 누설 전류 감지기 66 kV 6.6kV 배전선 전력 C C C 시스템 진공 차단기 고장 주상 변압기 저압 배전선 / 시스템 소비자 접지 B 등급 / TOV 로 인한 전류 C 선과 접지 사이의 표류 정전용량 그림 E.12 - 일본의 일반적인 전력 시스템 구성 Chart Type: line 1 2 t item_01 600Volts (V) 300Volts (V) 150Volts (V) 그림 E.13 - 일본의 고압 시스템 고장에 의한 TOV 특성 99 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
cad7a940-315a-4aa8-ab56-3d873e17233d | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 부속서 F (참고) 협조 규칙과 원칙 F.1 일반사항 7.2.7 에서 설명된 대로 SPD 사이의 협조는 에너지 및 전압 보호 레벨 조정을 모두 만족하기 위해 취해진다. F.2 에너지 협조 F.2.1 일반사항 에너지 협조는 두 번째 SPD 의 최대 에너지 내력에 기초한다. 그러나 이 에너지는 때때로 KS C IEC 61643-11 에 설명된 대로 파형과 시험에 따라 달라진다. 일반적으로 하나의 파형으로만 협조를 한다 (예를 들면 II 등급 시험의 경우 8/20). 이러한 이유로 직접 값 Emax 를 제조자로부터 받는 것이 더 좋 고 쉽다(대부분 기술 설명서에 인쇄된다). SPD 의 에너지 내력을 만족스럽게 구하려면 두 가지 값이 필요하다. 짧은 파형인 경우 Emax S, 예를 들어 8/20(II 등급 시험) - 긴 파형인 경우 Emax L, 예를 들어 10/350(I 등급 시험) 두 파형 Emaxs 와 EmaxL 의 값은 특정기술에서 같을 수도 있다. SPD 는 짧은 파형(II 등급 시험에 사용됨)의 경우 /n, 긴 파형(1 등급 시험에 사용됨)의 경우 /imp 의 두 전 류에 의해 특징 지어지며, 이는 Emax s 와 EmaxL 에 대한 에너지 내력과 관련이 있다. 제조자가 Imax 를 선언한 경우 해당 값을 Emax s 에 대해 고려해야 한다. 관련 서지 파형에 맞는 최대 에너지 내력 Emax 를 이용하여 SPD 1 과 2 를 협조할 필요가 있다. 즉, 다 음 두 가지 경우를 다루어야 한다. · 긴 파형에서의 협조 · 짧은 파형에서의 협조 일반적으로 협조는 짧은 파형에서 달성하기가 쉽다. 스위치형 SPD 의 경우, 파두장이 긴 파형을 다룰 필요가 있다. 이 문제는 IEC 에서 고려 중이다. F.2.2 분석적 연구: 2 개의 금속 산화 배리스타(MOV) 기반 SPD 의 협조의 간단한 예 F.2.2.1 일반사항 다음 고려사항은 Ures(1) 곡선이 알려진 I 등급과 II 등급 시험된 1 포트 제한 SPD 에만 적용된다. 이 곡 100 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c63e21c1-c323-4fc5-a25e-6f9179c905a0 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 선은 8/20 파형을 사용하여 측정되며, 제조자가 SPD 기술 문서에 제공한다. 3 등급 2 포트 SPD 는 특 별한 주의 가 필요하다(고려 중임). 아래의 예는 협조 문제의 이해를 돕기 위한 것이다. 먼저 금속 산화 배리스터(MOV)로 만들어진 SPD 1 과 2 로 구성된 경우를 다루는데, 여기에서는 분석적 연구가 가능하다. 이러한 분석적 연구는 전류의 분배에 기초한다는 점에 유의 해야 한다. 에너지 기준을 확실히 충족시키기 위해 일반적으로 는 다루기 힘든 부가적인 계산이 필요할 수도 있다. · 2 개의 배리스터가 지름은 같지만(그로 인하여 공칭 방전 전류 In 이 같고 에너지 내력도 같다. 선언 된 경우 동일한 Imax 와 동일한 /imp) 전압 보호 레벨 Up1 과 Up2 가 다른(두께가 다른) 경우, 다음과 같 은 식을 갖는다. Inl = In2 Imaxl = Imax2 (선언된 경우) Iimpl = Iimp2 이때 가능한 곡선 Ures(I)가 그림 F.1 에 그려져 있다. Chart Type: line 1 mA Limp In Max item_01 1Inches (In) 2Inches (In) 2.5Inches (In) 5Inches (In) 그림 F.1 - 공칭 방전 전류가 같은 2 개의 금속 산화 배리스터(MOV) Up1 > Up2 인 경우에, 곡선 a)는 SPD 1 에 대응하고 곡선 b)는 SPD 2 에 대응한다. ¦> 몇 미터(일반적으로 5m 와 10m 사이)인 경우 일반적으로 짧은 파형에서는 이 협조가 받아들여질 수 있다. 긴 파형의 경우 역결합 효과 가 줄어든다. 따라서 SPD 2 는 전체 입력 서지 i 를 견딜 수 있어야 한다. SPD 2 는 SPD 1 과 동일한 설계를 가지고 있기 때문에 전체 스트레스를 견딜 수 있다. Up1 < Up2 인 경우 곡선 a 는 SPD 2 에 대응하고 곡선 b 는 SPD 1 에 대응한다. 따라서 대부분의 전류는 SPD 1 에 흐른다. 이 경우 SPD 2 에 흐르는 전류는 침입한 전류보다 작다. 두 SPD 의 전류 용량이 같으므로 두 경우 모두 에너지 분배 기준을 만족한다. 이 첫 번째 경우는 동일한 에너지 내력을 가진 SPD 를 두 개 사용해도 얻을 것이 거의 없다는 것을 설명하기 위한 것이다. · 두 배리스터의 공칭 방전 전류가 다르다면 101 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
aca59490-d2de-452d-853f-f70844c0d406 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 이런 응용의 실질적인 예는 In1> In2 이고 Emax1 > Emax2 인 경우이다. 또한, SPD 1 및 SPD 2 는 Ures1(In1) < Ures2 (In1)와 같은 특성을 가질 수 있다. 이 Ures (1) 곡선은 그림 F.2 에 나타낸다. 분석적 연구에서 임 피던스를 다루는 것이 쉽지 않기 때문에 이 그림에는 임피던스가 나타나지 않는다. 짧은 파형인 경 우 대부분의 전류가 첫 번째 SPD 로 흘러서 협조가 잘 이루어지는 것을 그림 F.2 에서 알 수 있다. 그 러나 긴 파형의 경우 적당한 협조 방법을 결정하기가 어렵다. 긴 파형에 전류의 크기가 두 곡선의 교차점(그림 F.2 참조)의 전류값보다 낮을 때에는 협조가 이루어지지 않을 수 있다. 전류가 이런 범 위일 때 Ures2 곡선이 Ures1 보다 낮으면 유입 전류의 대부분이 SPD2 로 흘러 들어간다. 따라서 두 SPD 사이에 인덕턴스가 필요하다. 결국 제조자의 기술 문서에 주어진 Ures1(In1)과 Ures2(In2)(각각 Up1 및 Up2)를 단순 비교하는 대신 곡선 Ures(i)를 I 와 0.1 x /n2 에서 최대 /n1 또는 /max1(선언된 경우)까지 비교하여 서로 교차하는지 확인할 필요 가 있다. 이 교차점 /cr (있는 경우)의 전류는 가능한 한 낮은 것이 좋다. 이 경우에 에너지 배분 기준은 충족될 가능성이 매우 높으며, Icr 이 낮으면 낮을 수록 성공 가능성이 더욱 높아진다. 의문의 여지가 남아 있으면, 두 번째 SPD 에 흐르는 에너지를 계산하기 위해서 SPD 사이의 임피던스와 긴 파형을 고려해야 한다. 그러한 계산을 분석적으로 수행하는 것은 쉽지 않다. 정보의 부족으로 이런 곡선을 구할 수 없거나 간단하고 빠른 결과 가 필요할 때에는 동일한 수준의 Ures1 및 Ures2 곡선을 비교할 필요가 있다. 이러한 경우 협조가 쉽게 잘 이루어질 수 있는 조건은 Ures1 (/n2) < Ures2 (In2)이다. 이 보존 곡선(그림 F.2 참조)은 이러한 경우를 만족한다. 그러나 당연하게도 이러한 배리스터를 사용하면 불필요한 여유가 들어가게 된다. 또한 이 배리스터는 일시적 과전압과 같이 네트워크에서 나타나는 스트레스를 견뎌야 하는 문제가 생길 수도 있다. 이 경우 두 번째 SPD 의 전류가 낮더라도 긴 파형 서지에 대하여 에너지 기준을 충족시키지 못할 수 도 있다. 두 번째 SPD 로 들어가는 에너지에 대한 추가 계산이 필요할 수도 있다. 또한 장치의 보호 가 계속 이루어지는지 확인할 필요가 있다(SPD2 의 낮은 전류가 배리스터의 비직진성으로 인해 고압 을 유발할 수 있음). Chart Type: line Impf Ier Impf2 Imax item_01 2.5 3.5 5 6.5 식별부호 a SPD2 에 대응하는 곡선 b SPD1 에 대응하는 곡선(SPD2 의 곡선과 교차하는 곡선) C SPD1 에 대응하는 보존 곡선(SPD2 의 곡선과 교차하지 않는 곡선) d 긴 파형의 서지 전류 범위 e 짧은 파형의 서지 전류 범위 그림 F.2 - 공칭 방전 전류가 다른 2 개의 금속 산화 배리스터(MOV) 102 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c224d8de-bf62-4c0a-8aee-3df93a245e1d | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 F.2.2.2 결론 두 개의 금속 산화 배리스터(MOV)가 협조해야 되는 모든 경우에 다음 5 단계 절차를 따라야 한다. a) 어느 하나의 SPD 가 없을 때 발생할 것으로 예상되는 과전압을 확인하고 긴 파형과 짧은 파형을 구분한다. b) 이 스트레스를 견딜 수 있는 SPD1 을 선택한다. a) 단계의 정보가 없다면, 충분한 용량의 SPD 를 허용하고(위험 분석 참조) 제조자로부터 /n1, Imax1 (선언된 경우) 및 /imp1 값을 구한다. 그런 다음 a)에 서 주어진 데이터와 함께 이러한 값을 고려한다. c) 필요한 보호 특성에 맞추어 SPD2 를 선택한다. d) 0.1 x In2 에서 /n1 또는 Imax1(선언된 경우)에 이르는 곡선 Ures(1)를 비교한다. 그런 다음 교차점 Icr 을 결정한다. 이 전류 Icr 이 충분히 낮다면(일반적으로 0.1 x /n2) 두 번째 SPD 의 에너지를 계산할 필 요가 없다. 에너지 기준은 SPD 사이의 거리에 관계없이 충족된다. 의심의 여지가 있으면 SPD 간 의 임피던스를 고려하여 두 번째 SPD 의 에너지를 계산하고 에너지 기준을 확인한다. 이러한 곡선 을 구할 수 없다면, 다음과 같은 간단한 조건을 가지고 SPD 2 를 선택한다. SPD2 의 공칭 방전 전류가 동일한 경우: Ures1 (In)<Ures2(In). SPD2 의 공칭 방전 전류가 더 작은 경우: Ures1 (/n2) < Ures2 (/n2). 에너지 기준을 확인하기 위하여, 그리고 보호가 여전히 이루어지고 있는지를 확인하기 위해서는 SPD2 의 에너지를 계산하는 것이 바람직하다. e) c) 단계에서 만족스러운 결과 를 얻을 때까지 반복한다. 비고 1 매우 낮은 전류에서의 전압(일반적으로 기준 전압이라고 함)은 협조에 적용되지 않는다. 비고 2 어떤 경우에도(MOV(금속 산화 배리스터) 유무에 관계없이) EMC(전자파 적합성)를 고려할 때 에는 SPD2 에 흘러 들어간 전류가 가능한 한 작아야 한다. 비고 3 곡선 Ures(I)는 최댓값이다. 제조상의 오차로 인하여 특성이 다양한 값을 가진다는 것을 고려 하여야 한다. 비고 4 이전 연구는 2 개 이상의 SPD 에 대하여 일반화될 수 있다. F.2.3 분석적 연구: 갭 기반 SPD 와 금속 산화 배리스터(MOV) 기반 SPD 사이의 협조 예 F.2.3.1 일반사항 일반적으로 사용되는 또 다른 예는 SPD1 로는 갭을, SPD2 로는 금속 산화 배리스터(MOV)를 사용하는 것이다. 그림 F.3 에서, SPD2 에 작용하는 스트레스가 너무 커지기 전에 스파크가 발생하면 협조가 이 루어지는 것이다. 이 스파크가 일어나기 전에 다음과 같이 된다. U1 = Ures2(i)+L x di/dt 일반적으로 Ures2 (i)의 값이 알려져 있지 않으므로 다음 공식을 사용하여 대강의 값을 구한다. 103 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
31249db9-6f6b-41c1-af2a-23d8255811cb | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 U1 = Vv2(i) + L X di/dt 여기에서 Vv2 는 금속 산화 배리스타(MOV) 2 의 기준 전압이다. 이 기준 전압은 배리스터의 특성을 결 정하는 요소이며 U-i 특성의 꺾이는 지점에 매우 가깝다. U1 이 갭(이 부속서에서 Udyn 이라고 함)의 동적 스파크오버 전압을 초과 하자마자 협조가 이루어진다. 그 전류의 작은 일부만이 두 번째 SPD 로 흐른다. 협조는 금속 산화 배리스터(MOV)(SPD2)의 특성, 캡(SPD 1)의 동적 스파크오버 전압, 입력 서지의 상승률과 절대값 i, SPD 사이의 거리 d 에 따라 달라 진다(이 경우 R 이 무시되므로 임피던스 Z 의 일부인 인덕턴스 L 이 사용된다). F.2.3.2 갭과 배리스터 사이의 결합 방지 인덕턴스에 필요한 값의 계산 예 예를 들어, 현대의 무선 통신 기지국과 같이 물리적 공간의 제약으로 인하여 하부에 있는 MOV 기반 SPD 가 과도 전압의 수준을 상부에 있는 갭 기반 SPD 의 트리거 전압보다 훨씬 아래로 제한할 수도 있다. 이렇게 하면 갭의 동작을 방해하고 모든 입력 에너지가 MOV 기반 SPD 로 흘러가도록 한다. 넓은 공간에서 SPD 사이의 케이블 연결 거리가 더 길어지고 따라서 스파크 갭이 동작하기에 충분한 인덕턴스를 제공해 줄 수도 있다. 들어온 과도 전류가 병렬 경로를 통하여 분산되어 갭이 방전을 일으키기에는 불충분한 전압이 될 가 능성은 언제나 있다. 이런 경우에 하부에 있는 SPD 는 자체적으로 총 에너지를 흡수하기에 충분한 정격을 가져야 하다. 에너지 수준이 높을 때 스파크 갭이 동작하지 않으면 과도한 에너지가 하부 SPD 로 흐르게 되어 SPD 가 파괴된다. 하부 SPD 의 한계를 초과 하는 모든 에너지 수준에 대해 갭의 동작을 보장할 수 있 도록 충분한 직렬 결합 방지 임피던스를 삽입하여 협조를 이룰 수 있다. 협조를 보장하는 데 필요한 인덕턴스 값은 간단하게 계산할 수 있다. 첫째, 갭의 매개변수를 알아야 한다. 스파크 갭은 일반적으로 4kV 미만에서 200 ns 이내에 트리거된다. 둘째, 하부 SPD 매개변수를 알아야 한다. 배리스터 전압 1 mA 가 430 V +/-10 %이고 정격이 275 V AC 인 일반적인 기기는 약 800 V 에서 제한을 시작한다. 8/20 파형을 사용하는 II 등급 시험에 따를 때 h 이 10 kA ~ 20 kA 정도이다. 그러나 갭의 정격은 10 smi ~ 350 us 또는 이에 상응하는 구형파 임펄스의 I 등급 시험에 따라 표시된다 는 사실을 기억해야 한다. 이 등급의 임펄스에 따른 추가 에너지를 감당하기 위하여 하부 SPD 의 피 크 전류를 줄여야 한다. 이 저감 계수는 10 : 1 로 가정한다. 따라서 피크 전류 정격(10/350 smi 파동)은 예를 들어 12.5 kA 에서 1.25 kA 로 줄어든다. 상승 시간이 10 us 라면 di/dt 는 125 A/�s 가 된다. 갭의 확실한 동작을 보장하기 위하여 필요한 인덕턴스는 다음 식으로 계산할 수 있다. U=L x di/dt+Ix R 여기에서 U : 스파크 갭 트리거 전압 di/dt : 입력 임펄스의 상승 비율 Ix R : 하부 SPD 에 걸리는 전압 강하(R 은 비선형 값임) 이 경우에 104 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
1743abf9-53c2-4c9d-a2e0-69ae7b1ae6e6 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 U-IxR L= di/dt 갭이 200 ns 이내에 트리거한다고 가정하면 하부 SPD 에 흘러 들어가는 전류는 다음과 같다. I= 0.2/10 x 1 250 A = 25 A 전압 /x R 은 600 V 정도 된다. 따라서 4000-600 L= 125x106 즉, L = 27.2 �H 이 인덕턴스는 단일 집중값으로 기리 1 미터당 1 �H 의 인덕턴스를 가지는 케이블 27.2m 이거나 작은 인덕터와 케이블의 조합일 수 있다. ![image](/image/placeholder) L 2 1 U1 U2 식별부호 L 인덕턴스 그림 F.3 - 갭 기반 SPD 와 금속 산화 배리스터(MOV) 기반 SPD 의 협조 예 이 예를 사용하면, 이러 협조를 설계하는 데 필요한 일반적인 조건을 얻을 수 있다. F.2.3.3 결론 갭으로 된 SPD 1 이 선정되면, 다음 조건들을 만족시키는 SPD 2 를 선정할 필요가 있다. I 등급의 시험 파형에 맞는 입력 서지: Udyn < VV2 + L x /imp2/10 II 등급의 시험 파형에 맞는 입력 서지: Udyn < VV2 + L x /n2/8 (또는 /max2 선언된 경우) 이런 규칙은 어림의 결과 를 도출한다. 어쩔 수 없이 L 값이 작을 때, 협조가 이루어지는가를 확인하 기 위해서는 컴퓨터 시뮬레이션이 필요하다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. 105 | {}
9d2c42f4-58e2-483d-9231-3abd415720fe | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 비고 다른 경우에는 어 나쁜 결과 가 도출될 수도 있는데, 특히 지금 고려 중인 파두가 긴 파형을 사 용할 때 그렇다. IEC TC81 은 현재 더 긴 파두장 100 �s 를 검토 중이다. F.2.4 분석적 연구: 두 SPD 의 일반적인 협조 2 개의 배리스터, 즉 갭-금속 산화 배리스터(MOV) 방식의 경우에 대한 연구는 협조 문제의 복잡성을 분명히 보여준다. u 대 i 곡선이 거의 알려져 있지 않고 실제로는 허용값이 상당히 크기 때문에, 이 분석적 연구는 단지 간단한 경우에만 적용된다. SPD2 에 흘러 든 에너지를 계산해야 될 경우, 시뮬레 이션을 실시하는 것이 더 쉽다. 이러한 분석적 연구의 주요 관심은 사용자에게 이 현상에 대한 보다 나은 이해를 제공하는 데 있다. SPD 기술이 무엇이든 위에 주어진 일반적 원칙과 특히 에너지 기준은 여전히 응용할 수 있는 것이다. 응용 가능한 협조를 달성하기 위해서는 일반적으로 제조자나 사용자에 의하여 수행되는 모의 시험이 나 시험을 이용하거나, 또는 아래의 간단한 방법을 사용할 필요가 있다. 특성이 알려지지 않은 SPD 가 장치의 내부에 설치되어 있을 가능성도 있다. 설비의 수명이 지속되는 동안에 장치가 바뀔 가능성이 있으므로, 협조가 되지 않아 장치에 내장된 SPD 에 과도한 스트레스가 가해지지 않도록 각별한 주의 가 필요하다. F.2.5 통과 에너지(LTE) 방법 F.2.5.1 일반사항 KS C IEC 62305-4 에 설명된 표준 임펄스 계수를 가지고 이루어지는 협조는 SPD 를 선정하고 협조하 는 과정이다. 이 방법의 주요 이점은 SPD 를 블랙 박스로 간주할 수 있다는 것이다(그림 F.4 참조). 여기에서 입력 포트에서 주어진 서지에 대하여 개방 회로 전압뿐만 아니라 출력 전류(예를 들면 단 락 회로에 흐르는)도 결정된다("통과 에너지" 원칙). 이러한 출력 특성은 등가 "2� -조합파"-스트레스 (1.2/50 개방 회로 전압, 8/20 단락 회로 전류)로 변환된다. 그 장점은 SPD 의 내부 설계에 대한 특별 한 지식이 필요하지 않다는 것이다. ![image](/image/placeholder) In SPD1 Out U(t) I(1) In SPD2 C W G 상응하는 표준 임펄스로의 변환 - Zi =20 일 때, 1.2/50, 8/20 으로 Uoc SPD1/out ≤ Uoc SPD2/in 식별부호 U 부하 전압 그림 F.4 - LTE - 표준 임펄스 계수를 사용한 협조 방법 106 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
12459625-5054-45d3-b19f-793d8af1e79d | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 이 협조 방법의 목적은 SPD2 의 입력 값(예를 들면 방전 전류)을 SPD1 의 출력값(예를 들면 전압 보 호 레벨)에 알맞게 만드는 것이다. 단계적인 보호의 경우 뒤에 있는 SPD 에 의해 손상 없이 방전될 수 있는 등가 입력 조합 임펄스가 앞에 있는 SPD 의 등가 출력 조합 임펄스와 같거나 높아야 한다는 사실을 염두에 두어야 한다. 신뢰할 수 있는 협조를 위해 등가 조합 임펄스 내력은 최악의 경우(Imax, Umax, 통과 에너지)에 상응하 도록 결정되어야 한다. 결합 방지 요소의 설계에서 최악의 경우는 단락 회로로 인한 문제이다. 그러나 협조의 목적으로 이 것은 너무 심하다. "부하 측 전압"(이른바 "역전압")을 포함하는 것이 더 현실적이다. 스파크 갭의 하부 SPD 는 일반적으로 MOV(금속 산화 배리스터)로 구성되어 있다. 이러한 SPD 의 잔 류 전압은 어떤 경우에도 공칭 전압의 피크 값보다 높다(예를 들어 공칭 전압이 240 V 인 AC 시스템 에서 피크 전압은 V2x 240 = 340 V 이고, 이것은 설치된 SPD 의 기준 전압보다 낮다). 이 공칭의 피크 는 SPD 의 가장 낮은 잔류 전압에 해당된다. 따라서 이 피크 전압은 최소 역전압으로 간주할 수 있 다. 역전압 대신에 단락 회로의 전류를 사용하면 결합 방지 소자를 과도하게 크게 하는 결과 를 불러 온다. 비고 1 이 방법은 SPD1 의 특성이 SPD2 의 특성과 는 너무 달라서 SPD2 의 서지 조건이 쿼지 인가 전류일 때 좋은 결과 를 낼 수 있다. 예를 들어 방전 갭과 MOV 사이의 협조인 경우에 조건이 충족된다. 이 방법을 사용할 때의 제약 조건은 다음과 같다. 어림 결과 를 얻으려면 결합 방지 요소는 두 번째 SPD 의 일부로 포함된다. - 어림 결과 를 얻으려면 제안된 "역전압"은 두 번째 SPD 에 스위칭 부품이 있을 경우, 0 이다. 두 번째 SPD 에 스위칭 부품이 있을 때, 이 방법은 스위칭 부품을 현실적으로 모델링하지 못하기 때문에 그 결과 가 과소 평가될 가능성이 있다. 이 경우에는 이 방법을 적용할 때 조심해야 한다. 설비의 인입구에서 서지 파형은 서로 같은 전류 파형(10/350 또는 8/20)으로 간주된다. 서지 전류 i 의 크기는 일반적으로 알려져 있다. 서지 전압 U 의 크기는 그 시스템의 서지 임피던스에 달려 있다. 검토할 때 SPD 특성의 허용값을 고려해야 한다. F.2.5.2 방법 아래에 설명된 방법은 일반적으로 두 SPD 사이의 결합 방지 요소(임피던스)에 대한 어림 값을 제공 한다. 즉, 이러한 임피던스가 두 SPD 사이에 설치되어 있다면, 대부분의 경우 협조는 계산을 통해 예측했던 것보다 더 잘 이루어진다는 것을 의미한다. 이 방법의 기초는 각 SPD 의 출력을 무부하 전압 Uoc 1.2/50 그리고 단락 전류 /sc 8/20 에 의하여 정의 되는 등가 조합파 발생 장치로 나타내는 것이다. 이때 발생 장치의 임피던스는 2�이다(Uoc = 2 x /sc). III 등급 시험에 따라 시험된 SPD 는 이미 그러한 CWG 에 의하여 시험되었다. II 등급 시험에 따라 시험 된 SPD 의 경우 /sc = In 또는 Imax (선언된 경우)를 고려하여야 한다. 앞에 있는 SPD 는 구조물에 직격뢰가 떨어질 경우 I 등급 또는 II 등급 시험을 받는다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 107 | {}
d6ba74ae-d655-451e-919e-076ee947c14b | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 각 SPD 의 출력에서 전압은 일반적으로 1.2/50 및 8/20 의 파형과 똑같지는 않다. 따라서 실제 파형을 1.2/50 및 8/20 파로 변환하기 위하여 실제 파형을 표준화할 필요가 있다. 이것은 다음 값을 계산하여 할 수 있다. U 의 파고값 = ⌀, Su dt 및 Su2dt i 의 파고값 = i, ⌀i dt 및 ⌀i2 dt 비고 이 공식과 표에 사용되는 단위는 일치해야 한다. 이 값은 표 F.1 에 사용되어 있다. 표 F.1 ¦ 전압 ¦ 0 ¦ Sudt ¦ /Su2dt ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 전류 ¦ i ¦ Sidt ¦ VSi2dt ¦ 1V 크기의 전압을 가진 CWG 에 대한 동일한 표는 다음(표 F.2)과 같다. 표 F.2 ¦ 전압 ¦ 1 ¦ 70 x 10-6 ¦ 6 x 10-3 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 전류 ¦ 0.5 ¦ 12 x 10-6 ¦ 2 x 10-3 ¦ 따라서 표 F.1 의 각 셀을 표 F.2 의 동일한 위치의 셀로 나누면 다음과 같은 새로운 표 F.3 을 얻을 수 있다. 표 F.3 ¦ 전압 ¦ 0 ¦ Sudt/ (70 x 10-6) ¦ V/Su2dt/ (6x10-3) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 전류 ¦ 1 x 2 ¦ Sidt/ (12 x 10-6) ¦ VSi2dt / (2x10-3) ¦ 표 F.3 에서 최고값은 Uoc(CWG) 값을 나타내고, CWG 의 Uoc 의 등가값은 SPD 의 출력에 상응한다. 무부하 전압 Uoc test 인 CWG(또는 II 등급 시험의 경우에는 등가 CWG)로 이루어진 III 등급 시험에 따라 서 하부 SPD 가 시험되는 순간에 협조가 만족스러운지 즉시 알 수 있다. Uoctest > UoccWG 인지 확인하는 것으로도 충분하다. 입력 시 주어진 스트레스에 대한 SPD 출력 값은 시뮬레이션 소프트웨어를 사용하여 계산해야 한다. 이러한 값은 제조자가 계산하므로 매번 계산할 필요는 없다. 각 제품에 대하여 제조자는 SPD 특성 의 허용값과 맹점[때때로 SPD 의 가장 중요한 스트레스는 최댓값 /imp,In 또는 Imax(선언된 경우), Uocmax 에 의해서가 아니라 더 낮은 값에 의하여 주어진다]을 둘 다 고려하면서, 주어진 스트레스[1 등급 시험 에서는 /imp, II 등급 시험에서는 Imax (선언된 경우), III 등급 시험에서는 Uoc max]에 대한 출력 등가 CWG 임펄스를 구할 수 있다. 108 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
314302e2-3a48-4458-b0ff-0a87dc0f5059 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 F.3 협조 시험: 에너지 및 전압 보호 협조 F.3.1 서론 전기 설비를 보호하려면 보호 대상 기기의 과전압 범주와 전기 설비의 배선(케이블 길이, 경로 등)에 따라 둘 이상의 SPD 유형을 사용할 필요가 있다. 이 경우 하부 SPD 에 과도한 스트레스를 주지 않 고 과전압 수준을 보호할 기기의 내전압보다 낮은 값으로 제한하기 위해 효과 적인 SPD 협조를 연구 해야 한다(이 새로운 기준을 전압 보호 레벨 기준이라고 하며, 아래에서 설명한다). 이 장은 효과 적으 로 SPD 를 협조하기 위해 몇 가지 예를 제공하고자 한다. F.3.2 협조 기준 위에 제시된 바와 같이 SPD 를 협조하려면 두 가지 기본 기준인 에너지 기준과 전압 보호 레벨 기준 을 검토해야 한다. 총 유입 뇌/서지 전류 값에 대해 상부 SPD 를 통해 소산되는 에너지 부분이 하부 SPD 를 통해 소산 되는 에너지보다 높을 경우 에너지 협조가 이루어질 수 있다. 또한 상부와 하부 SPD 사이의 모든 요소는 하부 SPD 와 동일한 에너지를 견딜 수 있는 것이 좋다. 또한, 하부 SPD 에 대한 전압 보호 레벨은 더욱 엄격한 전압 보호가 필요한 보호 대상 장비에 더 가 깝기 때문에 상부 SPD 보다 같거나 낮아야 한다는 것이 추가로 제안된다. 두 SPD 를 협조하는 동안 고려해야 하는 가장 중요한 매개변수는 다음과 같다. · SPD 형태(즉, 스위칭 유형 - 스파크 갭, 제한 유형 - 금속 산화 배리스터) · SPD 형태의 특성(즉, 스파크 갭에 대한 스파크오버 전압, MOV 에 대한 최대 연속 사용 전압, 전압 보호 레벨, 최대 방전 전류 용량 등) · 주입 파동(즉, 8/20, 10/350 등) · 보호 대상 장비의 형태(즉, 높은 유도 부하, 민감한 전자 등) · 두 SPD 사이의 이격 거리 F.3.3 협조 기술 협조하기 전에 적합한 SPD 와 이들 사이의 협조 방법을 선택하기 위해 특정 단계를 따라야 한다. · 1 단계 SPD 가 없을 경우 예상되는 과전압 레벨을 확인하여 더 잘 응답하는 SPD 유형을 선정한다. 빠른 과전압을 줄이려면 스위칭 유형보다 SPD 를 제한해야 한다. 과전압을 확인한 후 이상적인 SPD 가 있는 경우 예상 뇌/서지 전류의 최대 에너지를 평가하는 것이 좋다. 최대 에너지 수준에 따라 적합 한 SPD 형태를 선정할 수 있다. · 2 단계 견딜 수 있는 최대 에너지에 따라 상부 SPD 를 선정한다. · 3 단계 원하는 장비의 전압 보호 레벨에 따라 하부 SPD 를 선정한다. 109 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
0dd3d776-b92c-4155-9211-8a9f540694cb | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 · 4 단계 선정한 SPD 의 경우 에너지 및 전압 보호 레벨 기준을 모두 충족하는 것이 좋다. 이것은 주로 소 프트웨어 시뮬레이션 또는 실험적 시험의 도움으로 수행될 수도 있다. 이 마지막 경우 다음 방법 을 사용하여 이를 확인할 수 있다. F.3.4 시험 프로토콜 F.3.4.1 일반사항 SPD 간의 협조는 전류 분배를 기반으로 한다. 협조 규칙을 세우는 데 필수적인 세 가지 매개변수를 정의 한다. · SPD 자체(하나의 SPD 가 다른 SPD 와 협조됨) · 인입구에서의 서지 전류(SPD 의 특성에 따라 고정됨) · 2 개의 SPD(상부 및 하부 SPD) 사이의 결합 방지 임피던스 Z 두 SPD 사이의 임피던스 Z(일반적으로 인덕턴스)는 물리적 임피던스(두 SPD 간의 에너지 분배를 용 이하게 하기 위해 선로에 삽입된 특정 부품)이거나 두 SPD 간 케이블 길이의 인덕턴스를 나타낼 수 있다. SPD 의 협조 시험은 SPD 제조자, 설치자 또는 사용자가 수행할 수 있다. SPD 의 협조는 이 두 가지 기준을 충족할 경우 대부분 이루어진다. a) 최소 시험 에너지에서 최대 시험 에너지까지 모든 서지 전류값에 대해 SPD2 를 통해 소산되는 에 너지 부분이 최대 에너지 내력(EMAX2)보다 낮거나 같은 경우 에너지 협조가 이루어진다 (II 등급 시 험의 경우 In 의 0.1, 0.25, 0.5, 0.75,1 배, I 등급 시험의 경우, /imp 의 0.1, 0.25, 0.5, 0.75, 1 배와 동일한 피크값을 가지는 8/20 전류 임펄스와 상부 SPD /imp 의 0.1, 0.25, 0.5, 0.75, 1 배). b) 최소 시험 에너지에서 최대 시험 에너지까지 모든 서지 전류값에 대해 SPD2 의 잔류 전압이 선언 된 보호 레벨 Up 보다 낮거나 같으면 보호 협조가 이루어진다 (II 등급 시험의 경우 In 의 0.1, 0.25, 0.5, 0.75,1 배, I 등급 시험의 경우, /imp 의 0.1, 0.25, 0.5, 0.75, 1 배와 동일한 피크값을 가지는 8/20 전 류 임펄스와 상부 SPD /imp 의 0.1, 0.25, 0.5, 0.75, 1 배). 선언된 In 또는 /imp 전류의 일부를 이용한 시험은 낮은 스트레스에서 최대 스트레스까지 맹점이 존재 하지 않는지 조사하기 위함이다. Imax 가 II 등급 시험에 대해 선언된 경우 In 은 /max 로 대체되어야 하고 8/20 전류 임펄스에 대한 I 등급 시험의 경우에는 피크값이 /imp 또는 Imax 중 더 큰 값이 된다. F.3.4.2 시험 설정 협조 시험을 위한 SPD 배열은 그림 F.5 에 나타낸다. 110 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
fc69bb12-db91-4534-82d2-51f7ceb9890b | KSCIEC61643-12_KR | KS CIEC 61643-12:2020 ![image](/image/placeholder) 1 d O/c 2 Eq SPD 1 SPD 2 O/c Z 2 Eq U1 U2 12 SPD 1 SPD 2 식별부호 ¦ Eq ¦ 정상 작동 시 보호 대상 장비 ¦ ¦ --- ¦ --- ¦ ¦ O/c ¦ 개방 회로(공급 장치에서 분리된 장비) ¦ ¦ i ¦ 유입 서지 ¦ 그림 F.5 - 협조 시험을 위한 SPD 배열 연결 리드는 무시되며 가능한 한 짧아야 하고 두 SPD 에 대해 유사하게 배열되어야 한다. 외부 분리 기가 있는 경우 이 협조 시험에서는 고려하지 않는다. Z 가 물리적 임피던스를 나타낼 때 선로의 인덕턴스는 Z 에 비해 값이 낮아서 무시될 수 있다. Z 는 두 경우 모두 그림 F.5 와 같이 개략적인 방식으로 표시된다. Z 가 두 SPD 간 케이블 길이의 인덕턴스를 나타내는 경우. 진행 도체와 귀환 도체는 제조자, 설치자 또는 사용자의 선언에 따라 고정되어야 한다. 특정 배열이 없는 경우 진행 도체와 귀환 도체는 10mm 이하의 거리에서 꼬여서도 안 되고 고리를 만들어서도 안된다. 이전에 어떠한 시험도 받지 않은 시료 3 세트로 시험을 수행하여야 한다. SPD 협조 가능성 유형은 협조 절차에 따라 시험되어야 한다. 111 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
28d80649-de22-45ff-a671-e8debd04a28c | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 · 유형 1 SPD 는 유형 2 SPD 와 협조됨 · 유형 1 SPD 는 유형 3 SPD 와 협조됨 · 유형 2 SPD 는 유형 2 SPD 와 협조됨 · 유형 2 SPD 는 유형 3 SPD 와 협조됨 시험 중, SPD 의 시스템은 시험 받는 한 SPD 의 고장을 감지할 수 있을 만큼 충분히 높은 단락 전류 (최소 5 A)로 Uc 에서 전원을 공급받는다. 전류 보호는 전원 장치 분기에서 사용할 수 있지만 서지 전 류 분기에서는 사용할 수 없다. SPD 1 및 SPD 2 가 예를 들어 상, 중성선, 그리고 접지(PE)용 단자가 있는 멀티모드형 SPD 인 경우, 모든 모드는 L-N, N-PE, L-PE 를 시험해야 한다. 이 경우 나머지 단자 는 SPD 1 과 SPD 2 간에 상호 연결될 필요가 있다. 상부 SPD 가 I 등급으로 시험될 때 선언된 /imp 는 협조 절차에 사용된다. Imax 가 선언되면 8/20 전류 임 펄스의 경우, 피크 값은 Iimp 또는 Imax 중 더 큰 값이 된다. 상부 SPD 가 II 등급으로 시험될 때 선언된 In 은 협조 절차에 사용된다. Imax 가 선언되면 Imax 는 협조 절 차에 사용된다. 협조 시험 절차는 하부 SPD 의 방전 매개변수를 초과 하는 8/20 전류 임펄스로만 수행할 수 있다. 정극성 전류 임펄스는 정극성 전압파에서 영점 교차 후 SPD 가 60°에서 Uc 로 전원을 공급받는 동안 적용되어야 한다. 임펄스 사이의 간격은 SPD 가 주변 온도로 냉각될 수 있도록 충분히 길어야 한다. 시험 절차는 상부 SPD 유형에 따라 표 F.4 에 요약되어 있다. 표 F.4 - 협조 시험 절차 ¦ 상부 SPD (SPD 1) ¦ 하부 SPD (SPD 2) ¦ 시험 임펄스 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ I 등급 시험된 SPD ¦ II 혹은 III 등급 시험된 SPD ¦ Iimp 의 0.1. 0.25, 0.5, 0.75, 1 배 또는 선언된 경우 Ima 중 상부 SPD 보다 큰 값과 동일한 피크값을 가지는 8/20 전류 임펄스와 상부 SPD Iimp 의 1.0.25,0.5,0.75, 1 배 ¦ ¦ II 등급 시험된 SPD ¦ II 혹은 III 등급 시험된 SPD ¦ In 의 0.1. 0.25, 0.5, 0.75, 1 배 또는 선언된 경우 Ima 중 상 부 SPD 보다 큰 값 ¦ 협조 시험은 하부 SPD 의 방전 매개변수를 초과 하는 8/20 전류 임펄스로만 수행할 수 있다. F.3.4.3 합격 기준 협조된 SPD 시험의 각 임펄스 후에 속류가 자체 소화되고 열 안정성이 이루어지면 SPD 가 시험을 통과 한 것이다. 육안 검사와 함께 전압 및 전류 기록 모두 시료의 구멍이나 뇌방전을 표시하지 않아 야 한다. 이 시험 동안 기계적 손상이 발생하지 않아야 한다. SPD2 의 측정된 잔류 전압은 선언된 Up 을 초과 해서는 안 된다. 112 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
9c43c0fd-5bf3-4a1f-8efb-1e493d5db259 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 부속서 G (참고) 응용 예 비고 이 부속서는 SPD 가 설치된 송선탑뿐만 아니라 가정 및 산업 설비에 대한 가상 시스템을 나타 낸다. 이 부속서는 제시된 표준을 사용하는 응용 원칙을 설명하여 제한된 상황에서 SPD 선택 시 필요한 정보를 제공하는 데 그 목적이 있다. 모든 설비나 시스템에서 일어나는 특수한 상황 을 설명하기 위한 것은 아니다. G.1 가정에서의 응용 MV 네트워크: 가공선 10 km. LV(230/400 V) 네트워크: 가공선 1 000 m, 지중 케이블 200 m. NG: 2 번의 뇌격/km2/년(5.2.2 참조). 보호되는 구조물의 위치: 평탄한 지역. 전력 시스템의 구조: 인입구에서 S 형 RCD 에 의해 보호되는 시스템(3kA 8/20 을 견뎌낸다, 7.2.5.3 참 조). 설비 인입구의 단락 전류 용량은 3kA 이다. 집의 입구에 주 분전반, 1 층에 보조 분전반 1 개가 있다. 보호되는 구조물의 접지: 50 요. LV 네트워크의 접지 시스템: TT 시스템. 1 상 및 중성선 포설 보호되는 장치의 특성: 전기 세탁기, 컴퓨터, 현관 경보기, VTR, TV 등 위험 분석(4 절 참조)에 따라 SPD 를 설치하는 것이 좋을 수도 있다(NG 값이 크고 변압기의 MV 및 LV 측 모두 가공선이며 전자 장비가 있다). 가공선에 예상되는 중간 정도의 낙뢰 전류, 인입구에서 와이어당 공칭 방전 전류(ln) ≥ 5 kA 8/20. 현관에서 경보 장치 보호(민감한 장치). Up≤ 1.5kV. 이것은 Up = 1.5 kV 로 II 등급 시험된 1 포트 SPD (3.1.21 참조)에 의해 달성될 수도 있다. 인입구에서 단락 전류 용량은 3kA RMS 이다. SPD ≥3kA RMS 의 단락 내력(6.5.4 참조). 이를 위해 제 조자는 퓨즈 또는 단락 전류 차단 능력(백업 보호)이 있는 RCD 분리기의 사용을 권고한다. RCD S 형 회로 분리기가 인입구에서 사용되는 경우 3 kA 8/20 을 초과 하는 유입 서지에 대해 서비스의 연속성이 보장되지 않는다. RCD 가 있기 때문에 간접 접촉에 대비하기 위한 추가 보호 장치는 필요 없다. 열 분리기는 SPD 자 체에 내장되어 있다(7.3.1 참조). TT 시스템이므로 상과 중성선 사이에 지나치게 높은 스트레스가 걸리는 것을 피하려면 세 가지 보호 모드(상-중성선, 중성선-접지 및 상-접지)의 보호 장치가 있는 SPD 를 사용하는 것이 좋다 (7.1.3 참 조). 113 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
3a953e7a-e6c6-4a4d-bf6c-5dac9f5e9e5d | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 안전을 위해 접지되어 있는 세탁기를 제외하면 다른 기기들은 접지에 연결되어 있지 않으므로 보호 되려면 상과 중성선 사이에만 보호가 필요하다. 이 경우 상과 접지, 중성선과 접지 사이의 보호가 필 요할 수도 있다. 비고 TV 안테나가 접지된 경우 추가 보호가 필요할 수 있다. 인입구의 SPD 와 다른 기기, 특히 1 층에서 다른 장치 사이의 거리가 너무 멀 때(각각 10 m 및 20 m) 보호되는 장치와 가까운 곳에 다른 SPD 가 필요하다(7.2.3). 하나는 세탁기 근처에, 다른 하나는 VTR 과 TV 근처에 있어야 한다. 다른 하나는 1 층 분전반에 연결되지만 직접 컴퓨터 플러그에 연결될 수 도 있다(이 분전반과 컴퓨터 사이의 거리는 짧다). 다른 SPD 는 더 낮은 서지 전류를 겪는다. 또한 II 등급 시험에서 사용되는 In = 2 kA 로도 충분하다. 이 때 제조자의 카탈로그에는 Up = 0.8 kV 로 제시된다. 20 m 의 거리는 입구에 설치된 SPD 와 1 층 SPD 사이의 결합을 방지하기에 충분하다. 그러나 인입구 SPD 와 1 층에 있는 다른 SPD 사이의 거리 10m 는 Up=0.8 kV 가 낮아서 결합을 방지하기에 충분하지 않다(7.2.7 참조). 예를 들어 1 층의 SPD 에 대해 Up = 1.5kV 인 다른 종류의 SPD 를 선택하는 것이 좋다. 이러한 SPD 의 경우 해당 위치의 단락 전류가 작아서 제조자는 필요한 분리기(열 및 단락)를 내장시 킨다. 그림 G.1 을 참조한다. ![image](/image/placeholder) TV 안테나 MV 상 LV 10km 중성선 1 km n p n p 50� - 200m 1 층 전기 기판 SPD 컴퓨터 20m 주 전기보드 10m SPD SPD Alarm RCD Stype 비디오 및 SPD TV 세트 세탁기 TV 안테나 그림 G.1 - 가정 설비 114 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
88da06a0-8df6-4c71-9bb1-8825d7866d1f | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 G.2 산업에서의 응용 MV 네트워크: 가공선 10 km LV (230/400 V) 네트워크: 지중 케이블 100 m 2 번 NG = 0.5 번의 뇌격/km2/년(5.2.2 참조) 보호되는 구조물의 위치: 평탄한 지역 전기 설비의 구조물: 주 건물 내 MV/LV 변압기(MB) 주 건물 MB 에서 3 상 주 배전반 MDB 에 전력을 공급하는 LV TN-C 배전 시스템. TN-C 시스템은 별도 의 건물 B1 에 3 상 전원을 공급하고 TN-C-S 시스템은 건물 B2 에 3 상 전원을 공급한다. B1 과 B2 는 MB 건물에서 약 100 m 떨어져 있다. 보호되는 장치: 주 건물 MB - 에어컨 공장, 공장 조명, 산업용 모터 제어기, 가변 속도 드라이브 및 컴퓨터 수치 제어(CNC) 선반 포함 전원 장치(MV/LV 변압기) 산업 제조 공장 건물 B1 - DB1 근처에 위치한 복사기, 팩스, 근거리 컴퓨터 네트워크, 전화 교환기(PABX)를 포함 한 일반 사무 장비 건물 B2 - 일반적으로 DB2 에서 약 50 m 떨어진 곳에 위치한 플랜트 관리, 감독 제어 및 데이터 수 집(SCADA) 시스템용 프로그래밍 가능한 로직 제어기(PLC), 웨이트 브리지 장비, 모니터를 포함한 프로세스 및 제어 장비 구조물의 접지: 건물 MB 의 접지는 11 �으로 측정되고 건물 B1 및 B2 의 국부 접지는 각각 TNC PE 도체로 연결될 때 약 7 �의 전체 접지 시스템 저항이 주어지면 각각 49 �와 51 �이다. 건물 MB, B1 및 B2 에는 각각 등전위 본딩 바 EB, EB1, EB2 가 있다. 위험 분석(4 절 참조): 설비는 직격뢰의 영향에 노출되지 않지만 MV/LV 변압기 자체는 MV 피뢰기를 사용하여 MV 측에서 보호해야 할 수도 있다(본질적으로 노출이 높은 MV 가공선을 사용하기 때문에). 서지 전류는 변압기의 접지 전위 상승으로 인해 여전히 국부 접지 시스템으로 흐를 수 있으며 LV SPD 는 변압기의 LV 측과 건물 B1 및 B2 의 입구에 필요하다. 보호 철학: 위험 분석에 따라 일반적으로 그러한 산업 설비의 지속적인 운영의 필요성을 '중요한 성 격'으로 분류한다. 따라서 분산 서지 보호는 주 배전반 MDB 뿐만 아니라 각 건물 B1 및 B2 에 있는 별도의 배전반 DB1 및 DB2 에서 일차 진입 지점 보호를 위해 시설 전체에서 사용되어야 한다. 주 건물 - SPD 는 각 상과 주 등전위 본딩 바 EB 사이의 주 배전반 내부에 연결된다. 이러한 LV SPD 는 II 등급으로 시험된다. 예를 들어, 전압 보호 레벨 Up1 ≤ 1.2 kV 인 10 kA 의 공칭 방전 전류 In(MV 피뢰기와 동일한 정격)은 하부에서 사용되는 추가 SPD 와의 협조를 보장하기 위해 이 위치에 서 사용할 수도 있다(아래 참조). SPD 의 단락 내력(스위칭 SPD 의 경우 속류 차단 정격)은 MDB 의 예상 단락 전류와 협조해야 한다. 협조는 제조자가 지정한 외부 직렬 연결 과전류 장치(예를 들면 퓨즈, 회로 분리기 등)이거나 SPD 내부에 있는 분리기를 사용하여 이루어질 수 있다. 건물 내부에는 민감한 장비(KS C IEC 60664-1 에 따른 정격 임펄스 전압 Uw = 1.5kV)를 포함하여 내 115 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
e223e2e0-b4b6-4471-bf15-46ce1c12748a | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 전압 기능이 서로 다른 다양한 유형의 장비가 있다. 장비는 설비 인입구에 설치된 SPD 에서 30 m 떨 어진 곳에 위치한다. 그러면 진동이 발생할 수 있다(7.1.4 참조). 이 경우 장비의 전압 레벨은 최대 2* Up1 이 될 수 있으며, Up1 은 인입구 SPD 의 보호 레벨이다. 이 예 에서 최악의 경우 Up1 은 7.1.4 에 따라 1.5kV*0.8/2(즉, 600 V)보다 낮아야 한다. 가능한 TOV 에 따라 이러한 낮은 보호 레벨은 SPD 의 고장 확률을 증가시킬 수 있으며 Up1 = 2.5 kV 와 같이 더 높은 Up(TOV 에 덜 민감함)을 갖는 인입구 SPD 를 선택하는 것이 좋을 수 있다. 이러한 경우 장비(Eq) 앞 에 Up2 ≤ 1 200 V(0.8* Uw)의 추가 SPD 가 필요하다. 민감한 장비에 가까이 있기 때문에 더 이상 2 로 나눌 필요가 없다. 더 낮은 Up1 의 SPD 를 사용하는 경우(Up1 ≤ 600 V) 두 번째 SPD 는 필요하지 않다. 이 프로세스는 장 비의 내전압 Uw(절연 조정)를 다룬다. 장비의 오작동을 피하기 위해 더 낮은 전압 보호 레벨 Up(2 개의 SPD 가 사용되는 경우 Up2 또는 단 일 SPD 가 사용되는 경우 Up1)가 필요할 수 있다(7.1.4.5 참조, 임펄스 내성 고려). SPD1 을 EB 에 연결하는 리드 길이가 7.1.4.4 의 기준을 충족하지 않는다. 이러한 이유로 SPD1 과 PEN 사이에 추가 도체를 사용한다. SPD2 를 PEN 에 연결하는 리드 길이는 7.1.4.4 의 기준을 충족하므 로 추가 도체를 사용하지 않는다. 데이터 및 제어 회로의 보호는 KS C IEC 61643-22 에 기초한다. 건물 1 - MB 에서 B1 의 거리가 100 m 임을 감안할 때 II 등급 시험된 SPD(SPD3)는 각 상과 등전위 본딩 바 사이에 연결되어야 한다 5 kA 의 공칭 방전 전류 In 과 전압 보호 레벨 Up ≤ 1 가 이 위치에서 사용된다고 가정한다(B1 에 민감한 장비가 설치되어 있어 ≤ 1kV 가 필요하다. 건물이 작고 장비가 DB1 과 가깝기 때문에 전압 증배 효과 에 신경 쓸 필요가 없다, 7.1.4 참조). 이것은 장비의 정격 임펄스 전압 Uw(절연 조정)을 다룬다. 장비의 오작동을 방지하기 위해 낮은 전압 보호 레벨 Up 이 필요할 수 도 있다. SPD3 을 EB1 에 연결하는 리드 길이는 7.1.4.4 의 기준을 충족하므로 추가 도체를 사용하지 않는다. 데이터 및 제어 회로의 보호는 KS C IEC 61643-22 에 기초한다. 건물 2 - B1 과 마찬가지로 B2 는 MB 에서 약 100 m 떨어져 있으며 SPD(SPD4)는 각 상과 PE 도체/ 바 PEN 도체/바 사이에 연결되어야 한다. 이러한 LV SPD 는 II 등급 시험을 해야 한다. 5 kA 의 공칭 방 전 전류 In 과 전압 보호 레벨 Up≤ 1.2kV 가 이 위치에서 사용된다고 가정한다. 민감한 장비(KS C IEC 60664-1 에 따른 정격 임펄스 전압 Uw = 1.5kV)를 포함하여 내전압이 다른 다 양한 유형의 장비가 건물 내부에 있다. 장비는 SPD 입구에서 50 m 떨어진 곳에 있다. 이로 인해 진 동이 발생할 수 있다(7.1.4 참조). 이러한 최악의 경우 장비의 전압 레벨은 최대 2* Up1 이며, Up1 은 인입구 SPD 의 보호 레벨이다. 7.1.4.5 에 따르면 Up1 은 1.5 kV*0.8/2(즉, 600 V)보다 낮아야 한다. 건물 1 에서와 같이 TOV 를 고려한다. 인입 구 SPD(SPD4)는 최대 1.2 kV 의 Up1 을 가질 수 있다. 이러한 경우 장비 앞에 Up2 가 1.2 kV(0.8* Uw) 이하인 추가 SPD(SPD5)가 필요하다. 더 낮은 Up1 이 사용되는 경우(Up1 ≤600V) 두 번째 SPD 는 필요 하지 않다. 이 프로세스는 장비의 정격 임펄스 전압 UW 를 다룬다(절연 조정). 장비의 오작동을 피하기 위해 더 낮은 전압 보호 레벨 Up(2 개의 SPD 가 사용되는 경우 Up2 또는 단 일 SPD 가 사용되는 경우 Up1)이 필요할 수도 있다(7.1.4.5 참조). 116 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
54a8a439-8d53-4ca6-a902-b83a7e449672 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 휴대용 장비(SPD5) 가까이에 추가 SPD 가 필요한 경우 각 상과 중성선 사이 및 중성선과 PE 간에 보호를 제공해야 한다. 이는 장비가 DB2 의 중성 PE 본드에서 50 m 떨어져 있기 때문에 발생하는 중 성 도체의 잠재적 상승 위험을 다루는데 필요하다(그림 G.3 참조). SPD4 를 EB2 에 연결하는 리드 길이와 SPD5 중성선을 PE 에 연결하는 리드 길이는 7.1.4.4 의 기준을 충족하므로 추가 도체를 사용하지 않는다. 데이터 및 제어 회로의 보호는 KS C IEC 61643-22 에 기초한다. 그림 G.2 및 그림 G.3 을 참조한다. ![image](/image/placeholder) MB B2 B1 Eq MDB TN C MV TN C TN C-S Eq Eq DB1 DB2 EB Eq 100m 100m Eq EB2 EB1 식별부호 ¦ B1, B2 ¦ 건물 1,2 ¦ ¦ --- ¦ --- ¦ ¦ MB ¦ 주 건물 ¦ ¦ EB ¦ 등전위 본딩 바 ¦ ¦ MDB ¦ 주배전반 ¦ ¦ DB ¦ 배전반 ¦ ¦ Eq ¦ 부하 장치 ¦ 그림 G.2 - 산업 설비 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 117 | {}
ab8a9046-3630-4d96-a83d-c8d97dc3756a | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) MB TN-C MVA MDB PEN SPD1 30m CB SPD2 Eq SPD 11 Ohns. Do to/Control 100m Circuit B1 TN-C 100m SPD3 <10m CBI B2 TN-C-S 49 Ohns. DB2 190 분 SPD4 SPD5 EB2 Eq >50m 51 Ohas. 식별부호 ¦ B1, B2 ¦ 건물 1, 2 ¦ ¦ --- ¦ --- ¦ ¦ MB ¦ 주 건물 ¦ ¦ EB ¦ 등전위 본딩 바 ¦ ¦ MDB ¦ 주 배전반 ¦ ¦ Eq ¦ 부하 장치 ¦ ¦ PB ¦ 배전반 ¦ ¦ MVA ¦ 중압 서지 피뢰기 ¦ 그림 G.3 - 산업 설비의 회로 118 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b9f78c07-0bf4-465a-afef-091f9c352c34 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 G.3 뇌 보호 시스템의 존재 LPS 가 장착된 송신탑 ¦ MV 네트워크: ¦ 가공선 10km ¦ ¦ --- ¦ --- ¦ ¦ LV 네트워크: ¦ 가공선 500 m ¦ ¦ NG: ¦ 6 번 뇌격/km2/년 ¦ ¦ 보호되는 구조물 위치: 전기 설비의 구조물: 국부 보호 접지에 접지된 장비 ¦ 언덕의 정상 중성선이 언덕 아래에 접지되어 있다. ¦ ¦ ¦ 10 요 ¦ ¦ 보호되는 구조물의 접지: ¦ ¦ ¦ MV/LV 변압기의 접지: ¦ 10 요 ¦ ¦ LV 네트워크의 접지 시스템: 보호되는 장비의 특성: ¦ TT 시스템; 단상 및 중성선 포설 전자 장비 ¦ 설비의 중요한 특성(위험 분석, 4 절 참조)으로 인해 I 등급 시험을 거친 SPD 를 사용하여야 한다. SPD 는 상과 국부 접지 사이, 중성선과 국부 접지 사이, 상과 중성선 사이에 연결되어 있다. 전류 분배에 대한 계산이 되지 않았기 때문에 이러한 SPD 는 I 등급 시험을 하여야 하며 탑을 뇌격하는 아주 큰 용량의 직격뢰를 방전해야 하므로 25 kA 의 전류 용량을 가져야 한다(부속서 D 참조). 변압기를 보호 하기 위해 가공선의 반대쪽에 동일한 전류 정격을 가진 다른 SPD 를 사용할 수도 있다. 민감한 장비 에 가까운 SPD 의 보호 레벨은 1.5 kV 보다 낮거나 같아야 하며(임펄스 내성을 포함하기 위해 더 낮은 값이 필요할 수 있음) 변압기에 가까운 SPD 는 최대 6 kV 의 보호 레벨을 가질 수 있다(절연 조정을 기반으로 한 일반적인 변압기 절연 내성). 또한 변압기의 MV 측에서 SPD 를 사용하여야 한다. 이것은 KS C IEC 60099-5 에 설명되어 있다. 그림 G.4 를 참조한다. 119 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
fa2770b9-55ff-4f40-9481-26fcba1685af | KSCIEC61643-12_KR | KS CIEC 61643-12:2020 ![image](/image/placeholder) 상 500 m LV 중성선 변압기 MV 10 km MV 어레스터 상 상 SPD 중성선 S S 비고 그림 K.3 에 나타낸 보호 구조를 적용할 수 있다. 그림 G.4 - LPS 의 예 G.4 풍력 터빈 G.4.1 일반사항 풍력 발전 시스템에는 이중 전원 공급 유도 발전기(DFIG), 직접 구동 발전기 및 반 직접 구동 발전 기 등 세 가지 유형의 풍력 터빈이 있다. 현재는 DFIG 가 풍력 발전소에서 가장 널리 적용되고 있다. 비고 DFIG 는 이중 전원 공급 유도 발전기라고도 한다. 고주파수 스위칭을 사용한 에너지 변환은 SPD 에 특별한 문제를 발생시킨다. 한 가지 예는 DFIG 풍 력 터빈 컨버터 회로다. G.4.2 DFIG 컨버터 회로의 과도 과전압 DFIG 는 유도 발전기, 컨버터 및 전력망으로 구성된다. 그림 G.5 는 발전기 회전자와 전력망 사이에 전력이 흐를 수 있음을 보여준다. 120 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
5fe08a71-a0e2-44b5-ab16-19c0147aa6c3 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) 발전기 전력망 Gear Box 고정자 라인 회전자 라인 2 4 3 Filter Filter AC AC DC 컨버터 그림 G.5 - DFIG 풍력 터빈의 구성 IGBT 는 컨버터의 스위칭 부품으로 널리 사용된다. 1 MW 이상의 컨버터 스위칭 주파수는 일반적으로 몇 kHz 다. 예를 들어, 1.5 MW 컨버터의 스위칭 주파수는 2kHz 다. 회전자 회로의 DC 전압은 일반적 으로 1 050 V 만큼 높다. IGBT 조정은 그림 G.6 에서 볼 수 있듯이 출력 PWM 전압에서 높은 피크 값 과 매우 가파른 상승 시간을 갖는 반복적인 과도 현상을 일으킨다. 이 피크 값과 급격한 상승 시간 (du/dt)은 발전기와 컨버터의 절연 및 그 사이에 설치된 SPD 에 부정적인 영향을 미칠 수 있다. ![image](/image/placeholder) -152ms 37.19V 95.6ms 35.00V △248ms 스 2.188V ●500V 最大 l S94kV Z 100ms 10.0M�/秒 1.82kV 最小 -509.0V 00000s 10M 번호 40 22gus 경오는 15.57% 10:11:2011 980.0V Chart Type: line Red Line Green Line Blue Line item_01 673638Voltage (V) 6741400Voltage (V) 5912800Voltage (V) a) L-L b) L-PE 그림 G.6 - 회전자 회로에서 발전기와 컨버터 사이의 PWM 전압 DFIG 의 고정자 회로와 회전자 회로의 특성은 다르다. 고정자 회로는 전력망과 동일한 AC 주파수에서 전력망에 직접 연결된다. · 회전자 회로는 컨버터를 통해 전력망에 연결된다. 높은 피크값과 du/dt 의 반복적인 과도 전압을 갖 는 방형파로 구성된 PWM 전압을 생성한다. G.4.3 긴 케이블로 인한 과도 전압의 전달 효과 실제로 컨버터는 그림 G.7 에서 볼 수 있듯이 보통 발전기와 별도로 설치된다. 발전기는 일반적으로 탑 상단의 엔진실에 설치된다. 컨버터는 일반적으로 탑의 바닥에 설치된다. 발전기와 컨버터는 엔진 실에서 탑의 바닥까지 긴 케이블로 연결된다. 발전기와 컨버터는 상당한 거리를 두고 설치되고 약 100 m 의 케이블로 연결되기 때문에 케이블을 따 라 전달되는 PWM 파는 발전기에서 반사된다. 그러면 발전기 측에서 PWM 파형 및 du/dt 의 피크 값 121 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
0dd5f82e-3a7e-4f49-a818-2b476f2c6784 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 이 인버터 측보다 높아지게 된다. 2011 년 중국의 조사에 따라 그림 G.5 의 2 와 3 지점에서 PWM 전 압과 du/dt 의 피크 값을 표 G.1 에 나열했다. ![image](/image/placeholder) 고정자 □□ 회전자 케이블 tower 컨버터 그림 G.7 - 컨버터 및 발전기의 위치 표 G.1 - 2011 년 중국 조사에 따른 두 단자의 PWM 전압 및 du/dt 피크 값 ¦ ¦ U 의 피크 값 (L-L) kV ¦ du (L-L)/dt 의 피크 값 V/�s ¦ U 의 피크 값 (L-PE) kV ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 2 지점 ¦ 1.70 ¦ 970 ¦ 2.0 ¦ ¦ 3 지점 ¦ 1.54 ¦ 852 ¦ 1.96 ¦ 표 G.1 에서 발전기 측(2 지점)의 PWM 상 대 상 전압의 피크 값은 인버터 측(3 지점)의 피크 값보다 10 % 이상 높다. du/dt 는 약 14 % 더 높다. 이러한 차이는 케이블을 따라 전달되는 반사 영향 때문이 다. 그러면 발전기의 절연과 발전기 측에 설치된 SPD 가 더 스트레스를 받게 된다. G.4.4 풍력 터빈 시스템의 SPD 와 장비 간의 전압 조정 2.5 MW 직접 구동 터빈 컨버터를 실험실에서 시험했다. Uc = 750 V 및 VV = 1 450 V 의 MOV 를 갖는 여러 SPD 는 원래 발전기 측의 L-PE 사이에 설치되었다. 그러나 내부 분리기는 컨버터를 켠 후에 동 작했다. 그런 다음 그림 G.8 b)에서 볼 수 있듯이 컨버터의 발전기 측에서 L-PE 전압이 관찰되었으며 일부 타격은 2kV 까지 높게 발견되었다. 그림 G.8 b)에서 SPD 의 Vv 는 타격의 피크 값보다 훨씬 낮다. 이 경우 SPD 가 손상되고 누설 전류로 인해 MOV 가 가열되며, 이로 인해 내부 분리기가 작동한다. Uc = 1 000 V 정격 SPD 를 설치하여 문제를 해결하였다. 비고 SPD 의 커패시터는 누설 전류로 인해 SPD 가 L 과 PE 사이에 연결될 때도 고려한다. 122 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
08d4d362-a1d6-4d88-9695-30120debc5ba | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) ![image](/image/placeholder) DSOX 3014A 500V/ 2 -2,1200 2,000M Trige 1.740 ※ a) b) 그림 G.8 실험실에서 시험한 컨버터와 L-PE 전압 파형 표 G.2 는 CLC/TR 50539-22 에서 복사한 것이며 유사한 상황을 설명한다. 표 G.2 - 교류 발전기 여자 회로 및 관련 SPD 의 특성 예 ¦ 시스템의 최대 작동 전압, L-L ¦ 750 Vrms (± 10 %), 0....200 Hz ¦ ¦ --- ¦ --- ¦ ¦ L-접지 전압에 부가된 반복적인 과도 현상 ¦ 1.7 kV ¦ ¦ 동작 전압 L-L 에 부가된 반복적인 과도 현상 ¦ 2.95 kV ¦ ¦ 전압에 부가된 반복적인 과도 현상의 du/dt ¦ 1.4 kV/�s ¦ ¦ 컨버터 스위칭 주파수 ¦ 2 000 Hz ¦ ¦ SPD 주요 특성 ¦ SPD 주요 특성 ¦ ¦ Uc ¦ 사용전압에 부가된 반복적인 과도 현상의 스트레스를 견디도록 선택해야 한다. ¦ ¦ 작동 주파수 ¦ 컨버터의 스위칭 주파수를 고려하여 선택해야 한다. ¦ ¦ 보호 모드당 /imp, (T1) ¦ 1...5 kA ¦ ¦ 보호 모드당 In, (T2) ¦ 15 kA ¦ ¦ 단락 전류 ISCCR ¦ < 20 kA, 50 Hz ~ 60 Hz ¦ ¦ 준수해야 할 표준 ¦ KS C IEC 61643-11 ¦ 유사한 특성이 인버터에도 적용될 수 있다. 123 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
5231da92-0233-4aec-80c4-62c2f56f16db | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 표 G.3 - 풍력 터빈 시스템과 저압 배전 시스템 간의 비교 ¦ 번호 ¦ 인자 ¦ 저압 배전 시스템 ¦ DFIG 전기 시스템 ¦ DFIG 전기 시스템 ¦ 비고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 번호 ¦ 인자 ¦ 저압 배전 시스템 ¦ 고정자 회로 ¦ 회전자 회로 ¦ ¦ ¦ 1 ¦ 파형 ¦ 정현파 AC ¦ 정현파 AC ¦ PWM ¦ ¦ ¦ 2 ¦ 주파수 ¦ 50 Hz ¦ 50 Hz ¦ 스위칭 주파수: ≤ 3 kHz 기본 주파수: ≤ 20 Hz ¦ ¦ ¦ 3 ¦ 접지 시스템 ¦ TN、 TT、 IT ¦ IT ¦ IT ¦ ¦ ¦ 4 ¦ 전력 시스템 ¦ 단상 시스템 3 상 시스템 ¦ 3 상 시스템 ¦ 3 상 시스템 ¦ ¦ ¦ 5 ¦ 단락 전류 ¦ 배전 변압기의 용량에 따라 ¦ 발전기 및 승압 변압 기의 용량에 따라 ¦ 미정 ¦ ¦ ¦ 6 ¦ TOV ¦ 고(중) 전압 시스템의 고장으로 인한 TT 및 IT 시스템의 TOV ¦ ¦ ¦ 승압 변압기 는 풍력 터빈 과 등전위 결 합되어 있다. ¦ ¦ 6 ¦ TOV ¦ TN, TT 또는 IT 시스 템의 저압 고장 또는 장애로 인한 TOV ¦ ¦ ¦ 승압 변압기 는 풍력 터빈 과 등전위 결 합되어 있다. ¦ ¦ 7 ¦ 전압의 피크 값 ¦ V2UN (UN =230/400) ¦ V2UN (UN =400/690) ¦ 구형파, 상승 기울기 ≤ 1.5 kV/us, 피크 값 ≤ 1.7 kV(L-PE) 피크 값 ≤2.95 kV(L-L) ¦ CLC/TR 50539-22 에 따름 ¦ G.4.5 CLC/TR 50539-22 에 설명된 예에 대한 가능한 솔루션 기본적으로 두 가지 솔루션이 있다. Uc 가 더 높은 SPD 를 사용하거나. MOV 의 Vv 는 과도 상태의 피크 값보다 크거나 적어도 같아야 한다. 일반적으로 Vv/Uc = 1.6 사이 에는 관계가 있다. 그러면 다음과 같이 추론할 수 있다: · L-PE 간 SPD 의 Uc 는 1.7 kV 까지 과도 상태를 유지하기 위해 1.06 kV 이상이어야 한다. 결과 적으로 SPD 의 Up 는 보통 4 kV 에 도달한다. · L-L 사이 SPD 의 Uc 는 2.95 kV 까지 과도 상태를 유지하기 위해 1.85 kV 이상이어야 한다. 결과 적으로 SPD 의 Up 는 보통 6 kV 에 도달한다. 리드 및 외부 분리기의 전압 강하로 인해 컨버터 및 발전기 절연에 대한 전압 스트레스는 매우 심각할 것이다. 이것은 성공적인 절연 조정을 달성하기 위해 고려하고 시험하는 것이 좋다. 또는 이 스트레스를 견딜 수 있도록 특별히 설계된 SPD 를 사용한다. 비고 그러한 솔루션이 다른 경우에도 추정될 수 있다. 124 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
cab65904-d2a7-4397-b017-9070661de27b | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 부속서 H (참고) 위험성 평가 방법 및 응용 사례 H.1 일반사항 KS C IEC 62305-2 는 구조물과 연결 서비스에 대한 낙뢰 위험을 설정하기 위해 잘 확립된 방법이다. KS CIEC 62305-2 에 기초한 단순화된 위험 분석 방법은 KS C IEC 60364-4-44 에 명시되어 있다. 그것 은 아래에 제시한다. 다른 응용에는 다른 방법을 설정할 수 있다. 제안된 방법론도 아래에 제시한다. H.2 KS c IEC 60364-4-44 에 명시된 저전압 위험 평가를 위해 제안된 단순화된 방법 H.2.1 과전압 제어 IEC 62305 시리즈는 과전압으로 인한 결과 가 다음과 같은 장소가 있는 설비에 영향을 미치는 경우 적용된다. a) 폭발의 위험이 있는 구조물 b) 주변 구조물 또는 환경도 포함해서 손상될 수 있는 구조물(예를 들면 화학 물질 또는 방사능 배출) 과전압의 영향이 미치는 다음과 같은 장소에 대하여 과도 과전압 보호기능을 제공해야 한다. c) 인간의 생명을 다루는 안전 구조 센터, 의료 기관 등 d) 공공서비스 제공기관, IT 센터, 박물관 등 공공 서비스 제공기관 및 문화 유산 e) 호텔, 은행, 산업체, 상가, 농장 등 상거래 및 산업활동 장소 기타 모든 경우에는 과도 과전압에 대한 보호가 유익한지 결정하기 위해 위험 평가를 수행해야 한다. 위험 평가가 수행되지 않은 경우 전기 설비는 과도 과전압에 대한 보호 기능과 함께 제공되어야 한 다. 그러나 지역 전기 규정에 따라 단독 주택에는 이러한 보호가 필요하지 않을 수 있다. 설비의 과전압 유형에 따른 스위칭 과전압 크기 및 장애 정도를 초과 하는 장비의 경우 스위칭 과전 압에 대한 보호를 고려해야 한다. 예를 들어 LV 발전기가 전력을 공급하는 설비 또는 유도성 또는 용량성 부하(예를 들면 모터, 변압기, 커패시터 뱅크 등), 저장 장치 또는 대전류를 소비하는 전기설비 H.2.2 단순화된 위험 평가 방법 위험 수준 산정법(CRL)은 대기 근원의 과도 과전압에 대한 보호가 필요한지 여부를 결정하는 데 사 용된다. CRL ≥ 1 000 이면 대기 근원의 과도 과전압에 대한 보호가 필요하지 않다. CRL < 1 000 인 경우 대기 근원의 과도 과전압에 대한 보호가 필요하다. CRL 의 값은 표 H.1 에 따라 계산한다. 125 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
6fdc30f3-41cf-4860-9f4d-9c91ce7f6fd3 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 표 H.1 - CRL 계산 ¦ 환경 ¦ CRL ¦ ¦ --- ¦ --- ¦ ¦ 농촌 및 교외 환경 ¦ (85 x F) /(Lp x Ng) ¦ ¦ 도시 환경 ¦ (850 x F) /(Lp x Ng) ¦ 여기에서 계수 값 F 는 모든 설비에 대하여 1 을 적용하나, 국가표준위원회는 장소별로 계수 값 F 를 1 에서 3 까지 조정할 수 있다. NG 는 전력선 및 연계된 구조물의 위치와 관련된 대지 내방전 밀도(회/km2, 매년)다. 위험 평가 기간 Lp 는 다음과 같이 계산된다. Lp=2 x LPAL + LPCL + 0.4 LPAH + 0.2 LPCH; 여기에서(그림 H.1) LPAL : 가공 저압선로 거리(km) LPCL : 저압 지중케이블 거리(km) LPAH : 가공 고압선로 거리(km) LPCH : 고압 지중케이블 거리(km) 총 거리(LPAL + LPCL + LPAH + LPCH)는 1 km 로 제한하거나 전력망에 최초 시설된 과전압 보호 장치(SPD 또는 서지 어레스터)에서 설비 입구까지의 거리 중 더 작은 것으로 한다. 배전선로의 거리를 전체적으로 또는 부분적으로 알 수 없다면, LPAL 은 총 길이가 1 km 에 도달하기까 지의 잔여 거리로 한다. 예를 들어, 지중케이블의 거리만 알려진 경우(예를 들면 100 m), LPAL 은 900 m 로 간주한다. ![image](/image/placeholder) LPAL Surge LPAH Arrester 2 LPCL LPCH LPCL 식별부호 1 설비 시설 지점 2 LV/HV 변압기 그림 H.1 - 전력선의 개별 시설의 예 대기 근원 위험이 낮아 SPD 가 필요하지 않은 경우에도 스위칭 서지에 대한 보호가 필요할 수 있다 (5.2.3 참조). 위의 그림 H.1 를 참조한다. 126 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b941128b-79ed-40f4-85e9-2a284ace17a7 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 H.2.3 예 1 - 농촌 환경 건물 NG = 1,F= 1 Lp=2x LPAL+ LPCL + 0.4 LPAH + 0.2 LPCH = (2x 0.4) + (0.4x0.6)= 1.04 여기에서 LPAL : 가공 저압선로 거리(km): 0.4km LPAH : 가공 고압선로 거리(km): 0.6 km LPCL : 저압 지중케이블 거리(km) = 0 LPCH : 고압 지중케이블 거리(km) =0 CRL = 85 xF / (Lp x NG) =85 x 1 / (1.04 x 1)=81.7 이 경우 SPD 보호 장치를 설치해야 한다. H.2.4 예 2 - HV 에서 전력을 얻는 농촌 환경 건물 NG = 0.4,F= 1 Lp=2 x LPAL + LPCL + 0.4 LPAH+ 0.2 LPCH= 0.2 x 1 = 0.2 여기에서 LPAL : 가공 저압선로 거리(km) =0 LPAH : 가공 고압선로 거리(km) = 0 LPCL : 저압 지중케이블 거리(km) = 0 LPCH : 고압 지중케이블 거리(km): 1 km CRL = 85 xF / (Lp x NG) = 85 x 1 / (0.2 x 0.4) = 1 062.5 이 경우 SPD 보호 장치는 필수가 아니다. H.2.5 예 3 - 도시 환경 건물 NG = 1,F= 1 Lp=2xLPAL + LPCL + 0.4 LPAH + 0.2 LPCH = (2x 0.4) + (0.4x0.6)= 1.04 여기에서 LPAL : 가공 저압선로 거리(km): 0.4km LPAH : 가공 고압선로 거리(km): 0.6 km LPCL : 저압 지중케이블 거리(km) = 0 LPCH : 고압 지중케이블 거리(km) = 0 CRL = 850 xF/(Lpx NG)=850 x 1 /(1 x 1.04) = 817 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. 127 | {}
9ce9be18-24b5-4a33-8604-bf2d480e8fd8 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 이 경우 SPD 보호 장치를 설치해야 한다. H.2.6 예 4 - HV 에서 전력을 얻는 도시 환경 건물 NG = 0.5,F= 1 Lp=2x LPAL + LPCL + 0.4 LPAH + 0.2 LPCH = 1 여기에서 LPAL : 가공 저압선로 거리(km) =0 LPAH : 가공 고압선로 거리(km) = 0 LPCL : 저압 지중케이블 거리(km): 1 km LPCH : 고압 지중케이블 거리(km): 0 CRL = 850 xF / (LpxNG) = 850 x 1 /(1 x 0.5)= 1 700 이 경우 SPD 보호 장치는 필수가 아니다. H.2.7 예 5 - 전기 자동차 공급 장비 이 경우는 HV/LV 변압기에 의해 전원 공급되는 전기 자동차 공급 장비 EVSE 다(그림 H.2 참조). HV 선로의 길이는 1 km 이상이다. 변압기의 HV 측에 서지 피뢰기가 없고 LV 측에는 SPD 가 없다. 주 캐비닛은 슈퍼마켓 건물 내부에 있으며 충전소는 주차장에 있다. 25 m x 15 m 주차장의 전용 구역에 많은 기둥이 있다. 지역은 교외다. NG 는 1 이고 F 도 1 이다. ![image](/image/placeholder) 1 000 m 기둥 주 캐비닛 25 m 10m 20 m 15 m LPAH LPCL LPCL LPCL 그림 H.2 - 전기 자동차 공급 장비의 예 NG = 1,F=1 Lp=2xLPAL + LPCL + 0.4 LPAH + 0.2 LPCH = (2 x 0.07) + (0.4x 0.93)= 0.512 여기에서 LPAL : 가공 저압선로 거리(km): 0.07 km (70 m = 10 m + 20 m + 40 m, 40 m 는 더 멀리 있는 기 등의 최대 길이) LPAH : 가공 고압선로 거리(km): 0.93 km (이 길이는 LPAL + LPAH = 1 km 을 통해 결정) LPCL : 저압 지중케이블 거리(km) = 0 128 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
62347154-c7a4-4c84-9e2b-419db5800a9c | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 LPCH : 고압 지중케이블 거리(km) =0 CRL = 85 xF /(LpxNG)=85 x 1 /(0.512 x 1)= 166 이 경우 SPD 보호 장치는 HV/LV 변압기의 LV 측에 설치하거나 주 캐비닛에 설치해야 한다. 또한 캐비닛과 기둥 간 배선에서 유도된 서지로 인해 기둥에도 추가 SPD 를 설치하는 것이 좋다. H.2.8 예 6 - 화학 시설 500 m 길이의 HV 가공선이 100 m 지하 HV 케이블을 통해 화학 시설 발전소에 전력을 분배하고 있 다(그림 H.3 참조). 발전소(5 x 5 m, h = 3 m)는 관리 건물(10 x 10 m h = 6 m)과 화학 시설(100 x 20 m, h = 6 m + 굴뚝 h = 9 m)에 LV 전력을 공급하고 있다. 지역은 시골이다. NG 는 1 이고 F 도 1 이다. ![image](/image/placeholder) 500 m 발전소 100 m CHO 23 300 m 100 m ○○ H= 6 m 20 m LPCL_Production Ht II 9 m LPAH LPCH 10 m 50 m 생산 건물 LPCL_admin H = 6 m 관리 건물 그림 H.3 - 화학 시설의 예 현장은 산업현장이므로 H.1.1 의 요구사항 e)를 충족하기 위해 발전소의 LV 측에 LV SPD 를 제공해야 한다. 화학 시설(그림 H.3 참조)이 환경에 영향을 미칠 수 있으므로 H.1.1 의 요구사항 b)을 만족하기 위해 화학 시설에도 KS C IEC 62305-2 를 사용해야 한다. 단순화된 위험 방법은 실제로 관리 건물에 만 적용된다. 비교를 위해 KS C IEC 62305-2 뿐만 아니라 단순화된 버전을 세 가지 구조물에 적용한다(표 H.2 참조). 경제적 위험(KS C IEC 62305-2 에 따른 R4)만 계산된다. 이 예에서는 화학 장치의 환경에 대한 영향을 고려하지 않는다. 129 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
014cd1c0-52b9-49c0-9b6b-809027c6fc70 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 표 H.2 - 단순화된 방법 ¦ ¦ 1 ¦ 2 ¦ 3 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ 발전소 ¦ 화학 장치 ¦ 관리 건물 ¦ ¦ LPAL ¦ 0 ¦ 0 ¦ 0 ¦ ¦ LPCL ¦ 0 ¦ 0,3 ¦ 0.05 ¦ ¦ LPAH ¦ 0.5 ¦ 0 ¦ 0 ¦ ¦ LPCH ¦ 0.1 ¦ 0 ¦ 0 ¦ ¦ Lp ¦ 0.22 ¦ 0.3 ¦ 0.05 ¦ ¦ NG ¦ 1 ¦ 1 ¦ 1 ¦ ¦ F ¦ 1 ¦ 1 ¦ 1 ¦ ¦ 환경 ¦ 시골 ¦ 시골 ¦ 시골 ¦ ¦ CRL ¦ 386 ¦ 283 ¦ 1 700 ¦ ¦ SPD ¦ 필요 ¦ 필요 ¦ 불필요 ¦ ¦ 비고 ¦ 산업활동 때문에 SPD 가 필요하다 (요구사항 e). ¦ 산업활동 때문에 SPD 가 필요하다(요구사항 e 및 가능하면 a) ¦ 스위칭에 대한 SPD 보호 또는 UPS, 개인용 컴퓨터 또는 통신 장비와 같은 특정 장비를 보호하기 위한 SPD 는 여전히 필요할 수도 있다. ¦ KS C IEC 62305-2 에 따른 전체 방법은 10-3 과 동일한 R4 에 대한 허용 값으로 적용된다. 각 구조물은 더 작은 구조물로 둘러싸여 있다고 가정한다. 토양의 저항은 400 옴이고 배전 회로는 큰 루프를 방지하는 방식으로 만들어진다(PE 도체는 활성 도체와 동일한 케이블로 라우팅됨). Uw 는 LV 선로의 경우 2.5 kV 로, HV 인입 선로의 경우 KS C IEC 62305-2 의 최댓값으로 고정된다. 화재 위험의 경우, 그 위험이 높은 화학 장치를 제외하고 모든 구조물은 평균이다. 화학 장치에는 자동소화장치가 설치되어 있고 다른 건물에는 수동소화장치만 구비되어 있다. 이것은 다음 값을 제공한다. 표 H.3 를 참조한다(부품 RB 에서 Rz 에 대한 설명은 KS C IEC 62305-2 를 참조한다. R4 는 B 에서 Z 까지 i 가 있는 모든 R 의 합이다). 130 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
7f837343-6532-4859-ab30-ef9fac6d9a9c | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 표 H.3 - KS C IEC 62305-2 방법 ¦ ¦ 1 ¦ 2 ¦ 3 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ 발전소 ¦ 화학 장치 ¦ 관리 건물 ¦ ¦ RB ¦ 1.72 x 10(-6) ¦ 1.10 x 10(-4) ¦ 6.90 x 10(-6) ¦ ¦ Rc ¦ 2.30 x 10(-6) ¦ 3.67 x 10(-5) ¦ 9.20 x 10(-6) ¦ ¦ Rv ¦ 1.99 x 10(-7) ¦ 1.45 x 10(-7) ¦ 1.29 x 10(-7) ¦ ¦ RM ¦ 1.20 x 10(-4) ¦ 1.87 x 10(-4) ¦ 9.22 x 10(-6) ¦ ¦ Rw ¦ 1.60 x 10(-4) ¦ 6.23 x 10(-5) ¦ 1.23 x 10(-5) ¦ ¦ Rz ¦ 2.40 x 10(-3) ¦ 1.80 x 10(-3) ¦ 3.00 x 10(-4) ¦ ¦ R4 ¦ 2.68 x 10(-3) ¦ 2.20 x 10(-3) ¦ 3.38 x 10(-4) ¦ ¦ NG ¦ 1 ¦ 1 ¦ 1 ¦ ¦ 환경 ¦ 지방 ¦ 지방 ¦ 지방 ¦ ¦ SPD ¦ 필요 ¦ 필요 ¦ 필요하지 않음 ¦ 다른 매개변수에 기초했음에도 불구하고 이 특정 경우에는 전체 방법과 단순화된 방법이 경제적 위 험에 대해 일치한다. 그러나 인간 및 환경 위험 또는 서비스 손실에 대해 전체 방법을 적용하면 다 른 결과 가 발생할 수 있으며 특히 LPS 를 구현하게 되면 다른 유형의 SPD 및 추가 SPD 가 발생할 수도 있다. H.3 위험 평가 시 고려해야 할 요소 H.3.1 환경 낙뢰 발생률 및 심각도 Ng 는 연간 대지 뇌방전 밀도로, 뇌격 횟수/km2/연당(5.2.2 과 I.1.1.1 참조) · 건물 뇌보호 시스템(LPS) 또는 전기 공급 및 통신 선로에 직격뢰 · 저항 또는 유도 결합 위험 평가에는 LPS, 인입 전력선, 금속 전화선, 데이터 케이블, 무선 주파수 케이블, 도파관 및 수도 관과 같은 비전기 도체를 통한 진입을 포함하여 모든 유형의 낙뢰 유도 에너지 직간접 모드를 고려 해야 한다. 광섬유 케이블은 보호 영역을 관통하는 금속 도체가 없을 경우 대부분의 경우 내성이 있다. 전력 스위칭 발생률 및 심각도 모터 컨트롤러와 같은 전력 스위칭 장비와 근접하거나 동일한 회로에 있는 전자 장비는 부하 생성 과도 현상으로 인해 손상 또는 성능 저하를 겪을 수 있다. 또한 전력 유틸리티 스위칭, 시스템 오류 또는 부하의 내부 장애로 인해 과도 현상이 발생할 수 있다. 주변건물의 LPS 에 대한 노출 및 결합 손상은 전류 소산과 관련된 접지 전위 상승을 포함하여 인근 건물 또는 시설의 피뢰시스템에 전달되 는 낙뢰 전류의 과도 결합을 통해 발생할 수 있다. 이러한 에너지 분배는 일반적으로 전력 유틸리티 131 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
8592c18d-4046-4536-a280-69c9709e5f4b | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 케이블을 통해 발생하며 사용자가 직접 제어할 수 없다. 소산되는 에너지는 로컬 네트워크의 다양한 접지 저항의 크기와 관련이 있다. 시설 또는 건물의 위치 · 지형 · 주변 구조물 및 나무에 의한 차폐 높은 언덕이나 산의 상단 또는 측면에 있는 시설은 계곡 및 자연 노출이 낮은 지역에 있는 유사한 시설보다 직사광선에 더 취약하다. 마찬가지로, 높은 통신 탑이 있는 설비는 낙뢰 접촉 위험이 증가 할 수 있다. 소형 및 저층 시설은 인접한 더 높은 물체에 의해 직격뢰로부터 보호될 수 있다. 그러나 이러한 차폐는 시설에 들어가는 케이블을 통한 에너지 유입에 영향을 미치지 않는다. H.3.2 장비 및 시설 장비 임펄스 내력 범주 및 내성 레벨 제조자는 다양한 임펄스 전압 내력 레벨로 전기 및 전자 장비를 설계할 수 있다. 레벨이 낮을 수록 위험이 높아진다. 제조자가 달리 조언하지 않는 한 장비에 특정 내성이 내장되어 있지 않다고 가정 하는 것이 가장 좋다. 올바르게 설계된 보호는 케이블 인입점에서 에너지 전환을 최대화하고 장비로 의 전달을 최소화한다. 접지 시스템 · 접지 저항 및 임피던스 · 레이아웃 및 근접성 · 다른 접지 시스템으로 연결 가장 중요한 것은 갈바닉 또는 SPD 본딩으로 접지 등전위 본딩을 얻는 것이다. 분리된 접지 시스템은 주의 해서 고려되어야 한다. 전력 시스템 레이아웃 · 상부 · 지하 · 또는 둘다 매설된 LV 전력 케이블은 가공 전력선보다 위험이 낮지만 매설된 케이블 근처에서 직격뢰 특히 고저 항 토양에서 상당한 과전압을 유발할 수 있다. 설계자는 매설된 케이블의 길이, 부지에서 일정 거리 떨어져 있는 상부 여부, MV 전력 유틸리티 네트워크가 싱부인지 여부를 고려해야 한다. LV 및 MV 전 력선 모두에서 전선의 총 길이와 높이는 관련 매개변수다. 더 길고 더 높은 선로는 낙뢰 접착의 위 험이 더 크므로 낙뢰 에너지를 시설이나 건물로 전달할 위험이 더 커진다. H.3.3 경제성 및 서비스 중단 서비스 저하 또는 서비스 손실 132 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
3e63bfa6-d5c5-4c27-a98a-00b75017c289 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 중단 및 손상은 비즈니스 운영에 어려움을 야기한다. 서비스 저하에는 직접적인 재정적 손실 외에 질적 요소가 포함될 수 있다. 예를 들어 광범위한 자동화 또는 컴퓨터화가 수반되는 경우 수동 작동 으로 되돌리는 것이 사실상 불가능할 수 있다. 운영 손실 여기에는 장비, 컴퓨터, 통신 및 정보 기술 시스템의 서비스 이용 불가와 관련된 운영 수익 및/또는 비즈니스 생산성 손실로 인한 실시간 비용이 포함된다. 긴급 서비스, 특정 중앙 정보 시스템과 같은 중요한 시스템은 운영 손실과 관련된 직간접 비용이 매우 높을 수 있다. 영리 기업은 고장 시간으로 직접적인 수익을 잃는다. 수리 및 복구 작업에 소요되는 예상 시간은 인 력, 예비 인력, 절차 및 정보의 가용성에 따라 달라진다. 장비 또는 시설의 수리 또는 교체 이는 장비 교체 및 재설치에 대한 직간접 비용을 포함한 물리적 손상 비용이다. 장비 부품의 점진적 인 열화는 겉보기에 무작위로 고장을 일으키는 반복적인 작은 크기의 펄스를 통해 발생할 수도 있다. 이러한 사고는 고장 시 낙뢰 또는 스위칭 사고와 즉시 또는 직접 연관되지 않을 수 있다. 이러한 누 적 효과 로 인해 정기 보수 또는 예방 유지보수의 비용이 증가할 수 있다. 긴급 서비스 장비를 파손하거나 사람을 다친 경우, 소방, 구급차, 경찰 등 기업, 개인 또는 지역사회에 비용이 드 는 긴급 서비스를 이용해야 할 수 있다. 화재 경보 시스템과 비상 서비스 통신의 고장은 그러한 서 비스의 효율성을 감소시킨다. 긴급 서비스는 보통 높은 수준의 보호를 요구할 것이다. H.3.4 안전 작업자 안전은 설계자와 설치자에게 중요한 문제다. 각 국가와 관련된 산업 보건 및 안전 규칙을 준 수해야 한다. 절연 파괴로 인해 사람에게 안전 위험이 있는 경우 SPD 사용을 고려해야 한다. H.3.5 보호 비용 · 설비의 설계 · 재료 및 장치 · SPD 설치 보호 비용에는 SPD, 공학 설계 및 감독, 전기 설비가 포함된다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. 133 | {}
b233de57-349e-42c4-ba95-40160e9056a4 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 부속서 I (참고) 시스템 스트레스 비고 이 부속서는 이 표준의 5 절 본문에 대한 확장이다. 정보가 특정한 항과 관련된 경우 다음과 같이 [xxx]로 나타낸다. I.1 낙뢰 과전압과 전류[5.2.2] I.1.1 SPD 의 필요성에 영향을 미치는 배전 시스템의 관점 I.1.1.1 일반사항 KS C IEC 60364-4-44:2007 의 443 절은 위험 분석에 따라 그리고 내부 스위칭으로 인한 서지의 위험이 없는 경우 SPD 를 사용할 필요가 없다는 것을 나타내 준다(H.1 참조). 이 지침은 통상적인 설비에 대한 특정 가정을 기반으로 한다. 고려하고 잇는 설비의 특정 계수가 보 통의 것이 아니라면, 서지 보호가 더 필요할 수 있다. 이러한 계수 중 일부는 I.1.1.2 및 I.1.1.3 에서 검토한다. 입력 서지의 가능성과 보호와 그 결과 간의 경제적 균형을 기초로 하여 위험 분석이 이루어져야 한다. I.1.1.2 낙뢰의 활동 낙뢰가 설비에 스트레스를 줄 위험성을 결정하는 데 사용할 수 있는 가장 유용한 수치는 국부 대지 뇌방전 밀도, NG 이다. 대지 뇌방전 밀도 NG 는 연간 km2 당 낙뢰 횟수다. 세계 여러 지역에서 IEC 62858:2015 를 준수하는 LLS(뇌 위치 시스템)에서 제공하는 데이터에서 이 값이 나올 수 있다. 대지 기반 뇌 위치 시스템이 없는 지역에서는 NG 맵을 사용해도 된다. 대지 기반 뇌 위치 시스템 또는 NG 맵이 없는 지역에서는 IEC 62305-2 를 참조한다. I.1.1.3 설비의 노출 특히 KS C IEC 60364-4-44:2007 의 443 절에서 고려하지 않은 직격뢰와 간접뢰의 경우에는 지중 케이 블에 의해 전력이 공급되는 곳에서도 이 케이블이 설비를 보호하기에 충분한 것은 아니다. 이것이 바로 지중 케이블에 의해 전력이 공급된다는 그 자체만으로는 SPD 의 필요성을 결정할 수 없는 이유 이다. I.1.2 구조물 내의 서지 전류 분포 자세한 내용은 KS C IEC 62305-1 및 KS C IEC 62305-4 를 참조한다. 비고 1 뇌 임펄스 전류는 두 가지 중요 요소를 결합한다. 첫 번째는 유도 효과 에 의한 전압 값을 결 134 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
2054a93b-71f6-4e23-930c-fb15367a8c04 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 정하는 데 유용한 빠른 상승 시간이다. 두 번째는 본질적으로 타격시 에너지와 관련이 있는 긴 지속 시간이다. 긴 지속 시간에는 고주파 효과 가 존재하지 않고, 따라서 분포를 계산하는 데 저항이 사용된다. LPS 가 장착된 구조물에 SPD 를 설치하는 경우, SPD 에 대한 스트레스를 결정하기 위해 접지 DC 저 항 값(예를 들어 건물 및 배전 시스템의 접지, 배관 등)을 사용하여 계산하면 충분하다. 개별 평가(예를 들어 계산)가 가능하지 않은 곳에서는, 총 뇌전류(1)의 50 %가 구조물의 LPS 의 접지 단자에 흘러 들어가는 것으로 간주할 수 있다. 나머지 50 %의 전류(ls)는 외부의 도체 부분, 전선, 통 신선 등과 같은 구조물에 인입되는 설비에 분배된다. 각 설비에 흐르는 전류(h)값은 / = /s In 을 사용하 여 평가할 수 있는데, 이때 n 은 인입되는 설비의 수이다. 비차폐 케이블의 개별 도체에 흐르는 전류 lv 를 평가하기 위해 케이블 전류 /를 도체의 수 m 으로 나 눈다(lv = h/m). 차폐 케이블의 경우 직접 또는 SPD 를 통하여 양단이 접지에 연결하여야 한다. 이 경우 케이블 뇌 전류의 대부분(통상 50 %)은 차폐로 흐르고 전류의 더 낮은 부분은 내부 도체를 통해 흐른다. 모든 경우에 SPD 는 차폐 본딩 점과 최대한 가깝게 설치해야 한다. 비고 2 SPD 의 /imp 또는 Imax 의 우선 값은 lv 에 상응한다. 가공선에 대한 직격뢰도 유사한 방식으로 고려할 수 있다. 1.2 스위칭 과전압[5.2.3] 스위칭 서지에 의해 일어나는 스트레스에 대한 자세한 내용은 C.3 을 참조한다. I.3 일시적인 과전압 UTov[5.2.4] LV 시스템의 고장으로 인해 발생하는 일시적인 과전압은 두 가지 요소 k1 및 k2 로 정의 할 수 있다. · k1 은 공칭 시스템의 표준 전압에 대한 최대 전압의 비다. k1 은 일반적으로 1.05 에서 1.1 사이에 있 다. 여기에는 정상적인 전압 변동 수준이 포함된다. Ucs = k1 x Uo · k2 는 전력 시스템의 Ucs 이상에서 발생하는 전력 시스템 과전압의 최대 크기이다. 고장이 일어나지 않은 상의 전압은 3 상 저압 시스템에서 고장이 발생하면 1.25 에서 이론적인 값인 V3 까지 변할 수 있다. 비고 1 단상, 3 선식(분할상) 시스템 k2 는 2 까지 올라갈 수 있다. 전체적인 일시적 과전압은 다음과 같이 표현할 수 있다. UTOV(LV)= k1 xk2x U0 = k2 x Ucs 일시적인 과전압은 일반적으로 저압 배전 시스템 사고, 커패시터 스위칭, 모터의 기동, 정지 등에 의 해 발생한다. 이러한 과전압은 지속 시간이 짧다. 3 상 배전 시스템의 고장으로 인해 발생하는 과전압 은 0.05 초 미만에서 최대 5 초까지 지속된다. 중성선 연결이 불량한 단상 모터를 기동할 때 일반적으 로 최대 5 초동안 과도한 과전압이 발생할 수 있다. 커패시터 스위칭 및 전압 조정은 5 초 이상의 지 135 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
6a5a96c1-be92-45ef-9949-a617c98ee364 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 속 시간으로 과전압을 생성하지 않아야 한다. 따라서 이 표준에서는 일시적인 과전압 지속 시간을 0.05 초에서 5 초로 선택되었다. 비고 2 일부 네트워크에서는 고압 시스템(UTOV(HV))의 고장으로 인해 Uo + 1 200 V 의 단시간(5 초 미만) 일시 과전압을 고려할 필요가 있다(KS C IEC 60364-4-44 참조). 이러한 높은 전압 값이 SPD 의 고장으로 이어질 경우, 이 고장으로 인해 인력 또는 장비 또는 설비에 위험이 발생하지 않는지 확인하기 위해 적절한 시험을 수행한다. Uo + 1 200 V 의 이 값은 최대 5 초에 대한 일시 적인 과전압의 최댓값이다. 저압 설비 및 고압 시스템의 접지 시스템 유형에 따라 이 값이 존재할 수도 있고 없을 수도 있다(부속서 E 참조). 또한 5 초보다 긴 지속 시간을 갖는 일시 적 과전압은 KS C IEC 60364-4-44 에 정의 되어 있으며 이 과전압은 긴 지속 시간으로 인해 고 장이 발생할 수도 있다. 이 표준에서는 LV 시스템의 고장으로 발생하는 TOV 를 UTOV(LV)로, HV 시스템의 고장으로 발생하는 TOV 를 UTOV(HV)로 나타낸다. 위에 주어진 공식에 기초하여 이론적으로 네트워크에서 UTOV 의 전압 대 시간 곡선을 그릴 수 있다. 실제로 네트워크, 특히 SPD 설치 지점에서 UTOV 의 실제 값이 항상 알려져 있지는 않다. 이러한 경우 에는 몇 가지 대표적인 지점만 알려져 있기 때문에 위에서 언급한 곡선을 그리는 것은 다소 어렵다. 일반적으로 단지 표준화된 최댓값만 알려져 있고 곡선은 일부 지점에 대해서만 그린다. SPD 선정에 특히 관심을 가져야 하는 값은 200 ms 와 5 s 다. UTOV 의 최대 규정값은 그림 14 를 참조한다. 136 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
be9a98d2-03ec-4ff5-8606-ed5cc9b1db3f | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 부속서 J (참고) SPD 의 응용 비고 이 부속서는 이 표준의 7 절 분문을 확장한다. 정보가 특정한 항과 관련된 경우 다음과 같이 [xxx]로 나타낸다. J.1 위치와 SPD 에 의한 보호[7.1] J.1.1 보호 가능 모드와 설비[7.1.3] 그림 J.1 은 대체 가능한 접지 옵션(그림 J.5)를 보여준다. 비고 1 가장 좋은 방법은 설비의 보호 수준과 스트레스를 모두 낮게 유지하도록 2 개의 옵션을 모두 사용하고 PE 연결점과 SPD 의 공통 접지점 사이의 연결을 가능한 한 짧게 유지하는 것이다. 허용 가능한 설치는 다음 다섯 단계의 과정을 거친다. 비고 2 다음 단계는 주로 선로 또는 중성선과 접지 사이에 접속된 고정 SPD 에 대해서 유효하다. 다 른 SPD 에는 다른 규칙이 필요하다. a) 방전 전류의 경로를 결정한다. b) 기기의 단자에 추가로 전압 강하를 일으키는 전선을 확인한다[그림 J.6a) 및 그림 J.6 b)]. 비고 3 그림 J.6 에서 Ures 는 I 등급과 II 등급에 따라 시험된 SPD 의 잔류 전압 또는 일반적으로는 제한 전압이다. c) 불필요한 유도 루프를 없애기 위해 각 장치의 도체 경로를 조절한다[그림 J.6c), 그림 J.6d) 및 그 림 J.7 참조]. 접지점을 하나로 할 수 없으면 그림 J.6 d)와 같이 두 개의 SPD 가 필요하다. d) 장치와 SPD 간의 등전위 본딩을 한다. e) 협조 요구사항에 따라 SPD 를 선정한다. 설비의 보호되는 부분과 보호되지 않은 부분 사이의 유도 결합을 제한하기 위해서 필요한 수단을 강 구해야 한다. 상호 인덕턴스는 유도 전원과 희생되는 회로 사이를 분리, 루프 면적을 제한하며 루프 사이의 각도를 선택해서 감소시킬 수 있다(그림 J.7 참조). 전류가 흐르는 전선이 루프 영역의 일부일 경우 이 전선을 케이블 가까이에 배치하여 유도 전압을 줄일 수 있다[그림 J.7 a) 참조]. 일반적으로 보호되는 선로를 그렇지 않은 선로와 분리하는 것이 좋다. 전력선과 통신선 사이에 전류 에 의한 교차 결합을 피하기 위해서 필요한 수단을 강구해야 한다[그림 J.7b) 참조]. EMC 의 측면에서 허용되는 SPD 설치의 몇 가지 예는 그림 J.7 을 참조한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. 137 | {}
f67f8276-12ca-4102-b980-c941394c6e3d | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) 2 1 L1 L2 L3 PE PEN N F 5b 4 SPD SPD SPD 5a 6 6 3 R RA 식별부호 1 설비의 기점 2 배전반 3 주 접지 단자 또는 바 4 서지보호장치 5 서지보호장치의 접지 연결, 위치 5a 또는 5b 6 보호되는 장비 F SPD 제조자에 의하여 지시된 보호 장치(예를 들면 퓨즈, 분리기, RCD) RA 설비의 접지 전극(접지 저항) Rg 전력 시스템의 접지극(접지 저항) 그림 J.1 - TN 시스템에서의 서지보호장치 설치 138 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c4fe6664-3c5c-4923-a5a4-216b4596aa2c | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) 2 1 L1 L2 I△ 。 L3 9 PE N N 7 F 4 SPD SPD SPD SPD 5b 5a 6 3 Rg RA 그림 J.2a -연결 유형 1 식별부호 1 설비의 기점 2 배전반 3 주 접지 짧은 파형 또는 바 4 서지보호장치 5 서지보호장치의 접지 연결, 5a 또는 5b 6 보호되는 장비 7 누전 차단기(RCD) F SPD 제조자가 표시한 보호 장치(예를 들면 퓨즈, 분리기, RCD) RA 설치의 접지극(접지 저항) Rg 전력 시스템의 접지극(접지 저항) 그림 J.2 - TT 시스템에서의 서지보호장치 설치(RCD 의 SPD 하부) 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 139 | {}
cba9e171-fa61-48cd-bea6-45d45b454164 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) 2 1 L1 L2 IA L3 PE N N 7 F 4 SPD SPD SPD 5b SPD 5a 6 3 Rg RA 그림 J.2b - 연결 유형 2 (CT2) 식별부호 1 설비의 기점 2 배전반 3 주 접지 단자 또는 바 4 서지보호장치 5 서지보호장치의 접지 연결, 5a 또는 5b 6 보호되는 장치 7 누전 차단기(RCD) F SPD 제조자가 표시한 보호 장치(예를 들면 퓨즈, 분리기, RCD) RA 설치의 접지극(접지 저항) Rg 전력 시스템의 접지극(접지 저항) 그림 J.2 - TT 시스템에서의 서지보호장치 설치(RCD 의 SPD 하부)(계속) 비고 연결 유형이 있는 SPD(CT1)는 RCD 의 상부에서 사용할 수 없다. 140 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
cbe9e475-51c1-482d-819c-95475eca7237 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) 2 7 L1 L2 0 I△ L3 。 9 9 PE 9 N N 7 5b 4 SPD SPD SPD →← 4a 5a 6 3 Rg RA 식별부호 1 설비의 기점 2 배전반 3 주 접지 단자 또는 바 4 서지보호장치 4a KS C IEC 60364-5-53 의 2.3.2 또는 스파크 갭에 따른 서지보호장치 5 서지보호장치의 접지 연결, 5a 또는 5b 6 보호되는 장치 7 누전 차단기(RCD) F SPD 제조자가 표시한 보호 장치(예를 들면 퓨즈, 분리기, RCD) RA 설치의 접지극(접지 저항) Rg 전력 시스템의 접지극(접지 저항) 그림 J.3 - TT 시스템(RCD 의 SPD 상부)에서의 서지보호장치 설치 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 141 | {}
0a3234d3-f672-40d9-9e5c-4c0e88b6ec2d | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) 2 1 L1 L2 I△ L3 PE F 5b 4 SPD SPD SPD 5a 6 3 RA 식별부호 ¦ 1 ¦ 설비의 기점 ¦ ¦ --- ¦ --- ¦ ¦ 2 ¦ 배전반 ¦ ¦ 3 ¦ 주 접지 단자 또는 바 ¦ ¦ 4 ¦ 서지보호장치 ¦ ¦ 5 ¦ 서지보호장치의 접지 연결, 5a 또는 5b ¦ ¦ 6 ¦ 보호되는 장치 ¦ ¦ F ¦ SPD 제조자가 표시한 보호 장치(예를 들면 퓨즈, 분리기, RCD) ¦ ¦ RA ¦ 설치의 접지극(접지 저항) ¦ ¦ Rg ¦ 전력 시스템의 접지극(접지 저항) ¦ ¦ O/ ¦ 개회로 혹은 저항 ¦ 그림 J.4 - 중성선이 없는 IT 시스템에서의 서지보호장치 설치 142 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
9b003f89-dd5e-4394-bbe9-b59609270bdd | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) a b TN - C-S Entrance SPD SPD SPD SPD SPD SPD SPD SPD SPD PEN N SPD SPD PE 식별부호 장치와 설비 인입구 사이의 거리가 멀 경우 추가 SPD 연결 가능(7.1.4 참조): a SPD 가 L-N 및 N-PE 에 연결됨 b SPD 가 L-PE 및 N-PE 에 연결됨 그림 J.5 - TN C-S 시스템에서 설비 인입구에 일반적으로 설치되는 SPD ![image](/image/placeholder) a I b I Eq Eq △U1 Ue Ue Ures SPD Ures SPD △U2 Ue = Ures Ue = Ures + Uw1 + Uw2 C d 6 6 SPD Eq1 Eq2 SPD Eq1 SPD Eq2 식별부호 Eq 장치 구성 a, C, d 는 채택 가능하다. 구성 b 는 △U1 과 △U2 가 충분히 낮으면 채택할 수 있다. 비고 전류 /는 SPD 로 흘러 들어가고 이 전류에 의해서 생긴 자기장이 장치 단자에 연결된 리드에 의해 형성된 루프로 들어간다. 이것은 SPD 의 잔류 전압에 유도 전압을 더하는 효과 를 가진다. 이렇게 결합된 전압이 장치의 단자에 나타난다. 그림 J.6 - 1 포트 SPD 를 설치하는 일반적인 방법 143 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
95b87e6d-4188-4f29-b0be-a152fed138c9 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 a ![image](/image/placeholder) Eq I i SPD I 1 Eq I I SPD I I Eq I SPD b i Load SPD ii SPD Load 식별부호 a 전자 결합 i 나쁜 예 루프 면적이 넓어 di/dt 에 의해 생긴 d�/dt 를 많이 포함한다. ii 좋은 예 루프 면적이 좁아 d�/dt 를 적게 포함한다. iii 가장 좋은 예 케이블 차폐에 의해 차폐드 내부의 d⌀/dt = 0 이 된다. b 유도 결합 i 나쁜 설치 *로 표시된 점에서 유도 결합이 일어난다. ii 좋은 설치 SPD 의 상부와 하부 케이블이 잘 분리되어 있다. 그림 J.7 - EMC 측면에서 볼 때 채택 가능하고 채택 불가능한 SPD 의 설치 예 144 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
ffe82a6a-efec-47ce-b69e-d35a4b49c854 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 J.1.2 진동 현상이 보호 거리에 미치는 영향[7.1.4.2] 일반적으로 보호 대상 장비와 가까운 곳에 SPD 를 사용하는 것만으로는 충분하지 않다. EMC 면에서 볼 때 전력 인입구에 SPD 를 설치하는 것이 더 좋다(서지 전류로 인한 전자파 교란을 피하기 위해 인입구에서 그 전류를 분산시키는 것이 더 좋다). 그리고(도체 간 방전을 방지하기 위해) 설비를 보 호하기에도 인입구에 SPD 를 설치하는 것이 더 좋다. 장치가 인입구에 설치된 SPD 의 보호 거리 내 에 있지 않다면, 필요한 경우 장치와 가까운 곳에 다른 SPD 를 설치해야 한다. 그런 다음 협조에 대 한 검토가 필요하다(7.2.7 참조). 추가로 서지 보호가 필요한 이유는 서지 임펄스에 의해 일어나는 진동 또는 진행파가 보호되는 장치 에서 예상보다 높은 전압을 일으킬 가능성이 있기 때문이다. 그림 J.8 은 그러한 시스템의 물리적, 전 기적 회로도의 예를 보여준다. ![image](/image/placeholder) U u'= ku a) d b) Surge (L,r) Surge L C Eq SPD SPD (C) 그림 J.8 - 보호 대상 장치가 보호 장치인 SPD 로부터 떨어져 있는 시스템의 물리적 및 전기적 회로도 장비에 걸리는 전압은 서지 주파수와 도체 길이에 따라 달라진다. r 의 값에 따라 L 과 C 사이의 진동 은 장비 단자에 걸리는 전압 u'를 최대 ku 까지 증가시킬 수 있다. k 값은 많은 매개변수에 따라 달라 진다. 실제로 부하의 임피던스가 큰 장비에서 k 는 2 보다 작다. 그림 J.9 에 주어진 회로는 부하 정전 용량이 5nF 인 장치로부터 떨어진 곳에 설치된 금속 산화 배리 스터(MOV) SPD 에 인가되는 5kA 8/20 임펄스를 발생하는 서지 전원을 나타낸다. 이 회로는 시뮬레이 션 결과 그림 J.10 에 주어진 응답이 나왔다. 이것은 보호 대상 장비의 단자에 걸리는 전압이 SPD 단 자 전압의 2 배에 이를 수 있는 방법을 보여준다. ![image](/image/placeholder) 10m 5kA 8/20 C=5nF 그림 J.9 - 금속 산화 배리스터(MOV) SPD 와 보호 대상 장치 사이의 가능한 진동 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 145 | {}
162a3e02-0699-430f-9e70-af6a33aac1c1 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 Chart Type: bar 0 1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 21 22 23 24 25 26 27 28 29 30 31 32 33 34 35 36 37 38 39 40 41 42 43 44 45 46 47 48 49 50 51 52 53 54 55 56 57 58 59 60 61 62 63 64 65 66 67 68 69 70 71 72 73 74 75 76 77 78 79 80 81 82 83 84 85 86 87 88 89 90 91 92 93 94 95 96 97 98 99 100 101 102 103 104 105 106 107 108 109 110 111 112 113 114 115 116 117 118 119 120 121 122 123 124 125 126 127 128 129 130 131 132 133 134 135 136 137 138 139 140 141 142 143 144 145 146 147 148 149 150 151 152 153 154 155 156 157 158 159 160 124V 125V 126V 127V 128V 129V 130V 131V 132V 133V 134V 135V 136V 137V 138V 139V 140V 141V 142V 143V 144V 145V 146V 147V 148V 149V 150V 151V 152V 153V 154V 155V 156V 157V 158V 159V 160 item_01V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 0V 식별부호 VSPD SPD 에서의 전압 Veq 장비 단자에서의 전압 그림 J.10 - 전압 배가의 예 J.1.3 보호 구역 개념[7.1.4.6] 건물의 전력 배전 시스템을 보호 구역과 서지보호장치의 할당으로 재분할하는 예를 직격뢰에 대한 KS C IEC 62305-4 에 따른 그림 J.11 이 보여주고 있다. ![image](/image/placeholder) LPZ 。 A LPZ OB SPD SPD PZ 1 PZ2 PZ 1 SPD SPD PZ 1 PZ2 PZ3 PZ2 PDS SPD SPD SPD SPD PZ 1 PZ2 PZ 3 PZ2 6 Q LPZ OB RA 식별부호 LPZ 뇌 보호 구역 PDS 배전 시스템 SPD 서지보호장치 그림 J.11 - 보호 구역에 따른 건축물 소분할 146 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
9773d5e5-3ee1-4ff8-98ad-8f63c3472e2a | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 뇌 보호 구역(LPZ)은 다음과 같이 정의 된다. · 뇌 보호 구역 0A (LPZ 0A, KS C IEC 62305-4) 그 영역 내의 품목이 직격뢰의 여향을 받으며, 따라서 최대 뇌전류까지 흘러야 하는 구역. 여기에 서는 감쇠되지 않은 전자기장이 발생한다. · 뇌 보호 구역 0B (LPZOB, KS C IEC 62305-4) 그 영역 내의 품목이 직격뢰의 여향을 받지는 않지만, 감쇠되지 않은 전자기장이 발생하는 구역. 감쇠되지 않은 전도성 뇌전류 및 스위칭 서지가 발생한다. · 뇌 보호 구역 1 (LPZ1) 품목이 부분적인 직격뢰의 영향을 받고 있는 영역. 전도된 임펄스 뇌전류 및/또는 스위칭 서지는 LPZ 0A 또는 LPZ OB 에 비해 감소한다. · 뇌 보호 구역 2(LPZ2) 남아 있는 뇌 임펄스 전류 및/또는 스위칭 서지가 LPZ 1 에 비해 감소한다. · 뇌 보호 구역 3(LPZ3) 진동이나 자기장 결합에 의한 서지, 내부 스위칭 서지가 LPZ 2 에 비해 감소한다. LPZ 경계에 서지보호장치를 설치함으로써 전도된 위협적인 매개변수가 줄어들었다. 이러한 SPD 간 의 협조는 7.2.7 에 따라 수행되어야 한다. 이들 장치의 성능 매개변수는 설치된 장소의 전도된 위협 적인 매개변수에 맞아야 한다(7.2.2 및 7.1.1 참조). 비고 KS C IEC 62305-4 에 따라 I 등급 시험된 SPD 를 사용해야 하는 경우 그 SPD 를 LPZ 1 과 LPZ 0B 경계에 설치해야 한다. 7.1.4 에 따라 SPD 가 설치될 때마다 새로운 LPZ 가 생성된다. J.2 SPD 의 선정 J.2.1 Uc 의 선정[7.2.2.1] 대부분의 SPD 에 대해 지속 시간이 5 초 이상인 일시적 과전압을 영구적인 스트레스로 간주해야 한다. 따라서 정상적인 조건과 5 초 이상 지속되는 고장 조건(일시적인 과전압)을 고려하여 Uc 를 선정해야 한다. a) 정상적인 조건 1) 상과 중성선 사이 상과 중성선 사이에 있는 SPD 의 Uc 는 Ucs (특히 일반적으로 U0 의 1.10 배: 전압 규정의 10 % 또는 SPD 의 성능 저하와 다른 비정상적인 시스템 조건을 감안하여 5 %의 여유를 생각한다면 1.15) 이상이어야 한다. 2) 상과 상 사이 SPD (일반적으로 U0 에 V3 을 곱한 것은 한다. 상 사이의 Uc 는 Ucs 1.10 배) 이상이어야 비고 1 경우에 따라 전압 변동 한도(예를 들면 전압 변동이 계량기에서만 정의 되는 초대형 건 물의 경우)에 따라 Ucs 는 위에 주어진 일반적인 제한(각각 10 %와 10 % x V3)을 초과 할 수도 있다. 147 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
4e980750-19ec-4c59-8f33-542eb84a54ed | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 어떤 경우에는 전압 변동 폭이 더 좁아진다(예를 들면 5 %). 이 경우 더 낮은 값이 충분할 수 도 있다[예를 들면 Uc 가 단지 U0 의 1.05 배보다 높을 수도 있다(각각 1.05 x V3 x Uo)]. 3) 상과 접지 또는 중성선과 접지 사이 · TT 및 TN 시스템에서는 상과 접지 또는 중성선과 접지 사이의 SPD Uc 가 Ucs 와 같거나 높아 야 한다(일반적으로 U0 의 1.10 배). · IT 시스템의 경우에는 아래의 비정상적인 조건을 참조한다. 비고 2 전력이 변압기의 2 차측에 중간 탭이 있는 변압기에 의해 공급된다면, Uc 가 2 개의 값을 가진다. Uc 중 하나는 Ucs 의 1.0 배이고 다른 하나는 (V3)12 x Ucs 이다. 고조파가 있으면, 서비스 전압의 피크 값이 증가할 수 있다. 따라서 이러한 고조파가 없을 때 의 Uc 에 비해 Uc 값을 증가시킬 필요가 있다. b) 비정상적인 조건(고장 상태) 때로는 상과 접지 사이에 연결된 SPD 에 대한 Uc 를 선정할 때 특정 고장 상황을 고려해야 할 수 도 있다. 이는 시스템에 고장이 발생할 때 너무 많은 SPD 가 파괴되는 것을 방지하기 위한 것이다. IT 시스템의 경우 반드시 그런 고장 상황을 고려해야 한다. TT 및 TN 시스템이 접지 고장 상태에 있을 때, 상과 접지 사이의 전압이 Ucs 를 초과 할 수 있다. 이것은 고압 시스템 또는 저압 게통의 고장으로 인해 발생하고, 전압의 최대 크기와 접지에 따라 달라진다. 이 주제에 대한 자세한 내용은 5.2.4.2 를 참조한다. 따라서 Uc 는 고장 조건에서 나타나 는 실제 전압에 따라 선정한다. 시스템에서 어떠한 고장이 발생하더라도 SPD 가 손상되지 않을 만 큼 Uc 값을 높게 하면 안 된다. 그렇게 하면 보호 레벨이 떨어지기 때문이다. 일반적으로, 시스템 상과 무관하게, 적절한 값은 Uc 를 1.5 x Uo 보다 높게 하는 것이다. IT 시스템이 접지 고장 상황에 있을 때, 상과 접지 사이의 전압은 일반적으로 V3 x U0 이다. 저압 시스템에서 이런 고장은 영구적인 상황으로 간주될 정도로 충분히 길게 지속될 수도 있다. 이 경우에 Uc 를 상과 상 전압보다 더 높게 하는 것을 강력하게 권고한다. SPD 의 Uc 와 전력 시스템의 공칭 전압 사이의 관계에 대한 예는 부속서 B 에 나타낸다. J.2.2 협조 문제[7.3.7.2] 문제를 더 잘 설명하기 위해 그림 J.12 는 인덕턴스에 의하여 분리되어 있는 2 개의 금속 산화 배리스 터(MOV)의 에너지 협조의 일반적인 예를 보여준다. SPD2 는 더 낮은 Up 값과 In 값을 가진다. 서지 전면의 인덕턴스 효과 로 인해 대부분의 전류는 SPD1 으로 흘러 들어가고 SPD2 의 전류는 인덕턴스와 SPD2 의 특성에 의해 주어진 시정수에 따라 점진적으로 증가한다. 이러한 방식으로 시간이 지남에 따라 점점 더 많은 전체 전류가 SPD2 를 통해 흐르게 된다. 그림 J.12 는 전체 전류, SPD1 및 SPD2 에 흐르는 전류, 그리고 SPD1 및 SPD2 에 걸리는 전압을 보 여준다. · 이 응용 지침서에서 최대 에너지 내력(Emax)은 SPD 의 성능 저하 없이 견딜 수 있는 최대 에너지로 정의 된다. 시험 결과(I 등급의 경우 /imp, II 등급의 경우 In 에서의 동작 책무 시험을 통해 측정된 에너 지)로부터 얻을 수 있거나 제조자에 의해 주어지는 In (II 등급 시험) 또는 /imp (1 등급 시험) 또는 Umax 와 같은 정보를 고려하여 계산할 수 있다. 148 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
708fd3df-2ec3-4ad4-89a2-adda79b6c50c | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 Chart Type: line U U2 item_01 2kV 0kV Time 식별부호 U1 앞에 있는 SPD 단자의 잔류 전압 U2 두 번째 SPD 단자의 잔류 전압 a) - 배리스터의 잔류 전압 Chart Type: line I I2 I3 item_01 10kA 0kA 0kA 식별부호 斤 전체 전류 /1 앞에 있는 SPD 의 전류 /2 두 번째 SPD 의 전류 b) - 두 배리스터 사이의 전류 분배 그림 J.12 - 두 개의 금속 산화 배리스터(MOV)의 협조 임피던스 Z 에 해당하는 두 SPD 사이의 거리 d 는 결합 방지 요소로 사용될 수도 있다. 제한형 SPD 의 경우 이런 결합 방지 임피던스는 일반적으로 삼각파(예를 들면 8/20)에만 효과 적이 다. 긴 파형(예를 들면 10/350)의 경우 케이블에 의해 생성된 이 자연적인 결합 방지 임피던스로는 좀처럼 만족할 수가 없다. 적절한 협조를 제공하려면 추가 분리 부품이 필요할 수도 있다. 앞에 있는 SPD 가 스위칭 유형인 경우 두 가지 다른 특성을 고려해야 한다. 맹점이 있을 수 있다. 즉, /imp 보다 낮은 전류에서 갭 단자의 전압이 너무 낮아 갭이 스파크오버 를 일으키지 못하고, 따라서 두 번째 SPD 를 보호할 수도 없는 상태가 있을 수 있다. 갭의 스파 크오버가 서지 전면에서 발생하는 것이 중요한다. 긴 규약 파두장의 경우 결합 방지 요소는 8/20 또는 10/350 파에 비해 덜 효과 적일 수 있다. 149 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
3af7ea1a-eb53-448b-9d60-fa452c6a66c1 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 이러한 긴 규약 파두장은 현재 IEC 에서 연구 중이다. 일반적으로 두 가지 형태의 서지에 대하여 협조를 다룰 필요가 있다. · 긴 파형 서지와 의 협조(예를 들면 I 등급 시험에 사용된 것) · 짧은 파형 서지와 의 협조(예를 들면 II 등급 시험에 사용된 것) 비고 SPD 의 최대 에너지 내력은 적어도 두 SPD 가운데 낮은 SPD 의 에너지 내력과 같다. 새로운 SPD(SPD2)가 기존의 SPD(SPD1)를 이미 포함하는 시스템에 연결될 때, 적절한 협조가 이루 어지도록 해야 한다. J.2.3 실제 예[7.2.7.2] 설비에서 위의 간단한 예보다 협조를 연구하기는 항상 훨씬 복잡하다. 실제에서는 · 리드 길이 또는 분리기와 같은 추가 장치가 있으면 그 구성에 인덕턴스를 증가시킬 수도 있다. 많 은 SPD 간의 전류 분배도 연구가 필요하다. ==> 실제 설비 구성이 필요하다. · SPD 에 사용되는 부품의 특성 허용값이 어떤 특정 전류에 대한 실제 잔류 전압을 불확실하게 할 수도 있다. 또한 보통 제조자로부터 알 수 있는 값은 보호 레벨 Up 인데 여유가 포함되어 있어서 그 실제 전압은 표시된 것보다 25 %나 더 낮을 수 있다. · SPD 의 에너지 내력 Emax 는 긴 파형과 짧은 파형에 따라 달라질 수 있다. 일반적으로 이러한 값은 등급 시험에 의하여 주어진다(I 등급 ---> 긴 파형, II 등급 ---> 짧은 파형). 때로는 이 에너지 내력이 주어지지 않아 계산이 필요하다. J.3 LPS 로 보호되는 건물의 경우 I 등급 시험된 SPD 에 대한 /imp 의 간단한 계산 전기 설비를 관리하는 건물에 LPS 가 장착된 경우, 인입구에 위치한 SPD 의 전류 및 전류 내력 /imp 의 전류 분배를 계산하기 위해 IEC 62305 시리즈에 주어진 규칙을 상기할 필요가 있다. IEC 62305 시리즈에 따르면, LPS 가 건물에 있는 즉시 설비 인입구에서 등전위 SPD 를 사용할 필요가 있다. 이 SPD 는 I 등급 시험되었으며 주로 10/350 내력 /imp 로 정의 된다. LPS 의 뇌 보호 레벨(LPL)에 따라 이 값은 I ~ IV 이며, 전류는 하나의 전력 선로만 장착되고 다른 모 든 선로 및 도관이 존재하지 않거나 무시되는(가장 심각한 경우) 간단한 경우에서 다음 공식을 통해 계산할 수 있다. 실제로 위의 방법은 하나의 설비만 시설에 들어온다고 가정한다. 일반적으로 뇌전류의 일부를 시설 에서 멀리 옮기는 설비(예를 들면 금속 파이프)가 더 많을 수 있으며 이로 인해 /imp 값은 낮아질 것 이다. 아래 표에서 /imp 값은 최댓값이다. 뇌전류 분배에 대한 추가 정보는 KS C IEC 62305-1 을 참조한 다. 이 경우 피뢰시스템의 LPL 에 연결된 최대 전류는 선로의 도체 수로 균등하게 나누고 2 로 나눈다(전 류의 50 %가 접지 시스템에 흐르는 것으로 가정함). 따라서 SPD 가 각 보호 모드에 대해 견뎌야 하는 임펄스 전류 /imp 는 다음 공식으로 쉽게 계산할 수 있다. Iimp=LPL / (2n)에 해당하는 최대 전류 150 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
5429ed0d-a4a8-47e2-8ef2-ad8ba4ca288a | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 이렇게 하면 해당 구성을 사용할 수 있는 경우 CT1 및 CT2 연결 구성 모두에 대해 다음과 같은 /imp 표가 나온다. 오래된 설비의 경우 또는 전기 계약자가 설치 세부사항을 알지 못하는 경우, 최악의 경 우를 가정해야 한다(LPLI). 표 J.1 은 가장 일반적인 LV 전원 시스템에 대한 것이다. 그러나 이러한 값은 일부 국가에서 매우 특 정한 LV 시스템 구성에 따라 직접적으로 좌우된다. 표 J.2 는 표 J.4 에 따른 LV 시스템의 경우 일본 에서 추가적인 일반 LV 전력 시스템의 예를 제공한다. 표 J.1 - /imp 의 값 결정 ¦ ¦ ¦ ¦ LV 시스템(단상 및 3 상 시스템) ¦ LV 시스템(단상 및 3 상 시스템) ¦ LV 시스템(단상 및 3 상 시스템) ¦ LV 시스템(단상 및 3 상 시스템) ¦ LV 시스템(단상 및 3 상 시스템) ¦ LV 시스템(단상 및 3 상 시스템) ¦ LV 시스템(단상 및 3 상 시스템) ¦ LV 시스템(단상 및 3 상 시스템) ¦ LV 시스템(단상 및 3 상 시스템) ¦ LV 시스템(단상 및 3 상 시스템) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ TT ¦ TT ¦ TT ¦ TN-C ¦ TN-S ¦ TN-S ¦ TN-S ¦ 중성선이 없는 IT ¦ 중성선이 있는 IT ¦ 중성선이 있는 IT ¦ ¦ ¦ ¦ ¦ LPL ¦ LPL 에 해당하는 최대 전류 ¦ 도체 수 n ¦ 연결 유형 ¦ 연결 유형 ¦ 연결 유형 ¦ ¦ 연결 유형 ¦ 연결 유형 ¦ 연결 유형 ¦ 연결 유형 ¦ 연결 유형 ¦ 연결 유형 ¦ ¦ LPL ¦ LPL 에 해당하는 최대 전류 ¦ 도체 수 n ¦ CT1 ¦ CT2 ¦ CT2 ¦ ¦ CT1 ¦ CT2 ¦ CT2 ¦ CT1 ¦ CT2 ¦ CT2 ¦ ¦ LPL ¦ LPL 에 해당하는 최대 전류 ¦ 도체 수 n ¦ L-PE N-PE ¦ L-N ¦ N-PE ¦ L- PEN ¦ L-PE N-PE ¦ L-N ¦ N-PE ¦ L-PE ¦ L-N ¦ N-PE ¦ ¦ I 또는 알려 지지 않음 a ¦ 200 kA ¦ ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ ¦ I 또는 알려 지지 않음 a ¦ 200 kA ¦ 5 ¦ NA ¦ NA ¦ NA ¦ NA ¦ 20 ¦ 20 ¦ 80 ¦ NA ¦ NA ¦ NA ¦ ¦ I 또는 알려 지지 않음 a ¦ 200 kA ¦ 4 ¦ 25.0 ¦ 25.0 ¦ 100.0 ¦ 25.0 ¦ NA ¦ NA ¦ NA ¦ NA ¦ 25.0 ¦ 100.0 ¦ ¦ I 또는 알려 지지 않음 a ¦ 200 kA ¦ 3 ¦ NA ¦ NA ¦ NA ¦ NA ¦ 33.3 ¦ 33.3 ¦ 66.7 ¦ 33.3 ¦ NA ¦ NA ¦ ¦ I 또는 알려 지지 않음 a ¦ 200 kA ¦ 2 ¦ 50.0 ¦ 50.0 ¦ 100.0 ¦ 50.0 ¦ NA ¦ NA ¦ NA ¦ NA ¦ 50 ¦ 100.0 ¦ ¦ II ¦ 150 kA ¦ ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ ¦ II ¦ 150 kA ¦ 5 ¦ NA ¦ NA ¦ NA ¦ NA ¦ 20 ¦ 20 ¦ 80 ¦ NA ¦ NA ¦ NA ¦ ¦ II ¦ 150 kA ¦ 4 ¦ 18.8 ¦ 18.8 ¦ 75.0 ¦ 18.8 ¦ NA ¦ NA ¦ NA ¦ NA ¦ 18.8 ¦ 75.0 ¦ ¦ II ¦ 150 kA ¦ 3 ¦ NA ¦ NA ¦ NA ¦ NA ¦ 25.0 ¦ 25.0 ¦ 50.0 ¦ 25.0 ¦ NA ¦ NA ¦ ¦ II ¦ 150 kA ¦ 2 ¦ 37.5 ¦ 37.5 ¦ 75.0 ¦ 37.5 ¦ NA ¦ NA ¦ NA ¦ NA ¦ 37.5 ¦ 75.0 ¦ ¦ III 또 는 ≥ ¦ 100 kA ¦ ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ ¦ III 또 는 ≥ ¦ 100 kA ¦ 5 ¦ NA ¦ NA ¦ NA ¦ NA ¦ 10.0 ¦ 10.0 ¦ 40.0 ¦ NA ¦ NA ¦ NA ¦ ¦ III 또 는 ≥ ¦ 100 kA ¦ 4 ¦ 12.5 ¦ 12.5 ¦ 50.0 ¦ 12.5 ¦ NA ¦ NA ¦ NA ¦ NA ¦ 12.5 ¦ 50.0 ¦ ¦ III 또 는 ≥ ¦ 100 kA ¦ 3 ¦ NA ¦ NA ¦ NA ¦ NA ¦ 16.7 ¦ 16.7 ¦ 33.3 ¦ 16.7 ¦ NA ¦ NA ¦ ¦ III 또 는 ≥ ¦ 100 kA ¦ 2 ¦ 25.0 ¦ 25.0 ¦ 50.0 ¦ 25.0 ¦ NA ¦ NA ¦ NA ¦ NA ¦ 25.0 ¦ 50.0 ¦ a LPL 값을 알 수 없는 경우 최악의 경우를 가정한다. 식별부호 LPL 뇌 보호 레벨(위험 수준) n 전기 네트워크의 도체 수. TN 시스템(TN-C 및 TN-S)의 경우, n 은 활성 도체와 동일한 전류가 흐르는 PE(PEN) 도체를 포함한다. n = TN-S 시스템과 같은 3 상 + N 네트워크용 5 개 n = TT, TN-C 및 IT 시스템과 같은 3 상 + N 네트워크용 4 개 n = 단상 + TN-S 와 같은 N 네트워크용 3 개 또는 TT, TN-C 및 IT 시스템과 같은 분리된 중성선이 없는 3 상 IT 시스템 + N 네트워크용 3 개 CT1, CT2 이 표준에 따른 SPD 의 연결 모드(KS C IEC 60364-5-53 에 따라 CT1 연결 유형 A 및 B 에 해당하는 반면 CT2 는 연결 유형 C 에 해당한다. CT2 모드에서 SPD 로 보호되는 IT 시스템의 경우 중성선과 PE 도체 사이에 연결된 SPD 의 후속 전류 차단 정격은 상과 중성선 사이에 연결된 SPD 의 경우와 동일해야 한다. 설치 지점에서 중성선 단락 전류에 대한 예상 선로 이상이어야 한다(KS C IEC 60364-5-53). 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 151 | {}
2935bd7e-e1d3-4788-872e-811c16fd0de7 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 표 J.2 - 일본에서 사용되는 추가 시스템에 대한 /imp 값 결정 ¦ ¦ ¦ ¦ LV TT 시스템 ¦ LV TT 시스템 ¦ LV TT 시스템 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ LPL ¦ LPL 에 해당하는 최대 전류 ¦ 도체 수 n ¦ 연결 유형 ¦ 연결 유형 ¦ 연결 유형 ¦ ¦ LPL ¦ LPL 에 해당하는 최대 전류 ¦ 도체 수 n ¦ CT1 ¦ CT2 ¦ CT2 ¦ ¦ LPL ¦ LPL 에 해당하는 최대 전류 ¦ 도체 수 n ¦ L-PE N-PE 분포되어 (N 이 있는 경우) ¦ L-N ¦ N-PE ¦ ¦ I 또는 알려지 지 않음 a ¦ 200 kA ¦ ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ ¦ I 또는 알려지 지 않음 a ¦ 200 kA ¦ 3(분리된 중성선 없이 접지 된 3 상 Y 중간점) ¦ 33.3 ¦ NA ¦ NA ¦ ¦ I 또는 알려지 지 않음 a ¦ 200 kA ¦ 3(단상 - 분할 상 및 분리된 중성선이 있는 3 상 코너 접지 DELTA) ¦ 33.3 ¦ 33.3 ¦ 100,0 ¦ ¦ I 또는 알려지 지 않음 a ¦ 200 kA ¦ 2(단상 - 분리된 중성선이 없는 분할 상) ¦ 50 ¦ - ¦ - ¦ ¦ II ¦ 150 kA ¦ ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ ¦ II ¦ 150 kA ¦ 3(분산 중성선 없이 접지된 3 상 Y 중간점) ¦ 25.0 ¦ NA ¦ NA ¦ ¦ II ¦ 150 kA ¦ 3(단상 - 분할 상 및 분산 중성선이 있는 3 상 코너 접지 (델타) ¦ 25.0 ¦ 25.0 ¦ 75.0 ¦ ¦ II ¦ 150 kA ¦ 2(단상 - 분리된 중성선이 없는 분할 상) ¦ 37,5 ¦ - ¦ - ¦ ¦ III or IV ¦ 100 kA ¦ ¦ /imp [KA] ¦ /imp [KA] ¦ /imp [KA] ¦ ¦ III or IV ¦ 100 kA ¦ 3(분리된 중성선 없이 접지된 3 상 Y 중간점) ¦ 16.7 ¦ NA ¦ NA ¦ ¦ III or IV ¦ 100 kA ¦ 3(단상 - 분할 상 및 분리된 중성선이 있는 3 상 코너 접지 (델타) ¦ 16.7 ¦ 16.7 ¦ 50.0 ¦ ¦ III or IV ¦ 100 kA ¦ 2(단상 - 분리된 중성선이 없는 분할 상) ¦ 25 ¦ - ¦ - ¦ ¦ a LPL 값을 알 수 없는 경우 최악의 경우를 가정한다. 식별부호 LPL 뇌 보호 레벨(위험 수준) ¦ a LPL 값을 알 수 없는 경우 최악의 경우를 가정한다. 식별부호 LPL 뇌 보호 레벨(위험 수준) ¦ a LPL 값을 알 수 없는 경우 최악의 경우를 가정한다. 식별부호 LPL 뇌 보호 레벨(위험 수준) ¦ a LPL 값을 알 수 없는 경우 최악의 경우를 가정한다. 식별부호 LPL 뇌 보호 레벨(위험 수준) ¦ a LPL 값을 알 수 없는 경우 최악의 경우를 가정한다. 식별부호 LPL 뇌 보호 레벨(위험 수준) ¦ a LPL 값을 알 수 없는 경우 최악의 경우를 가정한다. 식별부호 LPL 뇌 보호 레벨(위험 수준) ¦ n 전기 네트워크의 도체 수 n = 분리된 중성선 없이 3 상 TT 시스템 Y 구성(중간점 접지)용 3 개 n = 단상(2 개의 도체) + 분할 상 시스템 또는 3 상 코너 접지 델타 시스템과 같은 N 네트워크용 3 개. 여기에서 접지된 상 전선은 중성 전선으로 정의 될 수 있다. n= 분리된 중성선이 없는 분할 상 시스템과 같은 단상(2 개의 도체)용 2 개 CT1, CT2 IEC 61643-12 에 따른 SPD 의 연결 모드(KS C IEC 60364-5-53 에 따라) CT1 연결 유형 A 및 B 에 해당하는 반면 CT2 는 연결 유형 C 에 해당한다. 152 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
b0e490c9-0f2f-4d82-974f-8e1687986da3 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 TT, TN 및 IT-LV 전원 시스템의 가장 일반적인 원칙은 표 J.3 에 나타낸다. 표 J.3 - 전력 공급 장치의 일반적인 구조와 관련된 도체 수 ¦ 도체 수 n ¦ TT or TN-C 시스템 ¦ TN-S 시스템 ¦ 분리된 중성선이 있는 IT 시스템 ¦ 분리된 중성선이 없는 IT 시스템 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 5 ¦ ¦ 3 상 ¦ ¦ ¦ ¦ 5 ¦ ¦ N PE ¦ ¦ ¦ ¦ 4 ¦ 3 상 ¦ ¦ 3 상 N ¦ ¦ ¦ 4 ¦ Nor PEN ¦ ¦ ¦ ¦ ¦ 3 ¦ ¦ 단상 ¦ ¦ 3 상 ¦ ¦ 3 ¦ ¦ N PE ¦ ¦ ¦ ¦ 2 ¦ 단상 ¦ ¦ 단상 ¦ 단상 ¦ ¦ 2 ¦ Nor PEN ¦ ¦ L L(N) ¦ L L(N) ¦ 일본에서는 추가 LV 전력 시스템이 사용된다. 표 J.4 - 일본에서 사용되는 추가 시스템과 관련된 도체 수 ¦ 도체 수 n ¦ 분리된 중성선이 있는 추가 TT 시스템 ¦ 분리된 중성선이 있는 추가 TT 시스템 ¦ 분리된 중성선이 없는 TT 시스템 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 3 ¦ (단상) 분상기동형 ¦ 3 상 - 코너 접지 DELTA ¦ 3 상 - Y 중간점 접지 ¦ ¦ 3 ¦ L N L ¦ L1 L2 L3(N) ¦ ¦ ¦ 2 ¦ ¦ ¦ (단상) 분상기동형 ¦ ¦ 2 ¦ ¦ ¦ L L ¦ 153 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c8043e52-246c-4169-8268-bbf178af3007 | KSCIEC61643-12_KR | KS CIEC 61643-12:2020 부속서 K (참고) 내성 대 정격 임펄스 전압 내력 Uw 를 얻는 방법을 설명하는 KS C IEC 60664-1 에도 불구하고 실제로 설비 내의 모든 유형의 장비에 대한 Uw 값을 얻는 것은 어려울 수도 있다. 기술 위원회는 다음 일반 설명에 따라 과전압 범주를 지정하여야 한다. 과전압 범주 IV 의 장비는 설비 원점에서 사용하기 위한 것이다. 비고 1 이러한 장비의 예로는 전기 계량기 및 1 차 과전류 보호 장치가 있다. 과전압 범주 III 의 장비는 높은 수준의 신뢰성이 필요한 경우 고정 설비 안에 있는 장비다. 비고 2 이러한 장비의 예로는 고정 설비의 스위치와 고정 설비에 영구적으로 연결된 산업용 장비 가 있다. 과전압 범주 II 의 장비는 고정 설비에서 공급되는 에너지 소비 장비다. 비고 3 이러한 장비의 예로는 가전 제품, 휴대용 도구 및 기타 가정용 및 유사한 부하가 있다. 그러한 장비가 신뢰성 및 가용성과 관련하여 특별한 요구사항의 대상이 되는 경우 과전압 범주 III 가 적용된다. 비고 4 SPD 의 전압 보호 레벨은 각 과전압 범주에 대해 표 K.1 에 주어진 정격 임펄스 전압을 초과 하지 않도록 선정하는 것이 좋다. 과전압 범주 I 의 장비는 과도 과전압을 적절하게 낮은 수준으로 제한하기 위한 조치가 취해진 회 로에 연결하기 위한 장비다. 이러한 조치는 발생할 수 있는 과도 과전압이 충분히 제한되어 피크 값이 관련 정격 임펄스 전압을 초과 하지 않도록 하여야 한다(표 K.1 참조). 비고 5 이러한 장비의 예로는 이 수준으로 보호되는 전자 회로가 포함된 장비가 있다. 154 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
6a0ebdd8-d582-4703-bbbd-5eb8eb849ad9 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 표 K.1 - 일반적인 정격 임펄스 전압(KS C IEC 60664-1 에서 파생) ¦ f 까지 포함하 ¦ 현재 세계에서 사용되는 공칭 전압 IEC 60038 d 에 기반한 공급 시스템의 공칭 전압 ¦ 현재 세계에서 사용되는 공칭 전압 IEC 60038 d 에 기반한 공급 시스템의 공칭 전압 ¦ 현재 세계에서 사용되는 공칭 전압 IEC 60038 d 에 기반한 공급 시스템의 공칭 전압 ¦ 현재 세계에서 사용되는 공칭 전압 IEC 60038 d 에 기반한 공급 시스템의 공칭 전압 ¦ 현재 세계에서 사용되는 공칭 전압 IEC 60038 d 에 기반한 공급 시스템의 공칭 전압 ¦ 정격 임펄스 전압 a V ¦ 정격 임펄스 전압 a V ¦ 정격 임펄스 전압 a V ¦ 정격 임펄스 전압 a V ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 는 공칭 전압 AC 에서 파생된 중성선 또는 선 간(상 또는 코 너 접지 시스템 의 경 우) 전 압 선 ¦ 접지 되거나 접지된 중성점 (성형점)이 있는 3 상 시스템, 예를 들면 오 ¦ 3 상 시스템 상 접지 (코너 접지) ¦ 3 상 시스템 상 접지 (하이 레그 델타) HL N/G ¦ 단상 2 선식 시 스템 접 지 또는 비접지 AC ¦ 단상 3 선 식 시스템 (분할상) 접지 AC ¦ 과전압 범주 e ¦ 과전압 범주 e ¦ 과전압 범주 e ¦ 과전압 범주 e ¦ ¦ V ¦ V ¦ V ¦ V ¦ V ¦ V ¦ I ¦ II ¦ " ¦ IV ¦ ¦ 50 ¦ ¦ ¦ ¦ 12,5; 24; 25; 30; 42; 48 ¦ 30 - 60 g ¦ 330 ¦ 500 ¦ 800 ¦ 1 500 ¦ ¦ 100 ¦ 66/115 ¦ 66 ¦ ¦ 60 ¦ ¦ 500 ¦ 800 ¦ 1 500 ¦ 2 500 ¦ ¦ 150 ¦ 120/208 b 127/220 ¦ 115, 120, 127 ¦ ¦ 100°; 110, 120b ¦ 100-200 c,g 110-220 g 120-240 b,g ¦ 800 ¦ 1 500 ¦ 2 500 ¦ 4 000 ¦ ¦ 300 ¦ 220/380, 230/400, 240/415, 260/440, 277/480 b ¦ 200°C, 220, 230, 240, 260, 277 b ¦ 120/208/ 240 j ¦ 220 ¦ 220 - 440 g ¦ 1 500 ¦ 2 500 ¦ 4 000 ¦ 6 000 ¦ ¦ 600 ¦ 347/600 b, 380/660, 400/690, 415/720, 480/830 ¦ 347, 380, 400, 415, 440, 480, 500, 557, 600 ¦ 240/415/ 480 j ¦ 480 ¦ 480 - 960 g ¦ 2 500 ¦ 4 000 ¦ 6 000 ¦ 8 000 ¦ ¦ 1 000 ¦ ¦ 660, 690, 720, 830, 1 000 ¦ ¦ > 601 ≤ 1 250 i ¦ > 601 ≤ 2 500 h,i ¦ 4 000 ¦ 6000 ¦ 8 000 ¦ 12000 ¦ ¦ 1 500 ¦ ¦ ¦ ¦ > 1 250 ≤ 1 500 i ¦ > 1 250 ≤ 3 000 h,i ¦ 6 000 ¦ 8 000 ¦ 10000 ¦ 15000 ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 155 | {}
06fdff36-1a4f-4a59-ac21-f5c5ee66db64 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 표 K.1 - 일반적인 정격 임펄스 전압(KS C IEC 60664-1 에서 파생)(계속) ¦ 따른 ¦ 따른 ¦ ¦ --- ¦ --- ¦ ¦ a 이 정격 임펄스 내전압을 가진 장비는 KS C IEC 60364-4-44 에 설치에 사용할 수 있다. b 미국과 캐나다의 사례 C 일본의 사례 d / 표시는 4 선식 3 상 분배 시스템을 나타낸다. 더 낮은 값은 전압 선 대 중성선이고 더 높은 값은 전압 선 대 선이다. 하나의 값만 표시되는 경우 3 선, 3 상 시스템을 나타내며 선간 값을 지정한다. e 과전압 범주에 대한 설명은 표 위의 텍스트를 참조한다. f 3 상 IT 시스템에서 이것은 상과 분리된 중성선 또는 비분산 성형점 또는 델타 시스템의 가상 성 형점 사이의 공칭 전압이다: 대부분의 시스템에서 이 전압은 상 간 전압을 V3 으로 나눈 값과 같다(KS C IEC 62477-1:2012 참조). 이 열에 제공된 전압은 해당 과전압 범주 선정에만 적용되며 과전압 범주 이외의 다른 매개변수 를 기반으로 하는 절연 설계에는 적용되지 않는다(예를 들면 접지 또는 접촉 가능한 표면까지의 연면 거리에 대해서는 3 상 IT 시스템의 첫 번째 고장 조건에서 상 대 상 전압을 고려해야 한다.) g - 표시는 전압 선에서 중간 지점까지를 전압 상 대 상과 구분한다. h 첫 번째 값은 중간 지점까지의 전압 선에 대한 최솟값이고 두 번째 값은 전압 상에서 상으로의 최댓값이다. i IEC 60038 에 정의 된 1 000 V 이상의 공칭 시스템 전압은 없다. 전압 범위는 여기에 제공된다. / 마크는 하이 레그 델타 3 상 분배 시스템의 전압을 나타낸다. 위에 표시된 전압은 L-N/HL-N/L-L 전압이다. ¦ a 이 정격 임펄스 내전압을 가진 장비는 KS C IEC 60364-4-44 에 설치에 사용할 수 있다. b 미국과 캐나다의 사례 C 일본의 사례 d / 표시는 4 선식 3 상 분배 시스템을 나타낸다. 더 낮은 값은 전압 선 대 중성선이고 더 높은 값은 전압 선 대 선이다. 하나의 값만 표시되는 경우 3 선, 3 상 시스템을 나타내며 선간 값을 지정한다. e 과전압 범주에 대한 설명은 표 위의 텍스트를 참조한다. f 3 상 IT 시스템에서 이것은 상과 분리된 중성선 또는 비분산 성형점 또는 델타 시스템의 가상 성 형점 사이의 공칭 전압이다: 대부분의 시스템에서 이 전압은 상 간 전압을 V3 으로 나눈 값과 같다(KS C IEC 62477-1:2012 참조). 이 열에 제공된 전압은 해당 과전압 범주 선정에만 적용되며 과전압 범주 이외의 다른 매개변수 를 기반으로 하는 절연 설계에는 적용되지 않는다(예를 들면 접지 또는 접촉 가능한 표면까지의 연면 거리에 대해서는 3 상 IT 시스템의 첫 번째 고장 조건에서 상 대 상 전압을 고려해야 한다.) g - 표시는 전압 선에서 중간 지점까지를 전압 상 대 상과 구분한다. h 첫 번째 값은 중간 지점까지의 전압 선에 대한 최솟값이고 두 번째 값은 전압 상에서 상으로의 최댓값이다. i IEC 60038 에 정의 된 1 000 V 이상의 공칭 시스템 전압은 없다. 전압 범위는 여기에 제공된다. / 마크는 하이 레그 델타 3 상 분배 시스템의 전압을 나타낸다. 위에 표시된 전압은 L-N/HL-N/L-L 전압이다. ¦ IEC 61000-4-5 는 전자 장비와 시스템에 대한 전압 및 전류 서지로부터의 내성을 결정하기 위한 시험 을 설명한다. 시험할 장비나 시스템은 블랙박스로 간주되며 시험 결과 는 다음 기준에 의해 판단된다. 1) 정상 성능 2) 작업자가 필요하지 않은 일시적인 기능 상실 또는 일시적인 성능 저하 3) 작업자가 필요한 일시적인 기능 상실 또는 일시적인 성능 저하 4) 장비에 대한 영구적인 손상으로 인한 기능 상실(시험 실패를 의미함) IEC 61000-4-5 의 시험은 장비와 시스템의 영구적 손상과 파괴를 포함하여 전자 장비와 시스템에 대 한 비교적 낮은 전류 서지의 가능한 영향의 전체 범위를 조사하는 반면, 일시적인 기능 상실보다는 장비의 실제 손상 또는 파괴와 관련된 다른 관련 시험 표준이 있다. KS C IEC 60664-1 은 저압 시스템 내 장비의 절연 조정에 관한 것이다. 선 대 선 및 선 대 접지를 측정하지만 이 시험에서는 장비의 출력 특성을 측정하지 않는다. KS C IEC 61643-11 은 저압 전력 시스템에 연결된 서지보호장치에 대한 시험 표준이다. 또한 이 두 표준은 장비에 대한 일시적 과전압의 영향과 관련이 있다. IEC 61000-4-5 및 IEC 61000 시리즈의 기타 표준은 일시적 과전압이 장비 또는 시스템에 미치는 영향을 고려하지 않는다. 영구적인 손상은 시스템 고장 시간과 수리 또는 교체 비용을 초래하기 때문에 거의 허용되지 않는다. 이러한 유형의 고장은 일반적으로 서지 보호 기능이 불충분하거나 없기 때문에 고압과 과도한 서지 전류가 장비의 회로로 유입되어 작동 중단, 부품 고장, 영구적인 절연 파괴 및 화재, 연기 또는 감전 의 위험을 초래한다. 그러나 특히 장비나 시스템이 중요하며 서지 활동 중에 동작 상태를 유지해야 하는 경우, 기능 손실 또는 장비나 시스템의 저하를 경험하는 것도 바람직하지 않다. IEC 61000-4-5 에 설명된 시험의 경우 인가된 전압 시험 수준(설치 등급)의 크기와 그 결과 로 생긴 서지 전류는 장비의 응답에 직접적인 영향을 미친다. 간단히 말해서, 서지의 전압 레벨이 높을 수록 장비가 적절한 서지 내성을 제공하도록 설계되지 않은 경우 기능 손실 또는 성능 저하 가능성이 높아진다. 156 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
e68746fe-0e95-4aca-ae38-a6a08df90903 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 저압 전력 시스템에 사용되는 서지보호장치(SPD)를 시험하기 위해 KS C IEC 61643-11, III 등급 시험은 8/20 단락 전류 파형과 1.2/50 개방 회로 전압 파형을 생성하는 2 �의 가상 임피던스를 갖는 조합파 발생기를 지정한다. IEC 61000-4-5 는 동력 장비와 시스템에 대한 서지 내성 시험에 동일한 조합파 발 생기를 사용하지만 다른 결합 요소, 그리고 때로는 추가 직렬 임피던스를 사용한다. 또한 시설 내에 서 발생하는 과도 현상에 사용되는 더 긴 시험 파형이 있으며, 이는 ITU-T 의 10/700 다. 이 표준의 전 압 시험 수준(설치 등급)과 IEC 61643-11 의 피크 개방 회로 전압 Uoc 의 의미는 동일하다. 이 전압은 발생기 단자의 피크 단락 전류 값을 결정한다. 시험방법의 차이로 인해 시험 결과 는 직접 비교되지 않을 수 있다. 장비 또는 시스템의 서지 내력은 내장형 서지 보호 부품(SPC), 서지보호장치 또는 외부 SPD 를 통해 달성할 수 있다. SPD 에 대한 가장 중요한 선택 기준 중 하나는 IEC 61643-11 에 정의 및 설명된 전압 보호 레벨 Up 다. 이 매개변수는 KS C IEC 60664-1 에 따라 장비 Uw 의 내전압과 조정되어야 하며 특정 조건에서 시험하는 동안 SPD 단자에서 예상되는 최대 전압이다. Up 는 장비 Uw 의 내전압과 의 조정을 위해 이 표준에서만 사용된다. 비교 가능한 스트레스에서 전압 보호 레벨의 값은 IEC 61000-4-5 에 따 라 시험된 장비의 이러한 비교 가능한 스트레스에서 전압 내성 레벨보다 낮아야 한다. 그러나 이것 은 특히 두 표준 간에 항상 파형을 비교할 수 있는 것은 아니기 때문에 현재로서는 다루지 않는다. 일반적으로 IEC 61000-4-5 에 따른 장비의 서지 내성 레벨은 KS C IEC 60664-1 에 따른 절연 정격 임 펄스 전압 내성 레벨보다 낮지만 KS C IEC 60364-4-44 에 따른 일시적인 과전압에 의해 보호 수준이 지나치게 낮은 SPD(또는 내장형 서지 보호 부품)에 미치는 영향에 주의 해야 한다. 장비를 고장으로 부터 보호하고 서지 활동 중에 동작 상태를 유지하며 대부분의 일시적 과전압 조건을 견딜 수 있는 SPD 를 선택할 수 있다. 감응성(내성) 수준은 표 K.2 에 제시되어 있다. 명시되지 않은 한 장비의 감응성 수준(Ui)은 선 대 선 및 선 대 접지 2kV 로 가정한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 157 | {}
48340ade-2915-4f0e-ae01-66cb3214d40d | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 표 K.2 - 설치 조건에 따른 내성 시험 수준 선정 ¦ 설치 등급 ¦ 시험 수준 kV ¦ 시험 수준 kV ¦ 시험 수준 kV ¦ 시험 수준 kV ¦ 시험 수준 kV ¦ 시험 수준 kV ¦ 시험 수준 kV ¦ 시험 수준 kV ¦ 시험 수준 kV ¦ 시험 수준 kV ¦ 시험 수준 kV ¦ 시험 수준 kV ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 설치 등급 ¦ AC 전원 공급 장치 및 AC 주 네트워크에 직접 연결된 I/O 결합 모드 ¦ AC 전원 공급 장치 및 AC 주 네트워크에 직접 연결된 I/O 결합 모드 ¦ AC 전원 공급 장치 및 AC 주 네트워크에 직접 연결되지 않은 I/O 결합 모드 ¦ AC 전원 공급 장치 및 AC 주 네트워크에 직접 연결되지 않은 I/O 결합 모드 ¦ DC 전원 공급 장치 및 그 장치에 직접 연결된 DC I/O 결합 모드 ¦ DC 전원 공급 장치 및 그 장치에 직접 연결된 DC I/O 결합 모드 ¦ 비대칭으로 작동되는 d.f 회로/라인 결합 모드 ¦ 비대칭으로 작동되는 d.f 회로/라인 결합 모드 ¦ 대칭으로 작동되는 d.f 회로/라인 결합 모드 ¦ 대칭으로 작동되는 d.f 회로/라인 결합 모드 ¦ 차폐 I/O 및 통신 라인 f 결합 모드 ¦ 차폐 I/O 및 통신 라인 f 결합 모드 ¦ ¦ 설치 등급 ¦ 선간 ¦ 선대지 간 ¦ 선간 ¦ 선대지 간 ¦ 선간 ¦ 선대지 간 ¦ 선간 ¦ 선대지 간 ¦ 선간 ¦ 모든 선 대 지간 ¦ 선간 ¦ 선대지 간 ¦ ¦ 0 ¦ NA ¦ NA ¦ NA ¦ NA ¦ NA ¦ NA ¦ NA ¦ NA ¦ NA ¦ NA ¦ NA ¦ NA ¦ ¦ 1 ¦ NA ¦ 0.5 ¦ NA ¦ NA ¦ NA ¦ NA ¦ NA ¦ 0.5 ¦ NA ¦ 0.5 ¦ NA ¦ NA ¦ ¦ 2 ¦ 0.5 ¦ 1.0 ¦ NA ¦ NA ¦ NA ¦ NA ¦ 0.5 ¦ 1.0 ¦ NA ¦ 1.0 ¦ NA ¦ 0.5 ¦ ¦ 3 ¦ 1.0 ¦ 2.0 ¦ 1.0 e ¦ 2.0 b,e ¦ 1.0 e ¦ 2.0 b, e ¦ 1.0 C ¦ 2.0 b, C ¦ NA ¦ 2.0 b,c ¦ NA ¦ 2.0°C ¦ ¦ 4 ¦ 2.0 ¦ 4.0 b ¦ 2.0 e ¦ 4.0 b, e ¦ 2.0 e ¦ 4.0 b, e ¦ 2.0 C ¦ 4.0 b, C ¦ NA ¦ 4.0 b, C ¦ NA ¦ 4.0 C ¦ ¦ 5 ¦ a ¦ a ¦ 2.0 ¦ 4.0 b ¦ 2.0 ¦ 4.0 b ¦ 2.0 ¦ 4.0 b ¦ NA ¦ 4.0 b ¦ NA ¦ 4.0 C ¦ a 국부 전력 공급 시스템의 등급에 따라 다르다. b 일반적으로 1 차 보호 장치를 사용하여 시험한다. C 케이블 길이가 10m 보다 짧거나 같으면 시험 레벨을 한 단계 낮출 수 있다. d 10m 미만의 케이블에 대한 데이터 연결부에서는 시험을 하지 않는 것이 좋다. e EUT 에서 상부로 보호가 지정되어 있는 경우, 시험 수준은 보호 장치가 마련되어 있지 않을 때 보호 수준에 해당해야 한다. f 고속 통신선은 비대칭, 대칭, 차폐 I/O 및/또는 통신선 아래에 포함될 수 있다. 일반 장비의 내성 수준에 대한 추가 고려사항: IEC 61000-3-15 및 IEC 61000-2-14 에 따르면 정격 임펄스 전압은 오작동을 방지하기 위해 활선 도체 사이의 공칭 전압보다 5 배 높을 것을 권고한다. 서지 내성 레벨은 임펄스 내성 수준보다 낮다(표 K.3 참조). 표 K.3 - AC 입력에 대한 내성 수준 ¦ 장비의 공칭 전압 ¦ 장비의 요구 서지 내성 전압 kV ¦ IEC 61000-4-5 의 관련 시험 레벨(예시) ¦ IEC 61000-4-5 의 관련 시험 레벨(예시) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 장비의 공칭 전압 ¦ 장비의 요구 서지 내성 전압 kV ¦ 전압 ¦ 전류 ¦ ¦ 120/240 ¦ 0.6/1.2 ¦ 0.5 kV (level 1) ¦ 0.25 kA ¦ ¦ 230/400 ¦ 1.2/2.0 ¦ 1.0 (level 2) ¦ 0.5 kA ¦ ¦ 277/480 ¦ 1.4/2.4 ¦ 2.0 (level 3) ¦ 1.0 kA ¦ ¦ 400/690 ¦ 2.0/3.5 ¦ 4.0 (level 4) ¦ 2.0 kA ¦ 컴퓨터나 고성능 처리 장치와 같은 민감한 장비에서는 서지 내성을 위한 추가 보호가 필요할 수 있 다. 이 장비는 스위칭 모드 전원 장치(SMPS)에서 낮은 값의 DC 전원을 사용한다. SMPS 의 입력 회 로는 강한 임펄스 내전압을 가지고 있지만 SMPS 의 출력 전압은 서지에 따라 달라질 수 있다. 따라 서 소형 특정 ABD 나 사이리스터와 같은 SMPS 의 출력 DC 회로에는 추가적인 보호 방법이 필요하 다. 내성 시험 중 출력 직류 전압을 미리 측정하여 적절한 보호 소자를 적용해야 한다. 158 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
e327190c-5774-4e3b-9992-17a021c3880a | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 IEC 61000-4-5 및 KS CIEC 60050-161:1990 의 161-01-20 에 따른 내성은 전자기 교란이 있을 때 성능 저하 없이 작동하는 장치, 장비 또는 시스템의 능력이다. 위에서 언급했듯이 매개변수를 기반으로 SPD 를 선택할 수 있으며 이는 과전압으로부터 장비를 보호 한다. 이렇게 하면 활성 도체와 접지 사이의 뇌방전으로부터 장비를 보호할 수 있다(예를 들면 절연 조정). 이는 7.1.4.5 에 설명된 대로 장비의 정격 임펄스 내전압 Uw 와 관련된 보호 수준 Up 를 기반으 로 SPD 를 선택함으로써 달성된다. 비고 이러한 원칙은 KS C IEC 62305-4, KS C IEC 60664-1 및 IEC 60364 시리즈와 같은 표준에서도 다루어진다. 매개변수를 장비의 내성과 단순히 일치시키는 것을 바탕으로 SPD 를 선정할 수 없기 때문에 위의 조 치는 장비의 완전한 내성을 반드시 보장하지는 않는다. 예를 들어, IEC 61000-4-5 에 따라 2kV 내성을 갖는 장비는 보호 레벨 Up 가 2kV 미만인 SPD 로 보호되더라도 더 높은 스트레스에 따른 손상 또는 오작동으로부터 반드시 내성이 있는 것은 아니다. 내성 측면에서 장비와 SPD 의 협조는 다음을 포함한 다양한 매개변수에 따라 달라진다. SPD 형태(스위칭, 제한형, 조합형) 및 그 특성 장비 내의 모든 SPC(형태 및 특성) 장비 내의 모든 과전류 보호 장비 내의 모든 커패시터/필터링 부품 SPD 와 기기 사이의 상호 연결 도체의 임피던스 및 저항 부과 된 스트레스(전류, 주파수, 파형 등) 이러한 매개변수가 알려져 있지 않거나 잘 정의 되어 있지 않은 경우가 매우 많다. 이는 SPD 가 많은 경우 내성(장비의 정격 임펄스 내전압에 따른 선택에 기초한 선정) 측면에서 장비를 보호하지만, LEMP 에 대한 시스템의 완전한 내성을 보장하기 위해 시스템 수준에서 시험 또는 시뮬레이션을 통한 추가 평가가 필요하다는 점을 의미한다, 부속서 O 를 참조한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. 159 | {}
bbed22ae-790d-40ca-a0b9-b35898684e2d | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 부속서 L (참고) 일부 국가에서 배전반에 SPD 설치 예 그림 L.1 ~ 그림 L.5 는 일부 국가에서 배전반에 SPD 를 설치하는 일반적인 방법을 보여준다. 이 표준 에서 이미 논의 한 바와 같이 리드 길이를 최소화하고 SPD 의 단락 저항 정격이 패널 위치에서 예상 단락 전류 Isc 와 협조되도록 하는 것이 중요하다. ![image](/image/placeholder) 2 1 ○ 3 SPD 식별부호 1 유입 전원 2 주 스위치(일부 국가에서는 절연체라고 함) 3 SPD 및 해당 분리기(SPD 외함 내에 설치 가능) 그림 L.1 - 별도의 아이솔레이터(SPD 외함에 포함될 수 있음)를 통해 주 유입 아이솔레이터의 부하 측에 연결된 SPD 의 배선도 SPD 에 이러한 분리기를 사용하는 것은 주 절연기를 분리하지 않고도 장치를 차단할 수 있으므로 좋 은 방법이다. 이는 설치의 유전체 내성 시험(일부 국가에서는 플래시 시험이라고 함)를 위해 SPD 를 분리해야 하기 때문이다. 160 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
1e3e9757-2bc1-4970-81ed-c11e8c3d90a6 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) 1 ● 5 SPD 8 7 6 4 3 ON 2 OFF PE L1 L2 L3 N 식별부호 1 배전반 2 주 스위치주 아이솔레이터 또는 주 회로 차단기(MCB)] 3 주 접지 단자 4 중성 단자 5 SPD 용 외함 6 1 차 하부 퓨즈 블록 7 대체 1 차 하부 퓨즈 블록 8 배전반 섀시에 대한 크로스 본드 그림 L.2 - 유입 전원에 가장 가까운 사용 가능한 유출 MCB 에 연결된 SPD (영국에서 일반적으로 볼 수 있는 TNS 설치) MCB 는 또한 SPD 를 퓨즈하고 격리 수단을 제공하는 편리한 수단을 제공한다. 배전반 내부 공간이 부족하여 SPD 는 전기 안전을 위해 별도의 외함에 장착된다. 이 외함은 연결 리드가 짧게 유지되도 록 배전반 옆에 직접 장착된다. 연결 리드의 전압 강하를 더욱 최소화하기 위해 추가 접지 본드가 생성된다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 161 | {}
2cfea68c-aa01-41ff-a7cb-467b1c29dcf4 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) 5 SPD 2 3 1 ○ 4 식별부호 1 유입 전원 2 주 스위치[주 아이솔레이터 또는 주 회로 차단기(MCB)] 3 1 차 하부 퓨즈 블록 4 대체 1 차 하부 퓨즈 블록 5 퓨즈(또는 MCB) 그림 L.3 - 퓨즈(또는 MCB)를 통해 배전반의 첫 번째 출구 방향에서 션트에 연결된 SPD 의 단일 선로 배선 다이어그램 적절한 퓨즈(또는 MCB)를 사용하면 SPD 를 설치할 때 편리하다. 예를 들어 설치 플래시 시험을 위해 SPD 를 분리해야 하기 때문에 주 아이솔레이터를 분리하지 않고도 장치를 분리할 수 있으므로 좋은 예시다. 따라서 퓨즈 크기는 SPD 의 서지 전류 처리 능력을 저하시키지 않고 유입 공급 퓨즈와 의 협 조를 허용하도록 선택된다. 162 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
cab255e3-cb6e-416e-aeee-d228b711c55f | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) 5 1 6 SPD 3 4 ON 2 OFF G L1 L2 L3 N 식별부호 1 주 배전반 2 주 차단기 3 주 접지 바 4 중성 바 5 G-N 본드 6 SPD 의 외함 그림 L.4 - 유입 전원에서 가장 가까운 사용 가능한 차단기에 연결된 SPD (미국 3 상 4W + G, TN-C-S 설치) MCB 의 부하 측면은 또한 전류 제한 퓨즈를 통해 SPD 를 연결할 수 있는 편리한 지점을 제공한다. 이 배열은 또한 유지관리 중 격리 수단을 제공한다. 배전반 내부 공간이 부족하여 SPD 는 전기 안전 을 위해 별도의 외함에 장착된다. 이 외함은 연결 리드가 가능한 한 짧게 유지되도록 배전반 옆에 직접 장착된다. 163 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
229d2f2a-19ef-4466-a119-97f0e0b24779 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) 5 6 SPD 4 3 ON 2 OFF G L1 L2 N 식별부호 ¦ 1 ¦ 주 배전반 ¦ ¦ --- ¦ --- ¦ ¦ 2 ¦ 주 차단기 ¦ ¦ 3 ¦ 주 ¦ ¦ 4 ¦ 접지 바 중성 바 ¦ ¦ ¦ G-N 본드 ¦ ¦ 5 ¦ ¦ ¦ 6 ¦ SPD 의 외함 ¦ 그림 L.5 - 유입 전원에서 가장 가까운 사용 가능한 차단기에 연결된 SPD[미국 단(분할)상 3W + G, 120/240 V 시스템 - 주거 및 소규모 사무실 애플리케이션에 일반적] MCB 의 부하 측면은 또한 전류 제한 퓨즈를 통해 SPD 를 연결할 수 있는 편리한 지점을 제공한다. 이 배열은 또한 유지관리 중 격리 수단을 제공한다. 배전반 내부 공간이 부족하여 SPD 는 전기 안전 을 위해 별도의 외함에 장착된다. 이 외함은 연결 리드가 가능한 한 짧게 유지되도록 배전반 옆에 직접 장착된다. 비고 미국에서는 미국 전기 규범(National Electric Code, 이하 NEC)에 따라 NEC 에서 정의 한 SPD 의 단락 전류 정격이 설치 지점의 예상 고장 전류와 일치해야 한다. 164 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
3d40eff2-149b-424f-8cd3-b51fb204cf22 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 부속서 M (참고) 장비에 신호 및 전원 단자가 모두 있는 경우의 협조 장비의 두 포트가 협조되지 않은 SPD 에 의해 보호될 때 발생할 수 있는 문제를 설명하기 위해 모뎀 이 장착된 개인용 컴퓨터(PC)를 예로 들어 설명한다. 일반적인 시스템은 협조되지 않은 하위 시스템에서 조립될 수 있으며 이러한 하위 시스템은 협조되 지 않은 서지 보호로 인해 위험에 처할 수 있다. 각 전원 및 통신 시스템에는 서지 보호 기능이 포 함될 수 있지만 서지 보호 시스템 사이에 흐르는 서지 전류는 PC 의 전원 및 통신 포트 간에 전위차 를 일으킬 수 있다. PC/모뎀의 특성과 내성 수준에 따라 이러한 전위차가 PC/모뎀을 손상시키거나 이 장비의 동작을 방해할 수 있다. 이러한 첫 번째 예는 이 문제가 어떻게 발생할 수 있는지 보여준다. 이 예는 전력 및 통신 시스템을 기반으로 한다. 그림 M.1 에서 PC 에는 접지 도체가 포함된 3 선 코드에 의해 분기 회로에서 전원이 공급되는 모뎀이 장착되어 있다. 접지 도체는 전원 패널에서 섀시의 안정 상태 전위 기준을 설정한다. 모뎀의 통신 포 트는 해당 위치의 금속 전화 콘센트에 연결된다. 이 콘센트는 통신 인터페이스 종단에 연결되어 있 다. 이 패널은 일반적으로 건물 인입구에 있으며 통신 SPD 를 포함한다. 165 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
03249675-8744-414d-9195-bfd3be837785 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) 5 4 N 3 PE 2 6 식별부호 1 전력 및 통신을 위한 별도의 포트가 있는 모뎀 또는 유사한 전자 장치가 있는 컴퓨터 2 차단기 및 전원 SPD 를 포함한 주 배전반 3 통신 SPD 를 포함한 통신 인터페이스 종단 4 단상 3 선식 전력선 5 가공 통신선 6 등전위 본딩 시스템 그림 M.1 - 미국 전원 및 통신 시스템에서 모뎀이 있는 PC 의 예 협조되지 않은 서지 보호의 효과 와 제안된 솔루션의 이점을 입증하기 위해, 그림 M.2 에 표시된 것처 럼 전원, 전화 및 등전위 본딩 시스템을 포함하는 주택 배선 시스템의 실물 크기 복제에서 측정했다. 166 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
82a7a4f1-294c-43ba-a63a-f2f425ee7bdd | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) MGCN 9 8 2 3 6 6 SPD 6 PE SPO 10 10 Udiff g 식별부호 ¦ 1 ¦ 전원 및 통신을 위한 별도의 포트가 있는 모뎀 또는 유사한 전자 장치가 있는 컴퓨터 ¦ ¦ --- ¦ --- ¦ ¦ 2 ¦ 차단기 및 전원 SPD 를 포함한 주 배전반 ¦ ¦ 3 ¦ 통신 SPD ¦ ¦ 4 ¦ 단상 3 선식 전원선 ¦ ¦ 5 ¦ 가공 통신선 ¦ ¦ 6 ¦ 전원 SPD (배리스터 기반) ¦ ¦ 7 ¦ 등전위 본딩 시스템 ¦ ¦ 8 ¦ 배전용 변압기 ¦ ¦ 9 ¦ MGCN: 다중 접지 공통 중성선 ¦ ¦ 10 ¦ 통신 SPD (GDT 기반) ¦ 그림 M.2 - 실험 시험에 사용된 그림 M.1 의 회로도 그림 M.2 는 통신 인터페이스 패널에 있는 가스 방전관의 작동으로 인해 통신 회로에서 발생하는 서 지가 어떻게 PC 에 전압(전위차) Udiff 를 초래할 수 있는지 보여준다. 통신 인터페이스 패널 가스 방전 관이 동작할 때 볼 수 있듯이 등전위 시스템에 서지 전류가 흐르고 그 결과 통신 포트와 PC 의 전원 포트 사이에 전위차가 발생한다. 이는 인덕턴스 'L'을 통해 관에 흐르는 서지 전류 /surge 때문이다. 관 양단의 전압 강하는 U=Rx /surge + Ld/surge/dt, 식으로 표현되며, 여기에서 d/surge/dt 는 관에 흐르는 전류 의 시간 변화율이다. 계수 L 은 통신 인터페이스 패널과 등전위 시스템 사이의 관 및 접지 케이블의 인덕턴스다. 그림 M.3 은 통신 산업 표준에서 지정한 것과 같은 통신 인터페이스 패널에서 상부로 서지를 주입할 때 얻은 기록을 보여준다. 75 A/�s 의 서지 전류 변화율에 대해 루프에서 4.3 kV 의 피크가 유도되는 것 으로 나타났다. 이 전압은 PC 의 두 포트 사이에 나타날 것이다(물론 실험용 포트는 없었다. 루프는 측정을 허용하고 실험에서 PC 를 불필요하게 위험에 빠뜨리지 않도록 열린 상태로 유지되었다). 비고 8/20 은 통신 산업에서 사용되는 유일한 표준 펄스가 아니다. ITU 는 5/300 전류 임펄스와 함께 10/700 전압 임펄스를 사용한다. KS C IEC 61643-21 는 또한 많은 다양한 파형을 사용한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 167 | {}
643b4e5a-19b8-40c9-b6a5-3a62f993ae08 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 X-Axis: Time (μs) Y-Axis: I(A) Chart Type: line (J) (A) (B) (C) (D) (E) (F) (Red) 식별부호 / 통신 SPD 에 영향을 미치는 전류: 50 A/division - di/dt = 75 A/�s U 전화 포트와 보호 도체(PE) 사이의 전압: 2 kV/division n - 4.3 kV 최댓값 수평 스위프: 2 �s/division 그림 M.3 - 예에서 서지 인가 동안 PC/모뎀에 대한 기준점에 기록된 전압 (전압 및 전류 대 시간(�s)) 문제를 설명하기 위해 사용한 두 번째 예는 그림 M.4 에 설명되어 있다. 이것은 전화선이 연결된 설 비에 전원을 공급하는 전원 공급 장치(TT, 상 및 중성선)를 나타낸다. 국부 접지에 대한 두 네트워크 의 등전위 본딩을 위해 SPD 는 이러한 선로의 인입구 지점에 설치된다. 이 경우를 연구하기 위해 두 개의 결합 지점이 서로 다른 다음 인덕턴스(이 두 지점 사이의 거리와 동일)에 의해 분리되는 실제 사례를 시뮬레이션했다. 또 다른 SPD 도 장비 바로 앞의 통신선에 추가되었다. 거리 L2 는 GDT 와 MOV 사이의 거리이고 거리 L1 은 통신선의 본딩 지점과 전력선의 본딩 지점 사이이다. ![image](/image/placeholder) MV/LV 100 m 100 m 변압기 장비 Phase 10 kA 0.1 요 8/20 us 1nF 100 m 100 m 0.1mH Neutral 00 Uam = 700 V 10kA Zc=50� 8/20 jus L1 Ra = 10 요 Rb = 100 요 그림 M.4 - 시뮬레이션에 사용되는 일반적인 TT 시스템 168 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
fbc89cda-81f2-4149-9d3a-31733f7b5b67 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 그림 M.2 의 통신 회로에 인가되는 서지 전류의 영향도 컴퓨터 시뮬레이션을 통해 분석되었으며 실제 시험과 동일한 결과 를 얻었다. 변압기의 고주파 모델과 선로에 대한 전파 효과(양 선로 모두 200 m) 를 사용했다. 전원 공급용 SPD 는 배리스터형(제한 부품)이고 통신선용 SPD 는 가스 방전관(스위칭 부품)이다. 접지 Rb 의 저항은 GDT 의 스파크오버 전압뿐만 아니라 이 연구의 매개변수였다. 전원 공급 장치 SPD(3 가지 보호 모드)의 공칭 방전 전류는 10 kA 이고 전압 보호 수준은 1.5kV 다. L1=L2= 10m 에 대해 다음 결과 가 얻어진다. 리드 길이 L1 은 낙뢰가 전력 네트워크를 칠 때 12.5kV 의 전압 강하를 경험하고 낙뢰가 통신 네트워크를 칠 때 23 kV 의 전압 강하를 경험한다. 이 수준은 장비 내부에 뇌방전을 생성하기에 충분한다. 따라서 두 네트워크가 SPD 로 보호되고 두 네트워크가 동일한 접지 시스템에 본딩되는 경우에도 내 부 뇌방전은 계속 발생할 수 있다. 이러한 결과 를 일반화할 수 있도록 두 네트워크에 약간의 부하가 있는 시뮬레이션도 수행했으며 결 과는 동일했다. 또한 다른 유형의 네트워크(TN 및 IT)와 다양한 서지 파형을 사용한 시뮬레이션도 수 행했다. 결과 는 표 M.1 에 요약되어 있다. 표 M.1 - 시뮬레이션 결과 ¦ TN 시스템 ¦ 전원 공급 장치에서 오는 10kA 8/20 서지의 경우 ¦ 통신선에서 오는 10kA 8/20 서지의 경우 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ L1 전압 강하 ¦ 12kV ¦ 35 kV ¦ ¦ IT 시스템, 중성선의 임피던스 = 1 000 � ¦ 전원 공급 장치에서 오는 10kA 8/20 서지의 경우 ¦ 통신선에서 오는 10kA 8/20 서지의 경우 ¦ ¦ L1 전압 강하 ¦ 8 kV ¦ 35 kV ¦ ¦ TT 시스템 ¦ 전원 공급 장치에서 오는 10kA 10/350 서지의 경우 ¦ 통신선에서 오는 10kA 10/350 서지의 경우 ¦ ¦ L1 전압 강하 ¦ 8 kV ¦ 23 kV ¦ 장비의 뇌방전 위험에 관한 결과 는 모든 유형의 전원 공급 시스템에서 동일함을 알 수 있다. 장비의 내성은 대부분의 경우 최대 2.5 kV 정도이므로 약한 서지에 의해 생성된 전압(10 kA 만 해당)은 이 서 지 내성(8kV ~ 35kV)을 훨씬 초과 한다. 비고 10 kA 10/350 은 전화선에 비현실적이다. 그것은 약 2kA 에서 퓨즈가 될 것이고 원격 네트워크 에서의 측정은 100 A 와 같은 값을 보여준다. 그러나 그러한 값은 전력 측과 통신 측 사이의 비교를 위해 사용되었다. 가능한 솔루션 위의 문제를 피하기 위해 두 가지 가능성이 있다. 다양한 선로(위에서 설명한 예의 경우 통신 및 전력선) 사이의 루프 크기를 줄이기 위해 케이블의 다른 라우팅을 찾아 인덕턴스 L 을 줄인다. 하지만 기존 건물에서는 이것이 쉬운 일이 아니다. 신 축 건물의 경우 단일 출입구 본딩 지점이 최상의 솔루션이다. 169 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f8d86047-c47e-41b2-9c9f-524727927144 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 전력 시스템의 단자와 공통 본딩 지점 사이의 장비 근처에 SPD 를 설치하고 다른 시스템(예를 들 면 통신) 단자와 이 공통 본딩 지점 간에 동일한 작업을 수행한다. 일반적으로 이러한 장치에는 "멀티서비스형 SPD"라고도 하는 단일 패키지에 전원 SPD 및 통신 SPD 가 포함되어 있다. 이렇게 결합된 SPD 에는 공통 본딩 지점으로 매우 짧은 리드에 의해 기준이 된 장비의 모든 연결부를 위 한 서지 보호 기능이 포함된다. 이 공통 본딩 지점이 PE 에 연결되어야 한다. 이 공통 본딩 지점 은 PE 에 연결된 경우 보호할 장비의 하우징이 될 수 있다. 그림 M.5 는 그림 M.1 에 설명된 실험에서 이러한 SPD 의 효과 를 보여준다. 그림 M.5 는 그림 M.3 과 비교되어야 한다. ¦ U(V) 400 200 0 -200 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ I(A) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ U(V) 400 200 0 -200 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 250 ¦ ¦ U(V) 400 200 0 -200 ¦ (U) ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 200 ¦ ¦ U(V) 400 200 0 -200 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 150 ¦ ¦ U(V) 400 200 0 -200 ¦ 2 ¦ 4 (I) ¦ ¦ ¦ 10 ¦ 12 ¦ 14 ¦ 16 ¦ 100 ¦ ¦ U(V) 400 200 0 -200 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 50 ¦ ¦ U(V) 400 200 0 -200 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 0 ¦ 식별부호 / 통신 SPD 에 영향을 미치는 전류 - di/dt = 75 A/�s U 전화 포트와 보호 도체(PE) 간 전압: 200 V/division - 200 Vmax 수평 스위프: 2 �s/division 그림 M.5 - 멀티서비스형 SPD 가 그림 M.1 과 같은 구조의 회로에 설치된 경우 서지를 인가하는 동안 측정된 전압 및 전류 파형 170 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
beff1b74-5d9b-4cea-86a5-f8b8dd8d1325 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 부속서 N (참고) 단락 후비 보호 및 서지 내력 N.1 일반사항 서지 전류는 SPD 를 통해서만 흐르는 것이 아니라 서지 전용이 아닌 다른 장치를 통해서도 흐르도록 되어 있다. 백업 보호 및 상부에 설치된 모든 종류의 고장 전류 보호가 이러한 상황에 있으므로 원 치 않는 트리핑 또는 용융이 발생할 수 있다. 서지 보호를 위한 부적절한 사용을 방지하기 위해 이 러한 장치의 내성 기능을 아는 것이 유용하다. 백업 보호 장치를 통해 서지 전류가 흐를 때 추가적인 전압 강하가 발생할 수 있다. 이 전압 강하는 백업 보호로 사용되는 장치의 종류와 정격 전류에 따라 달라진다. 이 부속서에서 N.2, N.3, N.4 및 N.5 은 수행된 형식 시험과 SPD 제조자 및 퓨즈 제조자에서 얻은 실 험 데이터를 기반으로 퓨즈 서지 내성에 대한 명확한 계산 및 정보를 제공한다. 다른 과전류 보호 장치(OCPD)의 경우 서지 내성은 장치의 형태 및 설계에 따라 크게 달라질 수 있다. 여러 SPD 분리 기 설계의 장단점을 비교하기 위한 몇 가지 정보는 N.6 에 나타낸다. 특수 목적으로 설계된 장치에는 다른 특성이 있을 수 있다. 필요한 경우 제조자는 SPD 를 CB 와 같은 다른 장치와 연관시키는 정보를 제공해야 한다(MCB, MCCB, RCD 등). 제조자의 설명서를 참조하는 것이 좋다. N.7 은 일부 국가에서 사용되는 SPD 분리기에 대한 추가 시험 값을 제공한다. 사용자는 SPD 고장 시 안전 및 서지 내력으로 인해 다른 SPD 분리기를 선정할 수 있음을 상기해야 한다. 사용자는 항상 이를 고려하고 SPD 제조자 지침을 참조해야 한다. N.2 서지 8/20 및 10/350 파형의 1 회에 대한 퓨즈 내력 정보 제조자에서 제공한 퓨즈 프리아크 Pt(1 ms)와 비교하여 임펄스 파형의 12t 계산을 사용하면 1 회 서지 에 대한 퓨즈 서지 내력을 추정할 수 있다. 임펄스의 12t 는 다음 공식을 사용하여 임펄스 전류의 파고값과 공칭 파형으로부터 추산할 수 있다. · 파형 10/350 의 경우(KSC IEC 61643-11:2011 의 8.1.1 도 참조) Rt[A2s] = 2.5 x 10~4 x Icrest2 [A2] · 파형 8/20 의 경우 비고 이것은 공칭 임펄스 파형(상승 시간 및 반값까지 시간)을 기반으로 하며 허용된 최대 시험 허 용값을 포함하지 않는다. Rt[A2 s] = 0.14 x 10~4 x Icrest2 [A2] 171 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
d1038f1d-0284-4ca9-bfae-c143515a8b5c | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 예: · 크기가 9kA 인 단일 8/20 임펄스 전류를 견디려면 백업 퓨즈의 최소 프리아크 값이 다음 값보다 커야 한다. Rt[A2 s] = 0.14 x 10~4 x 92 = 1 134[A2s] · 크기가 5 kA 인 단일 10/350 임펄스 전류를 견디려면 백업 퓨즈의 최소 프리아크 값이 다음 값보다 커야 한다. Rt[A2s] = 2.5 x 10~4 x 52 = 6 250[A2s] 21 200 A2s 의 프리아크 값을 가진 사용하지 않은 100 A gG 퓨즈는 다음과 같은 단일 8/20 임펄스 전 류를 견딜 수 있다. Icrest [A] = V21200 /(0.14 x 10~4) = 38 914 [A] 퓨즈 특성, 치수 및 제조자에 따라 다양한 Rt 값을 퓨즈 데이터 시트에서 찾을 수 있다. N.3 사전시험 및 동작 책무 시험에 대한 퓨즈 영향 요인(감소) KS C IEC 61643-11 에 기술된 시험 절차 동안 퓨즈는 단일 임펄스뿐만 아니라 전체 임펄스 순서(전제 조건 시험 및 동작 책무 시험)를 견뎌야 한다. 이러한 임펄스는 퓨즈를 저하시켜 단일 임펄스 내구성 보다 내력이 감소한다(N.2 참조). 전체 사전 조정 시험 및 동작 책무 시험을 통과 하려면 실험 데이터는 0.5 에서 0.9 로 감소 계수가 단 일 임펄스 내성 값에 적용되어야 함을 보여준다. 세 가지 주요 요소를 고려해야 한다. · In 과 /imp 사이의 비율. In 에서 15 개의 임펄스로 사전 조정 시험을 수행하고 /imp 의 0.1, 0.25, 0.5, 0.75, 1 배로 최종 책무 시 험을 수행한다. In 의 파고 값이 /imp 에 비해 낮으면 /imp 스트레스에 비해 사전 조정 시험에 의한 성 능 감소를 무시할 수 있다 반대로 In 의 파고 값이 /imp 에 가깝거나 더 높으면 사전 조정 시험에 의 한 스트레스를 무시할 수 없다. · 단일 임펄스 퓨즈 내성과 비교한 절대값이다. In 또는 limp 값이 퓨즈가 견딜 수 있는 최대 임펄스 파고값에 가까우면 각 임펄스가 적용될 때마다 성능이 저하되는 반면, 최대 임펄스 파고값보다 훨씬 낮으면 그 효과 를 무시할 수 있다. · 퓨즈 Pt 값의 허용 오차 대부분의 경우 퓨즈 제조자는 퓨즈 표준에 따라 장치에 대한 허용값을 제공한다. 이 허용값은 실제 서지 내성 기능과 관련이 없으며 계산에 사용할 수 없다. N.4 실험 데이터를 기반으로 하고 IEC 60269 시리즈에 지정된 매개변수 및 한계를 기반으로 한 계산으로 확인된 퓨즈의 동작 책무 내성 단사 내성과 전체 사전 조정/동작 책무 시험 간의 비율의 예는 표 N.1 에 나타낸다. 172 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
148b9744-aaff-4ff7-8e30-2707c94847c3 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 표 N.1 - 단사 내성과 전체 사전 조정/동작 책무 시험 간 비율의 예 ¦ 추가 동작 책무 시험에 대한 gG 퓨즈 링크의 내성 ¦ 추가 동작 책무 시험에 대한 gG 퓨즈 링크의 내성 ¦ 추가 동작 책무 시험에 대한 gG 퓨즈 링크의 내성 ¦ 추가 동작 책무 시험에 대한 gG 퓨즈 링크의 내성 ¦ 추가 동작 책무 시험에 대한 gG 퓨즈 링크의 내성 ¦ 추가 동작 책무 시험에 대한 gG 퓨즈 링크의 내성 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 퓨즈 링크의 정격 전류 (A) ¦ 최소 프리아크 12t (표 113, KS C IEC 60269-2) ¦ 평가된 최소 단열량 12t (A2s) ¦ 안전 계수 (전류 값에 대한) ¦ 최대 In (kA) (8/20 �sec) ¦ 최대 /Imp (kA) (10/350 �sec) ¦ ¦ 8 ¦ 40 ¦ 24 ¦ 0.85 ¦ 1.2 ¦ 0.3 ¦ ¦ 10 ¦ 68 ¦ 41 ¦ 0.85 ¦ 1.5 ¦ 0.3 ¦ ¦ 12 ¦ 130 ¦ 78 ¦ 0.85 ¦ 2.1 ¦ 0.5 ¦ ¦ 16 ¦ 291 ¦ 175 ¦ 0.85 ¦ 3.1 ¦ 0.7 ¦ ¦ 20 ¦ 640 ¦ 384 ¦ 0.85 ¦ 4.6 ¦ 1.0 ¦ ¦ 25 ¦ 1 210 ¦ 726 ¦ 0.85 ¦ 6.4 ¦ 1.4 ¦ ¦ 32 ¦ 2 500 ¦ 1 750 ¦ 0.85 ¦ 9.9 ¦ 2.2 ¦ ¦ 40 ¦ 4 000 ¦ 2 800 ¦ 0.85 ¦ 12.5 ¦ 2.8 ¦ ¦ 50 ¦ 5 750 ¦ 4 025 ¦ 0.85 ¦ 15 ¦ 3.4 ¦ ¦ 63 ¦ 9 000 ¦ 6 300 ¦ 0.85 ¦ 19 ¦ 4.2 ¦ ¦ 80 ¦ 13 700 ¦ 10 960 ¦ 0.85 ¦ 25 ¦ 5.6 ¦ ¦ 100 ¦ 21 200 ¦ 19 080 ¦ 0.85 ¦ 33 ¦ 7.3 ¦ ¦ 125 ¦ 36 000 ¦ 32 400 ¦ 0.85 ¦ 42 ¦ 9.6 ¦ ¦ 160 ¦ 64 000 ¦ 57 600 ¦ 0.85 ¦ 57 ¦ 13 ¦ ¦ 200 ¦ 104 000 ¦ 93 600 ¦ 0.85 ¦ 72 ¦ 16 ¦ ¦ 224 ¦ 139 000 ¦ 125 100 ¦ 0.85 ¦ 83 ¦ 19 ¦ ¦ 250 ¦ 185 000 ¦ 166 500 ¦ 0.85 ¦ 96 ¦ 22 ¦ ¦ 315 ¦ 302 000 ¦ 271 800 ¦ 0.85 ¦ 123 ¦ 28 ¦ ¦ 400 ¦ 557 000 ¦ 445 600 ¦ 0.85 ¦ 157 ¦ 35 ¦ ¦ 500 ¦ 900 000 ¦ 720 000 ¦ 0.85 ¦ 200 ¦ 45 ¦ ¦ 630 ¦ 1 600 000 ¦ 1 280 000 ¦ 0.85 ¦ 267 ¦ 60 ¦ 표 N.1 에 제공된 데이터 설명: ¦ 2 열 ¦ 이러한 최소 프리아크 Pt 값은 KS C IEC 60269-2, 표 113 에서 추출된다. 이는 4 ms 의 프리아크 시간을 참조하며 원래 SC32B 에 의해 참조 값으로 설정되었다. ¦ ¦ --- ¦ --- ¦ ¦ 3 열 ¦ 이 값은 재료 상수와 퓨즈 스트립의 모양을 기반으로 계산된다. 이는 약 3 ms 의 용단 시간을 말하며 경험에 의해 확인된다. ¦ ¦ 4 열 ¦ 이것은 다양한 퓨즈 치수를 고려한 안전 계수다. ¦ ¦ 5 + 6 열 ¦ 이 값은 3 열의 계산을 기반으로 하며 동작 책무 시험의 실험 데이터에 의해 확인된다. ¦ 표 N.1 에 포함된 값은 치수에 관계없이 모든 종류의 gG 퓨즈 링크에 적용되어야 하지만 다른 퓨즈 특성에는 적용되지 않는다. 물론 비교 계산을 기반으로 한 추산에 사용할 수 있다. 다른 퓨즈 특성은 KS C IEC 61643-11 에 설명된 대로 전체 동작 책무 시험 절차를 적용하여 별도로 173 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b0b6f09d-f812-4caa-955e-15acb666d3f1 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 확인해야 한다. 비고 표 N.1 의 기초로 사용되는 실험 데이터의 대부분과 10/350 임펄스 전류에 대한 해당 계산은 NH 퓨즈를 기반으로 한다. 그러나 몇 개의 원통형 퓨즈에 대해 수행된 일부 시험에서 해당 퓨 즈 치수에 대해 위에서 언급한 내력이 확인되었다. N.5 외부 분리기 기술 모드 CB 및 퓨즈에 대한 다음 모드(표 N.2 참조)는 지난 3 년 동안의 조사를 기반으로 하며 현재 상황에 대한 간략한 개요를 제공한다. 다음 요약은 전류 분리기 및 퓨즈 기술 및 크기(시험은 230/400 V 에서 수행됨)와 연결되어 있으며 향후 이러한 변경이 있을 경우 제시된 결과 에도 상당한 영향을 미칠 수 있음을 고려해야 한다. 표 N.2 - 외부 분리기 기술 모드 ¦ 정격 전류 (in A) ¦ 0-80 ¦ 80-... ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 서지 전류 내력(8/20) ¦ 일반적으로 차단기는 퓨즈보다 휠 씬 높은 내성을 나타낸다(2 배 이 상). ¦ 일반적으로 차단기는 여전히 퓨즈 보다 높은 내구성을 보인다(30 % ~ 50 % 이상). ¦ ¦ 뇌전류 내력(10/350) ¦ 실제 보고는 불가능하다. 이것은 CB 의 정격 전류와 관련이 없지만 기 술과 관련이 있으며 퓨즈보다 훨씬 낮거나 높을 수 있다. ¦ 실제 보고는 불가능하다. 이것은 CB 의 정격 전류와 관련이 없지만 기 술과 관련이 있으며 퓨즈보다 훨씬 낮거나 높을 수 있다. ¦ ¦ 분리기가 SPD 분기에 있을 때 동작 없이 잔류 전압에 추가되는 전압 강하(VD) ¦ 일반적으로 차단기가 더 높게 나타 난다. 퓨즈에 비해 전압 강하의. 차이가 없을 때까지 정격 전류가 증가함에 따라 차이가 감소한다. ¦ 일반적으로 차단기는 퓨즈에 비해 더 높게 나타난다. 차이가 없을 때 까지 정격 전류가 증가함에 따라 차이가 감소한다. ¦ ¦ 분리기가 SPD 분기에 있을 때 동작 시 * 잔류 전압에 추가되는 전압 강하(VD) ¦ 퓨즈의 경우 아킹 중 전압 강하는 CB 의 아킹 전압 강하보다 높지만 회 로 차단기의 시간 동작은 전압 제한 또는 전압 스위칭 SPD 의 사용과 속류의 진폭에 따라 다르다. ¦ 퓨즈의 경우 아킹 중 전압 강하는 CB 의 아킹 전압 강하보다 높지만 회 로 차단기의 시간 동작은 전압 제한 또는 전압 스위칭 SPD 의 사용과 속류의 진폭에 따라 다르다. ¦ ¦ * 이것은 분리기가 데이터 시트에서 제조자가 지정한 최대 차단기 정격보다 작은 정격을 가질 때 ¦ * 이것은 분리기가 데이터 시트에서 제조자가 지정한 최대 차단기 정격보다 작은 정격을 가질 때 ¦ * 이것은 분리기가 데이터 시트에서 제조자가 지정한 최대 차단기 정격보다 작은 정격을 가질 때 ¦ 발생할 수 있다. SPD 상부의 모든 부품은 설비의 서지 내력에 영향을 미칠 수 있으며 이들의 서지 내력을 알고 있어 야 한다. N.6 일부 국가에서 사용되는 SPD 외부 분리기에 대한 추가 요구사항 및 시험 값 일부 국가에서는 SPD 외부 분리기에 대한 추가 요구사항 및 시험 값을 제공한다. 일본 표준은 SPD 퓨즈 분리기(SFD)에 대한 요구사항을 제공한다. 비고 1 JEITA RC4501: 일본의 SPD 퓨즈 분리기(SFD)에 대한 저압 서지보호장치용 SPD 분리기 성 능 요구사항 및 시험방법 비고 2 JEITA RC4502: 일본의 SPD 퓨즈 분리기(SFD)에 대한 저압 서지보호장치용 SPD 분리기 선 정 및 적용 원칙 중국 에너지 산업 표준 및 중국 통신 산업 표준은 SPD 특정 분리기(SSD)에 대한 요구사항 및 시험 174 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
fff570ad-870d-4fcb-97a4-5a4cf25e1fb6 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 방법을 제공했다. 비고 3 NB/T 42150-2018: 중국의 저압 서지보호장치용 특정 보호 장치, YD/T XXXXX: 통신국/현장에 서 사용되는 서지보호장치용 외부 회로 분리기(출간 중) 기본적으로 이러한 SFD 및 SSD 요구사항은 다음과 같다. a) 큰 서지 내력(표 N.3 참조) b) 서지 전류에 의해 유도된 더 낮은 전압 강하 c) SPD 고장 시 상부 OCPD 와의 과전류 조정 및 안전 분리를 위한 시간-전류 특성이 있는 저 정격 전류(그림 N.1 참조) d) 상부 OCPD 와의 과전류 조정을 위한 시간-전류 특성(그림 N.2 참조) 표 N.3 - SFD 에 대한 전기 정격의 예 ¦ 정격 전류 ¦ 서지 내력 ¦ 서지 파형 ¦ 차단 용량 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 30 A ¦ 20 kA: 15 회 ¦ 8/20 ¦ AC 250 V 100 kA ¦ ¦ 28 A ¦ 15 kA: 15 회 ¦ 8/20 ¦ AC 250 V 100 kA ¦ ¦ 23 A ¦ 10 kA: 15 회 ¦ 8/20 ¦ AC 250 V 100 kA ¦ 표 N.4 - SSD 에 대한 트리핑 전류의 예 ¦ 최소 트리핑 전류 ¦ 서지 내력 ¦ 서지 파형 ¦ 차단 용량 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 3A ¦ 25 kA: 1 회 ¦ 10/350 ¦ AC 250, 100 kA ¦ ¦ 3A ¦ 60 kA: 15 회 ¦ 8/20 ¦ AC 250, 100 kA ¦ ¦ 3A ¦ 10 kA: 15 회 ¦ 8/20 ¦ AC 250, 25 kA ¦ 그림 N.1 은 SPD 내부 분리기와 외부 분리기(SFD 또는 SSD)의 시간-전류 특성과 SPD 내부 MOV 의 시간-전류 고장(버닝) 곡선의 예를 보여준다. MOV 내부 SPD 와 SPD 내부 및 외부 분리기(SFD 또는 SSD) 간의 동작 조정을 위해 다음을 확인해야 한다. 외부 분리기의 특성 곡선은 전체 고장 전류 범위를 포함하도록 내부 분리기의 특성 곡선과 교차해 야 한다. 내부 및 외부 분리기의 특성 곡선은 MOV 고장(버닝) 전에 회로를 차단하기 위해 MOV 고장(버닝) 곡선의 왼쪽 아래에 있어야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. 175 | {}
099e6c84-8548-4abc-b6b9-332afc368158 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 X-Axis: 시간(s) Y-Axis: 전류(A) Chart Type: line SPD 외부 차단기 MOV SPD 내부 차단기 item_01 30Amperes (A) 20Amperes (A) 20Amperes (A) 식별부호 ¦ 녹색 곡선 ¦ MOV 의 전류-시간 고장(버닝) 곡선 ¦ ¦ --- ¦ --- ¦ ¦ 적색 곡선 ¦ SPD 외부 분리기의 전류-시간 특성 곡선 ¦ ¦ 청색 곡선 ¦ SPD 내부 분리기의 전류-시간 특성 곡선 ¦ 그림 N.1 - MOV 를 사용한 SPD 내부 및 외부 분리기의 조정을 위한 개략도 그림 N.2 는 OCPD 및 SPD 분리기의 시간-전류 특성 예를 보여준다. 50A MCCB 또는 125A gG 퓨즈 가 OCPD 로 설치된 경우 SPD 분리기는 OCPD 보다 빠르게 동작해야 한다. 즉, SPD 분리기의 시간 전류 특성은 OCPD 의 왼쪽 아래에 있어야 한다. 176 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
69f3dfbf-59fe-44e6-b2e7-0e4881a9c464 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 X-Axis: 시간(s) Y-Axis: 전류(A) Chart Type: line SPD OCPD 1 OCPD 2 item_01 100 100 1000 식별부호 ¦ 녹색 곡선 ¦ 50 A MCCB 의 전류-시간 곡선 ¦ ¦ --- ¦ --- ¦ ¦ 적색 곡선 ¦ 125 A Cyl Gg 퓨즈의 전류-시간 특성 곡선 ¦ ¦ 청색 곡선 ¦ SPD 외부 분리기의 전류-시간 특성 곡선 ¦ 그림 N.2 - SPD 분리기의 시간-전류 특성 예 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 177 | {}
923e853c-df8f-452d-8f2e-30af92196b5a | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 부속서 o (참고) 뇌방전 조건에서 시스템 레벨 내성을 시험하기 위한 실용적인 방법 0.1 일반사항 다음 시험방법을 사용하여 전체 시스템 내성 수준을 평가할 수 있다. O.2 정상적인 서비스 조건에서 SPD 방전 전류 시험 a) 시스템 레벨 내성 시험 전: 보호할 장비의 내성을 결정해야 한다. 전력선에 접속하는 기기는 KS C IEC 60664-1, IEC 61643-12 를 사용하고, 통신선에 접속하는 기기는 KS C IEC 61643-22, ITU-T K.20 K.21, K.45 를 사용한다. b) SPD 가 제공하는 보호는 시험 및 성능 표준 KS C IEC 61643-11 또는 KS C IEC 61643-21 에 설명된 시험 절차를 사용하여 결정해야 한다. 보호할 장비는 제조업체의 지침에 따라 SPD 를 설치한 상태에서 시험해야 한다. 장비는 공칭 공급 전압에서 전원이 공급되어야 하며 SPD 에 대해 정격의 공칭 방전 전류 매개변수로 스트레스를 인 가해야 한다. 해당되는 경우 통신선, 센서, 모터와 같은 추가 회로를 연결해야 한다. c) 그림 0.1 은 정상적인 서비스 조건에서 방전 전류 시험을 수행하는 데 사용되는 회로의 예를 제공 한다. O.3 뇌전류에 의한 유도 시험 a) 시뮬레이션된 뇌방전에 의해 생성된 전자기장으로 인한 전체 시스템의 동작을 조사하기 위해 임 펄스 전류를 금속 장착 플레이트에 주입해야 한다. b) 시험 대상 시스템은 가능한 현실적으로 설치해야 한다. 이 시뮬레이션용 설치에는 보호되는 장비, 설치된 SPD 및 상호 연결 라인의 실제 길이 및 유형이 포함되어야 한다. c) 전체 시스템의 케이블링 내에서 발생하는 유도 임펄스 전류를 모니터링해야 한다. d) 1 차 뇌전류 방전의 특성 및 적용 가능한 값은 KS C IEC 62305-1:2010, 표 C.3 에 나와 있어야 한 다. e) 그림 0.2 는 II 등급 시험된 SPD 가 전원 및 제어 시스템에 설치된 경우 유도 시험의 예를 제공한다. 0.4 시스템 레벨 내성 시험의 권고 시험 분류(IEC 61000-4-5 에 따름) 이 표준은 다음의 통과 기준을 정의 한다. a) 제조자가 지정한 한계 내에서 정상적인 성능 178 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 해 무단 배포를 금합니다. | {}
f0f690c2-e23d-4e70-a8c7-635a33c28943 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 b) 고장 발생 후 중단되고 시험 대상 장비가 운전자의 개입 없이 정상 성능을 회복하는 일시적인 기 능 상실 또는 성능 저하 c) 작업자의 개입이 필요한 일시적인 기능 손실 또는 성능 저하 d) 하드웨어 또는 소프트웨어의 손상 또는 데이터 손실로 인해 복구할 수 없는 기능 상실 또는 성능 저하 ![image](/image/placeholder) 배전반 전원 S 장치 SP 1 3 P 모터 D D 8/20 S N 제어 전원 2 P 장치 시스템 D 데이터 S 버스 4 P 센서 PE D 서지 발생기 SPD + SPD2 + SPD3: 전원 회로용 서지보호장치 SPD4: 통신 및 신호 네트워크용 서지보호장치 그림 0.1 - 정상적인 사용 조건에서 방전 전류 시험을 수행하는 데 사용하는 회로의 예 ![image](/image/placeholder) 전류 생성기에 연결 모터 낙뢰 배선 채널의 영역 임펄스 전류 SPD 임펄스 주입 센서 전류 발생기 저전압 전원 장치 배전반 I H0 = 2�Sa [A/m] 금속 프레임 그림 0.2 - 뇌전류로 인한 유도 시험 회로의 예 179 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
6d5d7a48-434f-4d84-aecb-ba99a347875a | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 부속서 P (참고) 여러 부품이 포함된 SPD 시험 지침 P.1 일반사항 이 부속서는 다중 부품을 포함하는 SPD 의 몇 가지 예에 대해 어떤 전류 경로를 시험해야 하는지 지 침을 제공한다. 이 선택적 시험을 허용하려면 SPD 를 수정해야 할 수 있다. 시료 준비 요건은 SPD 내에서 주로 사용되는 주요 부품 배열을 기반으로 개발되었다. 오늘날 점점 더 복잡한 SPD 회로가 시장에 등장하고 있으며 이러한 시료 준비 요건을 원래의 의도에 따라 올바르게 적용하는 방법에 대 한 의문이 제기되고 있다. 이 표준은 비선형 부품만 언급하지만 그러한 부품이 서지 전류의 상당 부 분을 차지할 수 있는지 또는 그러한 부품이 고장날 경우 발생할 수 있는 일은 고려하지 않았기 때문 에 추가 지침이 필요하다. 이러한 지침은 새로운 회로 설계가 때때로 등장하기 때문에 일반적인 방 법으로 제공하기가 매우 어렵다. 따라서, 다음 예시는 제조자와 시험 엔지니어가 시료 준비를 위한 가장 적절한 결정을 하도록 안내해야 한다. P.2 저항/용량 트리거 제어와 직렬로 연결된 다중 스파크 갭의 예 저항/용량 트리거 제어와 직렬로 연결된 다중 스파크 갭의 예는 그림 P.1 에 나타낸다. ![image](/image/placeholder) 식별부호 1 스파크 갭 2 저항성 또는 용량성 트리거 제어 그림 P.1 - 저항/용량 트리거 제어와 직렬로 연결된 다중 스파크 갭의 예 180 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
5413f939-fd3a-4d7b-a1c7-509c0348d5c8 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 직렬로 연결된 스파크 갭은 시험할 유일한 전류 경로다. 옴 또는 용량성 분압기/트리거 제어 회로는 비선형 부품을 포함하지 않으며 상당한 양의 전류를 전도하지 않기 때문에 이 표준의 의미에 따라 별도의 전류 경로를 구성하지 않는다. P.3 용량성 트리거 제어 및 GDT + MOV 의 병렬 연결된 직렬 연결과 직렬로 연결된 2 개의 스파크 갭의 예 용량성 트리거 제어 및 GDT + MOV 의 병렬 연결된 직렬 연결과 직렬로 연결된 2 개의 스파크 갭의 예가 그림 P.2 에 나타낸다. ![image](/image/placeholder) 3 식별부호 1 스파크 갭 2 저항성 또는 용량성 트리거 제어 3 MOV(s) 4 GDT 그림 P.2 - 용량성 트리거 제어와 직렬로 연결된 2 개의 스파크 갭 직렬로 연결된 2 개의 스파크 갭은 시험을 위해 고려해야 하는 주요 전류 경로를 구성한다. GDT 와 MOV 의 직렬 연결을 통한 병렬 전류 경로는 별도의 시험을 위해 고려되어야 한다. GDT 와 MOV 의 직렬 연결을 통과 하는 전류의 비율은 불가능하진 않더라도 결정하기가 어렵고 이 표준에서 는 이러한 전류 비율에 대한 제한을 제공하지 않는다. 용량성 트리거 제어 회로는 비선형 부품을 포함하지 않으며 상당한 양의 전류를 소비하지 않기 때문 에 이 표준의 의미에서는 별도의 전류 경로를 구성하지 않는다. P.4 병렬 MOV 바이패스/트리거 제어를 사용하는 3 전극 GDT 의 예 병렬 MOV 바이패스/트리거 제어를 사용하는 3 전극 GDT 의 예는 그림 P.3 에 나타낸다. 181 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
8e774947-9b4e-4bc9-bfe5-e6e751ac6252 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) MOV GDT MOV 식별부호 GDT 3 전극 GDT MOV "고에너지" 바이패스 그림 P.3 - 병렬 MOV 바이패스/트리거 제어가 있는 3 전극 GDT 3 전극 GDT 는 시험을 위해 고려해야 할 하나의 전류 경로를 구성한다. MOV 의 직렬 연결을 통한 병렬 전류 경로는 GDT 가 동작할 때까지 직렬 연결된 MOV 를 통해 상당한 양의 전류를 예상할 수 있기 때문에 별도의 시험용으로 고려되어야 한다. P.5 GDT + MOV 트리거 제어가 있는 4 전극 간격의 예 GDT + MOV 트리거 제어가 있는 4 전극 간격의 예는 그림 P.4 에 나타낸다. ![image](/image/placeholder) 그림 P.4 - GDT + MOV 트리거 제어가 있는 4 전극 스파크 갭 4 전극 스파크 갭은 시험을 위해 고려해야 하는 주요 전류 경로를 구성한다. 182 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
879725f3-ea36-45f9-bc11-376c10b009ae | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 직렬로 연결된 GDT 와 MOV 를 통한 이 4-전극 갭의 단일 구간으로의 부분 병렬 전류 경로는 비선형 부품을 포함하지만, 4-전극 갭인 주요 부품에 대한 병렬 전류 경로를 구성하지 않기 때문에 별도의 시험을 고려할 필요가 없다. P.6 직렬 연결된 GDT 및 MOV 와 병렬인 스파크 갭의 예 직렬 연결된 GDT 및 MOV 와 병렬인 스파크 갭의 예는 그림 P.5 에 나타낸다. ![image](/image/placeholder) 2 3 4 식별부호 ¦ 1 ¦ 스파크갭 ¦ ¦ --- ¦ --- ¦ ¦ 2 ¦ ¦ ¦ ¦ 저항 ¦ ¦ 3 ¦ MOV ¦ ¦ 4 ¦ GDT ¦ 그림 P.5 - 직렬 연결된 GDT 및 MOV 와 병렬인 스파크 갭 GDT 는 시험을 위해 고려해야 할 하나의 전류 경로를 구성한다. MOV 와 GDT 의 직렬 연결을 통한 병렬 전류 경로는 해당 직렬 연결 MOV 를 통해 상당한 양의 전류 가 예상될 수 있으므로 별도의 시험용으로 고려해야 한다. P.7 트리거 변압기가 있는 3 전극 간격의 예 트리거 변압기가 있는 3 전극 스파크 갭의 예는 그림 P.6 에 나타낸다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. 183 | {}
10018db6-95dc-4975-ad1a-3057aa2dab93 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 ![image](/image/placeholder) Temp. 그림 P.6 - 트리거 변압기가 있는 3 전극 스파크 갭 3 전극 스파크 갭은 시험을 위해 고려해야 하는 주 전류 경로를 구성한다. MOV 와 트리거 변압기/커패시터의 직렬 연결을 통한 병렬 전류 경로는 선형 부품에 의해 전류가 제 한되는데, 해당 회로를 통해 예상되는 전류의 상당한 부분이 확실하게 필요하지는 않기 때문에 별도 의 시험용으로 고려할 필요가 없다. 184 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
399e151b-f98d-40d2-be84-2ec60cb518b4 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 부속서 Q (참고) I 등급 시험된 SPD 와 관련된 미국의 예외 미국에서는 I 등급 시험된 SPD 가 필요하지 않다. 이 예외는 전체 문서에 적용된다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 185 | {}
a2cfde13-1b43-4ffb-bbd5-61801109c7e7 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 참고문헌 [1] IEC 60038, IEC standard voltages [2] IEC 60269(all parts), Low-voltage fuses [3] KS C IEC 60364-4-42, 저 전압 전기설비 - 제 4-42 부: 안전을 위한 보호 - 열 영향에 대한 보 호 [4] KS C IEC 60364-4-43, 저압 전기설비 - 제 4-43 부: 안전을 위한 보호 - 과전류에 대한 보호 [5] KS C IEC 60898-1, 주택용 및 이와 유사한 설비에 사용되는 과전류 보호용 차단기 - 제 1 부: 교 류용 차단기 [6] KS C IEC 60947-2, 저압 개폐장치 및 제어장치 - 제 2 부: 차단기 [7] KS C IEC 60060-1, 고전압 시험 기술 - 제 1 부: 일반 정의 및 시험 요구사항 [8] KS C IEC 62305-3:2010, 피뢰시스템 - 제 3 부: 구조물의 물리적 손상 및 인명위험 [9] KS C IEC TR 61000-5-6:2002, 전자파적합성(EMC) - 제 5-6 부: 설치 및 완화 지침 - 외부 전자 파(EM) 영향의 완화 [10] KS C IEC 61008-1, 주택용 및 이와 유사한 용도의 과전류 보호장치가 없는 누전차단기(RCCBs) 제 1 부: 일반 요구사항 [11] KS C IEC 61009-1, 주택용 및 이와 유사한 용도의 과전류 보호장치를 가진 누전차단기(RCBO) 제 1 부: 일반 요구사항 [12] IEC TR 62066:2002, Surge overvoltages and surge protection in low-voltage a.c. power systems General basic information [13] KS C IEC 60050-151:2001, 국제전기기술용어 - 제 151 부: 전기 장치와 자기 장치 [14] IEC 60050-442:1998, International Electrotechnical Vocabulary(IEV) - Part 442: Electrical accessories [15] IEC 60050-826:2004, International Electrotechnical Vocabulary(IEV) - Part 826: Electrical installations [16] KS C IEC 60099-4:2014, 서지 피뢰기 - 제 4 부: 교류 시스템용 산화 금속형 갭리스 서지 피뢰기 [17] KS C IEC 60099-5, 서지 피뢰기 - 제 5 부: 선정 및 적용지침 [18] KS C IEC 61936-1, 교류 1 kV 초과 및 직류 1.5 kV 초과 전력설비 - 제 1 부: 교류 [19] KS CIEC 61643-21, 저압 서지 보호장치 - 제 21 부: 통신 및 신호망에 연결된 서지 보호장치 - 성능요건과 시험방법 [20] KS C IEC 61643-22, 저 전압 서지 보호장치 - 제 22 부: 통신망 보호용 - 선정 및 적용지침 [21] KS C IEC 61643-321, 저압 서지 보호장치의 부품 - 제 321 부: 애벌란시 다이오드(ABD)에 대한 규정 [22] KS C IEC 61643-331, 저압 서지 보호장치의 부품 - 제 331 부: 산화 금속 배리스터(MOV)에 대 한 규정 [23] KS C IEC 61643-341, 저압 서지 보호기 장치를 위한 부품 - 제 341 부: 사이리스터 서지 차단기 를 위한 명세(TSS) 186 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
9a2d22d3-9c28-4b36-a5c6-2227bdcf3d15 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 [24] KS C IEC 62305-3, 피뢰시스템 - 제 3 부: 구조물의 물리적 손상 및 인명위험 [25] KS C IEC 62561-6, 피뢰시스템 구성요소(LPSC) - 제 6 부: 뇌격 계수기(LSC)에 관한 요구사항 [26] IEEE 1159-2009, IEEE Recommended Practice for Monitoring Electric Power Quality [27] IEEE C62.41.1-2002, IEEE Guide on the Surge Environment in Low-Voltage(1000V and less) AC Power Circuit [28] IEEE C62.41.2, IEEE recommended practice on characterization of surges in lowvoltage(1 000 V and less) AC power circuits [29] IEEE C62.72-2016, IEEE Guide for the Application of Surge-Protective Devices for Use on the Load Side of Service Equipment in Low-Voltage (1 000 V or Less, 50 Hz or 60 Hz) AC Power Circuits [30] A. ROUSSEAU, P. AURIOL, A. RAKOTOMALALA, Lightning distribution through earthing systems, Hobart Lightning Protection Workshop, 1992 [31] H. ALTMAIER, D. PELZ, K. SCHEIBE, Computer simulation of surge voltage protection in low voltage systems, ICLP, 1992 [32] M. CLEMENT, J. MICHAUD, Overvoltages on the low voltage distribution networks, CIRED, 1993 [33] J. SCHONAU, F. NOACK, R. BROCKE, Coordination of fuses and overvoltages protection devices in low voltage mains. Fifth International Conference on Electrical Fuses and their Applications, 1995 [34] P. HASSE, P. ZAHLMANN, J. WIESINGER, W. ZISCHANK, Principle for an advanced coordination of surge protective devices in low voltage systems, ICLP 1994 [35] A. ROUSSEAU, T. PERCHE, Coordination of surge arresters in the low voltage field, INTELEC, 1995 [36] F. MARTZLOFF, J.S. LAI, Coordinating cascaded surge protective devices: high-low versus low-high, IEEE IAS, 1991 [37] J. HUSE et al., Coordination of surge protective devices in power supply systems: need for a secondary protection, ICLP, 1992 [38] A. ROUSSEAU, Choice of low voltage surge arresters based on risk analysis, Power Quality, 1995 [39] A. ROUSSEAU, V. CREVENAT, Protective levels at equipment terminals for various SPDs, GROUND, 2010 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 187 | {}
73af42d4-f515-4cce-981d-90091a9675f1 | KSCIEC61643-12_KR | KS C IEC 61643-12:2020 KS C IEC 61643-12:2020 해 설 이 해설은 이 표준과 관련된 사항을 설명하는 것으로 표준의 일부는 아니다. 서지보호장치(SPD)의 제품 표준인 KS C IEC 61643-1 에서 KS C IEC 61643-11 로 개정되면서 SPD 선 정 및 적용지침 표준인 본표준도 국제표준에서 전면 개정이 실행됨에 따라 KS C IEC 61643-12 표준 도 전면 개정하게 되었다. 기본적인 SPD 의 기술변화에 따른 표준의 변경은 없었으며, 주로 표준의 형식적인 부분이 대부분이 다. 제품 표준인 KS C IEC 61643-11 표준 개정에 따라 SPD 선정 및 적용지침 표준도 연계되어 부 합화 하였다. 이슈 사항으로는 SPD 신규 적용 분야로 풍력발전에 대한 적용 기술이 추가되어 부속서 G 의 응용 예에 사례 예시로 추가 되었다. 188 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
7a56674c-51d1-40dd-b5f7-c9e438b28768 | KSCIEC61643-12_KR | 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
dc97c94e-916f-46f4-a884-3c333d1bc1fe | KSCIEC61643-12_KR | KS c IEC 61643-12:2020 KSKSKS KSKSK KSKS KSK KS KSK KSKS KSKSK KSKSKS Low-voltage surge protective devices - Part 12: Surge protective devices connected to low-voltage power systems - Selection and application principles ICS 29.240.10 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
91abf3ea-a57e-4e36-b96b-2035d6a56356 | KSCIEC61140_2020확인_KR | KSKSKSKS KS C IEC 61140 KSKSKSK KSKSKS KSKSK KSKS KSK K KS 감전보호 - 설비 및 기기의 공통사항 KS C IEC 61 140:2014 (2020 확인 ) 산 업 표 준 심 의 회 2014 년 5 월 9 일 개정 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
d8bbc93e-59c5-413e-8c60-253048591805 | KSCIEC61140_2020확인_KR | KS CIEC 61140:2014 심 의 : 전기응용 기술심의 회 성 명 근 무 처 직 위 (회 장) 신 판 석 홍익대학교 교 수 (위 원) 권 오 화 KIC TECH 대 표 김 갑 일 명지대학교 교 수 김 재 희 한국산업기술시험원 본 부 장 박 효 성 한국화학융합시험연구원 전 문 위 원 박 현 주 한전전력연구원 책 임 연 구 원 서 호 선 KR 지식재산법률사무소 대 표 이 주 철 대한전기협회 처 장 임 영 민 전자부품연구원 수 석 연 구 원 장 우 진 서울과 학기술대학교 교 수 조 두 희 한국전자통신연구원 책 임 연 구 원 (간 사) 김 원 석 국가기술표준원 표준정책국 전기전자정보표준과 연 구 관 원안작성 협력기관 : 저압전기설비 전문위원회 성 명 근 무 처 직 위 (대표전문위원) 김 재 철 숭실대학교 교 수 (위 원) 이 주 철 대한전기협회 처 장 김 세 동 두원공과 대학교 교 수 이 창 열 한국전력공사 부 장 신 석 하 (주)건일이엔지 부 사 장 정 우 성 (주)동서엔지니어링 상 무 송 인 권 슈나이더일렉트릭코리아 부 장 김 영 석 한국전기안전공사 전기안전연구원 책 임 연 구 원 이 기 홍 한국토지주택공사토지주택연구원 수 석 연 구 원 박 원 석 ABB 코리아 부 장 신 효 섭 (주)더리코리아 회 장 이 강 수 (주)옴니엘피에스 상 무 주 문 노 한국전기연구원 책 임 안 준 호 한국전기산업연구원 선 임 신 성 수 대한전기협회 팀 장 류 기 환 대한전기협회 과 장 표준열람 : e 나라 표준인증 (http://www.standard.go.kr) ¦ 제 정 자 : 산업표준심의 회 위원장 제 정 : 2001 년 11 월 26 일 ¦ 담당부처 : 산업통상자원부 국가기술표준원 9 일 ¦ ¦ --- ¦ --- ¦ ¦ 확 인 : 2020 년 12 월 8 일 심 의 : 산업표준심의 회 전기응용 기술심의 회 원안작성협력 : 저압전기설비 전문위원회 ¦ 개 정 : 2014 년 5 월 ¦ 이 표준에 대한 의견 또는 질문은 e 나라 표준인증 웹사이트를 이용하여 주십시오. 이 표준은 산업표준화법 제 10 조의 규정에 따라 매 5 년마다 산업표준심의 회에서 심의 되어 확인, 개정 또는 폐지됩니다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및무단배포를 금합니다. | {}
03902058-ce06-44c6-adcc-51315b6c7b29 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 목 차 머 리 말 ............................. ii 개 요 ................................... 1 적용범위 ........................... 1 2 인용표준 ··························· 1 3 용어와 정의 ····················· 2 4 감전보호의 기본 규칙 ...... 10 4.1 정상상태 .............. 10 4.2 단일 W................... 10 4.3 특별한 경우 ············ 11 11 5 보호설비(보호대책의 의료비용 5.1 기본보호용 설비 ..... 12 5.2 고장보호 설비 --------- 14 5.3 강화 보호설비 ......... 17 6 보호 대책 .............. 18 6.1 전원의 자동차단에 의한 보호. ................... 19 6.2 이중 또는 강화절연에 의한 보호 ....................... 19 6.3 등전위본딩을 통한 보호 .......... 19 6.4 전기적 분리에 의한 보호. ··········· 19 19 6.5 비도전성 환경에 의한 ⌀ - - - - - - 20 6.6 SELV 에 의한 ⌀= = = = 6.7 PELV 에 의한 보호 ······· .................................... 20 20 6.8 안정상태의 접촉전류 및 전하제한에 의한 보호................................. 6.9 그 밖의 대책에 의한 보호 .......................... 20 7 전기설비 내의 기기 및 보호설비의 조................ 20 7.1 0 급 기기 ················ 21 7.2 I 급 기기 ................. 21 7.3 11 급 기기 ················ 22 7.4 III 급 기기 ·············· 23 7.5 접촉전류, 보호도체전류, 누설 전류. ............................ 24 7.6 고압 설비의 안전, 경계 이격 및 경고 표시............................. 26 8 특별한 작업 및 운전조건 ····················· 26 26 8.1 수동조작 장치와 수동교환용 부분.............. 8.2 단로 후 전기적인 값 .... 27 8.3 단로장치 .......... - - 28 부속서 A(참고) 보호조치에 의해 실행되는 보호대책의 기요.................................... 31 부속서 B(참고) 7.5.2.2a) 및 7.5.2.2b)에 관한 보호도체전류의 최대 교류 제한 값 ......................... 33 부속서 C(참고) 용어 색인 --- 34 KSCIEC 61140:2014 11111111 39 -i- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및무단배포를 금합니다. | {}
aacd5056-de44-465a-aaf3-8bbb65aa1330 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 머 리 말 이 표준은 저작권법에서 보호 대상이 되는 저작물이다. 이 표준의 일부가 기술적 성질을 가진 특허권, 출원공개 이후의 특허출원, 실용신안권 또는 출원공개 후의 실용신안등록출원에 저촉될 가능성이 있다는 것에 주의 를 환기한다. 국가기술표준원장 및 산업 표준심의 회는 이러한 기술적 성질을 가진 특허권, 출원공개 이후의 특허출원, 실용신안권 또는 출원 공개 후의 실용신안등록출원에 관계되는 확인에 대하여 책임을 지지 않는다. -ii- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
a58e2a1e-25f9-4590-8836-9efcaae08279 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 개 요 이 표준은 2009 년 제 3. 1 판으로 발행된 IEC 61140, Protection against electric shock Common aspects for installation and equipment 를 기초로, 기술적 내용 및 대응국제표준의 구성을 변경하지 않 고 작성한 한국산업표준이다. -iii- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
587d4022-13d8-452b-baeb-f8b83b6eef6e | KSCIEC61140_2020확인_KR | 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
8a785f4b-12e8-40c2-9d5b-5ab9c306275e | KSCIEC61140_2020확인_KR | 한국산업표준 KS C IEC 61140:2014 (2020 확인) 감전보호 - 설비 및 기기의 공통사항 Protection against electric shock - Common aspects for installation and equipment 1 적용범위 이 표준은 사람과 동물의 감전에 대한 보호에 적용한다. 전기설비, 시스템 및 기기에 공통적인 사항 또는 이들의 절연협조에 필요한 기본적인 원칙 및 요건을 제시하기 위함이다. 이 표준은 전압의 높고 낮음에 관계 없이 설비, 시스템 및 기기에 대하여 작성되었다. 비고 이 표준의 몇 개의 절은 저압 및 고압 시스템, 설비 및 기기에 관한 것이다. 이 표준의 목적을 위해 저압은 교류 1 000 V 이하 또는 직류 1 500 V 이하의 모든 정격 전압이고, 고압은 1 000 V 또는 직류 1 500 V 를 초과 하는 모든 정격 전압이다. 이 표준의 요구사항은 관련표준에 포함되거나 인용되는 경우에만 적용되며, 단독 표준으로 사용되는 것으로 의도된 것은 아니다. 2 인용표준 다음의 인용표준은 이 표준의 적용을 위해 필수적이다. 발행 연도가 표기된 인용표준은 인용된 판만 을 적용한다. 발행 연도가 표기되지 않은 인용표준은 최신판(모든 추록을 포함)을 적용한다. KS A ISO/IEC Guide 51:2003, 안전 측면 규격에 안전 측면을 포함시키기 위한 지침 KS C IEC 60050- 195, 국제전기기술용어 - 제 195 부: 감전보호용 접지 KS C IEC 60071- 1, 절연협조 - 제 1 부: 정의 및 일반 원칙 KS C IEC 60071-2, 절연협조 - 제 2 부: 적용 지침 KS C IEC 60364-4-41, 저압 전기설비 - 제 4-41 부: 안전을 위한 보호 - 감전에 대한 보호 KS C IEC 60364-5-54:2014, 건축전기설비 - 제 5-54 부: 전기기기의 선정 및 시공 - 접지배치, 보 호도체 및 결합도체 KS C IEC 60446:2009, 인력-기계 인터페이스, 마킹과 식별자를 위한 안전 원리 - 색이나 수에 의한 도체의 식별자 KS C IEC 60479- 1:2007, 인체와 가축에 대한 전류의 영향 - 제 1 부: 일반적인 양상 KS C IEC 60529:2006, 외곽의 방진 보호 및 방수 보호 등급(IP 코드) KS C IEC 60601(모든 부), 의료용 전기기기 KS C IEC 60601 - 1:2011, 의료용 전기기기 - 제 1 부: 기본 안전 및 필수 성능에 관한 일반 요구사항 KS C IEC 60664- 1:2009, 저압기기의 절연협조 - 제 1 부: 원칙, 요구사항, 시험 KS C IEC 60990:2003, 접촉전류와 보호도체 전류의 측정법 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 1 | {}
35cde855-94f4-45a0-87e0-bc3a861116a6 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 KS C IEC 61201:2013, 규약 접촉전압 한계의 이용 - 적용 지침 IEC 60038:1983, IEC standard voltages IEC 60050- 131, International Electrotechnical Vocabulary(IEV) - Chapter 131: Electric and magnetic circuits IEC 60050- 351:1998, International Electrotechnical Vocabulary Part 351: Automatic control IEC 60050- 826:1982, International Electrotechnical Vocabulary Chapter 826: Electrical installations of buildings IEC 60364-6-61:1986, Electrical installations of buildings - Part 6: Verification - Chapter 61: Initial verification IEC 60417- 2, Graphical symbols for use on equipment - Part 2: Symbol originals IEC 60721(all parts), Classification of environmental conditions IEC 62271 - 102:2001, High-voltage switchgear and controlgear Part 102: Alternating current disconnectors and earthing switches IEC Guide 104:1997, The preparation of safety publications and the use of basic safety publications and group safety publications 3 용어와 정의 이 표준의 목적을 위하여 다음의 용어와 정의 를 사용한다. 비고 정의 의 목록은 부속서 C 에 나타냄. 3.1 감전 (electric shock) 사람 또는 동물의 몸을 통과 하는 전류에 의한 생리학적 영향 [IEV 195-01-04] 3.1.1 기본보호 (basic protection) 고장이 없는 상태 에서의 감전보호 [IEV 195-06-01] 비고 저압 설비, 기기 및 시스템에서 기본보호는 일반적으로 KS C IEC 60364-4-41 에서 사용되는 직접접촉에 대한 보호에 해당한다. 3.1.2 고장보호 (fault protection) 단일 고장 상태 에서의 감전보호 [IEV 195-06-02] 비고 저압 설비, 기기 및 시스템에서 고장보호는 주로 기본절연의 파괴에 관한 것으로서 KS C IEC 60364-4-41 에서 사용하는 간접접촉에 대한 보호에 해당한다. 3.2 (전기)회로 (electric circuit) 전기가 흐를 수가 있는 장치 또는 매체의 조합 [IEV 131-01-01] 2 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c0bda9ac-dce3-4e4d-8698-d35f7c82718e | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 비고 건축전기설비에 관한 IEV 826-05-01 참조 3.3 (전기)기기 [(electrical) equipment] 전기에너지의 발전, 변전, 송전, 축전, 배전 또는 그 이용을 목적으로 사용하는 모든 품목, 예를 들어 기계, 변압기, 기구, 계측기, 보호장치, 배선계통의 부속품, 가정용 전기기기 [IEV 826-07-01, 수정] 3.4 충전부 (live part) 중성선을 포함하여 정상운전 시에 가압이 되는 도체 또는 도전부. 규약상 PEN 도체나 PEM 도체 또는 PEL 도체는 포함하지 않는다. [IEV 195-02-19] 비고 1 이러한 개념은 반드시 감전의 위험을 의미하는 것은 아니다. 비고 2 PEM 및 PEL 의 용어정의 는 IEV 195-02-13 및 IEV 195-02-14 참조 3.5 위험충전부 (hazardous-live-part) 어떤 조건 하에서 상해를 주는 감전을 초래할 수 있는 충전부 [IEV 195-06-05] 비고 고압의 경우, 위험 전압이 고체 절연물 표면에 나타날 수 있다. 이런 경우에 그 표면은 위험 충전부로 간주한다. 3.6 노출도전부 (exposed-conductive-part) 사람이 접촉할 수 있고 통상 충전되어 있지 않지만 기본절연이 파괴되었을 때 충전될 수 있는 기기의 도전부분 [IEV 195-06-10] 비고 충전되어 있는 노출도전부와 의 접촉을 통해서만 충전될 수 있는 기기의 도전부는 그 자체로서 는 노출도전부로 간주하지 않는다. 3.7 계통외도전부 (extraneous-conductive-part) 설비의 일부분은 아니나 일반적으로 국부 대지전위를 전도시킬 수 있는 도전성 부분 [IEV 195-06-11] 3.8 접촉전압 (touch voltage) 3.8.1 (유효)접촉전압 (effective touch voltage) 사람이나 동물이 동시에 접촉되었을 때 접촉된 도전부 사이의 전압 비고 유효접촉전압의 값은 이들 도전부와 전기적으로 접촉한 사람이나 동물의 임피던스에 상당히 영향을 받을 수 있다. [IEV 195-05-11] 3 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
ba998ddd-7715-4738-8fff-0f8eb80e7f27 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 3.8.2 예상 접촉전압 (prospective touch voltage) 사람이나 동물이 도전부에 접촉되지 않았을 때 동시에 접근 가능한 도전부 사이의 전압 [IEV 195-05-09] 3.9 접촉전류 (touch current) 전기기기나 설비의 한 곳 이상의 접근 가능한 부분에 사람이나 동물이 접촉하였을 때 사람이나 동물의 몸을 통과 하는 전류 [IEV 195-05-21] 3.10 절연 (insulation) 비고 절연은 고체, 액체, 가스(예를 들어, 공기) 또는 이러한 조합으로 될 수 있다. 3.10.1 기본절연 (basic insulation) 기본보호를 위한 위험충전부의 절연 비고 이 개념은 기능목적으로만 사용되는 절연에는 적용하지 않는다. [IEV 195-06-06] 3.10.2 보조절연 (supplementary insulation) 고장보호를 위해 기본절연에 추가하여 적용하는 독립적인 절연 [IEV 195-06-07] 3.10.3 이중절연 (double insulation) 기본절연과 보조절연의 두 가지 절연으로 구성되는 절연 [IEV 195-06-08] 3.10.4 강화절연 (reinforced insulation) 이중절연과 동등한 감전에 대한 보호를 제공하는 위험충전부의 절연 비고 강화절연은 기본절연 또는 보조절연과 같이 단독으로 시험할 수 없는 여러 개의 층으로 구성될 수 있다. [IEV 195-06-09] 3.11 비도전성 환경 (non-conductive environment) 사람이나 동물이 위험한 충전상태인 노출도전부에 접촉했을 때 높은 임피던스(예를 들어, 절연성 벽 또는 바닥) 환경과 접지된 도전부를 없앰으로써 보호되도록 하는 시설 [IEV 195-06-21] 4 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
54574e01-bee0-4e12-abb2-4b2529e9a526 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 3.12 (전기적)보호장애물 [(electrically) protective obstacle] 무의 식적인 직접접촉은 방지하지만 고의 에 의한 직접접촉을 방지하는 것은 아닌 부품 [IEV 195-06-16] 비고 직접접촉은 IEV 195-06-03 에서 정의 하고 있다. 3.13 (전기적)보호격벽 [(electrical) protective barrier] 통상적인 어떠한 접근 방향에 대해서도 직접접촉에 대한 보호를 위해 설치된 부품 [IEV 195-06-15] 비고 직접접촉은 IEV 195-06-03 에서 정의 하고 있다. 3.14 (전기적)보호외함 [(electrically) protective enclosure] 어떠한 방향에서도 위험충전부에 접근하는 것이 방지되도록 기기의 내부를 둘러싼 전기적 외함 [IEV 195-06-14] 비고 추가로, 외함은 일반적으로 내적 또는 외적 영향, 예를 들어 먼지 또는 물의 침입에 대한 보호를 하거나 기계적 손상을 방지한다. 3.15 촉수범위 (arm's reach) 사람이 통상 서서 또는 움직일 수 있는 면의 어떤 점에서도 도움 없이 임의 의 방향으로 사람의 손이 뻗쳐져 닿을 수 있는 접근 구역 [IEV 195-06-12] 3.16 등전위본딩 (equipotential bonding) 등전위를 이루기 위해 의도된 도전부 간의 전기적 연결 [IEV 195-01-10] 비고 등전위본딩의 효과 는 접속부에 흐르는 전류의 주파수에 의존될 수 있다. 3.16.1 보호등전위본딩 (protective equipotential bonding) 안전을 목적으로 하는(예를 들어, 감전에 대한 보호) 등전위본딩 [IEV 195-01-15, 수정] 비고 기능적 등전위본딩은 IEV 195-01-16 에 정의 하고 있다. 3.16.2 등전위본딩 단자(대) (equipotential bonding terminal) 기기나 설비에 설치되어 등전위본딩시스템과 전기적 접속을 목적으로 하는 단자(대) [IEV 195-02-32] 3.16.3 보호본딩 단자(대) (protective bonding terminal) 보호 등전위본딩을 목적으로 하는 단자(대) 5 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
65ed646b-463b-486e-908e-147cbe7a637c | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 3.16.4 보호도체, PE (prptective conductor, PE) 안전을 목적으로(예를 들어, 감전에 대한 보호) 설치된 도체 [IEV 195-02-09] 3.16.5 PEN 도체 (PEN conductor) 보호도체와 중성선의 두 기능 모두를 겸한 도체 [IEV 195-02-12, 수정] 3.17 대지 (earth) 비고 대지의 개념은 지구 및 지구의 모든 물리적 물질을 의미한다. 3.17.1 기준대지 [reference earth, reference ground(US)] 모든 접지설비의 영향범위 밖에 있는 도전성을 갖는 것으로 간주되는 대지의 일부로서, 전위는 규약적으로 영(0)으로 취한다. [IEV 195-01-01] 3.17.2 (국소)대지 [(local) earth, (local) ground(US)] 접지극과 전기적으로 접촉하고 있는 대지의 일부로서, 전위는 반드시 영(0)은 아니다. [IEV 195-01-03] 3.17.3 접지극 [earth electrode, ground electrode(US)] 특정 도전성 매체(예를 들어 콘크리트나 코크스)에 매입될 수 있는 대지와 전기적으로 접촉하고 있는 도전부 [IEV 195-02-01] 3.17.4 접지도체 [earthing conductor, grounding conductor(US)] 시스템, 설비 또는 기기의 주어진 점과 접지극 사이의 도전성 경로 또는 도전성 경로의 일부를 구성하는 도체 [IEV 195-02-03] 3.17.5 접지설비 [earthing arrangement, grounding arrangement(US)] 시스템, 설비 및 기기의 접지에 포함된 모든 전기적 접속 및 기구 [IEV 195-02-20] 비고 이것은 국지적으로 고전압 쪽에서 상호접속된 접지 전극의 제한된 배열일 수 있다. 3.17.6 보호접지 [protective earthing, protective grounding(US)] 안전을 목적으로 시스템, 설비 또는 기기의 한 점 또는 여러 점을 접지하는 것. [IEV 195-01-11] 6 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c5d36d50-1174-4a8b-b8cc-01ae30628985 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 3.17.7 기능접지 [functional earthing, functional grounding(US)] 전기안전 이외의 목적으로 시스템, 설비 또는 기기의 한 점 또는 여러 점을 접지하는 것. [IEV 195-01-13] 3.18 전원의 자동차단 (automatic disconnection of supply) 고장 시에 보호장치의 자동 작동에 의해 한 가닥 또는 그 이상의 선도체를 차단하는 것. [IEV 195-04-10] 비고 이것은 반드시 전원시스템의 모든 도체의 차단을 의미하는 것은 아니다. 3.19 강화보호설비 (enhanced protective provision) 2 개 이상의 독립된 보호장치와 같은 보호신뢰도를 갖는 보호설비 3.20 (도전성) 차폐물 [(conductive) screen, (conductive) shield(US)] 전기회로 및/또는 도체를 감싸거나 분리하고 있는 도전부 [IEV 195-02-38] 3.21 (전기적) 보호차폐물 [(electrically) protective screen, (electrically) protective shield(US)] 전기회로 및/또는 도체를 위험충전부로부터 분리하기 위해 사용되는 도전성 차폐물 [IEV 195-06-17] 3.22 (전기적) 보호 차폐 [(electrically) protective screening, (electrically) protective shielding(US)] 감전보호를 목적으로 보호등전위 접속계통에 전기적으로 접속된 보호차폐물에 의해서 위험충전부로부터 전기회로 또는 도체를 분리하는 것. [IEV 195-06-18] 3.23 단순분리 (simple separation) 기본절연에 의해 회로들 사이 또는 회로와 대지 사이를 분리하는 것. 3.24 (전기적) 보호분리 [(electrically) protective separation] 다음과 같은 방법으로 하나의 전기회로를 다른 것과 분리 - 이중절연 - 기본절연 및 전기적 보호차폐 - 강화절연 [IEV 195-06-19] 3.25 전기적 분리 (electrical separation) 회로의 위험충전부를 다른 모든 회로 및 부품, 대지 및 접촉으로부터 절연하는 보호대책 7 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
0feb5cd0-5f0d-4969-94d6-42bb9dba9b49 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 3.26 특별저압, ELV [extra-low-voltage(ELV)] KS C IEC 61201 에 규정된 관련 전압의 제한치를 초과 하지 않는 전압 3.26.1 SELV 시스템 (SELV system) 다음과 같은 상태에서 전압이 특별저전압을 초과 하지 않는 전기 시스템 정상상태하에서 - 다른 회로의 접지고장을 포함하는 단일 고장상태하에서 3.26.2 PELV 시스템 (PELV system) 다음과 같은 상태에서 전압이 특별저전압을 초과 하지 않는 전기 시스템 - 정상상태하에서 - 다른 회로의 접지고장을 제외한 단일 고장상태하에서 3.27 안정상태에서의 접촉전류 및 전하의 제한 (limitation of steady-state touch current and charge) 정상 및 고장 상태하에서 안정상태의 접촉전류 및 전하가 위험수준 이하로 제한되도록 회로 또는 기기의 설계를 통해 감전에 대한 보호를 하는 것. [IEV 826-03-16, 수정] 3.28 전류제한 전원 (limited-current-source) 다음과 같이 전기회로에 전기에너지를 공급하는 장치 위험충전부로부터 보호분리를 갖춤. - 정상 및 고장 조건하에서 안정상태의 접촉전류 및 전하를 위험수준 이하로 확실히 제한됨. 3.29 보호임피던스장치 (protective impedance device) 안정상태의 접촉전류 및 전하를 위험수준 이하로 확실히 제한하도록 하는 임피던스 및 구조를 갖는 부품이나 부품 집합체 3.30 (전기)숙련자 [(electrically) skilled person] 위 험을 인지하여 전기로 인한 재해를 피할 수 있도록 관련 교육 및 경험을 갖춘 사람 [IEV 195-04-01] 3.31 (전기)기능자 [(electrically) instructed person] 위험을 인지하여 전기로 인한 재해를 피할 수 있도록 숙련기술자로부터 적절한 충고 및 감독을 받은 사람 [IEV 195-04-02] 3.32 일반인 (ordinary person) 숙련자도 기능자도 아닌 사람 8 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
95d26629-e0f7-4f02-b9a4-bd5ce7a03980 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 [IEV 195-04-03] 3.33 보폭전압 (step voltage) 지표면상에서 사람의 보폭으로 간주되는 서로 1m 떨어져 있는 두 점 사이의 전위차 [IEV 195-05-12] 3.34 전위경도완화 (potential grading) 다수의 접지극을 사용하여 대지 전위, 특히 지표면의 전위경도를 완화하는 것. 3.35 위험구역 (danger zone) 고압의 경우에 직접접촉에 대하여 완전히 보호되지 않은 위험충전부 주위의 최소 이격거리에 의해 제한되는 구역 비고 위험구역에 들어가는 것은 위험충전부에 접촉하는 것과 동일한 것으로 본다. 3.36 누설전류 (leakage current) 정상운전조건에서 원하지 않는 도전성 경로로 흐르는 전류 [IEV 195-05-15] 3.37 고정형 기기 (stationary equipment) 고정 기기 - 영구접속기기 - 물리적 특성으로 인해 통상적으로 이동하지 않고 동일한 꽂음접속기에 꽂혀 있는 기기 3.38 보호도체전류 (protective conductor current) 보호도체에 흐르는 전류 (KS C IEC 60990 의 3.2 참조) 3.39 시스템 (system) 정의 된 상황에서 하나의 전체로서 그리고 주위로부터 독립된 것으로 간주되는 상호 관련을 가지는 요소들의 집합체 비고 1 이러한 요소들은 물적 대상 및 개념뿐만 아니라 그 결과(예를 들어, 조직 형태, 수학적 기법, 프로그래밍 언어)일 수도 있다. 비고 2 시스템은 시스템과 시스템 사이의 연결을 끊는 가상 표면에 의해 주위 및 다른 외부 시스템으로부터 분리된 것으로 간주한다. [IEV 351-11-01] 3.40 (전기)설비 [(electrical) installation] 특정 목적 또는 여러 목적을 충족하기 위해 협조된 특성을 갖는 연관된 전기기기의 집합체 [IEV 826-01-01] 9 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
a0097661-0745-4979-afdc-abf0f7a26388 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 3.41 단로 (isolation) 안전을 이유로 전기설비의 전부 또는 일부를 모든 전원에서 분리하여 전기설비의 전부 또는 분리된 부분을 무전압으로 하는 것을 의도하는 기능 [IEV 826-08-01] 3.42 임펄스내전압 (impulse withstand voltage) 명시된 조건에서 절연 파괴를 일으키지 않는 규정된 파형 및 극성의 임펄스 전압의 최대 파고 값 4 감전보호의 기본 규칙 위험 충전부는 접근이 불가능하여야 하며, 접근 가능한 도전부는 다음과 같은 경우에 위험충전이 되 지 않아야 한다. - 정상상태(사용 의도로 운전 시, KS A ISO/IEC Guide 51 의 3.13 참조 및 고장이 없는 상태)이거나 - 단일고장 상태(IEC Guide 104 의 2.8 참조) 비고 1 일반인에 대한 접근성의 규칙은 숙련자나 기능자의 규칙과 다를 수 있고 서로 다른 제품들 및 위치에 따라 또한 다를 수 있다. 비고 2 고압의 설비, 시스템 및 기기에서, 위험구역에 들어가는 것은 위험충전부에 접촉하는 것과 같다고 본다. 정상상태(4.1 참조)하에서의 보호는 기본보호에 의해 제공되고, 단일 고장상태(4.2 참조)에서의 보호 는 고장보호로 이루어진다. 강화 보호설비(4.2.2 참조)는 정상상태 및 고장상태 모두에 대한 보호를 제공한다. 4.1 정상상태 정상상태하에서 감전보호에 대한 기본원칙에 부합하기 위해서는 이 표준에 언급된 기본보호가 필요 하다. 기본보호의 구비 요건은 5.1 에 기술되어 있다. 비고 저압의 설비, 시스템 및 기기에서 기본보호는 일반적으로 KS C IEC 60364- 4-41 에서 사용되 는 것과 같이 직접접촉에 대한 보호에 해당한다. 4.2 단일 고장상태 다음의 경우를 단일고장상태라 한다. - 접근 가능한 비위험충전부가 위험충전부로 되는 경우(예를 들어, 안정상태의 접촉 전류 및 전하 제한의 실패로 인해) 또는 정상상태하에서 접근 가능한 비충전부인 도전부가 위험충전부로 되는 경우(예를 들어, 노출도전부 의 기본절연의 파괴로 인해) 또는 위험충전부에 접근 가능하게 되는 경우(예를 들어, 외함의 기계적 파괴로 인해)1) 단일고장상태에서 기본원칙에 부합하기 위해서는 이 표준에 언급된 고장보호가 필요하다. 이러한 보 1) 이러한 측면은 현재까지 고려되지는 않았으며, 적절한 기계적 요건 및 시험이 필요하고 전기적 파라미터 규 격으로는 대체할 수 없다. 10 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
da6ae206-48f5-41a5-85ca-189b4d56ad96 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 호는 다음에 의해 달성될 수 있다. - 기본보호(4.2.1 참조)와는 독립된 추가적인 보호설비 또는 - 기본보호와 고장보호 모두를 제공하는 강화보호 설비(4.2.2 참조) 가능한 모든 관련 영향을 고려한다. 고장보호용 설비요건은 5.2 에 기술되어 있다. 비고 저압의 설비, 시스템 및 기기에서 고장보호는 일반적으로 KS C IEC 60364 - 4-41 에서 사용되 는 것과 같이 간접접촉보호에 해당하고 특히 기본절연의 파괴에 대한 것이다. 4.2.1 2 개의 독립 보호설비를 통한 보호 2 개의 독립 보호설비 각각은 관련 기술위원회가 규정한 조건하에서 고장이 발생하지 않도록 설계되 어야 한다. 2 개의 독립 보호설비는 이들 중 하나의 고장이 다른 것을 손상하지 않도록 서로 간에 영향이 없어야 한다. 2 개의 독립 보호설비의 동시고장이 발생할 확률은 낮고 통상 고려할 필요가 없다. 남아 있는 유효한 하나의 보호설비에 의존할 수 있다. 4.2.2 강화보호설비를 통한 보호 강화보호설비의 특성은 2 개의 독립 보호설비가 제공하는 것과 같은 연속된 보호효과 가 있어야 한다. 강화보호설비의 요건은 5.3 에 주어져 있다. 4.3 특별한 경우 만일 대지전위를 갖는 사람과 저임피던스 접촉이 이루어지는 지역과 같이 사용상 증가된 내재적 위 험이 포함되는 경우에는 기술위원회는 추가보호의 규정에 대한 가능한 필요성을 고려해야 한다. 이 러한 추가 보호는 설비, 시스템 또는 기기에 구비될 수 있다. 비고 저압설비 및 기기에서 기본 및/또는 고장보호가 유효하지 않거나 기기 사용상의 부주의 에 대 해 정격 잔류전류 동작전류가 30 mA 를 초과 하지 않는 누전차단기를 사용하는 것이 감전에 대 한 추가보호로 인정된다. 이중고장 또는 다중고장의 결과 를 고려해야 될 수도 있으며, 특별한 경우에는 기술위원회의 판단에 맡길 수 있다. 5 보호설비(보호대책의 요소) 모든 보호설비는 의도한 대로 사용되고 적절히 유지되는 경우 설비, 시스템 또는 기기의 예상수명 동안 유효하도록 설계되고 제작해야 한다. 주위환경은 KS C IEC 60721 에 기술된 바와 같이 외부영향에 대한 등급을 고려하도록 한다. 특히 주 위온도, 기후조건, 물기의 존재, 기계적 응력, 사람의 능력 그리고 대지전위를 갖는 사람이나 동물의 접촉면적에 대한 주의 를 요한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 11 | {}
fc7ce8b1-ff61-4927-9c3c-1dbe2b4f932a | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 기술위원회에서는 절연협조 요건을 고려하여야 한다. KS C IEC 60664 - 1 에는 저압 설비, 시스템 및 기기에 대한 이러한 요건들이 기술되어 있으며 또한 고체절연의 치수산정 지침뿐만 아니라 (기중) 이 격거리 산정의 규칙도 제공하고 있다. 고압 설비, 시스템 및 기기에 관한 요건은 KS C IEC 60071-1 및 KS C IEC 60071 - 2 에 기술되어 있다. 5.1 기본보호용 설비 기본보호는 정상상태하에서 위험충전부와 의 접촉을 방지하는 하나 이상의 설비로 구성되어야 한다. 비고 페인트, 바니시, 래커 및 이와 유사한 제품만으로는 통상 정상사용 시에 감전보호용으로 적절 한 절연이 제공되지 못하는 것으로 간주한다. 5.1.1 5.1.8 에는 기본보호를 위한 약간의 개별규정을 명시하고 있다. 5.1.1 기본절연 5.1.1.1 고체가 기본절연으로 사용된 경우, 고체절연은 위험충전부로의 접촉을 방지하여야 한다. 비고 고압설비와 기기의 경우에 고체절연의 표면에 전압이 나타날 수 있기 때문에 추가적인 예방조 치가 필요할 수 있다. 5.1.1.2 기본절연을 공기로 할 경우에는 5.1.2 및 5.1.3 에 규정된 바와 같이 장애물, 장벽 또는 외함 으로 보호하거나 5.1.4 에 규정된 바와 같이 촉수범위 밖에 두어 보호하여야 한다. 5.1.2 장애물 또는 외함 5.1.2.1 장애물 또는 외함은 다음에 대한 보호를 하여야 한다. 저압 설비 및 기기의 경우에 KS C IEC 60529 에 의한 최소 IPXXB(또한 IP2X 도 적합)의 감전에 대한 보호등급으로 위험충전부에 접근 고압 설비 및 기기의 경우에 KS C IEC 60529 에 의한 최소 IPXXB(또한 IP2X 도 적합)의 보호등급 으로 위험지역에 들어가는 것. 5.1.2.2 장애물 및 외함은 주위환경 및 외함내부로부터 관련된 모든 영향을 고려하여 규정된 보호 등급을 유지할 수 있는 충분한 기계적 강도, 안정성 및 내구성을 갖고 있어야 한다. 이들은 정해진 위치에 확실하게 고정되어야 한다. 5.1.2.3 설계나 제작에서 장애물의 제거, 외함의 개방 또는 외함의 일부제거가 가능한 경우에는 위 험충전부로 접근하는 것이 다음에 의해서만 가능해야 한다. - 열쇠 또는 공구를 사용, 또는 외함이 보호를 못할 경우에는 공급회로로부터 위험충전부를 분리한 후, 전원의 복구는 격벽이나 외함의 일부를 원위치 시키거나 또는 문을 닫은 후, 또는 중간 장벽이 필요한 보호등급을 여전히 유지하고 있는 경우에는 이러한 장벽은 열쇠 또는 공구를 사용여야만 제거 가능 비고 8. 참조 5.1.3 장애물 12 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f7643944-300f-4ea6-b8cc-3143f2c0c9e1 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 5.1.3.1 장애물은 숙련기술자나 기능자를 보호하기 위한 것이며, 일반인을 보호할 의도는 아니다. 5.1.3.2 특수한 작동 및 사용 조건(8. 참조)하에 있는 설비, 시스템 또는 기기가 작동 중에 장애물은 다음을 방지하여야 한다. - 저압 설비 및 기기의 경우, 위험충전부와 무의 식적인 접촉 또는 - 고압 설비 및 기기의 경우, 위험구역에 무의 도적으로 들어가는 것. 5.1.3.3 장애물은 열쇠나 공구를 사용하지 않고 제거할 수도 있지만 무의 도적으로 제거되지 않도록 고정되어야 한다. 5.1.3.4 도전성 장애물이 기본절연만으로 위험충전부와 분리된 경우에는 그것은 노출도전부로서 고 장보호를 위한 조치(6. 참조)를 적용해야 한다. 5.1.4 촉수범위 밖에 설치 5.1.4.1 5.1.1.1, 5.1.2, 5.1.3, 5.1.5 및 5.1.6 에 명시된 규정이 적용 불가능할 경우에는 촉수범위 밖 에 설치하는 것이 다음 사항을 방지하는 데 적절하다. 저압 설비 및 기기의 경우에 위험 전압이 존재할 수 있는 도전부 간을 무의 도적으로 동시에 접근 하는 것. - 고압 설비 및 기기의 경우에 위험구역에 무의 도적으로 들어가는 것. 상세한 내용은 기술위원회가 규정하여야 한다. 비고 저압 설비의 경우, 2.5m 이상의 거리로 분리된 부분은 일반적으로 동시 접근이 가능한 것으로 간주하지 않는다. 숙련자 또는 기능자들만으로 접근이 제한되는 경우, 거리를 줄여 규정할 수 도 있다. 5.1.4.2 공구나 사다리와 같이 사람이 사용하거나 손으로 잡는 물체로 인해 거리가 감소할 것으로 예상되는 경우, 기술위원회는 관련 제한사항이나 위험 전압이 존재할 가능성이 있는 부분 사이의 적 정 거리를 규정하여야 한다. 5.1.5 전압의 제한 동시 접근가능 도전부 간의 전압이 KS C IEC 61201 에 규정된 특별저전압(ELV) 한계치를 초과 하지 않도록 전압제한이 이루어져야 한다. 비고 기본보호를 위한 이 규정은 고장보호를 위해 필요한 규정으로 적용하는 것은 아니다. 6.6 및 6.7 참조 5.1.6 안정상태의 접촉전류 및 전하의 제한 위험해지거나 감지할 수 있는 정도의 안정상태 접촉전류 및 전하의 값에 노출되는 사람이나 동물을 보호하도록 안정상태의 접촉전류 및 전하를 제한해야 한다. 비고 사람에 대해서는 다음의 값(100 Hz 까지의 주파수를 갖는 교류 값)이 지침으로서 주어져 있다. 감지 한계전류를 초과 하지 않는 2 000 �의 순저항을 통해 동시에 접근 가능한 도전부 간을 흐르는 안정상태 전류로 교류 0.5 mA 또는 직류 2 mA 가 권장된다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 13 | {}
c7689e7f-8e16-4248-a867-2d91b37e5790 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 고통 한계를 초과 하지 않는 전류 값으로는 교류 3.5 mA 또는 직류 10 mA 를 규정할 수 있 다. 동시 접근가능한 도전부 간의 충전전하가 0.5 �C(감지 한계치)를 초과 하지 않도록 권장하고 있으며, 고통한계치로는 50 mC 을 규정할 수 있다. 기술위원회는 자극반응용(예를 들어, 전기울타리)으로 특별히 필요한 부분에서의 충전전하 및 안정상태의 전류 값을 더 높게 규정할 수 있다. 심실세동 한계에 주의 할 필요가 있다. K S C IEC 60479-1 참조 안정상태의 교류전류 제한치는 주파수 15 Hz 에서 100 Hz 사이의 주파수를 갖는 정현파 전 류로 표시하고, 그 외의 주파수, 파형 및 직류가 중첩된 교류에 대한 값들은 현재 검토 중 이다. KS C IEC 60601 의 적용범위 내에서 의료용 전기기기는 다른 수준의 값을 필요로 할 수도 있다. 5.1.7 전위경도완화 고압 설비 및 기기의 경우에 전위경도완화용 접지극을 시설하여 정상 상태에서 위험한 보폭전압 및 접촉전압으로부터 사람과 동물을 보호하여야 한다. 비고 전위경도완화는 대표적으로 큰 대지 누설 전류가 발생하는 전기철도시스템에 사용되고 있다. 5.1.8 그 밖의 보호설비 기본보호를 위한 그 외의 규정은 기본적 규칙(4. 참조)에 따라야 한다. 5.2 고장보호 설비 고장보호는 기본보호 설비에 추가하여 하나 이상의 독립적인 설비로 구성되어야 한다. 하부항목 5.2.1 에서 5.2.8 까지는 고장보호를 위한 개별 설비를 규정하고 있다. 5.2.1 보조절연 보조절연은 기본절연에 규정된 바와 같이 동일한 응력에 견딜 수 있는 치수를 가져야 한다. 5.2.2 보호등전위본딩 보호등전위본딩 시스템은 다음 요소의 하나 또는 두 개 이상의 적절한 조합으로 구성해야 한다. - 기기에 보호등전위본딩을 위한 조치. 7. 참조 - 설비 내에 접지 또는 비접지된 등전위본딩(비고 참조) - 보호도체(PE) - PEN 도체 - 보호 차폐 - 전원의 접지점 또는 인위적 중성점 - 접지극(전위경도완화용 접지극을 포함) - 접지도체 비고 저압 설비에서 접지된 보호등전위본딩은 통상 다음으로 구성된다. 상호 연결되어 있는 주 등전위본딩 14 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
20aec694-44b6-404e-8bdd-9c10ef2d1afe | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 · 주 보호도체 · 주접지선 또는 주접지단자 · 건축물 내의 가스, 물 등을 공급하는 금속관 · 적용 가능한 경우, 금속구조물 일부, 중앙난방 및 공조시스템 · 케이블의 금속외장(통신케이블의 경우, 그 케이블의 소유자나 담당자가 허용할 경우) - 접근 가능한 도전부를 상호 연결하는 보조등전위본딩 - 특별한 조건이 있는 국부 지역에서 접근 가능한 도전부를 상호 연결하는 국부 등전위본딩 고압 설비 또는 시스템의 등전위본딩 시스템은 존재할 수 있는 특별한 위험, 예를 들어 높은 접촉전 압 및 보폭전압의 위험과 방전에 의해 노출도전부가 충전되는 위험을 방지하기 위해 접지해야 한다. 접지설비의 접지 임피던스는 위험한 접촉전압이 발생하지 않는 정격이어야 한다. 고장상태 하에서 충전상태로 될 우려가 있는 노출도전부는 접지설비에 접속해야 한다. 5.2.2.1 기본보호의 고장 시에 위험한 유효접촉전압이 발생할 수 있는 접근 가능한 도전부는, 예를 들어 노출 도전부 및 보호차폐, 보호등전위본딩 시스템에 접속해야 한다. 비고 충전상태가 되어 있는 노출도전부와 접촉을 통하여서만 충전부로 될 수 있는 전기기기의 도전 부는 그 자체를 노출도전부로 간주하지 않는다. 5.2.2.2 보호등전위본딩시스템은 절연고장 시에 부위 간 위험 전위차를 피할 수 있도록 충분히 낮 은 임피던스를 가져야 하며, 필요시 고장전류로 작동하는 보호장치와 함께 설치해야 한다(5.2.4 참조). 최대전위차 및 지속시간은 KS C IEC 60479- 1 에 근거해야 한다. 비고 1 이를 위해서는 보호 등전위본딩시스템의 서로 다른 요소들의 상대 임피던스 값에 대한 검토 가 필요할 수 있다. 비고 2 회로의 임피던스가 단일 고장 시에 안정상태 접촉전류를 제한하므로 인해 KS C IEC 60990 에 따라 측정하여 100 Hz 까지의 주파수를 갖는 교류는 실효치 3.5mA 또는 직류는 10 mA 를 초과 할 수 없을 경우에는 전위차를 고려할 필요가 없다. 비고 3 의료용 장소(KS C IEC 60601-1 에서 제한치 참조), 도전성이 높은 장소, 습한 지역 및 이와 유사한 지역과 같이 일부 환경이나 상황에서는 제한치를 낮게 할 필요가 있다. 5.2.2.3 보호 등전위본딩의 모든 부분은 고장전류로 인해 발생할 가능성이 있는 열적 및 기계적 스 트레스로 기본절연의 단락이나 고장의 결과 로 보호 등전위본딩시스템의 특성을 손상시키지 않도록 설계해야 한다. 비고 안전을 손상시키지 않는 일부 국부적 손상은, 예를 들어 외함의 금속판의 일부와 같은, 제품위 원회에서 제시하는 특별한 지침에 따라 고장이 발생한 부분만은 허용이 가능할 수 있다. 5.2.2.4 보호 등전위본딩의 모든 부분은 예상되는 내부 및 외부적 영향(기계적, 열적 및 부식 포함) 에 견딜 수 있어야 한다. 5.2.2.5 도전성 가동부품(예를 들어, 경첩 및 미끄럼접촉)은 5.2.2.2, 5.2.2.3, 5.2.2.4 의 요건을 충족 하지 못하는 한, 보호 등전위본딩시스템의 일부로 간주하지 않아야 한다. 5.2.2.6 설비, 시스템 또는 기기의 부품을 제거하려고 하는 경우, 어떤 부분으로의 전원공급이 우선 차단되지 않는 한, 그 부품을 제거할 때 설비, 시스템 또는 기기의 다른 부분의 보호 등전위본딩이 단절되지 않아야 한다. 5.2.2.7 5.2.2.8 에서 기술된 경우를 제외하고 보호 등전위본딩의 어떠한 부품도 전기적 연속성을 차 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 15 | {}
46b05ce8-786b-4cee-9397-f232987b316e | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 단하거나 또는 큰 임피던스를 도입시킬 것으로 예상되는 어떠한 장치도 포함되어서는 안 된다. 비고 이러한 요건은 보호도체의 연속성 검증이나 보호도체의 전류측정을 위해서 기술위원회에 의해 면제될 수도 있다. 5.2.2.8 보호 등전위본딩의 부품이 관련 전원선으로 동일 접속기 또는 꽂음접속기로 차단될 수 있 는 경우에 보호 등전위본딩은 전원선보다 먼저 차단되어서는 안 된다. 보호 등전위본딩은 전원의 재 접속보다 먼저 회복되어야 한다. 이러한 요건은 차단과 접속이 비가압 상태인 경우에만 가능한 기기 에서는 적용되지 않는다. 고압의 설비, 시스템 또는 기기에서는 기기의 주접점이 정격 충격파전압을 견디는 이격거리에 도달 하기까지는 보호등전위본딩이 단절되어서는 안 된다. 5.2.2.9 보호 등전위본딩 도체는 절연 또는 비절연에 관계없이 감기접속, 전자기기 내부의 이와 유 사한 배선 및 프린트기판의 트랙과 같이 손상시키지 않고는 분리시킬 수 없는 도체를 제외하고 형태, 위치, 표시나 색깔로 충분히 구분할 수 있어야 한다. 색깔 구분이 사용될 경우에는 KS C IEC 60446 에 따라야 한다. 5.2.3 보호 차폐 보호 차폐는 설비, 시스템 또는 기기의 위험충전부와 보호하려는 부분 간에 삽입된 도전성 스크린으 로 구성되어야 한다. 보호스크린은 다음과 같아야 한다. 보호스크린은 설비, 시스템 또는 기기의 보호 등전위본딩시스템에 연결되어야 하고 상호접속은 5. 2.2 요건을 따라야 한다. 보호스크린은 보호 등전위본딩시스템의 요소 요건에 따라야 한다. 5.2.2.2, 5.2.2.3 및 5.2.2.4 참조 5.2.4 고압 설비 및 시스템에서 표시 및 차단 고장을 표시하는 장치가 구비되어야 한다. 중성점 접지방식에 따라 고장 전류는 수동 또는 자동 (5.2.5 참조) 중 하나에 의해 차단되어야 한다. 고장 지속시간에 대한 접촉전압의 허용 값은 KS C IEC 60479- 1 에 따라 기술위원회에서 규정해야 한다. 5.2.5 전원의 자동차단 전원의 자동차단은 다음에 의한다. - 보호 등전위본딩시스템이 설치되어 있어야 하며 기본절연의 고장 시 고장전류로 작동하는 보호장치는 기기, 시스템 또는 설비에 전기를 공급하는 하나 또는 그 이상의 선도체를 차단해야 한다. 5.2.5.1 보호장치는 KS C IEC 60479- 1 에 기초하여 기술위원회에서 규정한 시간 내에 고장전류를 차단하여야 한다. 저압설비에서 그 규정시간은 보호 등전위본딩 구내에서 발생하는 예상접촉전압에 의한다. 비고 감전에 대한 보호와 관련하여 차단할 필요가 없는 안정상태 고장전류에 대해서는 규약접촉전 압 제한치 UL 을 규정할 수 있다. 5.2.5.2 보호장치는 설비, 시스템 또는 기기의 적절한 부위 어느 곳에든 설치할 수 있고 고장전류루 16 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
9e44f95f-84ea-430a-97d6-ea484a319232 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 프의 특성을 고려하여 선정해야 한다. 5.2.6 (회로 간) 단순분리 회로와 다른 회로 또는 대지 간의 단순분리는 주어진 최고전압에 대한 정격의 기본절연에 의해 달성 될 수 있다. 어떤 부품을 분리된 회로 간에 연결하는 경우에는 그 부품이 브리지 절연용으로 규정된 전기적 스트 레스를 견디어야 하며, 브리지 임피던스는 그 부품을 통해서 흐르는 예상전류를 5.1.6 에 지시된 안정 상태의 접촉전류 값으로 제한해야 한다. 5.2.7 비도전성 환경 비도전성 환경은 대지에 대하여 최소한 다음과 같은 임피던스를 가져야 한다. 공칭 계통전압이 교류 또는 직류 500 V 이하일 경우에는 50 k� - 공칭 계통전압이 교류 또는 직류 500 V 를 초과 하고 교류 1 000 V 또는 직류 1 500 V 이하일 경우 에는 100 k�(교류의 주파수는 100 Hz 까지) 비고 1 절연성 바닥 및 벽의 저항 측정방법은 IEC 60364- 6-61 의 부속서 A 에 포함되어 있다. 비고 2 더 높은 전압에 대한 임피던스 값은 고려 중 5.2.8 전위경도완화 전위경도완화는 고장 시에 나타나는 접촉전압 및 보폭전압을 저감하기 위해 추가 접지극을 설치하여 달성할 수 있다. 비고 접지극은 일반적으로 기기나 도전부의 1m 앞의 거리에, 지표면 아래 0.5m 깊이에 매설하여 접지설비에 연결한다. 5.2.9 그 밖의 설비 고장보호를 위한 다른 어떠한 설비도 기본적 원칙에 따라야 한다(4. 참조). 5.3 강화 보호설비 강화 보호설비는 기본보호 및 고장보호 모두를 구비해야 한다. 세부항목 5.3.1 에서 5.3.5 까지는 이러한 강화 설비를 규정하고 있다. 강화 보호설비에 의한 보호는 보호효과 가 저감되지 않고 단일고장이 발생되지 않도록 설치되어야 한 다. 5.3.1 강화절연 강화절연은 2 중절연(기본절연 및 보조절연은 각각 3.10.1 및 3.10.2 참조)과 동일한 보호신뢰도를 가 지도록 전기적, 열적, 기계적 및 환경적 스트레스를 견딜 수 있도록 설계해야 한다. 비고 1 이것은 기본절연에 대해 규정한 것보다 더욱 가혹한 설계 및 시험조건을 요구한다. 17 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
bd67163f-9d4c-40b1-ab8c-f0264bdab60c | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 비고 2 저압에 적용되는, 예를 들어 과전압 범주[IEC 60364 - 4-4432) 참조]의 개념이 적용되는 충격 파전압과 관련한 강화절연의 설계는 기본절연에 대해 규정한 것보다 한 단계 높은 범주의 과전압 요건에 따르도록 규정되어 있다. 비고 3 강화절연은 주로 저압설비와 기기에 사용되지만, 고압 설비 및 기기에의 적용을 배제하는 것은 아니다. 5.3.2 회로 간 보호분리 한 회로와 다른 회로 간의 보호분리는 다음의 어느 하나의 수단으로 이루어져야 한다. 각각의 최고전압에 대한 정격의 기본절연 및 보조절연, 즉 이중절연 - 각각의 최고전압에 대한 정격의 강화절연(5.3.1) - 인접회로의 전압에 대한 정격의 기본절연에 의해서 각 인접회로로부터 분리된 보호차폐물(5.2.3) 을 갖는 보호 차폐(6.6 의 마지막 구절 참조) 이러한 수단들의 조합 분리된 회로의 도체가 다른 회로의 도체와 함께 다심 케이블 또는 다른 도체의 집합에 포함되는 경 우, 그들은 이중절연이 되도록 최고전압에 대해 개별적으로 또는 집합하여 절연해야 한다. 어떤 부품이 분리된 회로 간에 연결될 때 그 부품은 보호임피던스장치의 요건을 따라야 한다. 5.3.4 참조 5.3.3 전류제한 전원 전류제한 전원은 5.1.6 에 제시된 제한 값을 초과 하는 접촉전류를 공급할 수 없도록 설계되어야 한다. 5.1.6 의 요건은 전류제한 전원의 단일부품에 고장이 발생할 가능성 3)이 있을 때에도 적용한다. 비고 제한 값은 관련 기술위원회에서 결정한다. 5.3.4 보호임피던스장치 보호임피던스장치는 5.1.6 에 기술된 값으로 접촉전류를 확실히 제한해야 한다. 보호임피던스장치는 브리지 절연용으로 규정된 전기적 스트레스를 견뎌야 한다. 이러한 요건은 보호임피던스장치의 단일부품에 고장이 발생할 가능성 3)이 있을 때도 적용한다. 5.3.5 그 밖의 설비 기본보호 및 고장보호 모두를 위한 그 밖의 강화보호설비는 기본적 규칙에 따라야 한다(4. 참조). 6 보호 대책 이 항은 전형적인 보호대책의 구조에 대해 기술하고 경우에 따라 기본보호 및 고장보호를 위한 보호 2) 이 표준은 KS C IEC 60364 - 4-44 로 대체될 예정이다. 3) 예를 들어, 부품 관련 안전특성을 전자부품 품질인증제도(IECQ)에서 규정하고 관리할 경우에는 정확하게 사 용된 인증 부품의 고장은 발생하지 않는 것으로 간주한다. 18 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
3526ba10-be63-49a1-a62f-290778e22b21 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 설비인지를 보여준다. 다음의 보호대책 중 두 가지 이상을 동일한 설비, 시스템 또는 기기 내에서 사용할 수 있다. 6.1 전원의 자동차단에 의한 보호 보호대책은 다음에 의한다. - 기본보호는 위험충전부와 노출도전부 사이의 기본절연에 의해 제공되며 - 고장보호는 전원의 자동차단에 의해 제공된다. 비고 전원의 자동차단은 5.2.5 에 따라 5.2.2 에 규정된 보호 등전위본딩시스템이 필요하다. 6.2 이중 또는 강화절연에 의한 보호 보호대책은 다음에 의한다. - 기본보호는 위험충전부의 기본절연에 의해 제공되며 - 고장보호는 보조절연에 의해 제공되거나 - 기본보호 및 고장보호는 위험충전부와 접근가능 부위(접근가능 도전부와 접근가능 절연재료의 표 면) 간의 강화절연에 의해 제공된다. 6.3 등전위본딩을 통한 보호 보호대책은 다음에 의한다. - 기본보호는 위험충전부와 노출도전부 간의 기본절연 - 고장보호는 동시 접근 가능한 노출도전부와 계통외도전부 간의 위험전압을 방지하는 보호 등전위 본딩 시스템 6.4 전기적 분리에 의한 보호 보호대책은 다음에 의한다. - 기본보호는 위험충전부와 분리된 회로의 노출도전부 간의 기본절연에 의해 제공되며 - 고장보호는 다음에 의해서 제공 · 다른 회로와 대지로부터 분리된 회로의 단순분리 · 기기의 둘 이상의 부품이 분리된 회로에 접속된 경우에 분리된 회로의 노출도전부를 상호 연결 하는 비접지 보호등전위본딩 노출도전부를 보호도체나 접지도체에 의도적으로 연결하는 것은 허용되지 않는다. 비고 1 전기적 분리는 주로 저압설비나 기기에 사용되나 고압설비나 기기에의 적용도 배제하지는 않는다. 비고 2 저압설비용으로 KS C IEC 60364 - 4-41 의 413.5 에 제공된 전기적인 분리는 더 엄격한 요건 을 포함하고 있다. 6.5 비도전성 환경에 의한 보호 19 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
037f5921-2bfb-4b50-96ae-7aa972557065 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 보호대책은 다음에 의한다. - 기본보호는 위험충전부와 노출도전부분 간의 기본절연에 의해 제공되며 - 고장보호는 비도전성 환경에 의해 제공 6.6 SELV 에 의한 보호 다음에 의해 제공되는 보호대책에 의한다. - 회로의 전압제한(SELV 시스템) - SELV 및 PELV 이외의 모든 회로로부터 해당 SELV 시스템의 보호분리 - 다른 SELV 시스템, PELV 시스템 및 대지로부터 해당 SELV 시스템의 단순분리 노출도전부를 보호도체나 접지도체에 의도적으로 연결하는 것은 허용되지 않는다. SEVL 가 필요하고 5.3.2 에 따라 보호차폐가 적용되는 특별한 장소에서 보호차폐물은 최고 전압에 대 하여 기본절연을 통해 각각의 인접한 회로로부터 분리되어야 한다. 6.7 PELV 에 의한 보호 다음에 의해 제공되는 보호대책에 의한다. - 접지할 수도 있는 회로 및/또는 접지할 수도 있는 노출도전부의 전압제한(PELV 시스템) - SELV 및 PELV 이외의 모든 회로로부터 해당 PELV 시스템의 보호분리 만약 해당 PELV 회로가 접지되고 5.3.2 에 따라 보호차폐가 사용된 경우에는 보호차폐와 PELV 시스 템 간의 기본절연은 필요가 없다. 비고 1 PELV 시스템의 충전부에 동시에 접근이 가능하며 고장 시에 1 차 회로의 전위를 가질 수 있 는 도전부에 대한 감전보호는 이러한 모든 도전부 간의 보호 등전위본딩에 의존한다. 비고 2 6.6 및 6.7 에 따르는 것 이외의 ELV 사용은 보호조치가 아니다. 6.8 안정상태의 접촉전류 및 전하제한에 의한 보호 다음에 의해 제공되는 보호대책에 의한다. 회로의 전기공급은 다음에 의한다. · 제한전류원으로부터 공급 · 보호임피던스장치를 통하여 공급 - 위험충전부에서 회로의 보호분리 6.9 그 밖의 대책에 의한 보호 그 밖의 어떠한 보호조치도 기본 규칙(4. 참조)을 따라야 하고 기본보호 및 고장보호가 제공되어야 한다. 7 전기설비 내의 기기 및 보호설비의 협조 보호는 설치방법과 함께 기기 및 장치에 대한 구조적 배치의 조합으로 이루어진다. 기술위원회는 6. 20 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
87262610-4f7c-4797-a939-614c779c70d7 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 에 기술된 보호조치를 사용하도록 권장한다. 기기가 등급화될 수도 있다. 기기의 몇 가지 등급에 대한 보호설비의 사용은 7.1 에서 7.4 에 기술되어 있다(표 1 참조). 이러한 방법으로 기기 및 장치를 구분하는 것이 적합하지 않을 경우에는 기술위원회는 제품들에 대 한 적절한 설치방법을 규정해야 한다. 일부 기기는 분류에 따른 적합성이 설치 후에야 얻어질 수 있는데, 일 예로 설치 후 충전부에 접근 이 불가능한 경우이다. 이러한 경우에는 적절한 지침을 제조자나 책임판매자가 제시해야 한다. 7.1 0 급 4) 기기 기본보호용 설비로 기본절연이 있고 고장보호용 설비가 없는 기기 7.1.1 절연 적어도 기본절연으로 위험충전부를 분리시키지 않은 모든 도전부는 위험충전부로 취급해야 한다. 7.2 1 급 기기 기본보호용 설비로는 기본절연이 되어 있고 고장보호 설비로는 보호본딩을 갖춘 기기 7.2.1 절연 적어도 기본절연으로 위험충전부를 분리시키지 않은 모든 도전부는 위험충전부로 취급해야 한다. 또 한 이는 기본절연으로는 분리되었으나 기본절연에서 규정한 동일한 스트레스에 대해 설계되지 않은 부품을 통해 위험충전부와 연결되는 도전부에도 적용한다. 7.2.2 보호 등전위본딩 기기의 노출도전부는 보호본딩 단자에 연결되어야 한다. 비고 1 노출도전부는 페인트, 바니시, 래커 및 이와 유사한 제품만으로 피복된 것을 포함한다. 비고 2 접촉 가능한 도전부가 보호분리에 의해 위험충전부로부터 분리되어 있는 경우에는 노출도전 부가 아니다. 7.2.3 절연재료의 부분이 접근 가능한 표면 기기가 도전부로 완전히 덮여지지 않은 경우에는 다음의 사항을 절연재료의 접근 가능부위에 적용한 다. 절연재료의 접근 가능 표면이 - 잡을 수 있도록 설계된 경우 - 위험전위가 전달될 수 있는 도전성 표면과 접촉할 가능성이 있는 경우, 또는 4) 국제표준에서는 0 급 기기를 배제하는 것을 권장하지만, 상당한 제품표준에서 여전히 이 등급을 언급하고 있기 때문에 이 내용에 포함시켰다. 21 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
7bdc18ad-e841-4b14-9f86-dec6e0a76640 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 - 인체의 일부와 상당히 면적으로 접촉(50mmx50mm 이상)할 수 있을 경우, 또는 - 오염물질의 도전성이 높은 지역에서 해당 부위가 사용될 경우 그 표면은 다음에 의해서 위험충전부로부터 분리되어야 한다. - 2 중 절연 또는 강화절연, 또는 - 기본절연 및 보호차폐, 또는 - 이러한 조치들의 조합 절연재료의 모든 접근 가능한 부분의 표면은 적어도 기본절연으로 위험충전부로부터 분리시켜야 한 다. 고정설비의 일부로 사용될 기기는 제조자가 기본절연을 시행하거나 또는 제조자나 또는 책임판 매자의 설명서에 명시한 바와 같이 설치 시에 기본절연이 제공되어야 한다. 이러한 요건은 절연재료의 접근 가능부위가 요건에 맞는 절연이 되어 있을 경우에는 적합한 것으로 간주한다. 비고 기술위원회는 인체와 접촉하게 되는 표면적을 고려하여 (예를 들어, 운전장치와 같이 자주 접 촉할 필요가 있는) 절연재료의 접근 가능한 특정부분에 대하여 기본절연보다 더 엄격한 요건 을 부과 할 수도 있다. 7.2.4 보호도체의 접속 7.2.4.1 접속장치는 꽂음접속기 접속을 제외하고 IEC 60417 - 2 의 5019 번 그림기호나 PE 문자 또 는 녹색과 노랑의 이중조합색으로 명확하게 확인될 수 있어야 한다. 도체의 접속 시 벗겨질 수 있는 나사, 와셔나 기타 부위에 표식을 하거나 고정해서는 안 된다. 7.2.4.2 코드로 접속하는 기기는 변위 방지장치의 고장 시에도 코드 내 보호도체가 마지막으로 단 로되는 도체가 되도록 만들어져야 한다. 7.3 11 급 기기 11 급 기기란 다음의 것을 말한다. - 기본보호 조치로 기본절연을 구비 - 고장보호 조치로 보조절연을 구비 - 기본보호 및 고장보호가 강화절연으로 구비 7.3.1 절연 7.3.1.1 접근가능 도전부 및 접근가능 부분의 절연재 표면은 다음 중 어느 하나이어야 한다. - 2 중절연 또는 강화절연으로 위험충전부에서 분리, 또는 - 동등한 보호가 제공되도록 설치상의 구성으로 설계, 예를 들어 보호임피던스장치 고정되는 설비의 일부가 되는 기기는 이 기기가 적절히 설치되었을 때 이 요건이 충족되어야 한다. 이것은 절연(기본, 보조 또는 강화) 및 보호임피던스를, 관련이 있는 경우 제조자가 제공하거나 또 는 제조자가 명시한 또는 책임판매자가 그의 설명서에 명시한 대로 설치 시에 구비하여야 함을 의 미한다. 22 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
ae36e864-e3e4-4fc5-baa4-72943ade6c69 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 비고 동등한 고장보호가 제공되는 구성방법은 기기의 특성 및 적용에 적합한 요건에 따라 기술위원 회에서 규정할 수도 있다. 7.3.1.2 기본절연만으로 또는 등가보호가 가능한 구성상의 방법으로 위험충전부에서 분리된 모든 도전부는 보조절연이나 등가보호가 가능한 구성상의 방법으로 접근 가능 표면으로부터 분리되어야 한다. 최소한 기본절연에 의해 위험충전부로부터 분리되지 않은 모든 도전부는 위험충전부로 간주되어야 한다. 즉, 7.3.1.1 에 따라 접근가능 표면으로부터 분리되어야 한다. 7.3.1.3 외함의 설치 및 유지 시에 나사 또는 다른 고정장치를 제거할 필요가 있거나 제거될 가능 성이 있는 경우와 금속나사 또는 다른 고정장치의 교체 시 필요한 절연이 손상될 수 있는 경우, 외 함은 이러한 절연재 고정용의 나사 또는 다른 고정장치를 포함해서는 안 된다. 7.3.2 보호접속 접촉 가능한 도전부와 중간부위는 보호도체의 기능으로서는 어떤 접속방법에 의해서도 의도적으로 연결해서는 안 된다. 7.3.2.1 기기가 보호등전위본딩의 연속성을 유지하기 위한 조치가 구비되어 있으나 다른 모든 측면 에서는 II 급기기로 제작된 경우에는 그러한 조치가 다음과 같아야 한다. - 기기의 충전부 및 접근 가능한 도전부는 기본절연이 되어야 하고 - I 급 기기에 필요한 표시를 한다. 해당 기기는 7.3.3 에 언급된 기호로 표시해서는 안 된다. 7.3.2.2 11 급 기기에는 관련 IEC 표준에서 필요성이 인정될 경우에만 기능용(보호용과 는 달리)으로 대지에 연결하는 장치를 구비할 수 있다. 7.3.3 표시 11 급 기기는 IEC 60417-2 의 5172 번 그림기호로 전원정보 가까이에 표시되어야 하는데, 예를 들어 정격명판 위에는 이 기호가 기술적 정보의 일부임이 분명하고 제조자의 이름 또는 다른 확인 표시사 항과 혼란이 발생하지 않도록 표기해야 한다. 7.4 III 급 기기 기본보호가 ELV 값의 전압제한에 의존하며 고장보호는 구비되지 않은 기기 7.4.1 전압 7.4.1.1 기기의 최고 공칭전압이 교류 50 V 또는 직류 120 V(맥동이 없는)를 초과 하지 않도록 설계 되어야 한다. 비고 1 무맥동(ripple-free)이란 실효맥동전압이 직류성분의 10 % 이하인 것으로 규약상 정의 되어 있 다. 비정현파 교류전압의 최대치는 현재 고려 중이다. 비고 2 KS C IEC 60364 - 4-41 의 411.에 따라 III 급 기기는 SELV 및 PELV 시스템에만 접속이 허용 된다. 23 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
a2bd2659-652b-40cc-bb3c-5bbab1d9cf76 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 7.4.1.2 내부회로는 7.4.1.1 에 규정된 한계치를 초과 하지 않는 어떤 공칭전압에서도 운전할 수 있다. 7.4.1.3 기기 내에 단일고장의 경우에는 나타나거나 발생할 수 있는 안정상태의 접촉전압은 7.4.1.1 에 규정된 한계를 절대로 초과 해서는 안 된다. 7.4.2 보호 접속 III 급 기기는 보호도체용으로서의 연결장치가 구비되어서는 안 된다. 그러나 관련 IEC 표준에서 그러 한 필요성이 인정된 경우에는 기능용(보호용과 달리)으로 대지와 의 연결장치를 구비할 수 있다. 어떠 한 경우에도 기기 내에 충전부를 대지에 연결하는 장치가 만들어져서는 안 된다. 7.4.3 표시 기기는 IEC 60417 - 2 의 그림기호 5180 번으로 표시하여야 한다. 이 요건은 전원으로의 접속수단이 특별히 설계된 SELV 또는 PELV 전원설비에만 맞도록 만들어진 경우에는 적용하지 않는다. 표 1 - 저압 설비에서 기기의 적용 ¦ 기기의 등급 ¦ 기기의 표시 또는 지침 ¦ 기기를 설비에 접속하는 조건 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 0 급 ¦ - 비도전성 환경에서만 사용 - 전기적 분리를 통한 보호 ¦ 비도전성 환경 ¦ ¦ 0 급 ¦ - 비도전성 환경에서만 사용 - 전기적 분리를 통한 보호 ¦ 각 개별 기기에 제공된 전기적 분리 ¦ ¦ I 급 ¦ IEC 60417-2 의 5019 번 기호로 보호본딩단 자를 표시, 또는 PE 문자, 또는 녹색-노랑의 조합색 ¦ 이 단자를 설비의 보호등전위본딩에 연 결한다. ¦ ¦ 11 급 ¦ IEC 60417-2 의 5172 번 기호로 표시 ¦ 설비보호조치에 대한 신뢰성 없음. ¦ ¦ III 급 ¦ IEC 60417-2 의 5180 번 기호로 표시(마름 모 내에 로마 숫자 III) ¦ SELV 나 PELV 시스템에만 연결 ¦ 7.5 접촉전류, 보호도체전류, 누설 전류 비고 1 7.5 는 저압 설비, 계통 및 기기에만 적용한다. 비고 2 누설전류의 영향은 이 표준에서 현재 고려하지 않았다. 7.5.1 접촉전류 접근 가능한 부분에 접촉되었을 때 KS C IEC 60479 시리즈 표준에 표시된 바와 같이 위험을 초래하 지 않도록 대책을 마련하여야 한다. 접촉전류는 KS C IEC 60990 에 따라 측정되어야 한다. 고장 상태 에서 추가적인 접촉전류를 허용하는 경우, 제품위원회는 그 조건 및 추가 허용 전류를 그 표준에서 특별히 인지시켜야 한다. 비고 I 급 기기에서 보호도체가 상실된 경우의 접촉전류 측정은 KS C IEC 60990 의 6.2.2 에서 다루고 있다. 24 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c635710a-bb43-4fd9-a2c1-ce1e62a4eb30 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 7.5.2 보호도체전류 설비 및 기기 내에서 전기설비의 안전 또는 정상적인 사용을 해치는 과도한 보호도체전류를 방지하 기 위한 대책이 마련되어야 한다. 기기로 공급되거나 기기에 의해서 발생하는 모든 주파수의 전류에 대한 적합성이 보장되어야 한다. 7.5.2.1 전류사용기기의 과도한 보호도체전류의 방지를 위한 요건 통상의 운전상태에서 보호도체에 전류가 흐르는 전기기기에 대한 요건은 정상적인 사용이 허용되고 보호대책에 적합하여야 한다. 7.5 의 요건은 꽂음접속기에 의해, 또는 영구적 접속에 의해 전원을 공급 받거나 또는 고정기기의 경우에 대해 고려하고 있다. 7.5.2.2 전류사용기기의 보호도체 교류 전류의 최대 한계 비고 보호도체전류 측정방법은 KS C IEC 60479 - 2 에 따른 고주파 성분의 가중치를 고려하여 TC 74 에서 검토 중이다. 측정은 납품된 상태의 기기에 대해서 수행한다. 다음 제한 값들은 정격 주파수 50 Hz 또는 60 Hz 로 공급되는 기기에 적용한다. a) 정격 32A 이하의 단상 또는 다상 꽂음접속기가 갖추어진 전기사용기기. 제한 값은 부속서 B 에 주어져 있다. b) 보호도체에 대한 특별한 대책이 없이 영구적 접속을 위한 전기사용기기와 고정형 전기사용기기 또는 정격 32 A 를 초과 하는 단상 또는 다상 꽂음접속기가 갖추어진 전기사용기기. 제한 값은 부속 서 B 에 주어져 있다. c) 7.5.2.4 에 의한 강화보호도체에 접속되도록 의도된 영구적 접속용의 전기사용기기. 보호도체전류가 1 상당 정격 입력전류의 5 %를 절대로 초과 하지 않는 범위에서 제품위원회가 최대 값을 결정하는 것이 바람직하다. 그러나 보호 목적상 설비에 누전차단기를 설치할 수는 있으나, 이 경우 제품위원회는 보호도체전류 가 누전차단기에 의한 보호대책에 적합한지를 고려해야 한다. 대안으로는 별도의 권선을 가지며 적 어도 단순 분리된 변압기를 사용하여야 한다. 7.5.2.3 직류 보호도체전류 정상적인 사용에서 교류 기기는 누전차단기 또는 다른 기기의 고유의 기능에 영향을 미치는 직류 성 분을 포함한 전류를 보호 도체에 발생시키지 않아야 한다. 비고 직류 성분을 포함한 고장 전류에 대한 요건은 고려 중이다. 7.5.2.4 10 mA 초과 보호도체전류용 강화보호도체회로에 접속하는 기기의 대책 전기사용기기에는 다음의 것이 구비되어야 한다. - 단면적이 구리 10mm2 또는 알루미늄 16mm2 이상인 보호도체 접속용으로 설계된 접속단자 또는 - 전기사용기기에 두 번째 보호도체를 접속하기 위해 통상적인 보호도체와 동일한 단면적의 보호도 25 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
341b58a1-77a4-463e-a5a5-1ec5c2fdcec7 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 체를 접속하도록 설계된 제 2 단자 7.5.2.5 정보의 제공 강화보호도체에 영구적으로 접속하는 기기의 보호도체 전류 값은 제조자의 문서에 제공되어야 하며, 기기를 7.5.3.2 의 규정에 의하여 시설하여야 한다는 것을 설치설명서에 나타내야 한다. 7.5.3 그 밖의 요건 7.5.3.1 신호시스템 건축전기설비에서는 보호도체뿐만 아니라 어떠한 충전도체도 신호용 귀로로 사용해서는 안 된다. 7.5.3.2 설비 내 10 mA 초과 보호도체 전류용 강화보호도체 회로 영구접속용으로서 보호도체 전류가 10 mA 를 초과 하는 전기사용기기는 KS C IEC 60364-5-54 에 기 술된 바와 같이 접지계통에 견고하고 확실하게 접속할 수 있도록 구비되어야 한다. 7.6 고압 설비의 안전, 경계 이격 및 경고 표시 설비는 위험구역으로의 접근이 제한되도록 설계되어야 한다. 숙련자 및 기능자가 운전과 정비를 위 해 접근할 필요성을 고려해야 한다. 안전거리를 확보할 수 없는 경우에는 영구적인 보호시설을 설치 하여야 한다. 기술위원회는 다음의 값을 규정해야 한다. - 격벽 이격거리 - 장애물 이격거리 - 외부울타리 및 출입문의 높이 - 출입 구역에서의 최소 높이 및 거리 - 건축물과 의 이격거리 경고표시는 모든 출입문, 울타리, 격벽 및 가공선로의 전주와 철탑 등에 확연히 보이도록 하여야 한 다. 8 특별한 작업 및 운전조건 비고 예를 들어, 다음과 같은 전기설비의 작업에 대한 상세 요건은 해당 기술위원회의 고려 과제이 다. - 활선 작업 - 정전 작업 - 충전부 근접 작업 8.1 수동조작 장치와 수동교환용 부품 비고 1 설비, 시스템 또는 기기의 기능의 (재)확립을 위한 것. 예를 들어, - 초기화(reset)가 필요한 장치(예를 들어, 차단기, 과전류/과전압/부족전압 보호장치) - 교환 가능한 부품(예를 들어, 램프, 퓨즈링크) 8.1.1 은 또한 사용자 정비를 위한 접근에 대해 적용한다. 비고 2 이 표준의 목적상 "수동"은 "공구의 유무에 관계없이 손으로 하는 것"을 의미한다. 26 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
2c7cb155-7f31-42fd-84fb-e9cb324604a9 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 8.1.1 저압 설비, 시스템 및 기기에서 일반인이 조작하는 장치 또는 교환하는 부품 위험충전부와 의 어떠한 접촉에 대한 보호도 장치의 조작이나 부품을 교환할 때에 유지되어야 한다. 비고 기존의 IEC 표준에 적합한 특정 램프홀더 및 퓨즈홀더는 부품을 교환할 시에 이 요건을 충족 하지 않는 것으로 알려져 있다. 8.1.1.1 설비, 시스템 또는 기기에 수동조작이 필요한 장치나 수동교환이 필요한 부품이 조합된 경 우에 이러한 장치 및 부품은 위험충전부에 접근할 수 없는 장소에 설치되어야 한다. 8.1.1.2 8.1.1.1 에 따르는 것이 곤란한 경우에는 위험충전부에 접근하기 전에 전원으로부터 확실히 단로하는 방법으로 보호해야 한다. 8.1.2 숙련자 또는 기능자가 조작하는 장치나 교환하는 부품 다음과 같은 경우, 8.1.2.1 및 8.1.2.2 에 따라 위험충전부로의 비의 도적인 접근을 막기 위한 보호가 이루어져야 한다. - 장애물 또는 외함이 없거나, 또는 - 장애물이나 외함을 숙련기술자나 기능자가 수동조작이 필요한 장치나 필요한 부품의 교환을 위해 접근하기 위하여 제거할 수 있는 경우 비고 기술위원회는 이 세부항목을 제한하거나 추가요건을 부과 할 수도 있으며, 이 보호방법이 허용 되는 수동조작의 종류를 규정할 수도 있다. 8.1.2.1 장치 및 부품의 위치 기기는 쉽고 안전하게 장치를 조작하거나 부품을 교환할 수 있는 위치에 있는 사람에게 장치와 부품 에 접근 가능하며 잘 보이도록 설계되고 설치되어야 한다. 비고 제조자가 제공하는 이러한 위치 및 관련정보를 기술위원회가 적절히 규정하는 것이 바람직하 다. 기기를 설치한 위치가 장치나 부품을 보거나 접근에 위험을 야기할 수 있는 악영향을 줄 수도 있는 경우에는 요구되는 설치위치가 지시되고 준수되어야 한다. 8.1.2.2 접근성 및 조작 조작에 필요한 공간이나 장치로의 접근경로는 적절한 거리에 의해서 위험충전부와 의 비의 도적인 접 촉보호 또는 비의 도적인 위험구역으로의 진입에 대한 보호가 되도록 하여야 한다. 해당 거리는 기술 위원회가 규정해야 한다. 대안으로서, 접근경로나 공간이 위험충전부로부터의 적정거리보다 작을 경우에는 장애물을 설치해야 한다. 이러한 장애물은 비의 도적인 접촉을 보호할 수 있는 것이어야 한다. 보호수준은 부품이나 장치 에 접근하는 방향으로부터는 KS C IEC 60529 의 IPXXB(IP2X 도 적합) 이상이거나 기타 적정방향으로 부터는 KS C IEC 60529 의 IPXXA(IP1X 도 적합) 이상이어야 한다. 8.2 단로 후 전기적인 값 27 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b7d28d37-ab03-4f70-940e-7bdf395fb066 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 전원으로부터 위험충전부의 단로를 통해 보호가 이루어지는 경우(예를 들어, 외함의 개방이나 격벽의 제거)에는 충전전하는 단로 후 5 초 이내에 KS C IEC 61201 의 6.5 에 규정된 전압 제한치를 초과 하지 않도록 자동적으로 방전되어야 한다. 이것이 기기의 적정 기능을 저해할 수도 있는 경우에는 제한 값까지의 방전시간을 나타내는 쉽게 볼 수 있는 경고표시를 설치하여야 한다. 비고 1 특별한 조건(예를 들어, 플러그 인출)에 대해서는 기술위원회가 보다 짧은 시간을 지정할 수 도 있다. 비고 2 단로 후에 고압의 범위에서는 특히 다음의 영향을 고려한다. - 커패시터는 큰 잔류 전하를 가질 수 있다. - 인덕턴스, 예를 들어 변압기 권선은 비교적 장시간 큰 포착전하(trapped charge)를 가질 수 있다. 8.3 단로장치 8.3.1 일반사항 단로장치는 모든 전기공급 충전도체로부터 해당 회로를 효과 적으로 단로해야 한다. 비고 1 저압 관해서는 8.3.2 도 참조 단로 위치에서의 접촉자 또는 다른 단로 수단의 상태를 외부에서 볼 수 있거나 명확하고 확실하게 표시해야 한다. 비고 2 그 표시는 단로 및 폐로 위치 각각을 적절하게 표시한다. 단로에 적합한 장치들은 의도하지 않은 또는 무단 조작을 방지하도록 설계 및/또는 설치되어야 한다. 비고 3 이러한 조작은, 예를 들면 충격 및 진동으로 발생할 수 있다. 8.3.2 저압용 단로장치 단로장치는 중성선을 포함한 모든 전기공급 충전도체로부터 해당 회로를 효과 적으로 단로해야 한다. 그러나 전원시스템이 TN-S 계통이며 중성선이 확실히 대지 전위로 간주될 수 있는 경우는 중성선을 단로할 필요는 없다. 단로장치는 다음 두 조건을 충족시켜야 한다. a) 신품이고 깨끗하며 건조한 상태에서 접촉자가 단로 위치에 있을 때 단로장치의 전원측 및 부하 측 단자 사이는 표 2 의 임펄스내전압에 견디어야 한다. 28 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
11aa6e61-8d56-4211-9b20-455b3cefec64 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 표 2 - 공칭전압별 단로장치의 최소 임펄스내전압 ¦ 전원시스템의 공칭전압 a V ¦ 전원시스템의 공칭전압 a V ¦ 최소 임펄스내전압 b kV ¦ 최소 임펄스내전압 b kV ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 3 상 계통 ¦ 중간점이 있는 단상계통 ¦ 과전압 범주 III ¦ 과전압 범주 IV ¦ ¦ 230/400, 277/480 400/690 1 000 ¦ 120~240 ¦ 3 5 8 10 ¦ 5 8 10 15 ¦ ¦ 비고 1 과전압 범주의 설명은 KS C IEC 60664-1 의 2.2.2.1.1 참조 비고 2 임펄스내전압은 고도 2 000 m 이하에 적용한다. ¦ 비고 1 과전압 범주의 설명은 KS C IEC 60664-1 의 2.2.2.1.1 참조 비고 2 임펄스내전압은 고도 2 000 m 이하에 적용한다. ¦ 비고 1 과전압 범주의 설명은 KS C IEC 60664-1 의 2.2.2.1.1 참조 비고 2 임펄스내전압은 고도 2 000 m 이하에 적용한다. ¦ 비고 1 과전압 범주의 설명은 KS C IEC 60664-1 의 2.2.2.1.1 참조 비고 2 임펄스내전압은 고도 2 000 m 이하에 적용한다. ¦ ¦ a IEC 60038 에 의함. b 과전압 범주 I 과 II 는 단로장치로 사용하지 않음. ¦ a IEC 60038 에 의함. b 과전압 범주 I 과 II 는 단로장치로 사용하지 않음. ¦ a IEC 60038 에 의함. b 과전압 범주 I 과 II 는 단로장치로 사용하지 않음. ¦ a IEC 60038 에 의함. b 과전압 범주 I 과 II 는 단로장치로 사용하지 않음. ¦ b) 열려 있는 극 사이의 누설 전류는 어떠한 경우에도 다음의 값을 초과 해서는 안 된다. 신품이며 깨끗하고 건조한 상태에서 1 극당 0.5 mA - 장치의 규약 수명의 경과 시점에서 1 극당 6mA 전원의 중성점 또는 중간점이 접지된 경우, 기기의 정격 전압에 해당하는 선도체 및 중성선 사이 의 전압의 110 % 전압과 동일한 전압 값을 각 극의 단자 사이에 인가하여 시험을 한다. 다른 모 든 경우의 전압 값은 전원계통 선간 전압의 110 %로 한다. 직류로 시험하는 경우, 직류 시험전압 값은 교류 시험전압의 실효 값과 같다. 비고 이 요구사항을 검증하기 위한 시험은 관련 기술위원회에서 규정할 수 있다. 8.3.3 고압용 단로장치 8.3.3.1 일반사항 모든 단로장치는 부과 된 책무에 적합한 것이어야 한다. 모든 일반 요건, 예를 들면 접지설비 및 필요한 경우 고도 등의 위치에 대한 특별 요건을 지정하고 고려해야 한다. 설비의 다른 부분으로부터 단로되었을 때에는 추가적으로 설비의 각 부분의 충전도체는 단락시켜 접 지하여야 한다. 해당 기기에 대응하는 규격서는 네트워크 구성, 그 장소의 특수 조건과 운전 및 정비의 경험을 고려 하여 설계된 것이어야 한다. 예상되는 전기적 스트레스는 정상운전 시에 나타나는 스트레스뿐만 아니라, 예를 들면 단락고장의 경우와 같은 추가적인 스트레스도 고려해야 한다. 뇌과 전압 및 개폐과 전압에 대해서도 고려되어야 한다. 기기의 설계과 정에서 설치장소의 외부 영향에 속하는 기계적, 기후적 및 그 밖의 특별한 스트레스를 고려하여야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 29 | {}
43eb9019-801a-4b12-b3ac-711f0cdce1f8 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 비고 1 적절한 개폐장치의 선정을 위해서는 이러한 스트레스 이외에도 KS C IEC 60071 - 1 의 절연 협조를 유의 할 필요가 있다. 비의 도적인 조작의 방지를 위해 안전상의 이유로 단로장치를 "개로"와 "폐로" 위치에서 잠글 수 있어 야 한다. 비고 2 단로장치의 구조상 또는 설치 시에는 개로 시에 전기 아크 또는 뜨거운 이온화가스가 발생 할 수 있음을 고려하여야 한다. 따라서 기기는 개폐 중에 생기는 이온화가스가 기기의 손상 이나 조작자에게 위험한 결과 가 초래되지 않도록 설계되거나 설치되어야 한다. 이것은 이온 화에 의해 충전되어 있지 않은 부분으로의 이차 섬락이 발생하는 경우에도 유효하다. 8.3.3.2 단로장치의 특성 단로 거리 사이의 정격 임펄스내전압 수준은 선간 또는 선과 대지 사이의 절연에 대한 정격 임펄스 내전압 수준보다 높아야 한다(IEC 62271 - 102 참조). 안전상의 이유로 단로장치는 어느 한 접촉자에서 다른 단자로 흐를 수 있는 어떠한 대지 누설전류도 허용 가능 수준으로 제한되도록 설계되어야 한다. 이 누설전류를 특별한 접속장치를 통해 확실히 대 지로 방류할 경우에는 이 안전 요건이 충족된다. 비고 1 대기압의 공기와 다른 절연매질을 가지는 단로장치는 단로 거리에 대한 절연조건을 제조자 와 사용자 간에 합의 할 수 있다. 비고 2 오염에 대한 보호 효과 및 누설 전류에 관한 절연물의 성능 검증 시험이 고려되어야 한다. 비고 3 고압 정격 임펄스내전압은 KS C IEC 60071 - 1 참조 30 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
0f618439-8a83-43d4-8abd-8b968a384d46 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 부속서 A (참고) 보호조치에 의해 실행되는 보호대책의 개요 비고 모든 보호규정이 저압 및 고압 모두에 적용할 수 있는 것은 아니라는 점에 유의 한다. 고장보호(4.2) ![image](/image/placeholder) 기본보호(4.1) 고장이 없는 상태에서의 보호 단일고장에서의 보호 강화절연 5.3.1a 이중 또는 강화절연에 의 한 보호 6.2b 기본절연 및 보조절연 세부적인 사항은 하기 참조 5.2.1a 기본절연 보호등전위본딩 세부사항: 5.2.2a - (고체)기본절연 5.1.1.1a 세부사항: 다음 중 하나 또는 적절 - 기본절연 한 조합 등전위본딩을 통한 보호 · 내부장애물 또는 외함 및 - 보호등전위본딩(설비에서) 6.3b - 보호등전위본딩(기기에서) 5.1.2a · 후면장해물 - 보호도체 5.1.3a - PEN 도체 - 촉수범위 밖에 설치 보호차폐 5.2.3a 5.1.4a 전원의 자동차단을 통한 기본절연 및 전원의 자동차단 보호 세부사항은 위를 참조 5.2.5a 6.1b 전기적 분리에 의한 보호 기본절연 및 (회로 간) 단순분리 6.4b 세부사항은 위를 참조 5.2.6a : 비도전성 환경에 의한 보 기본절연 및 비도전성 환경 호 세부사항은 위를 참조 5.2.7°C 6.5b 그 밖의 조치 및 그 밖의 조치 그 밖의 보호조치에 의한 5.1.8a 5.2.9a 보호 6.9b 그 밖의 강화보호조치 5.3.5a a 보호규정에 관한 항목번호(보호대책의 요소) b 보호대책의 항목번호 그림 A.1 - 기본보호 및 고장보호용 보호조치 31 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
74c2cbf7-e5b1-4d3e-ac2a-77caadb563ad | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 ![image](/image/placeholder) 대지, PELV 및 다른 및 및 SELV 에 의한 보호 전압의 제한 보호분리 SELV 시스템으로부터 6.6b 5.1.5a 5.3.2a 의 단순분리 5.2.6a 기능접지용 선택사항 및 및 7.4.2 일부 경우 추가적으로: PELV 에 의한 보호 전압의 제한 보호분리 기본절연 6.7b 5.1.5a 5.3.2a 5.1.1.1a 또는 장애물이나 외함 5.1.2a 안정상태 접촉전류 및 전하의 제한 및 안정상태 접촉전류 5.1.6a 및 전하의 제한에 세부사항: 보호분리 의한 보호 - 제한전류원 5.3.2a 6.8b 5.3.3a - 보호임피던스장치 5.3.4a 보호분리의 세부사항: 강화절연 5.3.1a 기본절연 및 보조절연 5.2.6a 5.2.1a 기본절연 및 보호차폐 5.2.6a 5.2.3a a 보호규정에 관한 항목번호(보호대책의 요소) b 보호대책의 항목번호 그림 A.2 - 전기량의 제한 값을 통한 보호조치 32 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
25a8eb14-e397-4fc2-9cc2-54468a384000 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 부속서 B (참고) 7.5.2.2 a) 및 7.5.2.2 b)에 관한 보호도체전류의 최대 교류 제한 값 이 값은 과도한 보호도체 전류를 방지하고 전기기기와 전기설비 내의 보호대책과 의 협조를 도모하기 위해 제품 위원회에서 고려하기 위한 것이다. 제품위원회는 보호도체 전류의 실제적인 최저 한도 값을 사용하는 것을 권장한다. 제품위원회는 대부분의 경우, 다음을 초과 하지 않는 제한 값의 채택이 누전차단기의 불필요한 동작 을 방지한다는 것에 유의 한다. 7.5.2.2 a)에 대한 값 정격 32A 이하의 단상 또는 다상 플러그와 꽂음접속시스템에 고정되는 전류사용기기에 대한 값 ¦ 기기 정격전류 ¦ 최대 보호도체전류 ¦ ¦ --- ¦ --- ¦ ¦ 4A 이하 ¦ 2 mA ¦ ¦ 4A 초과 10A 이하 ¦ 0.5 mA/A ¦ ¦ 10A 초과 ¦ 5 mA ¦ 7.5.2.2 b)의 값 , 보호 도체에 대해 특별한 대책이 없는 영구 접속 전기사용기기 및 고정형 전류사용기기 또는 정격 32 A 초과 단상 또는 다상 플러그 및 꽂음접속시스템이 장착된 전류사용기기에 대한 값 ¦ 기기 정격전류 ¦ 최대 보호도체전류 ¦ ¦ --- ¦ --- ¦ ¦ 7A 이하 ¦ 3.5 mA ¦ ¦ 7A 초과 20A 이하 ¦ 0.5 mA/A ¦ ¦ 20 A 초과 ¦ 10 mA ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 33 | {}
a24c4702-2646-4119-b295-83ec2280fa31 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 부속서 C (참고) 용어 색인 ¦ 용어 ¦ 영문 ¦ 항목 번호 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 촉수범위 전원자동차단 ¦ arm's reach automatic disconnection of supply ¦ 3.15 3.18 ¦ ¦ 격벽, (전기적) 보호 기본절연 기본보호 본딩, 등전위본딩 참조 ¦ barrier, (electrically) protective basic insulation basic protection bonding, see equipotential bonding ¦ 3.13 3.10.1 3.1.1 3.16 ¦ ¦ 회로, (전기적) (도전성)차폐물 (도전성)차폐물(미국) 도체 접지도체(미국) ¦ circuit, (electric) (conductive) screen (conductive) shield (US) conductor earthing conductor grounding conductor (US) ¦ 3.2 3.20 3.17.4 ¦ ¦ 접지도체 PEN 도체 보호도체, PE ¦ PEN conductor protective conductor, PE danger zone disconnection of supply, automatic ¦ 3.16.5 3.16.4 3.35 ¦ ¦ 위험구역 전원차단, 자동 이중절연 ¦ double insulation earth ¦ 3.18 3.10.3 3.17 ¦ ¦ 접지 접지극 접지극(미국) (국소)접지 (국소)접지(미국) 기준대지 기준대지(미국) ¦ earth electrode ground electrode (US) (local) earth (local) ground (US) reference earth reference ground (US) ¦ 3.17.3 3.17.2 3.17.1 ¦ ¦ 접지 접지설비 접지도체 기능접지 기능접지(미국) 접지설비(미국) 접지도체(미국) 보호접지 보호접지(미국) ¦ earthing earthing arrangement earthing conductor functional earthing functional grounding (US) grounding arrangement (US) grounding conductor (US) protective earthing protective grounding (US) ¦ 3.17.5 3.17.4 3.17.7 3.17.5 3.17.4 3.17.6 ¦ 34 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
d1427f29-646e-4d87-938a-814f00f64747 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 ¦ 용어 ¦ 영문 ¦ 항목 번호 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ (유효)접촉전압 ¦ (effective) touch voltage ¦ 3.8.1 ¦ ¦ (전기)회로 ¦ (electric) circuit ¦ 3.2 ¦ ¦ 감전 기본보호 고장보호 ¦ electric shock basic protection fault protection ¦ 3.1 3.1.1 3.1.2 ¦ ¦ (전기)기기 ¦ (electrical) equipment ¦ 3.3 ¦ ¦ 전기적 분리 ¦ electrical separation ¦ 3.25 ¦ ¦ (전기)기능자 ¦ (electrically) instructed person ¦ 3.31 ¦ ¦ (전기)숙련자 ¦ (electrically) skilled person ¦ 3.30 ¦ ¦ (전기적)보호격벽 ¦ (electrically) protective barrier ¦ 3.13 ¦ ¦ (전기적)보호외함 ¦ (electrically) protective enclosure ¦ 3.14 ¦ ¦ (전기적)보호장애물 ¦ (electrically) protective obstacle ¦ 3.12 ¦ ¦ (전기적)보호차폐물 (전기적)보호차폐물(미국) ¦ (electrically) protective screen (electrically protective shield (US) ¦ 3.21 ¦ ¦ (전기적)보호차폐 (전기적)보호분리 (전기적)보호차폐(미국) ¦ (electrically) protective screening (electrically) protective separation (electrically) protective shield (US) ¦ 3.22 3.24 3.21 ¦ ¦ 전극 접지극 접지극(미국) ¦ electrode earth electrode ground electrode (US) ¦ 3.17.3 ¦ ¦ 외함, (전기적)보호 ¦ enclosure, (electrically) protective ¦ 3.14 ¦ ¦ 강화보호조치 ¦ enhanced protective provision ¦ 3.19 ¦ ¦ 기기, (전기) ¦ equipment, (electrical) ¦ 3.3 ¦ ¦ 등전위본딩 등전위본딩단자 PEN 도체 보호본딩단자 보호도체, PE 보호등전위본딩 ¦ equipotential bonding equipotential bonding terminal PEN conductor protective bonding terminal protective conductor PE protective-equipotential-bonding ¦ 3.16 3.16.2 3.16.5 3.16.3 3.16.4 3.16.1 ¦ ¦ 노출도전부 ¦ exposed-conductive-part ¦ 3.6 ¦ ¦ 특별저압(ELV) PELV 시스템 SELV 시스템 ¦ extra-low-voltage (ELV) PELV system SELV system ¦ 3.26 3.26.2 3.26.1 ¦ ¦ 계통외도전부 ¦ extraneous-conductive-part ¦ 3.7 ¦ ¦ 고장보호 기능접지 기능접지(미국) ¦ fault protection functional earthing functional grounding(US) ¦ 3.1.2 3.17.7 ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 35 | {}
c37cd967-c2d0-4f74-b484-b5b7bdbb5afc | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 ¦ 용어 ¦ 영문 ¦ 항목 번호 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 완화, 전위 접지극(미국) 대지, (국소)(미국) 대지, 기준(미국) 접지설비(미국) 접지도체(미국) 접지, 기능적(미국) 접지, 보호(미국) ¦ grading, potential ground electrode (US) ground, (local) (US) ground, reference (US) grounding arrangement (US) grounding conductor (US) grounding, functional (US) grounding, protective (US) ¦ 3.34 3.17.3 3.17.2 3.17.1 3.17.5 3.17.4 3.17.7 3.17.6 ¦ ¦ 위험충전부 기능자 ¦ hazardous-live-part instructed person ¦ 3.5 3.31 ¦ ¦ ¦ ¦ 3.10 ¦ ¦ 절연 기본절연 이중절연 강화절연 ¦ insulation basic insulation double insulation reinforced insulation supplementary insulation ¦ 3.10.1 3.10.3 3.10.4 3.10.2 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 보조절연 ¦ ¦ ¦ ¦ ¦ ¦ 3.36 ¦ ¦ 누설전류 안정상태 접촉전류 및 전하의 한계 전류제한 전원 ¦ leakage current limitation of steady-state touch current and charge ¦ 3.27 ¦ ¦ 충전부 (국소)대지 (국소)대지(미국) ¦ limited-current-source live part ¦ 3.28 3.4 ¦ ¦ ¦ (local) earth (local) ground (US) ¦ 3.17.2 ¦ ¦ ¦ ¦ ¦ ¦ 비도전성환경 ¦ non-conducting environment ¦ 3.11 ¦ ¦ (전기적)보호 ¦ obstacle, (electrically) protective ¦ ¦ ¦ 장애물, ¦ ¦ 3.12 ¦ ¦ 일반인 ¦ ordinary person ¦ 3.32 ¦ ¦ PELV 시스템 ¦ PELV system ¦ 3.26.2 ¦ ¦ PEN 도체 ¦ PEN conductor ¦ 3.16.5 ¦ ¦ ¦ ¦ ¦ ¦ 사람 ¦ person: instructed person ¦ 3.31 3.30 ¦ ¦ 기능자 숙련자 일반인 ¦ skilled person ordinary person ¦ 3.32 ¦ ¦ ¦ ¦ ¦ ¦ 전위경도완화 예상접촉전압 ¦ potential grading prospective touch voltage ¦ 3.34 3.8.2 ¦ ¦ 보호 ¦ protection: ¦ ¦ ¦ 기본보호 ¦ basic protection ¦ 3.1.1 ¦ ¦ 고장보호 ¦ fault protection ¦ 3.1.2 ¦ ¦ 보호격벽 ¦ protective barrier ¦ 3.13 ¦ ¦ ¦ ¦ ¦ ¦ 보호본딩단자 보호도체, PE ¦ protective bonding terminal protective conductor PE ¦ 3.16.3 3.16.4 ¦ 36 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
1a41cf2a-7798-4325-a006-a7efe35a3273 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 ¦ 용어 ¦ 영문 ¦ 항목 번호 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 보호도체전류 ¦ protective conductor current ¦ 3.38 ¦ ¦ 보호접지 ¦ protective earthing ¦ 3.17.6 ¦ ¦ 보호외함 ¦ protective enclosure ¦ 3.14 ¦ ¦ 보호등전위본딩 ¦ protective-equipotential-bonding ¦ 3.16.1 ¦ ¦ 보호접지(미국) ¦ protective grounding (US) ¦ 3.17.6 ¦ ¦ 보호임피던스장치 ¦ protective impedance device ¦ 3.29 ¦ ¦ 보호장애물 ¦ protective obstacle ¦ 3.12 ¦ ¦ 보호차폐물 ¦ protective screen ¦ 3.21 ¦ ¦ 보호차폐 ¦ protective screening ¦ 3.22 ¦ ¦ 보호분리 ¦ protective separation ¦ 3.24 ¦ ¦ 보호차폐물(미국) ¦ protective shield (US) ¦ 3.21 ¦ ¦ 보호차폐(미국) ¦ protective shielding (US) ¦ 3.22 ¦ ¦ 기준대지 기준대지(미국) ¦ reference earth reference ground (US) ¦ 3.17.1 ¦ ¦ 강화절연 ¦ ¦ 3.10.4 ¦ ¦ ¦ reinforced insulation ¦ ¦ ¦ 차폐물, (도전성) 보호 ¦ screen, (conductive) ¦ 3.20 ¦ ¦ 차폐물, 차폐, 보호 ¦ screen, protective ¦ 3.21 ¦ ¦ ¦ screening, protective ¦ 3.22 ¦ ¦ SELV 시스템 분리 ¦ SELV system ¦ 3.26.1 ¦ ¦ ¦ separation ¦ ¦ ¦ 전기적 분리 ¦ electrical separation ¦ 3.25 ¦ ¦ (전기적) 보호분리 단순분리 ¦ (electrically) protective separation ¦ 3.24 ¦ ¦ ¦ simple separation ¦ 3.23 ¦ ¦ 차폐물, (도전성)(미국) 차폐물, 보호(미국) ¦ shield, (conductive) (US) ¦ 3.20 ¦ ¦ 차폐, 보호(미국) ¦ shield, protective (US) ¦ 3.21 ¦ ¦ ¦ shielding, protective (US) ¦ 3.22 ¦ ¦ 충격, 전기 ¦ shock, electric ¦ 3.1 ¦ ¦ 기능자 ¦ skilled person ¦ 3.30 ¦ ¦ 고정형 기기 ¦ stationary equipment ¦ 3.37 ¦ ¦ 보폭전압 ¦ step voltage ¦ 3.33 ¦ ¦ 보조절연 ¦ supplementary insulation ¦ 3.10.2 ¦ ¦ 시스템 ¦ system ¦ 3.39 ¦ ¦ 단자(대) ¦ terminal ¦ ¦ ¦ 등전위본딩단자(대) ¦ equipotential bonding terminal ¦ 3.16.2 ¦ ¦ 보호본딩단자(대) ¦ protective bonding terminal ¦ 3.16.3 ¦ ¦ 접촉전류 ¦ touch current ¦ 3.9 ¦ ¦ 안정상태 접촉전류 및 전하의 한계 ¦ limitation of steady- state touch current and charge ¦ 3.27 ¦ ¦ 제한된 전류원 ¦ limited - current- source ¦ 3.28 ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 37 | {}
7fcdfc44-e8bc-4777-a856-7cdd0871426a | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 ¦ 용어 ¦ 영문 ¦ 항목 번호 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 접촉전압 (유효)접촉전압 예상접촉전압 ¦ touch voltage (effective) touch voltage prospective touch voltage ¦ 3.8 3.8.2 ¦ ¦ 전압 보폭전압 접촉전압 ¦ voltage step voltage touch voltage ¦ 3.8.1 3.33 3.8 ¦ 38 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
d5d71748-1fdc-470c-9aef-3687363ddeca | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 KS C IEC 61140:2014 해 설 이 해설은 본체 및 부속서에 규정/기재한 사항 및 이와 관련된 사항을 설명하는 것으로, 표준의 일부 는 아니다. 1 개요 1.1 개정의 취지 이 표준은 2009 년 제 3.1 판으로 발행된 IEC 61140, Protection against electric shock Common aspects for installation and equipment 를 번역하여 부합화한 것이다. 1.2 개정의 경위 이 표준은 1997 년 제 2 판으로 발행된 IEC 61140, Protection against electric shock Common aspects for installation and equipment 가 2009 년 제 3.1 판으로 개정됨에 따라 IEC 표준과 일치(IDT)시켜 개정한 것이다. 2 주요 개정 내용 2.1 용어와 정의 KS C IEC 60050 및 KS C IEC 60364 시리즈 용어로 통일시키고 표준 사용자가 이해하기 쉽도록 다음 의 용어를 정비하였다. ¦ KS C IEC 61140:2001 ¦ KS C IEC 61140:2014 ¦ ¦ --- ¦ --- ¦ ¦ 기본적 보호 ¦ 기본 보호 ¦ ¦ 노출 도전성부 ¦ 노출도전부 ¦ ¦ 외부 도전성부 ¦ 계통외도전부 ¦ ¦ 기초절연 ¦ 기본절연 ¦ ¦ (전기적) 보호물 ¦ (전기적) 보호장애물 ¦ ¦ (전기적) 보호장벽 ¦ (전기적) 보호격벽 ¦ ¦ (전기적) 보호용기 ¦ (전기적) 보호외함 ¦ ¦ 접근 한계 ¦ 촉수범위 ¦ ¦ (도전성) 스크린 ¦ (도전성) 차폐물 ¦ ¦ 제한적 전류원 ¦ 전류제한 전원 ¦ ¦ 보호용 접지 ¦ 보호접지 ¦ ¦ 기능용 접지 ¦ 기능접지 ¦ 2.2 주요 내용 a) 부속서 B 에 보호도체전류의 최대 교류 제한 값이 참고로 신설되었다. 39 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b3c17b6f-c380-4708-b72f-f0058c139673 | KSCIEC61140_2020확인_KR | KS C IEC 61140:2014 b) 부속서 C 에 용어 색인이 참고로 신설되었다. 3 원안작성 협력자 대한전기협회 KEPIC 처 COSD 그룹 및 저압전기설비 전문위원회 40 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
1d4c4b31-1cd1-40da-9be3-497338a3a8ec | KSCIEC61140_2020확인_KR | 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
bff0beee-c137-44fd-ba7f-c45bc6d2e7a2 | KSCIEC61140_2020확인_KR | ¦ 한국산업표준 ¦ 감전보호 - 설비 및 기기의 공통사항 ¦ ¦ --- ¦ --- ¦ ¦ 발간 · 보급 ¦ 한 국 표 준 협 회 08506 서울특별시 금천구 가산디지털 1 로 145 에이스하이엔드타워 3 차(16 층) ☎ (02)2624-0114 ☎ (02)2624-0148 http://www.kssn.net ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c696a5c3-fec2-4514-8f48-6b4778eba7ac | KSCIEC61140_2020확인_KR | KS c IEC 61140:2014 ![image](/image/placeholder) KSKSKS KSKSK KSKS KSK KS KSK KSKS KSKSK KSKSKS ¦ Protection against electric ¦ shock - ¦ ¦ --- ¦ --- ¦ ¦ Common aspects ¦ for installation ¦ ¦ and ¦ equipment ¦ ICS 13.260; 29.020; 91.140.50 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
92ce0476-0e67-4b2b-aaf2-e4219e2907b8 | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | SK ecoplant SPECIFICATION FOR HVAC SYSTEM - GALV. 덕트공사 - ¦ DOC No. ¦ : 21036D-IC-M16G00-HV-A00-00131 ¦ ¦ --- ¦ --- ¦ ¦ DISCIPLINE ¦ : HVAC ¦ ¦ PROJECT No. ¦ : 21036D ¦ ¦ PROJECT TITLE ¦ : M16 Ph2 Project ¦ ¦ CLIENT ¦ : SK hynix ¦ ¦ LOCATION ¦ : Icheon city, Gyeonggi-do, Korea ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 0 ¦ 2022.01.25 ¦ APPROVED FOR CONSTRUCTION ¦ T.G.YU ¦ J.H. YANG ¦ Y.T.OH ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ REV. ¦ DATE ¦ DESCRIPTION ¦ PRPD ¦ CHKD ¦ APPD ¦ 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. | {}
ba5b2bba-3ae2-4c75-b2ad-d4aa7d0cf3d1 | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 Page 1 of 30 ¦ ¦ --- ¦ --- ¦ --- ¦ 1. 일반사항 1.1 적용범위 1.1.1 요약 (1) 이 절은 공기조화 및 환기용 덕트(아연도금강판 덕트) 공사에 적용한다. (2) 설계도서, 관계법규 또는 별도로 정한 규정에 의한 것을 제외하고는 모두 본 시방에 준한다. (3) 이 시방서에 기재되지 않은 사항은 국토교통부 제정 "기계설비공사 표준 시방서" 및 '1.3 항 참조표준'을 적용할 수 있다. 단, 본 시방서와 상이한 내용은 본 시방서를 우선하여 적용한다. (4) 이 시방서에 특별한 명기가 없는 사항 중 건축, 전기에 관한 사항은 해당 시방서에 따른다. (5) 시방서, 설계도면 및 내역서 중 어느 한 도서에라도 표기되어 있는 사항은 시공하여야 한다 (6) 산업안전보건법에서 규정한 법규에 의해서 시공하여야 한다. 1.1.2 적용 및 우선 (1) 본 시방서와 첨부사항과 의 사이에 내용이 서로 상이할 때는 첨부사항을 우선한다. (2) 모든 공사는 설계도면 및 시방서에 준하여 시공하며, 설계도면과 시방이 상이한 경우에는 설 (3) 계도면을 우선하되 발주 담당자와 협의 하여 정한다. (4) 본 시방서, 설계도면 또는 표준 시방이 정한 공법, 자재 및 제품 등의 내용이 현실적으로 이 행하기 불가능할 경우에는 반드시 발주 담당자에게 서면으로 보고하고 대안에 대한 승인을 득한 후 시공한다. 1.1.3 주요내용 (1) 덕트의 제작 및 설치 (2) 덕트용 부속품의 설치 (3) 덕트의 지지 1.2 관련 시방 1.2.1 일반공통사항 1.2.2 보온공사 1.2.3. 플랜지체결공사 1.2.4 도장 · 방청 및 부식공사 1.3 참조 표준 1.3.1 한국산업표준 ¦ KS T 1028 ¦ 점착 테이프 및 점착 시트의 시험 방법 ¦ ¦ --- ¦ --- ¦ ¦ KS B 1002 ¦ 6 각 볼트 ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
1b49eb40-2879-4722-9ca2-acbf8fc26355 | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 Page 2 of 30 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ KS B 1012 ¦ 6 각 너트 및 6 각 낮은너트 ¦ ¦ --- ¦ --- ¦ ¦ KS B 1101 ¦ 냉간 성형 리벳 ¦ ¦ KS B 5302 ¦ 유리제 온도계(전체 담금) ¦ ¦ KS B ISO 1771 ¦ 이중관 일반용 온도계 ¦ ¦ KS D 3051 ¦ 열간 압연 봉강 및 코일 봉강의 모양, 치수 및 무게와 그 허용차 ¦ ¦ KS D 3052 ¦ 열간 압연 평강의 모양, 치수 및 무게와 그 허용차 ¦ ¦ KS D 3500 ¦ 열간 압연 강판 및 강대의 모양, 치수, 무게 및 그 허용차 ¦ ¦ KS D 3501 ¦ 열간 압연 연강판 및 강대 ¦ ¦ KS D 3503 ¦ 일반 구조용 압연 강재 ¦ ¦ KS D 3506 ¦ 용융 아연도금 강판 및 강대 ¦ ¦ KS D 3512 ¦ 냉간 압연 강판 및 강대 ¦ ¦ KS D 3556 ¦ 피아노선 ¦ ¦ KS D 3770 ¦ 용융 55% 알루미늄 아연합금도금 강판 및 강대 ¦ ¦ KS D 6701 ¦ 알루미늄 및 알루미늄합금의 판 및 띠 ¦ ¦ KS D 6705 ¦ 알루미늄 및 알루미늄합금 박 ¦ ¦ KS D 6759 ¦ 알루미늄 및 알루미늄합금 압출 형재 ¦ ¦ KS F 2815 ¦ 배연 설비의 검사 표준 ¦ ¦ KS L 9102 ¦ 인조 광물섬유 단열재 ¦ 1.3.2 단체표준 ¦ SPS-KARSE B 0007-169 ¦ 공기취입 · 취출구 ¦ ¦ --- ¦ --- ¦ ¦ SPS-KARSE B 0008-170 ¦ 공기취입 · 취출구의 성능 시험방법 ¦ ¦ SPS-KARSE B 0009-171 ¦ 공기조화용 댐퍼 ¦ ¦ SPS-KARSE B 0010-172 ¦ 공기조화용 댐퍼의 성능 시험방법 ¦ ¦ SPS-KARSE B 0013-175 ¦ 공기조화용 덕트 및 부품 ¦ ¦ SPS-KARSE B 0016-178 ¦ 공기조화용 덕트누기 시험방법 ¦ ¦ SPS-KARSE B 0017-179 ¦ 공기조화용 덕트소음기 시험방법 ¦ 1.4 제출물 1.4.1 자재 공급 전 제출물 시공자는 다음의 사항을 자재공급 전에 발주 담당자에게 제출하여 승인을 받아야 한다. (1) 주요 기자재공급원 승인요청서 ① KS 규격 인증서 또는 ISO 품질인증서 ② 공급자의 사업자 등록증명원 (단, 외산자재인 경우 납품 회사 분) SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. SK ecoplant | {}
e763a7e5-6fa8-4d61-8a1e-10a77da7db7f | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 Page 3 of 30 ¦ ¦ --- ¦ --- ¦ --- ¦ ③ 국세 및 지방세 완납증명서 (유효기관 확인) ④ 납품실적증명서 (유효기관 확인) ⑤ 품질검사 전문기관 및 국·공립검사기관의 시험성과 표 ⑥ 품질보증각서 : KS 비인증제품, 공인기관 시험 불가제품, 해외제품(시험성적서 제출)등 필요 시 재료에 대한 견본품을 제출하여야 한다. (2) 1.4.2 자재 입고 검사 요청서 자재 반입 시 자재 입고 검사 요청서를 발주 담당자에게 제출하여 확인을 받는다. 1.4.3 검측 요청서 시공 담당자가 검측 요청서를 작성하여 건설사업관리기술인에게 확인을 받은 후 발주 담당자 에게 제출 한다. 1.5 운반, 저장 및 취급 1.5.1 모든 재료는 옥내에 보관한다. 1.5.2 보관, 운반, 상하차 및 시공할 때에는 충격 등으로 관이 손상되지 않도록 하며, 적재·보관 시 주변 하중으로 관의 변형이 발생하지 않도록 하여야 한다. 1.5.3 운반, 저장 및 취급기간 동안 현장제작 또는 공장제작된 덕트, 부속기기 및 구매된 제품이 손 상되지 않도록 보호해야 한다. 1.6 보온공사 '18154D-CJ-G00-HV-A00-00150 보온공사' 기준에 따른다 1.7 도장 · 방청 및 부식공사 '18154D-CJ-G00-HV-A00-00160 도장 · 방청 및 부식공사' 기준에 따른다. 2. 재료 2.1 일반사항 공기조화 및 환기용 덕트는 오염물질을 발생시키지 않고 비흡습성 재료를 사용하며, 도면 및 본 시 방서에 표기하지 않은 경우에는 발주 담당자의 승인을 득한 후 사용한다. 2.2 덕트재료 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
acd18d9a-083d-4429-92d5-f1cf95f1629c | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ SPECIFICATION FOR ¦ 21036D-IC-M16G00-HV-A00-00131 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ HVAC SYSTEM ¦ Rev. 0 Page 4 of 30 ¦ 2.2.1 아연도금 강판 KS D 3506(용융 아연도금 강판 및 강대)로 한다. (첨부파일 1 번 참조) 2.3 접합재료 및 지지재료 2.3.1 강재 KS D 3503(일반구조용 압연강재)으로 하며, 그 형상, 치수, 중량 및 허용차는 KS D 3051(열간 압연 봉강 및 코일의 모양, 치수 및 무게와 그 허용차), KS D 3052(열간 압연 형강의 모양, 치수, 무게 및 그 허용차)에 기재되어 있는 것으로 한다. 2.3.2 리벳 아연도금 강판제 덕트의 경우 KS B 1101(냉간 성형 리벳)에 의한 아연도금한 강리벳을 표준으로 한다. 2.3.3 볼트, 너트 및 와셔 (1) 볼트, 너트 및 와셔의 재료는 KS D 3503(일반 구조용 압연 강재) 및 스테인리스강제의 제품 으로 한다. (2) 볼트 및 너트는 다음의 제품으로 한다. KS B 1002(6 각 볼트) KS B 1012(6 각 너트 및 6 각 낮은너트) (3) 와셔는 KS B 1326(평와 셔) 제품으로 한다. (4) 앵커 볼트의 나사는 KS B 1002(6 각 볼트)의 나사에 준한다. (5) 고장력 볼트, 너트 및 평와 셔의 세트는 KS B 1010(마찰접합용 고장력 6 각볼트, 6 각너트, 평와 셔의 세트), TS 볼트, 너트는 KS B 2819(구조물용 토크 전단형 고장력 볼트, 6 각너트, 평와 셔의 세트)의 제품으로 한다. 2.3.4 플랜지용 개스킷(Gasket) NEOPRENE 계통의 난연성 테이프로서 기계식 덕트 플랜지 접합용으로 제작된 것이어야 한다. ¦ 재 질 ¦ 비 고 ¦ ¦ --- ¦ --- ¦ ¦ NEOPRENE SPONGE ¦ 내후성, 내약품성, 특히 SEAL 이 필요한 계통에 사용한다. 사용 온도 : -20 ~ 100°C ¦ ¦ PTFE (PolyTetraFluorEthylene) ¦ 내약품성이 뛰어나며, 높은 온도(325°C 에서 안정)에서 특성이 변화하지 않는다. 불연성으로 내후성도 좋고, 비점착성으로 마모계수도 작으며 무독성이다. ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
a12cfeba-5ca9-4f50-b9d3-fdac687780ea | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ SPECIFICATION FOR ¦ 21036D-IC-M16G00-HV-A00-00131 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ HVAC SYSTEM ¦ Rev. Page 5 of 30 ¦ 2.3.5 지지재료 (1) 지지재료는 KS D3503(일반 구조용 압연 강재) L-형강 및 �-형강으로 한다. (2) FAB 내부에 설치되는 지지재료는 용융 아연도금된 제품으로 한다. (3) 덕트 관말 부분에는 덕트 상하에 Double Angle 또는 Double Channel 을 설치하여 고정한다. (4) 행거볼트 끝난부는 너트 체결 후 10mm 이내로 절단 후 RED CAP 처리한다. 2.3.6 밀봉재 합성고무, 기타의 재료로 하고 덕트와 잘 접착하며 내구성이 있는 비 초산계로 한다. 2.4 덕트용 부속품 2.4.1 일반사항 덕트 기기류는 압력손실 및 누기시험, 유량시험, 토크시험, 디퓨저의 취출기류 분포시험, 도달거리 및 토출 풍속시험, 소음레벨 등 각종 시험에 합격한 덕트기구를 선정, 설치하여야 한다. 2.4.2 외기 흡입루버 (O.A Louver) (1) 두께 0.6mm 이상의 KS D 3506(용융 아연도금 강판 및 강대), KS D 3512(냉간 압연 강판 및 강 대) 또는 KS D 6701(알루미늄 및 알루미늄 합금의 판 및 띠)로 하며, 충분히 보강을 하여야 한 다. (2) 루버의 유효면적은 40% 이상을 원칙으로 하고, 빗물의 침입을 방지하는 구조로 한다. 2.4.3 배기루버 (E.A Louver) 외기 흡입루버와 같은 구조로 한다. 2.4.4 토출구, 흡입구 소음발생이 적고, 토출기능 및 흡입기능이 확실하고 토출구·흡입구 뒷면의 댐퍼 및 셔터는 두께 0.5mm 이상의 KS D 3512(냉간 압연 강판 및 강대) 또는 두께 1.0mm 이상의 KS D 6701(알루미늄 및 알루미늄 합금 판 및 띠) 혹은 KS D 6759(알루미늄 및 알루미늄 합금 압출강재)으로 한다. 풍속 에 의한 떨림 및 소음발생이 적고 쉽게 풍량을 조절할 수 있는 구조로 하며 각종 형태에 대한 사양은 다음과 같다. (1) 아네모디퓨저는 KS D 6701(알루미늄 및 알루미늄 합금의 판 및 띠) 또는 KS D 3512(냉간 압연 강판 및 강대)로 제작하며, 댐퍼 및 정류기를 부착하여 충분한 유인성능을 갖는 것으로 한다. 외부 콘(Cone)의 판두께는 목의 직경이 250mm 미만의 것은 0.6mm(알루미늄제는 0.8mm) 이상, 250mm 이상의 것은 0.8mm(알루미늄제는 1.0mm) 이상으로 한다 (2) 유니버셜형의 본체 프레임 및 가동날개는 KS D 6701(알루미늄 및 알루미늄 합금 판 및 띠), KS D 6759(알루미늄 및 알루미늄 합금 압출강재), 또는 KS D 3512(냉간 압연 강판 및 강대)로 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
5671c766-4098-44a6-90cf-1981f759e0b0 | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 Page 6 of 30 ¦ ¦ --- ¦ --- ¦ --- ¦ 본체의 두께는 1.0mm 이상, 설치용 개스킷은 5mm 이상의 스폰지 고무 또는 펠트로 한다. 날개 는 조정이 쉬운 구조로 하며, 토출구에 사용하는 셔터는 양쪽개방으로 한다. (3) 슬릿형의 본체 프레임 및 슬릿은 KS D 6701(알루미늄 및 알루미늄 합금 판 및 띠), KS D 6759 (알루미늄 및 알루미늄 합금 압출강재), 또는 KS D 3512(냉간 압연 강판 및 강대)에 따르고 본 체 프레임의 두께는 1.2mm 이상, 설치용 개스킷은 5mm 이상의 스폰지 고무 또는 펠트로 한다. (4) 펀칭메탈형의 유효면적은 단면적의 40% 이상이 되도록 하고, 전면판은 두께 0.8mm 이상의 강 판 KS D 3512(냉간 압연 강판 및 강대)를 펀칭 가공한 것으로 한다. (5) 경질 폴리염화비닐제 및 스테인리스제 토출구·흡입구는 별도의 제작사양에 따른다. 2.4.5 풍량조절댐퍼 (V.D : Volume Damper) (1) 댐퍼의 안내깃은 두께 1.2mm 이상의 KS D 3506(용융 아연도금 강판 및 강대)으로 제작하며, 기능이 확실하고 진동 및 소음이 적으며 개방 시 공기흐름에 대한 저항이 적은 것으로 한다. (2) 댐퍼 케이싱은 강판 또는 아연도금강판 재질로서 연결덕트보다 한 단계 이상 더 두꺼운 것으로 한다. (3) 장방형 덕트 댐퍼의 안내깃은 원칙적으로 덕트의 높이 200mm 이내 마다 1 매로 하며, 날개는 서로 15mm 정도 겹치게 한다. (4) 댐퍼축은 원칙적으로 아연도금 봉강, 베어링은 황동제 등 녹이 슬지 않는 재질을 사용하여 케이싱에 설치한다. (5) 원형덕트의 댐퍼는 단익으로 하고 기타의 것은 정방형 덕트에 준 한다. (6) 댐퍼의 조작용 개폐지시기를 설치한다. (수동 및 자동) (7) 댐퍼의 면적 1.2m2 를 넘을 경우 분할한다. 2.4.6 방화댐퍼 (F.D : Fire Damper) (1) 날개 및 틀재료는 1.6mm 이상의 KS D 3501(열간압연 연강판 및 강대) 또는 강판으로 하며, 열 에 의한 변형으로 기능에 지장을 받지 않도록 날개의 외주와 케이싱 내면과 의 틈은 일정하게 하고, 댐퍼 및 베어링은 '2.4.5'에 준하는 것으로 한다. (2) 온도 감지식 온도를 감지하여 자동적으로 폐쇄하는 구조로서 온도휴즈를 사용하는 것은 점검과 교체가 용 이한 구조로 한다. 온도휴즈는 72°C 를 표준으로 한다. 2.4.7 방화겸용 풍량조절댐퍼 (F.V.D : Fire Volume Damper) 방화 및 풍량조절용 댐퍼로서 '2.4.5' 및 '2.4.6'에 적합한 구조의 것은 겸용하여 사용 할 수 있다. 2.4.8 피스톤 릴리스 댐퍼 (P.R.D : Piston Release Damper) (1) 케이싱, 가동날개 및 피스톤 릴리서(Releaser)로 구성되며 피스톤 릴리서에 의해 자동적으로 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
9d083f24-3d42-476d-b52e-201615063bbb | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ SPECIFICATION FOR ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ HVAC SYSTEM ¦ Page 7 of 30 ¦ 폐쇄되는 구조로서, 개방 시에 공기유동 저항이 적고 방화기능이 확실해야 한다. (2) 케이싱, 가동날개의 판두께, 댐퍼축 및 베어링 재질 등은 '2.4.6'에 준한다. (3) 피스톤 릴리서는 소화용 가스에 의해 유효하게 구동되는 구조로, 재질은 황동제 또는 스테인 리스 강제로 하며 복구조작은 특별한 경우에 한해 수동식으로 한다. 2.4.9 정풍량 조정장치 및 가변풍량 조정장치 내식성이 높은 재료로 제작하며 1 차측의 압력변동에 영향을 받지 않고 소정의 풍량으로 확실하 게 조정할 수 있는 에너지절약형의 취급이 용이한 구조로 한다. 2.4.10 플렉시블 덕트 (Flexible Duct) (1) 난연재료로 하고 충분한 유연성과 내압강도를 갖고 있어야 하며, 냉난방에 사용하는 경우에 는 열전도율이 낮아야 한다. (2) 플렉시블 덕트는 AL.제품으로 그 사이에 철사로 보강된 것이어야 한다. (3) 보온된 플렉시블 덕트를 사용할 경우는 보온 두께가 25mm, 비중이 16kg/m2 인 유리솜(KS L 9102 인조 광물섬유 단열재)이며, 베이퍼 베리어(Vapor Barrior)로 커버된 것을 사용한다. 2.4.11 플렉시블 조인트 (Flexible Joint) (1) 플렉시블 조인트에 사용되는 재료는 원칙적으로 글래스 크로스(Glass Cloth)로 한다, (2) 편면(片面) 및 양면에 알루미늄 박 및 네오프랜으로 가공한 것으로 내열, 방염성능이 우수한 것으로 한다. (3) 양단의 플랜지 간격은 150~200mm 를 표준으로 한다. 2.4.12 점검구 및 청소구 (Access Door) (1) 개폐가 용이하며 폐쇄시에 공기누설이 적은 구조로 한다. (2) 점검구는 덕트와 같은 판두께의 KS D 3506(용융 아연도금 강판 및 강대) 또는 KS D 3512 (냉간 압연 강판 및 강대)를 사용한다. (3) 공조용 공기가 통과 하는 곳은 단열재를 충진하며 설치개소는 방화댐퍼 1 개소 마다 설치하며, 발주 담당자가 필요하다고 인정하는 부분에 설치한다. (4) 점검구 사이즈는 500X500 을 기본으로 하며, 설치 불가의 경우 발주 담당자와 협의 한다. (5) 규격 ① 가로 또는 세로 600mm 이상 : 500x500 점검구 적용 ② 가로 또는 세로 500mm 이하 : 덕트 SIZE 보다 100mm 작은 규격으로 적용 2.4.13 소음기 (Sound Attenuator) (1) 지정된 감음(�音) 성능을 유지하며 기류에 대해 악영향을 주지 않고 자기 발생음과 소음기 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
aa78f895-2e42-4c08-b5ed-a832ee1da4f3 | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ SPECIFICATION FOR ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ HVAC SYSTEM ¦ Page 8 of 30 ¦ 본체로부터의 투과 음이 저해요인으로 되지 않는 구조로 한다. (2) 흡음을 위하여 소음기 내부에 사용되는 흡음재는 불연성 또는 난연성으로 흡습성이 적고 부 패 또는 곰팡이가 발생하지 않으며, 소재의 먼지가 기류중으로 날리거나 떨어지지 않는 것으 으로 한다. (3) 케이싱 또는 보강틀은 두께 0.5mm 이상의 KS D 3506(용융 아연도금 강판 및 강대)로 하며, 견 고한 구조로 한다. (4) 기기저항은 15m/s 에서 80Pa 이하로 한다. 2.4.14 풍량측정구 (Test Hole) 알루미늄합금, 아연합금제 또는 스테인리스 제품으로 한다. 3. 시공 3.1 일반사항 공기 조화 및 환기용 덕트는 내부의 공기압력에 대해서 변형이 적고, 또 공기의 저항 및 누설이 적 으며 기류에 의해 발생하는 소음이 적은 구조로서 다음과 같은 조건을 만족시키도록 해야 한다. 3.1.1 덕트 만곡부의 구조 덕트 만곡부의 내측반경은 원칙적으로 장방형 덕트의 경우는 반경방향 덕트폭의 1/2 이상, 원형 덕트는 직경의 1/2 이상으로 한다. 단, 현장여건 상 덕트폭의 1/2 이상 불가능할 경우 발주 담당 자와 협의 한다. 3.1.2 덕트 단면변형의 구조 덕트의 단면을 변형시킬 때에는 급격한 변형을 피하고 점차적인 확대 또는 축소형으로 하며 확 대할 때는 경사각도를 15 도, 축소할 때는 30 도의 범위 이내로 한다. 3.1.3 일반벽체의 관통부처리 방화구획 이외의 벽면을 관통하는 덕트는 두께 1.0mm 이상의 KS D 3506(용융 아연도금 강판 및 강대) 또는 벽체와 동일 재질로 마감한다. 3.1.4 방화구획의 관통부처리 (1) 방화구획의 관통부에는 방화댐퍼를 부착한다. 내화구조의 인정 및 관리기준(국토교통부고시 제 2018-772 호)에 따른 내화충전구조로 인증된 방법 및 재료로 충진한다. (2) 관통부에는 방화댐퍼를 부착하지만 구획에 설치되지 않는 경우의 방화구획과 댐퍼 사이의 덕트는 1.6mm 이상의 강판제로 한다. SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
0672d9a0-a730-4ecf-864e-a77f6fead894 | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ SPECIFICATION FOR ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ HVAC SYSTEM ¦ Page 9 of 30 ¦ 3.1.5 덕트 입상의 지지보강 덕트 SHAFT 등과 같이 수평 DUCT 에서 입상 DUCT 로 바뀌는 ELBOW 부위는 입상 DUCT 자중에 의한 처짐을 방지하기 위해 지지간격과 별도의 추가 보강을 하여야 한다. 3.2 덕트 제작 및 설치 3.2.1 일반사항 (1) 각형 덕트 변의 이음은 PITTSBURGH LOCK SEAM 또는 LOCK GROOVED SEAM 으로 한다. 공기 흐름의 직각 방향의 이음은 내부 그루브씸으로 하고 동일면에서 피치가 900mm 이상 일 때는 측면 이음과 의 간격을 300mm 이상 떨어지지 않으면 안된다. 그리고 흐름 방향의 이음을 표준규격 철판으로 할 수 없을 때에는 내부 그루브씸으로 하여 사용하여야 한다. (2) HEPA 나 중성능 필터 등을 사용하는 공조 계통이 고정압이 되는 경우 공조기, 챔버류의 점검 구의 강도와 기밀성 확보에 주의 해야 한다. 또 개구부에 대해서는 운전 중에도 개폐가 가능한 방향으로 한다. 3.2.2 배기덕트 공사 (1) 배기덕트는 정압이 높아 운전경비가 많이 소요되므로 덕트계통에 정압이 최소로 유지될 수 있는 구조로 제작·설치하여야 한다. (2) 덕트에 LEAK 발생 시 소음, 진동, 압력저하 현상이 발생되므로 LEAK 를 최소화 하여야 한다. (3) 덕트 내·외의 압력차에 의한 변형이나 떨림이 없도록 보강을 하여야 한다. (4) 배기덕트는 정압이 높아 덕트 계통별로 적용되는 정압에 따라 덕트의 판두께와 보강방법을 달리하여야 한다. (PLENUM 내 덕트 및 옥상 노출덕트는 고속덕트 기준을 적용한다.) 3.2.3 덕트 호칭과 압력범위 (1) 고속덕트 적용 ¦ 구 분 ¦ FAB ¦ SUB C/R, CCSS, SMOCK ¦ 입상 ¦ 옥상노출 ¦ 외조기 ¦ 비고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ F.A DUCT ¦ N/A ¦ 고속 ¦ 고속 ¦ N/A ¦ 고속 ¦ ANGLE FLANGE ¦ ¦ PROCESS EXHAUST DUCT ¦ 고속 ¦ 고속 ¦ 고속 ¦ 고속 ¦ N/A ¦ ANGLE FLANGE ¦ ¦ EMER' EXHAUST DUCT ¦ 고속 ¦ 고속 ¦ 고속 ¦ 고속 ¦ N/A ¦ T.D.C ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
137f35f0-5fbc-48f7-bf8b-a290594b84f0 | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ SPECIFICATION FOR ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ HVAC SYSTEM ¦ Page 10 of 30 ¦ (2) 덕트 압력 분류에 의한 덕트 호칭과 압력범위 ¦ 압력분류에 의한 덕트호칭 ¦ 압력범위 ¦ 압력범위 ¦ 유속범위 [m/s] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 압력분류에 의한 덕트호칭 ¦ 상용압력 [Pa] ¦ 제한압력 [Pa] ¦ 유속범위 [m/s] ¦ ¦ 저 압 덕 트 ¦ +500 이하 - 500 이하 ¦ +1,000 이하 - 750 이하 ¦ 15 이하 ¦ ¦ 고압 1 덕트 ¦ +500 ~ +1,000 이하 -500 ~ - 1,000 이하 ¦ +,1500 이하 - 1,500 이하 ¦ 20 이하 ¦ ¦ 고압 2 덕트 ¦ +1,000 ~ +2,500 이하 -1,000 ~ -2,000 이하 ¦ +3,000 이하 -2,500 이하 ¦ 20 이하 ¦ ① 상용압력 : 정상운전 상태에서 덕트내의 최대정압 ② 제한압력 : 덕트내 댐퍼를 급격히 폐쇄하므로 인해 압력이 일시적으로 상승하는 경우의 제한압력을 말한다. 제한압력 이내이면 덕트의 안전강도와 공기누설량 등은 유지되고 있는 것으로 한다. 3.2.4 덕트의 판두께 (1) 장방형 덕트 장방형 덕트는 앵글플랜지 공법 및 코너볼트공법으로 하고, 덕트의 판두께는 아래의 표를 따 른다. 이형덕트의 경우에는 그 최대치수로 한다. ¦ 덕트속도 (압력)구분 ¦ 저압덕트 [mm] ¦ 고압 1, 2 덕트 [mm] ¦ 판두께 [mm] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 덕트의 장변 ¦ 450 이하 ¦ - ¦ 0.5 ¦ ¦ 덕트의 장변 ¦ 451 ~ 750 ¦ ¦ 0.6 ¦ ¦ 덕트의 장변 ¦ 751 ~ 1,500 ¦ 450 이하 ¦ 0.8 ¦ ¦ 덕트의 장변 ¦ 1,501 ~ 2,250 ¦ 451 ~ 1,200 ¦ 1.0 ¦ ¦ 덕트의 장변 ¦ 2,251 이상 ¦ 1,201 이상 ¦ 1.2 ¦ 코너볼트 공법은 공판플랜지 공법(共板工法) 및 슬라이드 온 플랜지(Slide On Flange) 공법을 말한다. ② 공판공법의 덕트는 단면의 종횡비를 1:4 이하로 한다. 1:4 의 비를 넘을 때에는 충분한 강도를 갖는 보강재로 보강한다. (2) 스파이럴덕트 직관은 아연도금철판 KS D 3506(용융 아연도금 강판 및 강대)을 스파이럴 형태로 기계제작한 것으로 호칭치수는 안지름을 표시하며 그 판의 두께는 아래의 표를 따른다. SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
706f6ed2-ced9-461c-b179-1d934a445a61 | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ SPECIFICATION FOR ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ HVAC SYSTEM ¦ Page 11 of 30 ¦ ¦ 덕트속도 (압력)구분 ¦ 저압덕트 [mm] ¦ 고압 1, 2 덕트 [mm] ¦ 판두께 [mm] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 덕트의 지름 ¦ 450 이하 ¦ 200 이하 ¦ 0.5 ¦ ¦ 덕트의 지름 ¦ 451 ~ 750 ¦ 201 ~ 600 ¦ 0.6 ¦ ¦ 덕트의 지름 ¦ 751 ~ 1,000 ¦ 601 ~ 800 ¦ 0.8 ¦ ¦ 덕트의 지름 ¦ 1,001 이상 ¦ 801 ~ 1,000 ¦ 1.0 ¦ ¦ 덕트의 지름 ¦ ¦ 1,001 이상 ¦ 1.2 ¦ 3.2.5 덕트의 이음매 (1) 장방형 덕트 덕트 모서리에 이음매는 1 개소 이상으로 하며, 피츠버그 보턴 펀치스냅 또는 더블 코너 이음 으로 한다. ② 분기덕트의 접속은 아래의 그림과 같이 한다. 분기덕트의 변이 긴 경우에는 형강을 사용한다. ![image](/image/placeholder) 형강 리벳 또는 리벳 또는 J 테이핑나사 테이핑나사 주덕트 분기덕트 주덕트 분기덕트 1 (2) 스파이럴 덕트 접음의 폭은 4.8mm 이상으로 하고, 그 피치는 아래의 표에 의한다. ¦ 덕트의 안지름 치수 [mm] ¦ 이음 피치 [mm] ¦ ¦ --- ¦ --- ¦ ¦ 100 이하 ¦ 100 이하 ¦ ¦ 101 ~ 1,000 ¦ 150 이하 ¦ 3.2.6 덕트의 접속 (1) 공판플랜지 공법(제살접기 공법) 덕트의 접속 공판플랜지 공법은 코너피스와 코너볼트, 공판으로 절곡 가능한 공판플랜지, 플랜지 누름클립, 개스킷을 사용하여 접속하며, 아래의 표에 의한다. SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
73ae5d5f-0d80-4d65-9443-dba632725a88 | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ SPECIFICATION FOR ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ HVAC SYSTEM ¦ Page 12 of 30 ¦ ¦ 덕트의 장변 [mm] ¦ 접 합 플 랜 지 ¦ 접 합 플 랜 지 ¦ 접 합 플 랜 지 ¦ 접 합 플 랜 지 ¦ 접 합 플 랜 지 ¦ 접 합 플 랜 지 ¦ 접 합 플 랜 지 ¦ 접 합 플 랜 지 ¦ 접 합 플 랜 지 ¦ 플랜지 최대간격 [mm] ¦ 플랜지 최대간격 [mm] ¦ 플랜지 최대간격 [mm] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 덕트의 장변 [mm] ¦ 공판플랜지 치수 ¦ 공판플랜지 치수 ¦ 공판플랜지 치수 ¦ 공판플랜지 치수 ¦ 코너 최소 치수 ¦ 코너 최소 치수 ¦ 코너 최소 치수 ¦ 플랜지 누름클립 최소치수 ¦ 플랜지 누름클립 최소치수 ¦ 플랜지 최대간격 [mm] ¦ 플랜지 최대간격 [mm] ¦ 플랜지 최대간격 [mm] ¦ ¦ 덕트의 장변 [mm] ¦ A [mm] ¦ B [mm] ¦ t 덕트판두께 [mm] ¦ t 덕트판두께 [mm] ¦ 판두께 [mm] ¦ 판두께 [mm] ¦ 접합 볼트의 호칭 경 ¦ 판두께 [mm] ¦ 판두께 [mm] ¦ 플랜지 최대간격 [mm] ¦ 플랜지 최대간격 [mm] ¦ 플랜지 최대간격 [mm] ¦ ¦ 덕트의 장변 [mm] ¦ A [mm] ¦ B [mm] ¦ 저압 ¦ 고압 1, 2 ¦ 저압 ¦ 고압 1, 2 ¦ 접합 볼트의 호칭 경 ¦ 저압 ¦ 고압 1, 2 ¦ 표준 ¦ 저압 ¦ 고압 1, 2 ¦ ¦ 450 이하 ¦ 30 ¦ 10 ¦ 0.5 ¦ 0.8 ¦ 1.6 ¦ 1.6 ¦ M9 ¦ 1.0 ¦ 1.2 ¦ 1,430 ¦ 2,860 ¦ 2,860 ¦ ¦ 451 ~ 750 ¦ 30 ¦ 10 ¦ 0.6 ¦ 1.0 ¦ 1.6 ¦ 1.6 ¦ M9 ¦ 1.0 ¦ 1.2 ¦ 1,430 ¦ 2,860 ¦ 1,430 ¦ ¦ 751 ~ 1,200 ¦ 30 ¦ 10 ¦ 0.8 ¦ 1.0 ¦ 1.6 ¦ 1.6 ¦ M9 ¦ 1.0 ¦ 1.2 ¦ 1,430 ¦ 2,860 ¦ 1,430 ¦ ¦ 1,201 ~1,500 ¦ 30 ¦ 10 ¦ 0.8 ¦ 1.2 ¦ 1.6 ¦ 1.6 ¦ M9 ¦ 1.0 ¦ 1.2 ¦ 1,430 ¦ 2,860 ¦ 1,430 ¦ ¦ 1,501 ~2,250 ¦ 30 ¦ 10 ¦ 1.0 ¦ 1.2 ¦ 1.6 ¦ 1.6 ¦ M9 ¦ 1.2 ¦ 1.2 ¦ 1,430 ¦ 1,430 ¦ 1,430 ¦ ¦ 2,251 이상 ¦ 30 ¦ 10 ¦ 1.2 ¦ 1.2 ¦ 1.6 ¦ 1.6 ¦ M9 ¦ 1.2 ¦ 1.2 ¦ 1,430 ¦ 1,430 ¦ 1,430 ¦ 주) 볼트 이외에 플랜지 누름 볼트 이외에 플랜지 누름클립 등으로 플랜지를 연결한다. 클램프 등으로 보강해도 무방하다. ② 클립의 폭은 150mm 이상, 판두께는 0.8mm 이상으로 한다. ③ 클립은 덕트 모서리로부터 150mm 이내, 클립간격은 150mm 이내에 설치한다. ④ 플랜지의 접합은 폭이 30mm 인 플랜지용 개스킷을 표준으로 한다. ⑤ 공판플랜지는 덕트의 끝을 접어서 성형한 것으로 덕트의 판두께와 동일한 판두께로 한다. ![image](/image/placeholder) 폭 ② ③ ⑤ ④ ⑥ 높 ① 이 ① 볼트(코너부위 4 개소) ② 너트(코너부위 4 개소) ③ 공판 플랜지 ⑥ ④ 코너피스 누름 m 표 all→1 29.=) 플랜지의 높이(A)는 30mm 이상, 플랜지의 폭(B)는 10mm 이상으로다. (a) 부정도 (DJ 글렌지 난번도 [공판플랜지 공법 덕트의 구성](2) 앵글플랜지 공법 덕트 접속] SK SK hynix ecoplant 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. | {}
3159df5c-a22c-4efd-9cb5-7382bf7bb0da | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ SPECIFICATION FOR ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ HVAC SYSTEM ¦ Page 13 of 30 ¦ (2) 앵글플랜지 공법 덕트의 접속은 아래의 표에 의한다. ▷ 저속덕트 ◁ ¦ 덕트의 장변 [mm] ¦ 접합용 플랜지 ¦ 접합용 플랜지 ¦ 접합용 플랜지 ¦ 접합용 플랜지 ¦ 접합용 플랜지 ¦ 접합용 플랜지 ¦ 플랜지 간격 [mm] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 덕트의 장변 [mm] ¦ 형강치수 [mm] ¦ 와셔형육각직결피스 ¦ 와셔형육각직결피스 ¦ 접합용 볼트 ¦ 접합용 볼트 ¦ 접합용 볼트 ¦ 플랜지 간격 [mm] ¦ ¦ 덕트의 장변 [mm] ¦ 형강치수 [mm] ¦ 와셔형육각직결피스 ¦ 와셔형육각직결피스 ¦ 볼트의 호칭 경 ¦ 볼트의 간격 (와셔형너트) ¦ 볼트의 간격 (와셔형너트) ¦ 플랜지 간격 [mm] ¦ ¦ 덕트의 장변 [mm] ¦ 형강치수 [mm] ¦ 호칭 지름 [mm] ¦ 간격 [mm] ¦ 볼트의 호칭 경 ¦ 코너부 [mm] ¦ 중앙부 [mm] ¦ 플랜지 간격 [mm] ¦ ¦ 750 이하 ¦ 40 X 40 X 3t ¦ 8 ¦ 65 ¦ M8 ¦ 100 ¦ 100 ¦ 1,510±10 ¦ ¦ 751 ~ 1,500 ¦ 40 X 40 X 3t ¦ 8 ¦ 65 ¦ M8 ¦ 100 ¦ 100 ¦ 1,510±10 ¦ ¦ 1,501 ~2,200 ¦ 40 X 40 X 3t ¦ 8 ¦ 65 ¦ M8 ¦ 100 ¦ 100 ¦ 1,510±10 ¦ ¦ 2,201 이상 ¦ 40 X 40 X 5t ¦ 8 ¦ 65 ¦ M8 ¦ 100 ¦ 100 ¦ 1,510±10 ¦ ▷ 고속덕트 ◁ ¦ 덕트의 장변 [mm] ¦ 접합용 플랜지 ¦ 접합용 플랜지 ¦ 접합용 플랜지 ¦ 접합용 플랜지 ¦ 접합용 플랜지 ¦ 접합용 플랜지 ¦ 플랜지 간격 [mm] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 덕트의 장변 [mm] ¦ 형강치수 [mm] ¦ 와셔형육각직결피스 ¦ 와셔형육각직결피스 ¦ 접합용 볼트 ¦ 접합용 볼트 ¦ 접합용 볼트 ¦ 플랜지 간격 [mm] ¦ ¦ 덕트의 장변 [mm] ¦ 형강치수 [mm] ¦ 와셔형육각직결피스 ¦ 와셔형육각직결피스 ¦ 볼트의 호칭 경 ¦ 볼트의 간격 (와셔형너트) ¦ 볼트의 간격 (와셔형너트) ¦ 플랜지 간격 [mm] ¦ ¦ 덕트의 장변 [mm] ¦ 형강치수 [mm] ¦ 호칭 지름 [mm] ¦ 간격 [mm] ¦ 볼트의 호칭 경 ¦ 코너부 [mm] ¦ 중앙부 [mm] ¦ 플랜지 간격 [mm] ¦ ¦ 750 이하 ¦ 40 X 40 X 3t ¦ 8 ¦ 65 ¦ M8 ¦ 100 ¦ 100 ¦ 1,510±10 ¦ ¦ 751 ~ 1,500 ¦ 40 X 40 X 3t ¦ 8 ¦ 65 ¦ M8 ¦ 100 ¦ 100 ¦ 1,510±10 ¦ ¦ 1,501 ~2,400 ¦ 40 X 40 X 5t ¦ 8 ¦ 65 ¦ M8 ¦ 100 ¦ 100 ¦ 1,510±10 ¦ ¦ 2,401 이상 ¦ 50 X 50 X 6t ¦ 8 ¦ 65 ¦ M8 ¦ 100 ¦ 100 ¦ 1,510±10 ¦ 플랜지는 형강을 사용하고, 네모퉁이를 외면 용접하며, 플랜지 접촉면이 평편하게 되도록 조립하여 구멍뚫기 작업을 한다. (단 보강용 플랜지는 외면 볼트체결 한다) ② 플랜지의 접속에는 플랜지 폭과 같은 플랜지용 개스킷을 사용하며, 볼트로 기밀이 유지되도 록 체결한다. ③ 덕트 절곡부의 접는 길이는 5mm 이상으로 하고 네모퉁이는 밀봉을 한다. 리벳 이외에 전기 점용접으로 해도 무방하며, 간격은 100mm 이내로 한다. SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
27f56d29-e0c6-44fb-bc45-ba44dfca1be2 | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 Page 14 of 30 ¦ ¦ --- ¦ --- ¦ --- ¦ 앵글 플랜지 덕트 HOLE 타공 예시 ¦ 75.100.100.100 75 100 100 100 ¦ 50100.100.100 10010011050 ¦ ¦ --- ¦ --- ¦ ¦ 100 단위 DUCT ¦ 50 단위 DUCT ¦ (3) 스파이럴 덕트의 접속 ① 커플링의 외면에 접착재를 발라 양끝을 덕트에 끼워넣고 강제(��) 테이핑나사로 접합하며 알루미늄 접착테이프로 감던가 또는 접합용 플랜지를 사용하여 마감한다. 또, 고압덕트의 경 우는 접속부에 밀봉을 한다. ② 커플링은 아연도금철판 KS D 3506 (용융 아연도금 강판 및 강대)으로 한다. ③ 이음매의 호칭치수는 외경기준으로 하고, 공차는 아래의 표와 같다. ¦ 호칭 치수 [mm] ¦ 공 차 [mm] ¦ ¦ --- ¦ --- ¦ ¦ 75 초과 600 이하 ¦ -1.5 초과 -2.5 이하 ¦ ¦ 600 초과 1,000 이하 ¦ -2.0 초과 -4.0 이하 ¦ ④ 이음매의 판두께는 아래의 표와 같다. ¦ 호칭 치수 [mm] ¦ 공 차 [mm] ¦ ¦ --- ¦ --- ¦ ¦ 300 이하 ¦ 0.6 ¦ ¦ 300 초과 700 이하 ¦ 0.8 ¦ ¦ 700 초과 1,000 이하 ¦ 1.0 ¦ ¦ 1,000 초과 1,250 이하 ¦ 1.2 ¦ ⑤ 이음매의 끼움길이는 아래의 표와 같다. ¦ 호칭 치수 [mm] ¦ 최 소 길 이 [mm] ¦ ¦ --- ¦ --- ¦ ¦ 300 이하 ¦ 25 이상 ¦ ¦ 300 초과 800 이하 ¦ 50 이상 ¦ ¦ 00 초과 1,250 이하 ¦ 100 이상 ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
0203e705-32b8-4beb-a775-71febd5c9cd0 | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ SPECIFICATION FOR ¦ 21036D-IC-M16G00-HV-A00-00131 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ HVAC SYSTEM ¦ Rev. 0 Page 15 of 30 ¦ ![image](/image/placeholder) 테이프 감은 폭 밀봉재 (고압덕트) [스파이럴 덕트 끼워넣기 이음 접합] (4) 볼트 조이기 ① 나사산 완전체결 후 여장길이는 최소 3 산 ~ 체결 BOLT 지름의 1.5 이하로 한다. ② 같은 플랜지에 체결되는 볼트/너트는 동일한 볼트/너트를 사용하여야 하며 같은 여장길이를 가져야 한다. ③ 볼트의 I 마킹대상 및 기준은 '18154D-CJ-G00-HV-A00-00170 플랜지체결공사'를 참조한다 ④ 플랜지체결은 '18154D-CJ-G00-HV-A00-00170 플랜지체결공사'에 의한다. 3.2.7 장방형덕트의 밀봉 덕트의 밀봉은 내부정압의 압력과 사용하는 이음매에 따라 필요한 등급의 밀봉을 한다. (1) 덕트의 밀봉등급과 밀봉이 필요한 장소는 아래의 표와 같다. ¦ 밀 봉 등 급 ¦ 밀봉의 필요장소 ¦ ¦ --- ¦ --- ¦ ¦ N 밀봉 ¦ - 덕트접합 플랜지부의 덕트굽힘 네모퉁이부 - 코너장착물과 플랜지부 ¦ ¦ A 밀봉 ¦ - 종방향의 이음부 ¦ ¦ B 밀봉 ¦ - 덕트의 접합부 ¦ ¦ C 밀봉 ¦ - 덕트이음부 전체 - 덕트관통부 (볼트, 리벳 등 모두 포함) ¦ * 스파이럴덕트의 록 이음(Lock Seam)은 밀봉조건으로부터 제외 한다. ![image](/image/placeholder) 밀봉재 밀봉재 앵글 플랜지 공법 (모서리부) N- 밀봉 코너 볼트공법 덕트 ![image](/image/placeholder) 내부밀붕 외부밀봉 종방향의 이음매 부분 A- 밀봉 [밀봉방식] SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
55251f6f-c5e6-42b3-8bbc-978ffedde4c0 | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ SPECIFICATION FOR ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ HVAC SYSTEM ¦ Page 16 of 30 ¦ (2) 용도 및 덕트압력 구분에 의한 이음과 밀봉등급의 조합은 아래의 표와 같다. ¦ 저 압 덕 트 ¦ 고압 1 덕트 ¦ 고압 2 덕트 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 보턴펀치 이음은 N 밀봉 ¦ 보턴펀치 이음은 N+A 밀봉 피츠버그 이음은 N 밀봉 ¦ 보턴펀치 이음은 N+A 밀봉 피츠버그 이음은 N 밀봉 정압 1,000Pa 를 넘는 공판덕트에서 보턴펀치 이음은 N+A+B 밀봉 피츠버그 이음은 N+B ¦ * 고압 1 덕트 및 고압 2 덕트의 덕트분기 접속부는 밀봉을 한다. (아래의 그림 참조) * 챔버 및 케이싱의 모퉁이 부분 등 누설의 염려가 있는 장소는 밀봉을 한다. ![image](/image/placeholder) 밀봉재 밀봉재 형강 리벳 또는 리벳 또는 护 -J 테이핑나사 테이핑나사 주덕트 주덕트 분기덕트 분기덕트 [고압덕트 접속부의 밀봉] 3.2.8 개스킷의 설치 (1) 개스킷은 덕트에 다루기가 쉽고 시공성이 확실한 것, 내부 공기 중에 함유된 약품류에 침식되 지 않는 것으로 NEOPRENE 고무 등을 일반적으로 사용하고, 유기성 덕트에는 PTFE 개스킷을 사용한다. (2) 캐스켓의 두께는 3~5mm 정도로, 개스킷의 경도에 따라서 부드러운 것은 5mm, 굳은 것은 3mm 와 같이 변화있게 사용하여 시공 불균등으로 인한 틈을 방지하여야 한다. 특히 코너 부분에 서 개스킷의 맞대기부의 틈새가 생기기 쉬우므로 시공 시 주의 하여야 한다. (3) 덕트의 분기 접속부와 접속방법은 플랜지를 사용하여 볼트로 연결하여야 한다. 또, 분기 접속 부의 SEAL 은 필히 행하여야 한다. (4) 기기 주위나 벽, 바닥 관통부와 덕트는 방진을 위해 CANVAS 이음을 사용한다. 재료는 GLASS FIBER FABRIC 양면에 PVC 코팅한 방염성능의 제품을 사용한다. (5) 신축이음부를 통과 하는 덕트 등은 쌍방의 건물에 생기는 최대 상대변위량을 흡수할 수 있도 록 플렉시블 이음의 장치를 한다. (6) 플렉시블 덕트의 길이는 2.0m 이내로 한다. SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
02a3e78b-ceee-457a-93ae-d4aed5e58fe0 | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ SPECIFICATION FOR ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ HVAC SYSTEM ¦ Page 17 of 30 ¦ 3.2.9 덕트의 보강 장방형 덕트의 보강기준은 아래의 표에 따른다. (1) 공판 플랜지 덕트(SA, RA, EMER. 배기) 보강 ¦ 덕트의 장변 [mm] ¦ 판두께 [mm] ¦ 보 강 형 식 ¦ 보 강 형 식 ¦ 덕트 접합 방식 ¦ 보강간격 [mm] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 덕트의 장변 [mm] ¦ 판두께 [mm] ¦ 외부 4 면 보강 ¦ 내부 종(�) 보강 ¦ 덕트 접합 방식 ¦ 보강간격 [mm] ¦ ¦ 450 이하 ¦ 0.5 ¦ - ¦ - ¦ 공판플랜지 ¦ ¦ ¦ 451 ~ 700 ¦ 0.6 ¦ - ¦ - ¦ 공판플랜지 ¦ ¦ ¦ 701 ~ 750 ¦ 0.6 ¦ V 보강바 ¦ - ¦ 공판플랜지 ¦ 715 ¦ ¦ 751 ~ 1,000 ¦ 0.8 ¦ V 보강바 ¦ - ¦ 공판플랜지 ¦ 715 ¦ ¦ 1,001 ~ 1,300 ¦ 0.8 ¦ V 보강바 ¦ - ¦ 공판플랜지 ¦ 715 ¦ ¦ 1,301 ~ 1,500 ¦ 0.8 ¦ V 보강바 ¦ TIE ROD X 1 개소 ¦ 공판플랜지 ¦ 715 ¦ ¦ 1,501 ~ 2,250 ¦ 1.0 ¦ V 보강바 ¦ TIE ROD X 1 개소 ¦ 공판플랜지 ¦ 715 ¦ ¦ 2,251 이상 ¦ 1.2 ¦ V 보강바 ¦ TIE ROD X 1 개소 ¦ 공판플랜지 ¦ 715 ¦ * 보강간격 715mm 는 Duct 한 개소의 Duct 보강 간격이다. * 압괴가 예상되는 덕트는 발주 담당자와 협의 하여 시공 시 덕트 상부 작업에 의한 찌그러짐 또는 훼손을 방지하기 위하여 추가 보강을 한다. * TIE ROD : 15A GAL'V PIPE (내부 전산볼트 12⌀) ![image](/image/placeholder) B ¦ DIMENSION ¦ A ¦ B ¦ C ¦ D ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ DIMENSION ¦ 65mm ¦ 31mm ¦ 41mm ¦ 1.0mm ¦ ¦ MATERIAL ¦ 1) HOT - DIP GALVANIZED 2) ZINC COATING 350g/m2 (0.433mm) ¦ 1) HOT - DIP GALVANIZED 2) ZINC COATING 350g/m2 (0.433mm) ¦ 1) HOT - DIP GALVANIZED 2) ZINC COATING 350g/m2 (0.433mm) ¦ 1) HOT - DIP GALVANIZED 2) ZINC COATING 350g/m2 (0.433mm) ¦ ¦ MATERIAL ¦ ¦ ¦ ¦ ¦ ¦ MATERIAL ¦ 3) KS-3520 ¦ 3) KS-3520 ¦ 3) KS-3520 ¦ 3) KS-3520 ¦ (2) ANGLE FLANGE 덕트 (FA, PROCESS EXHAUST) 보강 (Process Exhaust Sub Dcut 1,000mm 미만의 경우 TDC Duct 를 적용하며 제작 기준은 2-1 참조) ¦ 덕트의 장변 [mm] ¦ 판두께 [mm] ¦ 보 강 형 식 ¦ 보 강 형 식 ¦ 덕트 접합 방식 ¦ 보강간격 [mm] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 덕트의 장변 [mm] ¦ 판두께 [mm] ¦ 외부 4 면 보강 ¦ 내부 종(�)보강 ¦ 덕트 접합 방식 ¦ 보강간격 [mm] ¦ ¦ 450 이하 ¦ 0.8 ¦ 40 X 40 X 3t ¦ - ¦ ANGLE FLANGE ¦ 750 ¦ ¦ 451 ~ 1,200 ¦ 1.0 ¦ 40 X 40 X 3t ¦ ¦ ANGLE FLANGE ¦ 750 ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
ba10939b-f285-48b0-9c1c-e6a709331bbb | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ SPECIFICATION FOR ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ HVAC SYSTEM ¦ Page 18 of 30 ¦ ¦ 1,201 ~ 1,500 ¦ 1.2 ¦ 40 X 40 X 3t ¦ - ¦ ANGLE FLANGE ¦ 750 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1,501 ~ 2,400 ¦ 1.2 ¦ 40 X 40 X 5t ¦ ¦ ANGLE FLANGE ¦ 750 ¦ ¦ 2,401 ~ 2,700 ¦ 1.2 ¦ 50 X 50 X 6t ¦ TIE ROD x2 개소 ¦ ANGLE FLANGE ¦ 750 ¦ ¦ 2,701 이상 ¦ 1.2 ¦ 50 X 50 X 6t ¦ TIE ROD x2 개소 ¦ ANGLE FLANGE ¦ 750 ¦ * 압괴가 예상되는 덕트는 발주 담당자와 협의 하여 시공 시 덕트 상부 작업에 의한 찌그러짐 또는 훼손을 방지하기 위하여 추가 보강을 한다. * TIE ROD : 15A GAL'V PIPE (내부 전산볼트 12⌀) (2-1) Process Exhaust Sub Dcut 1,000mm 미만 TDC Duct 제작 기준 [Hook-up 연결 Duct] ORG, CABINET, HEAT GEN 덕트 해당 ¦ 덕트의 장변 [mm] ¦ Process Exhaust TDC 제작 기준 ¦ Process Exhaust TDC 제작 기준 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 덕트의 장변 [mm] ¦ 판두께 ¦ 보강방식 ¦ ¦ 덕트의 장변 [mm] ¦ [mm] ¦ 외부 4 면 보강 ¦ ¦ 450 이하 ¦ 1.0 ¦ V 보강바 ¦ ¦ 451 ~ 700 ¦ 1.0 ¦ V 보강바 ¦ ¦ 701 ~ 750 ¦ 1.0 ¦ V 보강바 ¦ ¦ 751 ~ 999 ¦ 1.2 ¦ V 보강바 ¦ * CR 내부 평면도 Chart Type: bar Cn Kn Cailing Catering Hook-up 연결 Sub Duct Sub Header Other item_01 1 3 2 2 1 1 2 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. | {}
4e900f05-a88f-448f-871b-2e0593ed01c2 | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ SPECIFICATION FOR ¦ 21036D-IC-M16G00-HV-A00-00131 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ HVAC SYSTEM ¦ Rev. Page 19 of 30 ¦ Chart Type: bar (Hook-up 연결 Sub Duct) (EngHA, Actual) (Flood, Actual) item_01 10Not specified 15Not specified 5Not specified - 단면도 - (3) ROOF 덕트(FA, SA, RA, PROCESS & EMER. EXHAUST) 보강 ¦ 덕트의 장변 [mm] ¦ 판두께 [mm] ¦ 보 강 형 식 ¦ 보 강 형 식 ¦ 덕트 접합 방식 ¦ 보강간격 [mm] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 덕트의 장변 [mm] ¦ 판두께 [mm] ¦ 외부 4 면 보강 ¦ 내부 종(�)보강 ¦ 덕트 접합 방식 ¦ 보강간격 [mm] ¦ ¦ 450 이하 ¦ 1.2 ¦ 50 X 50 X 6t ¦ - ¦ ANGLE FLANGE ¦ 500 ¦ ¦ 451 ~ 1,200 ¦ 1.2 ¦ 50 X 50 X 6t ¦ ¦ ANGLE FLANGE ¦ 500 ¦ ¦ 1,201 ~ 1,500 ¦ 1.2 ¦ 50 X 50 X 6t ¦ - ¦ ANGLE FLANGE ¦ 500 ¦ ¦ 1,501 ~ 2,400 ¦ 1.2 ¦ 50 X 50 X 6t ¦ - ¦ ANGLE FLANGE ¦ 500 ¦ ¦ 2,401 ~ 2,700 ¦ 1.2 ¦ 50 X 50 X 6t ¦ TIE ROD x2 개소 ¦ ANGLE FLANGE ¦ 500 ¦ ¦ 2,701 이상 ¦ 1.2 ¦ 50 X 50 X 6t ¦ TIE ROD x2 개소 ¦ ANGLE FLANGE ¦ 500 ¦ SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. SK ecoplant | {}
c802b66f-d0de-49d5-8322-ec4a20204075 | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ SPECIFICATION FOR ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ HVAC SYSTEM ¦ Page 20 of 30 ¦ * 압괴가 예상되는 덕트는 발주 담당자와 협의 하여 시공 시 덕트 상부 작업에 의한 찌그러짐 또는 훼손을 방지하기 위하여 추가 보강을 한다. * TIE ROD : 15A GAL'V PIPE (내부 전산볼트 12⌀) 3.2.10 노출 덕트의 도장 Clean Room 노출 덕트 도색 : 아이보리색 분체 도장을 한다. (분체 도장 색상은 발주처의 승인을 득한다.) ![image](/image/placeholder) 3.3 덕트의 지지 및 방진 3.3.1 수평지지 행거 및 덕트 지지 재료는 아래의 표에 의하며 방진이 필요한 경우에는 방진재를 사용 한다. (1) 장방형 덕트 행거 및 지지 ¦ 덕트의 장변 [mm] ¦ 행 거 지 지 ¦ 행 거 지 지 ¦ 행 거 지 지 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 덕트의 장변 [mm] ¦ 수평지지 철물 ¦ 환봉 ¦ 최대간격 [mm] ¦ ¦ 1,200 이하 ¦ L 형강 40 X 40 X 3T ¦ M9 ¦ 3,000 ¦ ¦ 1,201 ~ 1,500 ¦ L 형강 50 X 50 X 4T ¦ M9 ¦ 3,000 ¦ ¦ 1,501 ~ 2,500 ¦ L 형강 50 X 50 X 6T ¦ M9 ¦ 3,000 ¦ ¦ 2,501 이상 ¦ � 형강 75 X 40 X 5T X 7T ¦ M9 ¦ 3.000 ¦ ![image](/image/placeholder) 10M 이하(이중행거 적용) 말단부 :0.1M 이하 3M 이하(단일행거) -환봉 -형강 형강� 방진패드- 이중행거 행거 이중행거� 방진패드 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
520aceda-8333-43eb-8510-0fc1213c9866 | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ SPECIFICATION FOR ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ HVAC SYSTEM ¦ Page 21 of 30 ¦ [덕트 지지 방법] * 지상층 덕트 행거 고정 시 반드시 12m 이내에 1 개소 이상 �형강, L 형강 보강 할 것 (내진 설계 Guide Line 기준에 따른다.) 수평지지 철물의 길이는 덕트 폭(보온이 있을 경우 보온포함) 보다 50mm 크게 한다. 환봉의 길이가 2,400mm 이상 되어 흔들림이 있는 경우는 덕트 상부에 L 형강을 설치하여 흔 들림을 방지한다. 덕트의 연결 길이가 10m 이상일 경우 행거 지지는 10m 마다 1 개소씩 상·하부 이중 행거를 사용한다. ④ OAC 실의 F.A MAIN HEADER 지지용 환봉은 M16 을 적용한다. ⑤ 행거볼트 끝단부는 너트 체결 후 Max. 50mm 이내로 절단 후 RED CAP 처리한다. ⑥ 행거는 덕트 전용으로 설치해야 하며, 트레이 등 타용도의 지지물과 혼용해서는 안된다 ![image](/image/placeholder) 환봉㊹ 환 형강 (a) 매닮 방법 형강 덕트 형강 [행거 및 지지철물의 설치] (2) 스파이럴 덕트 행거 및 지지 ¦ 덕트의 장변 ¦ 행 거 ¦ 지 지 체 ¦ 최대간격 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
5cb606b1-8130-4400-9aa6-c16a284899fe | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ SPECIFICATION FOR ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ HVAC SYSTEM ¦ Page 22 of 30 ¦ ¦ [mm] ¦ 평강치수 [mm] ¦ 환봉 ¦ 형강치수 [mm] ¦ [mm] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1,250 이하 ¦ 30 X 3T ¦ M10 ¦ L 형강 30 X 30 X 3T ¦ 3,000 ¦ (3) 천정덕트 방진 방진은 전문 업체에 의뢰하여 계산·선정하며, 발주 담당자의 승인을 득한 후 설치하여야 한 다. (4) 덕트 장변 1000mm 기준 최소 2 개 방진 PAD 를 상부 또는 상/하부(이중행거)에 설치한다. 장변 500mm 초과 시 마다 1 개 방진 PAD 를 하부에 추가 설치 한다. (5) 방진 패드는 등 간격으로 설치하며, 방진 패드 너비는 덕트 서포트 양쪽 폭 방향으로 10mm 이상 나오도록 설치한다. (6) 회의 실이나 교육실등 소음에 민감한 AREA 의 덕트는 SPRING 행거 지지 및 소음 FLEXIBLE DUCT 를 설치해야 한다. 3.3.2 덕트용 부속품의 설치 (1) 외기흡입 및 배기루버 (O.A & E.A Louver) ① 루버는 건물에 견고하게 부착하며, 건축본체와 의 사이는 밀봉하여 기밀을 유지시킨다. 또, 루버와 덕트의 접합부는 접합플랜지 등으로 견고하게 공기의 누설이 없도록 설치한다. ② 스테인리스 망을 설치하고, 탈착이 용이해야 하며, 필요한 경우에는 댐퍼 등을 설치한다. ③ 외부에 접하여 빗물이 침투 될 수 있는 루버의 챔버에는 배수배관 및 밸브를 설치하여야 한다. (2) 토출구, 흡입구 토출구, 흡입구는 부착용 개스킷을 사용하여 기밀이 유지되도록 설치하고 외관이 건축마감재 와 조화 될 수 있어야 한다. (3) 풍량조절댐퍼 (V.D : Volume Damper) 기밀이 유지되고 조정이 용이하게 이루어질 수 있도록 설치한다. 천정이나 샤프트 내에 댐퍼 를 설치하는 경우에는 점검구를 설치하여 점검이 가능하도록 한다. (4) 방화댐퍼 (F.D : Fire Damper) KS F 2815 (배연설비의 검사표준)에 준하여 설치한다. SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
391fb059-aa3c-4598-aad1-e2409de49662 | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ SPECIFICATION FOR ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ HVAC SYSTEM ¦ Page 23 of 30 ¦ 바람직하지 롯한 설치 방법의 보기 바람직한 설치 방법의 보기 ![image](/image/placeholder) 구조체에 견고하게 설치한다. 등도의 나하에 달대 모르타르 견뎌 금 담대 등도 등도 등도 등도 15mm 이상의 일반 방화 대거 몸체 끝에서 담아 냉 방화 구획 방화 대저 참고 그림 2 방화 댐퍼의 설치 방법 [방화 댐퍼의 설치 방법(KS F 2815 기준)] (5) 방화겸용 풍량조절댐퍼 (F.V.D : Fire Volume Damper) 방화댐퍼 설치에 준한다. (6) 피스톤 릴리스 댐퍼 (P.R.D : Piston Release Damper) 방화댐퍼 설치에 준한다. (7) 플렉시블 덕트 (Flexible Duct) ① 기밀을 유지하고 유효면적에 영향을 미치지 않도록 설치한다. ② 플렉시블 덕트의 길이는 최대 2.0m 이내로 시공하고, 기류의 흐름이 원활히 이루어 지도록 시공한다. (8) 플렉시블 조인트 (Flexible Joint) ① 진동 발생 장비와 덕트의 접속부분에 사용하는 플렉시블 조인트는 그 양단의 플랜지 간격 을 약 150~200mm 로 하고, 한국공업규격에 따른 PVC 가 코팅된 KS L 2508 (유리 직물)로 직 조 된 2 중겹 CANVAS 로 하여 사용처에 충분한 강도를 갖는 것으로 한다. ② 방화 구조체에서는 GLASS FIBER FABRIC 양면에 PVC 코팅한 방염성능의 제품을 사용한다. (9) 점검구 (Access Door) 개폐가 용이하고 개폐시 공기누설이 없도록 설치한다. 또한 덕트의 접속부분도 개스킷 등을 사용하여 견고하게 설치한다. (10) 풍량측정구 (Test Hole) 덕트 내의 풍량, 풍속, 정압 및 온습도 측정을 위해 덕트의 정중앙 등에 10mm 크기 정도의 Test Hole 을 덕트의 장변과 단변에 설치하여야 한다. 3.4 덕트 DRAIN 배관 입상덕트의 하부나 응축수 고임 예상 부위 및 덕트 내 SPRINKLER HEAD 설치부에 원활한 배수를 위하여 DRAIN PORT 를 설치한다. DRAIN PORT 는 배출가스의 흐름에 방해가 되지 않는 모양으로 제 작하고 FM PVC, PE, STS 배관이나 밸브 등의 부속재와 연결하여 배수 될 수 있어야 한다. SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
8af85ebb-b415-4e49-ae9e-72be42b89034 | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ SPECIFICATION FOR ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ HVAC SYSTEM ¦ Page 24 of 30 ¦ 또한, 추후 CLEANING 을 위하여 분해 및 조립이 용이한 구조로 설치하여야 한다. 3.4.1 DRAIN PORT 및 배관 설치 구분 ¦ 구 분 ¦ SUB FAB ¦ SUB FAB ¦ PLENUM ¦ PLENUM ¦ Scrubber RM ¦ Scrubber RM ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 구 분 ¦ SUB ¦ HEADER ¦ SUB ¦ HEADER ¦ Riser Duct ¦ Header ¦ ¦ Acid ¦ 50A HF ¦ 100A HF (25m 간격) ¦ 50A HF ¦ 100A HF (25m 간격) ¦ 50A HF ¦ 100A HF (25m 간격) ¦ ¦ Acid(Mid.), Acid(PFC) ¦ 100A HF ¦ 100A HF (35m 간격) ¦ ¦ ¦ 50A HF ¦ - ¦ ¦ Alkali ¦ 50A HF ¦ 100A HF (15m 간격) ¦ 50A HF ¦ ¦ 50A HF ¦ 100A HF (25m 간격) ¦ ¦ Heat/Gen ¦ ¦ - ¦ 미적용 ¦ 미적용 ¦ 미적용 ¦ GALV. ¦ ¦ Organic ¦ ¦ ¦ 50A Solvent ¦ 50A Solvent (25m 간격) ¦ 50A Solvent ¦ 50A Solvent (25m 간격) ¦ ¦ Cabinet ¦ 미적용 ¦ 미적용 ¦ 미적용 ¦ - ¦ 미적용 ¦ 100A HF (25m 간격) ¦ ¦ Emer. ¦ 미적용 ¦ 미적용 ¦ 미적용 ¦ 미적용 ¦ 미적용 ¦ 미적용 ¦ * ACID, ALKALI, CABINET DUCT DRAIN 의 재질은 P.E(PolyEthylene) - FM PVC 로 한다. * ORG DUCT DRAIN 의 재질은 STS304 로 한다. * DRY, H/G 은 Roof Header 에 Port 만 구성하고 PVC 볼밸브로 마감한다. 설치 순서 Sub FAB & Plenum: Drain Port → Ball Valve → 무봉수 Trap F03, F04 Utility, CR 노출 Duct: Drain Port → Sight Glass → Ball Valve → Blind Flange 마감 3.4.2 PVC DRAIN 배관 (1) 작업 도구 준비 작업 시작 전 작업을 위한 각종 자재(프라이머, 접착제 및 각종 공구)를 사전에 준비한다. (2) 파이프 절단 파이프는 가능한 한 직각으로 CUTTING 하여야 한다. (3) 내외경 면취 내외경 면취의 경우 모서리 따기용 줄이나 BEVELLING TOOL 을 이용하되 파이프 끝에서 1/16" ~3/32"의 폭으로 10~15 °의 경사를 주어 면취한다. SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
ac0485ed-c4cd-419b-8c51-1e15865cffe9 | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 Page 25 of 30 ¦ ¦ --- ¦ --- ¦ --- ¦ (4) 접합면 청소 수분 및 유분 기타 이물질은 파이프 및 피팅의 표면 용해 및 접착에 방해를 줄 수 있으므로 깨끗하고 마른 걸레로 파이프와 피팅류의 안팎에 있는 먼지, 유분, 톱밥이나 물기들을 모두 제거하여야 한다. (5) 삽입 깊이 체크 ① 접착제를 도포하기 전에 파이프 및 피팅을 똑바로 가볍게 삽입시켜 파이프가 수구 길이의 1/3~2/3 지점에서 멈추어지는 지 확인한다. ② 파이프가 완전히 삽입되었는지를 확인하기 위해 피팅 소켓의 길이를 측정하여 그 간격을 파이프 외면에 표시한다. ③ 프라이머와 접착제를 도포할 때, 표시(Marking)가 지워질 수 있으므로 삽입 깊이 + 50mm 위치 추가 Marking 한다 (6) 접착제 도포 ① 파이프와 피팅이 깨끗하고 습기와 부스러기가 없을 때 솔벤트 접착제를 도포해야 하며, 바 른 프라이머가 진득진득할 때 즉시 도포해야 한다. ② 접착제는 칠붓, 천연모 브러시 또는 파이프 직경의 약 1/2 SIZE 인 롤러를 사용하여 접합 표 면에 도포해야 한다. 파이프 끝부분 바깥에 이음 소켓의 길이와 같게 접착제를 두껍게 칠한 다. ③ 칠하는 양은 간격을 채우는데 충분한 분량 이상이 되어야 하며, 이음 소켓에는 중간 정도로 칠하되 뒤범벅되지 않도록 한다. (7) 조립 ① 양쪽 표면이 솔벤트 접착제로 적셔져 있는 동안 파이프를 1/4 바퀴 회전시키면서 신속하게 이음매 소켓에 끼워넣는다. ② 파이프는 이음재 중단점에 완전하게 자리를 잡아야 한다. ③ 최초 접합이 확실히 되도록 약 30 초 동안 잡고서 조립상태를 유지한다. ④ 억지로 삽입한 맞춤부의 테이퍼(경사진면) 때문에 최초 접착 중에 일정한 압력이 유지되지 않으면 파이프는 이음매 중단점에서 뒤로 물러날 수 있다. ⑤ 파이프 주변과 이음재 연결부에 접착제 방울이 보여야 한다. 이 방울이 소켓 어깨 주위로 연속되어 나타나지 않으면 접착제가 충분하지 않게 도포되었 음을 표시하는 것이다. 불충분하게 접착제가 도포되면 접합부를 잘라내고 다시 접합하여야 한다. ⑥ 접착제 방울이 과다하면 헝겊으로 닦아내어야 한다. 3.4.3 STS DRAIN 배관 STS DRAIN 배관의 시공은 '18154D-CJ-G00-HV-A00-00122 PCW 배관공사' 시방에 따른다. 단, DUCT DRAIN 은 비압력부로, 육안검사만 수행한다. SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
4c6dfb43-18e9-4ba4-896b-f01d94e351c9 | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ SPECIFICATION FOR ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ HVAC SYSTEM ¦ Page 26 of 30 ¦ 3.4.4 입상덕트의 설치 (1) 원형덕트 ① Channel (100x50x5t) Support 는 바닥에 고정한다. (Set Anchor 또는 직결나사 또는 Welding 사용하여 고정) 원형 클램프 내부에 고무패드(3t)를 넣고, 덕트와 고정 한다. 원형 클램프에 고정된 원형 덕트를 Channel Support 위에 방진 패드(20t)와 함께 Bolting 고정 한다. D/S 의 경우는 Channel Support 와 원형덕트 사이는 Flashing 마감만 적용하고, FAB & 습식 구조 바닥의 경우 Channel Support 와 원형덕트 사이는 오염방지 및 최상층 누수시 물고임 방지를 위하여 방화 마감 후, GAL V(0.8t)로 적용한다. ![image](/image/placeholder) ④ ② 0.8t GAL V 이상 원형 클램프 (PL6Tx 904L /RUBBER PAD 3T) ① CHANNEL 3 (100x50x5tx7t) (2) 사각덕트 Channel (100x50x5t) Support 는 바닥에 고정한다. (Set Anchor 또는 직결나사 또는 Welding 사용하여 고정) ② 그외 Channel (100x50x5t) 2 개는 덕트에 100mm 간격으로 볼트(M8) 고정한다. Channel 에 고정된 사각 덕트를 Channel Support 위에 방진 패드(20t)와 함께 Bolting 고정 한다. D/S 의 경우는 Channel Support 와 사각덕트 사이는 Flashing 마감만 적용하고, FAB & 습식 구조 바닥의 경우 Channel Support 와 사각덕트 사이는 오염방지 및 최상층 누수시 물고임 방지를 위하여 방화 마감 후, GAL V(0.8t)로 적용한다. hynix SK SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
dc5279c8-964c-4128-9a59-61527b9925c9 | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 Page 27 of 30 ¦ ¦ --- ¦ --- ¦ --- ¦ ![image](/image/placeholder) ④ 0.8t GAL V 이상 3 ① CHANNEL (100x50x5tx7t) ② CHANNEL(100x50x5t) BOI TING (M8) 1 00mm 가격 3.5 부식방지 3.5.1 덕트를 고정·조립 할 경우 전위부식방지를 위하여 동일한 재질의 재료를 사용하여야 하고, 최 대한 이종금속사용을 배제하여야 하며 꼭 이종금속을 사용해야 하는 경우는 전위부식방지를 위 해 절연플랜지 또는 절연 볼트/ 너트/ 와셔등을 사용하는 적정한 조치를 취하여야 한다. 3.5.2 콘크리트 등 바닥위에 구조물 또는 장비를 설치할 경우에는 구조물 또는 장비의 부식방지를 위하여 콘크리트 등 바닥 구조물 또는 장비 사이에 RUBBER PAD 를 설치하여 시공한다. 3.5.3 부식방지를 위하여 볼팅을 하거나 나사못과 같은 것으로 조립작업 등을 할 경우 나사못 또는 이와 유사한 것과 철판 등의 피조립물 등 사이에 RUBBER PAD 를 설치한다. 3.5.4 장비 또는 구조물 등을 콘크리트 등 바닥에 고정할 경우 SET ANCHOR 등 고정물과 구조물 또는 장비는 같은 재질의 볼트와 너트를 사용하여 부식을 방지한다. 3.5.5 용접부위는 특히 부식에 취약하므로 충분한 조치를 하여 부식을 방지하도록 한다. 3.6 시공 허용오차 3.6.1 현장 시공오차 최소화방안 (1) 배관 시공 시 정확한 시공을 위해 시공 기준선(레이져, 먹선 등)을 활용한다. (2) 설계도면(Shop 도면)과 현장시공 오차 hynix SK SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
ee379820-584a-47a9-8ecb-820883fc5948 | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ SPECIFICATION FOR ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ HVAC SYSTEM ¦ Page 28 of 30 ¦ ¦ 구 분Ⓤ ¦ 오차 한계(mm)� ¦ ¦ --- ¦ --- ¦ ¦ F02 P ¦ 土 50p ¦ ¦ F03, F04, CUB 등⌀ ¦ 土 75p ¦ 3.7 검사 3.7.1 방진의 시공 규격 및 PAD 설치 상태 3.7.2 분기부 및 플랜지 누름 클립 체결 간격 3.7.3 Support / Hanger 의 간격 및 수직 · 수평 등 설치 상태 3.7.4 댐퍼 Type 및 작동 상태, 타공정 간섭 상태 3.7.5 방화벽체 관통부 마감상태 3.7.6 구간별 계통검사 (Route 및 기구류 위치 등 도면 일치 여부) 3.7.7 덕트 변형 및 훼손 여부 확인 3.7.8 타 설비 간섭 및 이격(진동 전달 방지) 확인 3.7.9 덕트 보양 상태 3.7.10 덕트 규격 도면 일치 확인 3.7.11 덕트 체결 상태 및 보온 상태 3.7.12 외부 D/S 구간은 옥외쪽으로 덕트경사(단차 : 100mm)를 두어 외부 빗물 유입의 근본적 차단 3.8 덕트 표식 '18154D-CJ-G00-HV-A00-00191 APPENDIX- I (눈 관리 STICKER)' 참조 3.9 PROCESS EXHAUST DUCT ACCESSORY '18154D-CJ-G00-HV-A00-00192 APPENDIX-II (PROCESS EXHAUST DUCT ACCESSORY)' 참조 3.10 안정적 VOC System 구축 1) Header 양 끝단에서 Duct 분기후, Header Duct 장변길이 이상 확보. Worst Case ![image](/image/placeholder) Best Case ![image](/image/placeholder) hynix SK SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
6c034b31-55a7-4a32-8238-80b5fa6ec372 | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 Page 29 of 30 ¦ ¦ --- ¦ --- ¦ --- ¦ 2) Header 분기되는 Duct 한쪽으로 편중되지 않게 균등배치 할 것. ¦ Worst Case ¦ Best Case ¦ ¦ --- ¦ --- ¦ ¦ ¦ ¦ 3) VOC FAN Inlet Duct 는 원형으로 시공. Worst Case Best Case ![image](/image/placeholder) 100)-54 1) 공간 협소등 Route 불합리 부분은 발주처 협의 하에 CFD 해석 검토 할 수 있음. - End of Document - SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
1c1fff24-6f91-42c5-8631-7b0e90611c70 | 21036D-IC-M16G00-HV-A00-00131 M16_Ph-2 시방서-GALV. 덕트공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ SPECIFICATION FOR ¦ 21036D-IC-M16G00-HV-A00-00131 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ HVAC SYSTEM ¦ Page 30 of 30 ¦ ¦ 첨부- 1 배기덕트 재질표 ¦ ¦ --- ¦ ¦ ¦ ¦ 구 분 ¦ DUCT MATERIAL ¦ DUCT MATERIAL ¦ DUCT MATERIAL ¦ DUCT MATERIAL ¦ DUCT MATERIAL ¦ DUCT MATERIAL ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 구 분 ¦ SUB FAB ¦ SUB FAB ¦ PLENUM ¦ PLENUM ¦ RISER ¦ 인입 SCR. HEADER ¦ ¦ 구 분 ¦ SUB ¦ HEADER ¦ SUB ¦ HEADER ¦ RISER ¦ 인입 SCR. HEADER ¦ ¦ ACID ¦ FM PVC ¦ FRP ¦ FM PVC ¦ FRP ¦ STS ¦ FRP ¦ ¦ ACID (MID,PFC) ¦ STS+ETFE COATING ¦ FRP ¦ - ¦ - ¦ STS+ETFE COATING ¦ FRP ¦ ¦ ALKALI ¦ FM PVC ¦ FRP ¦ FM PVC ¦ - ¦ STS ¦ FRP ¦ ¦ ORG ¦ - ¦ - ¦ GALV. ¦ GALV. ¦ GALV. ¦ GALV. ¦ ¦ DRY ¦ STS+ETFE COATING ¦ FRP ¦ FM PVC ¦ FM PVC ¦ STS+ETFE COATING ¦ FRP ¦ ¦ CABINET ¦ GALV. ¦ GALV. ¦ GALV. ¦ - ¦ GALV. ¦ GALV. ¦ ¦ H/G ¦ GALV. ¦ GALV. ¦ GALV. ¦ GALV. ¦ GALV. ¦ GALV. ¦ ¦ EMER' ¦ GALV. ¦ GALV. ¦ GALV. ¦ GALV. ¦ GALV. ¦ GALV. ¦ * Scrubber ROOM Duct 의 수평구간은 Main Header 재질과 동일하게 적용 * FM PVC Damper 중 1,100mm 이상은 FRP Damper 적용 (FM PVC Damper 제작 가능시 FM PVC 적용) * 입상 최하단 FAB - DS Elbow - ACID, ALKALI : FRP 적용 * 입상 최상단 DS - Scrubber Header Elbow - ACID : FRP 적용 - ALKALI : STS 적용 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
abd2417d-74ef-437d-8df1-ac5829d6f710 | 21036D-IC-M16G00-HV-A00-00150 M16_Ph-2 시방서-보온공사.pdf | SK ecoplant SPECIFICATION FOR HVAC & PLUMBING SYSTEM 보온공사 - ¦ DOC No. ¦ : 21036D-IC-M16G00-HV-A00-00150 ¦ ¦ --- ¦ --- ¦ ¦ DISCIPLINE ¦ : HVAC ¦ ¦ PROJECT No. ¦ : 21036D ¦ ¦ PROJECT TITLE ¦ : M16 Ph2 Project ¦ ¦ CLIENT ¦ : SK hynix ¦ ¦ LOCATION ¦ : Icheon city, Gyeonggi-do, Korea ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 0 ¦ 2022.01.25 ¦ APPROVED FOR CONSTRUCTION ¦ T.G.YU ¦ J.H. YANG ¦ Y.T.OH ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ REV. ¦ DATE ¦ DESCRIPTION ¦ PRPD ¦ CHKD ¦ APPD ¦ 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. | {}
b3eb2ed5-e5fb-4647-b54d-37eee1e2f505 | 21036D-IC-M16G00-HV-A00-00150 M16_Ph-2 시방서-보온공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00150 Rev. 0 Page 1 of 11 ¦ ¦ --- ¦ --- ¦ --- ¦ 1. 일반사항 1.1 적용범위 1.1.1 요약 (1) 이 절은 기기, 덕트 및 배관류의 결로방지, 동파방지, 보온 및 보냉공사에 적용한다. (2) 설계도서, 관계법규 또는 별도로 정한 규정에 의한 것을 제외하고는 모두 본 시방에 준한다. (3) 이 시방서에 기재되지 않은 사항은 국토교통부 제정 "기계설비공사 표준 시방서" 및, '1.3 항 참조표준'을 적용할 수 있다. 단 본 시방서와 상이한 내용은 본 시방서를 우선하여 적용한다. (4) 이 시방서에 특별한 명기가 없는 사항 중 건축, 전기에 관한 사항은 해당 시방서에 따른다. (5) 시방서, 설계도면 및 내역서 중 어느 한 도서에라도 표기되어 있는 사항은 시공하여야 한다. (6) 산업안전보건법에서 규정한 법규에 의해서 시공하여야 한다. 1.1.2 적용 및 우선 (1) 모든 공사는 설계도면 및 시방서에 준하여 시공하며, 설계도면과 시방이 상이한 경우에는 설 계도면을 우선하되 발주 담당자와 협의 하여 정한다. (2) 본 시방서, 설계도면 또는 표준 시방이 정한 공법, 자재 및 제품 등의 내용이 현실적으로 이 행하기 불가능할 경우에는 반드시 발주 담당자에게 서면으로 보고하고 대안에 대한 승인을 득한 후 시공한다. 1.2 관련 시방 1.2.1 일반공통사항 1.2.2 공조배관공사 1.2.3 PCW 배관공사 1.2.4 GALV 덕트공사 1.2.5 급수.급탕배관공사 1.3 참조 표준 1.3.1 한국산업표준 ¦ KS D 0201 ¦ 용융 아연 도금 시험방법 ¦ ¦ --- ¦ --- ¦ ¦ KS D 0229 ¦ 용융 알루미늄 도금 시험방법 ¦ ¦ KS D 3506 ¦ 용융 아연 도금 강판 및 강대 ¦ ¦ KS D 3520 ¦ 도장 용융 아연 도금 강판 및 강대 ¦ ¦ KS D 3552 ¦ 철선 ¦ ¦ KS D 3698 ¦ 냉간 압연 스테인리스 강판 및 강대 ¦ ¦ KS D 6701 ¦ 알루미늄 및 알루미늄 합금의 판 및 띠 ¦ hynix SK SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
18ac53d9-2e9a-4250-ad45-0a1c2efa6071 | 21036D-IC-M16G00-HV-A00-00150 M16_Ph-2 시방서-보온공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00150 Rev. 0 Page 2 of 11 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ KS D 6705 ¦ 알루미늄 및 알루미늄 합금 박 ¦ ¦ --- ¦ --- ¦ ¦ KS D 8302 ¦ 니켈 및 니켈크로뮴 도금 ¦ ¦ KS D 8304 ¦ 전기 아연도금 ¦ ¦ KS D 8308 ¦ 용융 아연도금 ¦ ¦ KS D 8309 ¦ 용융 알루미늄도금 ¦ ¦ KS F 2803 ¦ 보온,보랭 공사의 시공 표준 ¦ ¦ KS F 4552 ¦ 메탈라스 ¦ ¦ KS F 4714 ¦ 발수성 펄라이트 보온재 ¦ ¦ KS F 4901 ¦ 아스팔트 펠트 ¦ ¦ KS F 4902 ¦ 아스팔트 루핑 ¦ ¦ KS L 2508 ¦ 유리직물 ¦ ¦ KS L 9102 ¦ 인조 광물 섬유 단열재 ¦ ¦ KS M 3808 ¦ 발포 폴리스티렌(PS) 단열재 ¦ ¦ KS M 3809 ¦ 경질 폴리우레탄폼 단열재 ¦ ¦ KS M 3862 ¦ 발포 폴리에틸렌 보온재 ¦ ¦ KS M 6962 ¦ 고무발포 단열재 ¦ ¦ KS T 1035 ¦ 아스팔트 크라프트 방습지 ¦ ¦ KS T 1057 ¦ 포장용 폴리염화비닐 점착 테이프 ¦ ¦ KS T 1060 ¦ 방식용 폴리염화비닐 점착 테이프 ¦ ¦ KS T 1093 ¦ 포장용 폴리에틸렌 필름 ¦ ¦ KS L 9016 ¦ 보온재의 열 전도율 측정방법 ¦ 1.4 제출물 1.4.1 자재 공급 전 제출물 시공자는 다음의 사항을 자재공급 전에 발주 담당자에게 제출하여 승인을 받아야 한다. (1) 주요 기자재공급원 승인요청서 ① KS 규격 인증서 또는 ISO 품질인증서 ② 공급자의 사업자 등록증명원 (단, 외산자재인 경우 납품 회사 분) ③ 국세 및 지방세 완납증명서 (유효기관 확인) ④ 납품실적증명서 (유효기관 확인) ⑤ 품질검사 전문기관 및 국·공립검사기관의 시험성과 표 ⑥ 품질보증각서 : KS 비인증제품, 공인기관 시험 불가제품, 해외제품(시험성적서 제출)등 (2) 필요 시 재료에 대한 견본품을 제출하여야 한다. SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
91ef61bc-4273-43b4-9589-3f824ed53d08 | 21036D-IC-M16G00-HV-A00-00150 M16_Ph-2 시방서-보온공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00150 Rev. 0 Page 3 of 11 ¦ ¦ --- ¦ --- ¦ --- ¦ 1.4.2 자재 입고 검사 요청서 자재 반입 시 자재 입고 검사 요청서를 발주 담당자에게 제출하여 확인을 받는다. 1.4.3 검측 요청서 시공 담당자가 검측 요청서를 작성하여 건설사업관리기술인 에게 확인을 받은 후 발주 담당자에게 제출 한다. 1.5 운반, 저장 및 취급 1.5.1 모든 재료는 옥내에 보관한다. 1.5.2 운반, 저장 및 취급기간 보온재 제품이 손상되지 않도록 보호해야 한다. 1.6.4 모서리와 끝부분의 손상을 방지하고 표면에 이물질이 묻거나 내부에 습기가 차지 않도록 하여야 한다. 2. 재료 본 시방서에 명기되어있지 않을 경우에는 KS 제품 또는 그 동등품 이상이어야 한다. 2.1 보온재료 2.1.1 보온재 ¦ 종류 ¦ 재 료 명 ¦ 규 격 ¦ 비 고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 보 온 재 ¦ 유리면 보온재 ¦ KS L 9102 인조광물 섬유 단열재에 규정하는 보온판, 펠트, 보온통, 보온대 및 블랭킷으로서, 보온판 및 보온대는 48k 이상로 한다. ¦ ¦ ¦ 보 온 재 ¦ 고무발포 보온재 ¦ KS M 6962 고무발포 단열재 ¦ ¦ 2.1.2 옥외 노출 덕트의 CASING 재질 ¦ 재 질 ¦ 두 께 ¦ 도막두께 (�m) ¦ 도막두께 (�m) ¦ 비 고 (원자재 규격) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 재 질 ¦ 두 께 ¦ 내측 ¦ 외측 ¦ 비 고 (원자재 규격) ¦ ¦ POLYESTER 수지 칼라강판(PGS) ¦ 0.45t 이상 ¦ SERVICE : 4~10 ¦ PRIMER : 5~8 FINISH : 15~20 ¦ 아연도금강판 (KS D 3520) ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
2d71ac40-6c3c-44c3-8fca-40e857eb3eef | 21036D-IC-M16G00-HV-A00-00150 M16_Ph-2 시방서-보온공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00150 Rev. 0 Page 4 of 11 ¦ ¦ --- ¦ --- ¦ --- ¦ * 동등 이상의 칼라강판으로 외측(PRIMER+FINISH 도장) 부분이 노출되도록 사용 할 것. 2.1.3 외장재 및 보조재 ¦ 종 류 ¦ 종 류 ¦ 재 료 명 ¦ 규 격 및 적 요 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 외 장 재 ¦ 금속판 ¦ 칼라아연철판 ¦ KS D 3520(도장 용융 아연도금 강판 및 강대)에 의한 것으로서 판 두께는 0.45mm 로 한다. ¦ ¦ 외 장 재 ¦ 금속판 ¦ 알루미늄판 ¦ KS D 6701(알루미늄 및 알루미늄 합금의 판 및 조)에 의한 것으로서 판 두께는 0.6mm 로 한다. ¦ ¦ 외 장 재 ¦ 금속판 ¦ 스테인리스강판 ¦ KS D 3698(냉간 압연 스테인리스 강판 및 강대)에 의한 것으로서 판 두께는 0.2mm 로 한다. ¦ ¦ 외 장 재 ¦ 외장용 테이프 ¦ 매직테이프 ¦ 두께 0.15mm 이상의 난연 2 급 이상 제품으로 한다. ¦ ¦ 외 장 재 ¦ 알루미늄 가공시트 ¦ 알루미늄 박판 ¦ KS D 6705(알루미늄 및 알루미늄 합금 박)에 따른 두께 0.007mm 알루미늄 박에 그라프트지를 맞붙인 것으로 한다. ¦ ¦ 보 조 재 ¦ 방습 방수재 ¦ 아스팔트 루핑 ¦ KS F 4902(아스팔트루핑)에 규정하는 아스팔트루핑으로서 단위무게 1,500g/m2 의 것으로 한다. ¦ ¦ 보 조 재 ¦ 방습 방수재 ¦ 아스팔트 펠트 ¦ KSF 4901(아스팔 펠트)에 규정하는 아스팔트펠트로서 단위무게 650g/m2 의 것으로 한다. ¦ ¦ 보 조 재 ¦ 방습 방수재 ¦ 폴리에틸렌필름 ¦ KS T 1093(포장용 폴리에틸렌 필름)에 따른 두께 0.05mm 의 것으로 하고, 관 등에 사용하는 경우는 적당한 폭으로 재단하고 테이프모양을 한 것으로 한다. ¦ ¦ 보 조 재 ¦ 정형재 ¦ 정형용 원지 ¦ 판지 잡종 370g/m2 이상의 것으로 한다. ¦ ¦ 보 조 재 ¦ 정형재 ¦ 난연원지 ¦ 무가소성 염화비닐수지를 사용한 비닐원지로 500g/m2 이상으로 한다 ¦ ¦ 보 조 재 ¦ 부착재 ¦ 알루미늄박팍 (은박)점착테이프 ¦ 알루미늄박판의 면에 점착테이프를 도포하고, 박리지가 부착되어져 있고 점착강도를 완전하에 유지된 것으로 한다. ¦ ¦ 보 조 재 ¦ 부착재 ¦ 비닐점착테이프 ¦ KS T 1057(포장용 폴리 염화비닐 점착 테이프)에 의한 0.2mm 의 것으로 한다. ¦ ¦ 보 조 재 ¦ 보강재 ¦ 보온 핀 ¦ 스폿 용접용의 동 도금 또는 동제 보온 핀 및 절연관자금 (Excu-tcheon Plate)이 부착된 동 보온 핀으로 한다. 다만, 공조덕트 및 제연덕트에 사용하는 경우에는 강판제 관자금에 못이 부착된 접착용 보온 핀으로 하여도 된다. ¦ ¦ 보 조 재 ¦ 보강재 ¦ 메탈라스 ¦ KS F 4552(메탈라스)에 의한 호칭망눈 21~28 의 것으로, 사용철선은 지름이 0.4mm 이상의 아연도금이 되어진 것으로 한다. ¦ ¦ 보 조 재 ¦ 보강재 ¦ 코너비드 ¦ KS D 3506(용융 아연도금 강판 및 강대)에 의한 0.4mm 이상의 아연철판을 가공한 것으로 한다. 경량형강의 ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
97908aeb-6b59-4066-8fba-fad4ee572e7e | 21036D-IC-M16G00-HV-A00-00150 M16_Ph-2 시방서-보온공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00150 Rev. 0 Page 5 of 11 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ ¦ 경우에는 방식처리가 되어진 것으로 한다. ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 아연 철선 ¦ KS D 3552(철선)에 의한 아연도금 철선으로서 굵기는 0.6mm 이상으로 한다. ¦ ¦ ¦ 기 타 ¦ 알루미늄 BAND ¦ 배관경 900A 이하 : 0.5t X 19mm 배관경 900A 이상 : 0.6t X 32mm ¦ ¦ 기 타 ¦ 평 BAND ¦ KS D 3698(냉간 압연 스테인리스 강판 및 강대)에 따라 제작한것으로서 어느 쪽이든 두께 0.15mm 이상으로 한다. ¦ ¦ 기 타 ¦ 밀봉재 ¦ 클로로프렌 고무계 밀봉재 또는 실리콘 밀봉재로 한다. ¦ 2.1.4 보온재료의 화재안전성능 무기질 보온재를 제외한 유기질 보온재는 화재안전을 위하여 다음 표에 준하는 난연성능을 확보 한 보온재를 용도에 부합되도록 선택하여 사용하여야 한다. ¦ 시험방법 ¦ 시험항목 ¦ 기 준 ¦ 기 준 ¦ 기 준 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 시험방법 ¦ 시험항목 ¦ 난연 1 급 ¦ 난연 2 급 (자기소화성) ¦ 가연성 ¦ ¦ KS M ISO 4589-2 ¦ 산소지수 (L.O.I) ¦ > 32 ¦ ≥ 28 ¦ < 28 ¦ ¦ KS M ISO 5659-2 ¦ 소화점 임계 열류량 CFE (kW/m2) ¦ ≥ 20 ¦ > 10 ¦ < 10 ¦ * 산소지수(Limited Oxygen Index) : 연소가 지속되기 위하여 필요한 최소한의 산소농도 * 소화점 임계 열류량(Critical Flux at Extinguishment) : 연소 시 화염이 더 이상 진행되지 아니하는 지점에서의 단위면적이 시간당 받는 열량 3. 시공 3.1 보온공사 시공 3.1.1 공통사항 (1) 건축물의 방화구획, 방화벽, 기타 법규로 지정된 칸막이 또는 벽 등을 관통하는 배관, 덕트 등의 틈새부분에 대해서는 내화구조의 인정 및 관리기준(국토교통부고시 제 2018-772 호)에 따른 내화충전구조로 인증된 방법 및 재료로 충진한다. (2) 건축법, 소방법 등의 법규상 불연공법이 요구 되어지는 곳은 불연재 또는 불연재에 준하는 내화성능이 있는 보온재, 외장재 및 보조재를 사용하여 피복 시공한다. (3) 보온재의 이음부분은 틈새가 없도록 시공하고 겹침부위의 이음선이 동일선상에 있지 않도록 한다. (4) 배관의 철선감기는 대(�) 모양재일 때는 50mm 피치 이하의 나선감기로 조이고, 통 모양재일 때는 1 본에 대해 2 개소 이상 감아 조인다. 원형덕트의 철선감기는 150mm 피치 이하의 나선으 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
a5f4e7fd-7689-4dae-980c-3fc1f58e2752 | 21036D-IC-M16G00-HV-A00-00150 M16_Ph-2 시방서-보온공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00150 Rev. 0 Page 6 of 11 ¦ ¦ --- ¦ --- ¦ --- ¦ 로 감아 조인다. (5) 아스팔트펠트와 정형용 원지의 겹쳐 감는 폭은 30mm 이상으로 한다. (6) 외장용 테이프류의 겹쳐 감는 폭은 15mm 이상으로 하고, 입상관일 때는 아래에서 위쪽으로 감아 올라간다. 단, 폴리에틸렌 필름의 경우는 1/2 겹침 감기를 한다. (7) 금속판 등을 감아 마무리 하는 경우 관, 원형덕트의 직관부, 장방형덕트 및 각형 탱크류는 시 임(Seam) 이음으로 하고, 관 및 원형덕트의 굽힘부는 형태에 맞게 제작 도는 공장가공에 의 한 성형품으로 한다. 이음매는 삽입이음으로 하되 탱크류는 필요에 따라 겹침부위에 피스로 고정할 수 있다. 옥외 및 옥내 다습한 곳의 이음매는 밀봉재로 마감한다. (8) 보온핀의 부착 수는 장방형 덕트의 경우는 300mm 간격에 밑면 및 측면은 2 개, 윗면은 1 개로 한다. 흡음재 내장의 경우는 1m2 당 20 개 정도로 하고 모양에 따라 필요한 곳에 보온핀을 부 착하여야 한다. (9) 원칙적으로 덕트의 강판틀은 덕트의 네 모퉁이 및 종·횡 방향에 450mm X 900mm 이하의 격자 모양으로 설치한다. 또, 공기조화기나 탱크류에서는 900mm X 900mm 이하의 격자모양으로 할 수 있다. (10)옥내 노출배관의 바닥 관통부는 보온재의 보호를 위하여 바닥에서 150mm 높이까지 아연철판 또는 스테인리스 밴드 등으로 피복한다. (11)냉수 및 냉온수 배관의 지지부는 보온두께와 같은 합성수지제 등의 지지대로 설치하고, 그 위에 행거밴드 또는 U-볼트로 고정하여 보온재를 넣은 다음 외장재로 마감한다. 부득이 배관 을 보온재 내부에서 지지하는 경우는 보온표면보다 150mm 의 높이까지 결로방지를 위해 두께 19mm 로 지지부를 피복한다. (12)배관을 SHOE 에 설치하는 경우에는 SHOE 까지 보온재를 시공하여 결로나 동파가 발생하지 않도록 시공한다. (13)옥내노출관의 보온 변형부분과 분기굴곡부 등에는 밴드로 고정한다. 밴드 폭은 보온외경 150mm 미만은 20mm 로, 150mm 이상은 25mm 로 한다. (14)보온을 필요로 하는 기기의 문 및 점검구 등은 개폐에 지장이 없고 보온 효과 가 감소하지 않도록 시공한다. (15)보온을 필요로 하는 덕트 등의 지지대, 벽체부착 BRACKET 의 지지부 및 지지하는 곳에 대하 여도 보온한다. (16)밸브 및 플랜지의 보온시공은 배관 시공에 준하고, 노출 주철밸브류의 외장재는 공사시방서에 따른다. (17)배관보온용으로 보온통의 사용이 곤란한 곳은 동질의 보온대 및 보온판 등을 사용한다. (18)외기조건 등이 특수하여 보온통의 두께가 기성제품의 시방에 맞지 않을 때에는 보온통 위에 동질의 보온판 및 보온대를 감던가 또는 보온통을 이중으로 겹쳐 시공한다. (19) 냉수 배관에는 결로 방지를 위해 속비닐을 감는다. (20) 냉수 입상배관에 방진을 설치하는 경우에는 결로가 발생하지 않도록 방진 주위를 보온한다. SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
6d86a78b-b8e8-4a53-b606-b2b490b7c56a | 21036D-IC-M16G00-HV-A00-00150 M16_Ph-2 시방서-보온공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00150 Rev. 0 Page 7 of 11 ¦ ¦ --- ¦ --- ¦ --- ¦ 3.1.2 시공요령 (1) 배관에 대하여는 보온통 사용을 원칙으로 하며 아연도금철선 및 STEEL BAND 를 사용하여 보 온통 1 조에 대하여 2 개소씩 확실하게 조여 배관과 밀착 설치한다. (2) 보온통으로 나오지 않는 대구경 배관은 성형 BOARD 를 사용한다. (3) 곡관부의 보온 및 보냉은 성형 보온통을 사용하거나, 곡관부에 맞춰 절단하여 성형하며 보온 및 보냉재의 틈새는 동질의 보온재로 충진 시킬 것. (4) 외장판의 조여 붙임은 원칙적으로 STEEL BAND 로 할 것. (5) 열팽창 및 수축에 의하여 틈이 생기는 것을 방지할 수 있는 방법을 고려 할 것. (6) STEAM TRACIN 관의 보온은 주관과 TRACE 관을 합친 SIZE 에 맞는 보온통으로 사용 할 것. (7) 플랜지 및 밸브 본체 COVER 등 수리를 위하여 해체가 필요한 곳은 해체 가능한 구조로 하고 , GLASS WOOL 등으로 충진 할 것. 해체 가능한 분할식 COVER 는 정첩 및 나사 조임 형태로 한다. (8) 빗물이 새지 않도록 고려하여 외장판금의 종방향의 이음을 서로 물림으로 하고, 원주방향 이 음의 겹침은 50mm 이상으로 한다. (9) 외장판은 미끌어지지 않도록 STEEL BAND 로 조여 붙임과 동시에 STEEL BAND 에 'Z' CLIP 을 설 치 할 것. (10) 냉수 배관 보온 시 밸브 개도율이 확인 가능하도록 할 것. (11)기타 필요한 경우에는 발주 담당자의 지시에 따른다. 3.1.3 배관 유체별 보온 기준 ¦ 구 분 ¦ 보온 . 보냉 재질 및 두께 ¦ 보온 . 보냉 재질 및 두께 ¦ 외장판 재질 ¦ 외장판 재질 ¦ 열선 ¦ 비 고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 구 분 ¦ 옥내 ¦ 옥외 ¦ 옥내 ¦ 옥외 ¦ 열선 ¦ 비 고 ¦ ¦ 냉수(CHS/R) ¦ 25A 이하 : 고무발포보온재 19t 32A~150A : 고무발포보온재 25t 200A 이상 : 고무발포보온재 40t ¦ 고무발포보온재 50t ¦ 매직테이프 ¦ 칼라아연철판 ¦ X ¦ W/속비닐 ¦ ¦ 냉각수(CWS/R) (균압관/샌드필터) ¦ N/A ¦ 고무발포보온재 25t ¦ N/A ¦ 칼라아연철판 ¦ ○ ¦ ¦ ¦ 증기(SS) ¦ 80A 이하 : GLASS WOOL 40t 100A 이상 : GLASS WOOL 50t ¦ GLASS WOOL 100t ¦ 매직테이프 * FAB : PPA 탄성커버 ¦ 칼라아연철판 ¦ X ¦ ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
52f893a3-f7f3-4454-90cc-7529e5d956cf | 21036D-IC-M16G00-HV-A00-00150 M16_Ph-2 시방서-보온공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00150 Rev. 0 Page 8 of 11 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ .증기응축수(SR) ¦ 80A 이하 : GLASS WOOL 40t 100A 이상 : GLASS WOOL 50t ¦ GLASS WOOL 100t ¦ 매직테이프 * FAB : PPA 탄성커버 ¦ 칼라아연철판 ¦ X ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ DCC 냉수관 (DCWS/R) ¦ 25A 이하 : 고무발포보온재 19t 32A~150A : 고무발포보온재 25t 200A 이상 : 고무발포보온재 40t * FAB : 비보온 ¦ N/A ¦ 매직테이프 ¦ N/A ¦ X ¦ W/속비닐 * FAB : 비보온 ¦ ¦ 온수(RHWS/R) ¦ 40A 이하 : 고무발포보온재 25t 50A~125A : 고무발포보온재 32t 150A 이상 : 고무발포보온재 40t ¦ 고무발포보온재 50t ¦ 매직테이프 ¦ 칼라아연철판 ¦ X ¦ ¦ ¦ 공정냉각수(PCWS/R) ¦ 고무발포보온재 19t ¦ 고무발포보온재 25t ¦ 매직테이프 ¦ 칼라아연철판 ¦ X ¦ W/속비닐 ¦ ¦ 급수(IW, CTW, NPW) ¦ 80A 이하 : 고무발포보온재 19t 100A 이상 : 고무발포보온재 25t ¦ 고무발포보온재 25t ¦ 매직테이프 * FAB : PPA 탄성커버 ¦ 칼라아연철판 ¦ ¦ 냉각탑 보급수 열선시공 ¦ ¦ 급탕·환탕(DHWS/R) ¦ 40A 이하 : 고무발포보온재 25t 50A~125A : 고무발포보온재 32t 150A 이상 : 고무발포보온재 40t ¦ 고무발포보온재 50t ¦ 매직테이프 ¦ 칼라아연철판 ¦ X ¦ ¦ ¦ WSS/R ¦ 고무발포보온재 19T ¦ X ¦ 회색 매직테이프 ¦ X ¦ X ¦ W/속비닐 ¦ ¦ RD ¦ 회색 고무발포보온재 13T ¦ ¦ ¦ ¦ ¦ ¦ ¦ CD ¦ 고무발포보온재 19T ¦ X ¦ 회색 매직테이프 ¦ X ¦ X ¦ W/속비닐 ¦ ¦ CD (OAC 및 AHU R/M 내부) ¦ 회색 고무발포보온재 19T ¦ X ¦ ¦ X ¦ X ¦ ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
1c804232-26d2-4e2f-ad0d-0396242e30c0 | 21036D-IC-M16G00-HV-A00-00150 M16_Ph-2 시방서-보온공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00150 Rev. 0 Page 9 of 11 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ CD (DCC) ¦ 고무발포보온재 19T * FAB : 비보온 ¦ X ¦ 회색 매직테이프 ¦ ¦ ¦ W/속비닐 * FAB 비보온 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ STV ¦ 80A 이하 : GLASS WOOL 40T 100A 이상 : GLASS WOOL 50T ¦ X ¦ 매직테이프 ¦ ¦ ¦ ¦ * 온도와 습도가 높은 실의 보온두께는 실의 조건, 배관 내 유체 온도 및 보온재의 열전도율 등을 고려하여 결로가 발생하지 않는 두께 이상으로 계산하여 선정토록 한다. 3.2 덕트의 보온 시공 3.2.1 장방형 덕트의 보온 시공 장방형 덕트의 보온 시공 순서는 다음 표에 따른다. ¦ 사 용 구 분 ¦ 재 료 및 시 공 순 서 ¦ 비 고 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 옥 내 덕 트 (유 리 솜) ¦ 1) 보온핀 2) 보온재 3) 은박 테이프 4) 외장재 5) 밴드 ¦ 소방 입상 덕트 ¦ ¦ 옥 내 덕 트 (고 무 발 포) ¦ 1) 보온재 2) 접착 테이프 ¦ ¦ ¦ 옥 외 덕 트 (고 무 발 포) ¦ 1) 보온재 2) 접착 테이프 3) 케이싱 마감 ¦ ¦ 3.2.2 덕트의 보온(고무발포보온재) 시공 (1) 접착제 → 보온재 → 접착테이프 순으로 시공한다. (2) 플랜지 부분(보강 포함)은 플랜지 부분 보온재의 중복 너비를 200mm 이상으로 내부에 알맞게 들어가 있도록 시공한다. SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
508e9d7f-e9d4-4cfe-a3a7-214374fc19f3 | 21036D-IC-M16G00-HV-A00-00150 M16_Ph-2 시방서-보온공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00150 Rev. 0 Page 10 of 11 ¦ ¦ --- ¦ --- ¦ --- ¦ 3.2.3 덕트 보온 기준 ¦ 구 분 ¦ 구 분 ¦ 보온 재질 및 두께 ¦ 외장판 재질 ¦ 비고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ HVAC ¦ S.A / R.A ¦ 고무발포보온재 13t (FLANGE : 9t) ¦ N/A ¦ ¦ ¦ HVAC ¦ F.A ¦ 고무발포보온재 13t (FLANGE : 9t) ¦ N/A ¦ C/R 내부 : 비보온 SUB FAB 내부 : 보온 ¦ ¦ HVAC ¦ O.A ¦ 고무발포보온재 13t (FLANGE : 9t) ¦ N/A ¦ ¦ ¦ HVAC ¦ E.A ¦ N/A ¦ N/A ¦ ¦ ¦ (인 한 마트에 姜玉 ¦조능) EXHAUST PROCESS ¦ ACID ¦ STS 적용시 고무발포보온재 40t (FLANGE : 9t) ¦ 칼라아연철판 ¦ 옥외 덕트재질 : FRP, STS ¦ ¦ (인 한 마트에 姜玉 ¦조능) EXHAUST PROCESS ¦ ALKALI ¦ STS 적용시 고무발포보온재 40t (FLANGE : 9t) ¦ 칼라아연철판 ¦ 옥외 덕트재질 : FRP, STS ¦ ¦ (인 한 마트에 姜玉 ¦조능) EXHAUST PROCESS ¦ ORGANIC ¦ 고무발포보온재 40t (FLANGE : 9t) ¦ 칼라아연철판 ¦ 옥외 덕트재질 : GALV. ¦ ¦ (인 한 마트에 姜玉 ¦조능) EXHAUST PROCESS ¦ HEAT/GEN. ¦ 고무발포보온재 40t (FLANGE : 9t) ¦ 칼라아연철판 ¦ 옥외 덕트재질 : GALV. ¦ ¦ (인 한 마트에 姜玉 ¦조능) EXHAUST PROCESS ¦ DRY ¦ N/A ¦ N/A ¦ 옥외 덕트재질 : FRP ¦ ¦ (인 한 마트에 姜玉 ¦조능) EXHAUST PROCESS ¦ CABINET ¦ 고무발포보온재 40t (FLANGE : 9t) ¦ 칼라아연철판 ¦ 옥외 덕트재질 : GLAV. ¦ ¦ (인 한 마트에 姜玉 ¦조능) EXHAUST PROCESS ¦ 국소배기 ¦ N/A ¦ N/A ¦ 옥외 덕트재질 : FM PVC ¦ ¦ (인 한 마트에 姜玉 ¦조능) EXHAUST PROCESS ¦ MIDDLE (ACID) ¦ STS 적용시 고무발포보온재 40t (FLANGE : 9t) ¦ 칼라아연철판 ¦ 옥외 덕트재질 : FRP, STS ¦ ¦ (인 한 마트에 姜玉 ¦조능) EXHAUST PROCESS ¦ EMERGENCY ¦ 고무발포보온재 40t (FLANGE : 9t) ¦ 칼라아연철판 ¦ 옥외 덕트재질 : GALV. ¦ ¦ DUCT DRAIN ¦ DRAIN 배관 ¦ 고무발포보온재 25t ¦ 칼라아연철판 ¦ 옥외 ¦ * STS 와 STS Coating Duct 보온은 동일 하게 적용 3.2.4 FLEXIBLE 덕트 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
12fa3c1a-353e-45b3-8e3e-c08fbd6ba4ea | 21036D-IC-M16G00-HV-A00-00150 M16_Ph-2 시방서-보온공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00150 Rev. 0 Page 11 of 11 ¦ ¦ --- ¦ --- ¦ --- ¦ (1) 공조덕트(SA, RA) : 흡음보온 FLEXIBLE HOSE DUCT (2) 일반배기(화장실 배기등) : 일반 FLEXIBLE HOSE DUCT 3.3 시험 및 검사 3.3.1 공사를 착수하기 전에 그 공사에 사용된 보온재가 한국산업표준인증 제품인지를 확인한다. 3.3.2 시공면에 STINGER(�)를 찔러 그 두께를 검사한다. 단, 시공 전에 보온재 두께에 대해서 확 인을 득한 경우는 시공 후 두께 검사를 생략할 수 있다. 3.3.3 매직테이프의 겹침부위 및 색상, 방습재, 등을 검사한다. 3.3.4. 보온재의 연결부위 기밀상태를 검사한다. - End of Document - SK hynix SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
657dd3fc-534b-4e2a-8cf1-8166e195fa6d | KSCIEC60079-2_2024확인_KR | KSKSKSKS KS C IEC 60079-2 KSKSKSK KSKSKS KSKSK KSKS KSK K KS 폭발성 분위기 - 제 2 부: 압력방폭용기 "p"에 의한 기기 보호 KS C IEC 60079-2:2014 산 업 표 준 심 의 회 2019 년 1 월 25 일 개정 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
2bc6614e-a8b2-42a0-9ba9-b2f0f9665862 | KSCIEC60079-2_2024확인_KR | KS CIEC 60079-2:2014 심 의 : 전기응용 기술심의 회 성 명 근 무 처 직 위 (회 장) 신 판 석 홍익대학교 교 수 (위 원) 권 오 화 케이아이씨테크 대 표 김 갑 일 명지대학교 교 수 김 재 희 우리엔지니어링 대 표 박 효 성 한국화학융합시험연구원 연 구 위 원 박 현 주 한국전력공사 전력연구원 책임연구원 서 호 선 KR 지식재산법률사무소 대 표 이 주 철 (주)건일이엔지 연 구 소 장 임 영 민 한국전자기술연구원 수석연구원 장 우 진 서울과 학기술대학교 교 수 조 두 희 한국전자통신연구원 책임연구원 남 택 주 디티앤씨 고 문 (간 사) 채 예 린 국가기술표준원 표준정책국 전기전자정보표준과 연 구 사 원안작성협력 : 방폭전기설비 전문위원회 성 명 근 무 처 직 위 (대표전문위원) 김 두 현 충북대학교 교 수 (위 원) 김 기 회 한국가스안전공사 처 장 김 지 훈 방폭기술정보 소 장 박 동 선 한국산업안전보건공단 차 장 최 상 원 (사)과학기술연우연합회 이 사 최 용 원 한국산업기술시험원 센 터 장 강 정 일 한국산업안전보건공단 차 장 (간 사) 이 기 호 한국산업안전보건공단 차 장 표준열람 : e 나라표준인증(http://www.slandard.go.kr) 제 정 자 : 산업표준심의 회 위원장 담당부처 : 산업통상자원부 국가기술표준원 제 정 : 2001 년 10 월 8 일 개 정 : 2019 년 1 월 25 일 심 의 : 산업표준심의 회 전기응용 기술심의 회 원안작성협력 : 방폭전기설비 전문위원회 이 표준에 대한 의견 또는 질문은 e 나라표준인증 웹사이트를 이용하여 주십시오. 이 표준은 산업표준화법 제 10 조의 규정에 따라 매 5 년마다 산업표준심의 회에서 심의 되어 확인, 개정 또는 폐지됩니다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
02364746-5e82-42dc-a0a4-45a98fff7fd8 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 목 차 머 리 말 V 개 요 ・・・・ vi 1 적용범위(Scope) 1 2 인용표준(Normative references) 1 3 용어와 정의(Terms and definitions) 2 4 보호등급(Protection levels) 5 5 가압용기의 구조 요구사항(Constructional requirements for pressurized enclosures) 7 5.1 용기(Enclosure), 7 5.2 재료(Materials) 7 5.3 문 및 덮개(Doors and covers) 7 5.4 기계적 강도(Mechanical strength) 8 5.5 그룹 I 및 그룹 II 의 개방구, 칸막이, 구획 및 내부 부품(Group I and Group II Apertures, partitions, compartments and internal components) 9 5.6 정적가압을 위한 개방구(Apertures for Static Pressurization) 9 5.7 그룹 I 기기의 절연 재료(Insulating materials for Group I equipment) 9 5.8 밀봉(Sealing) 10 5.9 불꽃 및 입자 배리어(Spark and particle barriers) 10 5.10 전지 및 배터리(Cells and batteries) 10 6 온도 제한(Temperature limits) 10 6.1 일반사항(General) 10 6.2 보호등급 "pxb" 또는 보호등급 "pyb"(For Level of Protection "pxb" or Level of Protection "pyb") .. 10 6.3 보호등급 "pzc"(For Level of Protection "pzc") 11 7 안전 대책 및 안전장치(정적가압 제외)(Safety provisions and safety devices(except for static pressurization)) 11 7.1 폭발위험장소에 대한 안전장치의 적합성(Suitability of safety devices for hazardous area) 11 7.2 안전장치의 무결성(Integrity of safety devices) 11 7.3 안전장치의 제공자(Provider of safety devices) 12 7.4 관련기기로 평가되는 가압시스템 (Pressurization System evaluated as associated equipment) 12 7.5 보호등급 "pxb"에 대한 순서도(Sequence diagram for Level of Protection "pxb") 13 7.6 안전장치의 정격(Ratings for safety devices) 13 7.7 그룹 I 및 그룹 II- 보호등급 "pxb"의 자동 퍼지(Group I and Group II Purging automated for Level of Protection "pxb") 13 7.8 그룹 I 및 그룹 II - 퍼지 기준(Group I or Group II - Purging criteria) 14 7.9 그룹 III - 청소(Group III- Cleaning) 14 7.10 최소 유량이 요구되는 경우의 요구사항(Requirements when a minimum flow rate required) 14 7.11 최소양압 감지를 위한 안전장치(Safety devices to detect minimum overpressure) 14 7.12 최소 양압 값(Value of minimum overpressure) 15 7.13 복수 용기의 가압(Pressurizing multiple enclosures) 16 7.14 문 및 덮개의 안전장치(Safety devices on doors and covers) 16 7.15 통전 상태를 유지할 수 있는 기기(Equipment that may remain energized) 16 -i- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
a00640bd-0eac-4032-bc75-0ad54d75a690 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 7.16 보호등급 "pyb"에서 허용되는 기기(Equipment permitted within Level of Protection "pyb") ...... 16 8 정적가압을 위한 안전 대책 및 안전장치(Safety provisions and safety devices for staticpressurization) 16 8.1 폭발위험장소에 대한 안전장치의 적합성(Suitability of safety devices for hazardous area) ··· 17 8.2 보호가스(Protective gas) 17 8.3 내부 누출원(Internal sources of release) 17 8.4 그룹 I 및 그룹 II 충전 절차(Group I and Group II Filling procedure) 17 8.5 그룹 III 충전 절차(Group III Filling Procedure) 17 8.6 안전장치(Safety devices) 17 8.7 통전 상태 를 유지할 수 있는 기기(Equipment that may remain energized) 17 8.8 양압(Overpressure) 17 9 보호가스의 공급(Supply of protective gas) ..... 18 9.1 보조 공급장치(Backup supply) 18 9.2 독립적인 공급(Independent supplies) 18 9.3 가스의 종류(Type of gas) 18 9.4 온도(Temperature) ・・・・・・・・ 18 10 내부 누출원이 있는 가압용기(Pressurized equipment with an internal source of release) 18 11 누출 조건(Release conditions) 18 11.1 누출 없음(No release) 18 11.2 가스 또는 증기의 제한적 누출(Limited release of a gas or vapour) 19 11.3 액체의 제한적 누출(Limited release of a liquid) 19 12 컨테인먼트 시스템의 설계 요구사항(Designrequirements forthecontainmentsystem) 19 12.1 일반 설계 요구사항(General design requirements) 19 12.2 무고장 컨테인먼트 시스템(Infallible containment system) 19 12.3 제한적 누출이 있는 컨테인먼트 시스템(Containment system with a limited release) 20 13 내부 누출원이 있는 경우 보호가스 및 가압 방법(Protective gas and pressurizing techniques when there is an internal source of release) 20 13.1 일반사항(General) 20 13.2 누설보상식 가압(Pressurization with leakage compensation) 21 13.3 희석식 가압(Pressurization with dilution) 21 14 점화가능기기(Ignition-capable equipment) ··············· ····· 22 15 내부 고온표면(Internal hot surfaces) ····· 22 16 형식 검증 및 시험(Type verification and tests) 23 16.1 최대 양압 정격의 결정(Determining the maximum overpressure rating) 23 16.2 최대 양압시험(Maximum overpressure test) 23 16.3 누설시험(Leakage test) 23 16.4 내부 누출원이 없는 가압용기의 퍼지 시험 및 정적가압의 충전 절차 시험(Purging test for pressurized enclosures with no internal source of release and filling procedure test for static pressurization) 24 16.5 내부 누출원이 있는 가압용기의 퍼지 및 희석 시험(Purging and dilution tests for a pressurized enclosure with an internal source of release) 25 16.6 최소 양압의 검증(Verification of minimum overpressure) 27 16.7 무고장 컨테인먼트 시스템에 대한 시험(Tests for an infallible containment system) 27 16.8 제한적 누출이 있는 컨테인먼트 시스템에 대한 양압시험 (Overpressure test for a -ii- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f569f13d-c3f6-407c-ba96-7be02c81fbb8 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 containment system with a limited release) .... .... 27 17 일상시험(Routine tests) 27 17.1 기능시험(Functional test) 27 17.2 누설시험(Leakage test) 28 17.3 무고장 컨테인먼트 시스템 시험(Tests for an infallible containment system) 28 17.4 제한적 누출이 있는 컨테인먼트 시스템에 대한 시험(Test for a containment system with a limited release) 28 18 표시(Marking) 28 18.1 일반사항(General) 28 18.2 가압의 표시(Identifying as pressurized) 28 18.3 추가 표시(Supplementary marking) 28 18.4 내부 누출원(Internal source of release) 28 18.5 정적가압(Static pressurization) 29 18.6 가압시스템 (Pressurization systems) 29 18.7 다른 조항에서 요구되는 경고(Warnings required in other clauses) 29 18.8 사용자에 의한 양압 제한(Overpressure limited by user) 30 18.9 불활성 가스(Inert gas) ······ 30 19 사용설명서(Instructions) .... 30 부속서 A (규정) 퍼지 및 희석 시험(Purging and dilution tests) ···· 31 A.1 일반사항(General) 31 A.2 공기를 보호가스로 사용할 때의 판정 기준(Criteria for compliance where the protective gas is air) 31 A.3 불활성 가스를 보호가스로 사용할 때의 판정 기준(Criteria for compliance where the protective gas is inert) 31 부속서 B (참고) 기능 순서도의 예(Examples of functional sequence diagram) 32 부속서 C (참고) 덕트 및 용기의 압력 변화의 예 (Examples of the changes in pressure in ducts and enclosures) 34 부속서 D (참고) 사용자에게 제공할 정보 (Information to be provided to the user) 39 D.1 일반사항(General) 39 D.2 보호가스 덕트(Ducting of protective gas) 39 D.3 보호가스 공급장치 전원(Power for protective gas supply) 40 D.4 정적가압(Static pressurization) 40 D.5 컨테인먼트 시스템이 있는 용기(Enclosures with a containment system) 40 D.6 용기 최대 양압(Enclosure maximum overpressure) 40 부속서 E (규정) 용기 내부 누출 유형의 분류 (Classification of the type of release within enclosures) 41 E.1 일반사항(General) 41 E.2 정상 누출 없음, 비정상 누출 없음(No normal release, no abnormal release) 41 E.3 정상 누출 없음, 제한적인 비정상 누출 있음(No normal release, limited abnormal release) 41 E.4 제한적 정상 누출(Limited normal release) 41 부속서 F (참고) 희석지역 개념의 사용 예 (Examples for the use of the dilution area concept) 42 부속서 G (규정) 보호등급 "pxb" 및 보호등급 "pyb"에 대한 내부 전지 및 배터리 (Internal Cells and Batteries for Level of Protection "pxb" and Level of Protection "pyb") 44 G.1 일반 요구사항(General Requirements) 44 G.2 에너지 제한 회로에 의한 전기적 보호(Electrical Protection by energy limiting circuits) .... 45 -iii- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
8c631e8b-2418-49ef-beef-a200aacabeeb | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 G.3 1 차 배터리에 대한 추가 요구사항(Additional requirements for Primary batteries) 46 G.4 2 차 배터리에 대한 추가 요구사항(Additional requirements for secondary batteries) 47 G.5 본질적으로 안전한 전지 및 배터리에 대한 특정 요구사항(Specific requirements for Inherently Safe(IhS) cells and batteries) 47 G.6 가압용기 내부에 위치한 기기로서 가압용기 내부에 위치하고 가압 손실 시 분리되지 않는 배터리에 연결된 기기(Equipment located inside a pressurized enclosure connected to a battery which is also located inside the pressurized enclosure and not disconnected in the event of loss of pressurization) 48 G.7 하나 이상의 전지 또는 배터리를 포함하는 가압용기에 대한 추가적인 표시 및 구조 요구사 항(Supplementary marking and constructional requirements for pressurized enclosures containing one or more cells or batteries) 50 G.8 형식 시험(Type tests) 50 부속서 H (규정) 보호등급 "pzc"의 내부 전지 및 배터리 (Internal Cells and Batteries for Level of Protection "pzc") 52 H.1 일반 요구사항(General Requirements) 52 H.2 가압용기 내부에 위치한 기기로서 가압용기 내부에 위치하고 용기의 전원 차단 시 분리되지 않는 배터리에 연결된 기기(Equipment located inside a pressurized enclosure connected to a battery which is also located inside the pressurized enclosure and is not disconnected when power is removed from the enclosure) 52 H.3 하나 이상의 전지 또는 배터리를 포함하는 가압용기에 대한 추가적인 표시 및 구조 요구사 항(Supplementary marking and constructional requirements for pressurized enclosures containing one or more cells or batteries) - - 53 참고문헌 ·················· 54 KS C IEC 60079-2:2014 해 설 55 -iv- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
07defcc7-dd4c-4626-8811-71719578a586 | KSCIEC60079-2_2024확인_KR | KS CIEC 60079-2:2014 머 리 말 이 표준은 산업표준화법 관련 규정에 따라 산업표준심의 회의 심의 를 거쳐 개정한 한국산업표준이다. 이에 따라 KS C IEC 60079-2:2007(2012 년 발행)는 개정되어 이 표준으로 바뀌었다. 이 표준의 내용 일부 또는 전부는 저작권법에 따른 보호대상이 되는 저작물이 될 수 있다. 이 표준의 내용 일부 또는 전부가 ISO · IEC 등에서 제정한 표준을 참고하여 제정 또는 개정된 경우, 해당 표준의 저작권을 보유하고 있는 ISO · IEC 등의 저작권 보호 규정 등에 따라 보호되어야 한다. 이 표준의 일부가 기술적 성질을 가진 특허권, 출원공개 이후의 특허출원, 실용신안권 또는 출원공개 후의 실용신안등록출원에 저촉될 가능성이 있다는 것에 주의 를 환기한다. 관계 중앙행정기관의 장과 산업표준심의 회는 이러한 기술적 성질을 가진 특허권, 출원공개 이후의 특허출원, 실용신안권 또는 출원공개 후의 실용신안등록출원에 관계되는 확인에 대하여 책임을 지지 않는다. -v- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
7d45b331-5f23-4fb8-9ce4-d59f51376c0f | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 개 요 이 표준은 2014 년 제 6 판으로 발행된 IEC 60079-2, Explosive atmospheres - Part 2: Equipment protection by pressurized enclosures "p" 및 Corrigendum 1(2015)을 기초로 기술적 내용 및 대응국제표 준의 구성을 변경하지 않고 작성한 한국산업표준이다. KS C IEC 60079 의 이 부는 폭발성 분위기에서 보호가스가 다음과 같이 사용되는 경우 폭발성 분위기 에서 사용하기 위한 전기기기의 설계, 구조, 시험 및 표시에 대한 요구 사항을 제공한다. a) 외부 대기 이상의 압력으로 유지되는 보호가스가 인화성 가스 또는 증기의 내부 누출원을 포함 하고 있지 않은 용기 내부에 폭발성 가스 분위기가 형성되는 것을 방지하기 위해 사용되는 경우 b) 외부 대기 이상의 압력으로 유지되는 보호가스가 용기 내부에 폭발성 가스 분위기가 형성되는 것을 방지하기 위해 사용되고 하나 이상의 내부 누출원을 포함하는 용기에 폭발성 가스 분위기 가 형성되는 것을 방지하기 위해 공급된는 경우 c) 외부 대기 이상의 압력으로 유지되는 보호가스가 용기 내부에 폭발성 분진 분위기를 형성할 수 있는 가연성 분진의 유입을 방지하기 위해 사용되는 경우, 이 경우는 가연성 분진의 내부 누출 원이 없는 경우만 해당한다. 이 표준은 흡입구 및 배기 덕트를 비롯한 기기 및 관련 기기에 대한 요구사항과 가압 및/또는 희석 상태를 설정하고 유지하는데 필요한 보조 제어 기기에 대한 요구사항을 포함한다. -vi- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c6cef568-ebc3-4d09-a72a-80ef78e7bf72 | KSCIEC60079-2_2024확인_KR | 한국산업표준 KS C IEC 60079-2:2014 폭발성 분위기 - 제 2 부: 압력방폭용기 "p"에 의한 기기 보호 Explosive atmospheres - Part 2: Equipment protection by pressurized enclosures "p" 1 적용범위(Scope) KS C IEC 60079 의 이 부는 폭발성 가스 분위기 또는 폭발성 분진 분위기에서 사용하기 위한 압력방 폭구조 "p"의 가압용기(pressurized enclosures)가 있는 전기기기의 구조 및 시험에 관한 특정 요구사 항을 포함하고 있다. 또한 이 표준은 인화성 물질의 제한적 누출이 있는 가압용기에 대한 요구사항 을 포함한다. 이 표준은 KS C IEC 60079-0 의 일반 요구사항을 보완하고 수정한다. 이 표준의 요구사항이 KS C IEC 60079-0 의 요구사항과 상충하는 경우, 이 표준의 요구사항이 우선한다. 이 표준은 다음에 대한 요구사항은 포함하지 않는다. 다음과 같은 누출이 있을 수 있는 컨테인먼트 시스템(containment system)을 포함하는 가압용기 a) 산소 함량이 정상보다 큰 공기, 또는 b) 산소의 비율이 21 % 이상인 불활성 가스와 혼합된 산소 양압실 또는 분석실(pressurized rooms or analyser houses); IEC 60079-13 참조 폭발물 또는 불꽃이 존재하는 곳에 사용되는 가압용기 가스/증기와 가연성 분진의 하이브리드 혼합물(hybrid mixtures)이 존재하는 곳에 사용되는 가압용기 자체 산화제가 함유된 폭발물 또는 추진제와 같은 자연 발화성 물질이 존재하는 곳에 사용되는 가 압용기 가연성 분진의 내부 누출원이 있는 가압용기 비고 사용자가 제조자의 역할을 수행하는 경우, 일반적으로 이 표준의 모든 관련 부분이 기기의 제 조 및 시험에 적용됨을 확인하는 것은 사용자의 책임이다. 2 인용표준(Normative references) 다음의 인용표준은 전체 또는 부분적으로 이 표준의 적용을 위해 필수적이다. 발행연도가 표기된 인 용표준은 인용된 판만을 적용한다. 발행연도가 표기되지 않은 인용표준은 최신판(모든 추록을 포함) 을 적용한다. KS C IEC 60034-5, 회전기기 - 제 5 부: 회전기기 외함의 보호등급 분류(IP 코드) KS C IEC 60079-0, 폭발성 분위기 - 제 0 부: 기기 - 일반 요구사항 KS C IEC 60079-11, 폭발성 분위기 - 제 11 부: 본질안전 "i"에 의한 기기 보호 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 1 | {}
214fe890-61cb-4bd2-9041-097d5f73aa80 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 KS C IEC 60079-15, 폭발성 분위기 - 제 15 부: 방폭구조 "n"에 의한 기기 보호 KS C IEC 60112, 고체 절연 재료의 내트래킹 및 비교 트래킹 지수 측정 방법 KS C IEC 60529, 외함의 밀폐 보호등급 구분(IP 코드) KS C IEC 60664-1, 저압기기의 절연협조 - 제 1 부: 원칙, 요구사항 및 시험 IEC 60050(all parts), International Electrotechnical Vocabulary IEC 60127(all parts), Miniature fuses 3 용어와 정의(Terms and definitions) 이 표준의 목적을 위하여 KS C IEC 60050-151, IEC 60050-426 및 KS C IEC 60079-0 에 규정된 용어와 정의 및 다음을 적용한다. 비고 별도로 명시하지 않는 한, 용어 "전압" 및 "전류"는 교류, 직류 또는 합성 전압 및 전류의 실효 값(r.m.s.)을 의미한다. 3.1 경보기(alarm) 주의 를 끌기 위한 시각적 또는 청각적 신호를 발생하는 기기의 일부(piece of equipment) 3.2 컨테인먼트 시스템(containment system) 내부 누출원이 될 수 있는 인화성 물질을 포함하고 있는 기기의 일부(part of the equipment) 3.3 희석(dilution) 퍼지 후, 가압용기 내부의 인화성 물질의 농도가 잠재적인 점화원(즉, 희석지역 밖에 있는)에서 폭발 한도 범위 밖의 값으로 유지되도록 보호가스를 연속적으로 공급하는 것. 비고 불활성 가스에 의한 산소의 희석은 인화성 가스 또는 증기의 농도를 인화상한(UFL)보다 높일 수 있다. 3.4 희석지역(dilution area) 인화성 물질의 농도가 안전한 농도로 희석되지 않는 내부 누출원에 근접한 영역 3.5 용기 체적(enclosure volume) 내부 기기가 없는 빈 용기의 체적. 회전기기의 경우, 내부 빈 체적과 회전자가 차지하는 체적의 합 3.6 인화성 물질(flammable substance) 점화될 수 있는 가스, 증기, 액체 또는 그 혼합물 3.7 용융 밀봉 장치(hermetically sealed device) 외부의 대기가 내부에 접근할 수 없는 구조로 모든 밀봉이 용융(fusion) 방식으로 만들어진 장치 비고 용융 방식에는 브레이징, 용접 또는 유리-금속 용착 등이 있다. 2 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
e680d36c-6a22-4887-8764-20946db2662d | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 3.8 점화가능기기(ignition-capable equipment) ICE 정상 작동 중에 특정 폭발성 분위기에 점화원이 될 수 있는 기기 3.9 표시기(indicator) 유량 또는 압력이 적절한지를 나타내고 주기적으로 모니터링되도록 의도된 기기의 일부(piece of equipment) 3.10 내부 누출원(internal source of release) 공기의 존재하에서 폭발성 가스 분위기를 형성할 수 있는 인화성 가스 또는 증기 또는 액체 형태의 인화성 물질이 가압용기로 누출될 수 있는 지점 또는 위치 3.11 누설보상(leakage compensation) 가압용기 및 그 덕트에서 발생하는 누설을 보충하기에 충분한 보호가스를 공급하는 것. 3.12 양압(overpressure) 대기압 이상의 가압용기 내부의 압력 3.13 가압(pressurization) 용기 내부 보호가스의 압력을 외부 대기의 압력보다 높게 유지해서 외부 대기가 용기로 침투하는 것 을 방지하는 기술 3.14 가압시스템(pressurization system) 가압용기를 가압하고 모니터링하거나 제어하는 데 사용되는 안전장치 및 기타 구성 부품의 그룹화 (grouping) 3.15 가압용기(pressurized enclosure) 보호가스의 압력이 외부 대기보다 높게 유지되는 용기 3.16 보호가스(protective gas) 양압을 유지하고 필요한 경우, 희석 및 퍼지를 위해 사용되는 공기 또는 불활성 가스 비고 이 표준의 목적상, 불활성 가스라 함은 점화 및 인화 특성(폭발한계 등)을 더 부담스럽게 하지 않는 질소, 이산화탄소, 아르곤 또는 공기 중 산소를 1 로 하고 불활성 가스를 4 로 하는 비율로 혼합된 기타 가스를 의미한다. 3.17 보호가스 공급장치(protective gas supply) 양압의 보호가스를 공급하는 압축기, 송풍기 또는 압축 가스 용기 비고 1 보호가스 공급장치에는 인입(흡입) 배관 또는 덕트, 압력조절기(regulators), 배기 배관, 덕트 3 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
056a24e2-cea2-40b4-8041-03c89f4d3aff | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 및 공급 밸브를 포함한다. 비고 2 압력조절기 이외의 가압시스템의 부품은 포함되지 않는다. 3.18 퍼지(purging) 가압용기 에서 일정량의 보호가스를 용기 및 덕트를 통과 시켜 폭발성 가스 분위기의 농도를 안전한 수준으로 낮추는 작업 3.19 정적가압(static pressurization) 폭발위험 장소에서 보호가스를 추가하지 않고 가압용기 내의 양압을 유지 3.20 보호등급 "pxb"(Level of Protection "pxb") 기기보호등급(Equipment Protection Level) Mb, Gb 또는 Db 를 제공하는 가압용기 비고 이는 안전장치를 제외한 보호되지 않는 기기를 가압용기 내부에 설치하는 것을 허용한다(3.23 참조). 3.21 보호등급 "pyb"(Level of Protection "pyb") 가압용기 내부의 기기보호등급을 Gc 또는 Dc 로 하면서 기기보호등급 Gb 또는 Db 를 제공하는 가압 용기 비고 이는 안전장치를 제외하고 기기보호등급 Gc 또는 Dc 기기가 가압용기 내부에 설치되는 것을 허용한다(3.23 참조). 3.22 보호등급 "pzc"(Level of Protection "pzc") 기기보호등급 Gc 또는 Dc 를 제공하는 가압용기 비고 이는 안전장치를 제외한 보호되지 않는 기기를 가압용기 내부에 설치하는 것을 허용한다(3.23 참조). 3.23 안전장치(safety device) 방폭구조의 무결성(integrity)을 구현하거나 유지하는 데 사용되는 장치 3.24 인화하한(lower flammable limit) LFL 폭발성 가스 분위기를 형성하지 않는 공기 중의 인화성 가스 또는 증기의 백분율로 표시되는 하한 부피 분율(IEC 60079-20-1 참조) 비고 이는 폭발하한(Lower Explosive Limit, LEL)으로도 알려져 있다. 3.25 인화상한(upper flammable limit) UFL 폭발성 가스 분위기를 형성하지 않는 공기 중의 인화성 가스 또는 증기의 백분율로 표시되는 상한 4 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
6c4784ef-dff1-4156-8b50-ab4bb3909542 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 부피 분율(IEC 60079-20-1 참조) 비고 이는 폭발상한(Upper Explosive Limit, UEL)으로도 알려져 있다. 4 보호등급(Protection levels) 가압에 의한 보호는 내부 누출의 가능성 여부 및 가압용기 내부 기기의 점화가능 여부에 따라 요구 되는 기기보호등급(Mb, Gb, Db, Gc 또는 Dc)에 기초하여 선택된 세 가지의 보호등급("pxb", "pyb" 및 "pzc")으로 세분된다(표 1 참조). 그 후 보호등급에 따라 가압용기 및 가압시스템의 설계 기준이 정의 된다(표 2 참조). 표 1 - 보호등급의 결정 ¦ 내부 누출 조건이 있는가? ¦ 외부 폭발성 분위기에 대해 요구되는 최고 기기보호등급 ¦ 용기 내부에 점화가능기기(ICE)가 있는가? ¦ 보호등급 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 없음. ¦ Mb, Gb 또는 Db ¦ 있음 또는 없음. ¦ "pxb" ¦ ¦ 없음. ¦ Gb 또는 Db ¦ 없음. ¦ "pyb" ¦ ¦ 없음. ¦ Gc 또는 Dc ¦ 있음 또는 없음. ¦ "pzc" ¦ ¦ 있음, 가스/증기 ¦ Mb, Gb 또는 Db ¦ 없음 또는 있음(점화가능기기가 희석지 역에 위치하지 않음). ¦ "pxb" ¦ ¦ 있음, 가스/증기 ¦ Gb 또는 Db ¦ 없음. ¦ "pyb" ¦ ¦ 있음, 가스/증기 ¦ Gc 또는 Dc ¦ 있음(점화가능기기가 희석지 역에 위치하지 않음). ¦ "pxb" ¦ ¦ 있음, 가스/증기 ¦ Gc 또는 Dc ¦ 없음. ¦ "pyb" ¦ ¦ 있음, 액체 ¦ Gb 또는 Db ¦ 있음 또는 없음. ¦ "pxb" (불활성) ¦ ¦ 있음, 액체 ¦ Gb 또는 Db ¦ 없음. ¦ "pyb" (불활성) ¦ ¦ 있음, 액체 ¦ Gc 또는 Dc ¦ 있음 또는 없음. ¦ "pzc" (불활성) ¦ ¦ 인화성 물질이 액체인 경우, 정상 누출(normal release)은 허용되지 않는다. ¦ 인화성 물질이 액체인 경우, 정상 누출(normal release)은 허용되지 않는다. ¦ 인화성 물질이 액체인 경우, 정상 누출(normal release)은 허용되지 않는다. ¦ 인화성 물질이 액체인 경우, 정상 누출(normal release)은 허용되지 않는다. ¦ ¦ 보호등급 뒤에 "(불활성)"이 ¦ 표시되어 있다면 보호가스는 불활성이어야 한다(13 절 참조). ¦ ¦ --- ¦ --- ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 5 | {}
3e981602-6510-45bb-9d31-65b16a6dfbd4 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 표 2- 보호등급별 설계 기준 ¦ 설계 기준 ¦ 보호등급 "pxb" ¦ 보호등급 "pyb" ¦ 표시기가 있는 보호등급 "pzc" ¦ 경보기가 있는 보호등급 "pzc" ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ KS C IEC 60529 또는 KS C IEC 60034-5 에 따른 용기 보호등급 (IP) ¦ 최소 IP4X ¦ 최소 IP4X ¦ 최소 IP4X ¦ 최소 IP3X ¦ ¦ 용기의 내충격성 ¦ KS C IEC 60079-0 적용 ¦ KS C IEC 60079-0 적용 ¦ KS C IEC 60079-0 적용 ¦ KS C IEC 60079-0 기준 값의 1/2 적 용 ¦ ¦ 그룹 I 및 그룹 II 에 대 한 퍼지 시간의 검증 ¦ 타이밍 장치가 필요하고 압력 및 유량을 모니 터링 ¦ 시간 및 유량 표 시(marking) ¦ 시간 및 유량 표시 ¦ 시간 및 유량 표시 ¦ ¦ 백열입자(incandescent particles)가 정상상태 에서 닫혀 있는 (normally closed) 압력 배출구를 통해 EPL Mb, Gb 또는 Db 가 요 구되는 폭발위험장소로 배출되는 것을 방지 ¦ 정상상태에서 백 열입자가 발생할 수 있는 경우, 불 꽃 및 입자 배리 어(spark and particle barrier) 필요(5.9 참조) ¦ 요구사항 없음.a ¦ 보호등급 "pzc"는 EPL Mb, Gb 또는 Db 가 요구되는 장소에는 적용할 수 없음. ¦ 보호등급 "pzc"는 EPL Mb, Gb 또는 Db 가 요구되는 장소에는 적용할 수 없음. ¦ ¦ 백열입자가 정상상태에 서 닫혀 있는 압력 배 출구를 통해 EPL Gc 또는 Dc 가 요구되는 폭발위험장소로 배출되 는 것을 방지 ¦ 요구사항 없음.b ¦ 요구사항 없음.b ¦ 요구사항 없음.b ¦ 요구사항 없음.b ¦ ¦ 백열입자가 정상상태에 서 열려 있는 벤트 (vent)를 통해 EPL Mb, Gb 또는 Db 가 요구되 는 폭발위험장소로 배 출되는 것을 방지 ¦ 불꽃 및 입자 배 리어 필요(5.9 참 조) ¦ 불꽃 및 입자 배 리어 필요(5.9 참 조) ¦ 보호등급 "pzc"는 EPL Mb, Gb 또는 Db 가 요구되는 장소에는 적용할 수 없음. ¦ 보호등급 "pzc"는 EPL Mb, Gb 또는 Db 가 요구되는 장소에는 적용할 수 없음. ¦ ¦ 백열입자가 정상상태에 서 열려 있는 벤트를 통해 EPL Gc 또는 Dc 가 요구되는 폭발위험 장소로 배출되는 것을 방지 ¦ 정상상태에서 백 열입자가 발생할 수 있는 경우, 불 꽃 및 입자 배리 어 필요(5.9 참조) ¦ 요구사항 없음.a ¦ 정상상태에서 백 열입자가 발생할 수 있는 경우, 불 꽃 및 입자 배리 어 필요(5.9 참조) ¦ 정상상태에서 백 열입자가 발생할 수 있는 경우, 불 꽃 및 입자 배리 어 필요(5.9 참조) ¦ 6 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
a5ad9443-609f-4310-8fd1-a3fefd8a65ed | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 표 2- 보호등급별 설계 기준(계속) ¦ 설계 기준 ¦ 보호등급 "pxb" ¦ 보호등급 "pyb" ¦ 표시기가 있는 보호등급 "pzc" ¦ 경보기가 있는 보호등급 "pzc" ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 공구에 의해서만 열리 는 문 또는 덮개 ¦ 경고, 5.3 및 6.2 b)ii) 참조 ¦ 경고, 5.3.6 참조 b ¦ 경고, 5.3.6 참조 c ¦ 경고, 5.3.6 참조° ¦ ¦ 공구 없이 열 수 있는 문 또는 덮개 ¦ 인터록, 7.14 참 조(내부 고온부품 없음) ¦ 경고, 5.3.6 참조 a ¦ 경고, 5.3.6 참조 c ¦ 경고, 5.3.6 참조 c ¦ ¦ 용기를 열기 전에 냉각 기간이 필요한 내부 고 온부품 ¦ 6.2b)ii) 준수 ¦ 요구사항 없음 a ¦ 경고, 5.3.6 참조 ¦ 경고, 5.3.6 참조 ¦ a 6.2 b) ii)는 내부 고온부품이나 정상상태에서 발생하는 백열입자가 허용되지 않는 보호등급 "pyb" 에는 적용되지 않는다. b 비정상 작동상태에서 압력 배출 벤트(relief vent)가 열리는 경우, 외부 대기가 폭발 한계 내에 있 을 가능성이 없기 때문에 불꽃 및 입자 배리어는 필요하지 않다. C 정상 작동상태에서 용기의 문과 덮개가 닫힌 상태에서 가압되므로 보호등급 "pzc" 용기에는 공 구의 접근성에 대한 요구사항은 없다. 덮개나 문을 개방하는 경우라면 대기가 폭발한계 내에 있 을 가능성이 없다. 5 가압용기의 구조 요구사항(Constructional requirements for pressurized enclosures) 5.1 용기(Enclosure) 가압용기는 표 2 에 따른 용기의 보호등급(IP)을 가져야 한다. 표시된 온도등급을 초과 하는 내부 부품이 없는 보호등급 "pxb"와 보호등급 "pyb" 및 "pzc"는 KS C IEC 60079-0 에 따른 비금속 용기 및 용기의 비금속 부에 대한 내열 및 내한시험을 가압용기에 적용 할 필요는 없다. 그 이유는 용기의 성능 저하로 누설량이 증가되고, 결국 알람을 발생시키거나 점화가능 회로의 전원 을 차단시키기 때문이다. 따라서 비금속 용기 및 용기의 비금속 부에 대한 전처리 시험(pre- conditioning testing)은 필요하지 않은 것으로 간주한다. 5.2 재료(Materials) 용기, 덕트 및 연결부에 사용되는 재료는 명시된 보호가스에 악영향을 받지 않아야 한다. 5.3 문 및 덮개(Doors and covers) 5.3.1 그룹 I 가압용기(Group I pressurized enclosures) 문 및 덮개는 다음 중 하나와 같아야 한다. KS C IEC 60079-0 에 적합한 특수 패스너(special fasteners)가 있거나 7.15 에 나타낸 EPL 을 제공하지 않는 기기에 대한 전기 공급이 문 또는 덮개가 개방될 때 자동으 로 차단되고 닫히기 전까지는 전기가 공급되지 않도록 인터록 장치를 설치한다. 7.7 의 요구사항 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 7 | {}
c1d6e6e1-59ff-45c5-8318-c4d085c3066f | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 또한 적용한다. 5.3.2 정적가압을 하는 그룹 I 가압용기(Group I pressurized enclosures with static pressurization) 문 및 덮개에는 KS C IEC 60079-0 에 적합한 특수 패스너가 있어야 한다. 5.3.3 그룹 II 및 그룹 III 가압용기(Group II and Group III pressurized enclosures) KS C IEC 60079-0 의 특수 패스너에 대한 요구사항은 적용하지 않는다. 보호등급 "pxb"의 경우, 공구 또는 열쇠를 사용하지 않고 열 수 있는 문 및 덮개에는 인터록 장치가 설치되어 7.15 에 명시되지 않은 전기기기로의 전기 공급이 문 또는 덮개가 개방될 때 자동으로 차단 되고 닫히기 전까지는 전기가 공급되지 않도록 한다. 보호등급 "pyb" 및 보호등급 "pzc"의 경우, 공구나 열쇠의 사용이 요구되지 않는다. 패스너(fastener)를 해제할 때 내부 압력에 의해 문이나 덮개가 갑자기 열릴 수 있는 가능성을 고 려하여야 한다. 운전자 또는 유지보수 작업자는 다음과 같은 방법을 통해 부상으로부터 보호되어 야 한다. a) 여러 개의 패스너를 사용하여 패스너가 모두 풀리기 전에 용기의 압력이 안전하게 배출되도록 하 거나 b) 용기를 열 때 압력이 안전하게 배출되도록 두 점식 패스너(two-position fastener)를 사용하거나 c) 최대 내부 압력을 2.5 kPa 이하로 제한한다. 5.3.4 정적가압을 하는 그룹 II 및 그룹 III 가압용기(Group II and Group III pressurized enclosures wit h static pressurization) 문 및 덮개는 열쇠나 공구를 사용하지 않는 경우 쉽게 열 수 없어야 한다. 5.3.5 그룹 II 및 그룹 III 의 보호등급 "pxb"(Group II and Group III Level of Protection "pxb") 냉각 기간을 필요로하는 고온부품을 포함하는 가압용기는 공구나 열쇠를 사용하지 않는 경우 쉽게 열 수 없어야 한다. 5.3.6 그룹 II 및 그룹 III 의 문 및 덮개 경고(Group II and Group III Door and Cover warning) 용기를 열었을 때 존재할 수 있는 폭발성 가스 분위기 또는 폭발성 분진 분위기의 점화를 막기 위해, 용기의 문 및 덮개에는 다음과 같은 표시를 하여야 한다. 경고 - 폭발성 분위기가 존재할 때 열지 마시오. 5.4 기계적 강도(Mechanical strength) 가압용기와 해당하는 경우 덕트 및 그 연결 부분은 모든 배출구가 닫힌 상태로 정상 운전 중 제조자 가 명시한 최대 양압의 1.5 배(최소 200 Pa)에 해당하는 압력을 견뎌야 한다. 용기와 해당하는 경우 덕트 또는 그 연결 부분의 변형을 일으킬 수 있는 압력이 사용 중에 발생할 수 있는 경우, 내부 최대 양압을 방폭구조에 악영향을 미칠 수 있는 수준 이하로 제한하기 위하여 8 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
818aeb06-171b-452e-908e-79961ae96044 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 안전장치를 설치해야 한다. 제조자가 안전장치를 제공하지 않는 경우에는 KS C IEC 60079-0 의 표시 요구사항에 따라 인증번호에 "X" 접미사를 표시하고 인증서의 특정사용조건(Specific Conditions of Use) 에 사용자가 이 표준의 요구사항을 준수하는 데 필요한 정보를 상세히 기술하여야 한다. 5.5 그룹 I 및 그룹 II 의 개방구, 칸막이, 구획 및 내부 부품(Group I and Group II Apertures, partiti ons, compartments and internal components) 5.5.1 개방구 및 칸막이는 퍼지가 효과 적으로 이루어질 수 있는 위치에 있어야 한다. 퍼지되지 않는 구역은 보호가스의 유입구 및 배출구의 적절한 배치와 칸막이의 영향을 고려하여 제 거할 수 있다. 공기보다 무거운 가스나 증기의 경우, 보호가스의 유입구는 가압용기의 상부측에 위치하여야 하며 배출구는 용기 바닥측에 위치하여야 한다. 공기보다 가벼운 가스나 증기의 경우, 보호가스의 유입구는 가압용기의 바닥측에 위치하여야 하며 배출구는 용기 상부측에 위치하여야 한다. 유입구와 배출구를 용기의 반대편에 위치하게 하면 교차 환기(cross ventilation)가 원활해진다. 내부 칸막이(예: 회로 기판)는 보호가스의 흐름을 방해하지 않도록 배치하여야 한다. 다기관이나 배플 (manifold or baffles)을 사용하면 장애물 주변에 흐름을 개선할 수 있다. 개방구의 수는 기기 설계와 관련하여 선택해야 하며 특히 기기가 분할된 경우, 하부 구획의 퍼지를 고려해야 한다. 5.5.2 내부 구획(internal compartments)은 주 용기와 통기되거나 별도로 퍼지되어야 한다. 1 000 cm3 당 1 cm2 이상의 통기 면적을 갖는 통기구(vents)(최소 지름 6.3 mm)는 일반적으로 적절한 퍼지를 위해 충분하다. 5.5.3 음극선관(CRTs) 및 기타 용융 밀봉장치는 퍼지를 할 필요가 없다. 5.5.4 내부 빈 체적(free internal volume)이 20 cm3 미만인 부품은 이러한 모든 부품의 총 체적이 가압 용기의 내부 빈 체적의 1 %를 초과 하지 않는 경우 퍼지가 필요한 내부 구획으로 고려하지 않는다. 비고 1 여기서 1 %는 수소의 인화하한(LFL)의 25 %를 기준으로 한 것이다(A.2 참조). 트랜지스터, 마이크로 회로, 커패시터 등과 같이 밀봉된 것으로 간주되는 전기 부품은 부품의 총 체 적 계산에 포함되지 않는다. 5.6 정적가압을 위한 개방구(Apertures for Static Pressurization) 용기에는 한 개 이상의 개방구가 있어야 한다. 보호가스를 채우고 가압한 후, 모든 개방구는 막아야 한다. 5.7 그룹 I 기기의 절연 재료(Insulating materials for Group I equipment) 16 A 를 초과 하는 정격전류로 인한 공기 중 아크를 유발할 수 있는 전기적 응력을 받는 절연 재료(회 9 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
4c5f8a1d-f0ac-49e2-ad97-8cc292708930 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 로차단기, 접촉기, 분리기와 같은 스위칭 장치)는 다음 중 적어도 하나 이상을 만족해야 한다. KS C IEC 60112 에 따른 CTI 400 M 이상의 비교트래킹지수 용기 내부에서 절연 재료가 분해되어 위험한 상태가 될 수 있는 것을 감지하고 자동으로 용기 공 급측 전원을 차단하는 적합한 장치. 이러한 장치의 사용여부 및 그 기능은 검증되어야 한다. KS C IEC 60664-1 의 오염등급 3 의 재료 그룹 III(CTI)에서 등가 전압에 대해 표시된 값을 준수하는 노출 충전 도체 사이의 연면거리 5.8 밀봉(Sealing) 가압용기에 접속하는 모든 케이블 및 전선관 접속부는 용기의 IP 등급을 유지시키기 위해 밀봉되어 야 하며, 밀봉되지 않은 경우 용기의 일부로 간주하여야 한다. 5.9 불꽃 및 입자 배리어(Spark and particle barriers) 보호가스에 대한 가압용기 및 덕트(있다면)에는 폭발위험장소로 백열입자(incandescent particles)가 방 출하는 것을 방지하기 위한 불꽃 및 입자 배리어를 설치하여야 한다. 백열입자는 개폐(make/break) 접점이 10A 미만에서 작동하고 작동전압이 교류 275 V 또는 직류 60 V 를 초과 하지 않으며 접점에 덮개가 있는 경우를 제외하고 정상적으로 생성되는 것으로 가정해야 한다. 백열입자가 정상 작동 중에 발생하지 않는 용기는 EPL Gb 또는 Mb 를 필요로하는 폭발위험장소로 배출하는 정상상태에서 닫혀 있는 압력 배출구에 불꽃 및 입자 배리어를 설치할 필요는 없다. 백열입자가 정상 작동 중에 발생하지 않는 용기는 EPL Gc 를 필요로 하는 폭발위험장소로 배출하는 배출구에 불꽃 및 입자 배리어를 설치할 필요는 없다. 제조자가 불꽃 및 입자 배리어를 제공하지 않는 경우에는 KS C IEC 60079-0 의 표시 요구사항에 따라 인증번호에 "X" 접미사를 표시하고 인증서의 특정사용조건에 사용자가 이 표준의 요구사항을 준수하 는 데 필요한 정보를 상세히 기술하여야 한다. 5.10 전지 및 배터리(Cells and batteries) 부속서 G 는 보호등급 "pxb" 및 "pyb"에 대한 요구사항을 규정한다. 부속서 H 는 보호등급 "pzc"에 대 한 요구사항을 규정한다. 6 온도 제한(Temperature limits) 6.1 일반사항(General) 기기는 KS C IEC 60079-0 의 온도등급 요구사항에 따라 분류되어야 한다. 온도등급은 6.2 및 6.3 에 따 라 결정하여야 한다. 6.2 보호등급 "pxb" 또는 보호등급 "pyb"(For Level of Protection "pxb" or Level of Protection "pyb") 온도등급은 다음 온도 중 높은 온도를 기준으로 하여야 한다. a) 용기의 가장 뜨거운 외부 표면, 또는 10 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c9309b47-444b-41e0-bad2-bc5690c0c63f | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 b) 가장 뜨거운 내부 부품 표면 예외: 내부 부품은 다음과 같은 경우 표시된 온도 등급을 초과 할 수 있다. i) KS C IEC 60079-0 의 "소형 부품" 관련 요구사항을 준수하는 경우 ii) 가압용기의 보호등급이 "pxb"이며 KS C IEC 60079-0 의 개방 시간에 대한 요구사항을 준수하는 경우. 가압이 중단되면 고온부품이 허용된 최고 온도 이하로 냉각되기 전에 폭발성 가스 분위 기가 고온부품의 표면에 접촉하는 것을 방지할 수 있도록 적절한 조치가 이루어져야 한다. 이것은 가압용기 및 덕트 접합부의 설계 및 구조 또는 다른 방법, 예를 들어 보조 환기 시스템을 작 동시키거나 가압용기 내부의 고온 표면을 가스 밀폐형 또는 몰드형 용기(encapsulated housing)로 하 는 등의 방법으로 이루어질 수 있다. 보호등급 "pyb"의 경우, 용기 내부에 정상 작동 중 고온의 점화 가능 부품(hot ignition-capable parts)이 있어서는 안 된다. 6.3 보호등급 "pzc"(For Level of Protection "pzc") 온도등급은 용기의 가장 뜨거운 외부 표면을 기준으로 한다. 온도등급을 결정할 때 가압시스템의 차단 시에도 통전 상태를 유지하는 내부 방폭기기를 고려하여야 한다. 7 안전 대책 및 안전장치(정적가압 제외)(Safety provisions and safety devices(except for static pressurization)) 7.1 폭발위험장소에 대한 안전장치의 적합성(Suitability of safety devices for hazardous area) 가압으로 보호되는 전기기기의 점화 가능성을 감소시키는 데 사용하는 모든 안전장치는 그 자체가 점화를 일으킬 수 없거나(7.15 참조) 폭발위험장소 밖에 설치되어야 한다. 7.2 안전장치의 무결성(Integrity of safety devices) 이 표준에서 요구하는 안전장치(표 3 참조)는 제어시스템의 안전관련 부품을 구성한다. 제어 시스템 의 안전과 무결성은 다음과 일치해야 한다. 보호등급 "pxb" 또는 보호등급 "pyb"의 경우, 단일 고장 평가(a single fault evaluation) 보호등급 "pzc"의 경우, 정상 작동(normal operation) 비고 단일 고장 평가에 대한 지침으로 IEC 61511 시리즈 또는 유사한 표준을 사용할 수 있다. 팬 모터 또는 제어장치에 대한 전기적 인터록은 가압의 실패을 검출하는 데 충분하지 않은데, 이는 팬 벨트의 미끄러짐, 팬의 회전축에서의 풀림 또는 팬의 역회전과 같은 고장을 검출할 수 없기 때문 이다. 11 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
767c242f-4d88-4281-8b01-bc650555f2c8 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 표 3- 보호등급별 안전장치 ¦ 설계 기준 ¦ 보호등급 "pxb" ¦ 보호등급 "pyb" ¦ 보호등급 "pzc" ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 최소양압의 손실을 감지 하는 안전장치 ¦ 압력 센서, 7.11 참조 ¦ 압력 센서, 7.11 참조 ¦ 표시기 또는 압력 센서, 7.11 d) 참조 ¦ ¦ 그룹 I 및 그룹 II 의 퍼지 시간을 확인하는 안전장치 ¦ 타이밍 장치, 압력 센 서 및 배출구에서의 유량 센서, 7.7 참조 ¦ 시간 및 유량 표시 (marking), 7.8 c) 참조 ¦ 시간 및 유량 표시, 7.8 c) 참조 ¦ ¦ 공구를 사용하여야만 개 방할 수 있는 문 또는 덮 개에 대한 안전장치 ¦ 경고, 6.2b) 참조 ¦ 요구사항 없음. (내부 고온부 불허) ¦ 요구사항 없음. ¦ ¦ 공구 없이도 개방할 수 있는 문 또는 덮개에 대 한 안전장치 ¦ 인터록 장치, 7.14 참조 (내부 고온부 불허) ¦ 요구사항 없음. (내부 고온부 불허) ¦ 요구사항 없음. ¦ ¦ 컨테인먼트 시스템이 있 을 때 내부 고온부를 위 한 안전장치 (15 절 참조) ¦ 경보 및 인화성 물질의 흐름 차단 ¦ 내부 고온부가 허용되 지 않으므로 이 보호등 급에 적용되지 않음. ¦ 경보 (정상상태 누출 불허) ¦ 7.3 안전장치의 제공자(Provider of safety devices) 안전장치는 기기 제조자 또는 사용자가 제공하여야 한다. 제조자가 안전장치를 제공하지 않을 경우 에는 KS C IEC 60079-0 의 표시 요구사항에 따라 인증번호에 "X" 접미사를 표시하고 인증서의 특정사 용조건에 사용자가 이 표준의 요구사항을 준수하는 데 필요한 정보를 상세히 기술하여야 한다. 7.4 관련기기로 평가되는 가압시스템(Pressurization System evaluated as associated equipment) 7.4.1 보호등급 "pzc" 가압시스템(Pressurization systems for Level of Protection "pzc") 가압시스템은 7.11 에 따라 최소 양압을 제어할 수 있는 수단(예: 압력조절기) 및 최소 양압을 확인할 수 있는 수단(예: 표시기)을 최소한 포함하여야 한다. 벤트가 제공되는 경우에는 벤트에 불꽃 및 입자 배리어가 있어야 한다. 제공되는 압력조절기의 단일 고장 모드(single failure mode)가 압력조절기 입구 전체 압력이 배출구측 에 인가되는 유형인 경우, 용기의 내부 압력을 지정된 값으로 제한하는 수단(예: 릴리프 벤트)이 제공 되어야 한다. 이 압력 값은 사용설명서에 명시하고 시험이나 계산에 의해 설정한다. 여러 개의 압력 조절기 또는 릴리프 벤트가 옵션으로 제공되는 경우, 사용 가능한 각 압력조절기/릴리프 벤트 옵션에 대한 값을 결정하여야 한다. 가압시스템은 올바른 작동을 확인하기 위해 시험되어야 한다. 7.4.2 보호등급 "pyb" 가압시스템(Pressurization systems for Level of Protection "pyb") 가압시스템은 7.11 에 따라 최소 양압을 제어할 수 있는 수단(예: 압력조절기), 최소 양압을 확인할 수 있는 수단(예: 압력 센서) 및 자동 안전장치(automatic safety device)를 포함하여야 한다. 제공되는 압력조절기의 단일 고장 모드가 압력조절기 입구 전체 압력이 배출구측에 인가되는 유형인 경우, 용기의 내부 압력을 지정된 값으로 제한하는 수단(예: 릴리프 벤트)이 제공되어야 한다. 이 압 력 값은 사용설명서에 명시하고 시험이나 계산에 의해 설정한다. 여러 개의 압력조절기 또는 릴리프 12 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
5a1482c2-275c-4af0-bb5a-da29eadb6cbf | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 벤트가 옵션으로 제공되는 경우, 사용 가능한 각 압력조절기/릴리프 벤트 옵션에 대한 값을 결정하여 야 한다. 가압시스템은 올바른 작동을 확인하기 위해 시험되어야 한다. 7.4.3 보호등급 "pxb" 가압시스템(Pressurization systems for Level of Protection "pxb") 가압시스템은 7.11 에 따른 최소 양압을 제어할 수 있는 수단(예: 압력조절기), 최소 양압을 확인할 수 있는 수단(예: 압력 센서), 자동 안전장치 및 7.7 에 따른 유량 센서를 포함하는 자동 제어시스템을 포 함하여야 한다. 제공되는 압력조절기의 단일 고장 모드가 압력조절 입구 전체 압력이 배출구측에 인가되는 유형인 경우, 용기의 내부 압력을 지정된 값으로 제한하는 수단(예: 릴리프 벤트)이 제공되어야 한다. 이 압 력 값은 사용설명서에 명시하고 시험이나 계산에 의해 설정한다. 여러 개의 압력조절기 또는 릴리프 벤트가 옵션으로 제공되는 경우, 사용 가능한 각 압력조절기/릴리프 벤트 옵션에 대한 값을 결정하여 야 한다. 가압시스템은 자동제어시스템의 기능을 포함하여 올바른 작동을 확인하기 위해 시험되어야 한다. 7.5 보호등급 "pxb"에 대한 순서도(Sequence diagram for Level of Protection "pxb") 보호등급 "pxb" 가압시스템의 경우, 제조자는 제어시스템의 동작을 정의 하기 위한 기능 순서도 (functional sequence diagram)[예: 진리표(truth table), 상태도(state diagram), 흐름도(flow chart) 등]를 제공하여야 한다. 이 순서도는 안전장치의 작동 상태와 그에 따른 조치를 명확하게 식별하고 보여 주어야 한다. 순서도에 대한 적합성을 검증하기 위한 기능시험(functional tests)을 실시해야 한다. 이 러한 시험은 제조자가 별도로 지정하지 않는 한, 정상 대기 조건 하에서 실시한다. 비고 제조자가 제공하여야 하는 정보의 예가 부속서 B 에 제시되어 있다. 7.6 안전장치의 정격(Ratings for safety devices) 제조자는 안전장치의 최대 및 최소 작동 수준과 허용오차를 명시하여야 한다. 안전장치는 제조자가 명시한 정격 이내에서 사용하여야 한다. 7.7 그룹 I 및 그룹 II - 보호등급 "pxb"의 자동 퍼지(Group I and Group II Purging automated f or Level of Protection "pxb") 퍼지가 완료된 후에만 가압용기 내부의 전기기기에 전원을 공급하기 위해 안전장치가 포함된 자동제 어시스템을 제공하여야 한다. 제어시스템의 작동 순서는 다음과 같아야 한다. a) 순서도에 따라 작동이 시작되면, 가압용기를 통한 퍼지 유량 및 내부 최소 양압을 이 표준에 따 라 모니터링하여야 한다. b) 보호가스의 최소 유량이 확보되고 양압이 지정한 범위 내에 있을 때, 퍼지 타이머를 시작할 수 있다. c) 퍼지시간이 경과 된 후에 전기기기에 전류를 공급할 수 있다. d) 순서 중에 어떤 단계의 실패가 발생한 경우, 회로는 처음 시작 단계로 재설정되어야 한다. 13 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
1839acc5-0b3b-4cea-9ee7-1c7bba6a4907 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 7.8 그룹 I 및 그룹 II - 퍼지 기준(Group I or Group II - Purging criteria) 제조자는 용기가 열렸거나 양압이 제조자가 지정한 최소값 이하로 떨어진 후 적절한 퍼지에 필요한 조건을 명시하여야 한다. a) 보호등급 "pxb" 또는 보호등급 "pyb"의 경우, 제조자는 16.4 또는 16.5 의 시험을 만족할 수 있는 최소 퍼지 유량 및 시간을 명시하여야 한다. 회전기기 및 복잡한 형상을 가진 기기 이외의 경우, 최소 퍼지 유량 및 시간은 해당 퍼지가 시험 없이도 적절하다고 판단되면 용기 체적의 5 배에 해 당하는 퍼지를 기반으로 정할 수 있다. b) 보호등급 "pzc"의 경우, 회전기기 및 복잡한 형상을 가진 기기 이외의 경우, 제조자는 가압용기 가 5 배의 용기 체적에 해당하는 양의 보호가스로 퍼지될 수 있도록 최소 퍼지 유량 및 시간을 명 시하여야 한다. 효과 적인 퍼지가 16.4 또는 16.5 에 따른 시험을 통해 입증되는 경우, 보호가스의 양을 줄일 수 있다. 회전기기 및 복잡한 형상을 가진 기기에 대한 퍼지시험은 퍼지시간이 유사하거나 동등한 용기 (similar or comparable enclosures)로 이루어진 시험에 기초하는 경우 생략할 수 있다. c) 퍼지유량은 가압용기의 배출구에서 감시(monitor)해야 한다. 보호등급 "pxb"의 경우, 실제 유량을 감시해야 한다. 보호등급 "pyb" 또는 보호등급 "pzc"의 경우, 유량은 예를 들어 용기의 압력과 배 출구측에 정해진 오리피스를 통해 추론될 수 있다. 보호등급 "pyb" 또는 보호등급 "pzc"의 경우, 전기기기에 전원을 공급하기 전에 가압용기를 퍼지할 수 있도록 경고 표지를 부착하여야 한다. 경고 표지는 다음과 같은 내용 또는 이와 유사한 내용을 포함하여야 한다. 경고 - 용기가 개방된 후에 용기가 유량 에서 분간 퍼지될 때까지 전원을 투입하지 마시오. 비고 기기에 포함되지 않는 관련 덕트의 빈 공간을 결정하고 주어진 최소 유량에 대한 추가 퍼지시 간을 설정하는 것은 일반적으로 사용자의 책임이다. 7.9 그룹 III- 청소(Group III - Cleaning) 전원공급 장치를 켜기 전에 내부의 가연성 분진이 제거되어야 한다는 경고가 표시되어야 한다. 경고 표지는 다음과 같은 내용 또는 이와 유사한 내용을 포함하여야 한다. 경고 - 용기가 개방된 후에 내부에 쌓인 가연성 분진이 제거되기 전까지 전원을 투입하지 마시오. 7.10 최소 유량이 요구되는 경우의 요구사항(Requirements when a minimum flow rate required) 보호가스의 최소 유량을 제조자가 명시한 경우(예를 들면, 내부 기기가 표시된 온도 등급보다 더 높 은 온도를 발생시키는 경우), 배출구에서 보호가스 유량이 명시한 최소값 미만으로 떨어질 때 작동하 는 하나(또는 그 이상)의 자동 안전장치를 제공하여야 한다. 7.11 최소양압 감지를 위한 안전장치(Safety devices to detect minimum overpressure) 가압용기의 양압이 제조자가 명시한 최소값 미만으로 떨어질 때 작동하는 하나 이상의 자동 안전장 치를 제공하여야 한다. a) 자동 안전장치의 센서는 가압용기로부터 직접 신호를 받아야 한다. b) 자동 안전장치의 센서와 가압용기 사이에 밸브를 설치해서는 안 된다. 14 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
4c586e45-42e5-41f0-b789-026d4def3f04 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 c) 안전장치의 올바른 작동을 점검할 수 있어야 한다. 안전장치의 위치 및 설정은 7.12 의 요구사항을 고려해야 한다. 비고 자동 안전장치 사용의 용도(즉, 전원을 차단하거나 경보를 울리거나 또는 설치 안전성 보장) 는 일반적으로 사용자의 책임이다. d) 보호등급 "pzc"의 경우, 가압용기에 자동 안전장치 대신 표시기가 설치된 경우 다음 조건을 준수 하여야 한다. 1) 보호가스 공급장치에는 가압용기의 최소 압력을 유지하지 못하는 경우 보호가스 공급장치의 고장(failure)을 알리는 경보 장치가 있어야 한다. 2) 가압용기와 보호가스 공급장치의 경보기 사이에는 차단 밸브(isolating valve) 및/또는 압력이나 유량 제어장치 외에 어떠한 장치도 없어야 한다. 3) 차단 밸브는 다음과 같아야 한다. 다음과 같이 표시 경고 - 보호가스 공급용 밸브 - 밸브를 잠그기 전에 사용설명서를 따르시오. 열림 위치에서 밀봉 또는 고정(sealed or secured)이 가능 열렸는지 또는 닫혔는지를 나타내는 표시 가압용기 바로 옆에 위치 가압용기의 수리(servicing)하는 동안에만 사용 비고 차단 밸브는 해당 장소가 폭발성 가스 분위기가 존재하지 않거나 가압용기 내부의 모든 기기의 전원이 차단되고 냉각되어 있지 않는 한 열려 있어야 한다. 4) 압력 또는 유량 제어장치가 조정 가능한 경우, 이를 조작하기 위해서는 공구를 필요로 해야 한다. 5) 가압용기와 보호가스 공급장치의 경보기 사이에는 필터를 설치해서는 안 된다. 6) 표시기는 관찰하기 편리한 곳에 설치하여야 한다. 7) 표시기는 용기의 압력을 표시하여야 한다. 8) 표시기의 감지 위치는 가장 불리한 사용 조건을 고려하여 정하여야 한다. 9) 5.1 의 비금속 용기 또는 용기의 비금속 부에 대한 비적용 사항은 적용되지 않는다. 10) 표시기와 가압용기 사이에는 차단 밸브를 설치해서는 안 된다. 용기 압력과 퍼지 유량 모두를 나타내는 데 통상 사용되는 유량계는 배출구에 위치해야 한다. 압력을 나타내는 데만 통상 사용하는 유량계는 유입구를 제외한 용기의 어느 곳에나 위치할 수 있다. 비고 예외적인 경우에만 유량계를 유입구에 설치하여 용기의 압력 또는 용기를 통과 하는 유량을 나 타낸다. 7.12 최소 양압 값(Value of minimum overpressure) 가압용기 및 관련 덕트 내부, 누설이 발생할 수 있는 모든 지점에서 보호등급 "pxb" 또는 보호등급 "pyb"에 대해서 최소 양압 50 Pa, 보호등급 "pzc"에 대해서는 최소 양압 25 Pa 이 유지되어야 한다. 제조자는 사용 중 최소 및 최대 정상양압(normal overpressure), 퍼지 중 최대 양압 그리고 최대 정상 양압에서의 최대누설률(maximum leakage rate)을 명시하여야 한다. 내부 팬(예: 모터)에 의해 순환이 이루어지는 내부에 밀폐된 냉각 회로를 갖는 가압 기기의 적용 시 주의 가 필요하다. 그 이유는 이러한 팬의 영향으로 케이싱 일부에 음압을 생길 수 있고 가압이 중단 15 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
6bf1a515-a27a-4d64-b571-4bbaf8e714eb | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 되면 가스 또는 분진이 유입될 위험이 있기 때문이다(그림 C.3 참조). 다양한 시스템과 덕트 내부의 압력 분포가 그림 C.1 에서 그림 C.4 에 예시되어 있다. 관련 덕트 및 압축기 또는 팬의 설치로 인해 위험이 발생하지 않아야 한다. 덕트 시스템 설치에 대 한 기본 요구사항은 부속서 D 에 있다. 7.13 복수 용기의 가압(Pressurizing multiple enclosures) 하나의 보호가스 공급원을 여러 개의 개별 가압용기에 공통으로 사용할 경우, 결과 적인 제어 기능이 용기 그룹의 가장 불리한 구성을 고려한 경우라면 안전장치(들)를 이들 용기에 공통적으로 사용할 수 있다. 공용 안전장치를 설치했을 때, 다음 세 가지 조건이 충족되는 경우 문 또는 덮개의 열림으로 인해 모든 가압용기 내부의 전기기기 전원을 차단하거나 경보를 작동시킬 필요는 없다. a) 보호등급 "pxb"의 경우, 7.15 에서 허용하는 경우를 제외하고 문 또는 덮개의 개방 전에 해당 특정 가압용기의 전기기기 전원 공급을 차단하여야 한다. b) 공용 안전장치는 그룹의 다른 모든 가압용기 내의 양압 및 필요한 경우 유량을 지속적으로 감시 하여야 한다. c) 특정 가압용기의 전기기기에 전원을 다시 공급하기 전에 7.7 에 명시된 퍼지 절차를 실시하여야 한다. 7.14 문 및 덮개의 안전장치(Safety devices on doors and covers) 보호등급 "pxb"의 경우, 공구나 키를 사용하지 않고 열 수 있는 문 및 덮개는 개방되었을 때 7.15 에 명시되지 않은 전기기기의 전원이 자동적으로 차단되도록 연동(interlocked)되어야 하며 문과 덮개가 닫히기 전까지는 전원이 복구되어서는 안 된다. 7.7 의 요구사항 또한 적용되어야 한다. 7.15 통전 상태를 유지할 수 있는 기기(Equipment that may remain energized) 그룹 I 또는 그룹 II 가압용기의 경우, 보호수준 "pxb" 또는 보호수준 "pyb"이 작동하지 않을 때 통전 상태를 유지할 수 있는 전기기기는 그룹 I 에 대해서는 EPL Ma 또는 Mb 및 그룹 II 에 대해서는 EPL Ga 또는 Gb 로 보호되어야 한다. 그룹 II 가압용기의 경우, 보호수준 "pzc"가 작동하지 않을 때 통전 상태를 유지할 수 있는 전기기기 는 EPL Ga, Gb 또는 Gc 로 보호되어야 한다. 그룹 III 가압용기의 경우, 보호수준 "pxb"가 작동하지 않을 때 통전 상태를 유지할 수 있는 전기기기 는 EPL Da 또는 Db 로 보호되어야 한다. 그룹 III 가압용기의 경우, 보호수준 "pzc"가 작동하지 않을 때 통전 상태를 유지할 수 있는 전기기기 는 EPL Da, Db 또는 Dc 로 보호되어야 한다. 7.16 보호등급 "pyb"에서 허용되는 기기(Equipment permitted within Level of Protection "pyb") 보호등급 "pyb"의 가압용기 내부에 허용되는 전기기기는 그룹 II 에 대해서는 EPL Ga, Gb 또는 Gc 로 보호되어야 한다. 보호등급 "pyb"의 가압용기 내부에 허용되는 전기기기는 그룹 III 에 대해서는 EPL Da, Db 또는 Dc 로 보호되어야 한다. 8 정적가압을 위한 안전 대책 및 안전장치(Safety provisions and safety devices for 16 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
3c9ad9c1-cfa2-461e-a00b-db7e1db0313d | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 staticpressurization) 8.1 폭발위험장소에 대한 안전장치의 적합성(Suitability of safety devices for hazardous area) 정적가압에 의해 보호되는 전기기기의 폭발을 방지하기 위해 사용되는 모든 안전장치는 그 자체가 폭발을 일으킬 수 없어야 하며, 안전장치가 전기로 작동되는 것이라면 KS C IEC 60079-0 에 명시된 적용에 적합한 방폭구조 중 하나에 의해 보호되거나 폭발위험장소 밖에 설치되어야 한다. 8.2 보호가스(Protective gas) 보호가스는 불활성이어야 한다. 8.3 내부 누출원(Internal sources of release) 내부 누출원은 허용되지 않는다. 8.4 그룹 I 및 그룹 II 충전 절차(Group I and Group II Filling procedure) 사용설명서는 가압용기를 제조자가 규정한 절차에 따라 비폭발위험장소에서 불활성 가스로 충전해야 한다는 사항을 명시하여야 한다. 8.5 그룹 III 충전 절차(Group III Filling Procedure) 사용설명서는 가압용기 내부에 가연성 분진이 축적되지 않도록 필요에 따라 가압용기를 청소하여야 함을 명시하여야 한다. 사용설명서는 청소후에 가압용기를 제조자가 규정한 절차에 따라 비폭발위험 장소에서 불활성 가스로 충전해야 한다는 사항을 명시하여야 한다. 8.6 안전장치(Safety devices) 양압이 제조자가 정한 최소값 미만으로 떨어지는 경우, 보호등급 "pxb" 또는 "pyb"는 두 개의 자동안 전장치가 또는 보호등급 "pzc"는 한 개의 자동 안전장치가 작동하도록 설치하여야 한다. 기기가 사용 중일 때 안전장치가 올바르게 작동하는지 점검할 수 있어야 한다. 자동 안전장치는 공구나 열쇠를 사용해서만 재설정할 수 있어야 한다. 비고 자동 안전장치가 사용되는 용도(즉, 전원을 차단하거나 경보를 울리거나 또는 설치의 안전성 보장)는 일반적으로 사용자의 책임이다. 8.7 통전 상태를 유지할 수 있는 기기(Equipment that may remain energized) 압력 방폭구조 "p"가 동작하고 있지 않을 때 통전될 수 있는 가압용기 내의 전기기기는 7.15 에서 명 시된 EPL 을 가져야 한다. 8.8 양압(Overpressure) 최소 양압은 KS C IEC 60079-0 의 개방 시간 요구사항에 따라 내부 부품의 냉각에 필요한 시간의 100 배 이상의 시간(최소 1 시간) 동안 정상 작동 중에 측정된 최대 압력 손실보다 커야 한다. 양압의 최 소 값은 정상 작동 중의 명시된 가장 불리한 조건 하에서 외부 압력보다 50 Pa 이상 높아야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 17 | {}
48b89fb8-fcf0-49bc-b987-86482dfafa72 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 9 보호가스의 공급(Supply of protective gas) 9.1 보조 공급장치(Backup supply) 1 차 공급장치의 고장 시 보호가스의 보조 공급이 필요한 경우, 각 공급장치는 요구되는 보호가스의 압력 또는 공급 유량을 독립적으로 유지할 수 있어야 한다. 두 공급원은 공통의 배관 및 덕트를 사 용할 수 있다. 비고 보조 공급장치는 전기기기의 작동을 유지하기 위해 그것이 필요한 경우 사용하는 것을 권장한다. 9.2 독립적인 공급(Independent supplies) 점화가능기기의 용기가 보호등급 "pzc"의 가압용기로 보호되고, 이 용기가 보호등급 "pyb"의 가압용 기 내부에 위치하는 경우, 보호가스는 독립적으로 공급되어야 한다. 9.3 가스의 종류(Type of gas) 보호가스는 비인화성이어야 한다. 사용설명서는 보호가스 및 허용되는 대체 보호가스를 명시하여야 한다. 일반 산업용 품질의 공기나 질소 외 다른 보호가스가 명시되었을 경우, 보호가스는 그 화학적 특성이나 포함될 수 있는 불순물 로 인해 압력방폭구조 "p"의 성능을 감소시키거나 용기 내부 기기의 작동 및 성능에 악영향을 미치지 않아야 한다. 불활성 가스를 사용할 경우, 질식 위험이 있다. 따라서 경고를 용기에 부착하여야 한다(18.9 참조). 문이나 덮개를 열기 전에 불활성 가스를 제거하기 위해 용기를 퍼지하는 적절한 수단을 제공하는 것 을 고려하여야 한다. 9.4 온도(Temperature) 보호가스의 온도는 용기의 유입구에서 보통 40 °C 를 넘지 않아야 한다. 특별한 경우 높은 온도가 허 용되거나 더 낮은 온도가 필요할 수 있으며, 이러한 경우 용기에 온도를 표시하여야 한다. 10 내부 누출원이 있는 가압용기(Pressurized equipment with an internal source o f release) 누출 조건, 컨테인먼트 시스템의 설계 요구사항, 적합한 가압 방법 및 점화가능기기와 내부 고온 표 면에 대한 제한 사항은 11 절부터 15 절에 기술되어 있다. 11 누출 조건(Release conditions) 11.1 누출 없음(No release) 11.1.1 컨테인먼트 시스템이 무고장(infallible)일 경우에는 내부 누출이 없다(12.2 참조). 11.1.2 컨테인먼트 시스템 내부의 인화성 물질이 명시된 온도 한계 내에서 작동할 때 가스 또는 증 기 단계(phase)에 있고 다음 중 하나에 해당하는 경우에는 내부 누출이 없는 것으로 간주한다. a) 컨테인먼트 시스템 내의 가스 혼합물이 항상 인화하한(LFL)보다 낮다. 18 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
3548d53d-20c9-464c-9e69-7a3bc92e0436 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 b) 가압용기에 대해 명시된 최소 압력이 컨테인먼트 시스템에 대해 명시된 최대 압력보다 최소 50 Pa 높 고, 압력 차가 50 Pa 아래로 떨어지면 작동하는 자동 안전장치가 설치되어 있다. 비고 자동 안전장치의 신호가 사용되는 용도(즉, 전원을 차단하거나 경보음을 울리거나 또는 설치의 안전성 보장)는 일반적으로 사용자의 책임이다. KS C IEC 60079-0 의 표시 요구사항에 따라 인증번호에 "X" 접미사를 표시하여야 하며 인증서 상의 특정사용조건에는 사용자가 안전한 사용을 보장하기 위해 요구되는 필요한 정보를 상세히 기술하여 야 한다. 11.2 가스 또는 증기의 제한적 누출(Limited release of a gas or vapour) 인화성 물질의 가압용기로의 누출률(rate of release)은 컨테인먼트 시스템의 모든 고장 조건에서 예측 가능하여야 한다(12.3 참조). 이 표준의 목적상, 액화 가스 누출은 가스 누출로 간주한다. 11.3 액체의 제한적 누출(Limited release of a liquid) 인화성 물질의 가압용기로의 누출률은 11.2 와 같이 제한되지만, 액체의 인화성 증기로의 전환은 예측 할 수 없다. 가압용기 내에 액체가 축적될 가능성과 그에 따른 결과 를 고려하여야 한다. 액체에서 산소가 방출될 수 있다면 산소의 최대 누출량을 예측하여야 한다(13.2.2 참조). 12 컨테인먼트 시스템의 설계 요구사항(Design requirements for the containment system) 12.1 일반 설계 요구사항(General design requirements) 누설의 발생 여부를 결정하는 컨테인먼트 시스템의 설계와 구조는 제조자가 명시한 가장 불리한 사 용 조건을 기준으로 하여야 한다. 컨테인먼트 시스템은 무고장이거나 고장 발생 시 누출이 제한적이어야 한다. 인화성 물질이 액체인 경우에는 정상 누출(normal release)이 없어야 하며(부속서 E 참조) 보호가스는 불활성이어야 한다. 비고 보호가스는 방출된 증기가 보호가스의 희석 능력을 초과 하는 것을 방지하기 위하여 불활성이어 야 한다. 제조자는 컨테인먼트 시스템의 최대 유입구 압력(inlet pressure)을 명시해야 한다. 컨테인먼트 시스템의 설계 및 구조의 세부 사항, 컨테인먼트 시스템 내부의 인화성 물질의 종류 및 작동 조건 그리고 주어진 위치에서 예상되는 누출률은 컨테인먼트 시스템이 무고장 컨테인먼트 시스 템(12.2)인지 또는 제한적 누출이 있는 컨테인먼트 시스템(12.3)인지 분류하기 위해서 제조자가 제공 하여야 한다. 12.2 무고장 컨테인먼트 시스템(Infallible containment system) 무고장 컨테인먼트 시스템은 가동 접합부(moving joints)가 없는 금속, 세라믹 또는 유리, 배관, 튜브 또는 용기(vessels)로 구성되어야 한다. 접합부는 용접, 브레이징, 유리 대 금속 밀봉 또는 공정 방법 (eutectic methods)1)으로 이루어져야 한다. 1) 접합하고자 하는 각 부품의 응고 시작점보다 낮은 일정 온도에서 응고하는 이원합금계 또는 삼원합금계 (binary or ternary alloy system)를 사용하는, 보통 금속성인 둘 이상의 부품을 접합하는 기술 19 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
baf87b22-dcda-4896-a903-d554fdecd020 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 납/주석 복합 재료와 같은 저온 솔더(solder) 합금은 허용되지 않는다. 제조자는 불리한 작동 조건으로 잠재적으로 깨지기 쉬운 컨테인먼트 시스템의 손상을 신중하게 고려 하여야 한다. 사용설명서는 진동, 열충격 및 용기의 문 또는 덮개가 열려 있을 때의 유지보수 작업과 같은 제조자와 사용자 사이에 합의 된 조건에 대한 손상 위험을 감소시키기 위한 적절한 지침을 제공 하여야 한다. 12.3 제한적 누출이 있는 컨테인먼트 시스템(Containment system with a limited release) 제한적 누출이 있는 컨테인먼트 시스템의 설계는 컨테인먼트 시스템 고장의 모든 조건에서 인화성 물질의 누출률이 예측 가능하도록 하여야 한다. 가압용기로 누출되는 인화성 물질의 양은 컨테인먼 트 시스템 내부의 인화성 물질의 양과 공정으로부터 컨테인먼트 시스템으로 유입되는 인화성 물질의 유량을 포함한다. 유량은 가압용기 외부에 설치된 적절한 유량 제한장치(flow limiting devices)에 의해 예측 가능한 속도로 제한되어야 한다. 그러나 가압용기의 유입부에서 유량 제한장치의 유입부를 포함한 유입부까지 이어지는 컨테인먼트 시스템의 부분이 12.2 의 요구사항을 만족한다면, 유량 제한장치를 가압용기 내부에 설치할 수 있으며, 이 경우 유량 제한장치는 영구적으로 고정되어야 하며 움직일 수 있는 부분이 없어야 한다. 컨테인먼트 시스템에서 가압용기로의 최대 누출률을 예측할 수 있다면, 컨테인먼트 시스템으로 들어 가는 공정 유량을 제한할 필요가 없다. 이 조건은 다음과 같은 경우 충족될 수 있다. a) 컨테인먼트 시스템이 개별적으로 12.2 의 요구사항을 만족시키는 연결 부품(connected parts)으로 구성되고 이 부품 간의 접합부가 최대 누출량을 예측할 수 있도록 구성되고 영구적으로 고정된 경우 b) 컨테인먼트 시스템이 정상 작동 중에 방출(예: 불꽃)을 목적으로하는 오리피스 또는 노즐을 포함 하지만 12.2 의 요구사항을 충족하는 경우 유량 제한장치가 기기의 일부로 포함되지 않은 경우, 인증번호는 KS C IEC 60079-0 의 표시 요구사항 에 따라 "X" 접미사를 포함하여야 하며 인증서의 특정사용조건에 인화성 물질의 컨테인먼트 시스템 으로의 최대 압력 및 유량을 포함하여 사용자가 이 표준의 요구사항을 준수하는 데 필요한 정보를 상세히 기술하여야 한다. 불꽃을 포함하고 있는 가압용기는 불꽃이 꺼져있다고 가정하고 평가하여야 한다. 불꽃에 공급되는 연료/공기 혼합물의 최대량을 컨테인먼트 시스템에서 누출되는 양에 추가해야 한다. 컨테인먼트 시스템의 엘라스토머 실(elastomeric seals), 창 및 기타 비금속 부품은 허용된다. 배관용 나사, 압축 접합부(예: 금속 압축 피팅) 및 플랜지형 접합부도 허용된다. 13 내부 누출원이 있는 경우 보호가스 및 가압 방법(Protective gas and pressurizing t echniques when there is an internal source of release) 13.1 일반사항(General) 보호가스 선택은 컨테인먼트 시스템에서 누출이 발생할 가능성, 누출량 및 성분에 의존한다. 허용되 는 보호가스의 도표는 표 4 를 참조한다. 20 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
0971e4ba-4c75-4e26-9358-2c7c0eda783c | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 표 4- 컨테인먼트 시스템이 있는 가압용기에 대한 보호가스 요구사항 ¦ 내부 누출(부속서 E 참조) ¦ 내부 누출(부속서 E 참조) ¦ 내부 누출(부속서 E 참조) ¦ 내부 누출(부속서 E 참조) ¦ 연속희석 ¦ 연속희석 ¦ 누설보상 ¦ 누설보상 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 물질 ¦ 정상 ¦ 비정상 ¦ 부속서 ¦ UFL<80 % ¦ UFL>80% ¦ UFL<80 % ¦ UFL>80% ¦ ¦ 가스 또는 액체 ¦ 없음 ¦ 없음 ¦ E.2 ¦ 적용하지 않음 ¦ 적용하지 않음 ¦ 적용하지 않음 ¦ 적용하지 않음 ¦ ¦ 가스 ¦ 없음 ¦ 제한 ¦ E.3 ¦ 공기 또는 불활성 ¦ 공기 ¦ 불활성 ¦ <불가> ¦ ¦ 가스 ¦ 제한 ¦ 제한 ¦ E.4 ¦ 공기 또는 불활성 ¦ 공기 ¦ <불가> ¦ <불가> ¦ ¦ 액체 ¦ 없음 ¦ 제한 ¦ E.3 ¦ 불활성 ¦ <불가> ¦ 불활성 ¦ <불가> ¦ ¦ 액체 ¦ 제한 ¦ 제한 ¦ E.4 ¦ <불가> ¦ <불가> ¦ <불가> ¦ <불가> ¦ ¦ <불가> 가압 방법이 허용되지 않음을 의미 ¦ <불가> 가압 방법이 허용되지 않음을 의미 ¦ <불가> 가압 방법이 허용되지 않음을 의미 ¦ <불가> 가압 방법이 허용되지 않음을 의미 ¦ <불가> 가압 방법이 허용되지 않음을 의미 ¦ <불가> 가압 방법이 허용되지 않음을 의미 ¦ <불가> 가압 방법이 허용되지 않음을 의미 ¦ <불가> 가압 방법이 허용되지 않음을 의미 ¦ 제한적 누출의 컨테인먼트 시스템이 있는 가압용기의 설계는 잠재적 점화원(즉, 희석지역 밖에 있는) 에서 폭발성 가스 분위기가 형성되지 않도록 하여야 한다. 부속서 F 에는 잠재적 점화원이 희석지역 밖에 있음을 보장하기 위해 내부 칸막이가 어떻게 사용될 수 있는지에 대한 예를 제공한다. 불활성 가스를 보호가스로 사용하는 경우에는 가압용기에 18.9 에 따라 표시하여야 한다. 적용 가능한 가압 방법은 다음과 같은 누출 조건 및 누출 성분에 달려 있다. 13.2 누설보상식 가압(Pressurization with leakage compensation) 13.2.1 누출 없음(No release) 보호가스는 공기 또는 불활성 가스이어야 한다. 13.2.2 가스 또는 액체의 제한적 누출(Limited release of a gas or liquid) 보호가스는 불활성 가스로 하여야 한다. 인화성 물질의 산소 농도는 2 %(V/V)를 초과 하지 않아야 한다. 인화성 물질의 정상누출(normal release)은 없어야 한다(부속서 E 참조). 인화성 물질의 인화상한(UFL)은 80 %를 초과 하지 않아야 한다. 비고 인화성 물질이 산소가 거의 없거나 또는 전혀 없이도 반응할 수 있다면(즉, 인화성 물질의 UEL 이 80 %보다 크다는 의미) 불활성 가스를 사용한 누설보상식으로는 보호가 어렵거나 불가 능하다. 13.3 희석식 가압(Pressurization with dilution) 13.3.1 일반사항(General) 인화성 물질의 UFL 이 80 %를 초과 하거나, 산소 농도가 2 %(V/V)를 초과 하거나, 인화성 물질의 정상 누출이 있는 경우(부속서 E 참조)에는 연속흐름(continuous flow)을 사용해서 인화성 물질을 희석시켜 야 한다. 21 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
0114cb03-13bb-4f39-a8e5-5b59b1f697c2 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 13.3.2 누출 없음(No release) 보호가스는 공기 또는 불활성 가스로 하여야 한다. 13.3.3 가스 또는 증기의 제한적 누출(Limited release of a gas or vapour) 퍼지 후에 보호가스의 유량은 모든 컨테인먼트 시스템 고장조건 하에서 다음과 같이 희석지역 밖에 있는 잠재적인 점화원에서의 최대 누출을 희석시키기에 충분하여야 한다. a) 보호가스가 공기일 경우, 누출되는 인화성 물질의 농도가 LFL 의 25 %를 초과 하지 않도록 희석시 켜야 한다. b) 보호가스가 불활성 가스일 경우, 누출물의 산소 농도가 2 %(V/V)를 초과 하지 않도록 희석시켜야 한다. 컨테인먼트 시스템에서 누출되는 인화성 물질의 UFL 이 80 %보다 큰 경우, 인화성 물질의 농도가 LFL 의 25 %를 초과 하지 않도록 공기로 희석시켜야 한다. 비고 인화성 물질이 산소가 거의 없거나 또는 전혀 없이도 반응할 수 있다면(즉, 인화성 물질의 UEL 이 80 %보다 크다는 의미) LFL 의 25 %까지 희석시킬 필요가 있다. 13.3.4 액체의 제한적 누출(Limited release of a liquid) 보호가스는 불활성 가스이어야 하고 13.3.3 b)의 규정을 준수해야 한다. 인화성 물질의 정상누출(부속 서 E 참조)이 없어야 한다. 14 점화가능기기(Ignition-capable equipment) 희석지역 내에 있는 전기기기는 표 5 에 제시된 보호등급으로 보호되어야 한다. 이 요구사항은 화염 (flames), 점화장치(igniters) 또는 기타 화염을 점화하기 위한 유사한 기기에는 적용하지 않는다. 화염 이 발산되는 희석지역(the dilution area emanating from the flame)은 다른 희석지역과 겹쳐서는 안 된다. 표 5- 가압용기의 보호등급에 따른 희석지역 내에 허용되는 기기보호등급 ¦ 내부 누출 ¦ 보호등급 "pxb" 및 보호등급"pyb" ¦ 보호등급 "pzc" ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 비정상 ¦ Ga 또는 Gb ¦ Ga, Gb 또는 Gc ¦ ¦ 정상 ¦ Ga ¦ Ga ¦ 일반적으로 내부 누출원은 누출된 인화성 가스가 점화가능기기를 지나지 않고 가압용기에서 가장 짧 은 경로로 빠져나갈 수 있도록 배출구 근처에 있어야 하고 점화가능기기는 보호가스의 유입구 근처 에 있도록 한다. 비고 컨테인먼트 시스템 내부의 점화원으로부터 설비(plant)로 다시 점화하는 것을 방지하기 위해 화염방지기(flame arrestor)를 사용해야 할 수도 있다. 이러한 조치에 대해서는 이 표준에서 다 루지 않는다. 15 내부 고온표면(Internal hot surfaces) 가압용기 내부에 컨테인먼트 시스템에서 잠재적으로 누출 가능한 인화성 물질의 발화 온도를 초과 하 는 온도를 가진 표면이 있는 경우, 자동 안전장치를 제공하여야 한다. 11.1.2 b)에 명시한 안전장치의 22 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
43208628-22e3-4c9e-90a8-f641424466a0 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 작동(operation)에 따른 안전장치의 작용(action)은 표 3 에 나타나 있다. 추가로 다음 요구사항 중 하나를 만족시켜야 한다. a) 보호가스가 공기일 경우, 컨테인먼트 시스템에 남아 있는 인화성 물질의 누출이 고온표면 부근에 서 LFL 의 50 %보다 큰 농도를 형성해서는 안 된다. b) 보호가스가 불활성 가스일 경우, 가압용기 접합부의 설계 및 구조는 냉각 기간 동안 외부 공기와 내부 불화성 가스(또는 내부 인화성 가스나 증기)의 상당한 혼합을 방지 할 수 있어야 한다. 외부 공기의 유입은 산소 농도를 2 %(V/V)를 초과 하는 값으로 증가시키지 않아야 한다. 가압용기에는 다음과 같은 경고표시를 하여야 한다. 경고 - 전원을 차단한 후에 xxx 분 동안 문 또는 덮개를 열지 마시오. 여기에서 XXX 에 필요한 지연 시간을 분으로 나타낸다. 이 지연 시간은 고온표면이 컨테인먼트 시스템에서 누출된 인화성 물질의 발화온도 미만 또는 가압 용기의 온도 등급 아래로 냉각되는 데 걸리는 시간보다 길어야 한다. 16 형식 검증 및 시험(Type verification and tests) 16.1 최대 양압 정격의 결정(Determining the maximum overpressure rating) 용기의 최대 양압 정격은 제조자의 사용설명서에 따라 운전했을 때 발생하는 가장 높은 내부 작동 압력이다. 비고 최대 양압은 일반적으로 용기를 퍼지할 때 발생한다. 측정된 내압은 명시된 용기의 최대 정격 내압을 초과 하지 않아야 한다. 16.2 최대 양압시험(Maximum overpressure test) 16.1 에 의해 결정된 최대 양압의 1.5 배에 해당하는 압력 또는 200 Pa 중 더 높은 압력을 가압용기 및 가압용기와 일체형으로 연결된 관련 덕트와 접속부에 가하여야 한다. 시험 압력은 2 분 土 10 초 동안 가하여야 한다. 방폭구조의 성능에 영향을 미칠 수 있는 영구 변형이 발생하지 않으면 시험은 만족스러운 것으로 간 주한다. 16.3 누설시험(Leakage test) 16.3.1 정적가압 이외의 경우(Other than static pressurization) 가압용기의 압력을 제조자가 정상 사용(normal service) 중에 대해 명시한 최대 양압으로 조정한다. 배출구를 닫은 상태에서 유입구에서 누설 유량(leakage flow rate)을 측정하여야 한다. 더 높은 유량으로 용기를 퍼지하기 위해 벤트(vent)를 열 때 필요한 양압은 정상 사용 조건에 해당하 지 않는다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 23 | {}
7254b304-a518-4918-9718-b6481ca8a630 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 측정된 유량은 제조자가 명시한 최대 누설율보다 크지 않아야 한다. 16.3.2 정적가압(Static pressurization) 가압용기의 압력을 정상 사용 중에 발생할 수 있는 최대 양압으로 조정한다. 개방구를 막은 상태에 서 8.8 에 따라 일정 기간 동안 내부 압력을 모니터링한다. 압력은 최소 양압 미만으로 떨어지지 않아 야 한다. 16.4 내부 누출원이 없는 가압용기의 퍼지 시험 및 정적가압의 충전 절차 시험(Purging test for pressurized enclosures with no internal source of release and filling procedure test for static pressurization) 16.4.1 일반사항(General) 이 시험은 누설보상식 이든 아니든(즉, 연속흐름식) 적용한다. 16.4.2 공기를 보호가스로 사용하는 가압용기(Pressurized enclosure where the protective gas is air) 가압용기를 부속서 A 에 기술된 시험을 위해 준비한다. 가압용기를 모든 지점에서 농도가 70 % 이상 이 되도록 시험가스를 채워야 한다. 가압용기가 충전되면 바로 시험가스 공급을 중단하고 제조자가 명시한 최소 퍼지유량으로 공기를 공급하여야 한다. 어떠한 측정점(sample point)에서도 시험가스 농 도가 A.2 에서 규정한 값을 초과 하지 않을 때까지 걸리는 시간을 측정하고, 이 시간을 퍼지시간으로 기록하여야 한다. 두 번째 시험을 실시하여야 할 경우, 밀도 범위의 다른 쪽 끝을 대표하는 두 번째 시험가스를 가압 용기의 모든 지점에서 농도가 70% 이상이 되도록 채우고 두 번째 시험에 대한 퍼지시간을 측정하 여야 한다. 제조자가 명시한 최소 퍼지시간은 측정된 퍼지시간 또는 2 회의 시험을 실시한 경우에는 측정한 두 퍼지시간 중에 긴 시간보다 길어야 한다. 16.4.3 불활성 가스를 보호가스로 사용하는 가압용기(Pressurized enclosure where the protective gas is inert) 가압용기를 부속서 A 에 기술된 시험을 위해 준비한다. 용기는 초기에 정상 대기압에서 공기로 채워 야 한다. 그런 다음 제조자가 지정한 불활성 가스로 퍼지시켜야 한다. 어떠한 측정점에서도 산소 농도가 A.3 에서 규정한 값을 초과 하지 않을 때까지 걸리는 시간을 측정하 고, 이 시간을 퍼지시간으로 기록하여야 한다. 제조자가 명시한 최소 퍼지시간은 측정된 퍼지시간 이상이어야 한다. 16.4.4 공기 또는 밀도가 공기밀도의 ±10 %인 불활성 가스를 보호가스로 사용하는 가압용기 (Pressurized enclosure where the protective gas may be either air or an inert gas with a density equal to air ±10 %) 공기와 불활성 가스가 동일한 퍼지시간을 갖는 대체 보호가스로 허용되는 경우, 퍼지시간은 16.4.2 에 서 정한 방법대로 측정하여야 한다. 16.4.5 정적가압으로 보호되는 가압용기의 충전 절차 시험(Filling procedure test for a pressurized enclosure protected by static pressurization) 24 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
3a4e35c3-3bb4-403b-8ff4-0b6dbad99759 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 정적가압의 경우, 용기를 초기에 정상 대기압에서 공기로 채운다. 그다음, 제조자 사양에 따라 용기 에 불활성 가스를 채워야 한다. 그런 다음, 대기조건 기준 산소 농도 1 %(V/V)를 초과 하는 측정점이 없는지를 확인하여야 한다. 16.5 내부 누출원이 있는 가압용기의 퍼지 및 희석 시험(Purging and dilution tests for a pressurized enclosure with an internal source of release) 16.5.1 시험가스(Test gas) 시험가스의 선정 시에는 외부 가스 및 내부에서 방출되는 인화성 물질 모두를 고려하여야 한다. 16.5.2 인화성 물질의 산소 농도가 2 %(V/V) 미만이고 보호가스로 불활성 가스를 사용하는 가압 용기(Pressurized enclosure where the flammable substance has less than 2 %(V/V) oxygen and the protective gas is inert) 16.5.2.1 퍼지 시험(Purging test) 16.4.3 에 규정된 시험 절차에 따라 시험을 실시하여야 한다. 최소 퍼지유량은 컨테인먼트 시스템에서 누출되는 최대 누출량 이상이어야 한다. 제조자가 지정한 최소 퍼지시간은 측정된 퍼지시간의 1.5 배 이상이어야 한다. 퍼지 중에 컨테인먼트 시스템에서 누출될 수 있는 산소를 허용하기 위해 시험에서 확인된 퍼지시간 은 50 % 증가시킨다. 16.5.2.2 희석 시험(Dilution test) 인화성 물질이 2 %(V/V) 이상의 산소를 함유하고 있지 않기 때문에 희석 시험은 요구되지 않는다. 16.5.3 컨테인먼트 시스템의 산소 농도가 21 %(V/V) 미만이고 보호가스로 불활성 가스를 사용하는 연 속흐름식 가압용기(Pressurized enclosure with pressurization by continuous flow, containment system with less than 21 %(V/V) oxygen and the protective gas is inert) 16.5.3.1 퍼지 시험(Purging test) 용기를 공기로 채운다. 공기를 또한 누출부의 위치, 수량 및 특성과 희석지역 밖에 있는 잠재적인 점 화가능기기와 의 근접성 등을 고려하여 가장 불리한(onerous) 누출 조건을 대표하는 방식으로 최대 누출률에 상응하는 유량을 컨테인먼트 시스템을 통해 용기 안으로 주입하여야 한다. 그다음, 제조자가 지정한 최소 퍼지유량으로 보호가스를 공급한다. 어떠한 측정점에서도 산소 농도가 A.3 에서 규정한 값을 초과 하지 않을 때까지 걸리는 시간을 측정된 퍼지시간으로 기록하여야 한다. 제조자가 명시한 최소 퍼지시간은 측정된 퍼지시간 이상이어야 한다. 16.5.3.2 희석 시험(Dilution test) 16.5.3.1 에 명시된 퍼지 시험 직후 컨테인먼트 시스템에서 나오는 산소 유량을 16.5.3.1 에 명시된 유 량으로 유지하면서 보호가스 공급을 제조자가 지정한 최소 유량으로 조정한다. 25 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
fa781ae7-f543-40fe-8626-39f473072dbd | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 30 분 이상 측정한 산소 농도는 A.3 에 명시한 농도를 초과 하지 않아야 한다. 컨테인먼트 시스템 내의 산소와 동등한 양의 산소를 포함한 공기의 양을 12.3 에 따른 공기의 방출과 함께 컨테인먼트 시스템에서 가압용기로 방출시켜야 한다. 방출하는 동안, 잠재적인 점화가능기기 부근(즉, 희석지역 밖)의 산소 농도는 A.3 에 명시된 산소 농 도의 1.5 배를 초과 하지 않아야 하며 30 분 이내에 규정된 농도 이하로 감소되어야 한다. 비고 이 시험은 컨테인먼트 시스템의 치명적인 고장과 동등한 벌크 누출(bulk release)을 모의 시험 하기 위해 사용된다. 16.5.4 인화성 물질이 액체가 아니고, 보호가스로 공기를 사용하는 연속흐름 가압식 가압 용기 (Pressurized enclosure where the flammable substance is not a liquid, pressurization by continuous flow and the protective gas is air) 16.5.4.1 퍼지 시험(Purging test) 이 시험은 16.4.2 에 규정된 시험 절차에 따라 실시하여야 한다. 또한 시험 중에 시험가스를 누출부의 위치, 수량 및 특성과 희석지역 밖에 있는 잠재적인 점화가능 기기와 의 근접성 등을 고려하여 가장 불리한 누출 조건을 대표하는 방식으로 최대 누출률로 컨테인 먼트 시스템을 통해 가압용기 안으로 주입하여야 한다. 어떠한 측정점에서도 시험가스 농도가 A.2 에서 규정한 값을 초과 하지 않을 때까지 걸리는 시간을 측 정하여야 한다. 두 번째 시험이 요구되는 경우, 해당 시험은 두 번째 시험가스를 사용해 반복 실시하고 퍼지시간을 측정하여 기록하여야 한다. 제조자가 명시한 최소 퍼지시간은 측정된 퍼지시간 또는 2 회의 시험을 실시한 경우에는 측정한 두 퍼지시간 중에 긴 시간보다 길어야 한다. 16.5.4.2 희석 시험(Dilution test) 16.5.4.1 에 명시된 퍼지 시험 직후, 컨테인먼트 시스템에서 나오는 시험가스 유량을 16.5.3.1 에 명시 된 유량으로 유지하면서, 필요한 경우 보호가스 공급을 제조자가 지정한 최소 희석 유량으로 조정한다. 30 분 이상 동안 측정된 시험가스의 농도는 A.2 에 명시된 농도를 초과 하지 않아야 한다. 컨테인먼트 시스템 내의 인화성 가스의 체적과 동등한 양의 시험가스를 12.3 에 따른 인화성 가스의 방출에 상응하는 시험가스의 유량과 함께 컨테인먼트 시스템에서 가압용기로 방출시켜야 한다. 방출시키는 동안 잠재적인 점화가능기기 부근(즉, 희석지역 밖)의 시험가스 농도는 A.2 에 명시된 값 의 2 배를 초과 하지 않아야 하며 30 분 이내에 규정된 농도 이하로 감소되어야 한다. 두 번째 시험이 요구괴는 경우, 해당 시험은 두 번째 시험가스를 사용해 반복 실시해야 한다. 비고 이 시험은 컨테인먼트 시스템의 치명적인 고장과 동등한 벌크 누출(bulk release)을 모의 시험 하기 위해 사용된다. 26 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
6bf56b4d-5b63-47d5-a6e5-8d94d594e0d5 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 16.6 최소 양압의 검증(Verification of minimum overpressure) 가압시스템이 정상 사용 조건에서 7.12 를 준수하는 양압을 작동 및 유지할 수 있는지 확인하기 위한 시험을 실시하여야 한다. 용기 내에서 누설이 발생하기 쉬운 지점, 특히 최저 압력이 발생할 지점에서 압력을 측정하여야 한다. 보호가스를 최소 양압으로 가압용기에 공급하여야 하며, 필요한 경우 제조자가 명시한 최소 유량으 로 공급하여야 한다. 회전 전기기기의 경우, 시험은 기기를 정지 상태에서 및 최대 정격 속도로 운전 중에 모두 실시하여 야 한다. 16.7 무고장 컨테인먼트 시스템에 대한 시험(Tests for an infallible containment system) 16.7.1 양압시험(Overpressure test) 정상 사용 조건에 대해 지정한 최대 작동 압력의 최소 5 배의 시험 압력(최소 1 000 Pa)을 2 분 土 10 초 동안 컨테인먼트 시스템에 가한다. 컨테인먼트 시스템 정격 범위의 가장 불리한 온도 조건에서 시험 을 실시한다. 시험 압력을 5 초 이내에 최고 압력까지 올려야 한다. 이 시험은 영구 변형이 발생하지 않고 16.7.2 에 명시된 시험이 통과 되면 만족스러운 것으로 간주한다. 16.7.2 무고장 시험(Infallibility test) 컨테인먼트 시스템을 치환(flush)하고 순수 헬륨(95.0 % V/V 이상)으로 컨테인먼트 시스템의 최대 작 동 압력까지 가압하여야 한다. 그런 다음, 누설 여부를 확인하기 위하여 헬륨 누설 검출기(helium leak detector)를 사용하여야 한다. 누설이 감지되지 않는 경우, 시험은 만족스러운 것으로 간주한다. 비고 실내 측정 값보다 높은 값을 지시했을 때 누출로 간주한다. 16.8 제한적 누출이 있는 컨테인먼트 시스템에 대한 양압시험(Overpressure test for a containment system with a limited release) 비고 이 시험은 정상 작동 중에 제한적 누출이 있는 컨테인먼트 시스템에 대해서 실시한다. 정상 사용 조건에 대해 지정한 최대 내부 양압보다 최소 1.5 배 이상의 시험 압력(최소 200 Pa)을 컨 테인먼트 시스템에 가하고 2 분 土 10 초 동안 유지시킨다. 영구 변형이 발생하지 않으면 시험은 만족스 러운 것으로 간주한다. 17 일상시험(Routine tests) 17.1 기능시험(Functional test) 가압용기와 함께 제공되는 안전장치의 성능을 검증하여야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. 27 | {}
ec7ea25a-f636-4e4f-977a-20c255f7ef8f | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 17.2 누설시험(Leakage test) 보호가스의 누설시험을 16.3 에 따라 실시하여야 한다. 17.3 무고장 컨테인먼트 시스템 시험(Tests for an infallible containment system) 무고장 컨테인먼트 시스템은 16.7 에 따라 시험하여야 한다. 하지만 액체 시스템의 경우, 헬륨 누설시 험 대신에 양압시험 중 액체 누설을 확인하는 것이 적절하다. 17.4 제한적 누출이 있는 컨테인먼트 시스템에 대한 시험(Testfor a containment system with a limited release) 컨테인먼트 시스템을 16.8 에 따라 시험하여야 한다. 18 표시(Marking) 18.1 일반사항(General) KS C IEC 60079-0 의 요구사항에 추가하여 표시는 다음 사항을 포함하여야 한다. 이 표준에서 경고 표시를 하도록 규정한 경우, "경고" 다음에 오는 문구는 기술적으로 동등한 문구로 대체할 수 있다. 여러 경고를 동등한 하나의 경고로 결합할 수도 있다. 18.2 가압의 표시(Identifying as pressurized) 가압용기에는 "경고 - 압력방폭구조 용기(가압용기)" 표시를 하여야 한다. 18.3 추가 표시(Supplementary marking) 다음의 추가 정보도 적절하게 표시하여야 한다. a) 보호등급 "pxb", "pyb" 또는 "pzc" b) 다음 사항을 명시하여 용기를 퍼지하는 데 필요한 보호가스의 최소량 보호가스의 최소 퍼지유량 - 최소 퍼지시간 - 추가 덕트의 단위 체적당 최소 추가 퍼지시간(해당하는 경우) 비고 덕트의 퍼지를 보장하기 위해 보호가스의 양을 늘리는 것은 사용자의 책임이다. 보호등급 "pzc" 및 보호등급 "pyb"의 경우, 압력이 해당 유량의 올바른 지표가 되는 경우에는 유량 대신 최소 압력을 사용할 수 있다[7.8c) 참조]. c) 보호가스가 공기 이외의 가스일 경우, 보호가스의 종류 d) 최소 및 최대 양압 e) 보호가스의 최소 유량 f) 가압시스템에 대한 최소 및 최대 공급압력 g) 가압용기의 최대 누설률 h) 제조자가 지정한 경우, 가압용기의 유입구에서 보호가스 특정 온도 또는 온도 범위 i) 관련 문서에 명시되어 있지 않다면, 압력을 모니터링 할 지점(들) 18.4 내부 누출원(Internal source of release) 28 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
4c500ea3-7822-44a1-9d0d-b3bf51cf6895 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 해당하는 경우, 컨테인먼트 시스템이 있는 가압용기에는 다음 사항을 추가로 표시하여야 한다. a) 컨테인먼트 시스템의 유입구 최대 압력 b) 컨테인먼트 시스템으로의 최대 유량 c) 인화성 물질의 산소 농도가 2 %를 초과 하지 않아야 한다는 제한 d) 인화성 물질의 UFL 이 80 %를 넘지 않아야 한다는 제한 18.5 정적가압(Static pressurization) 정적가압으로 보호되는 가압용기에는 다음과 같은 표시를 하여야 한다. 경고 - 이 용기는 정적가압으로 보호되고 있음. 이 용기는 제조자 지침에 따라 비폭발 위험장소에서 충전하시오. 18.6 가압시스템(Pressurization systems) 별도의 인증서가 있는 가압시스템은 관련기기(associated pressurization equipment)로 표시된다. 별도의 인증서가 있는 가압시스템이 폭발위험장소에 설치되록 표시된 경우, "[p]"기호가 "Ex 표시"에 포함되어야 한다. 별도의 인증서가 있는 가압시스템이 비폭발 위험장소에만 설치되도록 표시된 경우, "Ex 표시"는 "[Exp]"로 표시된다. 비고 "[p]" 및 "[Exp]" 표시는 IEC 60079-0 의 제 6 판 또는 그 이전 판에는 나타나 있지 않다. 18.7 다른 조항에서 요구되는 경고(Warnings required in other clauses) 표 6 - 경고 표시 문구 ¦ 관련 조항 ¦ 권장 경고(유사 문구 허용됨) ¦ ¦ --- ¦ --- ¦ ¦ 5.3.6 ¦ 경고 - 폭발성 분위기가 존재하는 경우 열지 마시오. ¦ ¦ 7.8c) ¦ 경고 - 용기가 개방된 후 유량 에서 분간 퍼지될 때까지 전원을 투입하지 마 시오. ¦ ¦ 7.9 ¦ 경고 - 용기가 개방된 후 내부에 쌓인 가연성 분진이 제거되기 전까지 전원을 투입하지 마시오. ¦ ¦ 7.11 d) ¦ 경고 - 보호가스 공급 밸브 - 밸브를 잠그기 전에 사용설명서를 참조하시오. ¦ ¦ 15 절 ¦ 경고 - 전원을 차단한 후 xxx 분 동안 문 또는 덮개를 열지 마시오. ¦ ¦ G.7.1 ¦ 경고 - 용기 내에 배터리가 있음. 폭발성 분위기가 존재하는 경우 열지 마시오. ¦ ¦ G.7.2 ¦ 경고 - 이 가압용기는 외부 전원 차단 후에도 연결되어 있는 배터리가 포함되어 있음. 용기가 상당 시간 동안 압력방폭구조에 의해 보호되지 않을 경우 배터리를 제거해야 함. ¦ ¦ G.7.3 ¦ 경고 - 이 가압용기 내에 설치된 배터리는 정기적 점검이 필요함. 사용설명서 참조 ¦ ¦ H.3.1 ¦ 경고 - 용기 내에 배터리가 있음. 폭발 분위기가 존재할 경우 열지 마시오. ¦ ¦ H.3.2 ¦ 경고 - 이 가압용기에는 외부 전원 차단 후에도 연결되어 있는 배터리가 포함되어 있 음. 용기가 상당 시간 동안 압력방폭 구조에 의해 보호되지 않을 경우 배터리를 제거해 야 함. ¦ ¦ H.3.3 ¦ 경고 - 이 가압용기 내에 설치된 배터리는 정기적 점검이 필요함. 사용설명서 참조 ¦ 29 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
9c0b6b36-9f51-48b7-b712-666e6c87fcd0 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 18.8 사용자에 의한 양압 제한(Overpressure limited by user) 사용설명서에 따라 사용자가 압력을 제한하도록 요구되는 경우, 최대 작동 압력은 용기에 표시되어 야 한다. 사용설명서는 다음 중 하나의 요구사항을 포함하여야 한다. a) 사용자가 단일 고장 조건에서 용기의 최대 작동 압력을 초과 하지 않는 보호가스 공급장치를 설치 하여야 한다는 요구사항. 이 고장은 스스로 표시(self-revealing)되어야 한다. 보호 기능은 이중 압 력조절기(redundant regulator) 또는 최대 유량을 처리할 수 있는 외부 압력 방출 밸브(external pressure relief valve)를 사용한 것일 수 있다. b) 사용자가 보호가스 공급을 위해 압축 공기가 아닌 송풍 장치(blower system)만을 사용하여야 하다 는 요구사항 위 요구사항의 준수여부는 사용설명서와 표시를 검사하여 확인한다. 18.9 불활성 가스(Inert gas) 불활성 가스를 보호가스로 사용하는 가압용기에는 다음과 같은 표시를 하여야 한다. 경고 - 이 용기에는 불활성 가스가 들어 있어 질식 위험이 있음. 이 용기는 또한 공기에 노출되면 인화 한계에 달할 수 있는 가연성 물질도 들어 있음. 19 사용설명서(Instructions) KS C IEC 60079-0 에 의해 요구되는 사용설명서에 다음을 포함하여야 한다. 보호가스 및 허용되는 대체 보호가스는 명시되어야 한다. 그룹 III 기기를 위한 사용설명서에는 전원을 복구하기 전 적절한 방법으로 가연성 분진을 제거해야 할 필요성을 명시하여야 한다. 비고 가연성 분진을 제거하는 적절한 방법을 결정하는 것은 사용자의 책임이다. 부속서 D 는 가압과 관련된 사용자에게 제공하여야 하는 권고안을 제공한다. 30 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
0b697ed0-e2a7-491c-903e-074af3ab52a1 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 부속서 A (규정) 퍼지 및 희석 시험(Purging and dilution tests) A.1 일반사항(General) 가압용기의 내부 분위기는 시험가스가 가장 오래 존재할 가능성이 높다고 생각되는 지점 및 잠재적 인 점화가능기기(즉, 희석지역 밖에 있는) 주변의 지점에서 시험을 실시하여야 한다. 시험 지점에서의 가스농도는 시험하는 동안 지속적으로 분석 또는 측정되어야 한다. 예를 들어, 가압 용기에 다수의 작은 지름의 튜브를 장착하여 튜브의 개방 단부를 가압용기 내부의 측정 지점에 위치 시킨다. 시험이 샘플 채취로 이루어진 경우, 채취한 양이 시험에 큰 영향을 미치지 않아야 한다. 필요할 경우, 가압용기의 개방구는 퍼지 및 희석 시험을 할 때 다시 개방한다는 조건으로 가압용기 를 특정 시험가스로 채우기 위해 닫을 수 있다. 공기를 보호가스로 사용하는 경우, 시험방법은 다음과 같아야 한다. 특정 용도를 위해 필요할 경우, 시험은 특정 인화성 가스 및 증기에 대하여 실시할 수 있다. 이 경우 해당 인화성 가스(들)가 명시되어야 하며, 시험가스(들)는 그 밀도가 명시된 가스(들) 중 가 장 무거운 가스 및 가장 가벼운 가스의 밀도 ±10 % 이내의 밀도를 갖는 가스로 선택하여야 한다. 단일 특정 인화성 가스의 경우, 명시된 가스의 ±10% 이내의 밀도를 가진 하나의 시험가스로 시 험을 1 회 실시한다. 모든 인화성 가스를 커버(cover)해야 하는 경우, 시험을 2 회 실시하여야 한다. 첫 번째 시험은 공 기보다 가벼운 가스를 커버하기 위하여 헬륨을 시험가스로 사용해야 한다. 두 번째 시험은 공기 보다 무거운 가스를 커버하기 위하여 아르곤이나 이산화탄소를 시험가스로 사용해야 한다. 시험가스는 인화성과 독성이 없어야 한다. A.2 공기를 보호가스로 사용할 때의 판정 기준(Criteria for compliance where the protective gas is air) 퍼지 및 해당하는 경우, 희석을 한 후에 측정점에서 시험가스의 농도는 다음 값을 초과 하지 않아야 한다. 특정 인화성 가스들에 대해 시험(들)을 실시한 경우, 가장 불리한(onerous) LFL 의 25 %에 해당하 는 값 한 가지 특정 인화성 가스만을 커버하는 경우, 해당 가스의 LFL 의 25 %에 해당하는 값 모든 인화성 가스를 커버하는 경우, 헬륨 시험에서는 1%, 아르곤이나 이산화탄소 시험에서는 0.25 % 비고 이러한 값은 각각 가벼운 인화성 가스와 무거운 인화성 가스의 LFL 의 약 25 %에 해당한다. A.3 불활성 가스를 보호가스로 사용할 때의 판정 기준(Criteria for compliance whe re the protective gas is inert) 보호가스로 불활성 가스를 사용하는 경우, 퍼지 및 해당하는 경우 희석을 한 후에 산소 농도는 2 %(V/V)를 초과 하지 않아야 한다. 31 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c9c6854b-01b1-45ad-817b-861121804456 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 부속서 B (참고) 기능 순서도의 예(Examples of functional sequence diagram) 표 B.1 은 누설보상식 가압용기의 간단한 제어 시스템에 대해 제조자가 제공해야 할 정보의 예를 제 공한다. 표 B.1 - 누설보상식 퍼지 제어 시스템의 진리표 ¦ SO ¦ S1 ¦ S2 ¦ S3 ¦ MOP ¦ XOP ¦ PFLO ¦ PTIM ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ 1 ¦ 0 ¦ 1 ¦ ¦ 1 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ 1 ¦ ¦ 1 ¦ 0 ¦ 0 ¦ 0 ¦ 1 ¦ 1 ¦ 1 ¦ 0 ¦ ¦ 1 ¦ 0 ¦ 0 ¦ 0 ¦ 1 ¦ 1 ¦ 0 ¦ 1 ¦ ¦ 1 ¦ 0 ¦ 0 ¦ 0 ¦ 1 ¦ 1 ¦ 1 ¦ 1 ¦ ¦ 1 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ 1 ¦ 1 ¦ 1 ¦ ¦ 1 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ 1 ¦ 1 ¦ ¦ 1 ¦ 0 ¦ 0 ¦ 0 ¦ 1 ¦ 1 ¦ 0 ¦ 0 ¦ ¦ 1 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ 1 ¦ 0 ¦ 0 ¦ ¦ 1 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ ¦ 1 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ 1 ¦ 0 ¦ ¦ 1 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ 1 ¦ 1 ¦ 0 ¦ ¦ 0 ¦ 1 ¦ 0 ¦ 0 ¦ 1 ¦ 0 ¦ 0 ¦ 0 ¦ ¦ 0 ¦ 0 ¦ 1 ¦ 0 ¦ 1 ¦ 0 ¦ 1 ¦ 0 ¦ ¦ 0 ¦ 0 ¦ 0 ¦ 1 ¦ 1 ¦ 0 ¦ 0 ¦ 1 ¦ ¦ 0 ¦ 0 ¦ 0 ¦ 1 ¦ 1 ¦ 0 ¦ 1 ¦ 1 ¦ 그림 B.1 은 누설보상식 퍼지 제어 시스템의 상태도를 나타내고 있다. ![image](/image/placeholder) S1 S2 SO S3 IEC 그림 B.1 누설보상식 퍼지 제어 시스템의 상태도 32 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
4927d88e-ea3e-482d-8800-bfe6385847d8 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 ![image](/image/placeholder) 누설보상 논리 정의 최대 양압 값 초과=[XOP] 양압 > 50 Pa(보호등급 "pzc"의 경우, 25 Pa) = [MOP] 퍼지유량 > 최소 값 = [PFLO] 퍼지시간 미완료 = [PTIM] 퍼지시간 완료 = [PTIM] 초기 상태 = S0 [MOP] & [XOP] & [PFLO] & [PTIM] = S1, 퍼지를 시작하기 위한 최소 조건 [MOP] & [XOP] & [PFLO] & [PTIM] = S2, 퍼지 [MOP] & [XOP] & [PTIM] = S3, 퍼지 완료 후 전원공급 시스템의 각 상태는 모니터링 장치의 입력에 따라 정의 된다. 상태는 고유(unique)하다. 상태 간 전환 은 화살표로 정의 된 경로를 따라 화살표의 방향으로만 허용된다. 각 상태의 논리 조건은 불 논리식 (Boolean logical expressions)에 의해 고유하게 정의 된다. 가능한 모든 입력 조건 조합이 표에 나타나 있다. 모니터링 장치가 더 많은 다른 시스템도 각 작동 상태가 그 입력에 의해 고유하게 정의 된 경 우 이 방법으로 설명할 수 있다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 33 | {}
223523e7-c6de-4217-9f24-2da29494a802 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 부속서 C (참고) 덕트 및 용기의 압력 변화의 예 (Examples of the changes in pressure in ducts and enclosures) 그림 C.1 부터 그림 C.4 는 덕트 및 용기에서의 압력 변화의 예를 나타내고 있다. 비고 그림에서 팬을 사용해 양압이 유지되는 예가 나와 있다. 그러나 이는 압축 공기 실린더, 압축 기 등을 사용해 공기를 공급하는 것과 같은 다른 방법으로도 양압을 유지할 수 있다. 이러한 경우 용기 입구까지 다른 압력 저하가 발생한다. ![image](/image/placeholder) 2 3 2 4 2 5 9 Pa P1 50 0 11 10 식별부호 ¦ P1 ¦ 보호가스의 압력(덕트나 용기 내의 부품 해 결정됨.) ¦ 및 경우에 따라 초크를 통과 할 때 받는 흐름 저항에 의 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ 보호가스 유입구(비폭발 위험장소) ¦ 7 보호가스 배출구 ¦ ¦ 2 ¦ 덕트 ¦ 8 (이 도면 예에서는 사용하지 않음.) ¦ ¦ 3 ¦ 팬 ¦ 9 양압(overpressure) ¦ ¦ 4 ¦ 용기 ¦ 10 내부 압력 ¦ ¦ 5 ¦ 초크(choke)(양압 조절을 위해 필요한 경우) ¦ 11 외부 압력 ¦ ¦ 6 ¦ (이 도면 예에서는 사용하지 않음.) ¦ ¦ 그림 C.1 a) - 불꽃 및 입자 배리어가 없는 보호가스 배출구 그림 C.1 - 보호가스 배출구 34 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
033654c7-88be-47b6-a89e-3e39b350cb01 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 ![image](/image/placeholder) 2 3 2 4 2 5 8 H 9 Pa P1 10 50 0 11 식별부호 P1 보호가스의 압력(덕트나 용기 내의 부품 및 경우에 따라 초크, 불꽃 및 입자 배리어를 통과 할 때 받는 흐름 저항에 의해 결정됨.) 1 보호가스 유입구(비폭발 위험장소) 2 덕트 3 팬 4 용기 5 초크(양압 조절을 위해 필요한 경우) 6 (이 도면 예에서는 사용하지 않음.) 7 보호가스 배출구 8 불꽃 및 입자 배리어 9 양압 10 내부 압력 11 외부 압력 그림 C.1 b) - 불꽃 및 입자 배리어가 있는 보호가스 배출구 그림 C.1 - 보호가스 배출구(계속) 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 35 | {}
94e0614b-c852-454f-aea9-913d547a3bc5 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 ![image](/image/placeholder) 2 3 2 4 2 6 X 9 Pa P2 10 50 0 11 식별부호 P2 보호가스의 압력(거의 일정) 1 보호가스 유입구(비폭발 위험장소) 2 덕트 3 팬 4 용기 5 (이 도면 예에서는 사용하지 않음.) 6 배출구 밸브 7 보호가스 배출구 8 (이 도면 예에서는 사용하지 않음.) 9 양압 10 내부 압력 11 외부 압력 그림 C.2 - 누설보상식 가압용기, 가동부 없음 36 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f2d2ee7a-1734-4825-be3a-2f569443b127 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 ![image](/image/placeholder) 4 2 6 2 3 B 9 P3 Pa 10 50 0 B 11 식별부호 P3 보호가스의 압력(내부 부품의 흐름 저항에 따라 결정되며 내부 냉각 팬에 의해 A, B 및 C 사이 에 영향을 받음.) 1 3 ¦ ¦ 보호가스 유입구(비폭발 위험장소) 팬 용기 ¦ 7 보호가스 배출구 8 (이 도면 예에서는 사용하지 않음.) 9 양압 10 내부 압력 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 2 ¦ 덕트 (이 도면 예에서는 사용하지 않음.) ¦ ¦ ¦ 4 ¦ ¦ ¦ ¦ ¦ ¦ 11 ¦ ¦ 5 ¦ ¦ 외부 압력 ¦ ¦ 6 ¦ 배출구 밸브 ¦ ¦ 그림 C.3 - 누설보상식 가압용기, 내부 냉각 팬이 있는 회전 전기기기 누설이 발생할 수 있는 모든 지점에서의 압력은 보호등급 "pxb"에 대해 최소 50 Pa 이상이다. 내부 팬에 의해 순환이 보조되는 내부 밀폐 냉각 회로(internally enclosed cooling circuit)를 갖는 모터 에 가압을 할 때에는 주의 를 기울여야 한다. 그 이유는 이러한 팬의 효과 로 케이싱 일부에 부압을 발생시켜 외부 대기가 침입할 위험이 있기 때문이다. 내부 환기구가 있는 모터(internally ventilated motor)를 가압하고자 하는 경우에는 전동기 제조자에게 문의 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 37 | {}
02629a73-fa03-4e9b-a32a-e24f284b1616 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 ![image](/image/placeholder) 2 3 2 4 2 6 7 10 P4 Pa P5 Pa 0 250 11 식별부호 P4 보호가스의 압력(내부 부품의 흐름 저항 및 외부 공기 압의 최대 값에 따라 결정) P5 외부 공기의 압력, 외부 냉각 팬에 의해 발생 ¦ 1 ¦ 보호가스 유입구(비폭발 위험장소) ¦ 7 보호가스 배출구 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 2 ¦ 덕트 ¦ 8 (이 도면 예에서는 사용하지 않음.) ¦ ¦ 3 ¦ 팬 ¦ 9 (이 도면 예에서는 사용하지 않음.) ¦ ¦ 4 ¦ 용기 ¦ 10 내부 압력 ¦ ¦ 5 ¦ (이 도면 예에서는 사용하지 않음.) ¦ 11 외부 압력 ¦ ¦ 6 ¦ 배출구 밸브 ¦ ¦ 그림 C.4 - 누설보상식 가압용기, 외부 냉각 팬이 있는 회전 전기기기 38 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
31457a37-dd64-4913-a136-9874e86b4662 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 부속서 D (참고) 사용자에게 제공할 정보 (Information to be provided to the user) D.1 일반사항(General) 가압시스템을 정확히 설치하는 데 필요한 정보를 사용자에게 제공하는 것은 안전을 위해 반드시 필 요하다. 제조자가 적절하게 다루어야 하는 구체적인 현안은 D.2 부터 D.6 까지에 해당한다. D.2 보호가스 덕트(Ducting of protective gas) D.2.1 유입구 위치(Location of inlet) 실린더 공급식 및 일부 그룹 I 적용을 제외하고, 보호가스가 공급 덕트로 들어가는 지점은 비폭발 위 험장소에 위치해야 한다. 가압 소실 시, 비폭발 위험장소에서 폭발위험장소로의 인화성 가스 또는 가연성 분진의 이동을 최소 화할 수 있도록 고려해야 한다. 그룹 I 에서 보호가스가 폭발위험장소에서 공급 덕트로 유입되는 경우, 다음의 예방 조치를 취하여야 한다. a) 폭발성 갱내 가스(firedamp)의 농도가 폭발하한의 10 %를 초과 하는 경우, 자동으로 가압용기로 들어가는 전원을 차단하도록 팬이나 압축기의 배출 측에 두 개의 독립적인 가스감지기 설치해야 한다. b) 전원을 자동으로 차단하는 데 걸리는 시간은 보호가스가 검출 지점에서 가압용기에 도달하는 데 소요되는 시간의 1/2 이하로 하여야 한다. c) 전기가 자동 차단된 경우, 전기를 다시 공급하기 전에 가압용기를 다시 퍼지시킨다. 퍼지시간은 보호가스의 공급 지점에서 폭발성 갱내 가스의 농도가 인화하한의 10% 아래로 떨어질 때까지 시작하지 않아야 한다. D.2.2 가압용기와 유입구 사이의 덕트(Ducting between pressurized enclosure and inlet) 압축기로의 흡입 덕트는 일반적으로 폭발위험장소를 통과 해서는 안 된다. 압축기 흡입 배관이 폭발위험장소를 통과 하는 경우에는 불연성 물질로 구성되어야 하며 기계적 손상 및 부식으로부터 보호되어야 한다. 내부 압력이 외부 대기압보다 낮을 경우, 덕트에 누설이 없음을 보장하기 위한 적절한 예방 조치가 취해져야 한다(부속서 C 참조). 덕트에 인화성 농도의 가스 또는 증기가 없음을 확인하기 위하여 가 연성 가스 감지기와 같은 추가 보호 수단을 고려해야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 39 | {}
be4c3fe1-7063-4ce6-82cb-4cd1b72516ad | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 D.2.3 보호가스 배출구(Outlets for protective gas) 불꽃 및 입자 배리어가 제조자에 의해 제공되거나 사용자가 추가하지 않는 한, 보호가스를 배출하는 덕트의 배출구는 비폭발 위험장소에 설치하도록 한다. D.2.4 덕트를 고려한 추가 퍼지시간(Additional purge time to account for ducting) 퍼지 지속 시간은 기기에 포함되지 않은 관련 덕트 체적의 최소 5 배를 제조자가 지정한 최소 유량으 로 퍼지하는데 필요한 시간만큼을 증가시켜야 한다. D.2.5 유입구에서 보호가스의 온도(Temperature of protective gas at the inlet) 필요한 경우, 결로나 결빙을 피하기 위한 조치를 취해야 한다. D.3 보호가스 공급장치 전원(Power for protective gas supply) 보호가스 공급장치(예: 송풍기, 압축기 등)의 전력은 별도의 전원에서 공급받거나 아이솔레이터 (electrical isolator)(예: 단로기)의 1 차측에서 공급받아야 한다. D.4 정적가압(Static pressurization) 양압이 지정한 최소값 이하로 떨어지면 재충전하기 전에 용기를 비폭발 위험장소로 이동시켜야 한다. D.5 컨테인먼트 시스템이 있는 용기(Enclosures with a containment system) 컨테인먼트 시스템으로 들어가는 인화성 물질의 최대 압력과 유량은 제조자가 지정한 정격을 초과 하 지 않아야 한다. 컨테인먼트 시스템에 공기가 침투해 폭발성 혼합물이 생성될 가능성이 있는 경우, 추가적인 예방 조 치가 필요할 수 있다. 컨테인먼트 시스템을 손상시킬 수 있는 불리한 작동 조건을 방지하기 위한 적절한 예방 조치를 취하 여야 한다. 기술 문서에는 가압용기의 문이나 덮개를 열 때 생길 수 있는 진동, 열 충격 및 유지 보 수 작업과 같은 조건을 설명해야 한다. 예를 들어, 가연성 물질이 내부의 고온 표면에 의하여 점화될 수 있고 양압의 유지가 컨테인먼트 시 스템으로부터의 누출을 방지하기 위한 기능을 수행하고 있는 경우라면, 가연성 물질의 흐름을 차단 하기 위한 유량 스위치가 필요할 수 있다. 비정상 누출이 폭발위험장소 등급에 악영향을 미칠 수 있는 경우, 추가 예방 조치가 필요할 수 있다. 컨테인먼트 시스템으로 공기가 침투하여 폭발성 혼합물이 형성될 수 있는 가능성을 고려하여야 하며 이에 따른 추가적인 예방조치가 필요할 수 있다. D.6 용기 최대 양압(Enclosure maximum overpressure) 사용자는 제조자가 지정한 압력으로 제한하여야 한다. 40 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
943dc581-46db-41cb-85b9-bc57f245f3cd | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 부속서 E (규정) 용기 내부 누출 유형의 분류 (Classification of the type of release within enclosures) E.1 일반사항(General) 용기 내에서 인화성 물질의 누출 결과 는 대기에서(in free air)의 유사한 누출보다 더 심각하다. 용기 내에서 일시적인 누출은 누출이 멈춘 후에도 장시간 용기 내부에 남아 있는 인화성 물질을 생성한다. 이 때문에 개방된 대기에서의 누출보다 "정상 누출(normal release)" 및 "비정상 누출(abnormal release)"에 더 중점을 둘 필요가 있다. 모든 경우에, 컨테인먼트 시스템으로부터 가압용기로 인화성 물질의 흐름을 제한하기 위한 장치를 설치하여야 한다. 제한적인 누출만 허용된다. E.2 정상 누출 없음, 비정상 누출 없음(No normal release, no abnormal release) 컨테인먼트 시스템은 12.2 의 설계 요구사항과 무고장 컨테인먼트 시스템에 대한 16.7 의 시험 요구사 항을 만족해야 한다. E.3 정상 누출 없음, 제한적인 비정상 누출 있음(No normal release, limited abnormal r elease) 무고장 컨테인먼트 시스템에 관한 요구사항을 만족시키지 못하고 일상 유지보수 작업 중에 분리하지 않는 파이프용 나사, 용접, 공정 방법(eutectic methods) 또는 금속 압축 핏팅으로 만들어진 접합부가 있는 금속 파이프, 튜브 또는 부르동 튜브, 벨로우즈 또는 나선형 부품과 같은 엘리먼트로 구성된 컨 테인먼트 시스템은 정상 누출은 없으나 제한적인 비정상 누출은 있는 것으로 간주하여야 한다. 회전 또는 미끄럼 접합부, 플랜지 접합부, 탄성 중합체 밀봉 및 비금속 유연 튜브는 이 기준을 충족 하지 못한다. E.4 제한적 정상 누출(Limited normal release) "정상 누출 없음"의 요구사항을 만족시킬 수 없는 시스템은 제한적인 정상 누출이 있다고 간주하여야 한다. 여기에는 일상 유지보수(routine maintenance) 대상이 되는 접합부가 있는 컨테인먼트 시스템이 포함된다. 이러한 접합부는 명확하게 식별되어야 한다. 비금속 파이프, 튜브 또는 부르동 튜브, 벨로우즈, 다이어프램, 나선형 부품과 같은 엘리먼트, 탄성 중합체 밀봉, 회전 또는 미끄럼 접합부 등으로 구성되는 컨테인먼트 시스템은 정상 작동 중 누출원 으로 간주하여야 한다. 정상 작동 중에 화염이 있는 용기는 화염이 꺼진 상태에서 평가하여야 한다. 화염의 소화 현상은 정상 적으로 발생할 수 있는 것으로 가정하고, 화염이 꺼지는 경우 인화성 가스나 증기의 흐름을 자동으로 차단시키기 위한 장치가 설치되어 있지 않다면 기기는 정상 누출이 있는 것으로 분류되어야 한다. 41 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
7ba87b10-fab4-4646-ba1f-69ef780045f8 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 부속서 F (참고) 희석지역 개념의 사용 예 (Examples for the use of the dilution area concept) ![image](/image/placeholder) 2 3 d, e, m, ·· etc 4 ICA 6 7 5 식별부호 1 희석지역의 공칭 경계(nominal boundary) 2 인화성 물질 유입구 3 인화성 물질 배출구 4 희석 시험 지역(area of dilution testing) 5 퍼지 배출구 6 ICE 를 감싸는 칸막이 7 퍼지 유입구 그림 F.1 - 퍼지 및 희석 시험 요구사항을 단순화하기 위한 희석지역 개념의 사용을 보여주는 다이어그램 내부 용기 안 또는 칸막이 사용을 통해 점화가능기기(그림 F.1 부터 그림 F.3 에 ICA 로 표시)를 둘러싸 는 방식으로 ICE 가 희석지역 내에 있지 않음을 간단한 시험으로 증명할 수 있다. 여기서는 희석지역 의 범위를 결정할 필요는 없으며, 단지 희석지역이 ICE 까지 연장되지 않았음을 결정하면 된다. 42 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
5143d043-f65f-4779-bbd2-f1394159969b | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 ![image](/image/placeholder) 2 3 6 ICA 5 식별부호 ¦ 1 ¦ 내부 칸막이 ¦ 4 퍼지 배출구 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 2 ¦ 퍼지 입입구 ¦ 5 ICE 위치 ¦ ¦ 3 ¦ 컨테인먼트 시스템의 무고장 부분 ¦ 6 공칭 희석지역이 있는 잠재적 누출원 ¦ 그림 F.2 - ICE 주변의 퍼지 및 희석 요구사항을 단순화하기 위한 무고장 컨테인먼트 시스템 개념의 사용을 보여주는 다이어그램 내부 칸막이 안에 있는 컨테인먼트 시스템의 해당 부분은 무고장 컨테인먼트 시스템 요구사항을 충 족하므로 ICE(그림 F.1 부터 그림 F.3 에 ICA 로 표시)는 희석지역 내에 있을 수 없다. ![image](/image/placeholder) 2 ICA 3 식별부호 ¦ 1 ¦ 희석 시험 지역 ¦ 3 공칭 희석지역이 있는 잠재적 누출원 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 2 ¦ 불활성 가스의 퍼지 유입구 ¦ 4 퍼지 배출구 ¦ 그림 F.3 - 칸막이 밖에 있는 ICE 주변의 퍼지 및 희석 요구사항을 단순화하기 위한 잠재적 누출원 주변의 내부 칸막이 사용을 보여주는 다이어그램 희석지역이 내부 칸막이 내에 포함되어 있기 때문에 ICE(그림 F.1 부터 그림 F.3 에 ICA 로 표시)는 희 석지역 내에 있지 않다. 43 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
9b6f746b-c73a-4997-ac71-4442fb2c52c2 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 부속서 G (규정) 보호등급 "pxb" 및 보호등급 "pyb"에 대한 내부 전지 및 배터리 (Internal Cells and Batteries for Level of Protection "pxb" and Level of Protection "pyb") G.1 일반 요구사항(General Requirements) G.1.1 일반사항(General) 보호되는 기기가 배터리를 포함하고 있는 경우, 폭발성 가스, 스파크 또는 고온부(hot spots)가 발생하 는 것을 방지하기 위해 기기의 설계에 적절한 예방조치를 취해야 한다. G.1.2 허용되는 전기화학 시스템(Accepted Electrochemical Systems) KS C IEC 전지 표준이 존재하는 KS C IEC 60079-0 에 열거된 전지만을 가압용기에 사용하여야 한다. G.1.3 2 차 전지 및 2 차 배터리(Secondary cells and secondary batteries) 2 차 전지 및 2 차 배터리는 다음 중 하나를 만족할 때 허용된다. 개별 전지가 밀폐된 전지인 경우[가스 밀폐형 전지(sealed gas-tight cell) 또는 밀봉된 밸브 조절형 전지(sealed valve-regulated cell)] 배터리의 체적이 가압용기 내부 빈 체적의 1 %를 초과 하지 않는 경우 가압용기가 각각의 자체 충전시스템을 갖는 하나 이상의 독립된 배터리를 포함하는 경우, 하나의 독 립된 배터리로부터 가스 방출이 가장 악조건의 경우만을 고려해야 한다. G.1.4 기계적 보호(Mechanical Protection) 가압용기 내부에 설치된 전지, 배터리 및 관련 보호 부품의 통전 노출부는 가압용기의 문 또는 덮개 가 열린 상태에서도 최소 IP30 의 보호등급을 갖추어야 한다. 몰딩된(encapsulated) 전지의 경우, 압력 배출부(pressure relief facilities)가 막히지 않도록 주의 하여야 한다. 벤트(vent)의 크기는 배터리에서 가 장 악조건의 예상 방출 속도를 고려할 때 몰딩된 조립체의 위험한 가압을 방지하기에 충분히 커야 한다. 각 전지는 최소 한 개 이상의 벤트가 필요하다. 전지 및 배터리의 몰딩은 충전 중에 전지의 팽창을 허용할 수 있어야 한다. 이 표준에서 "몰딩하다(encapsulate)" 및 "몰딩(encapsulation)"이라는 용어는 KS C IEC 60079-18 에 대 한 적합성을 의미하지 않는다. 벤트의 물리적 특성은 배터리 배열의 형식 및 용량에 따라 다르다. 노화(ageing)가 배터리 용량에 미 치는 영향과 그에 따른 가스 방출률에 대한 영향을 고려하여야 한다. 44 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
329e41a6-f1b8-462e-9915-b5f38153bbe6 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 전지, 배터리 및 관련 보호 부품은 견고하게 고정되어야 한다. G.2 에너지 제한 회로에 의한 전기적 보호(Electrical Protection by energy limiting circuits) G.2.1 에너지 제한 평가(Assessing as energy limited) 이 절의 목적은 KS C IEC 60079-11 을 적용하여 평가될 수 있는 회로를 허용하는 것이다. G.2.2 보호 부품(Protective Components) 본질적으로 안전한 배터리(inherently safe battery)를 제외하고(G.5 참조), 안전성이 평가된 전류보다 큰 전류가 배터리로부터 인출되는 것을 방지하기 위해 저항 및/또는 퓨즈와 같은 보호 부품을 사용 하여 에너지 제한 회로를 구축해야 한다. 보호 부품은 다음 요구사항을 준수해야 한다. 제조자의 기술문서는 추가 시험 없이 이러한 요구사항 의 적합성을 검증하기에 충분하다. 1 차 전지의 충전 또는 역충전을 방지하기 위해 사용되는 다이오드는 인가 최대 역전압[rated Peak Inverse Voltage(PIV)], [또는 명시된 반복 최대 역전압(Repetitive Peak Reverse Voltage)]의 2/3 를 초과 하는 역전압에 노출되지 않아야 한다. 이 다이오드는 가장 극한의 온도조건(관련 회로의 단일 고장을 고려한)에서 역방향 누설 전류 (reverse leakage current)가 10uA 미만일 때 400 Vdc 의 역전압을 견딜 수 있어야 한다. 1 차 전지의 충전 방지를 목적으로하는 다이오드의 최대 순방향 전류(관련 회로의 단일 고장을 고려 한)는 제조자의 최대 순방향 전류 정격의 50 %를 초과 하지 않도록, 예로 퓨즈 또는 저항을 사용하 여 제한하여야 한다. 퓨즈는 다음과 같이 IEC 60127(해당 부)를 준수해야 한다. 퓨즈를 평가할 때 사용되는 전압은 퓨즈에 인가할 수 있는 플러스 공차를 고려한 최대 전압을 기준으로 한다. 배터리 공급 전압의 경우, 고려해야 할 전압은 사용된 전기화학 시스템에 해당하는 KS C IEC 표준에 정의 된 공칭 전압이어야 한다. 배터리를 보호하기 위해 퓨즈를 사용하는 경우, 1.7 In(퓨즈의 공칭 정격전류)가 연속적으로 흐르는 것으로 가정해야 한다. 퓨즈의 전류-시간 특성(fuse time-current characteristics)은 보호되는 부품의 과도 정격(transient ratings)을 초과 하지 않도록 보장해야 한다. 전류 제한용 저항은 다음 형(type) 중 하나이어야 하며 제조자 정격의 2/3 까지 사용할 수 있다. 필름 형 파손 시 외이어 풀림을 방지하는 보호 기능이 있는 와이어 권취 형(wire wound type) KS C IEC 60079-11 에 부합하는 코팅 또는 몰딩으로 덮인 하이브리드 및 유사 회로에 사용되는 인쇄 저항(printed resistors) 전류 제한용 저항은 개방 회로에만 고장이 발생하는 것으로 간주해야 한다. 다른 부품은 KS C IEC 60079-11 의 해당 요구사항을 준수하여야 한다. - G.2.3 과도한 가스 압력 방지(Preventing excessive gas pressure) 다음과 같이 과도한 가스 압력의 형성을 방지하기 위한 수단이 제공되어야 한다. a) 역충전 시. 예: 배터리의 각 전지에 걸쳐 장착된 션트 다이오드 b) 과도한 방전 시. 예: 배터리와 직렬로 장착된 퓨즈 c) 2 차 전지의 경우, 과도한 충전 시. 예: 충전 조건을 제조자가 권장하는 조건으로 제한하도록 설계 45 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b26a9bfd-5cc8-400d-83f8-9be3f3f7fb4e | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 된 충전기 G.3 1 차 배터리에 대한 추가 요구사항(Additional requirements for Primary batteries) G.3.1 역충전 방지(Prevention of reverse charging) 극성 반전에 의한 전해가스의 누출을 방지하기 위해 또는 다음과 같은 경우 동일 배터리에 있는 다 른 전지에 의한 전지의 역충전을 방지하기 위해 추가적인 보호장치를 설치할 필요가 없다. 1.5 Ah 이하의 용량(1 시간 방전율 기준) 체적이 용기의 빈 체적의 1 % 미만인 경우 또는 배터리 제조자가 전지가 전기화학적으로 평형을 이루며 방전 종료 시 각 전지의 내부 저항이 25 k�을 초과 함을 확인한 경우에는 추가적인 보호장치를 필요로 하지 않는다. 이러한 완화 조건은 전지에서 전해가스의 방출을 허용하는 것으로 해석되어서는 안 된다. 1 차 배터리가 3 개 이상의 직렬로 연결된 전지를 포함하는 경우, 수명이 만료된 전지의 역충전에 의 한 가스 발생을 방지하기 위해 하나 이상의 보호 부품을 설치해야 한다(그림 G.1 참조). Chart Type: line + Ve - Ve item_01 0Not specified 0Not specified 그림 G.1 - 역충전 보호 이러한 보호 조치가 효과 적이기 위해서는, 전지의 역충전을 방지하기 위해 설치된 각 다이오드의 순 방향 전압 강하가 해당 전지의 안전한 역충전 전압을 초과 해서는 안 된다. 실리콘 다이오드는 이 요 구사항을 충족시키기에 적절한 것으로 간주된다. G.3.2 1 차 배터리의 우발적인 충전 방지(Prevention of accidental charging of primary batteries) 기기 내부에 두 개 이상의 배터리 또는 다른 전압원이 있어 상호 연결될 가능성이 있는 경우, 1 차 배 터리로 충전 전류가 흐르는 것을 방지하기 위해 차단 다이오드(blocking diodes)와 같은 보호 부품을 설치하여야 한다. 단일 고장 조건 하에서도 1 차 배터리의 충전을 10 �A 또는 제조자가 명시한 값의 2/3 중 낮은 값을 초과 하지 않는 수준으로 제한하기 위해 최소 두 개의 직렬 연결된 보호 부품을 설치하여야 한다[예: 2 개의 다이오드 또는 1 개의 다이오드와 1 개의 저항(그림 G.2 참조)]. ![image](/image/placeholder) +Ve -Ve 그림 G.2 - 우발적 충전 방지 46 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
dbb845de-67cf-4ee9-8991-672407fbd16e | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 단일 고장으로 인해 두 보호 부품의 단락이 발생할 수 있는 위험을 감소시키기 위해 배터리는 보호 부품 사이에 연결되어야 한다. G.4 2 차 배터리에 대한 추가 요구사항(Additional requirements for secondary batteries) G.4.1 가압용기 내부에 있는 2 차 배터리의 충전(Charging of secondary batteries inside the press urized housing) 배터리가 가압용기 내부에서 충전될 때에는 충전 조건이 모두 명시되어야 하며 이러한 조건을 벗어 나지 않도록 보호 부품이 설치되어야 한다. 용량이 1.5 Ah 이하이고 용기 빈 체적의 1 % 미만의 체적을 갖는 배터리의 경우에는 재충전 전류에 의한 전해가스 방출을 방지하기 위한 추가적인 보호 부품을 배터리에 설치할 필요가 없다. 이러한 완화 조건은 전지에서 전해가스의 방출을 허용하는 것으로 해석되어서는 안 된다. 비고 위 조건은, 예를 들어 프로그램 가능한 전자회로의 메모리를 유지하기 위해 사용되는 "버튼 타 입 전지(button type cells)"로 알려진 유형의 보호 부품이 장착되지 않은 전지(또는 배터리)의 사 용을 효과 적으로 제한한다. 충전을 위해 가압용기에서 배터리를 제거하는 경우, 올바른 충전을 위해 제조자의 요구사항을 따라 야 한다. 심방전(deep discharging)의 결과 로 후속되는 충전 중에 전해가스의 방출 증가 및/또는 내부 기계적 손상을 초래할 수 있는 경우, 심방전을 방지하기 위한 안전장치(들)가 제공되어야 한다. 올바르지 않은 조립을 방지할 수 있는 적절한 예방조치가 취해져야 한다(예: 플러그 및 소켓이 극성 별로 다른 모양을 갖거나 또는 옳바른 결합을 위해 명확한 표시를 함). 플러그와 소켓을 사용하는 경우, 플러그를 분리하기 전에 안전하게 회로를 개방할 수 있는 방안을 마련해야 한다. 가압용기 내부의 배터리 위치는 점화가능기기의 위치를 고려하여 선택하여야 하며 누출된 가스가 용 기 전체에 걸쳐 자유로운 확산이 가능하도록 고려하여 선정한다. 점화가능기기는 배터리에서 방출되 는 가스가 있는 지역에 위치하지 않아야 한다. G.5 본질적으로 안전한 전지 및 배터리에 대한 특정 요구사항(Specific requirements for Inherently Safe(IhS) cells and batteries) IhS 배터리는 다음 조건을 충족하는 1 차 배터리다. 배터리의 내부 저항은 배터리의 단락 전류를 전압에 따른 도표화된(tabulated) 허용단락전류를 초과 하지 않는 값으로 제한하며, 배터리의 최대 개방 회로 전압에 따라 KS C IEC 60079-11 에 도표화된 기기 그룹으로 제한한다. 배터리 외부 표면의 최고 온도가 배터리 내부저항과 비교하여 무시할 만한 저항의 도체로 단락된 경우에 발생되는 국부적인 주위온도(local ambient temperature)를 고려하여 부여된 기기의 온도 등 급에 해당하는 최고표면온도를 초과 하지 않는다. 단락 회로의 저항은 배터리 내부저항의 1/10 보다 크지 않은 경우 무시할 수 있는 것으로 간주한다. 47 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b80a0173-baf8-40e4-8156-86df011892d5 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 역충전이 방지되어야 하는 3 개 이상의 전지가 연결되어 배터리를 형성하는 경우를 제외하고, IhS 전 지의 고장을 고려할 필요가 없다. 배터리의 내부 저항이 단락 전류의 최대 값을 전압에 따른 도표화된 허용단락전류를 초과 하지 않는 값으로 제한하고 배터리의 최대 개방 회로 전압에 따라 KS C IEC 60079-11 에 도표화된 기기 그룹으 로 제한하는 경우 IhS 전지가 상호 연결되어 IhS 배터리를 형성할 수 있다. IhS 배터리가 연결될 수 있는 회로의 특성(nature)은 G.6 에 명시되어 있다. 본질적으로 안전한 배터리의 올바른 교체를 돕기 위해서 필수 파라미터(예: 형식, 공칭전압 및 최소 내부 저항 등)를 배터리 옆에 표시하고 사용설명서에도 명시하여야 한다. G.6 가압용기 내부에 위치한 기기로서 가압용기 내부에 위치하고 가압 손실 시 분리 되지 않는 배터리에 연결된 기기(Equipment located inside a pressurized enclosu re connected to a battery which is also located inside the pressurized enclos ure and not disconnected in the event of loss of pressurization) G.6.1 일반사항(General) 배터리에 연결된 회로의 평가 및 시험을 위해 고려하여야 할 전압은 최대 개방 회로 전압이다. 기기의 온도 등급은 배터리에 연결된 기기를 구성하는 개별 부품의 표면 지역(surface area)을 고려하 여야 한다. 평가방법은 시험 또는 KS C IEC 60079-0 에 따른 소형 부품의 온도 평가를 이용한다. G.6.2 회로 분리(Circuit Isolation) 이 절의 목정상, 배터리가 퍼지가 완료된 이후에만 기기에 연결(connected)되고 압력 또는 유량의 실 패(failure) 시 배터리의 차단(disconnection) 대책이 마련되고 이러한 차단 또는 분리가 다음의 요구사 항을 충족하지 않는다면 기기는 배터리에 연결된 것으로 간주한다. 적절한 정격을 가지는 접점에 의한 차단, 또는 적절한 정격을 가지는 광-분리장치(opto-isolating device)에 의한 분리, 또는 배터리 최대 개방 회로 전압의 5 배(최소 500 Vac RMS)로 최소 60 초간 권선 간의 절연시험을 견딜 수 있는 적절한 정격을 가지는 2 중 권선 변압기(double wound transformer)로 분리, 또는 배터리와 분리 또는 차단 부품 및 관련 회로 간의 연면거리 및 공간거리가 KS C IEC 60079-11 의 연면거리 및 공간거리 표의 ia 또는 ib 의 해당 열에 표시된 값에 적합 G.6.3 방폭기기와 함께 사용되는 본질안전 배터리 또는 본질적으로 안전한 배터리(Intrinsically safe b attery or inherently safe battery used with "Ex" equipment) 배터리가 KS C IEC 60079-11 에 따른 본질안전(Intrinsic Safety)으로 보호되거나 본질적으로 안전 (inherently safe)하고 연결된 기기가 KS C IEC 60079-0 에 나열된 방폭구조 중 하나에 의해 보호되거나 KS C IEC 60079-11 에 정의 된 단순기기로 평가되는 경우, 추가 요구사항은 없다. G.6.4 비방폭기기와 함께 사용되는 본질안전 배터리 또는 본질적으로 안전한 배터리(Intrinsically Safe or Inherently Safe battery with non-"Ex" equipment) 가압용기 내에 설치되어 있는 본질안전 배터리 또는 본질적으로 안전한 배터리가 퍼지가 완료되기 48 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
227b2686-872a-4fd6-b2c3-600037b43735 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 전에 비방폭기기에 연결되는 경우 및/또는 압력(및 유량, 명시된 경우)이 없을 때 기기에 연결된 상태 로 유지되는 경우, 다음의 중 하나의 추가 요구사항을 연결되는 기기에 적용한다. a) 다음 조건을 만족하여야 한다. 배터리 및 관련 회로의 최대 개방 회로 전압은 6 V 를 초과 하지 않아야 한다. 배터리의 단락전류는 2A 를 초과 해서는 안 된다. 이는 배터리의 내부저항만으로 달성하거나 G.2.1 을 준수하면서 가능한 한 배터리에 가깝게 설치된 외부 전류 제한 저항을 추가함으로써 이 값으로 제한할 수 있다. 공차를 포함하여 집계된 총 회로의 정전용량은 1 000 �F 를 초과 하지 않아야 한다. 공차를 포함하여 집계된 총 회로 유도용량은 다음 식에 의해 계산된 L 값을 초과 하지 않아야 한다. 2e L= 12 여기에서 L : 허용 유도용량(�H) I : 유효 단락전류(available short circuit current)(A) e : 기기그룹에 부여된 점화 에너지(�J) ¦ 기기 그룹 ¦ 점화 에너지 ¦ ¦ --- ¦ --- ¦ ¦ IIC ¦ 40 �J ¦ ¦ IIB ¦ 160 �J ¦ ¦ IIA ¦ 320 mJ ¦ ¦ I ¦ 525 �J ¦ 또는 b) 가압용기는 G.7 에 따라 표시되어야 하며 다음 조건을 만족하여야 한다. 배터리 및 관련 회로의 최대 개방 회로 전압은 6 V 를 초과 하지 않아야 한다. 단락전류는 2A 로 제한되어야 한다. 회로를 검사하여 결정된 배터리에 연결된 상태의 유효 정전용량은 1 000 �F 을 초과 하지 않는다. G.2.1 의 유사한 부품에 대한 요구사항을 준수하는 정전용량과 관련된 보호 부품(예: 저항)은 안전계수 1.0 으로 KS C IEC 60079-11 을 사용하여 유효 정전용량을 결정할 때 고려될 수 있다. 회로를 검사하여 결정된 배터리에 연결된 상태의 유효 유도용량은 상기 표시된 L 값을 초과 하 지 않는다. G.2.1 의 유사한 부품에 대한 요구사항을 준수하는 유도용량과 관련된 보호 부품(예: 저항)은 안전계수 1.0 으로 KS C IEC 60079-11 을 사용하여 유효 유도용량을 결정할 때 고려될 수 있다. 또는 c) 전원 전압이 6V 이상이거나 단락전류가 2A 이상인 경우, 연결되는 기기는 KS C IEC 60079-11 의 범주 'ib'에 따라 평가되어야 한다. 또는 d) 고체 전자부품(예: 집적회로 내의 리튬 전지)에 내장된 전지는 다음 기준이 충족되는 경우 허용된다. 전지가 본질적으로 안전하여야 한다. 외부 전압을 검출할 수 없어야 한다. 제조자가 선언한 고체 전자부품의 내부 정전용량 및 유도용량은 상기 a)에서 주어진 값을 초 과하지 않아야 한다. 전지 전압이 외부에서 검출될 수 없기 때문에 G.5 의 요구사항에 따른 단락 회로 시험은 평가에 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 49 | {}
9a433c9d-1eef-44c6-9077-522ab6f01cee | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 의해 수행될 수 있다. G.7 하나 이상의 전지 또는 배터리를 포함하는 가압용기에 대한 추가적인 표시 및 구 조 요구사항(Supplementary marking and constructional requirements for pressurized enclosures containing one or more cells or batteries) G.7.1 일반사항(General) 가압용기의 문 및 덮개는 공구 또는 열쇠의 사용으로만 열 수 있어야 한다. 용기에 다음과 같거나 또는 이와 동등한 표시를 하여야 한다. "경고 - 용기 내에 배터리가 있음. 폭발성 분위기가 존재할 경우 열지 마시오." G.7.2 배터리 제거 경고(Battery removal warning) G.6.4b)에서 요구하는 경우, 용기에 다음과 같거나 또는 이와 동등한 표시를 하여야 한다. 경고 - 이 가압용기에는 외부 전원 차단 후에도 연결되어 있는 배터리가 들어 있음. 용기가 상당 시간 동안 압력방폭구조에 의해 보호되지 못하는 경우 배터리 제거 시 주의 하여야 함. G.7.3 정기 점검이 필요한 배터리(Batteries requiring routine maintenance) 용기에 다음과 같은 표시를 하여야 한다. "경고 - 이 가압용기 내에 설치된 배터리는 정기 점검이 필요함. 사용설명서 참조" G.8 형식 시험(Type tests) G.8.1 전압(Voltage) 온도시험에서는 배터리의 공칭전압(nominal voltage)을 사용한다. G.8.2 본질적으로 안전한 전지 또는 배터리의 단락 시험(Short circuit test for an Inherently Safe Cell or Battery) 새 전지 또는 배터리에 단락회로를 적용하고 다음 사항을 관찰하여야 한다. 회로에 흐르는 전류 가압용기의 문이 개방되었을 때 외부 폭발성 분위기와 접촉할 수 있는 전지 또는 배터리의 외부 표 면 온도 최대 전류는 G.5 에서 주어진 값을 초과 하지 않아야 한다. 최고표면온도는 기기의 온도 등급을 초과 하지 않아야 한다. 전지 또는 배터리에는 뒤틀림, 폭발 또는 연기가 발생하지 않아야 한다. G.8.3 본질적으로 안전한 배터리 이외의 배터리에 대한 전 부하 시험(Full load test for other than Inh 50 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
fbc3e261-7ba0-4054-8f30-9c2554acedd2 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 erently safe batteries) 새 1 차 배터리 또는 완충된 2 차 배터리를 정상 작동상태에서 연결되는 부하에 연결하여야 한다. 케 이스 온도(case temperature)는 기기의 온도 등급 또는 배터리 제조자가 허용한 최고온도 중 낮은 값 을 초과 하지 않아야 한다. 51 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
9d59c082-4c81-4d08-801b-758abd3b20d1 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 부속서 H (규정) 보호등급 "pzc"의 내부 전지 및 배터리 (Internal Cells and Batteries for Level of Protection "pzc") H.1 일반 요구사항(General Requirements) H.1.1 일반사항(General) 보호되는 기기가 배터리를 포함하고 있는 경우, 폭발성 가스, 스파크 또는 고온부가 발생하는 것을 방지하기 위해 기기의 설계에 적절한 예방조치를 취해야 한다. H.1.2 허용되는 전기화학 시스템(Accepted Electrochemical Systems) KS C IEC 전지 표준이 존재하는 KS C IEC 60079-0 에 열거된 전지만을 가압용기에 사용하여야 한다. H.1.3 2 차 전지 및 2 차 배터리(Secondary cells and secondary batteries) 2 차 전지 및 2 차 배터리는 다음 중 하나를 만족할 때 허용된다. 개별 전지가 밀폐된 전지인 경우[가스 밀폐형 전지(sealed gas-tight cell) 또는 밀봉된 밸브 조절형 전지(sealed valve-regulated cell)] 배터리의 체적이 가압용기 내부 빈 체적의 1 %를 초과 하지 않는 경우 가압용기가 각각의 자체 충전시스템을 갖는 하나 이상의 독립된 배터리를 포함하는 경우, 하나의 독 립된 배터리로부터 가스 방출이 가장 악조건의 경우만을 고려해야 한다. H.1.4 기계적 보호(Mechanical Protection) 몰딩된(encapsulated) 전지의 경우, 압력 배출부(pressure relief facilities)가 막히지 않도록 주의 하여야 한다. 벤트(vent)의 크기는 배터리에서 가장 악조건의 예상 방출 속도를 고려할 때 몰딩된 조립체의 위험한 가압을 방지하기에 충분히 커야 한다. 각 전지는 최소 한 개 이상의 벤트가 필요하다 전지 및 배터리의 몰딩은 충전 중에 전지의 팽창을 허용할 수 있어야 한다. 이 표준에서 "몰딩하다(encapsulate)" 및 "몰딩(encapsulation)"이라는 용어는 KS C IEC 60079-18 에 대 한 적합성을 의미하지 않는다. 벤트의 물리적 특성은 배터리 배열의 형식 및 용량에 따라 다르다. 노화(ageing)가 배터리 용량에 미 치는 영향과 그에 따른 가스 방출률에 대한 영향을 고려하여야 한다. 전지, 배터리 및 관련 보호 부품은 견고하게 고정되어야 한다. H.2 가압용기 내부에 위치한 기기로서 가압용기 내부에 위치하고 용기의 전원 차단 시 분리되지 않는 배터리에 연결된 기기(Equipment located inside a pressurized enc 52 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
7603e246-4cec-4311-a8bf-dadc714bdaa5 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 losure connected to a battery which is also located inside the pressurized enclosu re and is not disconnected when power is removed from the enclosure) 배터리의 전원으로 분터 분리되지 않는 기기는 KS C IEC 60079-15 에 따른 비점화 회로로 평가되거나 KS C IEC 60079-11 에 따른 기기보호등급 "ic"로 평가되지 않는 한, 개폐 접점이 있는 부품 (make/break components)을 포함해서는 안 된다. H.3 하나 이상의 전지 또는 배터리를 포함하는 가압용기에 대한 추가적인 표시 및 구 조 요구사항(Supplementary marking and constructional requirements for pressurize d enclosures containing one or more cells or batteries) H.3.1 일반사항(General) 전지 및 배터리로의 접근을 허용하는 가압용기의 문 및 덮개는 공구 또는 열쇠의 사용으로만 열 수 있어야 한다. 용기는 다음과 같거나 또는 동등하게 표시되어야 한다. "경고 - 용기 내에 배터리가 있음. 폭발성 분위기가 존재할 경우 열지 마시오." H.3.2 배터리 제거 경고(Battery removal warning) 가압이 손실되었을 때 전지나 배터리가 분리되지 않는 경우, 용기에 다음과 같거나 또는 이와 동등 한 표시를 하여야 한다. 경고 - 이 가압용기에는 외부 전원 차단 후에도 연결되어 있는 배터리가 들어 있음. 용기가 상당 시간동안 압력방폭구조에 의해 보호되지 못하는 경우 배터리 제거 시 주의 하여야 함. H.3.3 정기 점검이 필요한 배터리(Batteries requiring routine maintenance) 용기에 다음과 같은 표시를 하여야 한다. "경고 - 이 가압용기 내에 설치된 배터리는 정기 점검이 필요함. 사용설명서 참조" 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 53 | {}
c830e9d9-d674-42ca-b3b0-66a841df79cf | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 참고문헌 [1] KS C IEC 60050-151, 국제전기기술용어 - 제 151 부: 전기 장치와 자기 장치 [2] IEC 60050-426, International Electrotechnical Vocabulary - Chapter 426: Equipment for explosive atmospheres [3] KS C IEC 60051(모든 부), 직동식 지시 전기계기 [4] KS C IEC 60079-1, 폭발성 분위기 - 제 1 부: 내압방폭용기 "d"에 의한 기기 보호 [5] KS C IEC 60079-5, 폭발성 분위기 - 제 5 부: 충전 방폭구조 "q"에 의한 기기 보호 [6] KS C IEC 60079-6, 폭발성 분위기 - 제 6 부: 유입 방폭구조 "0"에 의한 기기 보호 [7] KS C IEC 60079-7, 폭발성 분위기 - 제 7 부: 안전증방폭구조 "e"에 의한 기기 보호 [8] IEC 60079-13, Explosive atmospheres - Part 13: Equipment protection by pressurized room "p" [9] KS C IEC 60079-18, 폭발성 분위기 - 제 18 부: 몰드방폭구조 "m"에 의한 기기 보호 [10] IEC 60079-20-1, Explosive atmospheres - Part 20-1: Material characteristics for gas and vapour classification - Test methods and data [11] KS C IEC 60079-26, 폭발성 분위기 - 제 26 부: 기기보호수준(EPL) Ga 기기 [12] KS C IEC 60079-28, 폭발성 분위기 - 제 28 부: 광학 방사를 사용하는 설비 및 전송 시스템의 보호 [13] IEC 61511(all parts) Functional safety - Safety instrumented systems for the process industry sector 54 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
7162c5b7-63a6-44f2-8672-5ef9b81a739c | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 KS C IEC 60079-2:2014 해 설 이 해설은 본체 및 부속서에 규정 · 기재한 사항과 이것들과 관련된 사항을 설명하는 것으로 표준의 일부는 아니다. 1 개정 취지 이 표준은 기존 2007 년 제 5 판 IEC 60079-2 를 기초로 하여 발행된 KS C IEC 60079-2:2012 표준을 최 신 국제표준인 2014 년 제 6 판으로 발행된 IEC 60079-2, Exprosive atmospheres - Part 2: Equipment protection by pressurized enclosures "p"에 부합하기 위해 해당 표준의 기술적 내용 및 대응국제표준의 구성을 변경하지 않고 작성한 한국산업표준이다. 2 개정 내용 기존 KS C IEC 60079-2:2012 에서 현 KS C IEC 60079-2:2014 로의 변경사항은 다음과 같다. ¦ ¦ ¦ 타입 ¦ 타입 ¦ 타입 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 변경사항에 대한 설명 ¦ 조항 ¦ 경미한 변경 및 편집상 변경 ¦ 확장 ¦ 주요 기술적 변경 ¦ ¦ 범위 가연성 분진을 포함한 기준으로 확대 ¦ 1 절 ¦ ¦ X ¦ ¦ ¦ 보호가스 "기구 (apparatus)"를 "기기(equipment)"로 대체 ¦ 3 절 ¦ ¦ ¦ ¦ ¦ 보호가스 폭발성 분진 분위기에서 퍼지가 요구되지 않 음을 보여주기 위해 개정 ¦ 3.16 ¦ X ¦ ¦ ¦ ¦ 보호등급 "pxb" EPL 및 보호등급 반영을 위한 용어와 정의 ¦ 3.21 ¦ X ¦ ¦ ¦ ¦ 보호등급 "pyb" EPL 및 보호등급 반영을 위한 용어와 정의 ¦ 3.22 ¦ X ¦ ¦ ¦ ¦ 보호등급 "pzc" EPL 및 보호등급 반영을 위한 용어와 정의 ¦ 3.23 ¦ X ¦ ¦ ¦ ¦ LFL(Lower Flammable Limit) KS C IEC 60079-0 에 일치하도록 용어와 정 의 변경 ¦ 3.26 ¦ X ¦ ¦ ¦ ¦ UFL(Upper Flammable Limit) KS C IEC 60079-0 에 일치하도록 용어와 정 의 변경 ¦ 3.27 ¦ X ¦ ¦ ¦ ¦ 표 1 - 보호등급의 결정 EPL 용어를 사용하도록 개정 ¦ 표 1 ¦ X ¦ ¦ ¦ ¦ 표 2- 보호등급에 따른 설계 기준 EPL 용어를 사용하도록 개정 ¦ 표 2 ¦ X ¦ ¦ ¦ ¦ 용기 특정 설계에 대한 요구사항의 완화 ¦ 5.1 ¦ ¦ X ¦ ¦ 55 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c6cd97fe-50d0-420b-82f4-70e1b72dac6f | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 ¦ ¦ ¦ 타입 ¦ 타입 ¦ 타입 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 변경사항에 대한 설명 ¦ 조항 ¦ 경미한 변경 및 편집상 변경 ¦ 확장 ¦ 주요 기술적 변경 ¦ ¦ 그룹 II 및 그룹 III 가압용기 EPL 을 사용하도록 개정된 문구 ¦ 5.3.3 ¦ X ¦ ¦ ¦ ¦ 그룹 II 및 그룹 III 보호등급 "pxb" 폭발성 분진 분위기에도 경고가 적용됨을 추가 ¦ 5.3.5 ¦ ¦ X ¦ ¦ ¦ 그룹 II 및 그룹 III 문 및 덮개의 경고 표시 폭발성 분진 분위기에도 경고가 적용됨을 추가 ¦ 5.3.6 ¦ ¦ X ¦ ¦ ¦ 그룹 II 및 그룹 III 문 및 덮개의 경고 표시 폭발성 분위기가 "존재할 수 있다"에서 "존재 한다"로 변경 ¦ 5.3.6 ¦ X ¦ ¦ ¦ ¦ 기계적 강도 "X" 조건에 대한 KS C IEC 60079-0 항 번호 에 의한 참조 삭제 ¦ 5.4 ¦ X ¦ ¦ ¦ ¦ 스파크 및 입자 배리어 "X" 조건에 대한 KS C IEC 60079-0 항 번호 에 의한 참조 삭제 ¦ 5.9 ¦ X ¦ ¦ ¦ ¦ 전지 및 배터리 전지 및 배터리에 대한 요구사항 추가 ¦ 5.10 ¦ ¦ ¦ C1 ¦ ¦ 보호등급 "pxb" 또는 보호등급 "pyb" EPL 과 일관된 용어를 사용하기 위해 표를 개정 ¦ 6.2 ¦ X ¦ ¦ ¦ ¦ 위험장소에 대한 안전장치의 적합성 UFL/LFL 용어를 반영하기 위해 단어 "폭발 (explosion)"을 "점화(ignition)"로 변경 ¦ 7.1 ¦ X ¦ ¦ ¦ ¦ 안전장치의 무결성 팬 고장의 감지 요구사항 추가 ¦ 7.2 ¦ ¦ ¦ C2 ¦ ¦ 표 3- 보호등급에 기반한 안전장치 보호등급 용어를 사용하도록 열 수정 ¦ 표 3 ¦ X ¦ ¦ ¦ ¦ 안전장치의 공급자 "X" 조건에 대한 KS C IEC 60079-0 항 번호 에 의한 참조 삭제 ¦ 7.3 ¦ X ¦ ¦ ¦ ¦ 관련기기로 평가되는 가압시스템 가압시스템에 대한 요구사항 추가 ¦ 7.4 ¦ ¦ ¦ C3 ¦ ¦ 보호등급 "pxb"에 대한 순서도 보호등급 용어를 사용하기 위해 문구 수정 ¦ 7.5 ¦ X ¦ ¦ ¦ ¦ 보호등급 "pxb"에 대한 그룹 I 및 그룹 II 자 동 퍼지 보호등급 용어를 사용하기 위해 문구 수정 ¦ 7.7 ¦ X ¦ ¦ ¦ ¦ 보호등급 "pxb"에 대한 그룹 I 및 그룹 II 자 동 퍼지 "pxb"에 대해 제어가 자동화되어야 함을 명 시하는 문구 추가 ¦ 7.7 ¦ ¦ ¦ C4 ¦ ¦ 그룹 I 또는 그룹 II- 퍼지 기준 보호등급 용어를 사용하기 위해 문구 수정 ¦ 7.8 ¦ X ¦ ¦ ¦ 56 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
8610a78a-e1ad-4c21-8453-983632d630a5 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 ¦ ¦ ¦ 타입 ¦ 타입 ¦ 타입 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 변경사항에 대한 설명 ¦ 조항 ¦ 경미한 변경 및 편집상 변경 ¦ 확장 ¦ 주요 기술적 변경 ¦ ¦ 그룹 III- 청소 폭발성 분진 분위기에서 사용되는 용기 청소 를 위한 문구 추가 ¦ 7.9 ¦ ¦ X ¦ ¦ ¦ 최소양압의 감지를 위한 안전장치 본문과 일치하도록 항 제목에 "최소"를 추가 ¦ 7.11 ¦ X ¦ ¦ ¦ ¦ 최소양압의 감지를 위한 안전장치 보호등급 용어를 사용하기 위해 문구 수정 ¦ 7.11 d) ¦ X ¦ ¦ ¦ ¦ 최소양압 값 본문과 일치하도록 항 제목에 "최소"를 추가 ¦ 7.12 ¦ X ¦ ¦ ¦ ¦ 최소양압 값 보호등급 용어를 사용하기 위해 문구 수정 ¦ 7.12 ¦ X ¦ ¦ ¦ ¦ 최소양압 값 부속서 C 의 비고를 반영하기 위한 문구 추가 ¦ 7.12 ¦ ¦ X ¦ ¦ ¦ 여러 개의 용기의 가압 보호등급 용어를 사용하기 위해 문구 수정 ¦ 7.13 ¦ X ¦ ¦ ¦ ¦ 문 및 덮개의 안전장치 보호등급 용어를 사용하기 위해 문구 수정 ¦ 7.14 ¦ X ¦ ¦ ¦ ¦ 통전 상태를 유지할 수 있는 기기 EPL 및 보호등급 용어를 사용하기 위해 문구 수정 ¦ 7.15 ¦ X ¦ ¦ ¦ ¦ 보호등급 "pyb"에 허용되는 기기 EPL 및 보호등급 용어를 사용하기 위해 문구 수정 ¦ 7.16 ¦ X ¦ ¦ ¦ ¦ 그룹 I 및 그룹 II 충전 절차 위험하지 않은 것으로 시험된 경우, 위험장소 에서 충전의 허용 ¦ 8.4 ¦ ¦ X ¦ ¦ ¦ 그룹 III 충전 절차 가연성 분진에 대한 정적 가압용기의 충전 절 차의 추가 ¦ 8.5 ¦ ¦ X ¦ ¦ ¦ 안전장치 보호등급 용어를 사용하기 위해 문구 수정 ¦ 8.6 ¦ X ¦ ¦ ¦ ¦ 통전 상태를 유지할 수 있는 기기 EPL 용어를 사용하기 위해 문구 수정 ¦ 8.7 ¦ X ¦ ¦ ¦ ¦ 양압 KS C IEC 60079-0 항 번호에 의한 참조 삭제 ¦ 8.8 ¦ X ¦ ¦ ¦ ¦ 보조 공급(backup supply) 보호가스의 예비 공급 요구사항 추가 ¦ 9.1 ¦ ¦ ¦ C5 ¦ ¦ 독립적 공급 독립된 공급의 요구사항 마련 ¦ 9.2 ¦ ¦ X ¦ C6 ¦ ¦ 누출 조건 "X" 조건에 대한 KS C IEC 60079-0 항 번호에 의한 참조 삭제 ¦ 11.1.2 ¦ X ¦ ¦ ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 57 | {}
cf3d1eaf-7f56-47d1-b356-1f9233b7b6bf | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 ¦ ¦ ¦ 타입 ¦ 타입 ¦ 타입 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 변경사항에 대한 설명 ¦ 조항 ¦ 경미한 변경 및 편집상 변경 ¦ 확장 ¦ 주요 기술적 변경 ¦ ¦ 제한적 누출이 있는 컨테인먼트 시스템 "X" 조건에 대한 KS C IEC 60079-0 항 번호 에 의한 참조 삭제 ¦ 12.3 ¦ X ¦ ¦ ¦ ¦ 13.3.3 가스 또는 증기의 제한적 누출 UFL/LFL 용어를 반영한 본문 수정 ¦ 13.3.3 ¦ X ¦ ¦ ¦ ¦ 점화가능기기(ignition-capable equipment) 보호등급 용어를 사용하기 위해 문구 수정 ¦ 14 절 ¦ X ¦ ¦ ¦ ¦ 형식 검증 및 시험 제 5 판 16.1 에서 16.7 까지가 제 6 판 16.2 에서 16.8 로 이동 ¦ 16 절 ¦ X ¦ ¦ ¦ ¦ 최대양압 정격의 결정 최대양압의 결정을 위한 요구사항 추가 ¦ 16.1 ¦ ¦ ¦ C7 ¦ ¦ 최대양압 시험 최대양압 시험을 16.2 로 이동 ¦ 16.2 ¦ ¦ ¦ C7 ¦ ¦ 누설 시험 시험의 합격기준을 명확히 함. ¦ 16.3.2 ¦ ¦ X ¦ ¦ ¦ 무고장 컨테인먼트 시스템 시험 정격을 명확히 함. ¦ 16.7.1 ¦ ¦ ¦ C8 ¦ ¦ 무고장 컨테인먼트 시스템 무고장 컨테인먼트 시스템에 대한 시험 수정 ¦ 16.7.2 ¦ ¦ ¦ C9 ¦ ¦ 제 5 판 내부 양압의 제한을 위한 가압용기의 능력 검증 시험 삭제 ¦ 16.8 ¦ ¦ ¦ C7 ¦ ¦ 기능 시험 가압용기에 제공된 안전장치에만 적용함을 명확히 함. ¦ 17.1 ¦ X ¦ ¦ ¦ ¦ 무고장 컨테인먼트 시스템의 시험 액체일 경우 헬륨 누설 시험의 생략 ¦ 17.3 ¦ ¦ X ¦ ¦ ¦ 추가 표시 방폭구조 표시의 계속된 사용의 허용 ¦ 18.3 ¦ ¦ ¦ ¦ ¦ 가압시스템 Ex[p] 및 [Exp] 표시 사용의 명확화 ¦ 18.6 ¦ X ¦ ¦ ¦ ¦ 다른 항에서 요구되는 경고 표시 표 번호 추가 ¦ 18.7 ¦ X ¦ ¦ ¦ ¦ 다른 항에서 요구되는 경고 표시 7.9 에 따른 경고표시 추가 ¦ 18.7 ¦ ¦ X ¦ ¦ ¦ 다른 항에서 요구되는 경고 표시 부속서 G 및 부속서 H 에서 요구되는 경고 표시 추가 ¦ 18.7 ¦ ¦ ¦ C1 ¦ ¦ 사용설명서 그룹 III 에 대해 추가함. ¦ 19 절 ¦ ¦ X ¦ ¦ ¦ 제 5 판 부속서 G - 컨테인먼트 시스템에 대 한 무고장 시험 삭제 및 대체 ¦ 부속서 G ¦ X ¦ ¦ ¦ 58 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
bca39072-fbe7-4a27-b512-2856d7ddb823 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 ¦ ¦ ¦ 타입 ¦ 타입 ¦ 타입 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 변경사항에 대한 설명 ¦ 조항 ¦ 경미한 변경 및 편집상 변경 ¦ 확장 ¦ 주요 기술적 변경 ¦ ¦ 제 5 판 부속서 H - "기기보호등급"을 포함하 는 대체 위험평가 방법의 도입 삭제 및 대체 ¦ 부속서 H ¦ X ¦ ¦ ¦ ¦ 부속서 G - 보호등급 "pxb" 및 보호등급 "pyb"에 대한 내부 전지 및 배터리 전지 및 배터리에 대한 요구사항 추가 ¦ ¦ ¦ X ¦ ¦ ¦ 부속서 H - 보호등급 "pzc"에 대한 내부 전 지 및 배터리 전지 및 배터리에 대한 요구사항 추가 ¦ ¦ ¦ X ¦ ¦ 설명: A) 정의 경미한 변경 및 편집상의 변경 명확화, 기술적 요구사항의 축소, 경미한 기술적 변경, 편집수정 이러한 변경은 편집상 또는 미미한 기술적인 요구사항을 수정하는 변경이다. 여기에는 기술적 변 경 없이 기술적 요건을 명확하게 하기 위한 표현의 변경 또는 기존 요구 수준의 감소가 포함된다. 확장 기술적 선택 사항 추가 이는 새로운 선택 사항을 제시하는 방식으로 새로운 기술적 요구사항을 추가하거나 수정하지만 기존의 표준을 완전히 준수하는 기기에 대한 요건을 강화시키는 변경은 아니다. 따라서 이는 이 전 판에 따른 제품에 대해 영향을 미치지 않는다. 주요 기술적 변경 기술적 요구사항의 추가, 기술적 요구사항의 증가 이는 이전 판에 따른 제품이 최신 판에 주어진 요구사항을 충족할 수 없는 방식으로 기술적 변경 (추가, 수준 강화 또는 제거)이 발생한 경우이다. 이러한 변경 사항은 이전 판에 부합하는 제품에 대해 고려되어야 한다. 이러한 변경 사항에 대해서 추가적인 정보는 아래 B)항에서 다룬다. B) '주요 기술적 변경'의 배경 정보 C1- 전지 및 배터리 사용에 대한 요구사항이 있는 부속서의 추가 C2- 팬의 고장이 팬의 전원공급 실패를 기반으로 할 수 없음을 추가 C3- 해당 기기의 시험에 균일성을 제공하기 위한 가압 시스템으로 평가된 기기에 대한 요구사항 추가 C4- 제 5 판에서 7.6 의 제목에 자동화 퍼지를 명시했지만 단어 자동화는 요구사항에 포함되지 않 았다. 모든 "pxb" 기기는 퍼지 사이클이 정상적으로 완료될 때까지 점화가능한 회로에 전원 이 공급되는 것을 방지하기 위해 자동화 퍼지 시스템을 갖추고 있다. 이를 위해서는 최소한 양압이 용기 내에 있는지 확인하는 것 이외에 유량이 퍼지 시간에 필요한 최소값 이상인지 확인해야 한다. C5- 보호가스의 보조 공급이이 제공되는 경우, 주 공급원과 보조 공급원 모두가 필요한 압력을 유지할 수 있어야 한다. C6- 가압용기가 더 큰 가압용기 내에서 사용되는 경우, 보호가스의 공급은 독립적이어야 한다. C7- 기존 제 5 판의 16.1 에 용기가 최대양압 정격을 가지고 있다고 가정했지만, 이것은 거의 드문 경우이다. 일부 시험소는 최대양압을 결정하기 위해 16.8 의 시험에 의존했다. 압력조절기의 고장을 시뮬레이션하기 위해 압력조절기의 를 제거하는 것과 같은 다양한 방법을 사용했지만 이로 인해 유량을 제한하는 오리피스도 제거되었다. 시험소의 경험에 의거, 내부 압력을 완 화하기 위해 용기 또는 개스킷이 변형하기 때문에 용기에서 파편이 날아갈 위험은 허용할 59 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
d3868c8b-1a94-4170-8141-cd10a6c746e3 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 수준으로 작다. 압력조절기의 고장을 가정한 양압시험은 배제하기로 결정했다. 또한 최대양 압의 정의 는 이제 가압용기가 정격 범위 내에서 작동할 때 도달할 수 있는 값을 기준으로 한다. 이 최대양압은 일반적으로 기기가 압력조절기의 유입구에 최대 정격 압력이 가해지면 서 급속한 퍼지 모드로 전환될 때 발생한다. 제 5 판의 16.1 은 16.2 로 수정되어 이동하였다. C8- 대부분의 경우, 양압(overpressure)이란 용어는 정상적인 정격을 벗어난 작동을 의미한다. "최 대 내부 양압(maximum internal overpressure)"이라는 표현보다 "최대 작동 압력(maximum operating pressure)"이라는 용어를 사용하도록 명확히 하였다. 해당 시험은 제 5 판에서 16.6.1 에 있었다. C9 - 이 시험은 진공 시스템의 성능에 달려 있기 때문에 진공 유지에 의존하기보다는 헬륨 누설 감지를 사용하도록 수정되었다. 해당 시험은 제 5 판에서 16.6.2 에 있었다. 3 기타 이 표준은 KS A 0001:2015(표준의 서식과 작성방법)에 따라 작성하였다. 60 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
03d95783-4d7b-45ce-ae45-1fc8e81f4478 | KSCIEC60079-2_2024확인_KR | 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
84702281-42f8-4abd-8d99-438b1ecdd908 | KSCIEC60079-2_2024확인_KR | KS C IEC 60079-2:2014 KSKSKS KSKSK KSKS KSK KS KSK KSKS KSKSK KSKSKS Explosive atmospheres Part 2: Equipment protection by pressurized enclosures "p" ICS 29.260.20 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
cc407ca0-01a8-4991-8aa2-42df544eed7e | HV-A00-000134 FRP 배기덕트공사.doc | ![image](/image/placeholder) SPECIFICATION FOR HVAC & PLUMBING SYSTEM - FRP 배기덕트공사 - SK hynix SK ecoplant 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. | {}
51ae234d-c4b2-494c-91f8-285250f9818f | HV-A00-000134 FRP 배기덕트공사.doc | [제정·개정 이력] ¦ REV. ¦ DATE ¦ 주요 내용 ¦ 비고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 0 ¦ 23.11 ¦ 23.11 이전 변경 내용 정리(M15, M16 시방서 통합) ¦ ¦ ¦ 1 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. | {}
dc7db933-08b9-4b10-a7c6-def53681999a | HV-A00-000134 FRP 배기덕트공사.doc | ¦ HV-A00-00134 FRP 배기덕트공사 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ Rev. 1 Page 1 of 27 ¦ ¦ --- ¦ --- ¦ --- ¦ 1. 일반사항 1.1 적용범위 1.1.1 요약 (1) 이 절은 FRP (Fiber Reinforced Plastics) 배기 덕트 공사에 적용한다. (2) 설계도서, 관계법규 또는 별도로 정한 규정에 의한 것을 제외하고는 모두 본 시방에 준한다. (3) 이 시방서에 기재되지 않은 사항은 국토교통부 제정 "기계설비공사 표준 시방서" 및, '1.3 항 참조표준'을 적용할 수 있다. 단 본 시방서와 상이한 내용은 본 시방서를 우선하여 적용한다. (4) 이 시방서에 특별한 명기가 없는 사항 중 건축, 전기에 관한 사항은 해당 시방서에 따른다. (5) 시방서, 설계도면 및 내역서 중 어느 한 도서에라도 표기되어 있는 사항은 시공하여야 한다. (6) 산업안전보건법에서 규정한 법규에 의해서 시공하여야 한다. 1.1.2 적용 및 우선 (1) 모든 공사는 설계도면 및 시방서에 준하여 시공하며, 설계도면과 시방이 상이한 경우에는 설 계도면을 우선하되 발주 담당자와 협의 하여 정한다. (2) 본 시방서, 설계도면 또는 표준 시방이 정한 공법, 자재 및 제품 등의 내용이 현실적으로 이 행하기 불가능할 경우에는 반드시 발주 담당자에게 서면으로 보고하고 대안에 대한 승인을 득한 후 시공한다. 1.1.3 주요내용 (1) 덕트의 제작 및 설치 (2) 덕트용 부속품의 설치 (3) 덕트의 지지 1.2 관련 시방 1.2.1 일반공통사항 1.2.2 플랜지체결공사 1.2.3. 도장 · 방청 및 부식공사 1.3 참조 표준 1.3.1 한국산업표준 KS B 1002 6 각 볼트 KS B 1012 6 각 너트 및 6 각 낮은너트 KS D 3051 열간 압연 연강판 및 강대 KS D 3052 열간 압연 평강의 모양, 치수 및 무게와 그 허용차 KS D 3500 열간 압연 강판 및 강대의 모양, 치수, 무게 및 그 허용차 KS D 3501 열간 압연 강판 및 강대 KS D 3503 일반 구조용 압연 강재 KS L 2313 유리 로빙 KS L 2314 처리된 유리직물 KS L 2315 유리 로빙포 KS L 2327 절단 유리 섬유 매트 KS M 3305 섬유 강화 플라스틱용 액상 불포화 폴리에스테르 수지 KS M 3331 액상 불포화 폴리에스테르 수지 시험방법 1.3.2 단체표준 SPS-KARSE B 0007-169 공기취입 · 취출구 SPS-KARSE B 0008-170 공기취입 · 취출구의 성능 시험방법 SPS-KARSE B 0009-171 공기조화용 댐퍼 SPS-KARSE B 0010-172 공기조화용 댐퍼의 성능 시험방법 SPS-KARSE B 0013-175 공기조화용 덕트 및 부품 SPS-KARSE B 0016-178 공기조화용 덕트누기 시험방법 SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. SK ecoplant | {}
bba0ae6c-d46d-4ab8-a8ae-2b6294582f52 | HV-A00-000134 FRP 배기덕트공사.doc | ¦ HV-A00-00134 FRP 배기덕트공사 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ Rev. 1 Page 2 of 27 ¦ ¦ --- ¦ --- ¦ --- ¦ SPS-KARSE B 0017-179 공기조화용 덕트소음기 시험방법 1.3.3 국제규격 ¦ ASTM-E 84 ¦ Standard Test Method for Surface Burning Characteristics of Building Materials1 ¦ ¦ --- ¦ --- ¦ ¦ ASTM D256 ¦ Standard Test Method for Determining the Izod Pendulum Impact ¦ ¦ Resistance ¦ of Plastics1 ¦ ¦ ASTM D638 ¦ Standard Test Method for Tensile Properties of Plastics ¦ ¦ ASTM D648 ¦ Standard Test Method for Deflection Temperature of Plastics Undre Flexural Load in the Edgewise Position ¦ ¦ FM 4910 ¦ Cleanroom Materials Flammability Test Protocol ¦ ¦ FM 4922 Exhaust Ducts ¦ Approval Standard for Fume Exhaust Ducts or Fume and Smoke ¦ ¦ ¦ ¦ ¦ SMACNA ¦ ¦ ¦ NBS VOLUNTARY ASTM D 3982 ¦ PS 15~69 Manufacturing to FRP standard Standard specification for Contact Molded"I Fiberglass"(Glass Fiber Reinforced Thermosetting Risin) Ducts ¦ 1.4 제출물 1.4.1 자재 공급 전 제출물 시공자는 다음의 사항을 자재공급 전에 발주 담당자에게 제출하여 승인을 받아야 한다. (1) 주요 기자재공급원 승인요청서 ① KS 규격 인증서 또는 ISO 품질인증서 공급자의 사업자 등록증명원 (단, 외산자재인 경우 납품 회사 분) ③ 국세 및 지방세 완납증명서 (유효기관 확인) ④ 납품실적증명서 (유효기관 확인) ⑤ 품질검사 전문기관 및 국·공립검사기관의 시험성과 표 ⑥ 품질보증각서 : KS 비인증제품, 공인기관 시험 불가제품, 해외제품(시험성적서 제출)등 (2) 필요시 재료에 대한 견본품을 제출하여야 한다. 1.4.2 자재 입고 검사 요청서 자재 반입 시 자재 입고 검사 요청서를 발주 담당자에게 제출하여 확인을 받는다. 1.4.3 검측 요청서 시공 담당자가 검측 요청서를 작성하여 건설사업관리기술인에게 확인을 받은 후 발주 담당자 에게 제출 한다. 1.5 운반, 저장 및 취급 1.5.1 모든 재료는 지정된 장소에 보관한다. 1.5.2 보관, 운반, 상하차 및 시공할 때에는 충격 등으로 관이 손상되지 않도록 하며, 적재·보관 시 주변 하중으로 관의 변형이 발생하지 않도록 하여야 한다. 1.5.3 운반, 저장 및 취급기간 동안 현장제작 또는 공장제작된 덕트, 부속기기 및 구매된 제품이 손 상되지 않도록 보호해야 한다. 1.6 보온공사 SK hynix SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
5514171b-d01f-4a5f-bff5-ec2fa4636105 | HV-A00-000134 FRP 배기덕트공사.doc | ¦ HV-A00-00134 FRP 배기덕트공사 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ Rev. 1 Page 3 of 27 ¦ ¦ --- ¦ --- ¦ --- ¦ 'HV-A00-000150 보온공사' 기준에 따른다. 1.7 도장 · 방청 및 부식공사 'HV-A00-000160 도장 · 방청 및 부식공사' 기준에 따른다. 2. 재료 2.1 일반사항 2.1.1 외부에서 발생하는 충격에 의한 변형을 방지 할 수 있는 충분한 구조적 강도를 유지하여야 한다. 2.1.2 반입시 자재의 변형을 방지하기 위해 보강대를 설치하여야 한다. 2.2 덕트재료 2.2.1 수지(RESIN) - VINYLESTER Type KS M 3305 (섬유 강화 플라스틱용 액상 불포화 폴리에스테르 수지) KS M 3331 (액상 불포화 폴리에스테르 수지 시험방법)의 규격품으로서 저압적측용 액상 불포화 폴리에스테르 수지(LIQUID UNSATURATED POLYESTER RESIN)를 사용한다. 방화등급은 ASTM E84(THE TUNNEL TEST) 규정에 따라 CLASS II(FLAME SPREAD75)등급을 만 족하여야 한다. 2.2.2 덕트 두께 덕트의 두께는 다음 표에 의한다 ¦ 원형덕트의 직경 [⌀] ¦ 내식층 [mm] ¦ 보강층 [mm] ¦ 합계 [mm] ¦ 각형덕트의 장변 [mm] ¦ 내식층 [mm] ¦ 보강층 [mm] ¦ 합계 [mm] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 50 ~ 80 ¦ 3 ¦ 3 ¦ 6 ¦ 150 ~ 450 ¦ 3 ¦ 3 ¦ 6 ¦ ¦ 100 ~ 300 ¦ 3 ¦ 3 ¦ 6 ¦ 500 ~ 850 ¦ 3 ¦ 3 ¦ 6 ¦ ¦ 350 ~ 500 ¦ 3 ¦ 3 ¦ 6 ¦ 900 ~ 1,350 ¦ 3 ¦ 4 ¦ 7 ¦ ¦ 550 ~ 750 ¦ 3 ¦ 3 ¦ 6 ¦ 1,400 ~ 1,650 ¦ 3 ¦ 5 ¦ 8 ¦ ¦ 800 ~ 950 ¦ 3 ¦ 4 ¦ 7 ¦ 1,700 ~ 1,950 ¦ 3 ¦ 6 ¦ 9 ¦ ¦ 1,000 ~ 1,200 ¦ 3 ¦ 6 ¦ 9 ¦ 2,000 ~ 3,000 ¦ 3 ¦ 7 ¦ 10 ¦ ¦ 1,250 ~ 1,450 ¦ 3 ¦ 7 ¦ 10 ¦ ¦ ¦ ¦ ¦ ¦ 1,500 ~ 1,900 ¦ 3 ¦ 8 ¦ 11 ¦ ¦ ¦ ¦ ¦ ¦ 2,000 ~ 2,300 ¦ 3 ¦ 9 ¦ 12 ¦ ¦ ¦ ¦ ¦ ¦ 2,400 ~ 3,000 ¦ 3 ¦ 10 ¦ 13 ¦ ¦ ¦ ¦ ¦ (1) C/R AREA SUB DUCT 의 내식층은 4mm 로 제작, 설치하여야 한다. (2) 탈포 및 성형 시 Touch Up 등의 작업으로 얇아진 적층벽 두께는 규정두께의 90% 이상 되어 야 한다. 그러나 어떠한 경우에도 규정두께의 3.2mm 이상 얇아져서는 안된다. (3) DUCT 는 시공상의 편의 를 위하여 한쪽을 HUB 또는 FLANGE TYPE 으로 제작하고, 1 본의 길이 는 4M(HUB Type 6M)로 하되 중량 혹은 작업성을 고려하여 길이를 조정하여 제작할 수 있 다. 단, 현장여건 상 표준성형 단위 미만으로 제작이 요구되는 경우와 장비(크레인 등) 사용 이 가능한 구역에서 표준성형 단위 길이 이상으로 제작할 경우 일체성형으로 제작하며, 사전 전에 발주 담당자의 승인을 득한 후 성형한다. SK hynix SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
7e11df43-8d1d-4749-a26e-2cfe2dad7caa | HV-A00-000134 FRP 배기덕트공사.doc | ¦ HV-A00-00134 FRP 배기덕트공사 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ Rev. 1 Page 4 of 27 ¦ ¦ --- ¦ --- ¦ --- ¦ 2.2.3 덕트의 물성 덕트의 최소 물성치수는 다음 표에 의한다. ¦ 덕트두께 [mm] ¦ 인장강도 [MPa] ¦ 굴곡강도 [MPa] ¦ 굴곡탄성율 [MPa] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 4.8 이하 ¦ 61.8 ¦ 108 ¦ 4,805 ¦ ¦ 6.4 ¦ 82.4 ¦ 128 ¦ 5,492 ¦ ¦ 8.0 ¦ 93.2 ¦ 137 ¦ 6,178 ¦ ¦ 9.6 이하 ¦ 107.9 ¦ 147 ¦ 6,865 ¦ 2.2.4 강화제(FIBER GLASS) 강화제는 시판되고 있는 유리섬유 중 수지와 의 함침성을 좋게 하기 위해 표면처리 한 것으로서 KS L 2327(절단 유리 섬유 매트), KS L 2313(유리 로빙), KS L 2315(유리 로빙포)의 규정품이거나 이 와 동등이상의 품질을 가진 것이어야 한다. 2.2.5 촉매제, 촉진제 촉매제와 촉진제는 수지공급자의 지정된 재료와 조성에 따라 배합 사용되며 기타 지정된 재료 외에 어떠한 목적에 의해 첨가제를 사용하는 경우는 충분한 실험에 의해 수지생산자가 지정한 범위내로 첨가 할 수 있다. 2.3 접합재료 및 지지재료 2.3.1 강재 (1) KS D 3503(일반 구조용 압연 강재)으로 하며 그 형사, 치수, 중량 및 허용차는 KS D 3051, KS D 3502 및 KS D 3500 에 기재되어 있는 것으로 한다. (2) 수지(RESIN), 강화제(FIBER GLASS), 촉매제, 촉진제, SLIP COLLAR 접합 및 비드 결합 시 사용 되며 '2.2 덕트재료'와 동일한 기준을 적용한다. (3) FRP BOND SLIP COLLAR 내부 접합 시 적용하며, VINYL ESTER 계 접합제를 사용한다. 2.3.2 볼트, 너트 및 와셔 (1) 볼트, 너트 및 와셔의 재료는 KSD 3503(일반구조용 압연강재), 스테인리스강제 및 DACRO 도금 제품으로 한다. (2) 볼트 및 너트는 다음의 제품으로 한다. KS B 1002(6 각 볼트) KS B 1012(6 각 너트 및 6 각 낮은너트) DACRO 도금 사용 시 시험성적서 첨부 (3) 와셔는 KS B 1326(평와 셔) 제품으로 한다. (4) 앵커 볼트의 나사는 KS B 1002(6 각 볼트)의 나사에 준한다. (5) 고장력 볼트, 너트 및 평와 셔의 세트는 KS B 1010(마찰접합용 고장력 6 각볼트, 6 각너트, 평와 셔의 세트), TS 볼트, 너트는 KS B 2819(구조물용 토크 전단형 고장력 볼트, 6 각너트, 평와 셔의 세트)의 제품으로 한다. 2.3.3 플랜지용 개스킷(테프론 Gasket) (1) 순수 PTFE(100%) 재질로 특수하게 제작된 것으로 종래의 Asbestos, Rubber 계통의 개스킷류 의 단점인 내약품성을 보완한 제품으로 한다. (2) 물리적 특성 SK hynix SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
fb41fe4c-7006-436f-bafc-6a3ff0256bc6 | HV-A00-000134 FRP 배기덕트공사.doc | ¦ HV-A00-00134 FRP 배기덕트공사 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ Rev. 1 Page 5 of 27 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 구 분 ¦ 내 용 ¦ 비 고 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 재 질 ¦ 연질 PTFE (Poly Tetra Fluoro Ethylene) ¦ 100% ¦ ¦ 융 해 점 ¦ 317°C ¦ ¦ ¦ 최소 체결 압력 ¦ WIDE 7~10mm : 12.26MPa 13mm : 14.71MPa ¦ ¦ ¦ 사용 가능 압력 ¦ 기체 : 1.96MPa 액체 : 4.9MPa ¦ ¦ ¦ 사용 가능 온도 ¦ -110°C ~ 250°C ¦ ¦ ¦ 열 전 도 율 ¦ 0.03 kcal/m.h.°C ¦ ¦ ¦ 내 화 학 성 ¦ 내산, 내알카리, 내약품성 ¦ ¦ 2.3.4 지지재료 (1) 지지재료는 KS D3503(일반 구조용 압연 강재) L-형강 및 � -형강 및 H-Beam 으로 한다. (2) FAB 내부에 설치되는 지지재료는 용융 아연도금된 제품으로 한다. (3) 덕트 관말 부분에는 덕트 상하에 Double Angle 또는 Double Channel 을 설치하여 고정한다. (4) 행거볼트 끝단부는 너트 체결 후 여산은 하부 받침 철물(앵글 등) 하단 이내로 절단 후 RED CAP 처리한다. 2.3.5 밀봉재 합성고무, 기타의 재료로 하고 덕트와 잘 접착하며 내구성이 있는 비 초산계로 한다. 3. 시공 3.1 공통사항 3.1.1 일반사항 (1) 외부에서 발생하는 충격에 의한 변형을 방지 할 수 있는 충분한 구조적 강도를 유지하여야 한다. (2) 덕트 설치 시 HUB 타입 시공을 원칙으로 하나 향후 재사용 및 증설을 필요로 할 경우를 고려하여 발주처 협의 하에 덕트를 플랜지(Flange)타입으로 시공한다. (3) FRP 덕트 접합 작업 시에는 충분한 환기를 실시하여야 한다. 건물 내부: 무취 수지 사용 3.2 덕트 제작 및 설치 3.2.1 FRP 덕트 제작 (1) 몰드(MOLD)의 준비 몰드의 제작 상테에 따라 품질이 비례하므로 정확한 규격과 뒤틀림이 없도록 목형 및 FRP, 금속제 등의 재질로 제작하며 철저히 검수하여 작업 후 문제점이 발생하지 않도록 한다. (2) 이형재 처리 몰드 표면에 제품의 탈형을 원활하게 하기 위해 왁스(Wax) 또는 P.V.A(Poly Vinyl Acetate)를 도포 후 상온에서 건조시킨다. (3) 표층(내식표면층) 적층 ① 몰드 표면에 털 로라 등을 사용하여 수지를 도포한다. ② 유리섬유가 노출되지 않도록 수지를 충분히 함침시켜 서페이스 매트(Surface Mat)를 1~2PLY (두께 0.25~0.5mm) 적층한다. ③ 적층시 서페이스 매트의 겹침은 최저 50mm 이상이 되어야 하고, 박리현상 및 잔크랙, 균열등 SK hynix SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
0dec0c56-ce9b-41c6-8597-dc9a54556e5e | HV-A00-000134 FRP 배기덕트공사.doc | ¦ HV-A00-00134 FRP 배기덕트공사 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ Rev. 1 Page 6 of 27 ¦ ¦ --- ¦ --- ¦ --- ¦ 이 있어서는 안되고, 직경 3mm 이상 핀홀이 30cm2 당 2 개 이상 존재해서는 안된다. (4) 중간층(내식층) 적층 ① 내식층을 형성하기 위해 춥드 스트랜드 매트(Chopped Strand Mat)를 3~4PLY(두께 3mm 이상) 수지에 함침시켜 적층한다. ② 중간층의 유리섬유와 수지의 비율은 25~35% : 75~65%로 한다. ③ 적층 작업시 탈포기를 사용하여 핀홀을 최대한 제거하며, 춥드 스트랜드 매트의 겹침은 최소 25mm 이상 되어야 하고 겹치는 부위의 중복을 피해야 한다. (5) 외층(강화층) 적층 ① 제품의 강도를 높이기 위해 와인딩 기계(Winding Machine)를 이용하여 그라스 로빙(Glass Roving)을 20~50 가락을 함침 후 감는다. ② 외층의 유리섬유와 수지의 비율은 65~70% : 35~30%로 한다. 와인딩 각도(Winding Angle)는 60~70° 내외가 적당하나 제품 규격에 따라 달라진다. ④ 만약 최외층이 부식환경에 접할 경우 표층과 동일한 방법으로 제작한다. (6) 최외층 도색 공기와 햇볕 접촉에 의한 경화 장해 및 스티렌 모노마(Styrene Monomer)의 휘산 등을 방지하 기 위해 파라핀 왁스(Paraffin Wax, 0.2~0.4wt%)와 자외선 차단재(0.2wt%)를 수지나 겔코트(Gel Coat)에 혼합하여 도색한다. 덕트 색상은 아이보리색으로 하며 아래 색상 코드를 참조하여 시공한다. - 한국페인트잉크공업협동조합 코드 : E-30891 - Munsell No. : 2.2Y 9.1/1.2 (7) 경화 및 탈형 성형 작업완료 후 상온에서 2~4 시간 동안 선경화 후, 60~100°C 에서 2~3 시간 동안 후경화를 시킨 후 탈형 한다. 3.2.2 덕트의 접합 (1) Slip Collar 접합 ① 덕트의 절단은 상대 덕트와 의 틈이 6.4mm 이상을 초과 하지 않아야 하며, 지그(Zig)를 이용하 여 Marking 후 직선, 회전공구로 절단하며, 내부를 본드로 접합한 후 외부에서 적층한다. ② 직경 ⌀600 이상의 덕트로써 분지, 현장가공 등으로 Slip Collar 이음을 하는 경우 덕트 이음 부 내부틈새는 FRP 본드를 사용하여 Overlay 를 실시하여야 한다. (하부측 180 。 원주만큼은 5PLY, 기타 상부는 3PLY) Slip Collar 규격은 다음 표에 의한다 ¦ 사각 덕트의 장변 또는 원형 덕트의 직경 ¦ Slip Collar ¦ Slip Collar ¦ Bead ¦ Bead ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 사각 덕트의 장변 또는 원형 덕트의 직경 ¦ 두께 (t) ¦ 삽입 길이 (L) ¦ 두께 (t') ¦ 폭 (b) ¦ ¦ 750 이하 ¦ 3 ¦ 105 ¦ 5 ¦ 6 ¦ ¦ 750 초과 ¦ 3 ¦ 120 ¦ 5 ¦ 6 ¦ SK hynix SK ecoplant 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. | {}
89283a93-b723-47e4-875d-f28b655bf4fc | HV-A00-000134 FRP 배기덕트공사.doc | ¦ HV-A00-00134 FRP 배기덕트공사 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ Rev. 1 Page 7 of 27 ¦ ¦ --- ¦ --- ¦ --- ¦ Chart Type: line Bead Thickness Internal Extension Length item_01 3Degrees (°) 2Degrees (°) [Slip Collar 설치 상세도] Slip Collar 적층 규격은 다음 표에 의한다 ¦ 사각 덕트의 장변 또는 원형 덕트의 직경 ¦ 적층 두께 (t) ¦ 적층 폭 (b) ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 500 이하 ¦ 3 ¦ 150 ¦ ¦ 500 초과 700 이하 ¦ 3 ¦ 150 ¦ ¦ 700 초과 1,500 이하 ¦ 4 ¦ 200 ¦ ¦ 1,500 초과 ¦ 5 ¦ 300 ¦ ![image](/image/placeholder) Bond Putty D(a) =Nominal Size Grinding Duct Thickness Overlay Thickness (t) Overlay Width (b) [Slip Collar 적층 설치 상세도] (2) BEAD 결합 덕트의 결합형성상 접합 Flange 를 낼 수 없거나 Main 덕트에서 Branch 덕트가 발생되는 경우 BEAD 결합을 할 수 있다. 결합부위는 덕트 본체 두께 이상으로 충분한 강도가 유지되어야 한다. SK hynix SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
b214b564-ac0e-4cba-a506-b846f04d0a94 | HV-A00-000134 FRP 배기덕트공사.doc | ¦ HV-A00-00134 FRP 배기덕트공사 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ Rev. 1 Page 8 of 27 ¦ ¦ --- ¦ --- ¦ --- ¦ ① Duct 접합 Point 의 위치가 Flange 나 Hub 를 낼 수 없는 경우 ② 가지관(Branch Duct), 점검창(Sight Glass) 및 기타 부속품(Test Port, Hook up 용 Nozzle 등) ③ 설계 변경 등으로 Duct 절단 후 Flange, Slip Collar, Hub 접합으로 시공이 불가한 경우 ④ 덕트 절단면과 상대 Duct 와의 틈은 FRP Putty 로 틈을 메우고 FRP Overlay 로 마감 한다 BEAD 결합 시 FRP Overlay 폭은 다음 표를 따른다. ¦ 덕트의 두께 [mm] ¦ 6 이하 ¦ 6 초과 ~ 8 이하 ¦ 8 초과 ~ 10 이하 ¦ 10 초과 ~ 15 이하 ¦ 18 초과 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 최소접합 폭 [mm] ¦ 100 ¦ 150 ¦ 200 ¦ 250 ¦ 300 ¦ (3) FLANGE 접합 Flange 접합 기준은 다음 표에 의한다 ¦ 사각 덕트의 장변 또는 원형 덕트의 직경 ¦ 접합용플랜지 ¦ 접합용플랜지 ¦ 접합용플랜지 ¦ 접합용플랜지 ¦ 접합용볼트 ¦ 접합용볼트 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 사각 덕트의 장변 또는 원형 덕트의 직경 ¦ 폭 ¦ 두께 ¦ 최대이음간격 ¦ 보강시겹침폭 ¦ 지름 ¦ 간격 ¦ ¦ 500 이하 ¦ 65 ¦ 13t ¦ 6,000 ¦ 3t X 100W ¦ M12 ¦ 100 ¦ ¦ 500 초과 750 이하 ¦ 65 ¦ 16t ¦ 6,000 ¦ 4t X 150W ¦ M12 ¦ 100 ¦ ¦ 700 초과 1,500 이하 ¦ 65 ¦ 18t ¦ 6,000 ¦ 5t X 150W ¦ M12 ¦ 100 ¦ ¦ 1,500 초과 2,000 이하 ¦ 75 ¦ 20t ¦ 6,000 ¦ 6t X 200W ¦ M12 ¦ 100 ¦ ¦ 2,000 초과 ¦ 75 ¦ 22t ¦ 6,000 ¦ 8t X 200W ¦ M12 ¦ 100 ¦ * 접합용 플랜지는 덕트본체와 일체성형 후 수작업으로 보강하여 접합용 볼트로 결속한다. * 볼트 재질은 STS304 및 DACRO 도금 재질이며 개스킷(Gasket)은 Top Seal 을 사용한다. * FLANGE SIZE 는 KS 규격에 따른다. (4) HUB 접합 ① 부속품의 재질, 제조방법, 기계적특성 등은 FRP 덕트에 준한다 ② 덕트 Hub 의 상대 덕트와 의 틈이 6.4mm 이상을 초과 하지 않아야 한다. ![image](/image/placeholder) 4040 4,000(L) - De+12 HUB 의 규격은 다음 표와 같다. ¦ 덕트 규격((D) ¦ HUB 적용 길이(A) ¦ ¦ --- ¦ --- ¦ ¦ ~850A ¦ 40 ¦ SK hynix SK ecoplant 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. | {}
77f774a2-821f-4b4a-a7b1-7b047c8c22e5 | HV-A00-000134 FRP 배기덕트공사.doc | ¦ HV-A00-00134 FRP 배기덕트공사 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ Rev. 1 Page 9 of 27 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 900A ~ 1350A ¦ 50 ¦ ¦ --- ¦ --- ¦ ¦ 1400A ~ 1950A ¦ 60 ¦ ¦ 2000A ~ 2450A ¦ 80 ¦ ¦ 2500A ~ 3000A ¦ 100 ¦ Hub 끼워맞춤 이음부의 틈은 FRP Putty 를 사용하여 면처리를 하고 FRP OVERLAY 처리한다 FRP PUTTY ![image](/image/placeholder) A B FRP OVERLAY 기준은 다음 표와 같이 한다 (단위 : mm) ¦ 덕트 규격(D) ¦ 덕트 시방 두께(t) ¦ FRP OVERLAY "A" ¦ FRP OVERLAY "B" ¦ FRP Overlay (접합폭) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 350A~750A ¦ 6 ¦ 5 ¦ 미적용 ¦ ~500A(150mm) ¦ ¦ 800A~950A ¦ 7 ¦ 5 ¦ 미적용 ¦ 600A~1700(200mm) ¦ ¦ 1000A~1200A ¦ 9 ¦ 5 ¦ 미적용 ¦ 600A~1700(200mm) ¦ ¦ 1250A~1450A ¦ 10 ¦ 5 ¦ 미적용 ¦ 600A~1700(200mm) ¦ ¦ 1500A~1900A ¦ 11 ¦ 5 ¦ 5 ¦ 1800A~2800A(250m m) ¦ ¦ 2000A~2300A ¦ 12 ¦ 5 ¦ 5 ¦ 1800A~2800A(250m m) ¦ SK hynix SK ecoplant 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. | {}
b43e4269-10c5-4204-b37e-04ed8124011e | HV-A00-000134 FRP 배기덕트공사.doc | ¦ HV-A00-00134 FRP 배기덕트공사 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ Rev. 1 Page 10 of 27 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 2400A~3000A ¦ 13 ¦ 5 ¦ 5 ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ 3.2.3 무단기 작업 무단기 작업을 하기 위하여 BLIND PANEL 을 설치 할 경우, FLANGE GASKET(TOP SEAL)을 FRP 덕트 플랜지에 결속 조치하여 BLIND 제거 시 SEAL 의 위치이탈, 손상이 발생하지 않도록 한다. (BLIND 제거 후 결속선 제거 및 FLANGE 볼트 체결) 3.2.4 볼트 조이기 (1) 나사산 완전체결 후 여장길이는 최소 3 산 ~ 체결 BOLT 지름의 1.5 이하로 한다. (2) 같은 플랜지에 체결되는 볼트/너트는 동일한 볼트/너트를 사용하여야 하며 같은 여장길이를 가져야 한다. (3) 스터드 볼트의 경우 동일한 플랜지에서는 양족으로 나온 볼트의 길이가 동일하게 여산이 나 오도록 체결한다. (4) 볼트의 I 마킹대상 및 기준은 'HV-A00-00170 플랜지체결공사'를 참조한다 (5) 플랜지체결은 배관과 동일하게 'HV-A00-00170 플랜지체결공사'에 의한다. (기체도 유체와 동일하게 관리 한다) 3.2.5 내화구조의 인정 및 관리기준(국토교통부고시 제 2018-772 호)에 따른 내화충전구조로 인증된 방법 및 재료로 충진한다. 3.3 덕트의 지지 및 방진 3.3.1 덕트의 지지 (1) HANGER 지지 옥내 설치 시 덕트를 상부에서 지지 할 때 사용한다. 장비에서 발생하는 진동이나 수축팽창 시 발생하는 응력이 덕트를 통해 건물에 직접 전달되 않도록 진동절연이 우수한 고무행거를 설치한다. 행거는 수직으로 정확히 설치되어야 한다. ① 지지간격은 발주 담당자와 협의 하여 변경 할 수 있음. ② 행거는 덕트전용으로 설치해야 하며 트레이 등 타용도의 지지물과 혼용하면 안된다. ③ 1,000mm 기준 최소 2 개 방진 PAD 상부 또는 상/하부(이중행거) 설치한다. 500mm 초과 시 마다 1 개 방진 PAD 하부에 추가한다 (방진 패드는 등 간격으로 설치) ④ 방진 패드 너비는. 서포트 양쪽 폭 방향으로 10mm 이상 나오도록 설치한다. ⑤ 덕트의 연결 길이가 10m 이상일 경우 행거 지지는 10m 마다 1 개소씩 상·하부 이중 행거를 사용한다. ⑥ 지상층 덕트 행거 고정 시 반드시 12m 이내에 1 개소 이상 � 형강, L 형강 보강 할 것. ⑦ 원형덕트의 지지는 다음 표에 의한다 ¦ 원형덕트의 직경 [⌀] ¦ BOLT & NUT ¦ RUBBER HANGER ⓑ ¦ 전산 BOLT ⓒ ¦ STEEL FLATBAR ⓓ ¦ RUBBER ¦ 방진 PAD ¦ SUPPOR T 간격 [mm] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 500 이하 ¦ M12 ¦ 100kg/EA ¦ M12 ¦ 100 X 6t ¦ 4.8t ¦ 100x50 ¦ 3,000 ¦ ¦ 500 초과 ~ 1,000 이하 ¦ M12 ¦ 100kg/EA ¦ M12 ¦ 100 X 9t ¦ 4.8t ¦ 100x50 ¦ 3,000 ¦ SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. SK ecoplant | {}
c3341adf-2443-4e51-9bff-0c1069d54651 | HV-A00-000134 FRP 배기덕트공사.doc | ¦ HV-A00-00134 FRP 배기덕트공사 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ Rev. 1 Page 11 of 27 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ 100kg/EA ¦ 4.8t ¦ ¦ ¦ 3,000 ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1,000 초과~ 1,500 이하 ¦ M12 ¦ ¦ M12 ¦ 100 X 12t ¦ 100x50 ¦ ¦ ![image](/image/placeholder) Rubber (3t) - - NEORENE Rubber PAD (20t) NEORENE Rubber PAD (20t) 방진 PAD : NEOPRENE RUBBER PAD [수평덕트 설치 상세도] ⑧ 전산볼트(달대볼트)의 적용에 의한 배관 및 덕트 등 천정 구조물의 지지시 전산볼트 (달대볼트)의 각 연결부에 대해 풀림방지를 위한 Flange Nut 를 적용하고 진동 등에 의해 풀리지 않도록 공구에 의해 조임을 진행하도록 한다. ![image](/image/placeholder) Flange Nut Flange Nut 연결 너트 - 풀림 방지기능 [전산볼트(달대볼트)의 적용 상세 - 배관 및 덕트] (2) SHOE 지지 옥외 설치 시 덕트를 하부에서 지지할 때 사용한다. 수평 덕트 등에 사용하며 덕트의 하중이 골고루 분포될 수 있는 구조의 SHOE 을 사용한다. SHOE 지지 기준은 다음 표에 의한다 SK hynix SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
32772b14-cb02-4079-bbca-26925a8e51f4 | HV-A00-000134 FRP 배기덕트공사.doc | ¦ HV-A00-00134 FRP 배기덕트공사 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ Rev. 1 Page 12 of 27 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 원형덕트의 직경 [⌀] ¦ STEEL PLATBA R ¦ BOLT & NUT ¦ STEEL FLATBAR ⓒ ¦ RUBBER ¦ SHOE 높이 [mm] ¦ SUPPORT 간격 [mm] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 400 이하 ¦ 50 X 6t ¦ M10 ¦ 75 X 6t ¦ 4.8t ¦ 100 ¦ 3,000 ¦ ¦ 400 초과 ~ 500 이하 ¦ 50 X 6t ¦ M12 ¦ 100 X 6t ¦ 4.8t ¦ 100 ¦ 3,000 ¦ ¦ 500 초과 ~ 700 이하 ¦ 50 X 6t ¦ M12 ¦ 100 X 6t ¦ 4.8t ¦ 100 ¦ 3,000 ¦ ¦ 700 초과 ~ 800 미만 ¦ 50 x 6t ¦ M12 ¦ 100 X 6t ¦ 4.8t ¦ 100 ¦ 3,000 ¦ ¦ 800 이상 ~ 1,500 이하 ¦ 65 X 6t ¦ M12 ¦ 100 X 9t ¦ 4.8t ¦ 100 ¦ 3,000 ¦ ¦ 1,500 초과 ~ 2,000 이하 ¦ 65 X 6t ¦ M16 ¦ 150 X 9t ¦ 4.8t ¦ 100 ¦ 3,000 ¦ ¦ 2,000 초과 ~ 3,000 이하 ¦ 65 X 6t ¦ M16 ¦ 200 X 9t ¦ 4.8t ¦ 100 ¦ 3,000 ¦ * Shoe 의 높이는 방진고무를 제외한 바닥으로부터 Flat Bar 아랫면까지의 거리로 한다. ![image](/image/placeholder) 120° 방진고무 20t 100l [SHOE 지지 상세도] (3) SUPPORT 지지 바닥 설치 시 덕트를 하부에서 지지할 때 사용한다. 별도의 SUPPORT 를 제작하여 설치 하며 하부 바닥 ANCHOR 시공을 한다. CHEMICAL ANCHOR 또는 SET ANCHOR 로 시공한다 SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. SK ecoplant | {}
62d6b335-8fdc-4645-a00a-5a86992ff395 | HV-A00-000134 FRP 배기덕트공사.doc | ¦ HV-A00-00134 FRP 배기덕트공사 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ Rev. 1 Page 13 of 27 ¦ ¦ --- ¦ --- ¦ --- ¦ ![image](/image/placeholder) 100 [SUPPORT 지지 상세도] SUPPORT 지지 기준은 다음 표에 의한다 ¦ 원형덕트의 직경 [⌀] ¦ 전산 BOLT ¦ BOLT & NUT ¦ STEEL PLATBAR ⓒ ¦ RUBBER ⓓ ¦ 방진 PAD ¦ ANCHOR ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 400 이하 ¦ M12 ¦ M12 ¦ 50 X 6t ¦ 4.8t ¦ 50x50 ¦ M12 CHEMICAL ¦ ¦ 400 초과 ~ 500 이하 ¦ M12 ¦ M12 ¦ 100 X 6t ¦ 4.8t ¦ 100x100 ¦ M12 CHEMICAL ¦ ¦ 500 초과 ~ 700 이하 ¦ M12 ¦ M12 ¦ 100 X 6t ¦ 4.8t ¦ 100x100 ¦ M12 CHEMICAL ¦ ¦ 700 초과 ~ 800 미만 ¦ M12 ¦ M12 ¦ 100 x 6t ¦ 4.8t ¦ 100x100 ¦ M12 CHEMICAL ¦ ¦ 800 이상 ~ 1,500 이하 ¦ M12 ¦ M12 ¦ 100 X 9t ¦ 4.8t ¦ 100x100 ¦ M12 CHEMICAL ¦ ¦ 1,500 초과 ~ 2,000 이하 ¦ M12 ¦ M12 ¦ 150 X 9t ¦ 4.8t ¦ 150x100 ¦ M12 CHEMICAL ¦ ¦ 2,000 초과 ~ 3,000 이하 ¦ M12 ¦ M12 ¦ 200 X 9t ¦ 4.8t ¦ 200x100 ¦ M12 CHEMICAL ¦ 3.3.2 덕트 입상의 지지보강 덕트 SHAFT 등과 같이 수평 DUCT 에서 입상 DUCT 로 바뀌는 ELBOW 부위는 입상 DUCT 자중에 의한 처짐을 방지하기 위해 지지간격과 별도의 추가 보강을 하여야 한다. 3.4 덕트 DRAIN 배관 입상덕트의 하부나 응축수 고임 예상 부위 및 덕트 내 SPRINKLER HEAD 설치부에 원활한 배수를 위하여 DRAIN PORT 를 설치한다. DRAIN PORT 는 배출가스의 흐름에 방해가 되지 않는 모양으로 제작하고 PE, STS, FM PVC 배관이나 밸브 등의 부속재와 연결하여 배수 될 수 있어야 한다. 또한, 추후 CLEANING 을 위하여 분해 및 조립이 용이한 구조로 설치하여야 한다. 3.4.1 DRAIN PORT 및 배관 설치 구분 ¦ 구 분 ¦ SUB FAB ¦ SUB FAB ¦ PLENUM ¦ PLENUM ¦ Scrubber RM ¦ Scrubber RM ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 구 분 ¦ SUB ¦ HEADER ¦ SUB ¦ HEADER ¦ Riser Duct ¦ Header ¦ ¦ Acid ¦ 50A HF ¦ 100A HF (25m 간격) ¦ 50A HF ¦ 100A HF (25m 간격) ¦ 50A HF ¦ 100A HF (25m 간격) ¦ ¦ Acid(MAC), Acid(PFC) ¦ 100A HF ¦ 100A HF (35m 간격) ¦ - ¦ - ¦ 50A HF ¦ - ¦ SK hynix SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
6fdc6bbd-3c94-4c07-b76d-b2961c5bc8e4 | HV-A00-000134 FRP 배기덕트공사.doc | ¦ HV-A00-00134 FRP 배기덕트공사 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ Rev. 1 Page 14 of 27 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Alkali ¦ 50A HF ¦ 100A HF (15m 간격) ¦ 50A HF ¦ - ¦ 50A HF ¦ 100A HF (25m 간격) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Heat/Gen ¦ · ¦ - ¦ 미적용 ¦ 미적용 ¦ 미적용 ¦ GALV. ¦ ¦ Organic ¦ ¦ ¦ 50A Solvent ¦ 50A Solvent (25m 간격) ¦ 50A Solvent ¦ 50A Solvent (25m 간격) ¦ ¦ Cabinet ¦ 미적용 ¦ 미적용 ¦ 미적용 ¦ - ¦ 미적용 ¦ 100A HF (25m 간격) ¦ ¦ Emer. ¦ 미적용 ¦ 미적용 ¦ 미적용 ¦ 미적용 ¦ 미적용 ¦ 미적용 ¦ * ACID, ALKALI, CABINET DUCT DRAIN 의 재질은 P.E(PolyEthylene) - FM PVC 로 한다. * ORG DUCT DRAIN 의 재질은 STS304 로 한다. * DRY, H/G 은 Roof Header 에 Port 만 구성하고 PVC 볼밸브로 마감한다. 설치 순서 Sub FAB & Plenum: Drain Port → Ball Valve → 무봉수 Trap F03, F04 Utility, CR 노출 Duct: Drain Port → Sight Glass → Ball Valve → Blind Flange 마감 3.4.2 FM PVC DRAIN 배관 (1) 작업 도구 준비 작업 시작 전 작업을 위한 각종 자재(프라이머, 접착제 및 각종 공구)를 사전에 준비한다. (2) 파이프 절단 파이프는 가능한 한 직각으로 CUTTING 하여야 한다. (3) 내외경 면취 내외경 면취의 경우 모서리 따기용 줄이나 BEVELING TOOL 을 이용하되 파이프 끝에서 1/16" ~3/32"의 폭으로 10~15 °의 경사를 주어 면취한다. (4) 접합면 청소 수분 및 유분 기타 이물질은 파이프 및 피팅의 표면 용해 및 접착에 방해를 줄 수 있으므로 깨끗하고 마른 걸레로 파이프와 피팅류의 안팎에 있는 먼지, 유분, 톱밥이나 물기들을 모두 제거하여야 한다. (5) 삽입 깊이 체크 ① 접착제를 도포하기 전에 파이프 및 피팅을 똑바로 가볍게 삽입시켜 파이프가 수구 길이의 1/3~2/3 지점에서 멈추어지는 확인한다. ② 파이프가 완전히 삽입되었는지를 확인하기 위해 피팅 소켓의 길이를 측정하여 그 간격을 파이프 외면에 표시한다. ③ 프라이머와 접착제를 도포할 때, 표시(Marking)가 지워질 수 있으므로 그 길이에 20mm 위 치 추가 Marking 한다. 소켓 사이 배관 최소 치수 50mm 이상(노출부 기준) (6) 접착제 도포 ① 파이프와 피팅이 깨끗하고 습기와 부스러기가 없을 때 솔벤트 접착제를 도포해야 하며, 바 른 프라이머가 진득진득할 때 즉시 도포해야 한다. ② 접착제는 칠붓, 천연모 브러시 또는 파이프 직경의 약 1/2 SIZE 인 롤러를 사용하여 접합 표 면에 도포해야 한다. 파이프 끝부분 바깥에 이음 소켓의 길이와 같게 접착제를 두껍게 칠한 다. ③ 칠하는 양은 간격을 채우는데 충분한 분량 이상이 되어야 하며, 이음 소켓에는 중간 정도로 칠하되 뒤범벅되지 않도록 한다. (7) 조립 ① 양쪽 표면이 솔벤트 접착제로 적셔져 있는 동안 파이프를 1/4 바퀴 회전시키면서 신속하게 이음매 소켓에 끼워넣는다. ② 파이프는 이음재 중단점에 완전하게 자리를 잡아야 한다. ③ 최초 접합이 확실히 되도록 약 30 초 동안 잡고서 조립상태를 유지한다. ④ 억지로 삽입한 맞춤부의 테이퍼(경사진면) 때문에 최초 접착 중에 일정한 압력이 유지되지 않으면 파이프는 이음매 중단점에서 뒤로 물러날 수 있다. ⑤ 파이프 주변과 이음재 연결부에 접착제 방울이 보여야 한다. SK hynix SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
e0ad18e2-9f07-4453-8ad6-dd1ca550338a | HV-A00-000134 FRP 배기덕트공사.doc | ¦ HV-A00-00134 FRP 배기덕트공사 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ Rev. 1 Page 15 of 27 ¦ ¦ --- ¦ --- ¦ --- ¦ 이 방울이 소켓 어깨 주위로 연속되어 나타나지 않으면 접착제가 충분하지 않게 도포되었 음을 표시하는 것이다. 불충분하게 접착제가 도포되면 접합부를 잘라내고 다시 접합하여야 한다. ⑥ 접착제 방울이 과다하면 헝겊으로 닦아내어야 한다. 3.4.3 FM PVC DRAIN PORT 제작 기준 ¦ 원형덕트 직경 [⌀] ¦ DRAIN PORT 규격 [mm X mm X ⌀] ¦ ¦ --- ¦ --- ¦ ¦ 400 미만 ¦ 100[⌀] 직결 ¦ ¦ 400 이상 ¦ 300x300x100 ¦ 3.5 점검구 및 점검창 설치 ¦ 덕트의 직경 [⌀] ¦ 점검구 ¦ 점검구 ¦ 점검창 ¦ 점검창 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 덕트의 직경 [⌀] ¦ SIZE ¦ 재질 ¦ SIZE ¦ 재질 ¦ ¦ 400 이하 ¦ 200x200 ¦ FRP ¦ 200x200 ¦ FRP+투명 PC ¦ ¦ 400 초과 ~ 800 미만 ¦ 200x200 ¦ FRP ¦ 200x200 ¦ FRP+투명 PC ¦ ¦ 800 이상 ~ 1,500 이하 ¦ 400x400 ¦ FRP ¦ 400x400 ¦ FRP+투명 PC ¦ ¦ 1,500 초과 ~ 2,000 이하 ¦ 500x500 ¦ FRP ¦ 500x500 ¦ FRP+투명 PC ¦ ¦ 2,000 초과 ~ 3,000 이하 ¦ 500x500 ¦ FRP ¦ 500x500 ¦ FRP+투명 PC ¦ 3.6 EXPANSION JOINTS 3.6.1 옥외에 설치되어 일사에 노출되는 FRP DUCT 는 THERMAL EXPANSION 을 해석하여 변위량을 산정후, EXPANSION JOINTS 적절하게 배치하여 (Max. 80m 간격) 외기 온도 변화에 따른 FRP DUCT 신축에 충분히 대응될 수 있도록 한다. 3.6.2 EXPANSION JOINT 는 내식성 재료로 제작되어야 하며 허용 압력에 충분한 강도를 가져야 한 다. 3.6.3 덕트 SIZE 별로 ⌀200~ ⌀1000 까지는 기성품 주문제작 (BELLOWS TYPE) 으로 TEFRON 재질을 적용 하고, ⌀1000 이상의 제품은 SLIDING TYPE 을 적용한다. 3.6.4 AXIAL MOVEMENT 는 THERMAL EXPANSION 해석하여 산정하며, 최소 ±100mm 이 되도록 한 다. 또한, EXPANSION JOINT 는 외부 보호를 위하여 적절한 COVER 를 설치한다. 3.6.5 EXPANSION JOINT 전후단 DUCT 에 GUIDE SHOE 를 설치하여 EXPANSION JOINT 자중으로 인한 처짐 방지 및 덕트 중량이 EXPANSION JOINT 에 영향을 미치지 않도록 한다. (1) EXPANSION JOINT 로 덕트를 지지할 수 없다. (2) 기성품 EXPANSION JOINT 의 SET BOLT 는 변위량 값의 여유를 주어 신축이 가능하도록 NUT 를 풀어준다. (3) EXPANSION JOINT 가 설치되는 DUCT 에는 적정한 위치에 ANCHOR (STOPPER) SUPPORTS 를 설치하여야 한다. (4) 각각의 DUCT SHOE or SADDLE 은 계산된 THERMAL MOVEMENT 만큼 원활한 SLIDING 이 이루어지도록 하고, SHOE or SADDLE 폭은 THERMAL MOVEMENT 를 고려하여 확정한다. SK hynix SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
5fddccc3-8f1d-4a92-8bab-6d1f93e34acc | HV-A00-000134 FRP 배기덕트공사.doc | ¦ HV-A00-00134 FRP 배기덕트공사 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ Rev. 1 Page 16 of 27 ¦ ¦ --- ¦ --- ¦ --- ¦ (5) DUCT SHOE or SADDLE 에는 DUCT 보호를 위하여 일정 거리마다 GUIDE or SLOT HOLES 을 설치 하고, SLOT HOLE 크기는 THERMAL MOVEMENT 를 충분히 흡수하도록 제작하고 THE- RMAL MOVEMENT 방향으로 설치 한다. 3.6.5 BELLOWS TYPE EXPANSION JOINT (DUCT SIZE : ⌀200~ ⌀1000) ![image](/image/placeholder) (1) EXPANSION JOINT 사양 ¦ SPECIFICATION ¦ SPECIFICATION ¦ ¦ --- ¦ --- ¦ ¦ FLUID ¦ ACID or ALKALI GAS ¦ ¦ DESIGN TEMPERATURE ¦ -20 ~ 60°C ¦ ¦ DESIGN PRESSURE ¦ 1500 mmAq ¦ ¦ AXIAL MOVEMENT ¦ THERMAL EXPANSION 산출량 (MIN. ±100mm) ¦ ¦ LATERAL MOVEMENT ¦ ±10mm ¦ (2) EXPANSION JOINT 구성 ![image](/image/placeholder) CUFF : TEFLON COATED G/F · ④ 않는 RUBBER) RUBBER 500 STS304 ⑥ ⑥ PTFE TUBE REAINFORNACE FABRIC ④ ④ 수 中 INSIDE RUBBER(SILICONE RUBBER) 最 TEFLON SHEET(0.3Tx2PLY) ¦ NO ¦ DESCRIPTION ¦ MATERIALS ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ FLANGE ¦ STS304 ¦ ¦ 2 ¦ BELLOWS ¦ 상기 상세 도면 참조 ¦ ¦ 3 ¦ END PIPE ¦ STS304 ¦ ¦ 4 ¦ OUT RING ¦ STS 304 ¦ ¦ 5 ¦ INNER RING ¦ STS 304 ¦ SK hynix SK ecoplant 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. | {}
9dde9ed2-bd99-404f-ab03-a397a0b3d2e8 | HV-A00-000134 FRP 배기덕트공사.doc | ¦ HV-A00-00134 FRP 배기덕트공사 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ Rev. 1 Page 17 of 27 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 6 ¦ RING-1 ¦ STS 304 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 7 ¦ RING-2 ¦ STS 304 ¦ ¦ 8 ¦ COVER 1 ¦ STS 304 ¦ ¦ 9 ¦ COVER 2 ¦ STS 304 ¦ ¦ 10 ¦ HOLDER ¦ STS 304 ¦ ¦ 11 ¦ SET BOLT & NUT ¦ SS 275 ¦ ¦ 12 ¦ GASKET ¦ 연질 TEFRON ¦ ¦ 13 ¦ HEX BOLT & NUT ¦ STS 304 ¦ 3.6.5 BELLOWS SLIDING TYPE EXPANSION JOINT (DUCT SIZE : ⌀1000~ ⌀3000) (1) FRP DUCT SIZE 가 ⌀1000 이 넘는 경우에는 아래 예시를 참조하여 SLIDING TYPE EXPANSION JOINTS 를 제작 및 설치하여야 한다. ![image](/image/placeholder) FRP COVER 행 Kony Tarp (KT-1000) CAULKING 마감처리 Flange 리 거리 1100mm 150 840 150 435 405 ●1350 20 20t 36-⌀15 HOLES LD 240 240 #1470 B.C.D 480 0.0 #1520 25 0150x8= 1200 25 I0.1350 ozel'00 00 DUCT 1340 EXPANSION JOINT FLANGE BOLT HOLE 6 EX. BOLT/N/2W STS304 M12 x 60L 26 ⑤ 5 IN. BOLT/N/2W STS304 M12 x 80L 36 은 10 4 DRAIN FRP ⌀25 1 3 BELLOWS KONY TARP 1.1MM 1 DUCT.FLANGE 2 COVER FRP 5T 2 TOP S(A. 코 DUCT.FLANGE BELLOWS 1 SLIDE FLANGE FRP 2 DETAIL OF "A" DETAIL OF "B" NO. DESCRIPTION MATERIAL SIZE Q'TY REMARK SK hynix SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
05fea128-9e6a-41c1-890c-d44034001c98 | HV-A00-000134 FRP 배기덕트공사.doc | ¦ HV-A00-00134 FRP 배기덕트공사 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ Rev. 1 Page 18 of 27 ¦ ¦ --- ¦ --- ¦ --- ¦ ![image](/image/placeholder) 1390 1390 25 70 150*8=1200 70 25 25 70 150*8=1200 70 25 150 085 150 085% THE ⌀25 Drain Nozzle ⌀1350 �1570 ⌀1350 ⌀1570 99 : 26-⌀15 HOLES 26-⌀15 HOLES 65 1260 65 65 1260 65 COVER 상부 COVER 하부 (2) BELLOWS 는 KT-1000 재질로 2 겹으로 제작하며, BELLOWS 길이는 BELLOWS 고정축 길이에 변위량을 더하여 THERMAL EXPANSION 에 따른 BELLOWS 파손을 방지한다. (3) EXPANSION JOINTS 의 각 JOINTS 부분은 LEAK 가 발생하지 않도록 도면을 작성하여 발주처 승인후 제작 및 설치한다. 3.7 SPRINKLER 설치 (IN DUCT) 3.7.1 SPRINKLER HEAD 설치용 NOZZEL 은 50⌀로 OPEN 되어야 하며, FLEXBILE 과 HEAD 가 일체화된 제품을 BOND 로 설치된 MOUNTING BLOCK 과 볼트·너트로 연결하여 설치하여야 한다. 3.7.2 수평 설치 간격은 소방법에서 기준하는 규정 이내로 설치하며, 수직 설치는 각층의 층막이 바 닥에서 1,000~1,500mm 사이에 한 지점을 설정하여 설치한다. SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. SK ecoplant | {}
5d1d6983-d094-4cbe-b1ce-1261df4f5ba9 | HV-A00-000134 FRP 배기덕트공사.doc | ¦ HV-A00-00134 FRP 배기덕트공사 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ Rev. 1 Page 19 of 27 ¦ ¦ --- ¦ --- ¦ --- ¦ ![image](/image/placeholder) 155 DUCT NOZZLE for 50 SPRINKLER (50A) SPRINKLER HEAD 120iAE DRAIN PORT 8" 200 ⑪ (금 [SPRINKLER HEAD 설치 상세도] 3.8 부식방지 3.8.1 덕트를 고정·조립 할 경우 전위부식방지를 위하여 동일한 재질의 재료를 사용하여야 하고, 최 대한 이종금속사용을 배제하여야 하며 꼭 이종금속을 사용해야 하는 경우는 전위부식방지를 위 해 절연플랜지 또는 절연 볼트/ 너트/ 와셔등을 사용하는 적정한 조치를 취하여야 한다. 3.8.2 콘크리트 등 바닥위에 구조물 또는 장비를 설치할 경우에는 구조물 또는 장비의 부식방지를 위하여 콘크리트 등 바닥 구조물 또는 장비 사이에 RUBBER PAD 를 설치하여 시공한다. 3.8.3 부식방지를 위하여 볼팅을 하거나 나사못과 같은 것으로 조립작업 등을 할 경우 나사못 또는 이와 유사한 것과 철판 등의 피조립물 등 사이에 RUBBER PAD 를 설치한다. 3.8.4 장비 또는 구조물 등을 콘크리트 등 바닥에 고정할 경우 SET ANCHOR 등 고정물과 구조물 또는 장비는 같은 재질의 볼트와 너트를 사용하여 부식을 방지한다. 3.8.5 용접부위는 특히 부식에 취약하므로 충분한 조치를 하여 부식을 방지하도록 한다. 3.9 허용 오차 3.9.1 덕트의 허용 오차 (1) 덕트의 두께 : 제작 두께는 설계 두께 이상으로 제작되어야 하며, 컷팅면에서 일부분이 설계 두께의 90% 까지는 허용되나 전체 두께가 90% 이하가 되면 안된다. (2) 덕트의 직경, 길이, 높이 : 사각덕트의 장변 또는 원형덕트의 직경이 300mm 이하는 ±3.0mm 이내, 300mm 초과 ~ 1,000mm 이하는 ±5.0mm 이내, 1,000mm 초과 ~ 2,000 이하는 ±0.5% 이내, 2,000mm 초과 는 ±0.4% 이내로 한다. 3.9.2 ELBOW, REDUCER, TEE 의 허용 오차 (1) 두께 : 덕트의 허용 오차와 동일 (2) 직경 : 덕트의 허용 오차와 동일 3.9.3 플랜지의 허용 오차 (1) 두께 : 덕트의 허용 오차와 동일 (2) 직경 : 덕트의 허용 오차와 동일 SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. SK ecoplant | {}
59c4758c-ba5b-4ebf-b3ac-cfa4f3b3d7e6 | HV-A00-000134 FRP 배기덕트공사.doc | ¦ HV-A00-00134 FRP 배기덕트공사 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ Rev. 1 Page 20 of 27 ¦ ¦ --- ¦ --- ¦ --- ¦ (3) 볼트 경 : ±2.0mm 이내로 한다. (4) 홀간 피치 : B.C.D 기준 ±3.0mm 이내로 한다. 단, 홀 개당 거리는 ±2.0mm 이내로 한다. 3.10 검사 FRP 덕트 및 부속품은 다음과 같은 검사를 실시한다. 3.10.1 덕트 (1) 설치 위치 및 사이즈 적합성 (2) 설치 LEVEL 및 간격 (3) 덕트 재질 및 보강 (4) 품질 CHECK LIST 결과 (5) 방진규격 (6) 지지간격 (7) 눈관리 표식 3.10.2 덕트 DRAIN (1) 트랩의 설치 위치 및 상태 (2) 배관의 훼손 여부 확인 (3) 배관 SUPPORT 간격 (4) 설치 LEVEL 및 간격 (5) 방화 벽체 관통부 마감 상태 (6) 밸브의 설치 상태 (7) 눈관리 표식 3.11 덕트 표식 'HV-A00-000191 APPENDIX-I(눈 관리 STICKER)' 참조 3.12 PROCESS EXHAUST DUCT ACCESSORY 'HV-A00-000192 APPENDIX-II (PROCESS EHXAUST ACCESSORY)' 참조 - SUB FAB HEADER (FRP DUCT) POWER CHAMBER 설치는 도면에 준한다. - End of Document - SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. SK ecoplant | {}
b043ce47-dea0-4075-868e-787ffc32f4e3 | HV-A00-000134 FRP 배기덕트공사.doc | ¦ HV-A00-00134 FRP 배기덕트공사 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ Rev. 1 Page 21 of 27 ¦ ¦ --- ¦ --- ¦ --- ¦ 첨 부 -1 Gasket 적용 기준 ¦ 구 분 ¦ 구 분 ¦ 종 류 ¦ Type ¦ 비고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 덕트 ¦ ACID, ALKALI (STS) ¦ TEFLON (연질) ¦ Top Seal ¦ ¦ ¦ 덕트 ¦ ACID, ALKALI (FM PVC) ¦ TEFLON (연질) ¦ Top Seal ¦ ¦ ¦ 덕트 ¦ ACID, DRY (STS Coating) ¦ VITON ¦ - ¦ ¦ ¦ 덕트 ¦ CABINET, EMER, H/G (GALV.) ¦ NEOPRENE ¦ - ¦ ¦ ¦ 덕트 ¦ ORG (GALV.) ¦ TEFLON (연질) ¦ Top Seal ¦ ¦ ¦ 덕트 ¦ ACID, ALKALI, DRY (FRP) ¦ TEFLON (연질) ¦ Top Seal ¦ ¦ ¦ 배관 ¦ 냉수, 온수, 냉각수, NPW, IW (백강관) ¦ 비석면 ¦ FF, RF ¦ 비석면 (SPECSEAL C-4404) ¦ ¦ 배관 ¦ CTW, NPW, IW, PCW (STS 배관) ¦ TEFLON (경질) ¦ FF, RF ¦ RF: PCW 20k ¦ ¦ 배관 ¦ Steam, 응축수 (흑강관) ¦ Spiral Wound (Filler: Graphite, Outer ring: CS) ¦ FF, RF ¦ RF: 20k (OAC 상부) ¦ ¦ 배관 ¦ Duct Drain (산, 알카리) ¦ EFLON ¦ FF ¦ ¦ ¦ 배관 ¦ Duct Drain (그 외) ¦ EPDM ¦ FF ¦ ¦ ¦ 배관 ¦ House Vacuum ¦ TEFLON 쿠션 ¦ FF ¦ ¦ ¦ 배관 ¦ 소방 (Flange 부위) ¦ EFLON ¦ FF ¦ ¦ ¦ 배관 ¦ 폐수 ¦ EFLON ¦ FF ¦ ¦ SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. SK ecoplant | {}
3960fefa-76a7-48cb-831a-5336a9adf100 | HV-A00-000134 FRP 배기덕트공사.doc | ¦ HV-A00-00134 FRP 배기덕트공사 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ Rev. 1 Page 22 of 27 ¦ ¦ --- ¦ --- ¦ --- ¦ ![image](/image/placeholder) PTES.VERSATLEGAME TEFLON TEFLON 비석면 FF Spiral TEFLON VITON NEOPRENE EFLON EPDM (Top Seal) 쿠션 (C-4404) Wound (경질) SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. SK ecoplant | {}
be36549b-cb2b-43aa-9b82-60319ccc75a2 | KSCIEC60204-1_KR | KS C IEC 60204-1 KSKSKSKS KSKSKSK KSKSKS KSKSK KSKS KSK K KS 기계류의 안전성 - 기계의 전기 장비 - 제 1 부: 일반 요구사항 KS C IEC 60204-1 :2016 산 업 표 준 심 의 회 2021 년 1 월 15 일 개정 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
a29b1c7a-a360-40d1-ac8d-20962b79a596 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 심 의 : 전기응용 기술심의 회 ¦ ¦ 성 명 ¦ 근 무 처 ¦ 직 위 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ (회 장) ¦ 신 판 석 ¦ 홍익대학교 ¦ 교 수 ¦ ¦ (위 원) ¦ 권 오 화 ¦ KIC TECH ¦ 대 표 ¦ ¦ ¦ 김 갑 일 ¦ 명지대학교 ¦ 교 수 ¦ ¦ ¦ 김 재 희 박 효 성 ¦ 한국산업기술시험원 한국화학융합시험연구원 ¦ 수석연구원 ¦ ¦ ¦ 박 현 주 ¦ 전력연구원 ¦ 연 구 위 원 책임연구원 ¦ ¦ ¦ ¦ 한전 ¦ ¦ ¦ ¦ 서 호 선 이 주 철 ¦ 케이알 지식재산법률사무소 ¦ 대 표 ¦ ¦ ¦ 임 영 민 ¦ 대한전기협회 한국전자기술연구원 ¦ 처 장 ¦ ¦ ¦ 장 우 ¦ 서울과 학기술대학교 ¦ 수석연구원 ¦ ¦ ¦ 진 조 두 희 ¦ 한국전자통신연구원 ¦ 교 수 임 ¦ ¦ ¦ ¦ ¦ 책 ¦ ¦ (간 사) ¦ 박 진 우 ¦ 국가기술표준원 표준정책국 전자전자정보표준과 원안작성협력 : 전기안전연구원 ¦ 주 무 관 ¦ ¦ ¦ ¦ 처 ¦ 위 ¦ ¦ ¦ 성 명 ¦ 근 무 ¦ 직 수 ¦ ¦ (대표위원) ¦ 홍 진 웅 ¦ 광운대학교 ¦ 교 교 ¦ ¦ (위원) ¦ 김 병 택 ¦ 군산대학교 ¦ 수 ¦ ¦ ¦ 박 재 준 ¦ 중부대학교 ¦ 교 수 장 ¦ ¦ ¦ 신 성 수 남 기 범 ¦ 대한전기협회 한국전기기술인협회 전력연구원 ¦ 팀 부 장 ¦ ¦ ¦ 정 종 만 ¦ 전력연구원 ¦ 본 부 장 ¦ ¦ ¦ 유 세 현 ¦ 한국전자기술연구원 ¦ 본 부 장 ¦ ¦ ¦ ¦ 안전보건공단 산업안전보건연구원 ¦ 차 장 ¦ ¦ ¦ 변 정 환 ¦ 동양티피티 ¦ 이 사 ¦ ¦ (간 사) ¦ 정 종 욱 채 동 주 ¦ 한국전기안전공사 ¦ 선 임 연 구 원 ¦ 표준열람 : e 나라표준인증(http://www.standard.go.kr) 제 정 자 : 산업표준심의 회 위원장 담당부처 : 산업통상자원부 국가기술표준원 제 정 : 2002 년 11 월 30 일 개 정 : 2021 년 1 월 15 일 심 의 : 산업표준심의 회 전기응용 기술심의 회 원안작성협력 : 전기안전연구원 이 표준에 대한 의견 또는 질문은 e 나라표준인증 웹사이트를 이용하여 주십시오. 이 표준은 산업표준화법 제 10 조의 규정에 따라 매 5 년마다 산업표준심의 회에서 심의 되어 확인, 개정 또는 폐지됩니다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
640e7950-15bd-444a-8b5e-146f32188a75 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 목 차 머 리 말 ............................. iv 개 요 ................................ V 1 적용범위 ........................... 1 2 인용표준 .............................. 3 용어, 정의 및 ⌀1000000000000000000 3.1 용어와 정의 ............ 3 3.2 약어 ........................ 12 4 일반 오지향........................... 13 4.1 일반사항........................... 13 4.2 장비의 선정 ........... 14 4.3 전원 ---------- 14 4.4 물리적 환경 및 작동 ⌀= = = = = = 15 17 4.5 운반 및 ---------------- 4.6 취급용 설비 ........... 17 5 입력 전원 도체 단말부 및 개폐 정하로 요양급으로 17 5.1 입력 전원 도체 단말부 ······· 17 5.2 보호 도체 접속용 단자 ..... 17 5.3 전원 단로(차단) 장치 ····_ 18 5.4 불시 기동 방지용 전용카드:��������������� 21 5.5 전기 장비의 단로 장치 ............... 21 5.6 미승인, 부주의 및/또는 오결선 별지 111111111111111111 22 6 감전에 대한 보호 ............ 22 6.1 일반사항............................ 22 6.2 기본 M.................... 22 24 6.3 고장 ..................... 6.4 PELV 의 사용에 의한 ----- 26 7 설비 보호. ..................... 27 7.1 일반사............................. 27 7.2 과전류 보호 ......... 27 7.3 전동기의 과부하 ⌀= = = = 29 7.4 이상 온도 보호 ・・・・・・・・・・・・・・・・ ....................................... 31 7.5 전원 차단 또는 전압 강하 영향의 보호 및 복구.................................. 31 7.6 전동기 과속 보호 .......... 31 31 7.7 추가적인 지락 전류 --- 7.8 역상 보호 ............ 31 7.9 뇌 및 개폐 서지로 인한 과전압 보호 ............................. 32 7.10 단락 전류 정격 .... 32 8 등전위 본딩 .................... 32 8.1 일반사항. ··············· 32 8.2 보호 본딩 회로 -------- 34 8.3 높은 누설 전류 제한 From: -i- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및무단배포를 금합니다. | {}
f67c7929-6e3f-42f3-8f27-1fa1de28f291 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 8.4 기능 본딩 ......... 37 9 제어 회로 및 제어 ⌀======== 38 9.1 제어 38 9.2 제어 기능 ................ 38 9.3 보호 연동 장치 ------ 44 9.4 결함 시 제어 기능 - - 46 10 조작자 인터페이스 및 기계 장착 제어 정치______________________ 54 10.1 일반사항 ------------ 54 10.2 액추에이터 --------- 55 10.3 표시등 및 디스플레이 ..... 56 10.4 조광 누름 버튼 -------- 57 10.5 회전식 제어 ⌀======= 58 10.6 기동 장치 ·········· 58 10.7 비상 정지 장치 ..... 58 10.8 비상 전원 차단용 2,000 원 58 10.9 허용 제어 장치 ····_ 59 11 제어 장치: 위치, 설치 및 의원료:2000 원 59 11.1 일반 요구사항 ....... 59 11.2 위치와 ---------------- 60 11.3 보호 등급 ·········· 61 11.4 외함, 문 및 개구부 ... 61 11.5 전기 설비에의 접근 62 12 도체 및 케이블 ------------- 63 12.1 일반 연합................. 63 12.2 도체 .................... 63 12.3 절연 .................... 64 12.4 정상 작동에서의 허용 2,000000 64 12.5 도체 및 케이블의 전압 --------- 65 12.6 유연 케이블 ..................... 66 12.7 컬렉터 선, 컬렉터 봉 및 슬립링 장치----------------------- 67 13 배선 지침 ········ 69 13.1 접속 및 ............... 69 13.2 도체의 식별 ......... 70 13.3 외함 내부 배선 ..... 72 13.4 외함 외부 배선 · .... 73 13.5 덕트, 접속함 및 기타 1000000 76 14 전동기 및 관련 장비 ······_ 77 14.1 일반 요구사항 ------- 77 14.2 전동기 ................ 78 14.3 전동기의 크기 ······· 78 14.4 전동기 설치 및 = = = = =⌀ 78 14.5 전동기 선정 기준 - 78 14.6 기계 제동기용 보호 정--- 79 15 소켓-수구 및 조명 .......... 79 15.1 생........................... 79 -ii- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며불법 복사및무단배포를 금합니다. | {}
5ec6ed48-d2e9-4dcc-96b9-a118f12be4a4 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 15.2 기계 및 장비의 국부 조명 .............. 79 16 표지, 경고 표시 및 기준 지정 .......... 80 16.1 말과 니........................... 80 16.2 경고 표시 ............. 80 16.3 기능 식별 ......... 81 16.4 전기 장비 외함의 표지 ......... 81 16.5 기준 지정 ............. 82 17 기술 문서 ・・・・・・・・・・・・・・・・・・・ 82 17.1 일반사항. ··············· 82 17.2 전기 징비 관련 정보.. ······· 82 18 검증 -······· 83 18.1 일반사항. ..... ........................................ 83 18.2 전원의 자동 차단에 의한 보호 조건 점증............................ 84 18.3 절연 저항 시험 .... 87 18.4 전압 시험 ---------- 88 18.5 잔류 전압 보호 .... 88 18.6 기능 시험 ·············· 88 18.7 재시험 .............. 88 부속서 A (규정) 자동 공급 차단에 의한 고장 보호 ................................................ 89 A.1 TN 시스템에서 제공하는 기계에 대한 고장 보호.................................. 89 A.2 TT-시스템이 공급하는 기계에 대한 고장 보호 ................................................... 92 부속서 B (참고) 기계의 전기 장비용 설문 ··························· 96 부속서 C(참고) 이 표준에 포함된 기계의 예시 .................................... 99 부속서 D(참고) 전기 장비의 도체와 케이블의 허용 전류 및 과전류 보호.................................. 101 D.1 일반사항. ・・・・・・・・・・・・・・・・・・・・・・・ www.kravickk.com/shappy.com/ 101 D.2 일반 작동 조건 ................................................... 101 D.3 과부하 보호 기능을 제공하는 보호 장치와 도체 간의 협조....................................... 104 D.4 도체의 과전류 보호 1000000000000000000000000000000000 105 D.5 평형 3 상 시스템에 대한 고조파 전류의 영향 ................................................... 106 부속서 E(참고) 비상 조작 기능의 설명 ······················· 107 부속서 F(참고) 이 표준의 사용 지침 ···················· 108 부속서 G(참고) 대표적인 도체 단면적의 비고........................ 110 부속서 H(참고) 전자기적 영향을 저감하는 조치 ....................................... 112 H.1 정의 ····················· ····················· 112 H.2 일반사항. ············ .......... 112 H.3 전자기 장해(EMI)의 ------ 112 H.4 케이블의 이격 및 분리 ................ 114 H.5 병렬 전원에 의한 기계의 전원 공급 ·········· - 117 H.6 전력 구동 시스템(PDS)를 사용하는 경우, 공급 임피던스 - 117 부속서 I (참고) 문서/정보 - 118 참고문헌 ............................. 120 -iii- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및무단배포를 금합니다. | {}
a7621b0b-34f9-4e76-9597-f88e03ada4b6 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 머 리 말 이 표준은 산업표준화법 관련 규정에 따라 산업표준심의 회의 심의 를 거쳐 개정한 한국산업표준이다. 이에 따라 KS C IEC 60204-1:2015 는 개정되어 이 표준으로 바뀌었다. 이 표준은 저작권법의 보호 대상이 되는 저작물이다. 이 표준의 일부가 기술적 성질을 가진 특허권, 출원공개 이후의 특허출원, 실용신안권 또는 출원공개 후의 실용신안등록출원에 저촉될 가능성이 있다는 것에 주의 를 환기한다. 관계 중앙행정기관의 장과 산업표준심의 회는 이러한 기술적 성질을 가진 특허권, 출원공개 이후의 특허출원, 실용신안권 또는 출원공개 후의 실용신안등록출원에 관계되는 확인에 대하여 책임을 지지 않는다. -iv- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
79fa4503-6e86-4983-b854-1b1d0d5aac34 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 개 요 이 표준은 2016 년 제 6.0 판으로 발행된 IEC 60204-1, Safety of machinery Electrical equipment of machines Part 1: General requirements 를 기초로, 기술적 내용 및 대응국제표준의 구성을 변경하지 않고 작성한 한국산업표준이다. - v - 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
9f9206af-0e4e-4690-bc3a-45d233e73886 | KSCIEC60204-1_KR | 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
cad8d4cd-2f53-4885-8edc-2de9b790221c | KSCIEC60204-1_KR | 한국산업표준 KS C IEC 60204-1:2016 기계류의 안전성 - 기계의 전기 장비 - 제 1 부: 일반 요구사항 Safety of machinery - Electrical equipment of machines Part 1 : General requirements 1 적용범위 이 표준은 함께 작동하는 기계군을 포함하여 작동 중에 손으로 이동되지 않는 전기, 전자 장비 및 설비에 적용한다. 비고 1 이 표준은 적용 표준으로, 기술 개선사항을 제한하거나 금지하기 위한 의도는 아니다. 비고 2 이 표준에서 "전기"라 함은 전기, 전자 모두를 포함한다(즉, "전기 장비"라 함은 전기 및 전자 장비 모두를 의미). 비고 3 이 표준에서 "사람"(person)이라 함은, 당해 기계의 사용 및 관리를 맡은 대리인 또는 사용자 에 의하여 지정되어 교육받은 사람(들)을 말한다. 이 표준에서의 장비는 기계류의 전기 장비에 전기를 공급하는 전원 인입점부터 시작한다(5.1 참조). 비고 4 시설물에 전기를 공급하기 위한 요구사항은 IEC 60364 시리즈를 참조한다. 이 표준은 정격 주파수 200 Hz 이하의 교류 1 000 V 또는 직류 1 500 V 이하인 전기 장비 또는 그 부품에 대하여 적용한다. 보다 높은 주파수 및 전압용 장비에는 특수 요구사항을 필요로 할 수 있다. 비고 5 더 높은 공칭 공급 전압으로 작동하는 전기 장비 또는 전기 장비의 부품에 대해서는 KS C IEC 60204-11 을 참조한다. 이 표준은 응용 표준으로 기술 발전을 제한하거나 억제하기 위한 것이 아니다. 또한 이 표준은 전기 적 위험 이외의 위험으로부터 사람을 보호하기 위한 다른 표준 또는 법령에 의하여 필요하거나 요구 되는 모든 요구사항(예: 보호, 연동 제어 등)을 포함하지는 않는다. 각각의 기계류는 적합한 안전을 위하여 부수적인 고유한 요구사항을 갖고 있다. 이 표준은 특히 3.1.40 에 정의 된 기계류의 전기 장비를 포함하지만 이에 국한하지는 않는다. 비고 6 부속서 C 에 이 표준에 포함되는 기계류의 전기 장비의 예에 대하여 목록화하였다. 이 표준은, 예를 들어 다음과 같은 기계류의 전기 장비에 적용할 수 있는 추가 및 특수 요구사항을 규정하지 않는다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 1 | {}
1f5dcb9b-c0b9-4957-b766-eaae188592e1 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 옥외(건물 또는 보호용 구조물의 외부)에서 사용되는 기계 페인트, 톱밥 등 폭발성 물질을 사용, 취급, 제조하는 기계 폭발 위험 지역에서 사용되는 기계 특정 물질의 제조 또는 취급 시에 특별한 위험이 있는 기계 광산용 기계 재봉용 기계, 설비 및 시스템(IEC 60204-31 에 포함된 기계) 호이스트(IEC 60204-32 에 포함된 기계) 반도체 제조장비(IEC60204-33 에 포함된 기계) 이 표준은 전기 에너지를 직접적인 작업 수단으로 사용하는 전기 회로의 경우에는 적용하지 않는다. 2 인용표준 다음의 인용표준은 전체 또는 부분적으로 이 표준의 적용을 위해 필수적이다. 발행연도가 표기된 인용표준은 인용된 판만을 적용한다. 발행연도가 표기되지 않은 인용표준은 최신판(모든 추록을 포함)을 적용한다. KS C IEC 60034-1, 회전 기기 - 제 1 부: 정격 및 성능 KS C IEC 60072(모든 부), 회전기기의 치수와 출력 시리즈 KS C IEC 60309-1, 산업용 플러그, 콘센트 및 커플러 - 제 1 부: 일반 요구사항 KS C IEC 60364-1, 저압 전기설비 - 제 1 부: 기본 원칙, 일반 특성 평가 및 용어 정의 KS C IEC 60529, 외곽의 밀폐 보호등급 구분(IP 코드) KS C IEC 60664-1, 저압기기의 절연협조 - 제 1 부: 원칙, 요구사항, 시험 KS C IEC 60947-2, 저압 개폐장치 및 제어장치 - 제 2 부: 차단기 KS C IEC 60947-6-2, 저전압 개폐장치 및 제어장치 - 제 6-2 부: 다기능 기기 - 제어 및 보호 개폐장 치(또는 기기) KS C IEC 61140, 감전 보호 - 설비 및 기기의 공통사항 KS C IEC 61310(모든 부), 기계류의 안전성 - 지시, 표시 및 작동 KS C IEC 61439-1, 저압 배전반 및 제어반 - 제 1 부: 통칙 KS C IEC 61558-1:2009, 전력용 변압기, 전원장치, 리액터 및 유사기기의 안전 - 제 1 부: 일반요구사 항 및 시험 KS C IEC 61558-2-6, 최대 공급전압 1 100 V 용 변압기, 리액터, 전원장치 및 유사기기의 안전 - 제 2- 6 부: 안전절연변압기와 안전절연변압기 통합 전원장치의 개별 요구사항 및 시험 KS C IEC 61984, 커넥터 - 안전요구사항 및 시험 KS C IEC 62023, 기술 정보 및 문서의 구성 KS B ISO 13849-1, 기계 안전 - 제어 시스템의 안전 관련 부품 - 제 1 부: 설계의 일반 원칙 KS B ISO 13849-2, 기계 안전 제어 시스템의 안전 관련 부품 - 제 2 부: 검증 2 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
ceb1f711-e328-4222-9170-108ada88e46d | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 KS B ISO 13850:2006, 기계안전 - 비상정지 설계원칙 KS S ISO 7010:2011, 그래픽 심볼 - 안전색과 안전 표지 - 등록된 안전 표지 IEC 60364-4-41:2005, Low voltage electrical installations Part 4-41: Protection for safety - Protection against electric shock 비고 IEC 60364-4-41:2005 에 대응되는 KS 는 2013 년도에 고시된 KS C IEC 60364-4-41 이다. IEC 60364-4-43:2008, Low-voltage electrical installations Part 4-43: Protection for safety - Protection against overcurrent 비고 IEC 60364-4-43:2008 에 대응되는 KS 는 2012 년도에 고시된 KS C IEC 60364-4-43 이다. IEC 60364-5-52:2009, Electrical installations of buildings Part 5-52: Selection and erection of electrical equipment - Wiring systems 비고 IEC 60364-5-52:2009 에 대응되는 KS 는 2012 년도에 고시된 KS C IEC 60364-5-52 이다. IEC 60364-5-53:2001, Electrical installations of buildings Part 5-53: Selection and erection of electrical equipment - Isolation, switching, control Amentment 1:2002 비고 IEC 60364-5-53:2001/AMD1 :2002 에 대응되는 KS 는 2005 년도에 고시된 KS C IEC 60364-5-53 이 다. IEC 60364-5-54:2011, Low-voltage electrical installations Part 5-54: Selection and erection of electrical equipment - Earthing arrangements and protective conductors 비고 IEC 60364-5-54:2011 에 대응되는 KS 는 2014 년도에 고시된 KS C IEC 60364-5-54 이다. IEC 60417, Graphical symbols for use on equipment (http://www.graphical-symbole.inlo/equipment 에서 이용 가능) IEC 60445:2010, Basic and safety principles for man-machine interface, marking and identification Identification of equipment terminals and of terminations of certain designated conductors, including general rules for an alphanumeric system 비고 IEC 60445:2010 에 대응되는 KS 는 2011 년도에 고시된 KS C IEC 60445 이다. IEC 60947-3, Low-voltage switchgear and controlgear Part 3: Switches, disconnectors, switch- disconnectors and fuse-combination units IEC 60947-5-1:2003, Low-voltage switchgear and controlgear Part 5-1: Control circuit devices and switching elements Electromechanical control circuit devices Amentment 1:2009 비고 IEC 60947-5-1:2003/AMD1 :2009 에 대응되는 KS 는 2012 년도에 고시된 KS C IEC 60947-5-1 이다. IEC 60947-5-5, Low-voltage switchgear and controlgear Part 5-5: Control circuit devices and switching elements Electrical emergency stop device with mechanical latching function IEC 62061, Safety of machinery Functional safety of safety-related electrical, electronic and programmable electronic control systems 3 용어, 정의 및 약어 3.1 용어와 정의 이 표준의 목적을 위하여 다음의 용어와 정의 를 적용한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 3 | {}
a56b112b-b485-43e9-a74e-8b949fb59e19 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 3.1.1 액추에이터(actuator) 외부로부터 구동력이 인가되는 구동 장치의 한 부분 비고 1 액추에이터는 핸들, 손잡이, 누름 버튼, 롤러, 플런저 등의 형식이 될 수 있다. 비고 2 이것은 외부의 구동력이 아닌 오직 움직임에 의한 작동 수단이다. 예: 터치스크린 비고 3 3.1.39 참조 3.1.2 주위 온도(ambient temperature) 장비가 사용되고 있는 주위의 공기 또는 기타 매체의 온도 3.1.3 배리어(barrier) 통상적인 접근 방향에서 활선부 접촉을 방지하기 위한 하나의 부분 3.1.4 기본 보호(basic protection) 고장 없는 조건에서 감전으로부터 보호 비고 이전에는 "직접 접촉에 대한 보호"라고 함. [출처: IEC 60050-195:1998, 195-06-01, 수정 - 비고 추가] 3.1.5 케이블 트레이(cable tray) 연속되어 있는 밑면과 턱이 있는 옆면에 덮개가 없이 구성되어 있는 케이블 받침 비고 케이블 트레이는 구멍이 있을 수도, 또는 없을 수도 있다. [출처: IEC 60050-826:2004, 826-15-08] 3.1.6 케이블 트렁킹 설비(cable trunking system) 절연된 도체, 혹은 케이블을 수용하는 덮개(제거 가능)와 밑받침이 있는 폐쇄 외함 구조로 된 설비 3.1.7 동시 발생(concurrent) 같은 시간(동시성이 필요 조건은 아님)에 발생 혹은 동작 3.1.8 도체 와이어(conductor wire) 도체 바(conductor bar) 슬라이딩 집전 장치가 있는 피더 시스템의 전도성 와이어 또는 바 3.1.9 전선관(conduit) 전기 설비 내의 절연 도체 및/또는 케이블용 원형 또는 비원형의 폐쇄된 배선 설비의 일부분 4 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c5c39263-5c1b-4fff-befb-728fd2813a97 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 비고 전선관은 절연 도체 및/또는 케이블이 인출만 할 수 있고, 측면으로의 삽입은 할 수 없도록 충 분히 접합되어야 한다. [출처: IEC 60050-442:1998, 442-02-03] 3.1.10 제어 회로, <기계>(control circuit, <of a machine>) 기계의 작동 제어 및 전기 회로의 보호용으로 사용하는 회로 3.1.11 제어 기구(control device) 제어 회로에 연결된 장비 및 기계 작동을 제어하는 데 사용하는 기구 보기 위치 센서, 수동 제어 스위치, 릴레이, 자석식 작동 밸브 3.1.12 제어 스테이션(control station) 운전자 제어 스테이션(operator control station) 동일한 패널에 고정되거나 동일한 외함에 위치한 하나 이상의 제어 액추에이터(3.1.1 참조)의 어셈블리 비고 제어 스테이션에는 전위차계, 신호 램프, 기기, 디스플레이 장치 등과 같은 관련 장비도 포함 될 수 있다. [출처: IEC 60050-441:1984, 441-12-08] 3.1.13 제어 장치(controlgear) 제어, 측정, 보호 및 조정 장비와 관련해서 작동되는 개폐 장치 또는 그 조립품을 말하며, 전기 에너 지를 소비하는 장비를 제어하기 위해 관련된 모든 기구나 장치 [출처: IEC 60050-441:1984, 441-11-03] 3.1.14 제어 정지(controlled stop) 기계의 작동이 멈추는 방식으로, 정지하는 중에도 기계의 액추에이터에 전원이 공급되는 방식 3.1.15 직접 접촉(direct contact) 충전부에 대한 사람 또는 동물의 전기적인 접촉 비고 3.1.4 참조 [출처: IEC 60050-826:2004, 826-12-03, 수정 - 비고 추가] 3.1.16 직접 개방 동작, <접촉 소자의>(direct opening action, <of a contact element>) 비회복성 부재를 통해 스위치 작동기의 직접적인 이동 결과 로서(예를 들어, 스프링에 의존하지 않음.) 발생하는 접점 분리 [출처: IEC 60947-5-1:2003, K.2.2] 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 5 | {}
155f2e69-330a-488d-9c84-4104ce2b93be | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 3.1.17 덕트(duct) 전기 도체, 케이블 및 버스바 등을 수납, 보호하도록 특별히 설계된 폐쇄 채널 비고 전선관(3.1.9 참조), 케이블 트렁킹 설비(3.1.6 참조) 및 바닥 밑 채널은 덕트의 형태이다. 3.1.18 접지(earth) 로컬 접지 (local earth) ground (US) local ground (US) 전위가 0 과 같을 필요는 없는 접지극과 전기적으로 접촉하고 있는 대지의 일부 [출처: IEC 60050-195:1998, 195-01-03] 3.1.19 전기 취급 지역(electrical operating area) 숙련자 또는 교육받은 자만이 열쇠나 도구를 사용하지 않고 장벽을 제거하거나 문을 열고 접근할 수 있도록 제한된, 전기 장비가 설치된 공간 또는 위치로 적합한 경고 표지에 의해 명백히 표시되는 지역 3.1.20 전자 장비(electronic equipment) 주로 전자 장비 및 구성요소를 바탕으로 한 회로 소자를 포함하는 전자 장비 3.1.21 비상 정지 장치(emergency stop device) 비상 정지 기능 개시를 위해 사용되는 수동 조작 제어 장치 비고 9.2.3.4.2 참조 [출처: KS B ISO 13850:2006, 3.2, 수정 - 비고 추가] 3.1.22 비상 차단 장치(emergency switching off device) 감전 위험 또는 또 다른 전원 위험이 없는 설치 시설의 모두 또는 일부에 대한 전기 에너지 공급을 차단하는 수동 조작 제어 장치 비고 9.2.3.4.3 참조 3.1.23 폐쇄 전기 취급 지역(enclosed electrical operating area) 숙련자 또는 교육받은 자만이 열쇠나 도구를 사용하여 장벽을 제거하거나 문을 열고 접근할 수 있도 록 제한된, 전기 장비가 설치된 공간 또는 위치로 적합한 경고 표지에 의해 명백히 표시되는 지역 3.1.24 외함(enclosure) 그 어떠한 방향의 외부 영향에 대하여 장비를 보호하고 직접 접촉을 방지하기 위한 것. 비고 기존 IEV 의 용어 정의 는 이 표준 내에서 다음과 같은 설명이 필요하다. a) 외함은 사람 또는 가축의 위험 부분 접근을 방지한다. 6 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
8e6eb4c3-e148-463d-b8e8-763ae1cb81b8 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 b) 배리어, 개구부 또는 규정된 탐침(probe)의 침투 방지 또는 제한에 적합한 어떤 기타 수단, 외함에 부속되거나 폐쇄 기구에 의해 형성된 것은 열쇠 또는 도구를 사용하지 않고 이동할 수 있는 것을 제외한 외함 부분으로 간주된다. c) 외함은 다음과 같을 수 있다. 기계에 설치되거나 분리된 캐비닛 또는 함(box) 기계 구조물 내의 폐쇄된 공간에 구성되어 있는 칸막이 [출처: IEC 60050-195:1998, 195-02-35, 수정 - 정의 내용 수정] 3.1.25 전기 장비(electrical equipment) 기계 또는 기계 부품에 의한 전기 사용과 관련하여 사용되는 품목(예: 재료, 부속품, 장치, 구성요소, 가전 제품, 고정 장치, 기구 등) 3.1.26 등전위 본딩(equipotential bonding) 실질상 등전위에서 전기적으로 접속된 여러 가지의 노출 도전부 및 외부 도전부 [출처: IEC 60050-195:1998, 195-01-10] 3.1.27 노출 도전부(exposed conductive part) 접촉될 수 있는 전기 설비의 도전성 부분으로서 정상 작동 시에는 비충전 상태이나 고장 상태에서 충전될 수 있는 곳 [출처: IEC 60050-826:2004, 826-12-10, 수정 - 정의 내용 수정] 3.1.28 기타 도전부(extraneous conductive part) 전기 설비의 일부분은 아니나 잠재적으로 전위가 형성될 수 있는 도전부 [출처: IEC 60050-195:1998, 195-06-11] 3.1.29 결함(failure) 요구되는 기능 수행(내용)의 정지 비고 1 결함 후에 고장(내용)이 온다. 비고 2 "결함"은 어떠한 상태를 말하는 "고장"과는 구별되는 사상이다. 비고 3 이 개념은 소프트웨어만으로 구성되는 곳에는 적용하지 않는다. 비고 4 고장과 결함이라는 용어는 실제에서는 종종 같은 의미로 사용된다. [출처: KS C IEC 60050-191:1990, 191-04-01] 3.1.30 고장, 실패(fault) 예방 보수, 기타 계획된 행위 또는 외부 동력의 미공급으로 인한 경우 이외에 요구되는 기능의 미수 7 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
031425a8-6919-4890-9f1a-ee810d1155ae | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 행을 나타나는 상태 비고 1 주로 그 자체의 결함의 결과 에 의하지만 결함 없이 존재할 수도 있다. 비고 2 영어에서 용어 "고장"과 이것의 정의 는 KS C IEC 60050-191:1990 의 IEV 191-05-01 에 주어진 것과 일치한다. 기계류의 분야에서 프랑스 용어 "defaut" 및 독일 용어 "Fehler"는 오히려 이 정의 에 나타낸 용어 "panne" 및 "Fehlzustand"가 사용된다. 3.1.31 고장 보호(fault protection) 단일 고장 조건에서 감전으로부터 보호 비고 이전에는 "간접 접촉에 대한 보호"라고 함. [출처: IEC 60050-195:1998, 195-06-02, 수정 - 비고 추가] 3.1.32 기능 본딩(functional bonding) 전기 장비의 적합한 기능을 위해 필요한 등전위 본딩 3.1.33 위험 (hazard) 건강상의 위해 또는 부상 가능성의 근원 비고 1 위험이라는 개념은 잠재적인 위험의 기원(예: 기계적인 위험, 전기적 위험) 혹은 본질(예: 감 전 위험, 독성 위험, 화재 위험)을 정의 하는 데 적합하다. 비고 2 이 정의 에서 위험은 기계의 의도 사용 중에 영구적으로 존재하거나(예를 들어, 위험한 기동 소자의 움직임, 용접 중의 전기 아크, 위험한 자세, 소음 방출, 고온) 예상치 않게 발생할 수 있다(예를 들어, 폭발, 의도치 않은/불시 기동의 결과 로 인한 충돌 위험, 파손의 결과 로 인한 방출, 가/감속 결과 로 인한 추락). [KS B ISO 12100:2010, 3.6, 수정] 3.1.34 간접 접촉(indirect contact) 고장 상태하에서 충전부가 될 수 있는 노출 도전부와 사람 또는 가축이 접촉되는 상태 비고 3.1.31 참조 [출처: IEC 60050-826:2004, 826-12-04, 수정 - 정의 내용 수정] 3.1.35 유도 전원 공급 계통(inductive power supply system) 전기 에너지를, 예를 들어 모바일 기계로 이송하기 위해 갈바닉 또는 기계적 접촉 없이 하나 이상의 픽 업 및 관련 픽업 컨버터가 움직일 수 있는 트랙 변환기 및 트랙 도체로 구성되는 유도 전원 공급 계통 비고 트랙 도체와 픽업은 변압기의 1 차, 2 차와 유사하다. 8 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
015e9ea0-3e72-4beb-9a13-d5e4c358a5c0 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 3.1.36 교육받은 사람(instructed person, <in electrically>) 전기로 인한 위험을 인지하고 피할 수 있도록 전기 전문가로부터 적절한 지도 또는 자문을 받은 사람 [출처: IEC 60050-826:2004, 826-18-02] 3.1.37 연동(interlock) 다음의 상황을 위하여 함께 작동하는 장치의 배치 · 위험한 상황으로부터 보호 · 장비나 재료의 손상을 보호 · 특정한 동작의 보호 · 적절한 동작 보장 3.1.38 충전부(live part) 중성 도체(일반적으로 PEN 도체는 제외함)를 포함하여 정상 사용 시에 전기 에너지가 인가되는 도체 또는 도전부 3.1.39 기계 액추에이터(machine actuator) 기계의 움직임에 영향을 주기 위하여 사용되는 동력 기구(예: 모터, 솔레노이드, 공압 또는 유압 실린 더) 3.1.40 기계류(machinery) 기계(machine) 재료의 가공, 처리, 이동 또는 포장과 같은 특정 목적을 위하여 기계 액추에이터, 제어 및 전기 회로 등이 상호 결합하여 최소한 한 개 이상의 가동되는 부품 등으로 이루어진 조립체 비고 1 "기계류"는 하나의 동일한 목적 달성을 위하여, 일체화된 기능을 수행하도록 선정되고 제어되 는 기계의 조립체를 포함한다. 비고 2 여기에서 "부품"이란 용어는 일반적으로 사용되는 용어로 전기 부품만 언급하지 않는다. [KS B ISO 12100:2010, 3.1 수정 ] 3.1.41 표시(marking) 부품 또는 장비의 제조자에 의하여 첨부된 부품 또는 장비의 형식을 인식하기 위한 표지 등 3.1.42 중성 도체(neutral conductor) N 계통의 중성점에 전기적으로 접속되어 전기 에너지의 전송에 기여하는 도체 [출처: IEC 60050-195:1998, 195-02-06] 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 9 | {}
7a65372c-c3f2-45c5-93e7-9068fbc0efdc | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 3.1.43 장애물(obstacle) 의도적인 직접 접촉은 방지할 수 없으나 무의 식적인 직접 접촉을 방지하기 위한 것. [출처: IEC 60050-195:1998, 195-06-16] 3.1.44 과전류(overcurrent) 정격값을 넘는 전류. 도체에서의 정격값은 허용 전류이다. 비고 도체의 경우 정격 값은 전류 전달 용량과 동일한 것으로 간주된다. [출처: IEC 60050-195:2004, 826-11-14, 수정 - 정의 내용 수정] 3.1.45 과부하[overload (of a circuit)] 고장 상태가 아닌 회로에서 전부하 정격을 넘는 회로에서의 시간/전류의 관계 비고 과부하는 과전류와 동등하게 사용되지 않는다. 3.1.46 플러그/소켓의 조합(plug/socket combination) 두 개 이상의 도체 연결 또는 분리용으로 도체 종단에 적합한 부품 및 적합한 결합 부품 비고 플러그/소켓 조합의 예는 다음과 같다. KS C IEC 61984 의 요구사항을 충족하는 커넥터 플러그 및 소켓 콘센트, 케이블 커플러 또는 KS C IEC 60309-1 에 따른 기기 커플러 KS C IEC 60884-1 에 따르는 플러그 및 소켓 콘센트 또는 KS C IEC 60320-1 에 따르는 전기 커플러 3.1.47 전기 회로(power circuit) 기계 작동에 사용되는 장비의 유닛 및 제어 회로용 변압기에 전력을 공급하는 데 사용하는 회로 3.1.48 예상 단락 전류(prospective short-circuit current) Icp 전기설비에 전력을 공급하는 도체가 전기설비의 전력 공급 단자에 가능한 가깝게 위치한 무시할 만 한 임피던스의 도체에 의해 단락됐을 때 흐르는 전기 설비전류의 실훗값 [출처: IEC 61439-1:2011, 3.8.7] 3.1.49 보호 본딩(protective bonding) 감전 방지를 위한 등전위 본딩 비고 1 감전 방지를 위한 보호 조치는 연소 또는 화재 위험도 줄일 수 있다 비고 2 보호 본딩은 보호 도체 및 보호 본딩 도체를 사용하고 기계와 전기 장비의 전도성 부품을 전 도성으로 접합하여 이루어진다. 10 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
1b096bd9-7aa2-49dd-807e-56a1c60dcaa9 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 3.1.50 보호 본딩 회로(protective bonding circuit) 설비 고장으로 인한 감전을 방지하기 위하여 사용하는 보호 접지 도체 및 도전부의 도체 3.1.51 보호 접지 도체(protective conductor) 전기 장비의 노출된 전도성 부분에서 보호 접지(PE) 단자까지 주요 고장, 실패 전류 경로를 제공하 는 도체 3.1.52 이중화(redundancy) 어떠한 기능 수행이 실패했을 경우, 이를 대신할 수 있는 다른 기능의 작동을 보증하기 위하여 하나 이상의 장비, 설비 또는 장비나 설비의 일부를 적용하는 것. 3.1.53 기준 지정(reference designation) 도표, 목록, 차트 및 장비 등에서의 항목 등을 구분하기 위한 특정 코드 3.1.54 위험성(risk) 위험 상황에서 부상 또는 건강 장해를 일으킬 확률과 정도의 조합 [출처: KS B ISO 12100:2010, 3.12 수정] 3.1.55 안전 장치(safeguard) 현존하거나 임박한 위험으로부터 사람을 보호하기 위한 방법으로 사용하는 방호물 또는 방호 장치 [출처: ISO 12100:2010, 3.26 ] 3.1.56 안전 보호(safeguarding) 설계에 의하여 제거될 수 없거나 충분히 제한될 수 없는 위험으로부터 사람을 보호하기 위하여, 안 전 장치라고 불리는 특정 수단 등을 적용하는 안전 조치 [출처: KS B ISO 12100:2010, 3.21] 3.1.57 안전 기능(safety function) 고장 시 즉시 위험을 증가시킬 수 있는 기계의 기능 [출처: ISO 12100:2010, 3.30; IEC 62062, 3.2.15] 3.1.58 바닥면(servicing level) 전기 장비의 작동이나 유지 보수 시에 사람이 통상 서 있는 바닥(level) 3.1.59 단락 전류(short-circuit current) 전기 회로의 부적합한 접속이나 고장으로 인한 단락 사고에 의한 과전류 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 11 | {}
d0f2f4bd-7708-42da-bf5b-5c3aee42d89b | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 [출처: IEC 60050-441:1984, 441-11-07] 3.1.60 단락 전류 정격(short-circuit current rating) 지정된 조건에서 단락 보호 장치(SCPD)의 총 작동 시간(클리어링 시간) 동안 전기 장비가 견딜 수 있는 예상 단락 전류 값 [출처: IEC 61439-1:2011, 3.8.10.4 ] 3.1.61 기술자(skilled person) 발생할 수 있는 전기 위험을 인지하고 피할 수 있도록 적절한 교육을 받고 경험을 보유한 사람 [출처: IEC 60050-826:2004, 826-18-01 ] 3.1.62 공급자(supplier) 기계 관련 장비나 서비스를 제공하는 사람. 예를 들어, 제조자, 하청업자, 설치자, 조립업자 비고 사용자 또한 그 자신이 공급자 역할을 할 수 있다. 3.1.63 개폐 기구(switching device) 한 개 또는 그 이상의 전기 회로에서 전류를 흘리거나 차단하기 위한 목적으로 설계된 기구 비고 개폐 기구는 하나 또는 이들 작동 모두 수행할 수 있다. [출처: IEC 60050-441:1984, 441-14-01] 3.1.64 비제어 정지(uncontrolled stop) 기계류 액추에이터에 전력을 제거하여 이루어지는 기계의 작동 정지 비고 이 정의 는, 예를 들어 기계 또는 유압 브레이크와 같은 다른 정지 장치의 특정한 상태는 의미 하지 않는다. 3.1.65 사용자(user) 기계 및 관련 전기 장비를 사용하는 사람 3.2 약어 ¦ AWG ¦ American Wire Gauge ¦ ¦ --- ¦ --- ¦ ¦ AC ¦ Alternating Current ¦ ¦ BDM ¦ Basic Drive Module ¦ ¦ CCS ¦ Cableless Control System ¦ ¦ DC ¦ Direct Current ¦ ¦ EMC ¦ Electro-Magnetic Compatibility ¦ ¦ EMI ¦ Electro-Magnetic Interference ¦ 12 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
946c85dd-896d-44ed-94ef-56207a833bc5 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 ¦ IFLS ¦ Insulation Fault Location System ¦ ¦ --- ¦ --- ¦ ¦ MMI ¦ Man-Machine interface ¦ ¦ PDS ¦ Power Drive System ¦ ¦ PELV ¦ Protective Extra-Low Voltage ¦ ¦ RCD ¦ Residual Current protective Device ¦ ¦ SPD ¦ Surge Protective Devices ¦ ¦ SCPD ¦ Short-Circuit Protective Device ¦ ¦ SELV ¦ Safe Extra-Low Voltage ¦ ¦ SLP ¦ Safely-Limited Position ¦ ¦ STO ¦ Safe Torque Off ¦ 4 일반 요구사항 4.1 일반사항 이 표준은 기계의 전기 장비에 대한 요구사항을 규정한다. 전기 장비에 관련된 위험과 위험성은 기계의 위험성 평가에 대한 전반적인 요구사항의 일부로서 실시되어야 한다. 여기에서, 위험 감소의 필요성을 식별 적절한 위험 감소를 결정 필요한 보호 조치 결정 들이 위험에 노출될 수 있는 사람을 위하여 수행되어야 하고, 기계와 설비는 적절한 성능을 유지되 어야 한다. 위험은 다음과 같은 원인에 의해 발생할 수 있다. 그러나 그 원인은 여기에 국한되지 않는다. 감전, 아크 또는 화재를 일으킬 수 있는 전기 장비의 결함 또는 고장 기계의 이상을 일으키는 제어 회로(또는 이 회로와 관련 있는 부품 및 장치)의 결함 또는 고장 기계의 이상을 일으키는 전기 회로의 결함 또는 고장 및 전원의 교란 또는 외란 안전 기능의 결함을 유발하는 회로의 연속성 상실(예: 습동 접점 또는 회전 접점) 기계류의 기능 결함을 야기하는 전기 장비의 외부 또는 내부에서 발생하는 전기 교란(전자계, 정 전기, 전파 간섭 등) 예를 들어 부상을 야기할 수 있는 감전, 예기치 못한 움직임을 초래하는 축적 에너지(전기나 기계 적인 것)의 배출 사람에게 해를 줄 정도의 소음과 기계적 진동 부상을 야기할 수 있는 표면 온도 안전 조치는 설계 단계에서의 조치와 사용자가 취해야 하는 안전 조치의 조합에 의한다. 설계 및 개발 시에는 위험성 감소가 첫 번째로 고려되어야 한다. 이것이 충분하지 않을 경우, 안전 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 13 | {}
c8127f03-9e24-424a-bbd3-62aa2f8ae826 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 보호 및 안전 작업 절차를 고려하여야 한다. 안전 보호는 안전 장치 및 인식 수단의 사용을 포함 한다. 사용자가 알려진 곳에서는 부속서 B 를 사용하여 정보 교환을 사용자와 공급자 사이의 별도 약정에 의하여 사용하기를 권고한다. 비고 이 추가 요구사항은 다음과 같다. 기계(또는 기계군)의 형식 및 그 적용에 따른 추가적인 특성 용이한 유지 보수 및 수리 신뢰도 향상 및 조작의 용이성 4.2 장비의 선정 4.2.1 일반사항 전기 부품 및 장치는 다음과 같다. 의도된 사용에 적합해야 하며 존재할 경우, 관련 IEC 표준을 준수해야 하며 공급자의 지침에 따라 적용되어야 한다. 4.2.2 개폐장치 이 표준의 요구사항 외에, 기계류, 사용 목적 및 전기 장비에 따라 설계자가 IEC 61439 시리즈의 관 련 부를 준수하는 기계류의 전기 장비 부품을 선정할 수 있다(부속서 F 참조). 4.3 전원 4.3.1 일반사항 전기 장비는 다음의 전원 조건에서 정상적으로 작동되도록 설계하여야 한다. 4.3.2 또는 4.3.3 에 규정된 사항 또는 사용자의 요구 조건 또는 특수 전원이 있는 경우에는 공급자가 정하는 조건(4.3.4 참조) 4.3.2 교류 전원 a) 전압 정상 상태 전압: 공칭 전압의 0.9 ~ 1.1 b) 주파수 연속(지속) 변동: 공칭 주파수의 0.99 ~ 1.01 순시(단시간) 변동: 0.98 ~ 1.02 c) 고조파 고조파 왜곡률은 제 2 고조파 ~ 제 30 고조파의 합이 선간 전압(총 실훗값)의 12 %를 넘지 않을 것. 14 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
e0d0c38f-53d8-4a06-9e8d-5ae73356c962 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 d) 전압 불평형 3 상 전원에서 역상 성분 전압 및 영상 성분 전압 모두 정상 성분의 2 %를 넘지 않 을 것. e) 전압 차단 전원 사이클의 임의 의 시간에서 전원 차단 또는 영전압이 3 ms 를 넘지 않을 것. 다만, 연속적인 차단 시에는 그 간격이 1 초 이상일 것. f) 전압 강하 전압 강하는 1 사이클 이상에서 전압 공급 실훗값의 20 %를 넘지 않을 것. 다만, 연속 적인 강하의 경우, 1 초 이상의 간격을 가질 것. 4.3.3 직류 전원 a) 축전지 전원 1) 전압 공칭 전압의 0.85 ~ 1.15 축전지 작동 차량의 경우에 공칭 전압의 0.7 ~ 1.2 2) 전압 차단 5 ms 를 넘지 않을 것. b) 변환 장비 전원 1) 전압 공칭 전압의 0.9 ~ 1.1 2) 전압 차단 20 ms 를 넘지 않을 것. 다만, 연속적인 차단 시에는 간격이 1 초 이상일 것. 비고 이것은 전자 장비의 적절한 작동을 보증하기 위한 IEC Guide 106 을 변형한 것이다. 3) 리플(첨두 대 첨두) 공칭 전압의 0.15 를 넘지 않을 것. 4.3.4 특수 전원 공급 시스템 전원 탑재된 발전기와 같은 특수 전원 공급 설비에서, 전기 장비가 당해 전원 조건에 적합하게 작동 되도록 설계된 경우에는 4.3.2 및 4.3.3 에서 규정하는 제한 조건을 넘을 수 있다. 4.4 물리적 환경 및 작동 조건 4.4.1 일반사항 전기 장비는 4.4.2 에서 4.4.8 에 규정된 물리적 환경 및 작동 조건에서 사용하기에 적합하여야 한다. 이 표준에 규정된 물리적 환경 또는 작동 조건 이외의 것의 경우에는 공급자와 사용자 사이에 별도 의 정보 교환이 필요할 수 있다(4.1 참조). 4.4.2 전자파 적합성(EMC) 전기 장비는 사용 장소에 따른 적정 수준 이상의 전자파 장애를 일으켜서는 안 된다. 또한 전기 장 비는 주위에서 발생할 수 있는 충분한 정도의 전자파 장애에 충분한 내성 등급을 가져야 한다. 다음 조건이 충족되지 않는 한 전기 장비에 대한 내성 및/또는 방출 테스트가 필요하다. · 통합된 장치 및 구성요소가 관련 제품 표준(또는 제품 표준이 없는 일반 표준)에 지정된 의도된 EMC 환경에 대한 EMC 요구사항을 준수한다. 전기 설치 및 배선은 상호 영향(케이블 연결, 차폐, 접지 등)과 관련하여 장치 및 구성요소 공급 업 체가 제공한 지침 또는 공급 업체에서 그러한 지침을 사용할 수 없는 경우 정보를 제공하는 부속 서 H 와 일치한다. 15 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
5d5c6a15-96f4-4d87-88c3-bf6449668f75 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 비고 일반적인 EMC 표준 IEC 61000-6-1 또는 IEC 61000-6-2 및 IEC 61000-6-3 또는 IEC 61000-6- 4 가 일반적인 EMC 방사 한계 및 내성 한계를 제공한다. 4.4.3 주위의 대기 온도 전기 장비는 의도된 주위 대기 온도에서 정상 작동하여야 한다. 모든 전기 장비의 최소 요구사항은 +5 °C ~ +40 °C 의 (캐비닛 혹은 함) 외함 외부의 주위 대기 온도에서 정상 작동하는 것이다. 4.4.4 습도 전기 장비는 최대 온도 +40 °C, 상대 습도 50 % 이하에서 정상 작동할 수 있어야 한다. 보다 높은 상대 습도는 저온(예: 20 °C 에서 90 %)에서 허용될 수 있다. 전기 장비에 습기가 응축될 가능성이 있는 경우, 이를 방지할 수 있는 적절한 설계 및 부가적인 수 단을 강구하여야 한다(예: 내장 히터, 공기 조절 장치, 배수구). 4.4.5 고도 전기 장비는 해발 1 000 m 이하에서 정상 작동할 수 있어야 한다. 더 높은 고도에서 사용되는 장비의 경우 다음 사항을 고려해야 한다. 절연 내력 장치의 스위칭 기능 공기의 냉각 효과 제품 데이터에 계수가 명시되지 않은 경우 사용할 보정 계수에 대해서는 제조업체에 문의 하는 것이 좋다. 4.4.6 오염 물질 전기 장비는 이물질의 침입으로부터 충분히 보호되어야 한다(11.3 참조). 오염 물질(예: 먼지, 산, 부식 가스, 소금)은 전기 장비가 설치되는 물리적 환경에 존재하는 전기 장 비의 이유가 적합하게 주어져야 한다. 4.4.7 전리 및 비전리 방사선 전기 장비가 방사선(예: 마이크로파, 자외선, 레이저, X 선)에 영향을 받을 경우, 장비의 작동 불량 및 절연 열화의 가속화가 일어나지 않도록 추가적인 조치를 하여야 한다. 4.4.8 진동, 충격, 충돌 전기 장비는 진동, 충격 및 충돌(기계와 그 부속 장비에 의하여 발생하는 것, 물리적인 환경에 의하 여 생성되는 것 포함)에 의한 악영향은 적합한 기계의 선정, 기계로부터 분리 설치 또는 방진 기구의 사용 등을 통하여 방지하여야 한다. 16 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f2cdff4b-40ab-446a-af81-32890e828bfa | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 4.5 운반 및 보관 전기 장비의 운반과 보관 시에는 -25 °C ~ +55 °C 의 온도(단시간 운송 · 저장 시에는 70 °C 이하에서 24 시간)에서 견디거나 적절한 보호가 되도록 설계하여야 하며, 또한 습도, 진동, 충격 등으로 인해 손상되지 않도록 적절한 수단을 강구하여야 한다. 비고 PVC 절연 케이블을 포함한 전기 장비는 저온에서 손상될 수 있다 4.6 취급용 설비 전기 장비가 크기나 무게로 인하여 운반시 기계 설비로부터 분리시켜야 하거나 독립형인 경우, 크레 인 또는 유사 장비를 사용할 수 있는 구조이어야 한다. 5 입력 전원 도체 단말부 및 개폐 장치 5.1 입력 전원 도체 단말부 전기 장비의 입력 전원은 가능한 한 단일 전원으로 하되 별도의 전원이 필요한 부품(예: 전자 회로, 전자기 클러치)의 경우, 이 부품의 전원은 당해 기계 설비의 전기 장비의 일부(예: 변압기, 컨버터)에 서 인출하도록 한다. 다만, 대형 복합 기계류의 경우에는 작업장 전원 공급 계통 여건에 따라 여러 전원을 사용할 수 있다(5.3.1 참조). 기계에 전원 접속용 플러그가 없는 경우[5.3.2 e) 참조], 입력용 도체는 전원 차단 장치에서 종료되어 야 한다. 이것이 곤란할 경우에는 별도의 단자대를 설치하여야 한다. 중성선이 사용되는 경우, 전기 회로도, 설치 도면과 같은 기계의 기술 문서에 분명히 표시되어야 하 며, 중성선에는 16.1 에 따라 "N"자 표시된 별도의 절연 단자를 사용하여야 한다. 중립 단자는 전원 차단 장치의 일부로 제공될 수 있다. 전기 장비 내부의 중성 도체와 보호 본딩 회로 사이에는 접속점이 없어야 한다. 예외: TN-C 계통의 경우, 기계의 입력점에서는 중성선 단자와 접지(PE) 단자에는 접속점이 있을 수 있다. 병렬 소스에서 공급되는 기계의 경우 다중 소스 시스템에 대한 KS C IEC 60364-1 의 요구사항이 적용 된다. 입력 단자용 단자는 IEC 60445 에 따라 명확히 확인할 수 있다. 외부 보호 접지 도체 단자의 구별은 5.2 참조 5.2 보호 도체 접속용 단자 각각의 입력 전원에서, 외부의 보호 접지 도체에 설비를 접속하기 위한 단자는 관련 선도체와 동일 한 구역에 설치하여야 한다. 단자는 표 1 에 따라 외부의 보호 구리 도체를 접속할 수 있는 충분한 굵기이어야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 17 | {}
cbe11d12-7e10-4b95-a232-eaa4e61fa87e | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 표 1 - 보호 구리 도체의 최소 단면적 ¦ 선도체의 단면적 S mm2 ¦ 상응하는 보호 도체의 최소 단면적 ¦ ¦ --- ¦ --- ¦ ¦ ¦ Sp mm2 ¦ ¦ S≤ 16 ¦ S ¦ ¦ 16 < S≤ 35 ¦ 16 ¦ ¦ S> 35 ¦ S/2 ¦ 구리 이외의 외부 보호 접지 도체를 사용하는 경우, 단자 크기와 타입은 적절히 선정하여야 한다. 기계 및 고정 설비 사이의 접속점에서의 혼란을 피하기 위하여, 각 전원 공급점에서 외부의 보호 도 체는 "PE" 문자 표기에 의하여 구분하여야 한다(IEC 60445 참조). 5.3 전원 단로(차단) 장치 5.3.1 일반사항 전원 차단 장치는 다음에 따라 설치하여야 한다. 기계는 각각의 전원을 공급 비고 유입 전원은 기계의 공급 차단 장치 또는 기계의 급전 시스템의 공급 차단 장치에 직접 연 결할 수 있다. 기계의 급전 시스템은 도체 와이어, 도체 바, 슬립링 조립체, 유연 케이블 시 스템(릴, 점형) 또는 비접촉식 전력 공급 시스템을 포함할 수 있다. 각각의 탑재 전원 전원 차단 장치는 기계 위에서의 필요한 작업 등의 경우 전기 장비의 전원을 차단할 수 있어야 한다. 2 개 이상의 차단 장치가 설치된 경우, 오조작 등으로 인하여 작업 중 위험한 상태 또는 기계 설비가 손상될 우려가 있다면 연동되도록 설치하여야 한다. 5.3.2 차단 방식 전원 차단 장치는 다음 방식 중 하나이어야 한다. a) 카테고리 AC-23B 또는 DC-23B 를 이용한 IEC 60947-3 에 따른 퓨즈부 또는 퓨즈 없는 개폐기 b) KS C IEC 60947-6-2 에 따른 절연에 적합한 제어 및 보호 스위칭 장치 c) KS C IEC 60947-2 에 의한 분리용으로 적합한 차단기 d) 해당 장치의 IEC 제품 표준에 따른 기타 개폐 기구 및 전동기 또는 기타 유도 부하의 탑재 개폐 장치에 적합한 제품 표준에 정의 된 적절한 이용 범주 및/또는 지정된 내구성 요구사항의 차단 요 구사항을 충족시키는 기타 개폐 기구 e) 유연 케이블 공급기용 플러그/소켓 조합 5.3.3 요구사항 전원 차단 장치가 5.3.2a) ~ d)에 규정된 앞의 종류 중 하나일 경우에는 다음 요구사항을 모두 충족하 18 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
4dcf55f3-d451-4ce5-9e84-15cb87c479e9 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 여야 한다. 오직 하나의 투입 및 개방 위치를 갖고 있는 전기 장비에는 "O" 및 "I"를 표시한다[IEC 60417-5008 (2002-10)의 기호 및 IEC 60417-5007(2002-10)의 기호, 10.2.2 참조]. 모든 접점이 실제적으로 개방되어 절연 기능 요구사항이 충족될 때까지 OFF(분리)가 표시되지 않 는 시각적인 간격 또는 위치 표시기를 구비할 것. 조작 수단(5.3.4 참조) OFF(분리) 상태에서 잠글 수 있는 수단(예: 자물쇠에 의해)을 구비하되, 잠금 상태에서는 원격 투 입은 물론, 현장 투입이 되지 않는 구조 전원 회로의 모든 상도체를 분리할 것. 그러나 TN 계통의 경우에는 중성선을 분리하지 않을 수도 있다(관련 법 규정에서 분리하도록 되어 있는 경우는 예외로 함). 다른 모든 전동기 및 다른 정상 부하 전류의 합한 것에서 가장 큰 전동기의 전류를 차단할 수 있 는 충분한 차단 용량을 보유할 것. 계산된 차단 용량은 입증된 부등률에 의해 감소될 수 있다. 모 터가 컨버터 또는 유사한 장치에 의해 공급되는 경우 계산 시 필요한 차단 용량에 대한 가능한 영향을 고려해야 한다. 전원 차단 장치가 플러그/소켓 조합일 때, 13.4.5 의 요구사항을 충족하여야 하며 개폐 성능을 구비할 것 또는 다른 모든 전동기 및 정상 부하 전류의 합한 것에서 가장 큰 전동기의 전류를 차단할 수 있 는 충분한 차단 용량을 보유한 개폐 기구에 연동한다. 계산된 차단 용량은 입증된 부등률에 의해 감 소될 수 있다. 연동된 개폐 기구는 전기로 작동해야 하고(예: 접촉기) 적합한 이용 범주가 있어야 한 다. 모터가 컨버터 또는 유사한 장치에 의해 공급되는 경우 계산 시 필요한 차단 용량에 대한 가능 한 영향을 고려해야 한다. 비고 KS C IEC 60309-1 에 따른 적합한 정격의 플러그 및 소켓 수구, 케이블 커플러 또는 기기 커플 러는 이 요구사항을 충족할 수 있다. 전원 차단 장치가 플러그/소켓 조합일 때, 기계를 on/off 하는 기능을 하는 이용 범주가 적합한 개폐 기구가 제공되어야 한다. 이는 앞에서 설명된 연동 개폐 장치를 이용하여 동작될 수 있다. 5.3.4 공급 차단 장치의 조작 도구 공급 차단 장치의 작동 수단(예: 핸들)은 전기 장비 밀폐함에 있어야 한다. 예외: 밀폐함의 외부에서 공급 차단 장치를 열 수 있는 다른 수단(예: 누름 버튼)을 제공하는 경우, 동력 구동 개폐장치 밀폐함의 외부에 핸들이 있을 필요는 없다. 전원 차단 장치의 조작 도구(예: 손잡이)는 쉽게 접근이 가능한 위치에 설치하되, 지면 위로부터 0.6 m ~ 1.9 m 사이에 위치하도록 한다. 가능한 한 1.7 m 이하를 권고한다. 비고 조작 방향은 KS C IEC 61310-3 을 참조한다. 비상 작동 시 외부 작동 수단을 사용하고자 하는 경우, 10.7.3 이나 10.8.3 을 참조한다. 비상 작동 시 외부 작동 수단을 사용하지 않는 경우, - 이를 검은색이나 회색으로 표시할 것을 권장한다(10.2 참조). 19 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c72135fc-e71c-446c-8651-b64b71865ece | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 키나 도구를 사용하지 않고 즉시 열 수 있는 보조 덮개나 문을 제공할 수 있다. 예를 들어 환경 조건이나 기계적 손상으로부터 보호하기 위하여 제공할 수 있다. 이런 덮개/문은 작동 수단에 접 근할 수 있다는 사실을 분명하게 표시한다. 예를 들어, IEC 60417-6169-1(2012-08)(그림 2)이나 IEC 60417-6169-2 (2012-08) (그림 3)과 같은 부호를 사용하여 이런 사실을 표시할 수 있다. ![image](/image/placeholder) L 그림 2 - 단로기 절연체 [ * L 그림 3 - 회로 차단기 5.3.5 적용 제외 회로 다음의 회로는 전원 차단 장치에 의하여 차단할 필요가 없고, 유지 보수 또는 수리 중에 필요한 조명용 전기 회로 수리 또는 유지 보수용 도구 및 장비의 접속용 소켓 수구(예: 핸드 드릴, 시험 장비 등)(15.1 참조) 전원 공급 실패 시 자동 차단용으로만 사용하는 부족 전압 보호 회로 정상 작동을 위하여 항상 전원이 공급되어야 하는 선로(예: 온도 제어 측정 장치, 가열기, 프로그 램 저장 장치) 자체 차단 장치로 차단하는 것을 권고한다. 다른 전원 차단 장치를 통해 공급되는 제어 회로는 해당 차단 장치가 전기 장비에 있든 다른 기계 또는 기타 전기 장비에 있든 관계없이 전기 장비의 전원 차단 장치로 분리할 필요가 없다. 위의 회로들이 전원 차단 장치로 차단되지 않는다면, 다음의 조치를 취한다. 전원 차단 장치의 조작에 가까운 적절한 위치에 위험에 대한 주의 를 주기위하여 반영구적인 경고 표지를 부착할 것. 사용 설명서에 관련 사항을 포함되어야 한다. 다음 사항 중 하나가 포함되어야 한다. · 도체를 13.2.4 의 권장사항을 고려하여 색으로 구분한다. · 적용 제외 회로를 다른 회로와 구별한다. · 예외 회로는 영구 경고 레이블로 식별된다. 20 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
7cfb11b8-cbf7-43e1-b61d-c95cbee4f7f1 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 5.4 불시 기동 방지용 전원제거 유지 보수 도중에 기계의 기동으로 위험을 초래할 우려가 있는 경우에는 불시 기동 방지용 전원제거 장치를 설치하여야 한다. 이러한 장치는 사용에 적합하고 편리하여야 하며, 용이하게 식별이 가능한 곳에 있어야 한다. 기능과 목적이 명확하지 않은 경우 (예: 위치에 따라) 이러한 장치는 전원 제거 범 위를 표시하도록 하여야 한다. 비고 1 이 표준은 불시 기동 방지를 위한 모든 장치를 다루지 않는다. ISO 14118(EN 1037)을 참조한 다. 비고 2 5.3.2 에 따른 전원 차단 장치 또는 기타 장치를 사용하여 예기치 않은 시작을 방지할 수 있다. 단로기, 분리형 퓨즈 링크 및 분리형 링크는 밀폐된 전기 작동 영역에있는 경우에만 예기치 않은 시 동을 방지하기 위해 사용할 수 있다(3.1.23 참조). 단로 기능을 충족시키지 못하는 장치[예: 제어 회로에 의한 접점 스위치 혹은 KS C IEC 61800-5-2 에 의해 안전 토크 제거(STO) 기능이 있는 전원 장치 시스템(PDS)]는 다음과 같은 작업 중 예기치 않은 시작 방지의 전원 차단용으로 사용된다. 검사 조정 전기 장비에서의 다음과 같은 작업의 경우: · 감전(6 절 참조) 및 화상의 재해 위험이 없는 경우 · 전원 차단 조치가 작업에 의하여 무효화될 우려가 없는 경우 · 작업이 간단한 경우(예: 배선을 만지지 않고 꽂음형 접속 장치 교체) 장치의 선정은 장치의 사용 목적을 고려한 위험 평가와 이를 운영하는 사람에 따라 달라진다. 5.5 전기 장비의 단로 장치 단로 장치는 감전 또는 화상의 위험 없이 전기 장비를 분리시킬 수 있어야 한다. 이러한 단로 장치 는 다음에 적합하여야 한다. 사용 목적에 적합하고 편리할 것. 적절한 위치에 설치할 것. 필요한 곳에는 적절한 표시를 하여 선로 구분이 용이하게 할 것. 기능과 목적이 명확하지 않은 경 우(예: 위치에 따라) 이러한 장치는 격리 된 장비의 범위를 표시하도록 표시되어야 한다. 일부의 경우, 전원 차단 장치(5.3 참조)는 그 기능을 수행할 수 있다. 그러나 전기 장비의 각 부분이 나 공통 모선 또는 컬렉터 배선 계통으로 공급되는 기계 설비 중 하나에 대해 작업이 필요한 경우, 각 부분 또는 각 기계마다 단로기를 설치하여야 한다. 전원 차단 장치에 추가하여 차단 기능을 충족하는 다음과 같은 장치가 이런 목적으로 사용될 수 있다. 21 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
14d3c025-07af-418c-9f3b-5e1a25a16996 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 5.3.2 에 기술된 차단 장치 단로기, 인출형 퓨즈 링크 또는 인출형 링크는 폐쇄 전기 취급 지역에 있는 경우에만 사용할 수 있다(3.1.23 참조). 관련 정보가 전기 장비에 제공되어야 한다(17 절 참조). 5.6 미승인, 부주의 및/또는 오결선 방지 폐쇄된 전기 취급 지역 외부에 있는 5.4 및 5.5 에 기술된 장치에는 OFF 위치(차단 상태)에 고정하는 장치가 있어야 한다(예를 들어, 패드 잠금, 키 잠금). 그런 고정 장치가 없을 때, 내부 재연결뿐만 아 니라 원격 연결이 방지되어야 한다. 5.4 및 5.5 에 설명 된 장치가 밀폐된 전기 작동 영역 내부에있는 경우 재연결에 대한 다른 보호 수 단(예: 경고 라벨)으로 충분할 수 있다. 그러나 5.3.2 e)에 따라 사용되는 플러그/소켓을 취급하는 사람이 즉각적인 감독을 받을 수 있는 위치 에 있는 경우에는 잠금 장비를 부착하지 않을 수 있다. 6 감전에 대한 보호 6.1 일반사항 전기 설비는 다음과 같은 보호를 통해 전격으로부터 인명을 보호하여야 한다. 기본 보호(6.2 및 6.4 참조) 고장 보호(6.3 및 6.4 참조) 이 보호 조치는 IEC 60364-4-41 의 6.2, 6.3 및 6.4(PELV 의 경우)에 따른다. 물리적 조건이나 운전조건 으로 인해 이러한 조치의 적용이 불가할 경우에는 IEC 60364-4-41 에 따른 다른 방법을 강구하여야 한다(예: SELV). 6.2 기본 보호 6.2.1 일반사항 전기 설비의 각 회로 및 부분에 대해서는 6.2.2 나 6.2.3 그리고 필요시 6.2.4 의 조치가 강구되어야 한 다. 예외: 이 조치가 곤란할 경우, IEC 60364-4-41 에 규정된 기본 보호를 위한 기타 조치(예: 배리어 사용, 이격 거리 확보, 장애물 사용, 접근 방지를 위한 구조 및 설치 기술의 사용)를 적용할 수 있다(6.2.5 및 6.2.6 참조). 설비가 아이들을 포함한 일반인에게 노출된 장소에 설치되는 경우, IP4X 또는 IPXXD(KS C IEC 60529 참조)에 상응하는 활선부 접촉에 대한 최소 보호 등급이 있는 6.2.2 나 6.2.3 의 조치를 적용하여야 한 다. 6.2.2 외함에 의한 보호 충전 부분은 외함 내에 설치하여야 하며, 최소 IP2X 또는 IPXXB 이상의 보호 등급으로 활선부 접촉 에 대한 보호를 하여야 한다(KS C IEC 60529 참조). 22 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
3355a10e-85ff-4531-a3e4-1472a4d61449 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 외함 윗표면이 쉽게 접근 가능한 경우, 윗표면에서의 활선부 접촉에 접촉에 대한 최소 보호 등급은 IP4X 또는 IPXXD 이어야 한다. 외함 개구부(즉, 문, 뚜껑, 덮개 등)는 다음 중의 한 가지 조건에서만 할 수 있어야 한다. a) 열쇠 또는 도구의 사용은 숙련자 또는 교육받은 자의 접근 시에 필요하다. 비고 1 열쇠 또는 도구의 사용은 숙련자 또는 교육받은 자의 접근으로 제한하기 위한 것이다 [17.2f) 참조]. 설비가 여전히 연결되어 있는 상태로 그런 취급 작업을 위해 장치를 리셋하거나 조정할 때 건드 리기 쉬운 (문 안쪽 부분 포함) 모든 충전 부분은 IP2X 또는 IPXXB 이상으로 접촉으로부터 보호 되어야 한다. 문 안쪽의 다른 활선부는 IP1X 또는 IPXXA 등급 이상에 의하여 무의 식적인 직접 접촉을 방지하여야 한다. b) 외함이 개방되기 전에 외함 내부 활선부의 차단. 단로기가 문이 열릴 때만 개방되고 문이 닫힐 때만 닫히는 방식으로 단로기(예: 전원 차단 장치) 와 문을 연동시킴으로써 성취될 수 있다. 예외: 다음의 조건이 충족되는 경우, 공급자에 의해 제공된 열쇠나 도구를 사용하여 연동을 방지 할 수도 있다. 연동 장치가 단로기를 개방할 수 없을 경우, 단로기를 OFF(분리) 위치에 고정하거나 단로기의 미인가 폐쇄를 방지하는 경우 문을 닫음과 동시에 연동 장치의 기능이 자동으로 복구되는 경우 설비가 여전히 연결되어 있는 상태로 그런 취급 작업을 위해 장치를 리셋하거나, 조정할 때 건 드리기 쉬운 (문 안쪽 부분 포함) 모든 충전 부분은 IP2X 또는 IPXXB 이상으로 무의 식적인 활 선부 접촉으로부터 보호된다. 문 안쪽의 다른 활선부는 IP1X 또는 IPXXA 등급 이상에 의하여 무의 식적인 접촉을 방지한다. 전기 설비 사용 설명서에 연동 실패에 대한 절차에 관한 관련 정보가 제공될 경우(17 절 참조) 숙련된, 또는 교육을 받은 자에게는 차단 장치를 직접 연동하지 않고 문 뒤의 충전 부품에 접 근하는 것을 제한하는 조치가 제공될 경우[17.2 b) 참조] 다음의 경우를 제외하면, 개폐 장치(5.3.5 참조)를 차단한 후에도 충전되는 모든 부분은 IP2X 또는 IPXXB 이상의 보호 등급에 의하여 직접 접촉을 방지하여야 한다(KS C IEC 60529 참조). 이러한 부분은 16.2.1 에 의한 감전 경고 표지가 부착되어야 한다(색상에 의한 도체 구분은 13.2.4 참조). 연동 회로에 접속하는 경우에만 충전될 수 있는 부분 및 13.2.4 에 의한 잠재적인 활선부로서 색깔로 구분되는 부분 별도의 분리된 외함 내부에 설치되는 전원 차단 장치의 전원 단자 c) 활선부를 차단하지 않는 상태에서 열쇠 또는 도구를 사용하지 않고 문을 여는 경우는 모든 활선 부의 보호 등급이 IP2X 또는 IPXXB 이상에 의하여 접촉을 보호하는 경우에 한한다(KS C IEC 60529 참조). 이 조치를 위해 배리어가 사용되는 경우는 특수 공구를 사용해서만 배리어를 제거할 수 있 도록 하거나, 배리어가 제거될 경우는 피보호 활선부가 자동으로 차단되어야 한다. 6.2.2 c)에 따라 접촉 방지 기능이 달성될 경우, 그리고 장치의 수동 조작(예: 접촉기 또는 계전기의 수동 폐쇄)에 의해 위험이 야기될 수 있는 경우, 그런 조작은 제거를 위해 도구를 필요로 하는 장애물 또는 배 리어로 방지되어야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 23 | {}
7decac81-5492-44a5-951c-5bcf403ebb3e | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 6.2.3 활선부 절연에 의한 보호 활선부는 내구성이 있는 절연체로 피복되어야 하며, 절연체는 정상 사용 상태에서 기계, 화학, 전기, 열 응력에 견디는 절연 내력이 있어야 한다. 비고 페인트, 바니스, 래커 등의 자체만으로는 정상 사용 조건에서 감전 보호용 절연물로 사용될 수 없다. 6.2.4 잔류 전압에 대한 보호 전원이 차단되었을 때 60 V 이상의 잔류 전압이 있는 활선부는 5 초 이내에 설비 기능에 영향을 미치 지 않는 범위 내에서 60 V 이하로 방전시켜야 한다. 다만, 충전 전하가 60 uC 이하인 경우는 예외로 한다. 이런 규정된 방전 범위가 기기의 적합한 기능을 간섭할 경우, 외함을 개방하기 전에 일정 시간 대기할 수 있도록 주의 표시를 취급자가 용이하게 볼 수 있는 위치나 활선부가 수납된 외함에 표시 하여야 한다. 플러그 등과 같이 접속 해제 시 도체(예: 핀 부위 등)가 노출되는 경우에는 60 V 이하로 1 초 이내에 방전되도록 하거나, 도체 부분을 IP2X 또는 IPXXB 이상으로 하여야 한다. 만약 방전 시간이 1 초 이내가 아니거나 보호 등급이 IP2X 또는 IPXXB 이상이 아닐 경우(도선, 도체 바 또는 슬립링 등의 제거할 수 있는 컬렉터의 경우, 12.7.4 참조)에는 추가적인 단로 장치 또는 적절한 경보가 이루어져야 한다. 예를 들어 위험에 주의 를 기울이고 필요한 지연을 나타내는 경고 표시가 제공되어야 한다. 설비가 어린이를 포함하여 모든 사람에게 개방된 장소에 있는 경우 경고만으로는 충분하지 않으므로 IP4X 또는 IPXXD 에 대한 충전 부품과 의 접촉에 대한 최소한의 보호 수준이 필요하다. 비고 주파수 변환기 및 DC 버스 공급 장치는 일반적으로 5 초보다 긴 방전 시간을 가질 수 있다. 6.2.5 배리어에 의한 보호 배리어에 의한 보호는 IEC 60364-4-41 의 요구사항을 적용한다. 6.2.6 이격 또는 장애물에 의한 보호 이격 조치에 의한 보호는 IEC 60364-4-41 의 요구사항을 적용하고, 장애물에 의한 보호는 IEC 60364-4- 41 의 요구사항을 적용한다. 보호 등급이 IP2X 혹은 IPXXB 이상인 컬렉터 선 설비 또는 컬렉터 봉 설비는 12.7.1 을 참조한다. 6.3 고장 보호 6.3.1 일반사항 고장 보호(3.31)는 활선부와 노출 도전성 부분 사이의 절연 고장으로 인한 감전 위험을 방지하는 데 있다. 전기 설비의 각 회로 또는 각 부분은 6.3.2 및 6.3.3 에 따른 조치 중 최소한 하나 이상의 방법을 적 용하여야 한다. 위험한 접촉 전압의 발생 방지를 위한 조치(6.3.2) 또는 접촉 전압에 접촉한 시간이 위험한 수준까지 올라가기 전에 전원의 자동 차단(6.3.3) 24 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
6e24a3cd-cce6-4cab-8f54-4c38db124d16 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 비고 1 접촉 전압이 인체에 미치는 유해한 위험은 접촉 전압의 값 및 가능 노출 기간에 따라 달라진다. 비고 2 KS C IEC 61140 의 설비 및 보호 규정에 대한 조항 참조 6.3.2 위험 접촉 전압의 발생 억제 조치 6.3.2.1 일반사항 위험한 접촉 전압의 발생 억제를 위한 조치 방법은 다음과 같다. 클래스 II 설비의 사용 또는 동등한 절연 전기적 분리 6.3.2.2 클래스 II 설비의 사용 또는 동급 절연에 의한 보호 이 조치는 기본 절연 고장 시 접촉이 우려되는 부위에 위험한 접촉 전압의 발생을 억제하기 위한 것 이다. 이것은 다음 방법 중 한 가지 이상이어야 한다. 클래스 II 전기 장비 또는 기기의 사용(KS C IEC 61140 에 따른 이중 절연, 강화 절연 또는 동등 이상의 절연) KS C IEC 61439-1 에 따른 도체의 절연이 확보된 개폐 장치 또는 제어 장치의 사용 IEC 60364-4-41 에 따른 부가 또는 강화 절연의 사용 6.3.2.3 전기적 분리에 의한 보호 각 회로의 전기적 분리는 회로 활선부의 기본 절연의 고장에 의해 충전될 수 있는 노출 도전성 부분 과의 접촉을 통한 위험한 접촉 전압을 억제하기 위한 것이다. 이 보호 형태는 IEC 60364-4-41 의 요구사항을 적용한다. 6.3.3 전원의 자동 차단에 의한 보호 이 조치는 고장의 경우, 보호 장치를 자동 작동하여 하나 이상의 라인 도체를 차단하는 것이다. 이런 차단은 접촉 전압의 시간을 TN 및 TT 시스템에 대해 부속서 A 에 지정된 제한 내 시간으로 제한하기 에 충분히 짧은 시간 내에 발생해야 한다. 이 조치는 다음 사항의 조정을 필요로 한다. 전원 계통, 전원 임피던스 및 접지 계통 방식 보호 본딩 회로를 통해 흐르는 고장 전류 경로와 관련된 요소 및 서로 다른 선로 요소의 임피던 스값 절연 고장을 감지하기 위하여 사용되는 보호 장치의 특성 비고 1 공급의 자동 차단을 통한 보호를 위한 조건의 검증에 대한 세부사항에 대해서는 18.2 에서 규 정한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 25 | {}
d787d481-f6c5-4c42-ba14-87f681e42c02 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 이런 보호 조치는 다음과 같다. 보호 본딩 회로와 노출 도전성 부분의 접속(8.2.3 참조) 다음 중 하나: a) TN 시스템의 경우, 다음의 보호 장치를 사용할 수 있다. · 과전류 보호 장치 · 누설 전류 보호 장치(Residual Current Protective Device, RCDs) 및 이와 관련한 과전류 보호 장치 비고 2 IEC 62020 를 준수하는 누설 전류 모니터링 장치(Residual Current Monitoring Device, RCM)를 사용함으로써 예방 보전을 강화할 수 있다. b) TT 시스템의 경우: · 활선부에서 노출 도전성 부분이나 접지로 절연 고장을 탐지 시 공급의 자동 차단을 시작하 는 RCD 및 이와 관련한 과전류 보호 장치 · 고장 보호를 위하여 과전류 보호 장치를 사용할 수 있다. 다만 고장 루프 임피던스 Zs (A.2.2.3 참조)의 값을 영구적으로 그리고 확실히 낮게 유지한다. 비고 3 IEC 62020 를 준수하는 누설 전류 모니터링 장치(RCM)를 사용함으로써 예방 보전을 강화할 수 있다. c) IT 계통은 IEC 60364-4-41 의 관련 요구사항을 준수하여야 한다. 절연 고장이 지속하는 동안, 음향 및 광 신호를 지속하여야 한다. 음향 신호를 보낸 후에는 이를 수동으로 음소거 할 수 있다. 이를 위하여 공급자와 사용자가 절연 모니터링 장치 및/또는 절연 고장 위치 시스템을 제공하는 데 대하여 합의 하여야 할 수 있다. 비고 4 대형 기계의 경우, KS C IEC 61557-9 에 따르는 절연 고장 위치 시스템을 제공함으로써 유지 보수를 용이하게 할 수 있다. a)에 따라 자동 차단 기능이 제공될 경우, A.1.1 내에 규정된 시간 내에 차단이 보장되어야 한다. A.1.3 의 요구사항을 충족시키기 위해 필요한 만큼 보조 보호 본딩이 제공되어야 한다. 전력 구동 시스템(Power Drive System, PDS)을 제공하는 경우, 변환기가 제공하는 전력 구동 시스템 의 회로에 대한 고장으로부터 시스템을 보호한다. 변환기가 이런 고장으로부터 시스템을 보호하지 않는 경우, 변환기 제조자의 지시 사항에 따라 필요한 보호 조치를 취한다. 6.4 PELV 의 사용에 의한 보호 6.4.1 일반 요구사항 PELV(보호 특별저압)의 사용은 간접 접촉 및 제한 구역 내에서 직접 접촉에 의한 전격 재해를 예방 하기 위한 것이다(8.2.1 참조). PELV 회로는 다음 조건 모두를 만족하여야 한다. a) 공칭 전압은 다음을 넘지 않아야 한다. 1) 설비가 건조한 장소에서 사용되고 인체가 활선부에 접촉하는 면적이 크지 않을 경우에는 교류 (실훗값) 25 V 또는 직류(무맥동) 60 V 26 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
786966a9-b969-4e47-82b8-5336221604e4 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 2) 교류(실훗값) 6V 또는 직류 맥동값 15V 비고 무맥동은 일반적으로 실훗값의 10% 이하의 맥동 성분인 사인파 맥동 전압으로 정의 한다. b) 회로의 한쪽 또는 전원의 한 점은 보호 본딩 회로에 접속하여야 한다. c) PELV 회로의 활선부는 다른 활선회로와 전기적으로 분리되어야 한다. 전기적 분리는 안전 절연 변압기(safety isolating transformer)의 1 차, 2 차 권선에서 요구하는 것 이상이어야 한다(KS C IEC 61558-1 및 KS C IEC 51558-2-6 참조). d) 각 PELV 회로의 도체는 다른 회로와 물리적으로 분리되어야 한다. 분리하기 어려운 경우에는 13.1.3 에 의한 절연 규정을 적용하여야 한다. e) PELV 회로용 플러그/콘센트 수구는 다음에 적합하여야 한다. 1) 플러그는 다른 전압 계통에 삽입될 수 없는 구조일 것. 2) 콘센트 수구는 다른 전압 계통의 플러그가 삽입될 수 없는 구조일 것. 6.4.2 PELV 용 전원 PELV 용 전원은 다음 중 하나를 만족하여야 한다. KS C IEC 61558-1 및 KS C IEC 61558-2-6 에 따른 안전 절연 변압기 안전 절연 변압기와 동등의 안전 등급의 전원(예: 동등 절연의 권선을 보유한 전동 발전기 등) 전기화학 전원(예: 축전지) 또는 고압 회로와 분리된 전원(예: 디젤 발전기) 내부 고장의 경우에도 출력 단자 전압이 6.4.1 에서 규정하는 전압을 넘지 않도록 보호 수단이 구 비된 약전 회로 공급 방식 사용 7 설비 보호 7.1 일반사항 이 7 절에서의 조치는 다음 영향에 대하여 설비를 보호하기 위한 것이다. 단락 과전류 모터 냉각의 과부하 및/또는 손실 이상 온도 전원 전압에서의 손실 또는 감소 기계/기계 부품의 과속 지락 전류 어긋난 상 순서 낙뢰 및 개폐 서지로 인한 과전압 7.2 과전류 보호 7.2.1 일반사항 27 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
40a112ff-f4d2-45e7-833b-09beef1c507a | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 과전류 보호는 어떤 회로의 전류가 각 부품의 정격 전류나 도체의 허용 전류를 초과 하는 경우에 이 중 낮은 값에 대한 과전류를 보호하여야 한다. 정격 및 설정 방법은 7.2.10 의 규정에 따른다. 7.2.2 전원용 도체 사용자가 특별히 지정하지 않는 한, 전기 장비의 공급자는 공급 도체와 전기 장비의 전원 도체용 과 전류 보호 장치를 설치할 의무는 없다. 도체 치수 (전기 장비의 단자에 연결될 수 있는 공급 도체의 최대 단면적 포함)와 과전류 보호 장치 를 선정하는 데 필요한 자료를 설치 문서에 기입하여야 한다(7.2.10 및 17 절 참조). 7.2.3 전기 회로 7.2.10 에 따라 선정된 과전류의 감지 및 차단 장치는 제어 회로 변압기를 공급하는 회로 포함하는 각 충전 도체에 적용하여야 한다. 중성 도체의 단면적이 상도체의 단면적과 같거나 클 경우, 중성 도체에 단로 장치는 물론 과전류 감 지기를 설치할 필요는 없다. 교류 전기 회로에는 중성 도체 직류 전류 회로에는 접지 도체 모바일 장치의 노출 도전부에는 직류 전원 도체 본딩 중성 도체의 단면적이 선도체의 단면적과 같거나 클 경우, 중성 도체에 단로 장치는 물론 과전류 감 지기를 설치할 필요는 없다. 관련 선도체보다 작은 단면적의 중성 도체에 대해서는 IEC 60364-5-52: 2009 의 524 절에 규정된 조치에 따른다. IT 계통에서는 중성 도체를 사용하지 않도록 권고한다. 그러나 중성 도체가 사용되는 경우에는 IEC 60364-4-43:2008 의 431.2.2 의 규정에 따른다. 7.2.4 제어 회로 전원 전압에 직접 접속되는 제어 회로의 도체는 7.2.3 에 따라 과전류에 대하여 보호되어야 한다. 변압기 또는 직류 공급기에 의해 공급되는 제어 회로의 도체는 과전류 방지가 되어야 한다(9.4.3.1.1 참조). 보호 본딩 회로에 연결된 제어 회로에서는 과전류 보호 장치를 개폐 도체에 삽입하여 보호 본딩 회로에 연결되지 않은 제어 회로에서는 · 장비의 모든 제어 회로가 동일한 전류 전달 용량을 갖는 경우, 과전류 보호 장치를 개폐 도체 에 삽입하여 · 장비의 제어 회로가 다른 전류 전달 용량을 갖는 경우, 과전류 보호 장치를 각 제어 회로의 개 폐 및 공통 도체에 삽입하여 7.2.5 소켓 수구 및 관련 도체 장비 보수에 필요한 범용의 전원용 소켓 수구 선로에는 과전류 보호 장치를 부착하되, 접지되지 않 은 충전 도체를 차단할 수 있어야 한다. 소켓 수구 같은 급전 기능이 있는 각 회로의 미접지 충전 28 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
01da8648-7bf0-46fc-8f26-1a87731b5f64 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 도체에는 과전류 보호 장치가 있어야 한다(15.1 참조). 7.2.6 조명 회로 조명 전원 선로의 접지되지 않은 모든 충전 도체는 다른 선로의 보호와 는 별도로 과전류 보호 장치 를 설치하여 단락 영향으로부터 보호되어야 한다. 7.2.7 변압기 변압기는 변압기 제조자의 요구사항에 따른 형식과 기능을 가지는 과전류 보호 장치로 보호가 되어 야 한다. 이러한 보호는 다음과 같다(7.2.10 참조). 변압기 자화 돌입 전류로 인한 불필요한 트립을 방지할 것. 2 차측 단자에서의 단락 사고에 의한 영향으로 변압기 권선의 절연 등급에 따른 허용값을 초과 하 는 온도 상승을 방지할 것. 7.2.8 과전류 보호 장치의 위치 과전류 보호 장치는 피보호 도체가 전원과 연결되는 지점에 설치하여야 한다. 이것이 곤란하여 과전 류 보호를 못할 경우에는 전원 도체의 허용 전류보다 작은 도체를 사용하여야 하며, 단락 사고의 확 률은 다음 조건을 모두 만족시킴으로써 줄일 수 있다. 도체의 허용 전류가 필요한 부하 전류 이상인 경우 과전류 보호 장치에 접속된 도체 길이가 각각 3m 이하인 경우 도체가 외함이나 덕트에 의해 보호된 경우 7.2.9 과전류 보호 장치 정격 차단 용량은 설치점에서 예상되는 고장 전류 이상이어야 한다. 전원측(예: 전동기, 역률 개선용 콘덴서)에 다른 전류원이 있는 경우에는 이 전류를 고려하여야 한다. 비고 회로 차단기와 다른 단락 보호 장치 사이의 단락 조건하에서 조정에 대한 정보는 IEC 60947-2: 2006, IEC 60947-2:2006/AMD1:2009 및 IEC 60947-2:2006/AMD2:2013 의 부속서 A 에 제공된다. 퓨즈가 사용되는 경우, 쉽게 구입이 가능한 형식을 선정하거나 예비품의 공급을 사용자가 할 수 있 는 것을 선정하여야 한다. 7.2.10 과전류 보호 장치의 정격 및 설정 퓨즈의 정격 전류 또는 기타 과전류 보호 장치의 전류 설정값은 가능한 한 낮게 선정하되, 예상 과 전류(예: 전동기 기동 또는 변압기 돌입 전류)에 적절한 것이어야 한다. 보호 장치를 선택할 경우, 과 전류로 인한 위험에 대하여 제어 개폐 기구가 보호되는지를 검토하여야 한다. 도체의 과전류 보호 장치의 정격 전류 또는 설정은 12.4, D.3 에 따른 장치에 의해 보호되는 도체의 허용 전류 용량으로 결정한다. 이때 피보호 선로 내의 다른 전기 장비와 의 협조의 필요성을 고려하 되, D.4 에 따라 허용 가능한 최대 차단 시간 t 에 의해 결정된다. 7.3 전동기의 과부하 보호 29 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
6fac0b64-6612-42e6-8576-68d696a4f389 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 7.3.1 일반사항 전동기의 과부하 보호는 정격 출력이 0.5 kW 이상인 각 전동기에 하여야 한다. 예외: 전동기 작동이 자동 정지되어서는 안 되는 경우(예: 소방 펌프), 과부하 감지는 조작자가 인지 할 수 있는 경고 신호를 주어야 한다. 전동기의 과열 보호는 다음 조치에 의해 달성될 수 있다. 과부하 보호(7.3.2) 비고 1 과부하 방지 장치는 회로의 정격 최대 부하를 초과 하는 회로에서 시간 및 전류 관계(12t) 를 감지하여 적합한 제어 반응을 개시한다. 과온 보호(7.3.3) 비고 2 온도 감지 장치는 과온을 감지하고 적합한 제어 반응을 개시한다. 전류 제한 보호 과부하 보호 장치가 작동된 후 전동기의 자동 재기동이 기계 또는 공정상의 손상이나 위험한 상황이 초래될 우려가 있는 경우에는 자동 재기동되지 않도록 하여야 한다. 7.3.2 과부하 보호 과부하 보호 기능이 제공될 경우, 과부하의 감지는 중성 도체를 제외한 모든 상도체에 각각 조치하 여야 한다. 그러나 전동기의 과부하 감지 장치(D.2 참조) 기능이 도체의 과부하 보호에 사용되지 않는 경우, 활 선 도체 중 하나에서 과부하 감지를 생략할 수 있다. 단상이나 직류 전동기는 한 개의 접지되지 않은 상도체에서만 감지가 허용된다. 과부하 보호가 전원의 차단에 의하여 이루어지는 경우, 개폐 장치는 모든 상도체를 차단시켜야 한다. 중성 도체의 개폐기는 필요하지 않을 수 있다. 특수 정격을 가진 전동기로서 빈번한 기동 및 정지 기능이 요구되는 경우(예: 급발진 및 정지 · 급격 한 역회전 또는 예민한 회전 운동이 필요한 전동기)로서 피보호 권선의 시상수에 상응하는 시상수를 가진 과부하 보호 장치의 설치가 어려울 경우에는 당해 전동기에 적합하도록 고안된 과부하 보호 장 치를 설치하는 것이 바람직하다(7.3.3 참조). 과부하가 될 수 없는 전동기(예: 토크 전동기, 기계적인 과부하 보호 장치로 보호되거나 적절한 표준 으로 보호되는 운행 장치)에 대한 과부하 보호 장치는 생략할 수 있다. 전동기의 과부하 보호는 온도 감지 장치 또는 전류 제한 장치, 과부하 보호 장치와 같은 장치의 사용으로 이룰 수 있다. 7.3.3 과열 보호 과열 보호 장치가 있는 전동기(KS C IEC 60034-11 참조)의 사용은 냉각이 불량할 경우(예: 먼지가 많 은 환경)에 권고된다. 전동기의 종류에 따라 내장형 온도 보호 방식이 회전자 구속 시 보호가 충분하 지 못할 경우에는 추가적인 보호 장치를 설치하여야 한다. 30 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
2d842835-4c9f-4bda-b84a-bc97f8a835dc | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 과열 보호 장치는 또한 과부하가 될 수 없는 전동기(예를 들어, 토크 전동기, 기계적인 과부하 보호 장치로 보호되거나 적절한 표준으로 보호되는 운행 장치)에도 과열 가능성이 존재할 경우(예를 들어, 냉각 기능 축소로 인해) 권장된다. 7.4 이상 온도 보호 장비는 위험한 상황을 초래할 수있는 비정상적인 온도로부터 보호되어야 한다. 7.5 전원 차단 또는 전압 강하 영향의 보호 및 복구 전원 차단 또는 전압 강하가 기계 또는 작업 공정상의 위험한 상태를 유발할 수 있을 경우, 부족 전 압 보호(예: 기계의 전원 차단)는 설정된 전압 크기에서 이루어져야 한다. 기계 작동에서 단시간 동안 전원의 차단이나 강하가 허용되는 경우, 지연형 부족 전압 보호를 적용 할 수 있다. 부족 전압 보호 장치의 작동은 기계의 다른 정지 제어에 영향을 주어서는 안 된다. 인입 전원 전압의 복구 또는 개폐와 관련하여 기계의 자동 재기동이나 갑작스런 재기동은 위험한 상 황을 발생시킬 수 있으므로 방지하여야 한다. 기계 또는 서로 연관되어 작동하는 기계군의 일부분만이 전압 강하 또는 전원 차단에 영향을 받는 경우, 부족 전압 보호는 협조를 유지하기 위하여 적합한 제어 명령을 이루어야 한다. 7.6 전동기 과속 보호 과속 보호는 과속이 발생할 수 있고 과속으로 인하여 위험한 상태를 초래할 우려가 있는 경우, 9.3.2 에 따른 조치를 취하여야 한다. 과속 보호는 적합한 제어 응답을 발생시켜야 하며 자동으로 재기동 하는 것을 막아야 한다. 이 과속 보호 장치는 전동기의 기계적 속도 제한이나 과부하가 되지 않도록 작동하는 것이다. 비고 이 보호는 원심 분리 스위치 또는 속도 제한 감시기로 구성할 수 있다. 7.7 추가적인 지락 전류 보호 6.3 에 따른 자동 차단에 의한 지락 전류 보호에 부가하여 이 보호는 과전류 보호의 감지 수준 이하 인 지락 전류에 의한 장비의 손상을 줄이기 위하여 사용된다. 보호 장치의 설정은 전기 장비의 올바른 작동으로 일관되게 낮게 하여야 한다. 직류 성분이 포함될 수 있는 고장 전류의 경우 IEC TR 60755 에 따라 유형 B 의 RCD 가 요구될 수 있다. 7.8 역상 보호 공급 전원의 부정확한 상 순서가 위험한 상태나 기계에 손상을 일으킬 수 있는 경우, 보호되어야 한다. 비고 부정확한 상 순서를 일으킬 수 있는 사용 조건은 다음과 같다. - 하나의 공급 전원이 다른 전원으로 전환되는 기계 - 기능상 외부로부터 전원이 공급되는 이동 기계 31 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c2e22fd1-f746-497e-9665-0e6455e1bb00 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 7.9 뇌 및 개폐 서지로 인한 과전압 보호 서지 보호 장치(SPDs)는 뇌 및 개폐 서지로 인한 과전압의 영향을 받을 수 있는 기계에 설치하여야 한다. 다음의 경우: 뇌로 인한 과전압 억제용 SPDs 는 전원 차단 장치의 인입 단자에 접속하여야 한다. 개폐 서지로 인한 과전압 억제용 SPDs 는 보호가 필요한 장비의 필요에 따라 접속하여야 한다. 비고 1 SPD 의 올바른 선택 및 설치에 대한 정보는 IEC 60364-4-44, IEC 60364-5-53, IEC 61643-12, IEC 62305-1 및 IEC 62305-4 에 나와 있다. 비고 2 기계, 전기 장비 및 외부 도전성 부분을 건물/주변의 공통 본딩 네트워크와 등전위 본딩을 실 시하면 설비에 대한 뇌의 영향을 포함한 전자기적 간섭을 줄일 수 있다. 7.10 단락 전류 정격 전기 장비의 단락 전류 정격을 결정해야 한다. 이것은 설계 규칙을 적용하거나 계산 또는 테스트를 통해 수행할 수 있다. 비고 단락 전류 정격은 예를 들어 KS C IEC 61439-1, IEC 60909-0, IEC/TR 60909-1 또는 IEC/TR 61912-1 에 따라 결정될 수 있다. 8 등전위 본딩 8.1 일반사항 이 8 절에서는 보호 본딩 및 기능 본딩의 요구사항에 대해 규정한다. 그림 4 에 이 개념을 도해하였다. 보호 본딩은 전격으로부터 인명을 보호할 수 있도록 고장을 방지하는 기본적인 장치이다(6.3.3 및 8.2 참조). 기능 본딩의 목적(8.4 참조)은 다음을 감소시키는 것이다. 기계의 작동에 영향을 줄 수 있는 절연 고장의 결과 기계 작동에 영향을 미칠 수 있는 민감한 전기 설비에 대한 전기적 장애 전기 설비를 손상시킬 수 있는 낙뢰로 인한 유도 전류 기능 본딩은 보호 본딩 회로를 연결하여 이루어지지만, 보호 본딩 회로의 전기적 외란의 수준이 전 기 설비가 적합한 기능을 할 만큼 충분히 낮지 않을 경우, 보호 및 기능 본딩을 위해 별도의 도체를 사용해야 할 수 있다. 32 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f244b0fd-f17e-4d99-8ad9-634c006156d2 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 기계 ![image](/image/placeholder) 전기 설비 U1 T1 V I a ~ ① � � L1 U E 2 2 L2 V (1/12) (10 2 L3 W N N M PE PE ≤2.5m 4 2 (9) 00 6 ¦ 보호 본딩 회로: ¦ 보호 본딩 회로: ¦ ¦ --- ¦ --- ¦ ¦ (1) ¦ 보호 도체와 PE 단자의 상호 연결 ¦ ¦ (2) ¦ 노출 도전성 부분의 연결 ¦ ¦ (3) ¦ 보호 도체로써 사용되는 전기 설비 설치 판에 연결된 보호 도체 ¦ ¦ (4) ¦ 전기 설비에 있는 도전성 구조부의 연결 ¦ ¦ (5) ¦ 기계의 도전성 구조부 ¦ ¦ 보호 본딩 회로에 연결되었지만 보호 도체로서 사용되지 않는 부분 ¦ 보호 본딩 회로에 연결되었지만 보호 도체로서 사용되지 않는 부분 ¦ ¦ (6) ¦ 가요성 또는 후강 구조의 금속 덕트 ¦ ¦ (7) ¦ 금속 케이블 시스 또는 외장 ¦ ¦ (8) ¦ 가연성 물질을 포함하는 금속 파이프 ¦ ¦ (9) ¦ 기계의 전원과 는 별도로 접지되고 일반적으로 대지 전위와 같은 전위를 유기하기 쉬운 경우, 예를 들어 다음과 같은 계통외 도전성 부분[17.2d) 참조]: 금속 파이프 울타리 사다리 난간 ¦ ¦ (10) ¦ 가요성 또는 연성 금속 덕트 ¦ ¦ (11) ¦ 지지선, 케이블 트레이 및 케이블 사다리의 보호 본딩 ¦ ¦ 기능적 이유에 따른 보호 본딩 회로에 연결 ¦ 기능적 이유에 따른 보호 본딩 회로에 연결 ¦ ¦ (12) ¦ 기능 본딩 ¦ ¦ 기준 명칭에 대한 레전드 ¦ 기준 명칭에 대한 레전드 ¦ ¦ T1 ¦ 보조 변압기 ¦ ¦ U1 ¦ 전기 설비의 설치 판 ¦ 그림 4 - 기계의 전기 설비에 대한 등전위 본딩의 예제 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 33 | {}
cdbb3e30-ec74-4ebb-8530-9bce8cf5418c | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 8.2 보호 본딩 회로 8.2.1 일반사항 보호 본딩 접지 회로는 다음을 상호 연결하여 구성된다. · PE 단자(5.2 참조) · 회로의 일부가 습동 접점을 포함하는 기계 설비에서의 보호 도체(3.1.51 참조) · 전기 설비의 노출 도전성 부분 및 도전성 구조부 예외: 8.2.5 참조 · 기계의 도전성 구조부 보호 본딩 회로의 모든 부분은 그 회로에 흐를 수 있는 지락 전류에 의하여 발생할 수 있는 최고 온 도와 기계적 응력을 견딜 수 있도록 설계되어야 한다. 케이블의 일부가 아니거나 선도체와 함께 공통 밀폐함에 있지 아니한 각 보호 도체의 단면적은 다음 보다 크거나 같다. - 기계적 손상으로부터 보호하는 경우, 2.5 mm2Cu 또는 16mm2 AI - 기계적 손상으로부터 보호하지 않는 경우, 4mm2Cu 또는 16 mm2 AI 비고 보호 도체용으로 강을 사용하는 것을 배제하지 않는다. 케이블의 일부가 아닌 보호 도체를 전선관, 트렁킹에 설치하거나 유사한 방식으로 보호하는 경우, 기 계적으로 보호된 것으로 간주한다. 6.3.2.2 에 따른 설비의 도전성 구조부는 보호 본딩 회로에 연결할 필요가 없다. 모든 제공 설비가 6.3.2.2 에 따르는 보호 본딩 회로에 기계의 도전성 구조부를 연결할 필요는 없다. 6.3.2.3 에 따른 기기의 노출 도전성 부분은 보호 본딩 회로에 연결되어서는 안 된다. 노출된 도전성 부분이 위험이 되지 않도록 노출된 도전성 부분을 장착하는 보호 본딩 회로에 노출된 도전성 부분을 연결할 필요는 없다. 그 이유는 다음과 같다. 노출된 도전성 부분의 표면을 손으로 만지거나 잡을 수 없다. 또한 노출된 도전성 부분은 그 크 기가 작다(약 50 mm x 50 mm 미만). 노출된 도전성 부분이 활선부와 접촉하거나 절연 고장이 발생하지 않도록 배치한다. 이를 나사, 리벳 및 명판과 같은 작은 부품 그리고 밀폐함 내부에 있는 부품에 적용한다. 부품의 크 기는 상관이 없다(예를 들어, 접촉기나 계전기의 전자 부품 및 장치의 기계적 부품). 8.2.2 보호 도체 보호 도체는 13.2.2 에 따라 구분되어야 한다. 보호 도체는 동선이 사용되어야 하며, 구리 이외의 금속이 사용되는 경우, 단위 길이당 전기 저항이 34 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
4f21c2e8-d7cb-4678-a17b-212c899c9a1a | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 동선의 저항값을 넘지 않아야 하고, 기계적 내구성을 위하여 그 단면적은 16mm2 이상이어야 한다. 보호 본딩 회로에 연결된 전기 설비의 금속 밀폐함, 프레임 또는 설치 판이 다음과 같은 세 가지 구 성요소를 충족하는 경우, 이를 보호 도체로 사용할 수 있다. · 기계적, 화학적 또는 전자기적 열화로부터 보호하도록 구조나 적절한 연결을 통하여 전기적 연속 성을 보장한다. · IEC 60364-5-54:2011, 543.1 의 요구사항을 준수한다. · 사전에 결정한 모든 탭 오프 지점에서 다른 보호 도체를 연결하는 것을 허용한다. 보호 접지 도체의 단면적은 IEC 60364-5-54:2011, 543.1.2 에 따라 계산하고 표 1 에 따라 선택한다(5.2 참조). 이 표준의 8.2.6 과 17.2 d)을 참조한다. 각 보호 도체는 다음과 같다. · 다심 케이블의 일부이다. · 선도체와 함께 공통 밀폐함 내에 있다. · 적어도 다음과 같은 단면적을 가진다. · 기계적 손상으로부터 보호하는 경우, 2.5 mm2 Cu 또는 16 mm2 AI · 기계적 손상으로부터 보호하지 않는 경우, 4mm2Cu 또는 16 mm2 AI 비고 1 보호 도체용으로 강을 사용하는 것을 배제하지 않는다. 케이블의 일부가 아닌 보호 도체를 전선관, 트렁킹에 설치하거나 유사한 방식으로 보호하는 경우, 기 계적으로 보호된 것으로 간주한다. 기계 및 그 전기 설비의 다음과 같은 부품을 보호 본딩 회로에 연결하지만 보호 도체로 사용하지 않 는다. · 기계의 도전성 구조부 · 가요성 또는 후강 구조의 금속 덕트 · 금속 케이블 시스 또는 외장 · 가스, 액체, 분말과 같은 가연성 물질을 포함하는 금속 파이프 · 가요성 또는 연성 금속 전선관 · 정상 사용 중 기계적 응력을 받는 구조부 · 유연한 금속 부품; 지지선; 케이블 트레이 및 케이블 사다리 비고 2 음극 보호에 대한 정보는 IEC 60364-5-54:2011 의 542.2.5 및 542.2.6 에서 제공한다. 8.2.3 보호 본딩 회로의 연속성 부품이 어떠한 이유로 제거되는 경우(예: 정기적인 유지 보수), 나머지 부품에 대한보호 본딩 회로는 차단되어서는 안 된다. 35 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
0db9c1ac-9044-4e27-a2ff-495dd15f389c | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 접속 및 본딩점은 통전 용량이 기계적, 화학적 또는 전기 화학적인 영향으로 손상되지 않도록 설계 되어야 한다. 알루미늄 또는 알루미늄 합금 재질의 외함 및 도체가 사용될 경우, 전식의 문제에 대하 여 특별한 주의 가 필요하다. 전기 설비가 덮개, 문 또는 덮개판 위에 설치되는 경우, 보호 본딩 회로의 연속성이 유지되어야 하며, 보호 도체(8.2.2 참조)의 사용이 권고된다. 보호 도체가 제공되지 않을 경우, 저항이 매우 적도록 고 안된 조임, 경첩 또는 습동 접촉을 고안하여야 한다(18.2.2 의 시험 1 참조). 위험이 노출된 케이블(예: 유연 트레일링 케이블) 내에서 접지 도체의 연속성은 적합한 방법으로 유 지되어야 한다(예: 감시 장치). 도선, 도체 바 및 슬립링 등을 사용하는 도체의 연속성에 대한 요구사항은 12.7.2 에 따른다. 보호 본딩 회로에는 개폐 장치, 과전류 보호 장치 (예: 스위치, 퓨즈) 또는 기타 차단 수단이 포함되 어서는 안 된다. 예외: 도구를 사용하지 않고는 열 수 없고 밀폐된 전기적 작동 영역에 있는 링크는 테스트 또는 측 정 목적으로 제공될 수 있다. 제거 가능한 집전체 또는 플러그/콘센트 조합을 통해 보호 본딩 회로의 연속성을 차단할 수 있는 경 우 보호 본딩 회로는 첫 번째 마지막 차단 접점에 의해 차단되어야 한다. 이는 탈착식 또는 탈착식 플러그인 장치에도 적용된다(13.4.5 참조). 8.2.4 보호 접지 도체의 접속부 모든 보호 접지 도체는 13.1.1 에 따라 마감 처리되어야 하며, 접속점이 기능이 다른 부분과 접속되어 서는 안 된다. 각 점에 연결되어 있는 보호 접지 도체는 그림 5 와 같이 기호 IEC 60417-5019:2006-08 에 사용된 것 과 같은 방법으로 구분되어야 한다. 그림 5 - 기호 IEC 60417-5019: 보호 접지 대안으로, 보호 접지 도체의 접속용 단자는 그래픽 기호인 PE 또는 초록색과 노란색이 조합된 2 색으 로 구분하거나 또는 이것을 조합해서 구분할 수 있다. 8.2.5 이동 기계 탑재 전원 공급 장치가 있는 이동 기계의 보호 회로, 노출 도전성 부분 및 계통외 도전성 부분 는 감전 방지를 위하여 보호 본딩 단자에 접속시켜야 한다. 또한 이동 기계가 외부 전원에 접속되는 경 우에도 보호 본딩 단자가 외부 보호 도체용 지점에 접속되어야 한다. 이동 기계가 외부 유입 전원에 연결될 수 없을 경우에는 이 보호 본딩 단자가 외부 보호 접지 도체의 접속점이 되어야 한다. 36 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
db9f0ba5-ede4-4239-acd3-ef31000ad49a | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 비고 전기 에너지의 공급이 설비의 고정식, 이동식 또는 움직일 수 있는 품목 내에서 자급식이고, 외부 전원에 연결되어 있지 않으면(예: 탑재된 축전지 충전기가 연결되어 있지 않는 경우), 외 부 보호 도체에 이러한 설비와 같은 것의 접속이 필요하지 않다. 8.2.6 누설 전류가 10 mA 보다 높은 전기 설비의 추가 요구사항 전기 설비의 모든 보호 도체에서 10 mA a.c. 또는 d.c.보다 높은 접지 누설 전류가 있을 경우, 누설 전류를 전달하는 관련 보호 본딩 회로의 각 섹션의 무결성에 대하여 아래 조건 중 하나 이상이 충족 되어야 한다. a) 보호 도체는 전기 설비 외함 내에 완전히 둘러싸이거나 기계적 손상으로부터 전장에 걸쳐 보호한다. b) 보호 접지 도체의 단면적은 적어도 10mm2 Cu 또는 16mm2 AI 가 되어야 한다. c) 보호 접지 도체 단면적이 10 mm2 Cu 또는 16 mm2AI 이하일 경우, 보호 접지 도체 단면적이 적 어도 10 mm2 Cu 또는 16 mm2 AI 가 되는 지점까지 적어도 단면적이 동일한 2 차 보호 접지 도체 가 제공되어야 한다. 이 경우, 전기 설비에 2 차 보호 도체 관련 별도 단자가 필요할 수 있다. d) 보호 도체 연속성 손실의 경우 전원의 자동 차단 e) 플러그-콘센트 조합이 사용되는 경우, IEC 60309 시리즈에 따른 산업용 커넥터, 적절한 스트레인 릴리프 및 다심 전력 케이블의 일부로 최소 보호 접지 도체 단면적 2.5 mm2 가 제공되어야 한다. 8.2.6 에 설명 된대로 설비를 설치해야 한다는 설명이 설치 지침에 제공되어야 한다. 비고 보호 도체 전류가 10 mA 를 초과 함을 알리는 경고 라벨이 PE 단자 옆에 제공될 수도 있다. 8.3 높은 누설 전류 제한 조치 높은 누설 전류의 영향은 해당 기기를 별도의 권선이 있는 전용 변압기에 연결하여 누설 전류가 높 은 설비로 제한될 수 있다. 이런 보호 본딩 회로는 기기의 노출 도전성 부분에 연결되어야 하고 변 압기의 보조 권선에도 연결되어야 한다. 설비와 변압기의 2 차 권선 간의 보호 도체는 8.2.6 에 설명된 내용의 하나 이상을 충족시켜야 한다. 8.4 기능 본딩 절연 고장의 결과 로서 오기능을 방지하기 위한 보호 조치는 9.4.3.1.1 에 따라 공통 도체를 연결하여 달성될 수 있다. 전자기 외란으로 인한 오기능 방지를 위한 기능 본딩 관련 권장사항은 4.4.2 와 부속서 H 를 참조한다. 기능적 본딩 연결 지점은 IEC 60417-5020:2002-10 기호를 사용하여 표시하거나 레이블을 지정해야 한다(그림 6 참조). 「 그 L 」 그림 6 - 기호 IEC 60417-5020: 프레임 또는 섀시 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 37 | {}
f89234a5-ba0c-4725-a770-8cefbf8ff675 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 9 제어 회로 및 제어 기능 9.1 제어 회로 9.1.1 제어 회로의 전원 제어 회로가 AC 전원에서 공급되는 경우 별도의 권선을 가진 변압기를 사용하여 전원 공급 장치와 제어 공급 장치를 분리해야 한다. 예는 다음과 같다. · KS C IEC 61558-2-2 에 따라 별도의 권선이있는 제어 변압기, · 개별 권선이 있는 변압기가 장착된 KS C IEC 61558-2-16 에 따른 스위치 모드 전원 공급 장치 · 개별 권선이 있는 변압기가 장착된 IEC 61204-7 에 따른 저전압 전원 공급 장치 다수의 변압기가 사용되는 경우, 변압기의 2 차 전압은 같은 상이 되도록 서로 연결되도록 하는 것이 바람직하다. 예외: 변압기 또는 변압기가 장착 된 스위치 모드 전원 공급 장치는 한 대의 전동기 기동기 및/또는 최대 2 대의 제어 장치(예: 연동 장치, 기동/정지 제어 위치)를 갖춘 기계에 대해서는 생략할 수 있다. AC 전원을 공급받는 직류 제어 회로가 보호 본딩 회로에 접속되는 경우(8.2.1 참조), 직류 제어 회로 는 AC 제어 회로용 변압기의 절연 변압기 또는 다른 제어 회로용 변압기로부터 공급받아야 한다. 9.1.2 제어 회로 전압 제어 전압의 값은 제어 회로의 올바른 작동에 지장이 없어야 한다, AC 제어 회로의 공칭 전압은 적정하게 다음 조건들을 초과 하지 않아야 한다. 공칭 주파수가 50 Hz 인 회로의 경우 230 V 공칭 주파수가 60 Hz 인 회로의 경우 277 V. DC 제어 회로의 공칭 전압은 220 V 를 초과 하지 않는 것이 좋다. 9.1.3 보호 장치 제어 회로에는 7.2.4 및 7.2.10 에 따라 과전류 보호 장치가 설치되어야 한다. 9.2 제어 기능 9.2.1 일반사항 비고 이 항에서는 제어 기능 이행에 사용되는 장치의 요구사항을 규정하지 않는다. 장비의 요구사항 관련에는 10 절을 참조한다. 9.2.2 정지 기능의 범주 38 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f26dc5dd-be07-4cc0-b488-ccb3f4c5c53a | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 정지의 분류는 다음의 3 가지 방식에 따른다. 분류 0: 기계 액추에이터 전원의 즉각적인 차단에 의한 정지(즉, 비제어 정지: 3.1.64 참조) 분류 1: 기계 액추에이터에는 전원이 공급된 상태에서 기계가 정지 후 전원이 차단되는 제어 정지 방식(3.1.14 참조) 분류 2: 기계 액추에이터에 전원이 인가된 상태에서의 제어 정지 방식 비고 동력을 제거하려면 토크 또는 힘을 생성하는 데 필요한 동력을 제거하는 것으로 충분할 수 있 다. 이는 클러치 해제, 분리, 전원 끄기 또는 전자적 수단(예: IEC 61800 시리즈에 따른 PDS) 등으로 달성할 수 있다. - 9.2.3 작동 9.2.3.1 일반사항 안전한 작동을 위해 필요한 안전 기능 및/또는 보호 조치[예: 인터로크(9.3 참조)]가 제공되어야 한다. 기계에 하나 이상의 조작반이 있을 경우, 다른 조작반의 명령 개시가 위험한 상황을 초래하지 않도 록 보장하는 조치가 제공되어야 한다. 9.2.3.2 기동 시작 기능은 관련 회로에 전원을 공급하여 작동해야 한다. 기동은 모든 안전 장치가 정상 설치되고 9.3.6 의 조건을 제외한 기능을 유지하는 경우에만 가능하여 야 한다. 안전 장치를 적용하기 곤란한 기계(예: 이동 기계)의 경우, 상황에 맞게 홀드투런(hold-to-run) 제어 방 식을 사용하는 허용 제어 장치(enabling control)와 함께 있을 때만 기동하여야 한다. 위험한 기계 작동을 시작하기 전에 청각적 및/또는 시각적 경고 신호 제공을 고려해야 한다. 순차 기동에 필요한 경우 적합한 연동 장치를 구비하여야 한다. 기계의 기동 제어반이 하나 이상일 경우, 각 제어반은 별도의 수동식 기동 제어 장치를 구비해야 하 며 다음 조건을 만족하여야 한다. 기계 작동에 필요한 모든 조건을 만족할 것. 모든 기동 제어 장치는 기동되기 전에 차단 위치에 있을 것. 모든 기동 제어 장치는 동시에 작동 준비가 되도록 할 것(3.1.7 참조). 9.2.3.3 정지 범주 0, 범주 1 및/또는 범주 2 의 정지 방식은 기계의 위험성 평가(4.1 참조) 및 기능 요구사항에 따 라 표시되어야 한다. 비고 1 공급 차단 장치(5.3 참조)이 작동시 정지 범주 0 으로 동작한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 39 | {}
638e0293-800c-4f47-b900-2c020740adc1 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 정지 기능은 관련 기동 기능을 무시하여야 한다. 하나 이상의 조작반이 제공될 경우, 기계의 위험 평가에 의해 요구 시 모든 조작반의 정지 명령이 유효해야 한다. 비고 2 정지 기능이 시작되면 동작 이외의 기계 기능을 중단해야 할 수 있다. 9.2.3.4 비상 조작(비상 정지, 비상 전원 차단) 9.2.3.4.1 일반사항 비상 정지 및 비상 전원 차단은 기계에서 1 차적인 위험(예: 트래핑, 감전 또는 연소) 축소 수단이 아 닌 보완적인 보호 조치이다(KS B ISO 12100 참조). 이 표준은 한 사람의 행위에 의해 기동되는 경우 이 표준 및 부속서 E 에 기술된 비상 조작 중 비상 정지 및 비상 전원 차단에 대한 요구사항을 규정한다. 비상 정지(10.7 참조) 또는 비상 전원 차단(10.8 참조) 조작기의 조작이 중지 또는 차단 명령에 따라 중지되면, 이 명령의 효과 는 리셋 시까지 유지되어야 한다. 이런 리셋은 명령이 개시된 해당 기계에 서만 가능해야 한다. 명령의 리셋은 기계를 재시동해서는 안 되고 단지 재시동을 허용하기만 해야 한다. 모든 비상 정지 명령이 리셋된 후에 기계 재시동이 가능해야 한다. 모든 비상 차단 명령이 재설정 될 때까지 기계에 전원을 공급할 수 없다. 9.2.3.4.2 비상 정지 기능적인 속성을 포함한 비상 정지 장비의 설계 관련 요구사항은 KS B ISO 13850 에 수록되어 있다. 비상 정지는 범주 0 정지 또는 범주 1 정지 방식이 선정되어야 한다. 비상 정지의 범주 선정은 기계 의 위험성 평가에 의해 결정되어야 한다. 예외: 경우에 따라 추가 위험을 방지하기 위해 제어된 정지를 수행하고 정지한 후에도 기계 액추에 이터에 대한 전원을 유지해야 할 수 있다. 정지 상태를 모니터링하고 정지 상태의 실패를 감지하면 위험한 상황을 만들지 않게 전원을 제거해야 한다. 정지 요구사항(9.2.3.3 참조)에 추가하여 비상 정지 기능은 다음 요구사항을 만족하여야 한다. · 모든 방식에서 기타 다른 모든 기능 및 작동을 무효화하여야 한다. · 다른 위험을 생성하지 않고 가능한 한 빨리 위험 모션을 중지해야 한다. · 복귀가 기계를 재기동시켜서는 안 된다. 9.2.3.4.3 비상 전원 차단 비상 전원 차단의 기능적인 면은 IEC 60364-5-53:2001 의 536.4 에 주어진다. 다음의 경우에는 비상 전원 차단 장치가 설치되어야 한다. 40 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
a3d4ae7f-8167-4e51-a7d2-19218f9b6fcc | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 · 기본 보호 방식이 (예: 도체 선, 도체 봉, 슬립링 조립체, 전기 취급 지역의 제어 장치) 장애물 (6.2.6 참조)이나 이격 설치를 통해 이루어지는 경우 또는 · 전기로 인하여 다른 위험 요인의 발생 또는 손상 우려가 있는 경우 비상 전원 차단은 전원 장치에 연결된 기계 액추에이터의 범주 0 정지 방식이 유효하도록 전기적 스 위칭 기계를 통한 전원 차단에 의해 이루어져야 한다. 기계가 범주 0 정지 방식을 감당하지 못하는 경우, 비상 전원 차단 장치가 필수적이지 않도록 기본 보호 방식과 같은 다른 보호 수단이 필요할 수 있다. 9.2.3.5 작동 방식 각 기계는 그 형태 및 사용 용도에 따라 하나 이상의 작동 방식(예: 수동 모드, 자동 모드, 설정 모드, 유지 관리 모드)을 가질 수 있다. 기계가 다양한 보호 조치가 필요하고 안전에 다른 영향을 미치는 여러 제어 또는 작동 모드에서 사 용할 수 있도록 설계 및 제작된 경우, 각 위치에서 잠글 수있는 모드 선택기가 장착되어야 한다(예: 키 작동 스위치). 선택기의 각 위치는 명확하게 식별할 수 있어야하며 단일 작동 또는 제어 모드에 해당해야 한다. 선택기는 기계의 특정 기능 사용을 특정 조작자 범주로 제한하는 다른 선택 방법(예: 액세스 코드)으 로 대체될 수 있다. 모드 선택 스위치 자체로 기계가 작동되어서는 안 되며, 조작자에 의한 별도의 작동이 요구되어야 한다. 각 특정한 작동 방식마다 관련 안전 기능 및/또는 보호 조치가 이행되어야 한다. 선정된 작동 방식이 표시되어야 한다(예: 방식 선정기 위치, 표시광 구비, 시각 표시 등). 9.2.3.6 지시 작동 감시 위험한 상황을 초래할 수 있는 기계의 움직임은 감시되어야 한다. 수동 제어 기계에서는 조작자가 감시 기능을 수행할 수 있어야 한다. 다만, 조작자가 감시할 수 없는 불가피한 경우 과주행 제한기, 과속 감지 장치, 기계식 과부하 방지 장치 또는 충돌 방지 장치를 포함한 별도의 수단을 강구하여야 한다. 비고 일부 수동 제어 기계(예: 수동 드릴링 머신)에서는 조작자가 감시 기능을 한다. 9.2.3.7 홀드투런 제어 홀드투런 제어(hold-to-run controls)는 조작 완료 시까지 제어 장치가 연속적으로 실행되어야 한다. 9.2.3.8 양수 조작 제어 양수 조작 제어의 3 가지 형태가 이용될 수 있으며(ISO 13851 참조) 선택은 위험성 평가에 따라 결정 된다. 이들은 다음과 같은 특성을 보유하여야 한다. 형식 I: 이것은 다음이 요구된다. 41 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
847c38f0-c8bc-4cdc-9c4e-f465004b365d | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 · 2 개의 제어 장치 구비로 양손으로 동시 조작 · 위험 상태에서는 계속적으로 동시 조작에 의해서 작동 · 위험 상태가 존재하는 경우, 제어 기구에서 두 손 또는 한 손이 떨어짐과 동시에 기계 작동이 중지 형식 I 양수 제어 기계는 위험한 작동을 개시하는 데 적합하지 않다. 형식 II: 기계가 재작동되기 전에 두 제어 장치 모두의 해제를 요하는 형식 I 제어 형식 III: 다음에 따라 제어 장치의 작동이 동시에 요구되는 형식 II 제어 · 한쪽 스위치 작동 후 0.5 초 이하의 정해진 시간 내에 다른 쪽 제어 기구를 작동시켜야 하는 기능 이 있을 것. · 시간 제한이 초과 될 경우, 두 제어 기구에서 두 손을 모두 떼어낸 후에야 재가동(초기화)이 가능 할 것. 9.2.3.9 허용 제어 장치 허용 제어 장치는 다음과 같은 수동 조작 제어 기능 연동 장치이다(10.9 참조). a) 작동 시 별도 기동 제어에 의해 기계 작동이 개시될 수 있다. b) 비활성 시 정지 기능을 개시하고 기계 작동 개시를 방지한다. 허용 제어 장치는, 예를 들어 기계 작동이 다시 개시되기 전에 허용 제어 장치의 활성 해제를 요구 하여 작동 실패할 가능성을 최소화하도록 설계되어야 한다. 9.2.3.10 기동 및 정지의 복합 제어 교대로 기동 및 정지 기능을 수행하는 누름 버튼 스위치 또는 기타 유사 제어 장치는 작동 시에 위 험한 상태를 유발시키지 않는 기능에서만 사용하여야 한다. 9.2.4 무선 제어 시스템(CCS) 9.2.4.1 일반 요구사항 이 항에서는 다른 제어 시스템과 조작 제어반 사이의 제어 신호 및 데이터를 전송을 위한 무선 제어 (예: 라디오파, 적외선) 기술을 채용하는 제어 시스템의 기능적 요구사항에 대하여 다룬다. 비고 1 9.2.4 에 있는 기계에 대한 언급은 "기계 또는 그 부품"으로 해석한다. 데이터 전송에 의존하는 CCS 의 안전한 기능을 위하여 전송 신뢰성 요구사항이 필요할 수 있다(예: 안전 관련 액티브 스톱, 모션 커맨드). CCS 는 위험 평가에 기초하여 애플리케이션에 적절한 기능과 반응 시간을 갖는다. 비고 2 IEC 61784-3 은 통신 네트워크의 통신 고장과 안전 관련 데이터 전송에 대한 요구사항을 설명 42 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
96def775-0c91-49dc-9dd7-db21ac7eafc4 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 한다. 비고 3 케이블이 없는 제어 시스템에 대한 추가적인 요구사항은 IEC 62745 초안의 IEC TC 44 에 따 라 개발 중이다. 9.2.4.2 기계 제어를 위한 무선 제어 시스템의 능력 감시 케이블이 없는 제어 시스템(Cableless Control System, CCS)이 기계를 제어할 수 있는 능력을 지속적 으로나 적절한 간격을 두고 자동 모니터링한다. 이런 능력의 상태를 분명하게 표시한다(예: 지시등, 시각 디스플레이 표시, 등). 통신 신호가 저하되어 기계를 제어할 수 있는 CCS 의 능력이 손실되는 경우(예: 신호 수준의 저하, 배터리 전원의 부족), 기계를 제어할 수 있는 CCS 의 능력이 손실되기 전에 이를 운용자에 경고한다. 기계를 제어할 수 있는 CCS 의 능력이 애플리케이션의 위험 평가를 통하여 결정한 시간 동안 손실된 경우, 기계를 자동으로 중지하기 시작한다. 비고 예를 들어 예상하지 못한 위험한 상황을 발생시킬 수 있는 자동 중지를 피하기 위하여 일부 경우에 기계가 사전에 정의 한 상태가 될 필요가 있을 수 있다. 기계를 제어할 수 있는 CCS 능력의 복원은 기계를 다시 시작하지 말아야 한다. 기계를 다시 시작하 기 위해서는 예를 들어 시작 버튼을 수동으로 작동시키는 것과 같은 의도적인 조치를 취하여야 한다. 9.2.4.3 제어 한계 케이블이 없는 대상 운용자 제어반의 신호 이외의 신호에 기계가 반응하는 것을 방지하기 위하여 조 치를 취한다(예: 코드화한 전송). 케이블이 없는 운용자 제어반은 대상 기계만 제어하고 해당 기계의 대상 기능에만 영향을 미친다. 9.2.4.4 여러 케이블이 없는 조작 제어반의 사용 케이블이 없는 조작 제어반을 하나 이상 사용하여 기계를 제어하는 경우: · 한 번에 케이블이 없는 조작 제어반을 오직 하나씩 활성화한다. 기계를 동작하기 위하여 필요한 케이블이 없는 운용자 제어반을 하나 이상 활성화하여야 하는 경우는 제외한다. 하나의 케이블이 없는 조작 제어반으로부터 다른 제어반으로 제어를 전환하기 위해서는 현재 제어 중인 제어반에서 수동으로 조치를 취하여야 한다. · 기계를 운영하는 동안 두 개의 케이블이 없는 조작 제어반의 기계 운영 모드 및/또는 기계의 기능 이 동일하게 설정된 경우에만 제어를 전환할 수 있다. · 제어를 전환하더라도 선택된 기계 운영 모드 및/또는 기계 기능은 변경되지 않는다. · 기계를 제어하고 있는 각각의 케이블이 없는 조작 제어반에 대하여 해당 제어반이 제어하고 있음 을 표시한다(예: 지시등, 시각 디스플레이 표시). 비고 위험 평가를 통하여 결정한 바와 같이 다른 위치들에서 표시하여야 할 수도 있다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 43 | {}
3c79fbeb-95b7-43e1-92e3-21b8fe8bc8cb | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 9.2.4.5 케이블이 없는 휴대형 조작 제어반 케이블이 없는 휴대형 조작 제어반은 무단 사용을 방지하는 수단을 제공한다(예: 키로 작동하는 개폐 기, 접속 코드). 케이블이 없는 제어의 대상인 각 기계는 케이블이 없는 제어의 대상이 되는 경우, 이를 표시하여야 한다. 케이블이 없는 휴대용 제어반이 여러 기계에 연결될 수 있는 경우, 어떤 기계에 연결될지를 선택할 수 있는 수단을 케이블이 없는 휴대형 조작 제어반에 제공한다. 연결될 기계를 선택하더라도 이는 제어 명령을 시작하지는 않는다. 9.2.4.6 케이블이 없는 조작 제어반의 의도적인 비활성화 제어 대상인 케이블이 없는 조작 제어반을 비활성화하는 경우, 이와 관련한 기계는 9.2.4.2 에서 규정 하는 기계를 제어할 수 있는 CCS 능력의 상실에 대한 요구사항을 준수하여야 한다. 기계 운영을 중단하지 않으면서 케이블이 없는 조작 제어반을 비활성화하여야 하는 경우, 다른 고정 또는 휴대용 제어반으로 제어를 전환하는 수단을 제공한다(예: 케이블이 없는 조작 제어반에 제공한 다). 9.2.4.7 케이블이 없는 휴대용 조작 제어반에 있는 비상 정지 장치 케이블이 없는 휴대용 조작 제어반에 있는 비상 정지 장치 이외에도 기계의 비상 정지 기능을 시작 하는 수단이 있어야 한다. 사용성을 위해 적절한 설계와 정보를 통해 활성 비상 정지 장치와 비활성 비상 정지 장치를 혼동하 지 않도록 한다. 또한 KS B ISO 13850 을 참조한다. 9.2.4.8 비상 정지 초기화 CCS 의 전력 손실, 비활성화 및 재활성화, 통신 손실 또는 부품 고장 이후에 케이블이 없는 제어를 다시 시작하는 경우에도 비상 정지 조건은 재설정하지 않는다. 케이블이 없는 휴대용 조작 제어반이 개시한 비상 정지 조건의 재설정은 그 이유가 명확해질 경우에 만 실행한다고 사용 지침은 명시한다. 위험 평가에 따라 케이블이 없는 휴대용 조작 제어반에 있는 비상 정지 구동기를 재설정하는 것에 더하여 보조 고정 재설정 장치를 하나 이상 제공하여야 한다. 9.3 보호 연동 장치 9.3.1 연동 안전 장치의 재작동 또는 재복귀 연동 안전 장치의 재작동 또는 재복귀가 위험한 상태를 일으킬 우려가 있는 경우, 기계 기동 또는 작동되어서는 안 된다. 비고 기동 기능(제어 안전 장치)가 있는 연동 안전 장치의 요구사항은 KS B ISO 12100:2010 의 6.3.3.2.5 에 규정되어 있다. 44 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
ae64641d-bd5d-4593-b0dd-0cd7190a978c | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 9.3.2 과주행 방지 과주행으로 인하여 위험이 유발될 수 있는 경우, 미리 설정된 제한 조건을 초과 하는 것을 감지하고 적절한 제어 동작을 개시하는 수단을 제공하여 과주행(예: 속도, 압력, 위치)을 방지하여야 한다. 9.3.3 보조 기능의 작동 보조 기능의 올바른 작동은 적합한 장치(예: 압력 센서)에 의해 확인되어야 한다. 보조 기능(예: 윤활유, 냉각제 공급, 스워프 제거)용 장비 및 전동기가 작동되지 아니함으로써 작업 공정 또는 기계에 손상을 초래하거나 위험 상태를 유발할 가능성이 있는 경우, 적합한 연동 장치가 설치되어야 한다. 9.3.4 여러 작동과 역작동 사이의 연동 장치 동시 작동 시 위험한 상태를 초래할 수 있는(예: 역운동을 야기시키는 것.) 모든 접점, 릴레이 및 다 른 제어 기구는 이상 동작 방지를 위해 상호 연동되어야 한다. 역회전용 접점(예: 전동기 회전 방향을 제어하는 것.)은 스위치 조작 시 회로 단락 사고가 일어나지 않도록 상호 연동되어야 한다. 기계 작동의 연속성과 안전상 기계의 여러 기능이 상호 연계되어 작동되는 경우(계단식 속도 제어 등), 상호 원만한 협조가 되도록 적절한 연동 기능을 구비하여야 한다. 또한 여러 기계가 상호 연계 되어 작업이 이루어지고 한 개 이상의 제어기로 동작하는 경우, 제어기 사이에는 적절한 상호 연동 이 이루어져야 한다. 기계 제동 액추에이터의 고장으로 인해 전원이 연결된 관련 기계의 액추에이터에 제동이 걸려 위험 상태를 초래할 우려가 있는 경우 연동 장치는 해당 액추에이터의 전원이 차단되도록 되어야 한다. 9.3.5 역전류 제동 역전류 제동 방식이 사용되는 전동기에서, 역방향 회전 시 작업 공정이나 기계의 손상 또는 위험을 초래할 우려가 있는 경우, 역회전이 방지되도록 적절한 수단이 강구되어야 한다. 이를 위하여, 시간 기능에 의해서만 작동하는 장비의 사용은 허용되지 않는다. 제어 회로는 예를 들어 수동적인 힘이나 다른 힘을 가함으로써 샤프트가 정지한 후 회전하는 경우 등 모터 샤프트의 회전이 위험한 상황을 초래하지 않도록 구성되어야 한다. 9.3.6 안전 기능 및/또는 보호 조치 중단 안전 기능 및/또는 보호 조치(예: 설정 또는 유지 관리 목적)를 일시 중지해야 하는 경우 제어 또는 작동 모드 선택기는 동시에 다음을 수행해야 한다. 다른 모든 작동 (제어) 모드 비활성화한다. 가동 유지 장치나 위험 요소를 볼 수 있도록 위치한 유사한 제어 장치를 사용하여 동작하는 것만 을 허용한다. 위험이 감소된 조건하에서만(예: 감소한 속도, 감소한 전력/힘, 제한적인 동작 제어 장치를 사용하 는 단계별 동작 등) 위험 요소가 동작하는 것을 허용한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 45 | {}
f192f662-3307-4e44-8d3c-afcf8ab191b9 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 기계의 센서에 대한 자발적이거나 비자발적인 조치를 통하여 위험한 기능을 수행하는 것을 방지 한다. 이런 네 가지 조건을 동시에 충족할 수 없는 경우, 제어나 운영 모드 선택기는 안전한 개입 구역을 보장하도록 설계되고 구성된 다른 보호 조치를 활성화한다. 또한 조작자는 조정 지점에서 작업을 진 행하고 있는 부품의 운영을 제어할 수 있어야 한다. 9.4 결함 시 제어 기능 9.4.1 일반 요구사항 전기 장비의 고장이나 교란으로 인하여 위험한 상태 또는 기계나 공정상 손상을 초래할 우려가 있는 경우, 이러한 고장인 교란의 발생률이 최소화되도록 적절히 조치하여야 한다. 요구되는 수단과 정도 는 각각의 애플리케이션에 관계되는 위험 정도에 따라 개별적으로 또는 복합적으로 적절히 선정되어 야 한다(4.1 참조). 위험을 줄일 수 있는 다음의 조치는 제한 없이 적용되어야 한다. · 전기 회로의 보호 연동 방식 · 입증된 회로 기술 및 부품의 사용(9.4.2.2 참조) · 전체 또는 일부의 이중화(9.4.2.3 참조) 또는 다양화 방식 채택(9.4.2.4 참조) · 기능 시험(9.4.2.5 참조) 실시 전기 제어 시스템에는 기계의 위험 평가로부터 결정된 적합한 성능이 있어야 한다. ISO 62061 및/또는 KS B ISO 13849-1, KS B ISO 13849-2 의 안전 관련 제어 기능 요구사항을 적용해야 한다. 전기 제어 시스템이 수행하는 기능이 안전에 영향을 미치지만 IEC 62061 을 적용하면 SIL 1 에서 요구 하는 것보다 적은 안전 무결성이 요구되는 경우 IEC 60204 의 이 부의 요구사항을 준수하면 다음과 같은 전기 제어 시스템의 적절한 성능을 얻을 수 있다. 예를 들어 배터리 전원으로 메모리 보존이 가능할 경우, 배터리의 고장, 저전압이나 제거로 인한 위 험한 상황을 방지하기 위한 조치가 취해져야 한다. 미인가 또는 우발적인 메모리 수정을 방지하기 위한 조치(예: 키, 접근 코드 또는 도구 요구)가 제공 되어야 한다. 9.4.2 결함 시 위험의 최소화 방법 9.4.2.1 일반사항 결함 발생 시 위험을 최소화하기 위한 조치에는 다음이 포함되지만 이에 국한되지는 않는다. · 입증된 회로 기술 및 구성요소 사용 · 부분적 또는 완전한 이중화 제공 · 다양성 제공 46 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
4111f46d-c7bb-42db-b03e-815d02a3df47 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 · 기능 시험 제공 9.4.2.2 입증된 회로 기술 및 부품의 사용 이 조치는 다음을 제한 없이 적용한다. 작동용 보호 본딩 회로에 제어 회로의 본딩(9.4.3.1.1 및 그림 4 참조) 9.4.3.1.1 에 따른 제어 장치의 연결 전원 차단에 의한 정지 제어되는 장치에서 모든 제어 회로 도체(예: 코일의 양면)의 개폐 능동(또는 직접) 개폐 작동을 하는 개폐 기구의 사용(IEC 60947-5-1 참조) 모니터링: · 기계적으로 연결된 접점 사용(IEC 60947-5-1 참조) · 미러 접점 사용(KS C IEC 60947-4-1 참조) 의도하지 않은 작동을 야기할 수 있는 고장률을 감소시키기 위한 회로 설계 9.4.2.3 부분적 또는 전체적 이중화 채용 부분적 또는 전체적인 이중화는 전기 선로상의 하나의 단순한 고장이 위험한 상태를 일으킬 가능성 을 최소화할 수 있다. 이중화 방법은 정상 작동 중 유효화시킬 수 있거나(즉, 온라인 이중화) 작동 기 능이 고장 난 경우에만 보호 기능이 영향을 받는(즉, 오프라인 이중화) 특수 회로로 설계할 수 있다. 정상 작동 중에 활성화되지 않는 오프라인 이중화의 경우, 필요시 당해 제어 회로 기능을 보증할 수 있는 적절한 수단이 강구되어야 한다. 9.4.2.4 다양성의 활용 다양한 작동 원리를 사용하거나 여러 형태의 장치를 이용한 제어 회로의 사용은 장치의 결함 및/또 는 고장으로 인한 위험 발생률을 줄일 수 있으며, 그 예는 다음과 같다. 상시 개방 또는 상시 폐쇄 접촉의 조합 사용 회로에서의 다양한 형태의 제어 장치 사용 이중화 구성 시 전자 기계식 및 전자식 회로의 조합 전기적 및 비전기적(예: 기계식, 유압식, 기압식) 설비의 조합은 이중화 기능 및 다양화를 제공할 수 있다. 9.4.2.5 기능 시험 기능 시험은 기동 시와 점검 주기에 따라 제어 설비에 의하여 자동으로 수행될 수도 있고, 검사나 시험에 의하여 수동, 또는 수동과 자동의 적절한 조합에 의하여 실시될 수도 있다(17.2 및 18.6 참 조). 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 47 | {}
7c6f167b-87f2-472e-861d-4e98bdfe6fba | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 9.4.3 제어회로 오작동에 대한 보호 9.4.3.1 절연 결함 9.4.3.1.1 일반사항 제어 회로의 절연 결함이 의도하지 않은 시작, 잠재적으로 위험한 동작과 같은 오작동을 유발하거나 기계의 정지를 방지할 수 있는 가능성을 줄이기 위한 조치를 제공해야 한다. 요구사항을 충족하기 위한 조치에는 다음 방법이 포함되지만 이에 국한되지는 않는다. 방법 a) 변압기에 의해 공급되는 접지된 제어 회로 방법 b) 변압기가 공급하는 비접지 제어 회로 방법 c) 변압기가 접지 중앙 탭 권선을 사용하여 공급하는 제어 회로 방법 d) 변압기가 공급하지 않는 제어 회로 9.4.3.1.2 방법 a) - 변압기가 공급하는 접지 제어 회로 공통 도체를 공급점에서 보호 본딩 회로에 연결한다. 전자기 또는 기타 장치(예를 들어 중계기, 지시 등)를 작동하기 위한 모든 접점, 고체 상태 요소 등을 제어 회로 공급의 개폐 도체와 코일이나 장치 의 한 쪽 단자 중 하나 사이에 삽입한다. 코일이나 장치의 다른 단자를 개폐 요소가 없는 제어 회로 의 공통 도체에 직접 연결한다(그림 7 참조). ![image](/image/placeholder) I > 1 u 3 3 2 2 1 개폐 도체 2 공통 도체 3 제어 개폐기 그림 7 - 방법 a) 변압기가 공급하는 접지 제어 회로 비고 DC 제어 회로에 대해서도 방법 a)를 사용할 수 있다. 이 경우, 그림 7 에 있는 변압기를 DC 전원 공급 장치로 대체한다. 예외: 연결부가 매우 짧아(예를 들어, 같은 밀폐함 안에 있어) 접지 고장이 발생할 우려가 없는(예를 들어 과부하 중계기가 접점에 직접 설치된) 경우, 보호 장치의 접점을 공통 도체와 코일 사이에 연결 48 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
32d7961c-c5f8-4ce1-8bf3-069a8e22fd67 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 할 수 있다. 9.4.3.1.3 방법 b) - 변압기가 공급하는 비접지 제어 회로 보호 본딩 회로에 연결되지 아니한 제어 변압기가 공급하는 제어 회로는 다음 중 어느 하나와 같다. 1) 두 도체 모두에서 동작하는 2 극 제어 개폐 장치가 있다. 그림 8 참조. 2) 예를 들어 절연 모니터링 장치와 같이 접지 고장이 발생하는 경우 회로를 자동으로 차단하는 장 치를 제공한다. 그림 9 참조 3) 상기 항목 2 에 따라 차단하면 위험이 증가하는 경우, 예를 들어 첫 번째 접지 고장이 발생하는 동안에도 계속 작동하여야 하는 경우, 기계에서 청각 및 시각적 신호를 시작하는 절연 모니터링 장치를 제공하는 것으로 충분할 수 있다(예: KS C IEC 61557-8 에 따름). 그림 10 참조. 기계 사용 자가 이런 경보에 대응하여 절차를 이행하여야 하는 요구사항을 사용 정보에서 설명한다. ![image](/image/placeholder) / > 3 2 3 2 1 개폐 도체 2 공통 도체 3 제어 개폐기 그림 8 - 방법 b1) 변압기가 공급하는 비접지 제어 회로 비고 1 DC 제어 회로에 대해서도 방법 b1)을 사용할 수 있다. 이 경우, 그림 8 에 있는 변압기를 DC 전력 공급으로 대체한다. 49 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f7b4d113-3fb4-4b75-89e5-145a3a447376 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 ![image](/image/placeholder) / > 1 3 3 R� 2 2 1 개폐 도체 2 공통 도체 3 제어 개폐기 그림 9 - 방법 b2) 변압기가 공급하는 비접지 제어 회로 비고 2 DC 제어 회로에 대해서도 방법 b2)를 사용할 수 있다. 이 경우, 그림 9 에 있는 변압기를 DC 전력 공급으로 대체한다. 비고 3 그림 9 는 절연 모니터링 장치를 보호하기 위하여 측정 회로에 있는 과전류 보호 장치를 보여 주지는 않는다. ![image](/image/placeholder) / > 1 1 3 3 R� 2 2 ¦ 1 ¦ 개폐 도체 ¦ ¦ --- ¦ --- ¦ ¦ 2 ¦ 공통 도체 ¦ ¦ 3 ¦ 제어 개폐기 ¦ 그림 10 - 방법 b3) 변압기가 공급하는 비접지 제어 회로 비고 4 DC 제어 회로에 대해서도 방법 b3)을 사용할 수 있다. 이 경우, 그림 10 에 있는 변압기를 DC 전력 공급으로 대체한다. 변압기와 정류기의 조합을 사용하는 경우, 절연 모니터링 장치 를 정류기 이후에 제어 회로의 DC 부에 있는 보호 본딩 회로에 연결한다. 50 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
79c1bb02-5e5a-4b17-9eb7-1638ac273656 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 비고 5 그림 10 은 절연 모니터링 장치를 보호하기 위하여 측정 회로에 있는 과전류 보호 장치를 보 여주지는 않는다. 9.4.3.1.4 방법 c) - 변압기가 접지 중앙 탭 권선을 사용하여 공급하는 제어 회로 보호 본딩 회로에 연결된 중앙 탭 권선을 사용하는 제어 변압기에서 공급하는 제어 회로에는 두 도 체 모두를 차단하는 과전류 보호 장치가 있다. 제어 개폐기는 두 도체 모두에서 동작하는 2 극 형태이다. ![image](/image/placeholder) / > 3 2 3 2 1 개폐 도체 2 공통 도체 3 제어 개폐기 그림 11 - 방법 c) 변압기가 접지 중앙 탭 권선을 사용하여 공급하는 제어 회로 9.4.3.1.5 방법 d) - 변압기가 공급하지 않는 제어 회로 제어 변압기나 KS C IEC 61558-2-16 에 따라 별도의 권선이 있는 변압기가 장착된 개폐기 모드 전원 장치가 공급하지 않는 제어 회로를 9.1.1 에 따라 최대 1 개의 전동기 기동기 및/또는 최대 2 개의 제어 장치가 있는 기계에 대해서만 허용한다. 공급 시스템의 접지에 따라 발생 가능한 상황은 다음과 같다. 1) 접지 공급 시스템(TN 시스템 또는 TT 시스템)에 직접 연결하고 다음 중 하나에 해당한다. a) 선도체와 중성 도체 사이에서 작동된다. 그림 12 참조 b) 두 선도체 사이에서 작동된다. 그림 13 참조 2) 접지하지 아니하거나 높은 임피던스를 통하여 접지하는 공급 시스템에 직접 연결하고(IT 시스템) 다음과 같다. a) 선도체와 중성 도체 사이에서 작동된다. 그림 14 참조 b) 두 선도체 사이에서 작동된다. 그림 15 참조 51 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
8f4fd3a9-27a6-4bd7-ad10-7828ce5f980e | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 방법 d1b)는 다중극 제어 개폐기를 요구한다. 다중극 제어 개폐기는 제어 회로에서 접지 고장이 발 생하는 경우 의도하지 아니하게 작동하는 것을 피하기 위하여 모든 활선 도체를 개폐한다. 방법 d2)는 접지 고장이 발생하는 경우, 회로를 자동으로 차단하는 장치를 제공할 것을 요구한다. ![image](/image/placeholder) L2 M L3 제어 스위치 그림 12 - 방법 d1a) 접지된 공급 시스템의 위상과 중성선 사이에 변압기가 연결되지 않은 제어 회로 비고 1 그림 12 는 공급 시스템이 TN 시스템 인 경우를 보여준다. 제어 회로는 TT 시스템의 경우 동 일하다. 비고 2 그림 12 는 전원 회로 및 제어 회로에 대한 보호 장치를 보여주지 않으며 이에 대한 조항은 6.3 및 7.2 에 명시되어 있다. ![image](/image/placeholder) L2 M L3 제어 스위치 그림 13 - 방법 d1b) 접지된 공급 시스템의 두 위상 사이에 연결된 변압기가 없는 제어 회로 비고 3 그림 13 은 공급 시스템이 TN 시스템인 경우를 보여준다. 제어 회로는 TT 시스템의 경우 동 일하다. 비고 4 그림 13 은 전원 회로 및 제어 회로에 필요한 보호 장치를 보여주지 않으며, 이에 대한 조항 은 6.3 및 7.2 에 명시되어 있다. 52 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f2384d59-368a-4e21-b422-b91e8ef76f6b | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 ![image](/image/placeholder) L2 M L3 N 제어 스위치 R = 그림 14 - 방법 d2a) 비접지 공급 시스템의 상과 중성 사이에 변압기가 연결되지 않은 제어 회로 비고 5 그림 14 는 전원 회로 및 제어 회로에 필요한 보호 장치를 보여주지 않는다. 규정은 6.3 및 7.2 에 명시되어 있다. ![image](/image/placeholder) L2 M L3 제어 스위치 R� 그림 15 - 방법 d2b) 비접지 공급 시스템의 두 위상 사이에 연결된 변압기가 없는 제어 회로 비고 6 그림 15 는 전력 회로 및 제어 회로에 필요한 보호 장치를 보여주지 않으며, 이에 대한 조항 은 6.3 및 7.2 에 명시되어 있다. 9.4.3.2 정전 7.5 를 참조한다. 제어 시스템에 기억 장치가 사용되는 경우, 정전 사고 시의 적합한 기능은 위험 상태를 초래할 수 있는 기억 상실을 방지하기 위한 조치가 보증되어야 한다(예: 비휘발성 기억 장치의 사용). 9.4.3.3 선로 단선 53 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
48b55451-f3fb-4105-b623-690ba069455c | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 습동 접점의 사용으로 제어 회로가 단선됨으로써 위험 상태가 초래될 수 있는 경우, 이중 습동 접점 방식의 채택 등 적절한 조치를 취해야 한다. 10 조작자 인터페이스 및 기계 장착 제어 장치 10.1 일반사항 10.1.1 일반 요구사항 조작자 인터페이스를 위한 제어 장치들은 가능한 한 KS C IEC 61310 시리즈에 따라 선정, 설치 및 식별 또는 코드화되어야 한다. 우발적인 조작 가능성은, 예를 들어 장치의 위치 선정, 적합한 설계, 추가 보호 초지에 의해 최소화 되어야 한다. 특히 터치스크린, 키패드 및 키보드와 같이 위험한 기계 조작과 센서(예: 위치 센서)를 제어하기 위한 조작 입력 장치의 선정, 배열, 프로그래밍 및 사용을 고려해야 한다. 더 자세한 사항 은 KS C IEC 60447 을 참조한다. 작업자 인터페이스 장치의 위치에서 인체 공학적 원칙을 고려해야 한다. 10.1.2 위치 및 설치 기계에 부착된 제어 장치는 가능한 한 다음 사항을 만족해야 한다. · 작동 및 유지 보수를 위해 쉽게 접근 가능할 것. · 재료의 취급 등과 같은 행위로부터 손상될 위험이 최소화되도록 부착될 것. 수동 제어 장치의 액추에이터는 다음과 같이 선정, 설치되어야 한다. · 작동 높이에서 최소 0.6m 이상의 높이이며 조작자의 정상 작업 위치에서 쉽게 닿을 수 있을 것. · 조작자가 취급 시 위험하지 않은 곳에 위치할 것. 발 조작 제어 기기의 액추에이터는 다음과 같이 선정, 설치되어야 한다. · 조작자의 정상 작업 위치에서 쉽게 닿을 수 있는 범위 내에 위치할 것. · 조작자가 취급 시 위험하지 않은 곳에 위치할 것. 10.1.3 보호 기타 적합한 조치와 함께 보호 등급(KS C IEC 60529 에 따른 IP 등급)은 다음에 대하여 보호할 수 있 어야 한다. · 물리적 환경 또는 기계에서 사용되는 액체, 증기 또는 가스에 의한 영향 · 오염 물질의 유입(예: 절삭 부스러기, 분진, 입자) 추가로, 조작자 인터페이스 제어 장치는 IPXXD 의 활선부 접촉에 대한 최소 보호 등급(KS C IEC 60529 참조)을 가져야 한다. 54 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
2a949230-792a-45a9-8711-4d3e4966edcb | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 10.1.4 위치 감지기 위치 감지기(예: 위치 스위치, 근접 스위치)는 과주행으로 손상될 우려가 없도록 설치되어야 한다. 안전과 관련된 제어 기능(예: 기계의 안전한 상태를 유지하거나 기계에서 발생하는 위험한 상황을 방 지하기 위해)에 사용되는 위치 감지기는 능동(직접) 개방 작동 방식(IEC 60947-5-1 참조), 또는 이와 유사한 신뢰성(9.4.2 참조)이 있어야 한다. 10.1.5 휴대형 및 펜던트 제어반 휴대형 및 펜던트(매달기형) 제어반과 그 제어 장치는 부주의 한 작동, 충격 및 진동(예: 제어반이 장 애물로 인해 낙하 또는 충격을 받을 때)으로 인한 동작의 우려가 최소화되도록 선정 및 배치되어야 한다(4.4.8 참조). 10.2 액추에이터 10.2.1 색상 액추에이터(3.1.1 참조)는 다음과 같이 색상 부호화하여야 한다. 기동/투입 액추에이터의 색상은 흰색을 기본으로 하되 흰색, 회색, 검은색 또는 초록색을 사용할 수 있다. 빨간색은 사용해서는 안 된다. 빨간색은 비상 정지 및 비상 전원 차단 액추에이터에만 사용되어야 한다(비상시 사용이 예상되는 공 급 차단 장치 포함). 액추에이터 바로 주변에 배경이 있으면 배경은 노란색으로 표시된다. 빨간색 액 추에이터와 노란색 배경의 조합은 비상 작동 장치에만 사용해야 한다. 정지/차단 액추에이터의 색상은 검은색을 기본으로 하되, 검은색, 회색 또는 흰색을 사용할 수 있다. 초록색은 사용해서는 안 된다. 빨간색 또한 허용되나, 비상 조작 장치에 근접한 곳에서 사용해서는 안 된다. 흰색, 회색 또는 검은색은 교대로 기동/투입 및 정지/차단되는 액추에이터용 색상으로 사용할 수 있 다. 빨간색, 노란색 또는 초록색은 사용해서는 안 된다. 흰색, 회색 또는 검은색은 누르고 있는 동안만 작동하고, 누름을 멈추면 작동을 멈추는 형식(예: hold- to-run)의 액추에이터에는 사용할 수 있으나 빨간색, 노란색 또는 초록색은 사용해서는 안 된다. 복귀 기능 액추에이터는 파란색, 흰색, 회색 또는 검은색이어야 한다. 이것이 정지/차단 액추에이터의 역할을 하는 경우, 검은색을 기본으로 하되 흰색, 회색 또는 검은색을 사용할 수 있다. 초록색은 사 용해서는 안 된다. 노란색은 비정상적인 조건에서 사용하기 위해 보류되어 있다(예: 프로세스의 비정상적인 조건 발생 시 또는 자동 사이클 중단 시). 흰색, 회색 또는 검은색과 동일한 색상이 여러 기능용으로 사용되는 경우(예: 기동/투입 및 정지/차단 액추에이터에 흰색 사용), 부호화의 부수적 수단(예: 모양, 위치, 구조)이 액추에이터의 식별에 사용되 어야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 55 | {}
d9964063-e3da-4c86-bb18-925a44f0d2d4 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 10.2.2 표시 16.3 에서 규정하는 기능 식별에 추가하여, 특정 액추에이터 근처 또는 가급적이면 바로 위에 표 2 또는 표 3 의 표시를 하는 것이 바람직하다. 표 2 - 액추에이터(전원)의 기호 ¦ 전원 ¦ 전원 ¦ 전원 ¦ 전원 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 투입 ¦ 차단 ¦ 기동/정지 (투입, 차단 누름버튼) ¦ 기동 (홀드투런) ¦ ¦ IEC 60417-5007 (2002-10) ¦ IEC 60417-5008 (2002-10) ¦ IEC 60417-5010 (2002-10) ¦ IEC 60417-5011 (2002-10) ¦ ¦ 「 ¦ □ ¦ □ □ ¦ ¦ 표 3 - 액추에이터(기계 동작)의 기호 ¦ 기계 동작 ¦ 기계 동작 ¦ 기계 동작 ¦ 기계 동작 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기동 ¦ 정지 ¦ 홀드투런 ¦ 비상정지 ¦ ¦ IEC 60417-5104 (2006-08) ¦ IEC 60417-5110A (2004-06) ¦ IEC 60417-5011 (2002-10) ¦ IEC 60417-5638 (2002-10) ¦ ¦ ◇ ¦ 「 ¦ 「 ¦ ! ¦ 10.3 표시등 및 디스플레이 10.3.1 일반사항 표시등 및 디스플레이는 다음과 같은 정보 형태를 주기 위한 것이다. 표시: 작업자의 주의 를 끌거나 지정된 절차를 준수하여야 하는 것을 나타내고자 할 경우, 빨간색, 노란색, 파란색 및 초록색으로 표시할 것. 점멸 표시등과 디스플레이에 관해서는 10.3.3 참조 확인: 명령 상태를 확인하거나 변경 또는 전환 시간 종료의 확인이 필요할 경우, 파란색과 흰색을 사용할 것(필요시 초록색도 사용 가능함). 표시등 및 디스플레이는 작업자의 정상 위치로부터 시각적으로 확인 가능한 방식으로 선정 및 설치 되어야 한다(KS C IEC 61310-1 참조). 56 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c2cde4f5-0eae-4394-b9fb-e4ba01ec821b | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 임박한 위험 상황을 경고하는 시각 또는 청각 장치에 사용되는 회로에는 이러한 장치의 작동 여부를 확인하는 시설이 장착되어야 한다. 10.3.2 색상 표시등은 표 4 에 따라 기계의 조건(상태)에 관하여 색상 부호화하여야 한다. 표 4 - 기계의 상태와 관련된 표시등 색상 및 의미 ¦ 색상 ¦ 의미 ¦ 설명 ¦ 조작자의 행동 방침 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 빨간색 ¦ 비상 ¦ 위험한 상태 ¦ 위험 상태에 대응하여 즉시행동(예: 기계 의 비상 상태를 경고, 기계 근처에 가지 않도록 제재, 기계 전원의 스위치 차단) ¦ ¦ 노란색 ¦ 비정상 ¦ 비정상 상태 긴급 상태 ¦ 감시 및 조치(예: 기능 재설정 등) ¦ ¦ 파란색 ¦ 의무 ¦ 조작자의 조치를 요하는 상태 표시 ¦ 의무 조치 ¦ ¦ 초록색 ¦ 정 상 ¦ 정상 상태 ¦ 선택사항 ¦ ¦ 흰색 ¦ 중성 ¦ 기타 상태(빨간색, 노란색, 초록색, 파란색 적용 모호 시 사용) ¦ 감시 ¦ 기계의 표시 타워 색은 위에서 아래로 다음과 같은 순서가 되어야 한다: 빨간색, 노란색, 파란색, 초록색, 흰색 10.3.3 점멸등 및 디스플레이 다음과 같은 목적에 따라 그 이상의 식별이나 정보, 특히 추가적인 강조가 필요한 경우에는 점멸등 및 디스플레이를 설치할 수 있다. 주의 를 환기시킬 필요가 있을 경우 즉각적인 조치가 필요할 경우 명령과 실제 상태의 불일치를 나타낼 경우 처리 과정 중 변경을 나타낼 경우(전이 과정 중 점멸) 우선 순위가 높은 내용의 전달 시에는 점멸 속도가 빠른 점멸등을 사용하도록 한다(점멸률 및 맥동/정 지율은 KS C IEC 60073 참조). 점멸등 또는 디스플레이가 더 높은 우선순위의 정보를 전달하기 위해 사용될 경우, 추가적인 청각 경고 장치도 고려되어야 한다. 10.4 조광 누름 버튼 조광 누름 버튼 액추에이터는 10.2.1 에 따라 색상 부호화하여야 한다. 적절한 색상을 정하기 어려운 경우에는 흰색을 사용해야 한다. 활성 비상 정지 액추에이터용 색상은 조광 상태와 는 무관하게 빨간색을 유지해야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 57 | {}
f8f59706-e9a2-4089-b476-f60d05fcd44b | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 10.5 회전식 제어 장치 전위차계 또는 선택 스위치와 같이 회전 부분을 가진 장치는 정지 부분이 회전하지 않도록 설치되어 야 한다. 마찰로만은 충분하지 않다. 10.6 기동 장치 기동 기능 또는 기계 요소의 움직임(예: 슬라이드, 스핀들, 캐리어)을 작동시키기 위한 액추에이터는 오작동을 최소화하도록 제조 및 설치되어야 한다. 10.7 비상 정지 장치 10.7.1 설치 위치 비상 정지 장치는 바로 접근이 용이한 장소에 설치되어야 한다. 비상 정지 장치는 비상 정지가 필요한 장소에 제공되어야 한다. 예를 들어, 플러그를 제거하거나 제어반 작동 무효화에 의해 야기된 비상 정지 기기의 활성/비활성 사이에 혼란이 발생할 수 있는 경우가 있다. 그런 경우, 혼란을 최소화하는 장치(예: 디자인과 사용 정보)가 제공되어야 한다. 10.7.2 형태 비상 정지 장치의 형태는 다음과 같다. 하지만 여기에 국한되지는 않는다. · 손바닥 또는 주먹으로 작동하는 누름 버튼 장치(예: 버섯 머리 유형) · 로프(pull-cord) 작동 스위치 · 기계 방호물(덮개)이 없는 페달형 스위치 장치는 IEC 60947-5-5 에 따라야 한다. 10.7.3 비상 정지에 영향을 주는 전원 차단 장치의 조작 정지 범주 0 이 적합한 경우, 전원 차단 장치가 다음 사항을 만족할 경우, 비상 정지 기능을 제공한다. · 조작자가 쉽게 접근할 수 있는 경우 · 5.3.2 의 a), b), c) 또는 d)에 규정된 형태인 경우 비상 사용을 위한 경우에 전원 차단 장치는 10.2.1 의 색상 요구사항에 적합하여야 한다. 10.8 비상 전원 차단용 장치 10.8.1 설치 위치 비상 전원 차단 장치는 주어진 기능에 적합한 장소에 설치하여야 한다. 일반적으로, 이러한 장치는 조작 제어반으로부터 분리된 곳에 설치한다. 비상 정지 장치와 비상 전원 차단용 장치 사이에 혼란 이 있을 수 있는 경우에는, 혼란을 최소화할 수 있는 수단을 제공해야 한다. 58 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
e1031ef6-b016-46c6-84e6-77ad04ddb475 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 비고 이는 예를 들어 비상 스위치에 유리 (깨지는) 외함을 제공하여 달성될 수 있다. 10.8.2 비상 전원 차단용 장치의 형식 비상 전원 차단을 위한 장치의 형태는 다음을 포함한다. · 손바닥으로 작동시키는 누름 버튼 또는 버섯 머리 모양의 액추에이터 · 로프 (pull-cord) 작동 스위치 장치는 능동(직접) 개방 작동형이어야 한다(IEC 60947-5-1:2003 과 IEC 60947-5-1:2003/AMD1:2009 의 부속서 K 참조). 10.8.3 비상 전원 차단에 영향을 주는 전원 차단 장치의 현장 조작 전원 차단 장치가 비상 전원 차단용으로 현장에서 조작되는 경우, 쉽게 접근할 수 있어야 하며 10.2.1 의 색상 요구사항을 만족하여야 한다. 10.9 허용 제어 장치 허용 제어 기능은 9.2.3.9 를 참조한다. 허용 제어 장치는 기능 불가 가능성을 최소화하도록 선택 및 배치되어야 한다. 다음과 같은 기능이 있는 허용 제어 장치가 선택되어야 한다. 인체 공학적 원리에 따라 설계 2 위치 형식 · 위치 1: 스위치의 off 기능(액추에이터 작동하지 않음.) · 위치 2: 허용 기능(액추에이터 작동) 3 위치 형식 · 위치 1: 스위치의 off 기능(액추에이터 작동하지 않음.) · 위치 2: 허용 기능(액추에이터가 중간 위치에서 작동) · 위치 3: off 기능(액추에이터가 중간 위치를 지나 작동) · 위치 3 에서 2 로 복귀할 때, 허용 기능은 작동하지 않음. 비고 KS C IEC 60947-5-8 은 3 상 허용 스위치에 대한 요구사항을 지정한다. 11 제어 장치: 위치, 설치 및 외함 11.1 일반 요구사항 모든 제어 장치의 위치 및 설치 시에는 다음 사항을 고려하여야 한다. 접근 및 유지 보수가 용이할 것. 기계의 의도되지 않은 작동 조건 또는 외부 영향에 보호될 수 있을 것. 기계의 작동 및 유지 보수에 용이하도록 할 것. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 59 | {}
9c82153f-fb48-47a7-8983-ea3dd23d0441 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 11.2 위치와 설치 11.2.1 접근 및 유지 보수 제어 장치의 모든 부품은 그 부품 또는 배선을 이동시키지 않고 식별할 수 있도록 설치 및 배치되어 야 한다. 정상 작동 여부의 확인이나 부품의 교체가 필요한 경우, 기계의 다른 장비나 부품 등을 분 해하지 않고도 작업이 가능하여야 한다(문을 열거나 덮개를 해제하는 것은 제외). 제어 장치와 직접 관련없는 단자들도 이 요구사항에 따라야 한다. 모든 제어 장치는 조작 및 보수할 수 있도록 부착되어야 한다. 장치를 조절, 유지, 제거하는 데 특수 한 도구가 필요한 경우에는 도구가 공급되어야 한다. 정기 보수 또는 조정을 위해 접근이 필요한 경 우, 관련 장치들은 작업장 바닥에서 0.4 m ~ 2.0 m 사이의 높이에 위치해야 하고, 단자는 최소한 0.2 m 이상 위에 도체와 케이블이 쉽게 접속할 수 있는 곳에 위치하는 것이 바람직하다. 작동, 표시, 측정 및 냉각용 장치 이외에는 외함의 문, 탈착 가능한 덮개 등에 장착되어서는 안 된다. 제어 장치가 플러그를 통해 접속되는 경우, 형태(구조), 표시, 회로 구성 등의 조합 또는 단독 등을 명확히 하여야 한다(13.4.5 참조). 정상 작동 중 조작되는 플러그 장치는 이 장치에 의하여 기계 장애가 발생할 수 있다면 중간 교환이 불가능한 구조로 하여야 한다. 정상 작동 중 조작되는 플러그/소켓의 조합은 접근이 용이하도록 배치, 부착되어야 한다. 시험설비 연결에 대한 시험점은 다음과 같아야 한다. 접근이 방해되지 않도록 부착 제공된 기술 자료에 따라 명확히 표시 적절한 절연 조치 시험 장비 또는 수단의 접속에 필요한 충분한 공간 확보 11.2.2 물리적 분리 및 그룹화 전기 장비와 직접적으로 관련되지 않는 비전기 부품 및 장치는 제어 장치를 내장하고 있는 외함 내 에 위치해서는 안 된다. 솔레노이드 밸브와 같은 장치는 다른 전기 장비와 분리시키는 것이 바람직 하다(예: 격리된 구획 장소). 같은 위치에 설치되고 전원 회로 또는 전원과 제어 회로 모두에 연결되는 제어 장치는 제어 회로만 연결된 제어 장치들로부터 구분되어 그룹화하여야 한다. 단자는 다음과 같은 단위로 그룹화하여, 분리되어야 한다. 전력 선로 기기의 제어 회로 외부 전원에서 공급되는 기타 제어 회로(예: 연동용) 각 그룹이 쉽게 구별할 수 있다면(예: 표시, 다른 크기의 사용, 배리어 또는 색상 사용) 그룹을 인접 60 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
de90c301-64ec-490e-94ae-faad99080d7c | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 하게 설치할 수 있다. 장치의 위치를 정할 때(상호 연결 포함), 유지 보수, 물리적 환경의 외부 영향 또는 조건을 고려하여 공급자가 지정한 간격 및 연면거리를 유지하여야 한다. 11.2.3 발열 영향 전기 장비 인클로저 내부의 온도 상승은 부품 제조업체가 지정한 주변 온도를 초과 하지 않아야 한다. 비고 1 IEC TR 60890 은 인클로저 내부의 온도 상승 계산에 사용할 수 있다. 열을 발생하는 부품(예: 내부 전열기, 전력 저항)들은 주변 각 부품의 온도가 허용 제한값 이내로 유 지되도록 배치되어야 한다. 비고 2 열 응력에 견디는 절연 재료 선택에 대한 정보는 IEC 60216 및 KS C IEC 60085 에 나와 있다. 11.3 보호 등급 외부의 고형물과 액체의 침투에 대한 제어 장치의 보호는 기계가 작동하기 위한 경우(즉, 위치 및 물 리적 환경 조건)에 외부 영향을 충분히 고려하여야 하며, 분진, 냉각제, 윤활유 절삭 찌꺼기에 대하여 충분히 견딜 수 있어야 한다. 비고 1 물의 침입에 대한 보호 등급은 KS C IEC 60529 에 포함되어 있다. 추가 보호 조치는 기타 액 체에 대하여 필요할 수 있다. 제어 장치 외함의 보호 등급은 최소한 IP22 이어야 한다(KS C IEC 60529 참조). 예외: a) 전기 취급 지역이 고형물 및 액체에 대하여 적합한 보호 등급을 제공하는 경우 b) 컬렉터 선 또는 컬렉터 봉 설비에서 이동 가능한 컬렉터를 사용하는 경우 및 12.7.1 의 조치를 적 용하는 경우 비고 2 외함에 의해 제공되는 전형적인 보호 등급의 적용한 예는 다음과 같다. 전동기의 기동 저항기 및 기타 대형 장비만을 포함한 환기되는 외함: IP10 기타 장비를 포함한 환기되는 외함: IP32 일반 산업에 사용되는 외함: IP32, IP43 및 IP54 저압 물 분사기(호스)로 청소하는 지역에서 사용하는 외함: IP55 미세한 먼지에 대하여 보호되는 외함: IP65 슬립링을 포함한 외함: IP2X 설치 조건에 관련되는 경우, 다른 보호 등급이 적합할 수 있다. 11.4 외함, 문 및 개구부 외함은 정상 상태에서 습기뿐만 아니라 열적, 전기적, 기계적 응력에 견딜 수 있는 재료를 사용하여 제조하여야 한다. 61 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
1674290f-901d-4f2a-af7c-0da7cea4a025 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 문과 덮개를 조이는 장치는 정체형으로 하고, 창의 외함 재질은 예상되는 기계 응력과 화학 작용에 견딜 수 있는 것이어야 한다. 외함의 문은 수직형 힌지를 사용하여 가급적 들어올림에 의한 열림 방식으로 하고, 적어도 95°의 각 도로 열리고 폭은 0.9m 이내인 것이 바람직하다. 문, 덮개, 외함의 개스킷 또는 연결 부위는 기기에 사용되는 유해한 액체, 증기, 가스에 의한 화학 작 용을 견디어야 한다. 작동이나 보수를 위해 열거나 분리해야 하는 문의 폐쇄, 뚜껑, 덮개의 보호 등 급을 유지하기 위한 방법은 다음과 같다. · 문/덮개 또는 외함에 확실하게 부착함. · 문이나 덮개의 제거 또는 교체로 인해 보호 등급의 손상이나 저하되지 않음. 기계의 일부, 바닥 또는 기초 쪽으로 향한 모든 외함의 개구부는 장비 보호를 위하여 명시된 제조 당시의 보호 등급 수준을 유지하여야 한다. 케이블 인입용 개구부는 그 위치에서 쉽게 재개봉할 수 있도록 하여야 하고, 기계 외함의 바닥 부분에 적절한 개구부를 설치하여 응축된 습기를 배출시킬 수 있어야 한다. 전기 장비가 있는 외함과 냉각제, 윤활용이나 수압용 액체, 기름 등의 액체나 먼지가 유입될 수 있는 곳에는 개구부가 없어야 한다. 다만, 기름 속에서 작동하도록 특별히 설계된 전기 장비(전자 클러치) 나 냉각제가 쓰이는 전기 장비는 예외로 한다. 외함 부착을 위한 구멍이 있을 경우, 부착 후 구멍으로 인하여 규정된 외함 보호 등급이 저하되지 않도록 하여야 한다. 기계는 정상 작동 또는 비정상 작동 상태에서 외함 표면이 화재 위험이나 해를 줄 수 있는 온도까지 상승할 수 있으므로 다음의 조치를 하여야 한다. 화재 발생이나 해로운 영향 없이 상승 온도에 견딜 수 있는 외함 내에 위치하도록 한다. 안전하게 열을 확산시키기 위해 인근 장비로부터 충분히 이격시켜 설치해야 한다(11.2.3 또한 참조). 화재나 해로운 영향 없이 장비의 열방사에 견딜 수 있는 재질에 의해 칸막이를 설치해야 한다. 비고 16.2.2 에 따른 경고 라벨이 필요할 수도 있다. 11.5 전기 설비에의 접근 전기 취급 지역으로의 통로 및 접근용 문은 다음과 같아야 한다. 적어도 폭 0.7 m 및 높이 2.0m 밖으로 개방 열쇠 또는 도구의 사용 없이 내부로부터 개구부로 향하는 수단(예: 패닉 볼트) 보유 비고 추가 정보는 IEC 60364-7-729 에 나와 있다. 62 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c27f9370-6c1d-45c7-8090-91b405b44d8b | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 12 도체 및 케이블 12.1 일반 요구사항 도체 및 케이블은 주어진 운영 조건(전압, 전류, 감전 보호, 케이블군 등)과 외부 영향[주위 공기 온 도, 물 또는 부식 물질의 존재, 기계 응력(설치 중의 응력 포함), 화재 위험]에 적합하게 선정되어야 한다. 이들 요구사항은 관련 IEC 표준(예:IEC61800 시리즈)에 따라 제조되고 시험된 부품, 부속품 및 장비 의 배선에는 적용하지 않는다. 12.2 도체 도체는 구리를 사용하여야 하고, 알루미늄이 사용될 경우 단면적은 16 mm2 이상이어야 한다. 적절한 기계적 강도를 확보하기 위한 도체의 단면적은 표 5 에서 나타난 값보다 작아서는 안 된다. 그러나 필요한 경우, 표 5 보다 단면적이 작은 도체라도 다른 수단에 의해 충분한 기계적 강도가 유 지되고 적절한 기능이 손상되지 않는 장비에서는 사용할 수 있다. 비고 도체 분류는 표 D.4 를 참조한다. 표 5 - 구리 도체의 최소 단면적 ¦ ¦ ¦ 도체 및 케이블의 종류 ¦ 도체 및 케이블의 종류 ¦ 도체 및 케이블의 종류 ¦ 도체 및 케이블의 종류 ¦ 도체 및 케이블의 종류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 위치 ¦ 적용 ¦ 단심 ¦ 단심 ¦ 다심 ¦ 다심 ¦ 다심 ¦ ¦ 위치 ¦ 적용 ¦ 유연 5 등급 또는 6 등급 ¦ 솔리드(1 등 급) 또는 스트랜드 (2 등급) ¦ 2 심 차폐 ¦ 2 심 비차폐 ¦ 3 심 이상의 차폐 또는 비차폐 ¦ ¦ 외함 외부 ¦ 비유연 전력 배선 ¦ 1.0 ¦ 1.5 ¦ 0.75 ¦ 0.75 ¦ 0.75 ¦ ¦ 외함 외부 ¦ 빈번하게 이동하는 기계 접속 ¦ 1.0 ¦ - ¦ 0.75 ¦ 0.75 ¦ 0.75 ¦ ¦ 외함 외부 ¦ 제어 회로에 접속 ¦ 1.0 ¦ 1.0 ¦ 0.2 ¦ 0.5 ¦ 0.2 ¦ ¦ 외함 외부 ¦ 데이터 통신 배선 ¦ - ¦ - ¦ - ¦ - ¦ 0.08 ¦ ¦ 외함 내부 a ¦ 비유연 전력 배선 ¦ 0.75 ¦ 0.75 ¦ 0.75 ¦ 0.75 ¦ 0.75 ¦ ¦ 외함 내부 a ¦ 제어 회로에 접속 ¦ 0.2 ¦ 0.2 ¦ 0.2 ¦ 0.2 ¦ 0.2 ¦ ¦ 외함 내부 a ¦ 데이터 통신 배선 ¦ - ¦ - ¦ - ¦ - ¦ 0.08 ¦ ¦ 비고 모든 단면적은 제곱밀리미터(mm2)이다. a 개별 표준의 특수 표준 제외, 12.1 참조 ¦ 비고 모든 단면적은 제곱밀리미터(mm2)이다. a 개별 표준의 특수 표준 제외, 12.1 참조 ¦ 비고 모든 단면적은 제곱밀리미터(mm2)이다. a 개별 표준의 특수 표준 제외, 12.1 참조 ¦ 비고 모든 단면적은 제곱밀리미터(mm2)이다. a 개별 표준의 특수 표준 제외, 12.1 참조 ¦ 비고 모든 단면적은 제곱밀리미터(mm2)이다. a 개별 표준의 특수 표준 제외, 12.1 참조 ¦ 비고 모든 단면적은 제곱밀리미터(mm2)이다. a 개별 표준의 특수 표준 제외, 12.1 참조 ¦ 비고 모든 단면적은 제곱밀리미터(mm2)이다. a 개별 표준의 특수 표준 제외, 12.1 참조 ¦ 1 등급 및 2 등급 도체는 주로 손상을 유발할 수 있는 진동이 고려되지 않는 개소로서 고정되고 움직 임이 없는 요소들 사이에 사용하기 위한 것이다. 자주 이동(예를 들어, 한 시간 기계 조작당 1 회 이동)하는 모든 도체는 5 등급 및 6 등급의 유연성 스 트랜딩이어야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 63 | {}
06226657-0abf-4f46-bffd-54913b8e5fd7 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 12.3 절연 도체 및 케이블의 절연이 화재의 확산 또는 유독성 또는 부식성 가스의 방출로 인한 위험을 초래할 수 있는 경우, 케이블 공급자의 지침을 구해야 한다. 안전 관련 기능을 보유한 선로의 유지를 위해 특별한 주의 를 주는 것이 중요하다. 사용된 케이블 및 도체의 절연은 시험 전압에 적합해야 한다. 교류 50 V 또는 직류 120 V 이상의 케이블에 대하여 5 분 동안 최소 2 000 V 의 교류 전압으로 요 구된 시험 전압에 적합하여야 한다. PELV 회로에 대하여 5 분 동안 최소 500 V AC 시험 전압에 적합하여야 한다(IEC 60364-4-41 의 클 래스 III 장비 참조). 절연체의 기계적 강도와 두께는 사용이나 포설 시, 특히 덕트 내로 케이블 포설 시에 절연이 손상되 지 않을 정도이어야 한다. 12.4 정상 작동에서의 허용 전류 허용 전류 용량은 여러 요인에 따라 달라진다. 예를 들어 절연 재료, 케이블의 도체 수, 설계(외장), 설치 방법 및 그룹화와 주위 공기 온도와 같은 여러 요인에 따라 달라진다. 비고 1 자세한 정보와 지침은 IEC 60364-5-52 나 제조자 제공 표준을 참조한다. 안정 상태 조건하에서 외함과 장비 개개 항목 사이의 PVC 절연 도체의 허용 전류는 표 6 과 같다. 비고 2 정확한 케이블 지름이 듀티 사이클 주기 및 케이블의 열 상수(예를 들어 높은 비활성 부하, 간헐적인 사용 방지를 위한 기동)에 따라 달라지는 특수한 적용에 관해서는 케이블 제조자가 정보를 제공할 수 있다. 64 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
e3b40ce3-7ee3-4771-a638-36992f1e79aa | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 표 6 - 다양한 절연 방법에 따른 주위 온도 40°C 의 정상 상태 조건하에서 PVC 절연 도체 또는 케이블의 허용 전류(Iz) ¦ ¦ 설치 방법(D.2.2 참조) ¦ 설치 방법(D.2.2 참조) ¦ 설치 방법(D.2.2 참조) ¦ 설치 방법(D.2.2 참조) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ B1 ¦ B2 ¦ C ¦ E ¦ ¦ ¦ 단면적 mm2 ¦ 허용 전류 용량(Iz) A ¦ 허용 전류 용량(Iz) A ¦ 허용 전류 용량(Iz) A ¦ 허용 전류 용량(Iz) A ¦ ¦ 0.75 ¦ 8.6 ¦ 8.5 ¦ 9.8 ¦ 10.4 ¦ ¦ 1.0 ¦ 10.3 ¦ 10.1 ¦ 11.7 ¦ 12.4 ¦ ¦ 1.5 ¦ 13.5 ¦ 13.1 ¦ 15.2 ¦ 16.1 ¦ ¦ 2.5 ¦ 18.3 ¦ 17.4 ¦ 21 ¦ 22 ¦ ¦ 4 ¦ 24 ¦ 23 ¦ 28 ¦ 30 ¦ ¦ 6 ¦ 31 ¦ 30 ¦ 36 ¦ 37 ¦ ¦ 10 ¦ 44 ¦ 40 ¦ 50 ¦ 52 ¦ ¦ 16 ¦ 59 ¦ 54 ¦ 66 ¦ 70 ¦ ¦ 25 ¦ 77 ¦ 70 ¦ 84 ¦ 88 ¦ ¦ 35 ¦ 96 ¦ 86 ¦ 104 ¦ 110 ¦ ¦ 50 ¦ 117 ¦ 103 ¦ 125 ¦ 133 ¦ ¦ 70 ¦ 149 ¦ 130 ¦ 160 ¦ 171 ¦ ¦ 95 ¦ 180 ¦ 156 ¦ 194 ¦ 207 ¦ ¦ 120 ¦ 208 ¦ 179 ¦ 225 ¦ 240 ¦ 제어 회로 쌍 ¦ 0.20 ¦ 4.5 ¦ 4.3 ¦ 4.4 ¦ 4.4 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 0.5 ¦ 7.9 ¦ 7.5 ¦ 7.5 ¦ 7.8 ¦ ¦ 0.75 ¦ 9.5 ¦ 9.0 ¦ 9.5 ¦ 10 ¦ ¦ 비고 1 표 6 의 허용 전류 값은 다음을 기준으로 한다. 단면적이 0.75 mm2 이상인 대칭 3 상 회로 단면적이 0.2 mm2 ~ 0.72 mm2 인 하나의 제어 ¦ ¦ --- ¦ ¦ 회로 쌍 부하가 더 많은 케이블/쌍이 설치될 경우, 표 6 의 값에 대한 경감 계수는 표 D.2 또는 표 D.3 에서 찾을 수 있다. 비고 2 주위 온도 40°C 기준, 그 이하일 경우, 허용 전류 용량에 대한 보정 계수는 표 D.1 에 나와 있다. 비고 3 이들의 값은 드럼에 감긴 유연 케이블에는 적용되지 않는다(12.6.3 참조). 비고 4 기타 케이블의 허용 전류 용량은 IEC 60364-5-52 참조 ¦ 12.5 도체 및 케이블의 전압 강하 전원 회로 케이블의 공급 지점에서 부하까지의 전압 강하는 정상 작동 상태하에서 공칭 전압의 5% 를 넘지 않아야 한다. 이 요구사항을 만족하기 위해서는 표 6 보다 더 큰 단면적을 가진 도체를 사용 할 필요가 있다. 제어 회로에서 전압 강하는 돌입 전류를 고려하여 해당 장치에 대한 제조업체의 규격보다 낮은 장치 의 전압을 감소시키지 않아야 한다. 또한 4.3 을 참조한다. 과전류 보호 장치 및 스위칭 장치와 같은 구성요소의 전압 강하를 고려해야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 65 | {}
b48c73d1-5266-482d-a6e1-e22c1e2ad0e2 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 12.6 유연 케이블 12.6.1 일반사항 유연 케이블은 5 등급 또는 6 등급 도체이어야 한다. 비고 1 6 등급 도체는 5 등급 도체보다 스트랜드 지름이 더 작아야 하고 더 유연해야 한다(표 D.4 참 조). 가혹한 환경에서 사용되는 케이블은 다음과 같은 위험 보호를 위해 적합한 구조로 되어 있어야 한다. 거친 표면에서의 기계적인 취급과 끌림에 의한 마모 가이드 없는 사용에 의한 꼬임 안내 롤러, 케이블 드럼에서의 강제 인출, 감김 및 재감김 등에 의한 응력 비고 2 이러한 조건에 대한 케이블은 몇몇 국가표준에서 규정하고 있다. 비고 3 케이블의 수명은 높은 인장 응력, 작은 굵기, 구부러짐, 빈번한 사용 등의 불량한 작동 조건 에서는 단축될 수 있다. 12.6.2 기계적 정격 기계의 케이블 취급 설비는 기계를 작동하는 동안 도체가 장력을 가능한 한 작게 받도록 설계하여야 한다. 구리 도체가 사용될 경우에는 장력이 단면적당 15 N/mm2 를 넘지 않도록 하여야 한다. 장력이 15 N/mm2 를 넘는 것이 요구되는 경우, 특수 구조 케이블을 사용하고 최대 허용 장력은 케이블 제조 자와 약정하여야 한다. 구리 이외의 재료로 제조된 유연 케이블의 최대 허용 장력은 케이블 제조자의 동의 를 받아야 한다. 비고 다음 조건은 도체의 장력에 영향을 줄 수 있다. 가속력 작동 속도 케이블의 처진(늘어진) 무게 포설 방법 케이블 드럼 설비의 설계 12.6.3 드럼에 감긴 케이블의 허용 전류 드럼에 감긴 케이블은 드럼에 완전히 감긴 상태에서 정상 부하를 흘렸을 때, 도체의 최대 허용 온도 를 넘지 않는 단면적을 가지는 도체를 선정하여야 한다. 드럼에 설치된 환형 단면적의 케이블의 경우, 대기에서의 최대 허용 전류는 표 7 에 따라 감소된다. 비고 대기에서의 케이블 허용 전류는 제조자 규격 또는 관련 국가표준에서 찾을 수 있다. 66 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
8b0e5001-8d8b-4da5-95f4-664dabf14bbe | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 표 7 - 드럼에 감긴 케이블의 감소 계수 ¦ 드럼 형식 ¦ 케이블의 감긴 층수 ¦ 케이블의 감긴 층수 ¦ 케이블의 감긴 층수 ¦ 케이블의 감긴 층수 ¦ 케이블의 감긴 층수 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 드럼 형식 ¦ 기타 ¦ 1 ¦ 2 ¦ 3 ¦ 4 ¦ ¦ 환기 원통형 ¦ - ¦ 0.85 ¦ 0.65 ¦ 0.45 ¦ 0.35 ¦ ¦ 환기 방사형 ¦ 0.85 ¦ - ¦ - ¦ - ¦ - ¦ ¦ 비환기 방사형 ¦ 0.75 ¦ - ¦ - ¦ - ¦ - ¦ 감소 계수의 사용 시에는 케이블 및 케이블 드럼 제조자들과 협의 하는 것이 바람직하다. 이는 사용 되고 있는 계수가 다를 수 있기 때문이다. 비고 1 방사형 드럼은 조밀한 플랜지들 사이에 케이블을 감을 수 있는 나선층이 있는 경우이며, 견고한 플랜지로 되어 있으면 비환기형이고, 플랜지가 적절한 틈이 있으면 환기형이다. 비고 2 환기 원통형 드럼은 넓은 공간의 플랜지 사이에 케이블을 감을 수 있는 나선층이 있는 경 우이며, 드럼 및 끝단 플랜지에는 환기 구멍이 있다. 12.7 컬렉터 선, 컬렉터 봉 및 슬립링 장치 12.7.1 기본 보호 기계의 일상적인 접근 중에 발생할 수 있는 기본 보호를 위하여, 다음의 보호 조치 중 하나의 방법 에 의하여 컬렉터 선, 컬렉터 봉 및 슬립링 장치를 설치하거나 밀폐하여야 한다. 충전부의 부분 절연에 의한 보호. 이것은 우선적 조치이다. 최소 IP2X 또는 IPXXB 이상의 외함 또는 배리어에 의한 보호 쉽게 접근할 수 있는 배리어 또는 외함의 상부 수평면은 최소한 IP4X 혹은 IPXXD 이상의 보호 등급 이어야 한다. 필요한 보호 등급을 충족하지 못하는 경우에는 9.2.3.4.3 에 따른 비상 전원 차단과 조합하여 충전부 의 이격 거리 확보에 의하여 보호하여야 한다. 컬렉터 선 및 컬렉터 봉은 다음과 같이 설치 및/또는 보호되어야 한다. 풀코드 스위치, 스트레인(변형) 안전 장치 및 조작 체인 등과 같은 도전성 부분이 있는 보호되지 않은 컬렉터 선 및 컬렉터 봉의 접촉 방지 매달린 부하(swinging load)로 인해 발생하는 손상 방지 또한 6.2.6 을 참조한다. 12.7.2 보호 도체 도체 와이어, 도체 바 및 슬립링 어셈블리가 보호 본딩 회로의 일부로 설치되는 경우, 도체 와이어는 정상 작동 중에 전류가 흐르지 않아야 한다. 따라서 보호 접지 도체(PE) 및 중심 도체(N)는 컬렉터 선, 컬렉터 봉 또는 슬립링을 각각 분리시켜 사용하여야 한다. 슬립링에 사용되는 보호 접지 도체의 연속성은 적합한 조치에 의해 확실히 하여야 한다(예: 전류 컬 렉터의 이중화, 연속성의 감시). 67 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
2078d02c-1796-4a36-a138-fa998e98aab9 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 12.7.3 보호 도체의 전류 컬렉터 보호 도체의 전류 컬렉터는 다른 전류 컬렉터와 교환할 수 없는 모양 및 구조를 가져야 한다. 이러 한 전류 컬렉터는 슬라이딩 접촉 형태이어야 한다. 12.7.4 분리할 수 있는 차단 기능이 있는 전류 컬렉터 차단 기능이 있는 분리할 수 있는 전류 컬렉터는 충전부가 분리된 후에만 보호 접지 도체가 차단되 고, 보호 접지 도체 회로의 연속성은 충전부가 재접속되기 전에 재설정되도록 설계하여야 한다(8.2.3 참조). 12.7.5 대기에서의 이격 거리 각각의 도체 사이, 인접된 설비, 컬렉터 선, 컬렉터 봉 및 슬립링 장치 및 전류 컬렉터자들 사이의 이격 거리는 오염도 3 조건(KS C IEC 60664-1 참조)에서 작동하기에 적합하여야 한다. 12.7.6 연면 거리 각각의 도체 사이, 인접된 설비, 컬렉터 선, 컬렉터 봉 및 슬립링 장치 및 전류 컬렉터들 사이의 연 면 거리는 오염도 3 조건에서 작동하기에 적합하여야 한다. 비정상적인 양의 먼지, 습기 또는 부식성이 있는 환경에서는 다음과 같은 연면 거리 요구사항을 적 용해야 한다. 비보호 컬렉터 선, 컬렉터 봉 및 슬립링 장치는 최소 연면 거리 60 mm 의 절연체를 갖추어야 한다. 내장형 컬렉터 선, 절연 다극 컬렉터 봉 및 각각의 절연 컬렉터 봉은 최소 연면 거리 30mm 를 확 보하여야 한다. 적합하지 않은 주위 환경(예: 도전성 분진의 축적, 화학 작용)으로 인한 절연값의 점진적인 감소를 방 지하기 위한 특정 조치에 관해서는 제조자의 권고 사항을 따라야 한다. 12.7.7 도체 계통 구역 구분 컬렉터 선 또는 컬렉터 봉이 절연 구역으로부터 분리될 수 있도록 배열된 경우, 전류 컬렉터 자체에 의한 인근 구역의 충전을 방지하기 위해 적절한 설계가 강구되어야 한다. 12.7.8 도체선, 도체봉 설비 및 슬립링 장치의 구조 및 설치 동력 회로에 사용되는 도체선, 도체봉 및 슬립링 장치는 제어 회로에 사용되는 것과 는 각각 분리되 어야 한다. 도체선, 도체봉 및 슬립링 장치는 단락 전류의 기계적 응력 및 열 영향에 의한 손상 없이 견딜 수 있어야 한다. 지하 또는 건물 바닥에 설치하는 도체선 및 도체봉 설비용 덮개(취외 가능한)는 도구의 도움 없이는 사람에 의해서 열 수 없도록 설계하여야 한다. 도체봉이 일반 금속 외함에 설치되는 경우, 외함 개개의 구역은 서로 본딩 및 접지하여야 한다. 지하 또는 바닥 밑에 설치하는 도체봉의 금속 덮개 또한 서로 본딩 및 접지하여야 한다. 68 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
5a8c5d21-739e-4539-9209-6424a0b202f9 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 보호 본딩 회로는 금속 인클로저 또는 바닥 아래 덕트의 커버 또는 커버 플레이트를 포함해야 한다. 금속 힌지가 보호 본딩 회로의 일부를 형성하는 경우 그 연속성이 확인되어야 한다(18 절 참조). 액체가 축적될 수 있는 도체봉 덕트는 배수 기구를 설치해야 한다. 13 배선 지침 13.1 접속 및 경로 13.1.1 일반 요구사항 모든 접속, 특히 보호 본딩 회로의 접속은 우발적으로 헐거워지지 않도록 고정되어야 한다. 접속 수단은 마감된 도체의 단면적 및 상태에 적합하여야 한다. 두 개 이상의 도체를 하나의 단자에 연결하는 것은 당해 목적으로 설계된 경우에만 허용된다. 그러 나 보호 접지 도체는 하나의 단자 접속점에는 하나만을 접속하여야 한다. 납땜 접속은 납땜이 적합하도록 구비된 단자에만 허용된다. 단자대의 단자들은 도면에 표시된 것에 따라 명확하게 구분되어야 한다. 비고 KS C IEC 61666 은 전기 장비 내에서 터미널을 지정하는 데 사용할 수 있는 규칙을 제공한다. 부정확한 전기 연결(예: 장치 교체로 인한)이 위험의 원인이 되고 설계 조치에 의해 부정확한 연결 가능성을 줄이는 것이 불가할 경우, 도체 및/또는 종단을 식별하여야 한다. 유연 전선관 및 케이블의 설치 시에는 액체가 잘 배출될 수 있도록 하여야 한다. 도체 지지대는 이러한 설비가 구비되지 않은 장치 또는 단자에 도체를 마감할 경우에 구비하여야 한 다. 납땜은 이러한 용도로 사용하지 않아야 한다. 차폐선은 소선의 마모를 억제하고 쉽게 분리할 수 있도록 하여야 한다. 식별 꼬리표는 읽기 쉽고, 반영구적이며, 물리적인 환경에 적합하여야 한다. 단자대는 배선이 단자 위에서 서로 교차되지 않도록 설치 및 배선하여야 한다. 13.1.2 도체 및 케이블 포설 도체 및 케이블은 접속점 없이 단자에서 단자로 연결하여야 한다. 우발적인 분리에 대한 적절한 보 호를 제공하는 플러그/소켓 조합을 사용하는 접속부는 13.1.2 의 목적을 위한 접속으로 간주되지 않는 다. 예외: 접속함에서 단자 설치가 곤란할 경우(예: 이동 기계, 긴 유연 케이블이 있는 기계, 한 케이블 드럼에 케이블 제조자가 공급해야 하는 길이를 초과 하는 케이블 연결이 있을 경우에는 스플라이스 또는 접속점을 사용할 수 있다. 케이블 및 케이블 조립체를 접속하고 분리해야 할 필요가 있을 경우에 충분한 길이의 케이블을 사용 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 69 | {}
efb6995f-4b03-4fe5-ac5f-185bd50341ee | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 하여야 한다. 케이블 말단부는 도체의 말단부에서 기계 적응력을 받지 않도록 적절히 지지하여야 한다. 보호 접지 도체는 가능하면 루프의 임피던스를 감소시키기 위하여 기타 도전부에 인접된 곳에 설치 하여야 한다. 13.1.3 여러 선로의 도체 여러 선로의 도체는 각각의 선로의 적절한 기능 수행에 방해가 되지 않는 배치로 같은 덕트(예: 전선 관, 케이블 간선 시스템)에 나란히 설치할 수도 있고, 동일 다심 케이블 또는 동일한 플러그/소켓 조 합에 설치할 수도 있다. · 선로의 전압이 서로 다를 경우, 도체는 적당한 배리어를 설치하여 도체를 분리하거나 · 도체들에 인가되는 전압 중 가장 높은 전압에 대해 도체들을 절연시켜야 한다. 13.1.4 교류 회로 - 전자기 효과(와전류 방지) 강자성 인클로저에 설치된 AC 회로의 도체는 각 회로의 보호 도체를 포함하여 각 회로의 모든 도체 가 동일한 인클로저에 포함되도록 배열되어야 한다. 그러한 도체가 철제 외함에 들어가는 경우, 도체 가 개별적으로 강자성 물질로 둘러싸이지 않도록 배열되어야 한다. 강철 와이어 또는 강철 테이프로 외장된 단일 코어 케이블은 AC 회로에 사용해서는 안 된다. 비고 1 단일 코어 케이블의 강철 와이어 또는 강철 테이프 외장은 강자성 인클로저로 간주된다. 단 일 코어 와이어 외장 케이블의 경우 알루미늄 외장을 사용하는 것이 좋다. 비고 2 IEC 60364-5-52 에서 파생되었다. 13.1.5 비접촉식 전력 공급 시스템의 픽업 및 픽업 변환기 사이에 연결 픽업 및 픽업 변환기 사이의 케이블은 아래와 같이 연결되어야 한다. 가능한 한 짧게 - 기계적인 손상을 방지하도록 정확하게 비고 픽업의 출력은 전원이 될 수도 있으므로 케이블 손상이 고전압 위험을 초래할 수 있다. 13.2 도체의 식별 13.2.1 일반 요구사항 도체는 기술 문서에 따라 각 말단에서 식별할 수 있어야 한다. 기타 도체의 식별은 색상(무늬가 없는 색이나 하나 이상의 줄무늬가 있는 색 사용), 숫자, 문자 또는 색상 및 숫자 또는 문자의 조합으로 하여야 한다. 숫자를 사용하는 경우 아라비아 숫자이어야 하며, 문자는 로마체(대문자 또는 소문자)를 사용하여야 한다. 비고 1 부속서 B 는 우선적 식별 방법에 관하여 공급자와 사용자 간의 약정용으로 사용될 수 있다. 70 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
67e98464-f7ce-421d-b070-3598ed84f8eb | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 비고 2 KS C IEC 62491 은 산업 설비, 장비 및 제품에 사용되는 케이블 및 코어/도체의 라벨링에 대 한 규칙과 지침을 제공한다. 13.2.2 보호 접지 도체의 식별/보호 본딩 도체 보호 접지 도체/보호 본딩 도체는 형태나 위치, 표시 또는 색을 통해 쉽게 식별할 수 있어야 한다. 한 가지 색상으로 식별해야 하는 경우, 초록색-노란색 두 가지 혼합색을 도체의 전체에 사용해야 한 다. 이 색상 식별은 보호 접지 도체/보호 본딩 도체에 대하여 엄격히 제한된다. 절연 도체에 대한 초록색-노란색 두 색의 조합은 도체 표면의 최소 30 %, 최대 70 %에 두 색상 중 하나의 색상이 길이 15mm 로 하고, 그 나머지 부분은 다른 색으로 하여야 한다. 보호 접지 도체를 형태, 위치 또는 구조(예: 편조선)로 쉽게 식별할 수 있는 경우 또는 절연 도체에 쉽게 접속할 수 없는 경우 또는 다심 도체의 부분일 경우, 도체에 식별 목적으로 색을 표기하지 않 을 수 있지만, 도체가 길이 전체에 걸쳐 명확하게 보이지 않는 경우 도체의 끝 또는 접근 가능한 위 치는 그림 기호 IEC 60417-5019:2006-08(그림 16 참조) 또는 PE 라는 글자 혹은 초록색-노란색의 두 가지 조합 색상으로 분명하게 식별되도록 해야 한다. ![image](/image/placeholder) L 그림 16 - 기호 IEC 60417-5019 예외: 보호 본딩 컨덕터는 문자 PB 및/또는 IEC 60417-5021(2002-10) 기호로 표시할 수 있다(그림 17 참조). ![image](/image/placeholder) 「 □ L 」 그림 17 - 기호 IEC 60417-5021 13.2.3 중성 도체의 식별 선로가 색상으로 식별하는 중성 도체를 포함하는 경우, 색상은 밝은 파란색이어야 한다. 밝은 파란색은 혼동할 수 있는 다른 도체에는 사용하지 않아야 한다(IEC 60445:2010 의 3.2.2 참조). 선택된 색이 중성 도체의 고유한 식별일 경우, 그 색을 혼동 가능한 다른 도체를 식별하는 데 사용해서는 안 된다. 색상으로 식별하는 경우의 중성 도체로 사용하는 나도체는 각 구획, 장치 또는 각 접근 가능한 위치 에 폭 15 mm ~ 100 mm 의 밝은 파란색 줄무늬를 입히거나 나도체에 밝은 파란색을 입힌다. 13.2.4 색에 의한 식별 색상 부호화가 도체 식별용[보호 접지 도체(13.2.2 참조) 및 중성 도체(13.2.3 참조) 외]으로 사용되는 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 71 | {}
6d6d5a60-6b73-4f2e-aae3-711cfc6f34fa | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 경우, 다음과 같은 색상을 사용할 수 있다. 검은색, 갈색, 빨간색, 주황색, 노란색, 초록색, 파란색(밝은 파란색 포함), 보라색, 회색, 흰색, 분 홍색, 청록색 비고 이 색상 목록은 IEC 60757 에 의한 것이다. 색상이 식별용으로 사용되는 경우, 절연색 또는 색표지에 의해 도체의 전체 길이에 표시한다. 선정된 위치에 추가로 식별 표시를 사용하는 것도 한 방법이다. 안전상의 이유로 초록색 또는 노란색은 초록색-노란색 이중 색상 조합으로 혼동할 우려가 있는 곳에 서는 사용하지 않아야 한다(13.2.2 참조). 위의 색상을 조합하여 사용한 색상 식별은 혼동되지 않도록 사용하여야 하며, 초록색 또는 노란색은 초록색-노란색 두 색의 조합을 제외하고는 사용하지 않아야 한다. 도체 식별용으로 색이 사용될 경우, 다음과 같이 색상 코드화하는 것이 바람직하다. 검은색: 교류 및 직류 전원 선로 빨간색: 교류 제어 회로 파란색: 직류 제어 회로 주황색: 5.3.5 에 따른 예외 회로 예외: 위의 내용에서 다음의 경우는 예외로 한다. 사용되는 절연재가 요구되는 색상이 없을 경우(예: 다심 케이블 13.3 외함 내부 배선 패널 내의 도체는 제위치에 있도록 지지되어야 한다. 비금속 덕트는 내화 절연재로 만들어졌을 때만 허용된다(IEC 60332 시리즈 참조). 외함 내부에 설치한 전기 장비는 외함 전면에서 배선을 변경할 수 있도록 설계 및 시설하도록 한다 (11.2.1 참조). 이것이 불가능하고 제어 장치가 외함 뒷면에 접속된 경우, 점검용 문이나 스윙 아웃 패널이 구비되어야 한다. 문에 설치된 장치 또는 기타 가동 부품의 접속은 빈번한 움직임에 무리가 없도록 12.2 및 12.6 에 따 라 유연한 도체를 사용하여야 한다. 도체는 전기 접속과 는 관계없이 고정 부품 및 가동 부품에 고정 되어야 한다(8.2.3 및 11.2.1 참조). 덕트 안에 설치되지 않는 도체 및 케이블은 적절한 방법으로 지지되어야 한다. 단자대 또는 플러그/소켓은 외함 외부까지 연장되는 제어 배선용으로 사용하여야 한다. 플러그/소켓 조합에 대해서는 13.4.5 와 13.4.6 을 참조한다. 전력 케이블 및 측정 회로의 케이블은 접속할 장치의 단자에 직접 접속할 수 있다. 72 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
6fa3f443-b0d7-4a15-a4ca-7020c879d57c | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 13.4 외함 외부 배선 13.4.1 일반 요구사항 외함 내로 인입되는 각각의 글랜드, 부싱 등을 장착한 케이블 또는 덕트는 보호 등급이 저하되지 않 도록 해야 한다(11.3 참조). 회로의 컨덕터는 다른 다중 코어 케이블, 도관, 케이블 덕트 시스템 또는 케이블 트렁킹 시스템에 배 포되어서는 안 된다. 하나의 회로를 구성하는 여러 개의 다중 코어 케이블이 병렬로 설치된 경우에 는 필요하지 않다. 다중 코어 케이블이 병렬로 설치되는 경우 각 케이블은 각상의 하나의 도체와 있 는 경우 중성선을 포함해야 한다. 13.4.2 외부 덕트 전기 설비 외함에 외부의 도체 및 접속부는 덕트 없이 케이블 트레이 또는 케이블 지지 수단의 사용 에 의하여 설치할 수 있는 적합하게 보호되는 케이블을 제외하고는 13.5 에 규정된 적절한 덕트(전선 관 또는 케이블 트렁킹 설비)로 보호하여야 한다. 위치 스위치 또는 근접 스위치와 같은 장치가 전용 케이블과 함께 공급될 경우, 케이블이 해당 목적에 적합하고 충분히 짧고 손상 위험이 최소화되는 위치에 보호된 경우, 해당 케이블은 덕트에 내장될 필요가 없다. 덕트에 사용되는 피팅은 물리적인 환경에 적합하여야 한다. 유연 전선관 또는 유연 다심 케이블은 펜던트 누름 단추 조작반에 도체 연결을 해야 하는 경우에 사 용하여야 한다. 펜던트 조작반의 무게는 전선관 또는 케이블이 당해 목적에 적합하도록 설계된 경우 는 예외로 하고 유연 전선관 또는 유연 다심 케이블 이외의 방법으로 지지되어야 한다. 13.4.3 기계 이동부의 접속 움직이는 부품에 대한 연결 설계는 예측 가능한 이동 빈도를 고려하고 부품에 대한 접속부는 12.2 및 12.6 에 의한 도체를 사용하여야 한다. 유연 케이블 및 유연 전선관은 특히 이음쇠 부위가 과도하 게 휘거나 장력을 받지 않도록 설치하여야 한다. 움직임이 있는 케이블은 접속 부위에 기계적인 힘이 가해지거나 심한 굴곡이 생기지 않도록 지지하 여야 하며, 케이블은 케이블 제조업체가 지정하거나 그러한 규격이 제공되지 않은 경우 굴곡 반지름 은 최소한 외부 반지름의 10 배 이상이 되도록 루프의 길이를 충분히 한다. 기계의 유연 케이블은 다음의 요소 등에 의하여 손상될 수 있는 외부 가능성을 최소화하도록 설치되 거나 보호되어야 한다. 자체 기계의 이동에 의해 짓눌리는 것. 차량 또는 다른 기계에 의해 짓눌리는 것. 이동 중에 기계 구조물과 의 접촉 케이블 바스켓에서의 인출 및 인입 또는 케이블 드럼에 감기거나 풀리는 경우 장식용 설비(festoon system) 또는 매달기형 케이블에 가속력 및 풍력이 작용하는 경우 케이블 감기의 과도한 마찰 과도한 방사열에 노출 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 73 | {}
5ddcb944-ad27-465d-a4e5-5432c8b87778 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 케이블 외장은 움직임과 대기 오염물(예: 기름, 물, 냉각제, 먼지)의 영향으로부터 예상할 수 있는 정 상 사용에 견디어야 한다. 가동부에 인접된 곳에서 이동 사용되는 케이블의 경우, 가동부와 케이블 사이에 최소한 25 mm 의 공 간을 유지하는 예방 조치를 취하여야 한다. 이 공간을 확보하기 어려울 경우, 고정 배리어를 케이블 과 가동부 사이에 설치하여야 한다. 케이블 취급 설비는 다음의 경우, 케이블이 비틀리지 않도록 측면 케이블의 각이 5°를 넘지 않도록 설계되어야 한다. 케이블 드럼의 풀림 및 감김 케이블 유도 장치에 케이블의 접근 및 멀어짐 케이블 드럼은 최소한 두 바퀴 이상의 케이블 여유분이 있도록 조치하여야 한다. 유연 케이블을 유인 및 이동시키기 위한 장치는 예상 피로 수명 및 허용 응력을 고려하되, 케이블 제조자의 동의 가 없는 한, 케이블의 굽어짐은 모든 점에서 표 8 에 주어진 값 이상을 유지하도록 설 계하여야 한다. 표 8 - 유연 케이블의 강제 유인의 최소 허용 굽힘 반지름 적용 ¦ 적용 ¦ 평면 케이블의 지름 또는 케이블 두께(d) mm ¦ 평면 케이블의 지름 또는 케이블 두께(d) mm ¦ 평면 케이블의 지름 또는 케이블 두께(d) mm ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 적용 ¦ d≤ 8 ¦ 8 < d≤ 20 ¦ d> 20 ¦ ¦ 케이블 드럼 ¦ 6 d ¦ 6 d ¦ 8 d ¦ ¦ 유인 롤러 ¦ 6 d ¦ 8 d ¦ 8 d ¦ ¦ 장식용 설비 ¦ 6 d ¦ 6 d ¦ 8 d ¦ ¦ 기타 ¦ 6 d ¦ 6 d ¦ 8 d ¦ S 자 모양의 2 굴곡부 사이의 직선 부분 또는 기타 평면의 굴곡부는 케이블 지름에 최소한 20 배 이 상이어야 한다. 유연 전선관이 가동 부품에 인접하여 설치되는 경우, 그 구조 및 지지 수단은 모든 작동 조건하에서 유연 전선관의 손상을 방지할 수 있어야 한다. 금속 유연 전선관은 당해 목적에 적합하도록 특별히 설계된 경우를 제외하고는 빠르거나 빈번한 이 동용으로는 사용되어서는 안 된다. 13.4.4 기계에서의 장치 사이의 접속 기구(예: 위치 감지기, 누름 버튼)가 설치된 다수의 기계가 직렬 또는 병렬로 접속되는 경우, 이들 장 치 사이는 중간 시험점을 형성하는 단자를 통하여 접속하는 것이 바람직하다. 이들 단자는 적절히 보호되고 작업에 편리한 곳에 설치하고, 관련 도면에 표시되어야 한다. 13.4.5 플러그/소켓의 조합 플러그/소켓 조합에 의해 모선 시스템에 연결된 플러그/소켓 조합(유연 케이블 없음) 또는 구성요소에 74 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
bd5d4753-990e-45c0-8f34-cbfc45594907 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 의해 종단된 외함 내부 구성요소 또는 장치에는 13.4.5 의 목적상 플러그/소켓 조합으로 간주되지 않 는다. 아래 항목 a)에 따라 설치 후에 플러그/소켓 조합은 커넥터의 삽입 또는 제거 동안을 포함하여 언제 든 충전부와 의도치 않은 접촉을 방지하는 형식이 되어야 한다. 보호 정도는 최소 IP2X 혹은 IPXXB 가 되어야 한다. PELV 회로는 이 요구사항에서 제외된다. 플러그/소켓에 보호 본딩 회로 용 접점이 포함되어 있는 경우 첫 번째 최종 차단 접점이 있어야 한 다 (8.2.4 참조). 부하 조건 중에 연결 또는 분리되어야 하는 플러그/소켓 조합은 부하 차단 용량이 충분해야 한다. 플 러그/소켓 조합 정격이 30 A 이상일 경우, 개폐 장치가 OFF 위치일 때만 연결 및 분리가 가능하도록 개폐 장치와 연동되어야 한다. 정격이 16A 이상인 플러그/소켓 조합에는 의도치 않는 또는 우발적인 분리를 방지하는 보호지지 수 단이 있어야 한다. 플러그/소켓 조합의 의도치 않은 또는 우발적인 분리가 위험한 상황을 야기하는 곳에는 보호지지 수 단이 있어야 한다. 플러그/소켓 조합의 설치 시 다음 요구사항을 충족해야 한다. a) 분리 후 충전 상태를 유지하는 구성요소는 요구 공간 거리 및 연면 거리를 고려하여 최소 IP2X 또는 IPXXB 보호 등급이 되어야 한다. 전기 장비가 분리 가능한 경우, 극성이 있는 플러그/소켓을 통한 접속이 허용된다. PELV 회로는 이 요구사항에서 제외된다. b) 플러그/소켓 조합의 금속 하우징은 보호 본딩 회로에 연결되어야 한다. c) 전원 부하를 전달하지만 부하 조건 중에 분리되지 않아야 하는 플러그/소켓 조합은 의도치 않은 또는 우발적인 분리가 위험한 상황을 야기할 경우, 리테이닝 장치가 있어야 하고 부하 하에서 분 리되지 않도록 명확한 표시가 있어야 한다. d) 동일한 전기 장비에 하나 이상의 플러그/소켓 조합이 제공될 경우, 관련 조합이 분명하게 식별가 능해야 한다. 부정확한 삽입을 방지하기 위해 기계 코딩을 사용할 것이 권장된다. e) 제어 회로에 사용된 플러그/소켓 조합은 KS C IEC 61984 의 해당 요구사항을 충족하여야 한다. 예외:KS CIEC 60309-1 에 따른 플러그/소켓 조합에서는 해당 목적의 제어 회로에 해당 접점만 사용되어 야 한다. 이 예외는 전원 회로에 중첩된 고주파 신호를 사용하는 제어 회로에는 적용되지 않는다. 13.4.6 선적을 위한 분해 선적을 위해 배선의 분리가 필요한 경우, 단자 또는 플러그/소켓은 분리점에 설치되어야 한다. 이러 한 단자는 적절하게 폐쇄되어야 하며, 플러그/소켓은 운송 및 보관중에 물리적인 환경으로부터 보호 되어야 한다. 13.4.7 여분의 도체 유지 보수 및 수리용으로 추가적인 도체를 설치할 필요가 있다. 예비 도체가 있는 경우, 충전부와 접 75 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
7b458628-1f5a-466a-9269-d666c0e4e9f1 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 촉되지 않도록 격리시키거나 예비 단자에 접속하여야 한다. 13.5 덕트, 접속함 및 기타 함 13.5.1 일반 요구사항 덕트는 적용에 적절한 보호 등급이어야 한다(KS C IEC 60529 참조). 도체 절연이 접촉될 수 있는 모든 모서리, 날카롭거나 거친 면 또는 돌출부 등은 덕트와 피팅류에서 제거되어야 한다. 필요한 경우, 내화성, 방유성 절연 재질로 이루어진 추가적인 보호를 절연된 보호 접지 도체에 하여야 한다. 기름 또는 수분의 축적이 우려되는 배선용의 케이블 간선 계통, 접속함 및 기타 함에는 지름 6mm 의 배수 구멍의 설치가 허용된다. 기름, 공기 또는 물 등의 배관이 전선관과 혼동되는 것을 피하기 위하여 전선관을 물리적으로 분리 시키거나 적절하게 표시하여야 한다. 덕트 및 케이블 트레이는 손상이나 마모의 우려를 최소화하기 위하여 가동부로부터 충분한 거리에 견고하게 지지되어야 한다. 작업자가 통행하는 구역의 경우, 덕트 및 케이블 트레이는 작업 바닥에서 최소한 2m 이상 위에 설치하여야 한다. 부분적으로 덮여진 케이블 트레이는 덕트나 케이블 간선 계통(13.5.6 참조)으로 간주되지 않고, 사용 되는 케이블은 케이블 트레이의 설치가 적합하여야 한다. 13.5.2 견고한 금속 전선관 및 피팅류 견고한 금속 전선관 및 피팅류는 조건에 적합하게 아연 도금 강철 또는 부식 방지 재질로 하여야 하 며, 전기 발생의 원인이 되는 서로 다른 금속의 사용은 피하여야 한다. 전선관은 반드시 적절한 위치에 설치되고 양 끝단이 지지되어야 한다. 피팅류는 전선관 및 사용에 적합하여야 한다. 피팅류는 구조적으로 다른 것과 서로 조립되지 않도록 나사에 홈을 내야 한다. 나사산이 없는 피팅을 사용하는 경우에 전선관은 장비에 확실히 고정시켜야 한다. 전선관의 굴곡은 전선관이 손상되지 않는 방법을 사용해야 하며, 전선관의 내부 지름이 현저하게 감 소하지 않도록 하여야 한다. 13.5.3 유연 금속 전선관 및 피팅류 유연 금속 전선관은 유연 금속 관로 또는 편조 외장으로 구성하여야 하며, 예상되는 물리적 환경에 적합하여야 한다. 피팅류는 전선관 및 사용에 적합하여야 한다. 13.5.4 유연 비금속 전선관 및 피팅류 유연 비금속 전선관은 비틀림에 잘 견뎌야 하며 다심 케이블의 차폐선과 유사한 물리적 성질을 가지 76 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
92bb851e-0a66-4a1d-b71b-bbb75058aa57 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 고 있어야 한다. 전선관은 예상되는 물리적 환경에서의 사용에 적합하여야 한다. 피팅류는 전선관과 호환성이 있어야 하며 사용에 적합한 것이어야 한다. 13.5.5 케이블 트렁킹 설비 외함 외부의 케이블 트렁킹 설비는 단단히 고정시키고 기계의 모든 이동부 또는 오염되는 부분이 없 어야 한다. 덮개는 측면이 겹치지 않아야 하며, 개스킷을 사용하여야 한다. 덮개는 경첩 또는 체인에 의해 케이 블 트렁킹 설비에 부착하고, 정체 구조의 나사 또는 기타 적당한 점쇠로 고정시켜야 한다. 수평 케이 블 트렁킹 설비에서의 덮개는 바닥면에 설치하지 않아야 한다. 케이블 트렁킹 설비가 구획되어 설치되는 경우, 구획부 간의 접점은 단단히 고정해야 하며 개스킷을 설치할 필요는 없다. 허용된 개구부에서만 배선 또는 배출용으로 사용될 수 있다. 케이블 트렁킹 설비는 미사용 녹아웃을 제외하고는 개방하여서는 안 된다. 13.5.6 기계 구획 및 케이블 트렁킹 설비 외함 도체용의 기계 기둥이나 바닥 내의 칸막이 또는 케이블 트렁킹 설비의 사용은 칸막이 등이 완 전히 폐쇄되어 있는 냉각제 또는 기름 저장기와 격리되어 있는 경우에 허용된다. 폐쇄된 칸막이 및 케이블 트렁킹 설비에서의 도체 설치는 이들이 손상되지 않도록 안전하게 배열하여야 한다. 13.5.7 접속함 및 기타 함 배선용으로 사용되는 접속함 및 기타 함은 유지 보수를 위해 접근이 용이하여야 한다. 이들 함은 기 계가 작동하기 위한 경우에 외부 영향을 고려하여 고형체 및 유체의 인입에 대하여 보호하여야 한다 (11.3 참조). 이들 함은 미사용 녹아웃을 제외하고는 개방해서는 안 되고, 기타 어떠한 개구부도 없이 분진, 기름 및 냉각제와 같은 물질을 차단하도록 구성하여야 한다. 13.5.8 전동기 접속함 전동기 접속함은 전동기 및 전동기에 장착된 장치(예: 제동기, 온도 감지기, 플러그형 개폐기, 타코미 터 발전기)의 접속만을 위한 것이다. 14 전동기 및 관련 장비 14.1 일반 요구사항 전동기는 IEC 60034 시리즈의 관련 부를 따르도록 한다. 전동기 및 관련 장비용 보호 요구사항은 과전류 보호에 관해서는 7.2, 과열로부터 모터 보호에 관해서 는 7.3, 과속 보호에 관해서는 7.6 에 규정되어 있다. 77 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
8923088c-a186-408a-900d-0c71ee6600d7 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 전동기가 정지되어도 전원이 차단되지 않는 많은 제어기가 있기 때문에 5.3, 5.4, 5.5, 7.5, 7.6 및 9.4 의 요구사항을 충족시키기 위해 특별한 조치가 필요하다. 전동기 제어기는 11 절에 따라 위치하고 설 치하여야 한다. 14.2 전동기 외함 모터 외함은 KS C IEC 60034-5 를 따라야 한다. 모든 전동기의 보호는 적용 방안과 물리적 환경에 따라 다르다(4.4 참조). 모든 모터는 기계적 손상 으로부터 적절히 보호되어야 한다. 14.3 전동기의 크기 가능한 한 전동기의 크기는 KS C IEC 60072 시리즈에 적합한 크기이어야 한다. 14.4 전동기 설치 및 구획 각 전동기 및 이와 관련된 연결 장치, 벨트 및 활차 또는 체인은 적절하게 보호되고, 검사, 유지 보 수, 조정 및 정렬, 급유 및 교체를 위해 접근이 용이하도록 설치해야 한다. 전동기 설치 준비는 모든 전동기 점쇠를 움직일 수 있고 모든 단자함에 접근할 수 있도록 하여야 한다. 전동기는 적절한 냉각이 이뤄지도록 설치하고 온도 상승이 절연 등급 범위를 넘지 않도록 하여야 한 다(KS C IEC 60034-1 참조). 전동기 구획은 가능한 한 청결하고 건조하여야 하며, 필요한 경우 기계 외부로 직접 통풍되어야 한 다. 통풍구는 절삭 부스러기, 분진 또는 분무되는 물의 인입이 허용 등급이어야 한다. 전동기 구획과 전동기 구획 요구사항을 충족시키지 못하는 다른 구획 사이에는 어떠한 개구부도 설 치해서는 안 된다. 전선관 또는 파이프가 전동기 구획에서 전동기 구획에 관한 요구사항을 충족시키 지 못하는 타구획 장소로 연결될 경우, 전선관 또는 배관 둘레의 틈새는 밀봉되어야 한다. 14.5 전동기 선정 기준 전동기 및 관련 장비의 특성은 예상되는 작동 및 물리적 환경 조건에 적합하게 선정하여야 한다(4.4 참조). 이러한 관점에서 고려해야 할 사항은 다음과 같다. - 전동기 형태 사용 주기의 형태(KS C IEC 60034-1 참조) 고정 속도 또는 가변 속도 작동(및 수반하는 환기의 여러 영향) 기계적 진동 전동기 제어장치의 종류 모터에 공급되는 전압 및/또는 전류의 주파수 스펙트럼의 온도 상승 및 기타 영향(특히 컨버터에 서 공급되는 경우) 기동 방식 및 돌입 전류가 다른 사용자의 작동에 미치는 영향, 가능한 공급 근거에 의한 특수한 상황 고려 시간 및 속도에 따른 역토크 부하의 변화 78 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
6f63700e-5363-437b-857a-f7cc171639bb | KSCIEC60204-1_KR | 관성이 큰 부하의 영향 불변 토크나 일정 전력의 영향 전동기와 변환 장치 사이의 유도성 리액터 필요성 14.6 기계 제동기용 보호 장치 KS CIEC 60204-1:2016 기계 제동기의 액추에이터용 과부하 및 과전류 보호 장치의 작동은 관련 기계 작동기의 전원을 동시 에 차단하여야 한다. 비고 관련 기계 액추에이터는 동일 모션(예를 들어, 케이블 드럼 및 장기 이동 드라이브)과 관련된 것이다. 15 소켓-수구 및 조명 15.1 소켓-수구 기계 또는 관련 장비(예: 이동용 전동 공구, 시험 장비 등)를 사용할 수 있도록 소켓-수구가 설치되 어 있을 경우, 다음 조건을 만족해야 한다. 소켓-수구는 KS C IEC 60309-1 에 따르되, 그렇지 않을 경우 이들은 정격 전압 및 정격 전류를 명 확하게 표시하도록 한다. 소켓-수구는 보호 본딩 회로의 연속성이 확보되어야 한다. 소켓-수구에 연결된 모든 비접지 도체는 과전류로부터 보호되어야 하며, 필요한 경우 다른 선로 의 보호로부터 분리하여 7.2 및 7.3 에 따라 과부하로부터 보호되어야 한다. 소켓-수구의 전원 차단이 기계용 또는 기계 일부분용 전원 차단 장치에 의하지 않는 경우, 5.3.5 의 요구사항에 따라야 한다. 전원의 자동 차단에 의해 고장 보호가 되는 경우 차단 시간은 TN 시스템의 경우 표 A.1, 또는 TT 시스템의 경우 표 A.2 에 따라야 한다. 정격 전류가 20 A 를 초과 하지 않는 소켓-콘센트가 설치된 회로에는 정격 동작 전류가 30 mA 를 초 과하지 않는 잔류 전류 보호(RCD)가 제공되어야 한다. 15.2 기계 및 장비의 국부 조명 온/오프 전원 스위치는 램프 홀더 또는 전선의 중간에 접속해서는 안 된다. 15.2.1 일반사항 조명에 의한 스트로보 현상은 적절한 조명 장치의 사용으로 피할 수 있다. 기계 및 장비의 외함내에 조명기구를 설치하는 경우, 전자파 적합성은 4.4.2 의 규정을 따른다. 15.2.2 전원 공급 조명기기에 접속된 전선로의 선간 공칭전압은 220 V 를 넘지 않아야 하며, 부득이 높은 전압을 사용 하는 조명기기의 경우에도 선간전압은 50 V 를 넘지 않아야 한다. 79 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
70bc405a-e8b2-4cd5-b65b-1b490e7323d6 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 조명기기에 공급하는 전원은 다음중 하나에 의하여야 한다(7.2.6 참조). 전원 차단 장치의 2 차측에 접속된 절연 변압기. 과전류 보호 장치는 2 차측 전선로에 설치되어야 한 다. 전원 차단 장치의 1 차측에 접속된 절연 변압기. 다만, 이 전원은 조명기기 전선로의 유지 보수용 으로만 사용되어야 한다. 또한 과전류 보호 장치는 2 차측 선로에 설치되어야 한다(5.3.5 참조). 과전류 보호장치가 설치되어 있는 조명부하 전용회로 1 차 차단 장치(5.3.5 참조) 및 2 차 과전류 보호 장치가 전원 차단 장치에 인접한 제어설비 외함 내에 장착 및 설치되는 경우에 전원 차단 장치의 전원측에 접속된 절연 변압기 외부에서 공급되는 조명부하용 전선로(예: 공장 조명 공급). 다만, 조명기기 사용전력이 3 kW 를 넘 지 않는 곳에서 기계 작업 조명용으로 설치되어야 한다. 절연 변압기가 장착된 LED 광원에 대한 DC 공급용 전원 공급 장치(예: KS C IEC 61558-2-6 에 따 름). 예외: 정상 작동 중 고정 조명 장치가 조작자의 손이 닿지 않는 곳에 설치되는 경우, 이 규정을 적용 하지 않는다. 15.2.3 보호 국부 조명 선로는 7.2.6 에 따라 보호되어야 한다. 15.2.4 피팅류 조절 가능한 조명의 피팅류는 물리적 환경에 적합하여야 한다. 램프 홀더 설치는 다음에 따라야 한다. 관련 IEC 표준에 따를 것. 감전사고 방지를 위해 조명램프 캡은 절연재료로 제작될 것. 반사면은 조명램프 홀더가 아닌 브래킷으로 지지할 것. 예외: 고정된 조명기기가 정상 작동 중 조작자의 손이 닿지 않는 곳에 설치되는 경우에는 이 규정을 적용하지 않는다. 16 표지, 경고 표시 및 기준 지정 16.1 일반사항 경고 표시, 명판, 표지 및 식별판은 물리적 충격에 견딜 수 있도록 견고하게 부착되어야 한다. 16.2 경고 표시 16.2.1 감전 위험 전기기계설비 외함에는 일반인에게 위험을 알릴수 있도록 그림 기호 KS S ISO 7010-W012(그림 18 80 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b4b25abc-fa44-411e-952f-ad7e0d53adc2 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 참조)와 같이 검은색 삼각형 안에 노란색 바탕과 검은색 번개로 표시하여야 한다. 그림 18 - 기호 KS S ISO 7001 W012 이 경고 표시는 외함의 문 또는 덮개 등 사람이 쉽게 보이는 위치에 정확하게 부착하여야 한다. 다만, 경고 표시는 다음의 경우 생략할 수 있다[6.2.2b) 참조]. 누전 시 전원을 자동으로 차단하는 보호장치가 설치된 전기기계 외함 특정인인 조작자만 사용하는 전기기계설비 장치 자체가 외함 내에 설치되는 경우(예: 위치 감지기) 16.2.2 고온 위험 고온이 예상되는 전기기계설비에 고온 위험에 대한 경고표시를 하는 경우에는 그림 기호 KS S ISO 7010-W017 가 사용되어야 한다(그림 19 참조). 그림 19 - 기호 KS s ISO 7010-W017 비고 ISO 13732-1 은 고온으로부터 보호되는 안전장구를 갖추지 않은 상태에서 사람이 전기기계설비 의 뜨거운 표면을 접촉할 때 화상 위험을 평가하기 위한 지침을 제공한다. 16.3 기능 식별 전기기계설비를 안전하게 조작할 수 있도록 제어방법, 제어장치의 특성 등 기능식별에 대한 내용을 조작자가 보기 쉬운 장비의 위치에 견고하게 부착되어야 한다. IEC 60417 및 KS S ISO 7000 에 따라 작성하는 것이 권고된다. 16.4 전기 장비 외함의 표지 다음 정보는 전기기계기구의 외함에 명확하고 쉽게 이해할 수 있도록 표시하여야 한다. 81 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
35aecfa0-1a34-4043-be08-40d160e3ccb1 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 제작자의 상호명 인증 표시 또는 지역 또는 지역 법률에서 요구할 수 있는 기타 표시 해당되는 경우, 모델명 해당되는 경우, 일련번호 해당되는 경우, 전기 도면의 번호 또는 전기 도면의 색인 번호(KS C IEC 62023 참조) - 각 전원의 정격 전압, 상수 및 주파수(교류의 경우), 전부하 전류 정보는 주요 유입 공급 옆에 제공되는 것이 권고된다. 16.5 기준 지정 모든 외함, 조립품, 제어 장치 및 부품은 기술 문서에서 제시된 동일한 기준 지정에 의하여 분명하게 식별되어야 한다. 17 기술 문서 17.1 일반사항 기계 전기 장비의 식별, 운송, 설치, 사용, 유지 보수, 해체 및 폐기 시 필요한 정보가 제공되어야 한다. 비고 1 장비 장치와 함께 제공되는 기술 문서는 기계의 전기 장비 문서에 포함될 수 있다. 사용자가 전자 문서형태 혹은 인터넷 사이트에 제공되는 지침을 활용할 수 있다고 가정할 수 없기 때 문에 문서는 종이 형식으로 제공된다. 그러나 문서를 전자 형식과 인터넷 및 종이 형식으로 제공하는 것이 유용할 때가 많다. 사용자가 분실하였거나 원하는 경우 전자 파일을 다운로드 하고 종이 사본이 있으면 문서를 복구할 수 있기 때문이다. 이것은 또한 필요한 경우 문서의 업데이트를 용이하게 한다. 비고 2 특정 언어 사용 관련 요구사항이 법적인 요구사항으로 다루어지는 국가도 있다. 부속서 I 는 정보 및 문서 준비를 위한 지침으로 간주되어야 한다. 17.2 전기 징비 관련 정보 다음 정보를 제공한다. a) 하나 이상의 문서를 제공하는 경우, 전기 장비 전체에 대한 주요 문서, 전기 장비와 관련한 보충 문서의 목록 b) 전기 장비의 식별(16.4 참조) c) 다음을 포함하는 설치 및 장착에 대한 정보 · 전기 장비의 설치 및 장착, 전기 장비를 전기 공급에 연결하는 것 그리고 해당하는 경우 다른 공급에 대한 설명 · 각 인입 전원 공급에 대한 전기 장비의 단락 전류 정격 · 정격 전압, 위상 및 주파수(교류의 경우), 배전 시스템의 종류(TT, TN, IT) 및 각 인입 공급에 대 한 전부하 전류 82 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
e4e5cb29-6120-4826-b93c-d3c8867dca9b | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 · 각 인입 공급에 대한 추가적인 전기 공급과 관련한 요구사항(예를 들어 최대 공급원 임피던스, 누설 전류) · 전기 장비를 제거하거나 운용하기 위하여 필요한 공간 · 냉각을 위한 배치가 손상되지 않도록 하는 데 필요한 경우, 설치 요구사항 · 해당하는 경우, 환경상 제한(예를 들어, 조명, 진동, EMC 환경, 대기 오염 물질) · 해당하는 경우, 기능상 제한(예를 들어 첨두 기동 전류 및 허용 전압 강하) · 전자기 호환성과 관련하여 전기 장비를 설치하기 위하여 취하는 예방 조치 d) 다음과 같은 기계 근처에서(예를 들어 2.5 미터 안에서) 보호 본딩 회로로 동시에 접근할 수 있는 기타 도전부를 연결하는 데 대한 지침 · 금속 파이프 · 울타리 · 사다리 · 난간 e) 다음 등을 포함하는 기능과 작동에 대한 정보 · 전기 장비의 구조에 대한 개요(예를 들어 구조도나 개요도를 통하여) · 사용 목적을 위하여 필요한 경우, 프로그래밍하거나 구성하기 위한 절차 · 예상 밖으로 정지한 후 다시 시작하기 위한 절차 · 작동 순서 f) 다음 등을 포함하는 전기 장비의 유지보수에 대한 정보 · 기능 시험의 빈도와 방법 · 안전한 유지보수를 위한 절차에 대한 지침과 안전 기능 및/또는 보호 조치를 유예하기 위하여 필요한 경우(9.3.6 참조) · 예방 유지보수의 조정, 수리, 빈도 및 방법에 대한 지침 · 교체 대상인 전기 구성품의 상호 연결에 대한 세부사항(예를 들어, 회로도 및/또는 연결표를 통 하여) · 필요한 특수한 장치나 도구에 대한 정보 · 예비 부품에 대한 정보 · 발생 가능한 잔여 위험, 특정 시험이 필요한지에 대한 표시 그리고 필요한 개인 보호 장비의 규격에 대한 정보 적용 가능한 경우, 숙련된 사람이나 훈련받은 사람에 한하여 키나 도구를 사용하도록 제한하는 것에 대한 지침 · 설정(DIP 개폐 장치, 프로그램용 매개변수 값 등) · 수리하거나 개조한 후 안전 관련 제어 기능을 검증하기 위한 정보 그리고 필요한 경우, 주기적 인 시험을 위한 정보 g) 해당하는 경우, 취급, 수송 및 저장에 대한 정보(예를 들어, 치수, 무게, 환경상 조건, 노화와 관련 한 제약) h) 구성요소의 적절한 분해 및 취급에 대한 정보(예를 들어 재활용이나 처분에 대한 정보) 18 검증 18.1 일반사항 특정 기계 형태 관련 시험은 전용 제품 표준에서 주어질 수 있다. 기계에 대한 전용 제품 표준이 없 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 83 | {}
6e8465f1-18c1-45e1-a1d0-2045ccf083d0 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 는 경우, 검증은 a), b), c) 및 h)를 항상 포함하여야 하지만 d) ~ g) 중 하나 이상을 포함할 수 있다. a) 전기 장비가 기술 문서에 따른다는 것을 검증 b) 보호 본딩 회로의 연속성 검증(18.2.2 의 시험 1) c) 전원의 자동 차단에 의한 고장 보호 조건 검증(18.2 참조) d) 절연 저항 시험(18.3 참조) e) 전압 시험(18.4 참조) f) 잔류 전압 보호(18.5 참조) g) 8.2.6 의 관련 요구사항이 충족되었는지 확인한다. h) 기능 시험(18.6 참조) 이 시험이 실시될 때 상기 수록된 순서를 준수할 것이 권장된다. 전기 장비를 개조하는 경우, 18.7 에 규정된 요구사항을 적용하여야 한다. 측정을 포함하는 검증의 경우 KS C IEC 61557 시리즈에 부합하는 측정 장비를 권장한다. 검증 결과 는 문서화되어야 한다. 18.2 전원의 자동 차단에 의한 보호 조건 검증 18.2.1 일반사항 전원의 자동 차단(6.3.3 참조) 조건은 시험으로 검증해야 한다. 시험 1 은 보호 본딩 회로의 연속성을 검증한다. 시험 2 는 TN 시스템에서 전원을 자동으로 차단하여 보호 조건을 검증한다. TN-시스템의 경우, 시험 방식은 18.2.2 와 18.2.3 에 설명되어 있고, 다른 전원 조건 관련 적용은 18.2.4 에 명시되어 있다. TT 시스템의 경우, A.2 를 참조한다. IT 시스템의 경우, IEC 60364-6 을 참조한다. 18.2.2 시험 1-보호 접지 회로의 연속성 검증 PE 단자(5.2 및 그림 4 참조) 및 각 보호 본딩 부품의 관련 지점 사이의 저항은 최대 무부하 전압이 24 V a.c. 또는 d.c.인 전기적으로 분리된 전원(예: SELV 는 IEC 60364-4-41:2005 의 414 절 참조)으로부 터 최소 0.2 A ~ 약 10 A 전류로 측정되어야 한다. 측정된 저항은 길이, 단면적 및 관련 보호 본딩 회로의 재료에 따라 예상되는 범위 내에 있어야 한다. 접지된 PELV 전원은 이 시험에서 잘못된 결과 를 생성할 수 있으므로 사용해서는 안 된다. 84 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
caaad3ea-5a9c-4edb-b1e5-b5a4d0a03b96 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 비고 연속성 시험에 사용된 전류가 클수록 특히 저내성 값(즉, 단면적이 더 크고 도체 길이가 더 적 을 경우) 시험 결과 의 정확도가 증가한다. 18.2.3 시험 2- 고장 루프 임피던스 검증 및 관련 과전류 보호 장치의 적합성 기계의 PE 단자에 연결된 보호 도체의 연결을 포함하여 각 전원 공급 장치의 연결은 검사를 통해 확인되어야 한다. 6.3.3 및 부속서 A 에 따른 전원의 자동 차단에 의한 보호 조건은 다음 두 방식을 이용하여 검증되어 야 한다. a) 고장 루프 임피던스 검증 계산에 의해 A.1.4 에 따른 측정에 의해 b) 관련 과전류 보호 구역의 설정 및 특성이 부속서 A 의 요구사항에 적합한지 확인하고 전원 구동 시스템(PDS)이 사용되는 경우 PDS 와 관련된 보호 장치의 설정 및 특성이 컨버터 제조업체 및 보호 장치 제조업체의 지침을 따르는지 확인한다. 18.2.4 TN-시스템에 시험 방식의 적용 18.2.3 의 시험 2 가 측정에 의해 수행될 때, 18.2.2 의 시험 1 에 선행되어야 한다. 비고 보호 본딩 회로의 연속성은 시험기에 위험한 상황을 야기하거나 기타 인명 위험을 야기, 또는 루프 임피던스 시험 중에 전기 장비 손상을 초래할 수 있다. 상태가 다른 기계에 필요한 시험은 표 9 를 참조한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 85 | {}
b9497bb0-26ab-46d7-a062-834e8fb2a92e | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 표 9 - TN-시스템 시험 방식의 적용 ¦ 절차 ¦ 기계 상태 ¦ 현장 검증 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ A ¦ 기계의 전기 장비, 현장에 설치 및 연결, 현장 에 설치 및 연결 후 보호 접지 회로의 연속성 이 확인되었음. ¦ 시험 1(18.2.2 참조) 및 시험 2(18.2.3 참조) 예외: 시험 2 는 필요하지 않다. 이 경우, · 현장의 연결된 기계의 보호 본딩 도체에서 시험 1 을 실시한다. 각 인입 전원 공급과 관련 보호 도체 (Protective Conductor, PE)를 기계의 PE 단 자에 연결하는 것을 검사하여 검증한다. 그 리고 전기 장비의 제조자가 이전에 계산한 고장 루프 임피던스(또는 저항)를 값을 사용 할 수 있다. 계산에 사용된 해당 도체의 단면적 및 길이 의 검증이 가능한 설치 환경 · 현장의 전원 임피던스가 전기 장비의 제조 자가 명시한 값을 초과 하지 않는다는 것을 계산이나 측정 또는 고객이 제공한 정보를 통하여 확인할 수 있다. 17.2 c)의 네 번째 목록 참조 ¦ ¦ B ¦ 표 10 에 예시로 제시된 케이블 길이를 초과 하 는 보호 본딩 회로가 있으며, 시험 1 에 의한 보호 본딩 회로의 연속성 확인(18.1 참조) 또 는 시험 2 의 측정결과 가 제공된 기계. 완전 조립된 상태로 선적을 위해 해체되지 않 은 B1) 경우 선적을 위해 해제된 상태로 공급된 B2) 경우, 여기에서 보호 접지 도체의 연속성은 해체, 수 송 및 재조립 후에 확인된다(예를 들어 플러 그/소켓 연결을 사용하여). ¦ 시험 2(18.2.3 참조) 예외: 현장의 전원 임피던스가 전기 장비의 제 조자가 명시하는 값 또는 시험 2 의 측정을 실 시하는 동안 시험전원의 임피던스를 초과 하지 않는다는 것이 계산이나 측정을 통하여 또는 고객이 제공한 정보를 통해 확인 가능한 경우, 연결 검증과 별도로 현장 시험은 요구되지 않 는다. · B1) 경우, 각 인입 전원 공급 장치 및 기계 의 PE 단자에 연결된 보호 도체; · B2) 경우, 각 인입 전원 공급 장치 및 관련 보호 도체를 기계의 PE 단자에 연결하고 배송을 위해 분리된 보호 도체의 모든 연결. ¦ ¦ C ¦ 보호 본딩 회로가 표 10 에 수록된 예의 케이 블 길이를 초과 하지 않으며, 시험 1 에 의한 보호 접지 회로의 연속성 검증 확인서가 제공 된 기계(18.1 참조). 완전 조립된 상태로 선적을 위해 해체되지 않 은 C1) 경우 선적을 위해 해제된 상태로 공급된 C2) 경우, 여기에서 보호 접지 도체의 연속성은 해체, 수 송 및 재조립 후에 확인된다(예를 들어 플러 그/소켓 연결을 사용하여). ¦ C1)과 C2) 경우, 현장 시험은 요구되지 않는 다. 플러그/소켓 조합에 의해 전원 공급기에 연결되지 않은 기계의 경우, 기계의 PE 단자 에 연결된 외부 보호 접지 도체의 정확한 연 결을 육안 검사를 통해 확인해야 한다. 사례 C2)의 경우, 설치 문서(17.4 참조)는 선 적을 위해 분리된 모든 보호 접지 도체의 연 결부를 검증할 것을 요구한다(예를 들어 육안 검사에 의해). ¦ 86 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
2940b9d0-99c5-47f5-a1ed-64e9ca5e6132 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 표 10 - TN 시스템에서 보호 장치와 부하의 최대 케이블 길이 예 ¦ 1 최대 임피던스 대 보호 장치 ¦ 2 최소 단면적 ¦ 3 최대 공칭 정격 또는 보호 장치의 설정 IN ¦ 4 퓨즈 차단 시간 5 초 ¦ 5 퓨즈 차단 시간 0.4 초 ¦ 6 소형 회로 차단기, Char.B Ia= 5xIN ¦ 7 소형 회로 차단기, char.C I= 10xIN ¦ 8 소형 회로 차단기, char.D I= 20xIN ¦ 8 조정 가능한 회로 차단기 Ia= 8xIN ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ m� ¦ mm2 ¦ A ¦ ¦ 각 보호 장치에서 부하까지의 최대 케이블 길이(m) ¦ 각 보호 장치에서 부하까지의 최대 케이블 길이(m) ¦ 각 보호 장치에서 부하까지의 최대 케이블 길이(m) ¦ 각 보호 장치에서 부하까지의 최대 케이블 길이(m) ¦ 각 보호 장치에서 부하까지의 최대 케이블 길이(m) ¦ ¦ 500 ¦ 1.5 ¦ 16 ¦ 97 ¦ 53 ¦ 76 ¦ 30 ¦ 7 ¦ 31 ¦ ¦ 500 ¦ 2.5 ¦ 20 ¦ 115 ¦ 57 ¦ 94 ¦ 34 ¦ 3 ¦ 36 ¦ ¦ 500 ¦ 4.0 ¦ 25 ¦ 135 ¦ 66 ¦ 114 ¦ 35 ¦ ¦ 38 ¦ ¦ 400 ¦ 6.0 ¦ 32 ¦ 145 ¦ 59 ¦ 133 ¦ 40 ¦ ¦ 42 ¦ ¦ 300 ¦ 10 ¦ 50 ¦ 125 ¦ 41 ¦ 132 ¦ 33 ¦ ¦ 37 ¦ ¦ 200 ¦ 16 ¦ 63 ¦ 175 ¦ 73 ¦ 179 ¦ 55 ¦ ¦ 61 ¦ ¦ 200 ¦ 25(라인/16(PE) ¦ 80 ¦ 133 ¦ ¦ ¦ ¦ ¦ 38 ¦ ¦ 100 ¦ 35(라인 )/16(PE) ¦ 100 ¦ 136 ¦ ¦ ¦ ¦ ¦ 73 ¦ ¦ 100 ¦ 50(라인 )/25(PE) ¦ 125 ¦ 141 ¦ ¦ ¦ ¦ ¦ 66 ¦ ¦ 100 ¦ 70(라인 )/35(PE) ¦ 160 ¦ 138 ¦ ¦ ¦ ¦ ¦ 46 ¦ ¦ 50 ¦ 95(라인 )/50(PE) ¦ 200 ¦ 152 ¦ ¦ ¦ ¦ ¦ 98 ¦ ¦ 50 ¦ 120(라인 )/70(PE) ¦ 250 ¦ 157 ¦ ¦ ¦ ¦ ¦ 79 ¦ ¦ ¦ 표 10 의 최대 케이블 길이 값은 아래와 같은 가정을 기반한다. 구리 도체가 있는 PVC 케이블, 도체 온도는 단락 회로 조건하에 160 °C(표 D.5 참조) 최대 16 mm2 의 선도체가 있는 케이블은 단면적이 선도체와 동일한 보호 접지 도체를 제공한다. 16 mm2 이상의 케이블은 그림과 같이 축소된 크기의 보호 접지 도체를 제공한다. 3 상 시스템, 전원 공급기 공칭 전압 400 V(Uo = 230V) - 3 열 값은 표 6 과 관련(12.4 참조) 회로 차단기의 분리 시간은 ≤0.4 초(6 열 ~ 9 열)이다. ¦ 표 10 의 최대 케이블 길이 값은 아래와 같은 가정을 기반한다. 구리 도체가 있는 PVC 케이블, 도체 온도는 단락 회로 조건하에 160 °C(표 D.5 참조) 최대 16 mm2 의 선도체가 있는 케이블은 단면적이 선도체와 동일한 보호 접지 도체를 제공한다. 16 mm2 이상의 케이블은 그림과 같이 축소된 크기의 보호 접지 도체를 제공한다. 3 상 시스템, 전원 공급기 공칭 전압 400 V(Uo = 230V) - 3 열 값은 표 6 과 관련(12.4 참조) 회로 차단기의 분리 시간은 ≤0.4 초(6 열 ~ 9 열)이다. ¦ 표 10 의 최대 케이블 길이 값은 아래와 같은 가정을 기반한다. 구리 도체가 있는 PVC 케이블, 도체 온도는 단락 회로 조건하에 160 °C(표 D.5 참조) 최대 16 mm2 의 선도체가 있는 케이블은 단면적이 선도체와 동일한 보호 접지 도체를 제공한다. 16 mm2 이상의 케이블은 그림과 같이 축소된 크기의 보호 접지 도체를 제공한다. 3 상 시스템, 전원 공급기 공칭 전압 400 V(Uo = 230V) - 3 열 값은 표 6 과 관련(12.4 참조) 회로 차단기의 분리 시간은 ≤0.4 초(6 열 ~ 9 열)이다. ¦ 표 10 의 최대 케이블 길이 값은 아래와 같은 가정을 기반한다. 구리 도체가 있는 PVC 케이블, 도체 온도는 단락 회로 조건하에 160 °C(표 D.5 참조) 최대 16 mm2 의 선도체가 있는 케이블은 단면적이 선도체와 동일한 보호 접지 도체를 제공한다. 16 mm2 이상의 케이블은 그림과 같이 축소된 크기의 보호 접지 도체를 제공한다. 3 상 시스템, 전원 공급기 공칭 전압 400 V(Uo = 230V) - 3 열 값은 표 6 과 관련(12.4 참조) 회로 차단기의 분리 시간은 ≤0.4 초(6 열 ~ 9 열)이다. ¦ 표 10 의 최대 케이블 길이 값은 아래와 같은 가정을 기반한다. 구리 도체가 있는 PVC 케이블, 도체 온도는 단락 회로 조건하에 160 °C(표 D.5 참조) 최대 16 mm2 의 선도체가 있는 케이블은 단면적이 선도체와 동일한 보호 접지 도체를 제공한다. 16 mm2 이상의 케이블은 그림과 같이 축소된 크기의 보호 접지 도체를 제공한다. 3 상 시스템, 전원 공급기 공칭 전압 400 V(Uo = 230V) - 3 열 값은 표 6 과 관련(12.4 참조) 회로 차단기의 분리 시간은 ≤0.4 초(6 열 ~ 9 열)이다. ¦ 표 10 의 최대 케이블 길이 값은 아래와 같은 가정을 기반한다. 구리 도체가 있는 PVC 케이블, 도체 온도는 단락 회로 조건하에 160 °C(표 D.5 참조) 최대 16 mm2 의 선도체가 있는 케이블은 단면적이 선도체와 동일한 보호 접지 도체를 제공한다. 16 mm2 이상의 케이블은 그림과 같이 축소된 크기의 보호 접지 도체를 제공한다. 3 상 시스템, 전원 공급기 공칭 전압 400 V(Uo = 230V) - 3 열 값은 표 6 과 관련(12.4 참조) 회로 차단기의 분리 시간은 ≤0.4 초(6 열 ~ 9 열)이다. ¦ 표 10 의 최대 케이블 길이 값은 아래와 같은 가정을 기반한다. 구리 도체가 있는 PVC 케이블, 도체 온도는 단락 회로 조건하에 160 °C(표 D.5 참조) 최대 16 mm2 의 선도체가 있는 케이블은 단면적이 선도체와 동일한 보호 접지 도체를 제공한다. 16 mm2 이상의 케이블은 그림과 같이 축소된 크기의 보호 접지 도체를 제공한다. 3 상 시스템, 전원 공급기 공칭 전압 400 V(Uo = 230V) - 3 열 값은 표 6 과 관련(12.4 참조) 회로 차단기의 분리 시간은 ≤0.4 초(6 열 ~ 9 열)이다. ¦ 표 10 의 최대 케이블 길이 값은 아래와 같은 가정을 기반한다. 구리 도체가 있는 PVC 케이블, 도체 온도는 단락 회로 조건하에 160 °C(표 D.5 참조) 최대 16 mm2 의 선도체가 있는 케이블은 단면적이 선도체와 동일한 보호 접지 도체를 제공한다. 16 mm2 이상의 케이블은 그림과 같이 축소된 크기의 보호 접지 도체를 제공한다. 3 상 시스템, 전원 공급기 공칭 전압 400 V(Uo = 230V) - 3 열 값은 표 6 과 관련(12.4 참조) 회로 차단기의 분리 시간은 ≤0.4 초(6 열 ~ 9 열)이다. ¦ 이 전제조건과 차이가 있을 경우, 고장 루프 임피던스의 전체 계산 또는 측정이 필요할 수도 있다. 자세한 설명은 KS CIEC 60228 및 KS C IEC 61200-53 을 참조한다. 18.3 절연 저항 시험 전원선과 보호 본딩 회로 사이에 직류 전압 500 V 를 인가하여 측정한 절연 저항값은 1 M� 이상이어 야 한다. 이 시험은 전체 전기 설비에서 부분별로 이루어진다. 예외: 버스바, 도체선, 도체봉 설비 또는 슬립링 조립품 등과 같은 전기 장비 일부의 최소 절연 저항 값은 보다 낮을 수 있으나, 그 값은 50 k� 이상이어야 한다. 기계의 전기 장비에 시험 중에 작동할 가능성이 있는 서지 보호 장치가 있다면 이 장치를 분리하거나 또는 시험 전압을 서지 보호 장치의 전압 보호 레벨보다 낮은 값으로 줄여야 한다[그러나 공급(상 대 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 87 | {}
539a8c31-656a-446f-a921-b8b2900ca582 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 중성) 전압의 최대 한계 첨두 값 이하가 되지 않도록]. 18.4 전압 시험 전압 시험이 수행될 때, KS C IEC 61180-2 에 부합하는 시험 장비가 사용되어야 한다. 시험 전압은 50 Hz 또는 60 Hz 의 공칭 주파수가 되어야 한다. 최대 시험 전압은 장비의 정격 공급 전압의 2 배 또는 1 000 V 값 중(어느 것이든 더 큰 값)이 되어야 한다. 최소 1 초간 전기 회로 도체와 보호 본딩 회로 사이에 최대 시험 전압이 적용되어야 한다. 방전 이 발생하지 않으면 이 요구사항이 충족된 것이다. 시험 중에 시험전압을 견딜 수 없는 정격을 가진 부품과 작동 가능성이 있는 서지 보호 장치는 시험 으로부터 분리시켜야 한다. 제품 표준에 따라 전압 시험이 수행된 부품 및 장치는 시험 중에 분리할 수도 있다. 18.5 잔류 전압 보호 적합한 경우, 이 시험은 6.2.4 의 충족을 확인하기 위해 실시한다. 18.6 기능 시험 전기 장비의 기능을 시험해야 한다. 18.7 재시험 기계의 일부 및 관련 장비가 변경 또는 개조되는 경우, 전기 장비의 재 검증 및 테스트의 필요성을 고려해야 한다. 재시험이 장비에 미치는 불리한 영향에 특히 유의 해야 한다(예를 들어, 절연 응력, 장치의 분리/재 연결). 88 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
2b527e28-15e6-42a3-a97b-da1158d776ce | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 부속서 A (규정) 자동 공급 차단에 의한 고장 보호 A.1 TN 시스템에서 제공하는 기계에 대한 고장 보호 A.1.1 일반사항 부속서 A 의 조항은 IEC 60364-4-41:2005 및 IEC 60364-6:2006 에서 파생되었다. 고장 보호는 충분히 짧은 차단 시간 내에 충전부와 노출된 도전부 또는 회로나 장비의 보호 접지 도 체 사이에 고장이 발생할 경우, 회로나 장비의 전원 공급기를 자동으로 차단하는 과전류 보호 장치에 의해 제공되어야 한다. 차단 시간은 5 초 이하일 경우, 충분히 짧은 시간으로 간주된다. 차단 시간을 보장할 수없는 경우, A.1.3 에 따라 추가 보호 본딩을 실시하여 동시에 접근 가능한 도전 부 사이에서 예상 접촉 전압이 50 V AC 또는 리프 없는 120 V DC 를 초과 하지 않도록 해야 한다. 비고 추가 보호 본딩은 예를 들어 장비에서의 화재, 열적 스트레스 방지 등의 이유로 전원 차단 필요 성을 고려해야 한다. 소켓-수구를 통한 전원 또는 소켓-수구 없이 직접 공급되는 회로의 경우, 1 등급 수동 장비 또는 휴 대용 장비(예를 들어 접근 장비용 기계에 소켓-수구, 15.1 참조)의 경우, 표 A.1 이 충분히 짧다고 간 주되는 최대 차단 시간을 규정한다. 표 A.1 - TN 시스템의 최대 차단 시간 ¦ 시스템 ¦ 50 V < Uo ≤ 120 V ¦ 50 V < Uo ≤ 120 V ¦ 120 V < Uo ≤ 230 V ¦ 120 V < Uo ≤ 230 V ¦ 230 V < Uo ≤ 400 V ¦ 230 V < Uo ≤ 400 V ¦ Uo > 400 V ¦ Uo > 400 V ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 시스템 ¦ S ¦ S ¦ S ¦ S ¦ S ¦ S ¦ S ¦ S ¦ ¦ ¦ 교류 ¦ 직류 ¦ 교류 ¦ 직류 ¦ 교류 ¦ 직류 ¦ 교류 ¦ 직류 ¦ ¦ TN ¦ 0.8 ¦ 비고 1 ¦ 0.4 ¦ 5 ¦ 0.2 ¦ 0.4 ¦ 0.1 ¦ 0.1 ¦ Uo 는 공칭 AC 또는 DC 라인 대지 전압이다. ¦ 비고 1 감전 보호 ¦ 이외의 이유로 분리가 필요할 수 있다. ¦ ¦ --- ¦ --- ¦ ¦ 비고 2 IEC 60038 에 적용된다. 비고 3 전압의 중간 값에 대해서는 위 표에서 ¦ 명시된 허용 범위 내에 있는 전압의 경우, 공칭 전압에 적합한 차단 시간이 다음으로 높은 값이 사용된다. ¦ A.1.2 과전류 보호 장치에 의한 전원의 자동 차단에 의한 보호 조건 과전류 보호 장치 및 회로 임피던스의 특성은 선 도체와 보호 접지 도체 또는 노출된 도전부 어느 곳에서든 무시할 수 있는 임피던스 고장이 발생할 경우, 규정된 시간 내에 자동 전원 차단이 발생하 는 것이다(예: ≤5 초 또는 <표 A.1 에 따른 값). 아래와 같은 일반적인 조건이 이 요구사항을 충족한다. ZsxIa<Uo 여기에서 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 89 | {}
18621c33-334d-43e0-b8f9-70bd8326f33a | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 Zs : 소스를 구성하는 고장 루프의 임피던스, 고장 및 소스 간의 보호 접지 도체와 고장지 점까지의 충전 도체 Ia : 규정된 시간 내에 차단 보호 장치를 자동 작동시키는 전류 Uo : 상접지된 공칭 전압 고장 전류에 기인하는 온도 증가에 따라 도체 저항의 증가가 다음 식과 같이 고려되어야 한다. Z,(0)≤를 x40 여기에서 Zs(n)는 정상 작동 조건에서 Zs 의 측정 또는 계산된 값이다. 고장 루프 임피던스의 값이 2 Uo/3Ia 를 초과 하는 경우 IEC 60364-6:2006 의 C.61.3.6.2 에 설명된 절차 에 따라보다 정확한 평가를 수행할 수 있다. A.1.3 50 V 미만의 토치 전압을 감소하여 보호하는 조건 A.1.2 의 요구사항을 보장할 수없는 경우 접촉 전압이 50 V 를 초과 하지 않도록 확실한 방법으로 추가 적인 보호 본딩을 선택할 수 있다. 이방법은 보호 본딩 회로(ZPE)의 임피던스가 초과 하지 않을 때 가능하다. 50 ZPE≤ xZs U。 여기에서 ZPE 는 설치 시의 장비와 기계의 PE 단자(5.2 및 그림 4 참조) 사이 또는 동시에 접근 가능 한 노출된 도전부 또는 외부 도전부 사이의 보호 본딩 회로 임피던스이다. 이 조건은 저항 RPE 를 측정하는 18.2.2 의 시험 1 방식을 이용하여 확인할 수 있다. 보호 조건은 RPE 측정 값이 초과 하지 않을 때 달성된다. 50 RPE≤ I a(5s) 여기에서 Ia(5s) : 보호 장치의 5 초 작동 전류 RPE : PE 단자(5.2 와 그림 4 참조)와 기계의 장비 간 또는 동시에 접근 가능한 노출된 도전 부 또는 외부 도전부 사이의 보호 본딩 회로 임피던스의 저항 비고 1 추가적인 보호 본딩은 고장 보호를 위한 추가 보호 조치로 간주된다. 비고 2 추가적인 보호 본딩은 전체 설치, 일부 설치 또는 기기의 품목 설치, 또는 재배치를 전제로 할 수도 있다. A.1.4 전원의 자동 차단에 의한 보호 조건 검증 A.1.4.1 일반사항 A.1.2 에 따른 전원의 자동 차단에 의한 고장 보호 조치의 유효성을 다음과 같이 확인한다. 90 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
96bc0a4b-6bbd-4237-83a1-53d7a373c4f6 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 회로 차단기의 공칭 전류 설정 및 퓨즈의 전류 정격을 육안 검사하여 관련 보호 장치의 특성을 검증 고장 루프 임피던스(Zs)를 측정. 그림 A.1 참조 예외: 고장 루프 임피던스 계산이 이용될 수 있고 설치 구조가 도체의 길이 및 단면적 검증을 허용 할 경우, 보호 접지 도체의 연속성 검증이 측정을 대신할 수도 있다. 전력 구동 시스템(PDS)이 사용되는 경우, 고장 보호를 위한 분리 시간은 PDS 의 기본 구동 모듈 (BDM)의 입력 공급 단자에서이 부속서 A 의 관련 요구사항을 충족해야 한다. 그림 A.2 를 참조 A.1.4.2 고장 루프 임피던스에 의한 측정 고장 루프 임피던스의 측정은 KS C IEC 61557-3 을 참조하는 측정 장비를 이용하여 수행되어야 한 다. 측정 결과 의 정확성에 대한 정보 및 측정 방지의 문서에 수록된 준수해야 하는 절차를 고려해 야 한다. 측정은 기계가 의도된 설치에 사용된 전원 공급기의 공칭 주파수와 동일한 주파수를 가지는 전원 공 급기에 연결될 때 수행되어야 한다. 비고 그림 A.1 은 기계의 고장 루프 임피던스 측정을 위한 일반적인 배치도를 보여준다. 전동기를 시험 중에 연결하는 것이 불가능할 경우, 시험에 사용되지 않은 2 선 도체가 개방될 수 있 다(예를 들어 퓨즈를 제거하여). 고장 루프 임피던스의 측정 값은 A.1.2 에 따라야 한다. ![image](/image/placeholder) 기계 M I 3~ PE IEC 61557-3 에 전원 공급기 따른 고장 루프 Zs L1 임피던스 시험기 L2 I L3 PE PE 전기 기기의 다른 회로로 그림 A.1 - TN 시스템에서 고장 루프 임피던스(Zs) 측정을 위한 일반적인 배열 91 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
2281c478-13f1-4616-884e-9687d626d7ac | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 ![image](/image/placeholder) 기계 전력 구동 시스템 BDM M V 3~ PE 전원 공급기 IEC 61557-3 에 Zs 따른 고장 루프 L1 L2 임피던스 시험기 L3 PE 전기 기기의 다른 회로로 · 그림 A.2 - TN 시스템의 전력 구동 시스템 회로에 대한 고장 루프 임피던스(Zs) 측정을 위한 일반적인 배열 A.2 TT-시스템이 공급하는 기계에 대한 고장 보호 A.2.1 접지에 대한 연결 모든 노출 도전부와 모든 외부 도전부를 보호 본딩 회로에 연결한다. 예외: 8.2.5 참조 5.2 의 요구사항에 더하여 기계 요소의 추가 접지 및/또는 전기 장비의 PE 도체를 제공할 수 있다. 비고 TT 시스템에서 전원 공급 시스템의 중성점이나 회로 중간점을 접지한다. 또는 중성점이나 회 로 중간점을 사용할 수 없거나 이에 접근할 수 없는 경우, 선도체를 접지한다(IEC 60364-4- 41:2005 의 411.5.1 로부터 유도). A.2.2 TT 시스템에 대한 고장 보호 A.2.2.1 일반사항 일반적으로 TT 시스템에서는 RCD 를 사용하여 고장으로부터 보호한다. 그러하지 않는 경우, 과전류 보호 장치를 사용하여 고장으로부터 보호할 수 있다. 다만 Zs 의 값을 영구적이고 확실하게 낮게 유지 한다. Zs 는 고장 루프의 임피던스이다. 비고 일부 국가에서는 과전류 보호 장치를 TT 시스템에서 고장 보호의 수단으로써 사용하는 것을 허용하지 않는다. 고장 보호 수단으로 자동 공급 차단을 사용하는 경우, 전기 장비를 설계하는 자는 다음 중 어느 하 92 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
08d0aacf-afb4-4ac3-97c8-4a94fade1666 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 나를 할 수 있다. a) IEC 60364-6 이나 설비 사용자(부속서 B 참조)가 제시한 의도에 따라 측정한 접지극 저항이나 접 지 고장 루프 임피던스의 값을 사용하여 설계 계산을 한다. b) 시리즈로 제작된 기계의 경우, 설치 의도에 적합한 접지극 저항이나 접지 고장 루프 임피던스의 값을 명시한다. 그리고 전기 장비를 설계하는 데 사용하는 접지극 저항이나 접지 고장 루프 임피던스의 값을 설치 지침에 명시한다. 또한 이러한 값은 기계에 적용될 수 있는 최대 값이라는 점을 명시한다. 전력 구동 시스템(Power Drive System, PDS)을 사용하는 경우, 고장 보호를 위한 차단 시간은 PDS 기본 구동 모듈(Basic Drive Module, BDM)의 인입 공급 단자에서 이 부속서 A 의 관련 요구사항을 준 수하여야 한다. 그림 A.4 를 참조한다. A.2.2.2 누설 전류 보호 장치(Residual Current Protective Device, RCD)에 의한 보호 RCD 를 사용하여 고장을 보호하는 경우, 다음 조건을 충족하여야 한다. a) 표 A.2 에서 규정하는 차단 시간 b) RAxIAn≤50V 여기에서 RA : 각 노출 도전부에 대한 접지극 저항과 보호 도체 저항의 합 I△n : RCD 의 정격 잔류 작동 전류 예외: 배전 회로와 표 A.2 의 대상이 아닌 회로에 대하여 1 초 이하의 차단 시간을 허용한다. 비고 1 고장 임피던스가 미량이 아닌 경우, 고장 보호를 제공한다. 비고 2 RCD 를 식별하여야 하는 경우, IEC 60364-5-53:2001, 535.3 의 정보를 참조한다. 비고 3 표 A.2 에 따른 단락 시간은 RCD 의 정격 잔류 작동 전류보다 훨씬 더 큰 고유 잔류 고장 전 류에 대한 것이다(일반적으로 5IAn). 비고 4 RA 의 정의 는 IEC 60364-4-41 에서 비롯한다. 이 표준에서 RA 의 정의 에 있는 "접지극"은 IEC 60050-195:1998 의 195-02-30 이 정의 하는 바의 "접지 귀로 경로"를 의미한다. A.2.2.3 과전류 보호 장치에 의한 보호 과전류 보호 장치를 사용하는 경우, 다음 조건을 충족하여야 한다. ZsxIa≤Uo 여기에서 Zs : 다음으로 구성된 고장 루프의 임피던스 전원 고장 지점까지의 선도체 각 노출 도전부의 보호 도체 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 93 | {}
39863f03-5a8c-47df-8243-97c602293b8d | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 ¦ ¦ 접지 도체 설치 접지극과 전원의 접지극 ¦ ¦ --- ¦ --- ¦ ¦ Ia ¦ : 표 A.2 에서 명시하는 시간 안에 차단 장치를 자동으로 작동시키는 전류 ¦ 예외: 표 A.2 의 대상이 아닌 회로의 경우, 1 초 이하의 단락 시간을 허용한다. U。 : 접지 전압에 대한 공칭 직류선이나 교류선 표 A.2 에서 명시하는 최장 단락 시간을 32A 이하의 회로에 적용한다. 32 A 이상 회로의 경우, 최장 단락 시간은 1 초를 초과 하지 않는다. 표 A.2 - TT 시스템에 대한 최장 차단 시간 ¦ 시스템 ¦ 50 V < U。 ≤ 120 V S ¦ 50 V < U。 ≤ 120 V S ¦ 120 V < U。 ≤ 230 V S ¦ 120 V < U。 ≤ 230 V S ¦ 230 V < U。 ≤ 400 V S ¦ 230 V < U。 ≤ 400 V S ¦ U。 > 400 V S ¦ U。 > 400 V S ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ 교류 ¦ 직류 ¦ 교류 ¦ 직류 ¦ 교류 ¦ 직류 ¦ 교류 ¦ 직류 ¦ ¦ TT ¦ 0.3 ¦ 비고 ¦ 0.2 ¦ 0.4 ¦ 0.07 ¦ 0.2 ¦ 0.04 ¦ 0.1 ¦ ¦ TT 시스템에서 과전류 보호 우, 표 A.1 에서 명시하는 최장 U。는 접지 전압까지의 교류선 또는 ¦ 장치가 차단하고 모든 기타 도전부를 보호 본딩 회로에 연결하는 경 차단 시간을 사용할 수 있다. 공칭 직류선이다. ¦ ¦ --- ¦ --- ¦ ¦ 비고 감전 ¦ 보호 이외의 사유로 차단이 고려될 수 있다. ¦ A.2.3 잔류 전류 보호 장치를 사용한 자동 공급 차단을 통한 보호의 검증 TT 시스템에서 잔류 전류 보호 장치를 사용하여 공급을 자동으로 차단함으로써 고장으로부터 보호하 는 것을 다음과 같이 검증한다. · 트립 값에 대하여 정격 잔류 전류와 잔류 전류 보호 장치의 차단 시간 값을 검사한다. · 잔류 전류 보호 장치를 관련 IEC 표준에 따라 시험하였는지를 검증한다. · 잔류 전류 보호 장치와 보호 본딩 회로에 대한 연결을 검사한다. A.2.4 고장 루프 임피던스(Zs)의 측정 고장 루프 임피던스 측정은 KS C IEC 61557-3 을 부합되는 측정 장비로 실시하여야 한다. 측정 결과 의 정확성에 대한 정보와 특정 장비의 문서에서 명시하는 절차를 고려한다. 목표 설비에서 공급의 공칭 주파수의 99 % ~ 101 %인 공급에 연결된 전기 장비를 사용하여 고장 루 프 임피던스를 측정한다. 비고 1 그림 A.3 은 기계에서 고장 루프 임피던스를 측정하기 위한 일반적인 배치를 보여준다. 시험 중 전동기에 연결할 수 없는 경우, 시험에서 사용되지 않는 두 개의 선도체를 개방할 수 있다. 비고 2 그림 A.4 는 전력 구동 시스템을 사용하는 경우, 고장 루프 임피던스를 측정하기 위한 일반적 인 배치를 보여준다. 고장 루프 임피던스의 측정 값은 A.2.2.3 을 따른다. 94 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
48527b9a-5416-417a-b232-ad3c496ba463 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 비고 3 잔류 전류 보호 장치의 성능을 검증하는 것과 접지 고장 루프 임피던스를 측정하는 것에 대 한 정보를 IEC 60364-6 에서 확인할 수 있다. 기계 ![image](/image/placeholder) M 3~ PE 전원 공급기 IEC 61557-3 에 L1 따른 고장 루프 Zs L2 임피던스 시험기 L3 PE PE 전기 기기의 다른 회로로 그림 A.3 - TT 시스템에서 고장 루프 임피던스(Zs) 측정을 위한 일반적인 배열 ![image](/image/placeholder) 기계 전력 구동 시스템 BDM M 3~ PE 전원 공급기 IEC 61557-3 에 Zs 따른 고장 루프 L1 L2 임피던스 시험기 L3 PE 전기 기기의 다른 회로로 그림 A.4 - TT 시스템의 전력 구동 시스템 회로에 대한 고장 루프 임피던스(Zs) 측정을 위한 일반적인 배열 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 95 | {}
e32e19dd-c14c-41b2-b286-532bb71bec7e | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 부속서 B (참고) 기계의 전기 장비용 설문 이 요구사항 양식을 사용하면 기본 조건 및 추가 사용자 요구사항에 대한 사용자와 공급자 간의 정 보 교환을 용이하게 하며 특히 현장 조건이 가능한 경우 기계의 전기 장비(4.1 참조)를 적절하게 설 계, 적용 및 활용할 수 있다. 부속서 B 는 또한 연속적으로 제조된 기계에 대한 내부 체크리스트 역할을 할 수 있다. ¦ 제조자/공급자의 성명 ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 사용자의 성명 ¦ ¦ ¦ ¦ ¦ 공급/주문 번호 ¦ ¦ ¦ 날짜 ¦ ¦ 기계 형식 ¦ 유형 지정 ¦ 유형 지정 ¦ 일련번호 ¦ ¦ 1. 특수 조건(1 절 참조) ¦ ¦ ¦ ¦ ¦ a) 기계가 실외에서 사용되는가? ¦ 예/아니요 ¦ ¦ 예일 경우, 규격 ¦ ¦ b) 기계가 폭발성 또는 인화성 물질을 사용, 처리, 생산하는가? ¦ 예/아니요 ¦ ¦ 예일 경우, 규격 ¦ ¦ c) 잠재적으로 폭발성 또는 인화성 대기에서 사용되 는가? ¦ 예/아니요 ¦ ¦ 예일 경우, 규격 ¦ ¦ d) 기계가 특정 물질을 생산 또는 소비할 때 특수 한 위험이 존재하는가? ¦ 예/아니요 ¦ ¦ 예일 경우, 규격 ¦ ¦ e) 기계가 광산에서 사용되는가? ¦ 예/아니요 ¦ ¦ 예일 경우, 규격 ¦ ¦ 2. 전원 공급 및 관련 조건(4.3 참조) ¦ ¦ ¦ ¦ ¦ a) 예상 전압 변동률(±10% 초과 의 경우) ¦ ¦ ¦ ¦ ¦ b) 예상 주파수 변동률(±2% 초과 의 경우) ¦ 연속 ¦ ¦ ¦ ¦ c) 전원 요구사항의 증가에 따라 요구되는 전기 장 비의 예상되는 변경사항 표시 ¦ ¦ ¦ ¦ ¦ d) 전기 장비가 그런 조건하에 작동을 유지해야 할 경우, 4 절에 규정된 것보다 오래일 경우에 공급 기의 전압 차단을 규정 ¦ ¦ ¦ ¦ ¦ 3. 물리적인 환경 및 작동 조건(4.4 참조) ¦ ¦ ¦ ¦ ¦ a) 전자기 환경(4.4.2 참조) ¦ 주택, 상업 또는 경공업 환경 ¦ 공업 환경 ¦ ¦ ¦ 특수 EMC 조건 또는 요구사항 ¦ ¦ ¦ ¦ ¦ b) 주위 공기 온도 범위 ¦ ¦ ¦ ¦ ¦ c) 습도범위 ¦ ¦ ¦ ¦ ¦ d) 고도 ¦ ¦ ¦ ¦ ¦ 단기 e) 특수 환경 조건(부식성 대기, 먼지, 습식 환경) ¦ ¦ ¦ ¦ ¦ f) 방사 ¦ ¦ ¦ ¦ ¦ g) 진동, 충격 ¦ ¦ ¦ ¦ 96 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
1a9a617b-8e37-4753-bc84-7b77b11dd70b | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 ¦ h) 특수 설치 및 작동 요구사항(예: 내염성 케이블 및 도체) ¦ ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ i) 수송 및 저장(예를 들어 4.5 에 규정된 범위를 벗 어나는 온도) ¦ ¦ ¦ ¦ ¦ ¦ k) 크기, 무게 또는 포인트로드와 관련된 제한 ¦ ¦ ¦ ¦ ¦ ¦ 4. 유입 전원 공급기 ¦ ¦ ¦ ¦ ¦ ¦ 각 전원 규정 ¦ ¦ ¦ ¦ ¦ ¦ a) 공칭 전압(V) ¦ a.c. ¦ ¦ d.c. ¦ ¦ ¦ ¦ a.c.의 경우 상수 ¦ ¦ 주파수(Hz) ¦ ¦ ¦ 전기 장비 연결 지점의 공급 소스 임피던스(2) 값 ¦ ¦ ¦ ¦ ¦ ¦ 전기 장비 연결 지점에서 예상되는 단락 전류(kA r.m.s.) (항목 2. 참조) ¦ ¦ ¦ ¦ ¦ ¦ b) 배전 시스템의 접지 형태(KS C IEC 60364-1 참 조) ¦ TN[한 점을 직접 접지시키고, 이 점 에 보호 접지 도체 (PE)를 접속한 계 통] ¦ ¦ TT[한 점을 직접 접지시키고, 보호 접지 도체(PE)를 이 점과 접속하지 않은 계통] ¦ ¦ ¦ ¦ IT(직접 접지하지 않은 계통) ¦ ¦ ¦ ¦ ¦ IT 시스템의 경우 전기 장비 공급업체가 절연 모니 터링/고장 위치를 제공하는가? ¦ 예 ¦ ¦ 아니요 ¦ ¦ ¦ c) 전기 장비에 중성(N)선의 접속 여부(5.1 참조) ¦ 예 ¦ ¦ 아니요 ¦ ¦ ¦ 허용되는 최대 전류 (A) ¦ ¦ ¦ ¦ ¦ ¦ d) 공급 차단 장치 ¦ ¦ ¦ ¦ ¦ ¦ 중성 도체(N)의 차단이 요청되는가? ¦ 예 ¦ ¦ 아니요 ¦ ¦ ¦ 중성 도체(N)의 링크가 허용되는가? ¦ 예 ¦ ¦ 아니요 ¦ ¦ ¦ 차단 장치의 형태는? ¦ ¦ ¦ ¦ ¦ ¦ e) 외부 보호(PE) 도체의 단면적 및 재질 ¦ ¦ ¦ ¦ ¦ ¦ f) 설치 시 RCD 가 제공되는가? ¦ 예/아니요 ¦ ¦ 예일 경우, 유형 및 정격 누설 작 동 전류 ¦ ¦ ¦ 5. 감전 보호(6 절 참조) ¦ ¦ ¦ ¦ ¦ ¦ a) 장비의 정상 작동 중에 외함 내부에 접근할 수 있는 작업자의 등급은 다음 중 어느 것인가? ¦ 기술자 ¦ ¦ 훈련받은 자 ¦ ¦ ¦ b) 잠금 문 또는 덮개용의 자물쇠와 열쇠의 구비 여부(6.2.2 참조) ¦ 예 ¦ ¦ 아니요 ¦ ¦ ¦ 잠금 장치 유형 ¦ ¦ ¦ ¦ ¦ ¦ 기본 잠금 장치 (키 실린더 제외) 공급 및 설치 ¦ ¦ ¦ ¦ ¦ ¦ 공급 및 설치되는 키 실린더 ¦ ¦ ¦ ¦ ¦ ¦ 6. 장비의 보호(7 절 참조) ¦ ¦ ¦ ¦ ¦ ¦ a) 사용자 또는 전기 장비 공급 업체가 공급 도체 및 공급 도체에 대한 과전류 보호 여부(7.2.2 참조) ¦ ¦ ¦ ¦ ¦ ¦ 과전류 보호 장치의 형식 및 정격 ¦ ¦ ¦ ¦ ¦ ¦ b) 3 상 교류 전동기의 직입 기동 전력(출력)의 한계 값(최대값)(kW) ¦ ¦ ¦ ¦ ¦ ¦ c) 전동기 과부하 감지 장치의 수를 줄일 수 있는 지 여부(7.3.2 참조) ¦ 예 ¦ ¦ 아니요 ¦ ¦ ¦ d) 과전압 보호가 제공되는가? ¦ 예/아니요 ¦ ¦ 예일 경우, 규격 ¦ ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. 97 | {}
b3697586-c3ba-4e73-97e4-f13063166a04 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 ¦ 7. 작동 ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 무선 제어 설비에서, 유효한 신호가 없는 상태에서 기계의 자동 정지 신호가 초기화될 때까지의 시간 지연에 대하여 기술 ¦ ¦ ¦ ¦ ¦ 8. 조작자 인터페이스 및 기계 장착 제어 장치(10 절 참조) ¦ ¦ ¦ ¦ ¦ 특수한 색 선호도 (예: 기존의 기계류와 의 일치를 위해) ¦ 기동 ¦ 정지 ¦ ¦ ¦ ¦ 기타 ¦ ¦ ¦ ¦ 9. 제어장치 ¦ ¦ ¦ ¦ ¦ 외함의 보호 등급(11.3 참조) 또는 특수 조건 ¦ ¦ ¦ ¦ ¦ 10. 배선(13 절 참조) ¦ ¦ ¦ ¦ ¦ 도체에 사용되는 특수한 식별 방식이 있는가? (13.2.1 참조) ¦ 예 ¦ 아니요 ¦ ¦ ¦ 형식 ¦ ¦ ¦ ¦ ¦ 11. 부속물 및 조명(15 절 참조) ¦ ¦ ¦ ¦ ¦ a) 특정한 형식의 소켓-수구가 요구되는가? ¦ 예 ¦ 아니요 ¦ ¦ ¦ '예'일 경우, 어떤 형식? ¦ ¦ ¦ ¦ ¦ b) 국부 조명이 설치된 기계의 ¦ 최고 허용 전압(V) ¦ 조명 회로 전압을 전원공급장치로부터 직접 받을 수 없는 경우, 선호 전압 명시 ¦ ¦ ¦ 12. 표식, 경고 및 참조 지정(16 절 참조) ¦ ¦ ¦ ¦ ¦ a) 기능 식별(16.3 참조) ¦ ¦ ¦ ¦ ¦ 규격: ¦ ¦ ¦ ¦ ¦ b) 새김/특수 표시 ¦ 전기 장비에? ¦ 어떤 언어로? ¦ ¦ ¦ c) 준수해야 하는 특정 지역 규정 ¦ 예 ¦ 아니요 ¦ ¦ ¦ 있다면, 어떤 것? ¦ ¦ ¦ ¦ ¦ 13. 기술 문서(17 절 참조) ¦ ¦ ¦ ¦ ¦ a) 기술 문서(17.1 참조) ¦ 어떤 매체에서? ¦ 어떤 언어로? ¦ ¦ ¦ ¦ 파일 형식? ¦ ¦ ¦ ¦ b) 사용 지침(17.1 참조) ¦ 어떤 매체에서? ¦ 어떤 언어로? ¦ ¦ ¦ ¦ 파일 형식? ¦ ¦ ¦ ¦ c) 사용자가 구비해야 하는 덕트, 개방 케이블 트 레이 또는 케이블 지지대의 크기, 위치 및 용도 ¦ ¦ ¦ ¦ ¦ d) 설치 현장으로 특수 기계 또는 제어 장치 어셈 블리 등의 운송 시에 영향을 미치는 크기나 중량 에 특별한 제한이 있다면 표시: ¦ 최대 크기 ¦ 최대 중량 ¦ ¦ ¦ e) 특별히 제조되는 기계의 경우, 당해 기계의 부 하 시험 인증서 유무 ¦ 예 예 ¦ 아니요 ¦ ¦ ¦ f) 기타 기계의 경우, 견본의 부하 시험 인증서 유무 ¦ ¦ 아니요 ¦ ¦ 98 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
1939604a-e537-4ca8-b035-40566a2e5c18 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 부속서 C (참고) 이 표준에 포함된 기계의 예시 다음 목록은 전기 장비에서 이 표준에 따라야 하는 기계의 예이다. 이 목록이 전체적이지 않지만, 본 문에서의 기계류의 정의 와 부합된다(3.1.40 참조). 이 표준은 IEC 60335 시리즈의 범위 내의 가정용 및 유사 가정용 제품에는 적용할 필요가 없다. 금속 세공 기계류 금속 절단 기계 금속 성형 기계 플라스틱 및 고무 기계류 사출 성형 기계 압출 성형 기계 송풍 성형 기계 열경화성 성형 기계 분쇄기 ¦ 목재 기계류 ¦ 점검/시험 기계류 ¦ ¦ --- ¦ --- ¦ ¦ - 목공 기계 ¦ 조정 측정 기계 ¦ ¦ 적층 기계 ¦ 제조 과정 계량기 ¦ ¦ 제재용 기계 ¦ ¦ 조립 기계 압축기 재료 취급 기계 포장 기계 로봇 펠릿타이저/디펠릿타이저 컨베이어 포장 및 수축 포장 운송 기계 저장 및 수선기 세탁기 방직 기계 가열 및 통풍기 냉각 및 공조기 가죽/모조 가죽 제품 및 신발 제조기 절단 및 천공기 초벌 작업기, 마모기, 닦는 기계, 미세 조정 및 솔질하는 기계 인쇄기 식품 기계류 반죽 기계 믹서기 파이 및 타트 기계 고기 가공 기계 릴 및 슬릿 기계 연마기, 재단기, 폴더 인쇄, 종이 및 선반 기계류 폴더함 접착기 종이 및 선반 성형 기계 신발 성형 기계 마감 기계 건설 및 건물 재료 기계류 굴착기 콘크리트 배칭 기계 벽돌 제조기 석재, 도자기 및 유리 가공 기계 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 99 | {}
8136383d-1456-4005-8cdb-17c91bb7cf96 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 호이스트 기계류(IEC 60204-32 참조) 크레인 목재 가공 기계 - 호이스트 금속 가공 기계 작업자 운반용 기계류 이동 기계류 에스컬레이터 작업자 운송용 삭도. 예: 의자 리프트, 스키 리프트 승강기 동력 작동문 레저용 기계류 박람회장 및 놀이기구 양수기 농림 및 임업 기계 휴대 기계류 승강용 리프트 포크 리프트 운반차 건설용 기계 고온 금속 처리용 기계 제혁 기계류 다중 롤러기 밴드나이프기 수압 제혁기 채광 및 채석기 100 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
62d55fdb-5c2d-4075-9184-520a892c6c29 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 부속서 D (참고) 전기 장비의 도체와 케이블의 허용 전류 및 과전류 보호 D.1 일반사항 이 부속서는 표 6(12 절 참조)에서 주어진 조건을 변경해야 하는 경우, 도체 굵기의 선정에 대한 추가 적인 정보를 제공하기 위한 것이다(표 6 의 비고 참조). D.2 일반 작동 조건 D.2.1 주위 공기 온도 표 6 에 제시된 PVC 절연 도체에 대한 허용 전류 용량은 +40 °C 의 주위 공기 온도를 기준으로 한 것이며, 기타 온도 조건일 경우 설치자는 다음 표 D.1 에 주어진 계수를 사용하여 값을 보정하여야 한다. 고무 절연 케이블의 보정 계수는 제조자가 제공한다. 표 D.1 - 보정 계수 ¦ 주위 공기 온도 °C ¦ 보정 계수 ¦ ¦ --- ¦ --- ¦ ¦ 30 ¦ 1.15 ¦ ¦ 35 ¦ 1.08 ¦ ¦ 40 ¦ 1.00 ¦ ¦ 45 ¦ 0.91 ¦ ¦ 50 ¦ 0.82 ¦ ¦ 55 ¦ 0.71 ¦ ¦ 60 ¦ 0.58 ¦ ¦ 비고 보정 계수는 IEC 60364-5-52 를 근거로 한다. 정상 조건하의 PVC 최대 온도는 70 °C 이다. ¦ 비고 보정 계수는 IEC 60364-5-52 를 근거로 한다. 정상 조건하의 PVC 최대 온도는 70 °C 이다. ¦ D.2.2 설치 방법 기계에서, 그림 D.1 은 장비의 외함과 각 부품 사이의 도체 및 케이블 설치 방법의 대표적인 예이다 (문자는 IEC 60364-5-52 에 따라 사용됨). 방법 B1: 도체의 고정 및 보호용의 전선관(3.1.9)과 케이블 트렁킹 설비(3.1.6)의 사용(단심 케이블) 방법 B2: B1 과 동일(다심 케이블용) 방법 C: 덕트나 전선관 없이 벽에 설치되는 케이블 방법 E: 수평 또는 수직 개방형 케이블 트레이에 설치되는 케이블(3.1.5) 101 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
d74401e2-fefb-4209-aebf-4270225c59f1 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 B2 ![image](/image/placeholder) B1 a) 전선관 및 케이블 트렁킹 설비에 설치된 도체/단심 케이블 b) 전선관 및 케이블 트렁킹 설비에 설치된 케이블 C c) 벽에 설치된 케이블 ≥ 0.3De ≥ 0.3De E d) 개방형 케이블 트레이에 설치된 케이블 그림 D.1 - 도체/케이블의 수와 무관한 도체 및 케이블 설치 방법 102 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
ca0dc827-c967-430a-9545-dad4cef1ff12 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 D.2.3 그룹화(grouping) 보다 많은 부하의 케이블 또는 도체 쌍이 설치될 경우, 표 6 에 수록된 Iz 값 또는 표 D.2 나 표 D.3 에 따라 제조자가 제공한 값을 감소시킨다. 비고 Iz 의 Ib<30 %를 가진 회로는 값을 감소시킬 필요가 없다. 표 D.2 - 군 분류에 따른 Iz 로부터 감소 계수 ¦ 설치 방법 (그림 D.1 참조) (비고 3 참조) ¦ 케이블/도체의 수 ¦ 케이블/도체의 수 ¦ 케이블/도체의 수 ¦ 케이블/도체의 수 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 설치 방법 (그림 D.1 참조) (비고 3 참조) ¦ 2 ¦ 4 ¦ 6 ¦ 9 ¦ ¦ B1(도체 또는 단일 코어 케이블) 및 B2(다 심 케이블) ¦ 0.80 ¦ 0.65 ¦ 0.57 ¦ 0.50 ¦ ¦ C 케이블 갭이 없는 단층 ¦ 0.85 ¦ 0.75 ¦ 0.72 ¦ 0.70 ¦ ¦ E 케이블 간 갭이 없이 하나의 천공 트레 이 위에 있는 단층 ¦ 0.88 ¦ 0.77 ¦ 0.73 ¦ 0.72 ¦ ¦ E 전과 동일하지만 2~ 3 트레이, 각 트레이 수직 간격 300 mm(비고 4 참조) ¦ 0.86 ¦ 0.76 ¦ 0.71 ¦ 0.66 ¦ ¦ 설치 방법 무관한, 제어 회로 쌍≤0.5 mm2 ¦ 0.76 ¦ 0.57 ¦ 0.48 ¦ 0.40 ¦ 비고 1 이 계수는 케이블, 모두 동일한 부하, 회로 자체는 대칭 부하 허용 가능한 최대 작동 온도가 동일한 절연 도체 또는 케이블의 회로 그룹 비고 2 동일한 계수가 적용된다. 2 개 또는 3 개의 단심 케이블 그룹에 다심 케이블에 비고 3 IEC 60364-5-52:2009 에서 인용한 계수 비고 4 천공 케이블 트레이는 베이스 면적 30 % 이상을 구멍이 차지하고 있는 트레이(IEC 60364-5- 52:2009 에서 인용) 표 D.3 - 10 mm2 이하 다심 케이블의 Iz 로부터 감소 계수 ¦ 부하 도체 또는 쌍의 수 ¦ 도체(≥1 mm2) (비고 3 참조) ¦ 쌍 (0.25 mm2~ 0.75 mm2) ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ ¦ 1.0 ¦ ¦ 3 ¦ 1.0 ¦ - ¦ ¦ 5 ¦ 0.75 ¦ 0.39 ¦ ¦ 7 ¦ 0.65 ¦ 0.34 ¦ ¦ 10 ¦ 0.55 ¦ 0.29 ¦ ¦ 24 ¦ 0.40 ¦ 0.21 ¦ ¦ 비고 1 동일 부하의 비고 2 다심 ¦ 도체/쌍이 있는 다심 케이블에 해당 그룹화에 관해서는 표 D.2 의 ¦ 감소 계수를 참조 ¦ 케이블의 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 비고 3 IEC 60364-5-52:2009 에서 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 인용한 계수 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 103 | {}
47ad56f7-2def-4c9e-957e-4ef767010148 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 D.2.4 도체의 분류 표 D.4 - 도체의 분류 ¦ 등급 ¦ 설명 ¦ 용도 및 응용 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ 구리 또는 알루미늄 도체 ¦ 고정 설비용 ¦ ¦ 2 ¦ 스트랜드 구리 또는 알루미늄 도체 ¦ 고정 설비용 ¦ ¦ 5 ¦ 가느다란 소선이 많은 구리 도체 ¦ 진동이 있는 기계 설비용, 가동 부품 접속용 ¦ ¦ 6 ¦ 5 등급 이상 유연한 매우 가느다란 구리선 ¦ 움직임이 잦은 기계용 ¦ ¦ 비고 KS C IEC 60228 에서 인용 ¦ 비고 KS C IEC 60228 에서 인용 ¦ 비고 KS C IEC 60228 에서 인용 ¦ D.3 과부하 보호 기능을 제공하는 보호 장치와 도체 간의 협조 그림 D.2 는 과부하 보호 기능을 제공하는 보호 장치의 매개변수와 도체 매개변수 간의 관계를 보여 준다. ![image](/image/placeholder) 설계 전류 Ib 전류 용량 Iz 1.45xIz 도체의 매개변수 IA 트래핑 전류 12 의 보호 장치의 수락 범위 매개변수 공칭 전류 또는 전류 설정 In 그림 D.2 - 도체 및 보호 장치의 매개변수 케이블의 정확한 보호는 케이블의 과부하를 방지하는 보호 장치(예: 과전류 보호 장치, 전동기 과부 하 보호 장치)가 아래 두 조건을 충족시킬 것을 요구한다. 1b≤Inz 12≤ 1.45 ≤Iz 여기에서 Ib : 회로가 설계되는 전류 Iz : 특정 설치 조건하에 표 6 에 따른 연속 사용을 위한 케이블의 연속 사용 허용 전류(A) - 온도, Iz 감소, 표 D.1 참조 - 그룹화, Iz 감소, 표 D.2 참조 다심 케이블,Iz 감소, 표 D.3 참조 In : 보호 장치의 공칭 전류 104 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
10db07ad-e65f-431e-90d7-e06f1ec8009b | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 비고 1 조정 가능한 보호 장치의 경우, 공칭 전류 In 이 선택된 전류 설정 값이다. I2 : 규정된 시간 내에 보호 장치의 효과 적인 작동을 보장하는 최소 전류(예: 최대 63 A 보호 장치의 경우, 1 시간) 보호 장치의 효과 적인 작동을 보장하는 전류 I2 는 제품 표준에 수록되거나 제조자가 제공할 수 있다. 비고 2 전동기 회로 도체의 경우 도체의 과부하 보호 기능은 전동기의 과부하 보호에 의해 제공될 수 있는 반면, 단락 회로 보호 기능은 단락 방지 장치에 의해 제공된다. 과부하 및 단락 방지 기능을 모두 제공하는 장치가 도체 과부하 보호를 위한 이 항의 설명 에 준하여 사용될 경우, 모든 경우에 전체 보호 기능을 보장하는 것은 아니고(예를 들어 전 류가 I2 이하일 경우의 과부하) 또한 그 결과 가 반드시 경제적인 해결책이 되는 것도 아니 다. 따라서 전류가 I2 이하인 과부하가 발생할 가능성이 있는 경우, 그런 장치가 적합하지 않을 수 있다. D.4 도체의 과전류 보호 모든 도체는 당해 도체가 최고 허용 온도에 도달하기 전에 케이블에 흐르는 단락 전류를 차단하도록 모든 충전 도체에 설치된 보호 장치에 의하여 과전류(7.2 참조)에 대하여 보호할 수 있다. 비고 중성 도체의 경우, 7.2.3 의 세 번째 단락 참조 표 D.5 - 정상 조건 및 단락 조건하에 허용 가능한 최대 도체 온도 ¦ 절연 형태 ¦ 정상 조건하의 최대 온도 °C ¦ 단락 조건하의 최대 도체 온도 a °C ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ PVC ¦ 70 ¦ 160 ¦ ¦ 고무 ¦ 60 ¦ 200 ¦ ¦ XLPE ¦ 90 ¦ 250 ¦ ¦ EPR ¦ 90 ¦ 250 ¦ ¦ SIR ¦ 180 ¦ 350 ¦ ¦ 비고 최대 도체 온도가 200 °C 이상일 경우, 주석 또는 연동(bare copper) 도체가 둘 다 적합하지 않다. 200 °C 이상일 경우, 은 도금이나 니켈 도금 구리 도체가 적합하다. a 이 값은 단열 동작이 5 초 이상 지속되지 않는다는 전제를 기준으로 한다. ¦ 비고 최대 도체 온도가 200 °C 이상일 경우, 주석 또는 연동(bare copper) 도체가 둘 다 적합하지 않다. 200 °C 이상일 경우, 은 도금이나 니켈 도금 구리 도체가 적합하다. a 이 값은 단열 동작이 5 초 이상 지속되지 않는다는 전제를 기준으로 한다. ¦ 비고 최대 도체 온도가 200 °C 이상일 경우, 주석 또는 연동(bare copper) 도체가 둘 다 적합하지 않다. 200 °C 이상일 경우, 은 도금이나 니켈 도금 구리 도체가 적합하다. a 이 값은 단열 동작이 5 초 이상 지속되지 않는다는 전제를 기준으로 한다. ¦ 실제적으로, 7.2 의 요구사항은 전류 I 에서 보호 장치가 t(여기에서 t<5 초)를 넘지 않는 시간 내에 회 로를 차단할 수 있을 때에는 충족되게 되는 것이다. 시간 t 의 값은 다음 식을 이용하여 구할 수 있다. t=(kxS/I)2 여기에서 S : 도체의 단면적(mm2) I : 단락 전류의 교류 실훗값(r.m.s.)(A) k : 다음과 같은 재료로 절연된 구리 도체의 계수 PVC= 115 고무=141 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 105 | {}
0956dac4-cb27-4a19-a293-7e6b9961ebff | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 SiR= 132 XLPE= 143 EPR= 143 D.5 평형 3 상 시스템에 대한 고조파 전류의 영향 고조파를 포함한 부하 전류로 단상 부하를 공급하는 회로의 경우 회로의 중성 도체가 추가로 로드될 수 있으며 해당 케이블의 전류 전달 용량을 줄여야 할 수 있다. IEC 60364-5-52:2009 의 부속서 E 를 참조 106 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
da514640-4eec-4d1b-b8de-896b2de84970 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 부속서 E (참고) 비상 조작 기능의 설명 비고 이 개념은 여기서 단지 이 개념에 대한 이해를 제공하기 위해 수록된 것이다. · 비상 조작 비상 조작은 다음 사항의 개별적 또는 조합을 포함한다. 비상 정지 비상 기동 비상 전원 차단 비상 전원 투입 · 비상 정지 위험한 공정 또는 이동을 멈추게 하기 위한 비상 조작 · 비상 기동 위험한 상태의 제거 또는 회피하기 위한 공정 또는 이동을 시작하기 위한 비상 조작 · 비상 전원 차단 감전 또는 기타 전기적 위험과 관련된 경우, 설비의 일부 또는 전체에서 전기 에너지의 공급을 차 단하기 위한 비상 조작 · 비상 전원 투입 비상 상태 시 사용하기 위한 설비의 일부에 전기 에너지의 공급을 하기 위한 비상 조작 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 107 | {}
0e4938e5-ddeb-43b7-9945-880f37ac3852 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 부속서 F (참고) 이 표준의 사용 지침 이 표준은 특정 기계의 전기 장비에 적용할 수도 있고, 적용하지 않을 수도 있는 많은 일반 요구사 항에 대하여 규정하고 있다. 이 표준의 그 어떠한 조건도 없이 간단히 인용하는 것은 충분치 않다. 선택은 이 표준의 모든 요구사항에서 이루어질 필요가 있다. 제품 표준의 표준이군 또는 단위 표준 (ISO 및 CEN 의 형식 C)이 없는 경우에 이를 준비하는 기술 위원회 또는 공급자는 다음에 의하여 이 표준을 사용하는 것이 바람직하다. a) 인용에 의해서 b) 관련 조항에 주어진 요구사항으로부터 가장 적합한 선택사항의 선정 c) 전기 장비의 특수 요구사항이 다른 표준에 의하여 적용 가능할 경우, 필요하다면 일부 조항의 수정 선정된 선택사항 및 수정은 위험성 평가를 통해 기계에서 요구하는 보호 수준에 역영향을 주어서는 안 된다. 위의 세 가지 원칙 a), b) 및 c)를 적용할 때에는 다음에 의하는 것이 바람직하다. - 이 표준의 관련 조항 인용 · 적용 가능한 선택사항을 표시하고 이를 충족 · 특정 기계 또는 장비 요구사항의 수정 또는 확장 당해 표준에 의하여 충분히 만족되는 전기 장비 요구사항에 대하여 관련 표준을 직접 인용 다음과 같은 경우 특정 전문 지식이 필요할 수 있다. 기계의 필요한 위험성 평가 실행 - 이 표준의 모든 요구사항의 해독 및 이해 다른 방법이 주어진다면, 이 표준으로부터 적용 가능한 요구사항의 선택 이 표준의 요구사항과 다르거나 여기에 포함되지 않는 다른 요구사항이나 특수 요구사항의 확인, 기계 및 기계의 사용에 의하여 결정된 기타 요구사항의 확인 이러한 특수 요구사항의 정확한 기술 이 표준의 그림 1 은 전형적인 기계의 블록도로 이 업무의 시작점으로 활용할 수 있고, 이것은 특정 요구사항/장비 다루는 조항에서 나타낸다. 그러나 이 표준의 복잡한 문서 및 표 F.1 은 특정 기계에 선택사항을 적용하는 데 도울 수 있으며, 기타 관련 표준에서 참조할 수 있다. 108 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
9b585904-f98d-4d9e-8091-740b30064da8 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 표 F.1 - 적용 선택사항 ¦ 항목 ¦ 조항 ¦ i) ¦ ii) ¦ iii) ¦ iv) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 적용범위 ¦ 1 절 ¦ ¦ x ¦ ¦ ¦ ¦ 일반 요구사항 ¦ 4 절 ¦ x ¦ x ¦ x ¦ KS B ISO 12100 ¦ ¦ 장비의 선정 ¦ 4.2.2 ¦ ¦ x ¦ x ¦ IEC 61439 시리즈 ¦ ¦ 전원 차단(분리) 장치 ¦ 5.3 ¦ x ¦ ¦ ¦ ¦ ¦ 적용 제외되는 회로 ¦ 5.3.5 ¦ x ¦ ¦ x ¦ KS B ISO 12100 ¦ ¦ 불시 기동, 분리 방지 ¦ 5.4, 5.5, 5.6 ¦ x ¦ x ¦ x ¦ ISO 14118 ¦ ¦ 감전 보호 ¦ 6 절 ¦ x ¦ ¦ ¦ IEC 60364-4-41 ¦ ¦ 비상 조작 ¦ 9.2.3.4 ¦ x ¦ ¦ x ¦ KS B ISO 13850 ¦ ¦ 양수 조작 제어 ¦ 9.2.3.8 ¦ x ¦ x ¦ ¦ ISO 13851 ¦ ¦ 무선 제어 ¦ 9.2.4 ¦ x ¦ x ¦ x ¦ IEC 62745 ¦ ¦ 결함 시 제어 기능 ¦ 9.4 ¦ x ¦ x ¦ x ¦ KS B ISO 12100 KS B ISO 13849(모든 부) IEC 62061 ¦ ¦ 위치 감지기 ¦ 10.1.4 ¦ x ¦ x ¦ x ¦ KS B ISO 14119 ¦ ¦ 조작자 인터페이스 장치의 색상 및 표지 ¦ 10.2, 10.3, 10.4 ¦ x ¦ x ¦ ¦ KS C IEC 60073 KS C IEC 61310(모든 부) ¦ ¦ 비상 정지 ¦ 9.2.3.4.2 ¦ x ¦ ¦ ¦ KS B ISO 13850 ¦ ¦ 비상 정지 장치 ¦ 10.7 ¦ x ¦ x ¦ ¦ IEC 60947-5-5 ¦ ¦ 비상 개폐 장치 ¦ 10.8 ¦ x ¦ ¦ ¦ IEC 60364-5-53 ¦ ¦ 제어 장치 -오염 물질에 대 한 보호 등 ¦ 10.1.3, 11.3 ¦ x ¦ x ¦ x ¦ KS C IEC 60529 ¦ ¦ 도체의 식별 ¦ 13.2 ¦ x ¦ x ¦ ¦ KS C IEC 62491 ¦ ¦ 검증 ¦ 18 절 ¦ x ¦ x ¦ x ¦ IEC 60364-6 ¦ ¦ 추가적인 사용자 요구사항 ¦ 부속서 B ¦ ¦ x ¦ x ¦ ¦ ¦ TN 시스템의 오류 보호 ¦ 부속서 A (A.1) ¦ x ¦ ¦ ¦ IEC 60364-4-41 IEC 60364-6 ¦ ¦ TT 시스템의 오류 보호 ¦ 부속서 A (A.2) ¦ x ¦ ¦ ¦ IEC 60364-4-41 IEC 60364-6 ¦ 이 표준의 조항에서 고려하여야 할 조치는 다음과 같다(x 로 나타냄). i) 주어진 조치에서 선정 ii) 추가 요구사항 iii) 다른 요구사항 iv) 관련된 기타 표준의 예 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 109 | {}
3e535902-aa02-4835-a4ea-83fe653945e4 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 부속서 G (참고) 대표적인 도체 단면적의 비교 표 G.1 은 AWG 의 도체 단면적을 제곱밀리미터, 제곱인치, 서큘러 밀과 비교한 것이다. 표 G.1 - 도체 크기의 비교 ¦ 전선 크기 ¦ 게이지 번호 ¦ 단면적 ¦ 단면적 ¦ 20 °C 에서 구리의 직류 저항 값 ¦ 서큘러 밀 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ mm2 ¦ (AWG) ¦ mm2 ¦ in2 ¦ km 당 요 ¦ ¦ ¦ 0.2 ¦ ¦ 0.196 ¦ 0.000 304 ¦ 91.62 ¦ 387 ¦ ¦ ¦ 24 ¦ 0.205 ¦ 0.000 317 ¦ 87.60 ¦ 404 ¦ ¦ 0.3 ¦ ¦ 0.283 ¦ 0.000 438 ¦ 63.46 ¦ 558 ¦ ¦ ¦ 22 ¦ 0.324 ¦ 0.000 504 ¦ 55.44 ¦ 640 ¦ ¦ 0.5 ¦ ¦ 0.500 ¦ 0.000 775 ¦ 36.70 ¦ 987 ¦ ¦ ¦ 20 ¦ 0.519 ¦ 0.000 802 ¦ 34.45 ¦ 1 020 ¦ ¦ 0.75 ¦ ¦ 0.750 ¦ 0.001 162 ¦ 24.80 ¦ 1 480 ¦ ¦ ¦ 18 ¦ 0.823 ¦ 0.001 272 ¦ 20.95 ¦ 1 620 ¦ ¦ 1.0 ¦ ¦ 1.000 ¦ 0.001 550 ¦ 18.20 ¦ 1 973 ¦ ¦ ¦ 16 ¦ 1.31 ¦ 0.002 026 ¦ 13.19 ¦ 2 580 ¦ ¦ 1.5 ¦ ¦ 1.500 ¦ 0.002 325 ¦ 12.20 ¦ 2 960 ¦ ¦ ¦ 14 ¦ 2.08 ¦ 0.003 228 ¦ 8.442 ¦ 4 110 ¦ ¦ 2.5 ¦ ¦ 2.500 ¦ 0.003 875 ¦ 7.56 ¦ 4 934 ¦ ¦ ¦ 12 ¦ 3.31 ¦ 0.005 129 ¦ 5.315 ¦ 6 530 ¦ ¦ 4 ¦ ¦ 4.000 ¦ 0.006 200 ¦ 4.700 ¦ 7 894 ¦ ¦ ¦ 10 ¦ 5.26 ¦ 0.008 152 ¦ 3.335 ¦ 10 380 ¦ ¦ 6 ¦ ¦ 6.000 ¦ 0.009 300 ¦ 3.110 ¦ 11 841 ¦ ¦ ¦ 8 ¦ 8.37 ¦ 0.012 967 ¦ 2.093 ¦ 16 510 ¦ ¦ 10 ¦ ¦ 10.000 ¦ 0.001 550 ¦ 1.840 ¦ 19 735 ¦ ¦ ¦ 6 ¦ 13.3 ¦ 0.020 610 ¦ 1.320 ¦ 26 240 ¦ ¦ 16 ¦ ¦ 16.000 ¦ 0.024 800 ¦ 1.160 ¦ 31 576 ¦ ¦ ¦ 4 ¦ 21.1 ¦ 0.032 780 ¦ 0.829 5 ¦ 41 740 ¦ ¦ 25 ¦ ¦ 25.000 ¦ 0.038 800 ¦ 0.734 0 ¦ 49 338 ¦ ¦ ¦ 2 ¦ 33.6 ¦ 0.052 100 ¦ 0.521 1 ¦ 66 360 ¦ ¦ 35 ¦ ¦ 35.000 ¦ 0.054 200 ¦ 0.529 0 ¦ 69 073 ¦ ¦ ¦ 1 ¦ 42.4 ¦ 0.065 700 ¦ 0.413 9 ¦ 83 690 ¦ ¦ 50 ¦ ¦ 47.000 ¦ 0.072 800 ¦ 0.391 0 ¦ 92 756 ¦ 110 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
ab6a4ea5-34b3-4f48-a6a5-072b7a2a9139 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 20 °C 이상의 온도에서 내성은 다음 공식을 이용한다. R= R/[1 +0.003 93(t - 20)] 여기에서 RI : 20 °C 에서의 내성 R : t°C 에서의 내성 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 111 | {}
aae064d0-498b-415e-93e3-92ab27216780 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 부속서 H (참고) 전자기적 영향을 저감하는 조치 H.1 정의 다음 용어와 정의 를 이 부속서에만 적용한다. H.1.1 기구 하나의 기능적 구성단위로서 상업적으로 사용 가능한 완성된 장치 또는 그것의 조합, 최종 사용자를 위한 이러한 기구는 전자기 장해를 발생시키기 쉬우며 또는, 기구의 성능이 그러한 장해에 의해 영 향을 받기 쉽다. H.1.2 고정 설비 정해진 위치에서 영구적으로 사용될 목적으로 설치된 여러 형태의 기구, 해당되는 경우, 조립된 다른 장치들의 특정한 조합 H.2 일반사항 이 부속서 H 는 전자기 내성을 개선하고 전자기 장해의 발생을 저감하기 위한 권고사항을 제공한다. EMC 의 경우, 기계용 전기 장비는 기구이거나 고정 설비인 것으로 간주한다. 전기적 안전성과 전자 기 적합성을 위한 요구사항이 서로 다른 경우, 전기적 안전성이 항상 우선한다. 전자기 장해(Electromagnetic Interference, EMI)는 프로세스 모니터링, 제어 및 자동화 시스템을 교란 하거나 손상을 줄 수 있다. 낙뢰, 개폐 동작, 단락 및 다른 전자기 현상으로 인한 전류는 과전압과 전자기 장해를 초래할 수 있다. 이러한 영향은 예를 들어 다음과 같은 경우에 발생할 수 있다. · 큰 도전성 루프가 존재하는 경우 · 다른 전기배선 시스템이 공통 경로에 설치되는 경우, 예를 들어, 전원, 통신, 제어 또는 신호 케이블 높은 전류 변화율(di/dt)을 갖는 큰 전류를 전송하는 케이블은 다른 케이블에 과전압을 유도할 수 있 다. 이것은 연결된 전기 설비에 영향 또는 손상을 줄 수 있다. H.3 전자기 장해(EMI)의 완화 H.3.1 일반사항 전기 장비를 설계하는 데 있어 아래에서 설명하는 조치를 고려하여야 한다. 이를 통하여 전기 장비 에 미치는 전자기 영향을 저감한다. 112 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b3e2bf03-d16d-45cb-b1e1-f9c94d58a1aa | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 적절한 EMC 표준의 요구사항이나 관련 제품 표준의 EMC 요구사항을 충족하는 전기 장비를 사용하 여야 한다. H.3.2 EMI 를 저감하는 조치 다음 조치는 전자기 영향을 저감한다. a) 전도된 전자기 현상과 관련된 전자기 적합성을 개선하기 위해서 전자기 영향에 민감한 설비를 위 한 서지보호장치 또는 필터의 설치가 권고된다. b) 케이블의 전도성 시스(예를 들어 외장, 스크린)를 보호 본딩 회로에 결합하여야 한다. c) H.4 에 따라 회로 분리를 유지하면서 전력, 신호 및 데이터 회로 배선에 대하여 공통의 경로를 선 정함으로써 유도성 루프를 방지하여야 한다. d) 전력 케이블을 다른 신호 또는 데이터 케이블과 분리하여야 한다. e) 전력 케이블과 신호 또는 데이터 케이블이 서로 교차하여야 하는 경우, 서로 직각으로 교차하여 야 한다. f) 보호 도체로 유도되는 전류를 저감하기 위해서 동심도체 케이블을 사용한다. g) 전동기와 컨버터 사이의 전기적 연결에 대칭 다심 케이블(예를 들어, 별도의 보호 도체를 포함하 는 차폐 케이블)을 사용한다. h) 제조자가 권고하는 EMC 요구사항을 충족하는 신호 및 데이터 케이블을 사용한다. i) 차폐 신호 또는 데이터 케이블을 사용하는 경우, 접지된 신호 케이블이나 데이터 케이블의 차폐 를 통하여 흐르는 전류를 저감하도록 주의 한다. 우회 도체를 설치할 필요가 있을 수 있다. 그림 H.1 을 참조한다. ![image](/image/placeholder) 차폐 보강을 위한 분로 도체 그림 H.1 - 차폐 보강을 위한 분로 도체 비고 기계 구성요소의 등전위 본딩이 양호한 경우, 우회 도체에 대한 필요가 줄어든다. j) 등전위 본딩 연결은 가능한 한 짧게 해서 가능한 한 임피던스를 낮게 해야 하고 해당되는 경우 보다 높은 주파수를 전도하기 위해 편조하여야 한다. k) 전기 장비가 정확하게 동작하기 위하여 전위 수준의 기준 전압을 요구하는 경우, 이러한 기준 전 압은 기능 접지도체에 의해서 제공된다. 높은 주파수에서 동작하는 장비의 경우, 가능한 한 연결 을 짧게 유지한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 113 | {}
b8d04a1c-02fe-4757-8393-d2083a1b3d03 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 H.4 케이블의 이격 및 분리 동일한 경로를 공유하는 전력 케이블과 데이터 케이블은 이 부속서 H 의 요구사항에 따라 설치하여야 한다. 적용 가능한 다른 정보가 없는 경우, 전력 케이블과 데이터 케이블 사이의 케이블 이격거리는 표 H.1 과 그림 H.2 에 따라야 한다. 표 H.1 - 그림 H.2 가 보여주는 금속 트레이를 사용한 최소 이격거리 ¦ 금속 트레이를 사용하지 않는 분리 ¦ 메시형 금속 트레이 ¦ 펀칭형 금속 트레이 ¦ 바닥밀폐형 금속 트레 이 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ≥200 mm ¦ ≥150 mm ¦ ≥100 mm ¦ 0 mm ¦ ¦ ¦ 그물망 크기가 50 mm x 100 mm 인(사다리를 제외한) 용접 그물망 강철 통에 해당하는 차폐 성 능(DC-100 MHz). 비록 벽 두께가 1 mm 미만이고/미만이거나 균등하게 분배한 천공 영역이 20 %를 초과 하더라도, 강철 트레이를 사용하여 이 차폐 성능을 달성한다. 벽 ¦ ¦ --- ¦ --- ¦ ¦ ¦ 두께가 최소 1 mm 이고 균등하게 분배한 천공 영역이 20 % 이하인 강철 트레이에 해당하는 차폐 성능(DC-100 MHz). 차폐 전력 케이블을 사용하여 이런 차폐 성능을 달성한다. 금속 트레이 내에 있는 케이블 부분은 금속 트레이의 상부에서 아래로 10mm 미만이어야 한다. ¦ ¦ ¦ 벽 두께가 최소 1 mm 인 강철 도관에 해당하는 차폐 성능(DC-100 MHz). 칸막이/분리기가 제공 하는 분리에 더하여 명시한 바와 같이 분리한다. ¦ 표 H.1 에서 명시하는 최소 이격 요구사항은 인접한 케이블 트레이나 케이블 트렁킹 시스템을 수평 또는 수직으로 분리하는 데 적용한다. 데이터 케이블과 전력 케이블이 서로 교차하여야 하고 필수 최소 이격을 유지할 수 없는 경우, 그것들의 교차각은 요구되는 해당 이격거리 만큼의 길이에 대해 서 90 도로 유지하여야 한다. 그림 H.2 와 그림 H.3 은 이격 및 분리의 예를 보여준다. 114 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
5e7c02b6-3572-4de5-8d59-9afddc7850de | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 ![image](/image/placeholder) 거리에 대해서는 표 H.1 을 참조한다. = 전력 공급 케이블 = 데이터 케이블 = 보조 회로 = 민감 회로(예를 들어, 측정) 그림 H.2 - 수직 이격 및 분리의 예 ![image](/image/placeholder) 거리에 대해서는 표 H.1 을 참조한다. 그림 H.3 - 수평 이격 및 분리의 예 케이블 트레이나 케이블 트렁킹 시스템 내의 사용 가능한 공간은 합의 한 수량의 추가 케이블을 설치 하기에 충분하여야 한다(부속서 B 참조). 케이블 다발의 높이는 아래 그림 H.4 에서 보여주는 바와 같 이 케이블 트레이나 케이블 트렁킹 시스템의 측벽 높이보다 더 낮아야 한다. 케이블 트렁킹 시스템 의 중첩된 뚜껑을 통하여 전자기 호환성을 개선한다. U 자형 케이블 트레이의 경우, 두 모서리 근처에서 자기장이 감소한다. 이런 이유로 측벽을 높게 할 것을 권고한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 115 | {}
09c2b8c2-7f6f-45ae-bddb-136e4ee038e4 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 음영 부분은 차폐 성능을 나타낸다 ![image](/image/placeholder) 음영 부분은 차폐 성능을 나타낸다 권장하지 않는다 권장하지 않는다 권장한다 권장한다 그림 H.4 - 금속 케이블 트레이 내 케이블의 배치 전자기 호환성을 제공하기 위한 금속 케이블 트레이나 케이블 트렁킹 시스템은 양 종단에서 국소 등 전위본딩시스템에 항상 연결되어야 한다. 예를 들어, 50 m 를 초과 하는 긴 거리의 경우, 등전위 본딩 시스템에 추가로 연결하는 것을 권장한다. 등전위본딩시스템의 모든 연결부는 임피던스가 낮아야 한다. 여러 개의 금속 케이블 트레이나 케이블 트렁킹 시스템으로 구성되는 경우, 인접한 요소 사이에 유 효한 본딩을 사용하여 연속성을 보장하도록 주의 하여야 한다. 금속 부분의 형태는 그 전체 길이에 걸쳐 차폐의 연속성이 이루어져야 한다. 모든 상호 접속부분은 낮은 임피던스를 가져야 한다. 그림 H.5 를 참조한다. ¦ a ¦ 미준수 ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ b ¦ 준수 ¦ ¦ ¦ ¦ 권장 ¦ ¦ 그림 H.5 - 금속 케이블 트레이나 케이블 트렁킹 시스템의 연결 금속 케이블 트렁킹 시스템에 대하여 금속 덮개를 사용하는 경우, 전체 길이에 걸쳐 덮개를 사용할 것을 권장한다. 전체 길이에 대하여 사용할 수 없는 경우, 10cm 미만의 짧은 연결 장치(예를 들어 편 조 또는 그물망 끈)를 사용하여 최소한 양 종단에서 덮개를 케이블 트레이에 연결한다. 116 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
454501e1-4f94-46c5-b915-a5cd2d2bdef2 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 그림 H.6 은 방화벽이 설치된 벽과 금속 케이블 트레이가 교차하는 것을 보여준다. 금속 케이블 트레 이가 건물 구조물을 통과 하기 위하여 차단되어야 하는 경우, 낮은 임피던스의 상호접속이 두 금속 부분 사이에 제공하여야 한다. 방화벽에 대한 규정은 EMC 에 대한 고려사항보다 더 우선한다. ![image](/image/placeholder) B 미준수 준수 그림 H.6 - 방화벽에서 금속 케이블 트레이의 단절 H.5 병렬 전원에 의한 기계의 전원 공급 기계류가 병렬 전원에 의해서 전력을 공급받는 경우, KS C IEC 60364-1 을 참조한다. H.6 전력 구동 시스템(PDS)를 사용하는 경우, 공급 임피던스 너무 높은 전원 임피던스에 PDS 의 연결은 전도성 방사 문제를 야기할 수 있다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 117 | {}
1d114fa0-a43a-4ca0-96b5-1160bcf6f9a3 | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 부속서 (참고) 문서/정보 문서와 정보에 적용할 수 있는 표준의 목록은 표 I.1 과 같다. 국제적으로 표준화된 여러 문서에 대한 간단한 정의 는 공개적으로 사용할 수 있는 데이터베이스인 IEC 61355 DB(http://std.iec.ch/iec61355)에서 규정하는 바와 같다. 표 I.1 - 적용할 수 있는 문서/정보 ¦ 전기 장비에 대한 정보의 종류 ¦ 권장 표준 ¦ ¦ --- ¦ --- ¦ ¦ 구성 원칙 ¦ KS C IEC 81346-1: 산업시스템, 설비 · 장치 및 산업제 품 - 구성 원리 및 참조 지정 - 제 1 부: 기본 규칙 ¦ ¦ 문서 구성 ¦ KS C IEC 62023: 기술 정보 및 문서의 구성 (비고 참조) ¦ ¦ 부품 목록 ¦ KS C IEC 62027: 부품 목록 준비 ¦ ¦ 문서 목록 ¦ KS C IEC 62027: 부품 목록 준비 ¦ ¦ 전기 장비의 속성에 대한 시방서 ¦ KS C IEC/PAS 62569-1: 제품 정보의 일반 명세 - 제 1 부: 원칙 및 방법 ¦ ¦ 취급, 전달 및 저장에 대한 지침 ¦ KS C IEC 82079-1: 사용설명서의 작성 - 구조, 내용 및 표현 - 제 1 부: 일반적인 원칙 및 상세 요구사항 ¦ ¦ 설치, 건립, 현장 조립, 해체에 대한 지침 ¦ KS C IEC 82079-1: 사용설명서의 작성 - 구조, 내용 및 표현 - 제 1 부: 일반적인 원칙 및 상세 요구사항 ¦ ¦ 사용에 대한 지침 ¦ KS C IEC 82079-1: 사용설명서의 작성 - 구조, 내용 및 표현 - 제 1 부: 일반적인 원칙 및 상세 요구사항 ¦ ¦ 운용 및 유지 보수에 대한 지침 ¦ KS C IEC 82079-1: 사용설명서의 작성 - 구조, 내용 및 표현 - 제 1 부: 일반적인 원칙 및 상세 요구사항 ¦ ¦ 기준 명칭 ¦ KS C IEC 81346-1: 산업시스템, 설비 · 장치 및 산업 제품 - 구성 원리 및 참조 지정 - 제 1 부: 기본 규칙 및 IEC 81346-2: 산업시스템, 설비 · 장치 및 산업제품 구성 원리 및 참조 지정 - 제 2 부: 객체의 분류 및 클래스에 대한 코드 ¦ ¦ 단자 명칭 ¦ KS C IEC 61666: 산업시스템, 설비 · 장치 및 산업제 품 - 시스템 내의 터미널 식별 ¦ ¦ 케이블 및 코어의 명칭 ¦ KS C IEC 62491: 산업시스템, 설비, 장치 및 산업제 품 - 케이블과 코어의 표시라벨 ¦ ¦ 회로도 ¦ KS CIEC 61082-1: 전기공학 분야에서 사용되는 문서 준비 - 제 1 부: 일반적인 요구사항 ¦ ¦ 장비의 배열 및 전체적인 치수 ¦ KSCIEC 61082-1: 전기공학 분야에서 사용되는 문서 준비 - 제 1 부: 일반적인 요구사항 ¦ 118 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
635be9ae-13fd-4ee8-9d24-9dd08b805bab | KSCIEC60204-1_KR | KS CIEC 60204-1:2016 표 I.1 - 적용할 수 있는 문서/정보(계속) ¦ 전기 장비에 대한 정보의 종류 ¦ 권장 표준 ¦ ¦ --- ¦ --- ¦ ¦ 상호연결도, 단자 목록, 케이블 목록, 케이블 트레이 배열 ¦ KS CIEC 61082-1: 전기공학 분야에서 사용되는 문서 준비 - 제 1 부: 일반적인 요구사항 ¦ ¦ 명시한 기간에 대한 예비 부품 목록 ¦ KS C IEC 62027: 부품 목록 준비 ¦ ¦ 매개변수(예를 들어 변환기) 목록 ¦ (해당 표준 없음) ¦ ¦ 도구 목록 ¦ KS C IEC 82079-1: 사용설명서의 작성 - 구조, 내용 및 표현 - 제 1 부: 일반적인 원칙 및 상세 요구사항 ¦ ¦ 식별 시스템 ¦ KS C IEC 62507-1: 명확한 정보교환을 위한 식별체계 - 요구사항 - 제 1 부: 원칙 및 방법 ¦ ¦ 비고 KSCIEC 62023 은 간단한 장비의 경우 모든 정보를 하나의 문서에 포함시킬 수 있도록 한다. ¦ 비고 KSCIEC 62023 은 간단한 장비의 경우 모든 정보를 하나의 문서에 포함시킬 수 있도록 한다. ¦ 119 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
1a1176a3-96b1-4739-b4d0-407b51ec3a5b | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 참고문헌 KS C IEC 60034-5, 회전기기 - 제 5 부: 회전기기 외함의 보호등급 분류(IP 코드) KS C IEC 60034-11, 회전기기 - 제 11 부: 내장 열보호기 IEC 60038:2009, IEC standard voltages KS C IEC 60050, 국제전기기술용어 (<http://www.electropedia.org>에서 이용 가능) IEC 60073:2002, Basic and safety principles for man-machine interface, marking and identification Coding principles for indicators and actuators 비고 IEC 60073:2002 에 대응되는 KS 는 2009 년에 고시된 KS C IEC 60073 이다. KS C IEC 60085, 전기 절연 - 내열성 평가와 표시 IEC 60204-11:2000, Safety of machinery Electrical equipment of machines Part 11: Requirements for equipment for voltages above 1 000 V AC or 1 500 V DC and not exceeding 36 kV 비고 IEC 60204-11:2000 에 대응되는 KS 는 2003 년에 고시된 KS C IEC 60204-11 이다. IEC 60204-31:2013, Safety of machinery - Electrical equipment of machines - Part 31: Particular safety and EMC requirements for sewing machines, units and systems IEC 60204-32:2008, Safety of machinery Electrical equipment of machines - Part 32: Requirements for hoisting machines IEC 60204-33:2009, Safety of machinery Electrical equipment of machines - Part 33: Requirements for semiconductor fabrication equipment 비고 IEC 60204-33:2009 에 대응되는 KS 는 2010 년에 고시된 KS C IEC 60204-33 이다. IEC 60216(all parts), Electrical insulating materials Thermal endurance properties KS C IEC 60228:2004, 절연 케이블용 도체 KS C IEC 60269-1:2006, 저전압 퓨즈 - 제 1 부: 일반 요구사항 KS C IEC 60287(모든 부), 전기 케이블 - 정격 전류의 계산 KS C IEC 60320-1, 가정용 및 유사 용도의 기기용 커플러 - 제 1 부: 일반 요구사항 IEC 60332(all parts), Tests on electric and optical fibre cables under fire conditions IEC 60335(all parts), Household and similar electrical appliances - Safety IEC 60364(all parts), Low-voltage electrical installations KS C IEC 60447:2004, 인간과 기계 간 인터페이스(MMI), 표시, 식별의 기본 및 안전 원칙 - 작동 원칙 IEC TR 60755, General requirements for residual current operated protective devices IEC 60757:1983, Code for designation of colours IEC TR 60890, A method of temperature-rise verification of low-voltage switchgear and controlgear assemblies by calculation IEC 60909-0:2001, Short-circuit currents in three-phase a.c. systems - Part 0: Calculation of currents 비고 IEC 60909-0:2001 에 대응되는 KS 는 2014 년에 고시된 KS C IEC 60909-0 이 다. IEC TR 60909-1:2002, Short-circuit currents in three-phase a.c. systems Part 1: Factors for the 120 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
1744225c-99dd-47a9-be45-4c1264d3d2ca | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 calculation of short-circuit currents according to IEC 60909-0 IEC 60947-1:2007, Low-voltage switchgear and controlgear Part 1: General rules 비고 IEC 60947-1:2007 에 대응되는 KS 는 2014 년에 고시된 KS C IEC 60947-1 이다. KS C IEC 60947-4-1, 저전압 개폐장치 및 제어장치 - 제 4-1 부: 접촉기 및 모터기동기 - 전자식 접촉기 및 모터기동기 IEC 60947-5-2:2007, Low-voltage switchgear and controlgear Part 5-2: Control circuit devices and switching elements - Proximity switches 비고 IEC 60947-5-2:2007 에 대응되는 KS 는 2012 년에 고시된 KS C IEC 60947-5-2 이다. KS C IEC 60947-5-8, 저전압 개폐장치 및 제어장치 - 제 5-8 부: 제어회로장치 및 개폐소자 - 3 단 스위치 IEC 60947-7-1:2009, Low-voltage switchgear and controlgear Part 7-1: Ancillary equipment Terminal blocks for copper conductors. 비고 IEC 60947-7-1:2009 에 대응되는 KS 는 2014 년에 고시된 KS C IEC 60947-7-1 이다 IEC 61000-5-2:1997, Electromagnetic compatibility (EMC) - Part 5: Installation and mitigation guidelines Section 2: Earthing and cabling 비고 IEC 61000-5-2:1997 에 대응되는 KS 는 2014 년에 고시된 KS C IEC 61000-5-2 이다. IEC 61000-6-1:2005, Electromagnetic compatibility (EMC) Part 6-1: Generic standards: Immunity for residential, commercial and light-industrial environments 비고 IEC 61000-6-1:2005 에 대응되는 KS 는 2014 년에 고시된 KS C IEC 61000-6-1 이다. IEC 61000-6-2:2005, Electromagnetic compatibility (EMC) Part 6-2: Generic standards Immunity for industrial environments 비고 IEC 61000-6-2:2005 에 대응되는 KS 는 2014 년에 고시된 KS C IEC 61000-6-2 이다. IEC 61000-6-3:2006, Electromagnetic compatibility (EMC) Part 6-3: Generic standards Emission standard for residential, commercial and light-industrial environments IEC 61000-6-4:1997, Electromagnetic compatibility (EMC) Part 6: Generic standards - Section 4: Emission standard for industrial environments 비고 IEC 61000-6-4:1997 에 대응되는 KS 는 2002 년에 고시된 KS C IEC 61000-6-4 이다. KS C IEC 61082-1:2014, 전기공학 분야에서 사용되는 문서준비 - 제 1 부: 일반적인 요구사항 IEC 61084 (all parts), Cable trunking and ducting systems for electrical installations IEC 61175, Industrial systems, installations and equipment and industrial products Designation of signals KS C IEC 61180 (모든 부), 저전압 장비에 대한 고전압 시험방법 IEC TR 61200-53:1994, Electrical installation guide Part 53: Selection and erection of electrical equipment Switchgear and controlgear 비고 IEC TR 61200-53:1994 에 대응되는 KS 는 2011 년에 고시된 KS C IEC 61200-53 이다. IEC 61355, Collection of standardized and established document kinds (available at http://std.iec.ch/iec61355) IEC 61496-1:2004, Safety of machinery Electro-sensitive protective equipment - Part 1: General requirements and tests IEC 61506, Industrial-process measurement and control - Documentation of application software KS C IEC 61557(모든 부), 교류 1 000 V 및 직류 1 500 V 이하 저압 배전 계통의 전기적 안전성 - 보 호 수단의 시험, 측정 또는 감시용 장비 KS C IEC 61558-2-2, 전력용 변압기, 전원장치, 리액터 및 유사기기의 안전 - 제 2-2 부: 제어변압기 121 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
cc677706-1219-4b91-8e3a-41c544cdf058 | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 와 제어변압기 통합 전원장치의 개별요구사항 및 시험 KS C IEC 61558-2-16, 공급전압 1100 V 이하인 변압기, 리액터, 전원장치 및 유사제품안전 제 2-16 부: 스위치 모드 전원장치용 변압기와 스위치 모드 전원장치의 시험 및 개별 요구사항 IEC 61643-12:2008, Low-voltage surge protective devices Part 12: Surge protective devices connected to low-voltage power distribution systems Selection and application principles KS C IEC 61666, 산업시스템, 설비 · 장치 및 산업제품 - 시스템 내의 터미널 식별 IEC 61800 (all parts), Adjustable speed electrical power drive systems IEC TR 61912-1:2007, Low-voltage switchgear and controlgear Overcurrent protective devices Part 1 : Application of short-circuit ratings IEC 62020, Electrical accessories Residual current monitors for household and similar uses (RCMs) KS C IEC 62027:2011, 부품 목록 준비 IEC 62305-1:2010, Protection against lightning Part 1: General principles 비고 IEC 62305-1:2010 에 대응되는 KS 는 2012 년에 고시된 KS C IEC 62305-1 이다. IEC 62305-4:2010, Protection against lightning - Part 4: Electrical and electronic systems within structures 비고 IEC 62305-4:2010 에 대응되는 KS 는 2012 년에 고시된 KS C IEC 62305-4 이다. KS C IEC 62491, 산업시스템, 설비, 장치 및 산업제품 - 케이블과 코어의 표시라벨 KS C IEC 62507-1, 명확한 정보교환을 위한 식별체계 - 요구사항 - 제 1 부: 원칙 및 방법 IEC 62745, Safety of machinery Requirements for the interfacing of cableless controllers to machinery KS C IEC/PAS 62569-1, 제품 정보에 관한 일반 명세 - 제 1 부: 원칙 및 방법 KS C IEC 81346-1:2009, 산업시스템, 설비·장치 및 산업제품 - 구성 원리 및 참조 지정 - 제 1 부: 기본 규칙 IEC 81346-2:2009, Industrial systems, installations and equipment and industrial products Structuring principles and reference designations Part 2: Classification of objects and codes for classes KS C IEC 82079-1:2012, 사용설명서의 작성 - 구조, 내용 및 표현 - 제 1 부: 일반적인 원칙 및 상세 요구 사항 IEC Guide 106:1996, Guide for specifying environmental conditions for equipment performance rating KS S ISO 3864-1:2011, 그래픽 심볼 - 안전색 및 안전 표지 - 제 1 부: 안전 표지 및 안전 표시의 디자인 원칙 KS S ISO 7000:2014, 장비에 이용되는 그래픽 심볼 - 등록된 심볼 KS B ISO 12100:2010, 기계안전 - 설계 일반원칙 - 위험성평가와 위험성감소 ISO 13732-1, Ergonomics of the thermal environment Methods for the assessment of human responses to contact with surfaces Part 1: Hot surfaces ISO 13851:2002, Safety of machinery Two-hand control devices Functional aspects and design principles 비고 ISO 13851:2002 에 대응되는 KS 는 2003 년에 고시된 KS B ISO 13851 이다. ISO 14118:2000, Safety of machinery Prevention of unexpected start-up 비고 ISO 14118:2000 에 대응되는 KS 는 2002 년에 고시된 KS B ISO 14118 이다. ISO 14122-1:2001, Safety of machinery Permanent means of access to machinery Part 1: Choice of fixed means of access between two levels ISO 14122-1:2001/AMD1:2010 122 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
d06f55c1-8cd3-4ef6-b04f-4dbd1bca5dda | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 비고 ISO 14122-1:2001 에 대응되는 KS 는 2014 년에 고시된 KS B ISO 14122-1 이다. ISO 14122-2:2001, Safety of machinery Permanent means of access to machinery Part 2: Working platforms and walkways ISO 14122-2:2001/AMD1:2010 비고 ISO 에 대응되는 KS 는 2014 년에 고시된 KS B ISO 다. 14122-2:2001 14122-2 이 ISO 14122-3:2001, Safety of machinery Permanent means of access to machinery Part 3: Stairs, stepladders and guard-rails ISO 14122-3:2001/AMD1:2010 비고 ISO 14122-3:2001 에 대응되는 KS 는 2014 년에 고시된 KS B ISO 14122-3 이다. CENELEC HD 516 S2, Guide to use of low-voltage harmonized cables EN 50160:2010, Voltage characteristics of electricity supplied by public electricity networks EN 50160:2010/AMD1:2015 UL 508A,UL Standard for Safety for Industrial Control Panels, second Edition, 2013 revised 2014. NFPA 79, Electrical Standard for Industrial Machinery, 2015 edition. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 123 | {}
f25c2bd6-762b-47ca-9447-91d2b460c9ec | KSCIEC60204-1_KR | 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
e648cb84-83b4-4e6f-8d6d-c1ab7625919a | KSCIEC60204-1_KR | KS C IEC 60204-1:2016 KSKSKS KSKSK KSKS KSK KS KSK KSKS KSKSK KSKSKS ICS 13.110; 29.020 ¦ Safety of machinery - ¦ ¦ --- ¦ ¦ Electrical equipment of machines - ¦ ¦ Part 1: General requirements ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
43f858ce-9136-4758-819b-735d7fb48b1e | KSCIEC60079-14_KR | KSKSKSKS KS C IEC 60079-14 KSKSKSK KSKSKS KSKSK KSKS KSK K KS 폭발성 분위기 - 제 14 부: 전기설비 설계, 선정, 설치 KS C IEC 60079-14:2013 산 업 표 준 심 의 회 2020 년 12 월 30 일 개정 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
1b99b51a-3341-4f70-944d-1d387c720c3e | KSCIEC60079-14_KR | KS CIEC 60079-14:2013 심 의 : 전기응용 기술심의 회 성 명 근 무 처 직 위 (회 장) 신 판 석 홍익대학교 교 수 (위 원) 권 오 화 KIC TECH 대 표 김 갑 일 명지대학교 교 수 김 재 희 한국산업기술시험원 본 부 장 박 현 주 한전 전력연구원 책 임 박 효 성 한국화학융합시험연구원 연 구 위 원 서 호 선 퀄리아국제특허법률사무소 대 표 이 주 철 대한전기협회 처 장 임 영 민 전자부품연구원 수 석 장 우 진 서울과 학기술대학교 교 수 조 두 희 한국전자통신연구원 책 임 (간 사) 정 서 란 국가기술표준원 표준정책국 전기전자정보표준과 주 무 관 원안작성협력 : 방폭전기설비 전문위원회 성 명 근 무 처 직 위 (대표전문위원) 김 두 현 충북대학교 교 수 (위 원) 강 준 구 한국산업기술시험원 본 부 장 김 기 회 한국가스안전공사 처 장 김 지 훈 방폭기술정보 소 장 류 보 혁 (주)류앤컴퍼니 대 표 박 동 선 산업안전보건공단 차 장 안 병 준 산업안전보건공단 본 부 장 윤 동 현 현텍 대 표 이 형 섭 명지대학교 교 수 최 상 원 (전)산업안전보건연구원 실 장 황 경 용 한국가설협회 연 구 소 장 (간 사) 강 정 일 산업안전보건공단 안전보건인증원 차 장 표준열람 : e 나라표준인증(http://www.standard.go.kr) 제 정 자 : 산업표준심의 회 위원장 담당부처 : 산업통상자원부 국가기술표준원 제 정 : 2004 년 11 월 24 일 개 정 : 2020 년 12 월 30 일 심 의 : 산업표준심의 회 전기응용 기술심의 회 원안작성협력 : 전기응용 기술심의 회 방폭전기설비 전문위원회 이 표준에 대한 의견 또는 질문은 e 나라표준인증 웹사이트를 이용하여 주십시오. 이 표준은 산업표준화법 제 10 조의 규정에 따라 매 5 년마다 산업표준심의 회에서 심의 되어 확인, 개정 또는 폐지됩니다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
757432e1-28a1-42ad-8fcc-614f9991e735 | KSCIEC60079-14_KR | KS CIEC 60079-14:2013 목 차 머 리 말 .............................. V 1 적용범위 ........................... 1 2 인용 35................................. 3 용어의 정의 ...................... 3 4 일반사항 ····················· 10 4.1 일반 Pl................... 10 4.2 문서화 .................... 10 12 4.3 최초 4.4 기기 적합성 ⌀1000000000 12 4.5 담당자 적격성 ········· 13 5 기기의 선정 ................ 13 5.1 정보 드시................... 13 5.2 장소 ............... 13 5.3 기기보호등급(EPL)과 폭발위험장소 분류와 의 관계 ................................................... 14 5.4 기기보호등급(EPL)에 따른 기기 선정 ............................... 14 5.5 기기 그룹에 따른 선정 ------------------------ 17 5.6 가스, 증기, 분진의 발화온도 또는 주위온도에 따른 선정 - 17 5.7 방사기기 선정 ..... 19 5.8 초음파 기기 선정 ······ 20 5.9 외부 요인을 고려한 기기 선정 ...................... 21 5.10 이동형, 휴대형 및 (개인)착용형 기기 선정 ........................................ 22 5.11 회전 전기기기 ....... 23 5.12 등기구 ················· 26 5.13 플러그 및 소켓 .... 27 5.14 전지 및 배터리 ····· 27 5.15 RFID 1111111111111111111 27 5.16 가스 W................... 28 6 위험한(점화성) 스파크로부터의 보호 ···················· 28 6.1 구조용 재료로서의 경금속 ........... 28 6.2 통전부로 인한 위험 .................. 29 6.3 노출 및 외부 도전부로 인한 千절................ 29 6.4 등전위 .................... 31 6.5 정전기 ................... 32 34 6.6 낙뢰 ..................... 6.7 전자기 방사 ........... 34 6.8 금속부의 음극방식 ····· 35 6.9 광학 방사에 의한 2,000 원 35 7 전기적 보호 .................... 36 8 전기 차단(switch-off) 및 전기적 분리 ····················· 36 8.1 중소시기............................ 36 -i- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및무단배포를 금합니다. | {}
cb17048d-7b10-49c1-9313-0bf74845cdde | KSCIEC60079-14_KR | KS CIEC 60079-14:2013 36 8.2 전기 ...................... 8.3 전기적 분리 ............ 36 9 케이블 및 배선시스템 ····· 37 9.1 일반사항. ............. 37 9.2 알루미늄 도체 ------- 37 9.3 케이블 ........... 37 9.4 전선관 시스템 --------- 40 9.5 추가 요구사항 ....... 41 9.6 설치 요구사항 ......... 41 10 케이블 인입 시스템 및 블랭킹 결제안료 2 2012,010. 2.11. 42 10.1 일반사항 ······· 42 10.2 케이블글랜드의 선정 ....... 42 10.3 기기와 케이블의 연결 ········ 44 10.4 Ex"d", Ex"t" 또는 Ex "nR" 이외의 인입부에 적용되는 추가 요구사항 ................................ 44 10.5 미사용 개구부 ......................................... 44 10.6 내압방폭구조 "d"에 적용되는 추가 요구사항........................ 45 10.7 분진방폭구조 "t"에 적용되는 추가 요구사항 ................................................... 46 10.8 통기 제한 방폭구조 "nR"에 적용되는 추가 요구사항................................ 46 11 회전 전기........................... 47 11.1 일반사항.......................... 47 11.2 내압방폭구조 "d" 전용에 적용되는 항목에 요양기관에 47 11.3 안전증방폭구조 "e" 전동기 ··············· 48 11.4 압력방폭구조 "p" 및 분진압력방폭구조 "pD" 전동기................................. 50 11.5 분진방폭구조 "t" 전동기 -------------- 51 11.6 비점화방폭구조 "nA" = = = = = = = 52 12 등기구 ······················· 53 13 전기 가열 시스템 ··········· 53 13.1 일반사항 ------------ 53 13.2 온도 모니터링 ········ 53 13.3 온도 제한 ·············· 54 13.4 안전장치 ··············· ----- 55 13.5 전기 트레이스 히터 시스템 ................ 55 14 내압방폭구조 "d"에 적용되는 추가 유권함............... 56 14.1 일반사항 ----------- 56 14.2 고체 장애물 ······ 56 14.3 내압 접합면의 보호 ----- 56 14.4 전선관 시스템 ... 57 15 안전증방폭구조 "e"의 추가 요구사항.. ····················· 58 15.1 일반사항 ................ 58 15.2 단자 박스의 최대 소비전력 ---------------- 58 15.3 도체 단말처리 ....................................... 59 15.4 단면적 및 연속 허용전류에 따른 최대 도체 수 ................................................... 59 16 본질안전방폭구조 "i"의 추가 요구사항 ······················· 60 16.1 일반사항............. ............ 60 -ii- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및무단배포를 금합니다. | {}
4e0de42f-a467-4c34-9e4a-e69abc278be9 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 16.2 기기보호등급(EPL) "Gb", "Gc" 및 "Db", "Dc"의 요구사항에 따른 설치 ................................. 60 16.3 기기보호등급(EPL) "Ga" 또는 "Da" 요구사항을 만족하는 설치..................................... 68 16.4 단순 기기 ............. 69 16.5 단자 박스 ·············· 71 16.6 특수 용도 ------------- 72 17 압력방폭용기에 적용되는 추가 요구시청 2 2 2 2 2 2 2 2 2 2 73 17.1 일반사항 - 73 17.2 압력방폭구조 "p". - - 73 17.3 분진압력방폭구조 "pD" ··········· 77 17.4 폭발성 가스 분위기를 위한 통 joom)________________ 79 18 비점화방폭구조 "n"형에 적용되는 추가 요구사항_____________________ 79 18.1 일반사항. .............. 79 18.2 "nR" 기기 .......... 80 18.3 단자 및 도체의 = = = = = 80 18.4 도체 단말처리 ····· 80 19 유입방폭구조 "o"의 추가 현금영수증 공제신청(현금영수증 승인번호가 적힌 경우만 81 19.1 일반사항. .............. 81 19.2 외부 연결 ············ 81 20 충전방폭구조 "q"의 추가 현금영수증 공제신청(현금영수증 승인번호가 적힌 경우만 81 21 몰드방폭구조 "m"의 추가 2018-22- 81 22 광학 방사 기기 "op"의 추가 요구사항 ······················· 82 23 용기 "t"에 의한 분진방폭구조의 추가 요구사항.. ........................................... 82 부속서 A (규정) 책임자, 운용자/기술자, 설계자의 지식, 기술 및 적격성 ................................................... 83 A.1 범위 ························ ・・・・・・・・・ ··················································· 83 A.2 지식 및 --------------- 83 A.3 적격성 .................... 84 A.4 E............................. 85 부속서 B(참고) 폭발성 가스 분위기에서의 안전작업절차 지침 ··················································· 86 부속서 C(규정) 최초 검사 一 기기별 검사 계획 .................................... 87 부속서 D(참고) 매우 낮은 온도에서의 전기설비 ................................... 92 D.1 일반사항. .............. ........ 92 D.2 케이블 ......... ··········· 92 D.3 전기 트레이스 히팅 시스템 ················ 92 D.4 조명 시스템 ----------- 92 D.5 회전 전기기기 ........- 92 부속서 E(참고) 케이블의 통기제한 시험 ······················ 93 E.1 시험절차. ························ 93 부속서 F (참고) 전기 트레이스 히팅 시스템의 설치............................. 94 F.1 일반사항............................ 94 F.2 정의 ................. 94 F.3 일반적인 요구사항 ------------------------- 95 F.4 기기보호등급 "Gb", "Gc", "Db" 및 "Dc"에 대한 요구사항 - 96 -iii- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및무단배포를 금합니다. | {}
2d051fed-60c7-4f99-af98-623bbe883d18 | KSCIEC60079-14_KR | KS CIEC 60079-14:2013 F.5 설계 97 F.6 인수 검사 ... 99 F.7 트레이스 히터의 설치 ............ 101 F.8 제어 및 모니터링 기기의 설치 ..................... 103 F.9 단열 시스템의 설치 ····················· 107 F.10 배선의 설치와 분기회로의 배치 ·························· 107 F.11 최종 설치 검토 ---- 108 F.12 시운전 ---- 108 부속서 G(규정) 고정자 권선의 잠재적 방전 위험성 평가 - 점화위험인자 .................................... 111 부속서 H(규정) 선형 전류/전압 특성을 갖는 하나 이상의 관련기기로 구성된 본질안전회로의 검증 ........................ 112 H.1 일반사항. ............... 112 H.2 보호등급이 "ib"인 본질안전 ················ 112 H.3 보호등급이 "ic"인 본질안전 ················ 112 부속서 I(참고) 선형 전류/전압 특성을 갖는 하나 이상의 관련기기가 있는 본질안전회로에서의 최대 시스템 전압 및 전류의 결정 방법 ......................................... 113 I.1 선형 전류/전압 특성을 갖는 본질안전화로 211111100000000 원 113 1.2 비선형 전류/전압 특성을 갖는 본질안전회로 ................................................ 115 부속서 J (참고) 케이블 파라미터의 결정 ························· 116 J.1 측정 ................................................... 116 J.2 하나 이상의 본질안전회로를 포함하는 케이블.............................. 116 J.3 FISCO 101010111111110000010000000101110101001110000000001 117 부속서 K(규정) 광학 방사 기기 "op"의 추가 요구사항 ................................................... 118 K.1 일반사항 ············ 118 K.2 본질안전 광학 방사 "op is" .............. 118 K.3 보호 광학 방사 "op pr" ··········· 118 K.4 인터록된 광학 방사 "op sh" ················· 119 부속서 L(참고) 과도한 두께의 분진층의 예 ............................. 120 부속서 M (참고) 하이브리드 혼합물 ················ 121 M.1 일반사항. ............ 121 M.2 농도 한계 ----- 121 M.3 에너지/온도 제한 - 121 M.4 기기 선정 - 121 M.5 내압방폭기기의 사용 ------ 121 M.6 정전기 위험 -------- 121 M.7 설치 5.11................ 122 참고문헌 ························· 123 KS CIEC 60079-14:2013 해 설 ---------- 125 - iv- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및무단배포를 금합니다. | {}
b35afb95-b277-4f52-89e7-9d8bc422ba1a | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 머 리 말 이 표준은 산업표준화법 관련 규정에 따라 산업표준심의 회의 심의 를 거쳐 개정한 한국산업표준이다. 이에 따라 KS C IEC 60079-14:2002(2007 년 발행)는 개정되어 이 표준으로 바뀌었다. 이 표준은 저작권법의 보호 대상이 되는 저작물이다. 이 표준의 일부가 기술적 성질을 가진 특허권, 출원공개 이후의 특허출원, 실용신안권 또는 출원공개 후의 실용신안등록출원에 저촉될 가능성이 있다는 것에 주의 를 환기한다. 관계 중앙행정기관의 장과 산업표준심의 회는 이러한 기술적 성질을 가진 특허권, 출원공개 이후의 특허출원, 실용신안권 또는 출원공개 후의 실용신안등록출원에 관계되는 확인에 대하여 책임을 지지 않는다. KS C IEC 60079 는 '폭발성 분위기'라는 공통 명칭하에 다음과 같은 일련의 부로 구성된다. 제 0 부: 기기 - 일반 요구사항 제 1 부: 내압방폭용기 "d"에 의한 기기 보호 제 2 부: 압력방폭용기 "p"에 의한 기기 보호 제 3 부: 본질 안전 회로용 불꽃 점화 시험 장치 제 4 부: 발화온도 시험방법 제 5 부: 충전 방폭구조 "q"에 의한 기기 보호 제 6 부: 유입 방폭구조 "0"에 의한 기기 보호 제 7 부: 안전증 방폭구조 "e"에 의한 기기 보호 제 10-1 부: 폭발위험 장소의 구분 제 10-2 부: 장소 구분 - 가연성 분진분위기 제 11 부: 본질안전 "i"에 의한 기기 보호 제 14 부: 폭발 위험 장소에서의 전기 설비 제 15 부: 비점화 방폭구조 "n"에 의한 기기 보호 제 17 부: 전기설비 검사 및 유지보수 제 18 부: 몰드 방폭구조 "m"에 의한 기기 보호 제 25 부: 본질안전설비 제 26 부: 기기보호수준(EPL) Ga 기기 제 27 부: 필드버스의 본질안전 개념(FISCO) 제 28 부: 광학 방사를 사용하는 설비 및 전송 시스템의 보호 제 29-1 부: 가스감지기 - 가연성 가스용 감지기의 성능 요구사항 제 29-2 부: 가스감지기 - 가연성 가스 및 산소용 감지기의 선정, 설치, 사용 및 유지보수 제 30-1 부: 전기저항 트레이스 히터 - 일반 및 시험 요구사항 제 30-2 부: 전기저항 트레이스 히터 - 설계, 시공 및 유지를 위한 응용 가이드 제 31 부: 용기 "t"에 의한 기기의 분진 점화 보호 -v- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
6dbb21c2-f723-4953-abaa-613da5c8223c | KSCIEC60079-14_KR | KS CIEC 60079-14:2013 개 요 이 표준은 2013 년 제 5 판으로 발행된 IEC 60079-14, Explosive atmospheres - Part 14: Electrical installations design, selection and erection, COR1(2016), ISH1(2017) 및 ISH2(2020)를 기초로 기술적 내용 및 대응국제표준의 구성을 변경하지 않고 작성한 한국산업표준이다. 인화성 물질로 인한 폭발 위험을 줄이기 위한 예방 대책은 일반적으로 다음과 같은 순서로 적용되는 세 가지 원칙에 기초한다. 1) 대체 2) 통제 3) 완화 대체는 예를 들어 인화성 소재를 인화성이 없거나 낮은 소재로 대체하는 것을 의미한다. 통제의 예는 다음과 같다. a) 인화성 물질의 양을 줄임. b) 누출 억제 또는 최소화 c) 누출 통제 d) 폭발성 분위기 조성 예방 e) 누출된 물질 수거 및 격리 f) 점화원 방지 비고 1 f)를 제외한 나머지 모든 항목은 폭발위험장소 구분 과정에 반영되는 요소들이다. 완화의 예는 다음과 같다. a) 노출된 사람의 수를 줄임. b) 폭발 전파를 방지하기 위한 조치 c) 폭발압력 경감 d) 폭발압력 억제 e) 적절한 개인보호구 제공 비고 2 상기 항목들은 위험 평가의 일환인 사후관리에 포함된다. 대체 및 통제[a) ~ e)] 원칙을 적용하고 나면 남아 있는 폭발위험장소를 폭발성 분위기 존재 가능성에 따라 폭발위험장소의 종별로 분류해야 한다(KS C IEC 60079-10-1 또는 KS C IEC 60079-10-2 참고). 발화 시 발생할 수 있는 결과 에 대한 평가와 함께 사용할 수 있는 폭발위험장소 구분을 통해 기기보 호등급을 결정할 수 있으며, 장소별로 적합한 방폭구조를 구체적으로 선정할 수 있다. 폭발이 발생하기 위해서는 폭발성 분위기와 점화원이 함께 존재해야 한다. 방폭의 목적은 전기기기 가 점화원이 될 수 있는 가능성을 허용 가능한 수준으로 낮추는 것이다. 폭발위험성이 낮은 장소나 비폭발위험장소에서는 세심하게 설계된 대부분의 전기기기를 사용할 수 있다. -vi- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f208063c-3b6d-4585-a8c5-5b527c3b9e93 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 대기 중에 폭발범위에 들어가는 양의 인화성 가스, 증기 또는 분진이 존재할 수 있는 장소에 전기기 기를 설치하는 경우, 정상 작동 또는 특정 고장 조건에서 발생하는 아크, 스파크, 뜨거운 표면으로 인해 폭발이 발생할 수 있는 가능성을 줄이기 위한 방폭구조를 적용해야 한다. 발생, 가공, 처리, 저장되는 많은 종류의 분진이 가연성을 가지고 있다. 분진은 발화되면 빠르게 타들 어가며, 일정한 비율로 공기와 혼합되면 상당한 폭발력을 가진다. 이런 물질이 존재하는 장소에서도 전기기기를 사용할 필요성이 있는 경우가 많으며, 그럴 경우 외부 폭발성 분위기가 발화될 가능성을 줄이기 위한 적절한 방폭구조를 해당 기기에 적용해야 한다. 전기기기에서 발생할 수 있는 점화원으 로는 아크, 스파크, 뜨거운 표면, 마찰 스파크 등이 있다. 전기기기는 여러 가지 방법으로 분진을 발화시킬 수 있다. 분진의 최저발화온도를 넘어서는 기기의 표면 온도. 분진을 발화시킬 수 있는 온도는 분진의 특 성, 분진운인지 분진층인지 여부, 분진층의 두께, 열원의 기하학적 구조에 따라 달라진다. · 스위치, 접점, 정류자, 브러시 또는 그와 비슷한 전기 부품에서 발생하는 아크 또는 스파크 · 축적된 정전기 방전 · 방사 에너지(예: 전자기 방사) · 기기에서 발생하는 기계적 스파크 또는 마찰 스파크 분진 발화 위험을 피하기 위해서는 다음과 같은 사항들이 중요하다. 분진이 쌓일 수 있거나 분진운에 접촉될 수 있는 표면의 온도를 이 표준에 규정된 제한 온도 이 하로 유지해야 한다. 전기 스파크를 발생시키는 모든 부품 또는 이 표준에 규정된 제한 온도를 상회하는 부품의 경우 - 분진 유입을 충분히 막을 수 있는 용기에 넣어야 한다. 아크, 스파크, 분진을 발화시킬 수 있는 온도의 발생을 막기 위해 전기 회로의 에너지를 제한 해야 한다. · 그 밖의 점화원을 피해야 한다. 폭발위험장소(KS C IEC 60079-0 참조)에서 사용되는 전기기기에는 여러 가지 유형의 방폭구조가 적 용될 수 있다. 이 표준은 폭발성 분위기 내에 설치되는 전기설비의 설계, 선정, 설치에 적용되는 구 체적인 요구사항을 규정한다. 이 표준은 전기기기 요구사항에 관한 KS C IEC 60364 와 같은 다른 관련 IEC 표준을 보충하는 역할 을 한다. 이 부는 또한 KS C IEC 60079-0 과 그 관련 표준에 규정된 적합한 전기기기의 제조, 시험, 표시 요구사항을 인용한다. 이 표준은 폭발위험장소 내 전기설비의 설계, 선정, 설치 및 필수 최초 검사에 적용되는 구체적인 요 구사항을 규정한다. 이 표준은 제조자가 제공한 설명서를 따르는 것을 전제로 한다. 지속적인 검사, 유지보수 및 수리도 폭발위험장소 내 전기기기 관리에 중요한 역할을 한다. 이와 관련해서는 KS C IEC 60079-17, IEC 60079-19, 제조자 설명서에서 추가적인 정보를 얻을 수 있다. 크기와 상관없이 모든 산업 기기에는 전기기기와 관련된 것 외에도 다양한 점화원이 존재할 수 있다. 다른 점화원에 관련된 안전에 대해서도 물론 예방 조치가 필요하지만, 이에 대한 지침은 이 표준의 범위에서 벗어나는 주제이다. -vii- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f971d7cd-0652-41d3-bc5d-930df1416d77 | KSCIEC60079-14_KR | 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
e4723153-e4b6-4867-939f-3918461c6725 | KSCIEC60079-14_KR | 한국산업표준 KS C IEC 60079-14:2013 폭발성 분위기 - 제 14 부: 전기설비 설계, 선정, 설치 Explosive atmospheres - Part 14: Electrical installations design, selection and erection 1 적용범위 이 표준은 폭발성 분위기에서 또는 그와 관련하여 사용되는 전기설비의 설계, 선정, 설치 및 최초 검 사에 관한 구체적인 요구사항을 규정한다. 수분 침투 방지, 내부식성과 같은 다른 환경 조건에 대한 요구사항이 적용되는 기기의 경우, 추가적 인 보호가 필요할 수 있다. 이 표준의 요구사항은 KS C IEC 60079-0 에서 정의 하는 기본 대기 조건에서 사용되는 기기에만 적용 한다. 이와 다른 조건에서는 필요에 따라 추가적인 예방조치를 해야 하며, 해당 조건에 맞는 기기 인 증을 받아야 한다. 예를 들어 대부분의 인화성 물질과 통상적으로 비인화성으로 간주되는 물질도 산 소 농도가 높은 조건에서는 격렬하게 연소할 수 있다. 비고 1 KS C IEC 60079-0 에서 규정된 표준 대기 조건은 대기의 폭발 특성과 관련이 있으며 기기의 동작범위와 관련되는 것은 아니다. 대기의 폭발 특성을 예로 들면, · 온도: -20 C ~ 60 °C · 압력: 80 kPa(0.8 bar) ~ 110 kPa(1.1 bar) · 정상 산소 함량의 공기, 일반적으로 21 % v/v 이 요구사항은 비폭발위험장소에서 사용되는 기기에 대한 요구사항에 더해 추가적으로 적용된다. 비고 2 최고 1 000 V a.c. 또는 1 500 V d.c. 전압이 사용되는 경우, 이 표준의 요구사항은 KS C IEC 60364 의 설치 요구사항을 기반으로 하지만, 다른 관련 국가의 요구사항이 적용될 수 있다. 이 표준은 고정형, 휴대형, 이동형 및 (개인)착용형, 영구 또는 임시 설치를 포함한 모든 전기기기에 적용된다. 이 표준은 다음과 같은 경우에는 적용하지 않는다. - 폭발성 갱내가스(fire damp)가 존재할 우려가 있는 광산에 설치되는 전기설비 비고 3 이 표준은 광산의 지상에 설치되는 전기설비와 폭발성 갱내가스 이외의 가스 등이 존재할 우 려가 있는 광산에는 적용할 수 있다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 1 | {}
d2304afb-0d52-4b78-8d09-ef11a35b8a73 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 근원적인 폭발 상황과 폭발물의 분진 또는 자연발화성 물질(예를 들어 폭발성 물질의 제조 및 취 급 공정) 의학적인 목적으로 설치된 진료실 인화성 미스트로 인한 폭발위험장소의 전기설비 비고 4 분진 또는 부유물(flying), 인화성 가스 또는 증기의 하이브리드 혼합물로 인한 위험성에 대한 추가 지침은 부속서 M 에 제공된다. 이 표준에서는 일반적으로 인화하한에 훨씬 못 미치는 수준의 인화성 기체, 액체, 분진 농도에서 발 생할 수 있는 독성 위험에 대해서는 다루지 않는다. 독성이 나타날 수 있는 농도의 인화성 물질에 사람이 노출될 수 있는 장소에서는 그에 따른 예방조치를 취해야 한다. 이런 예방 조치는 이 표준의 범위를 벗어나는 것이다. 2 인용 표준 다음의 인용표준은 전체 또는 부분적으로 이 표준의 적용을 위해 필수적이다. 발행연도가 표기된 인 용표준은 인용된 판만을 적용한다. 발행연도가 표기되지 않은 인용표준은 최신판(모든 추록을 포함) 을 적용한다. KS C IEC 60034-1, 회전기기 - 제 1 부: 정격 및 성능 KS C IEC 60060-1, 고전압 시험 기술 - 제 1 부: 일반 정의 및 시험 요구사항 KS C IEC 60079 (모든 부), 폭발성 분위기 KS C IEC 60079-0, 폭발성 분위기 - 제 0 부: 기기 - 일반 요구사항 KS C IEC 60079-1, 폭발성 분위기 - 제 1 부: 내압방폭용기 "d"에 의한 기기 보호 KS C IEC 60079-6, 폭발성 분위기 - 제 6 부: 유입 방폭구조 "0"에 의한 기기 보호 KS C IEC 60079-7, 폭발성 분위기 - 제 7 부: 안전증 방폭구조 "e"에 의한 기기 보호 KS C IEC 60079-10-1, 폭발성 분위기 - 제 10-1 부: 장소 구분 - 폭발성 가스 분위기 KS C IEC 60079-10-2, 폭발성 분위기 - 제 10-2 부: 장소 구분 - 가연성 분진분위기 KS C IEC 60079-11, 폭발성 분위기 - 제 11 부: 본질안전 방폭 구조 "i"에 의한 기기 보호 KS C IEC 60079-15, 폭발성 분위기 - 제 15 부: 비점화 방폭구조 "n"에 의한 기기 보호 KS C IEC 60079-17, 폭발성 분위기 - 제 17 부: 전기설비 검사 및 유지보수 KS C IEC 60079-18, 폭발성 분위기 - 제 18 부: 몰드 방폭구조 "m"에 의한 기기 보호 KS C IEC 60079-26, 폭발성 분위기 - 제 26 부: 기기보호수준(EPL)Ga 기기 KS C IEC 60079-28, 폭발 분위기 - 제 28 부: 광학 방사를 사용하는 설비 및 전송 시스템의 보호 KS C IEC 60079-29-1, 폭발성 분위기 - 제 29-1 부: 가스감지기 - 가연성 가스용 감지기의 성능 요구 사항 KS C IEC 60079-30-1, 방폭 전기기계 기구 - 제 30-1 부: 전기저항 트레이스 히터 - 일반 및 시험 요 구사항 KS C IEC 60243-1, 절연 재료의 절연내력 - 시험방법 - 제 1 부: 상용 주파수 시험 2 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
3772d954-bc26-4018-afcd-13921b43f555 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 KS C IEC 60332-1-2, 화재 조건에서 전기/광섬유 케이블 시험 - 제 1-2 부: 단심 절연 전선 또는 케이 블 수직 불꽃 전파 시험 - 1 kW 혼합 불꽃 시험 절차 KS C IEC 60364(모든 부), 저압 전기설비 KS C IEC 60950(모든 부), 정보기술기기의 안전성 KS C IEC 61010-1, 측정, 제어 및 실험실용 전기 장비의 안전 요구사항 - 제 1 부: 일반 요구사항 KS C IEC 61285, 산업용 공정제어 - 분석기기 수용설비의 안전 KS C IEC 61558-2-6, 최대 공급전압 1 100 V 용 변압기, 리액터, 전원장치 및 유사기기의 안전 - 제 2-6 부: 안전절연변압기와 안전절연변압기 통합 전원장치의 개별 요구사항 및 시험 IEC 60050-426, International Electrotechnical Vocabulary (IEV) - Part 426: Explosive atmospheres IEC 60050-826, International Electrotechnical Vocabulary (IEV) Part 826: Electrical installations IEC 60079-13, Explosive atmospheres Part 13: Equipment protection by pressurized room "p" and artificially ventilated room "V" IEC TR 60079-16, Electrical apparatus for explosive gas atmospheres-Part 16: Artificial ventilation for the protection of analyzer(s) houses IEC 60079-19, Explosive atmospheres - Part 19: Equipment repair, overhaul and reclamation IEC 60079-29-4, Explosive atmospheres Part 29-4: Gas detectors Performance requirements of open path detectors for flammable gases IEC 60364-4-41:2005, Low-voltage electrical installations - Part 4-41: Protection for safety - Protection against electric shock 비고 IEC 60364-4-41:2005 에 대응하는 KS 는 2013 년도에 고시된 KS C IEC 60364-4-41 이다. IEC 62305-3:2010, Protection against lightning - Part 3: Physical damage to structures and life hazard 비고 IEC 62305-3:2010 에 대응하는 KS 는 2012 년도에 고시된 KS C IEC 62305-3 이다. 3 용어의 정의 이 표준의 목적을 위하여 KS C IEC 60079-0 에서 정의 하는 용어 외에 다음의 용어와 정의 를 적용한다. 비고 폭발성 분위기에 적용되는 그 밖의 용어에 대한 정의 는 IEC 60050-426 에서 제공된다. 3.1 일반사항 3.1.1 적격기관(competent body) 안전에 관하여 필요한 평가를 수행할 수 있는 전문 기술과 지식을 보유한 개인 또는 조직 3.1.2 검증문서(verification dossier) 전기기기 및 설치의 적합성을 입증하는 문서 3.1.3 전기기기(electrical equipment) 전기 에너지의 이용을 위해 전체적으로 또는 부분적으로 사용되는 기기 3 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
a065806c-e8a3-4545-b5d8-192c1068feb7 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 비고 여기에는 전자 통신 및 전기에너지의 생성, 전송, 분배, 저장, 측정, 제어, 변환 및 소비 품목이 포함된다. 3.2 폭발위험장소 3.2.1 폭발위험장소(hazardous area) 기기의 구조, 설치 및 사용에 특별한 주의 가 요구되는 양의 폭발성 분위기가 존재하거나 존재할 것 으로 예상되는 지역 3.2.2 비폭발위험장소(non-hazardous area) 기기의 구조, 설치 및 사용에 특별한 주의 가 요구되는 양의 폭발성 분위기가 존재하지 않을 것으로 예상되는 지역 3.2.3 기기 그룹(group of electrical equipment for explosive atmospheres) 기기가 사용되는 폭발성 분위기와 관련된 기기의 분류 체계 비고 폭발성 분위기에 사용되는 전기기기는 다음과 같이 세 가지로 분류한다. 그룹 I: 폭발성 갱내 가스가 발생하는 광산에서 사용하는 광산용 기기 그룹 II: 하위 그룹으로 나뉘며, 광산 이외의 폭발성 가스 분위기가 있는 모든 장소에서 사용되는 기기(5.5 참조) 그룹 III: 하위 그룹으로 나뉘며, 광산 이외의 폭발성 분진 분위기가 있는 모든 장소에서 사용되는 기기(5.5 참조) 3.2.4 하이브리드 혼합물(hybrid mixture) 인화성 가스 또는 증기와 가연성 분진의 혼합물 비고 KS C IEC 60079-10-2 의 "분진" 정의 에는 분진(dust)과 부유물(flying)이 모두 포함된다. 3.2.5 최고 허용표면온도(maximum permissible surface temperature) 발화를 회피하기 위하여 실제 사용 중에 도달하는 것이 허용된 전기기기의 최고표면온도 비고 이 정의 는 가스 분위기에는 적용되지 않는다. 최고 허용표면온도는 층 두께 및 안전계수적용 (5.6.3 참조)을 포함하여 분진운 또는 분진층과 같은 분진 형태에 따라 달라진다. 3.2.6 폭발위험장소의 종별(zones) 폭발성 분위기의 생성 빈도와 지속시간을 바탕으로 종별(zones)로 구분되는 폭발위험장소 3.2.7 0 종 장소(zone 0) 인화성 물질과 공기가 혼합된 가스 또는 증기 형태의 폭발성 분위기가 연속적, 길게 또는 자주 존재 하는 장소 4 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
422c0a30-2c8f-4960-8385-7167b14a640c | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 3.2.8 1 종 장소(zone 1) 인화성 물질과 공기가 혼합된 가스 또는 증기 형태의 폭발성 분위기가 정상작동 중 가끔 생성되는 장소 3.2.9 2 종 장소(zone 2) 인화성 물질과 공기가 혼합된 가스 또는 증기 형태의 폭발성 분위기가 정상작동 중 생성되지 않거나 생성된다 하더라도 짧은 기간에만 존재할 수 있는 장소 3.2.10 20 종 장소(zone 20) 공기 중 분진운 형태의 폭발성 분위기가 연속적 또는 장기간 또는 빈번히 존재하는 장소 3.2.11 21 종 장소(zone 21) 공기 중 분진운 형태의 폭발성 분위기가 가끔씩 정상 운전 시에 발생할 우려가 있는 장소 3.2.12 22 종 장소(zone 22) 공기 중 분진운 형태의 폭발성 분위기가 정상 운전 시에는 발생할 우려가 없으며, 발생한다고 해도 짧은 기간 동안만 지속될 수 있는 장소 3.3 내압방폭 구조 3.3.1 내압방폭구조 "d"(flameproof enclosure "d") 폭발성 가스 분위기를 발화시킬 수 있는 부품이 들어 있는 용기로 내부 폭발로 발생하는 압력을 견 디며, 용기 주변의 폭발성 가스 분위기로 폭발의 전파를 방지할 수 있는 용기 3.3.2 압력 중첩(pressure-piling) 용기의 구획 또는 분할된 공간에서, 예를 들어 다른 구획 또는 분할 공간의 1 차 발화에 의한, 예압된 가스 혼합물의 발화 결과 비고 이로 인해 예상되었던 것보다 높은 최대 압력이 유도될 수 있다. 3.4 안전증방폭구조 3.4.1 안전증방폭구조 "e"(increased safety "e") 전기기기 또는 방폭부품에 적용되는 방폭구조로, 과도한 온도 발생 가능성과 아크 및 스파크 발생에 대한 안전성을 증가하기 위해 추가 조치가 적용되는 보호 형식 3.4.2 초기기동전류(initial starting current) IA 정격 전압 및 주파수가 공급될 때 교류 전자석의 전기자가 최대 공극 위치로 고정되었거나 교류 전 동기가 정지하였을 때 흐르는 전류의 최대 실훗값 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 5 | {}
9510ccde-aa61-4ae1-bf46-f830d221a4ed | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 3.4.3 기동전류비(starting current ratio) IA/IN 초기기동전류 IA 와 정격전류 IN 의 비 3.4.4 (허용구속) 시간(time) tE 초기기동전류 IA 가 흐를 때 교류회전자 또는 고정자 권선이 최고 주위온도에서 정격 운전 중에 도달 한 온도에서 제한 온도까지 가열되는 데 걸리는 시간(초 단위) 3.5 본질안전방폭구조 3.5.1 본질안전방폭구조 "i"(intrinsic safety "i") 기기 내부 및 폭발성 분위기에 노출된 상호연결 배선(interconnecting wiring)의 전기적 에너지를 스파 크 또는 열적 효과(heating effects)로 인해 발화를 일으킬 수 있는 수준 이하로 제한하는 것에 기반한 방폭구조 3.5.2 관련기기(associated apparatus) 본질안전회로 및 비본질안전회로를 모두 포함하고 비본질안전회로가 본질안전회로에 악영향을 미치 지 않도록 구성된 전기기기 비고 관련기기는 다음 중 하나에 해당할 수 있다. a) 해당 폭발성 분위기 내에서 사용하기 위해 KS C IEC 60079-0 에 나열된 다른 방폭구조를 갖는 전기기기 b) 보호되지 않아 보통 폭발성 분위기 내에서 사용되지 않는 전기기기(예: 기록계 자체는 폭발 성 분위기 안에 있지는 않지만 폭발성 분위기 내에 위치한 열전대가 본질안전인 기록계의 입력 회로와 연결) 3.5.3 본질안전기기(intrinsically safe apparatus) 모든 회로가 본질안전회로인 전기기기 3.5.4 갈바닉 절연(galvanic isolation) 두 회로 사이의 직접적인 전기적 연결 없이 두 회로 사이에서 신호나 전력의 전송을 허용하는 기기 내의 배치 비고 갈바닉 절연은 주로 자기(변압기 또는 릴레이) 또는 광-결합 소자(opto-coupled elements)를 이 용한다. 6 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c7300fa8-6ca8-48f4-be49-ce7ff993ce1f | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 3.5.5 단순기기(simple apparatus) 명확히 정의 된 전기적 파라미터를 가지고 있고, 그것이 사용되는 회로의 본질안전에 적합한(compatible with) 단순 구성의 전기적 부품 또는 부품의 조합 3.5.6 본질안전회로(intrinsically safe circuit) 정상작동 및 특정 고장 조건을 포함하여 KS C IEC 60079-11 에서 규정한 조건에서 생성된 스파크 또 는 열 효과(any spark or any thermal effect)가 주어진 폭발성 분위기의 발화를 일으킬 수 없는 회로 비고 회로에는 관련기기가 포함될 수도 있다. 3.5.7 본질안전 전기시스템(intrinsically safe electrical system) 기술문서에 따라 전기기기들이 상호 연결되어 있고 그 내부의 회로 또는 회로의 일부가 폭발성 분위 기에서 본질적으로 안전하게 사용할 수 있도록 되어 있는 구조의 조합체 3.5.8 본질안전 부속회로(intrinsically safe sub-circuit) 동일 본질안전회로의 다른 부분들 또는 다른 본질안전회로와 갈바닉 절연되어 있는 본질안전회로의 일부분 3.6 본질안전 파라미터 3.6.1 최대외부인덕턴스 대 저항의 비(maximum external inductance to resistance ration) L。IR。 본질안전을 무효화하지 않고 전기기기의 외부 접속부에 연결할 수 있는 인덕턴스 대 저항 비율의 최 댓값 3.7 압력방폭구조 3.7.1 압력방폭구조 "p"(pressurization "p") 용기 내부의 보호가스 압력을 외부 대기 압력보다 높게 유지함으로써 외부 대기가 용기 내부로 유입 되지 아니하도록 한 방폭구조 3.7.2 연속 희석(continuous dilution) 퍼지 후 가압용기 내부의 인화성 물질의 농도가 잠재적인 점화원(즉, 희석지역 밖에 있는)에서 폭발 한도 범위 밖의 값으로 유지되도록 보호가스를 연속적으로 공급하는 것. 비고 희석 지역은 인화성 물질의 농도가 안전한 농도로 희석되지 않는 내부 배출원 부근 지역이다. 3.7.3 누설 보상(leakage compensation) 가압용기 및 그 덕트에서 발생하는 누설을 보충하기에 충분한 보호가스를 공급하는 것. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 7 | {}
fbf9e5f6-c8e6-4acd-9d7b-17e24e3d175c | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 3.7.4 정적 가압(static pressurization) 폭발위험장소에서 보호가스를 추가하지 않고 가압용기 내의 양압을 유지 3.8 비점화방폭구조 "n" 3.8.1 비점화방폭구조 "n"(Type of protection "n") 전기기기의 정상작동 및 특정된 정기적 예상고장 발생(specified regular expected occurrences) 시 주 위 폭발성 가스 분위기를 발화시킬 수 없도록 전기기기에 적용되는 방폭구조 비고 1 추가로, 해당 기기 표준의 요구사항은 발화의 원인이 되는 고장이 거의 발생하지 않도록 하 고 있다. 비고 2 특정 비정상 조건의 예로 고장 난 램프의 등기구를 들 수 있다. 3.8.2 에너지 제한 기기(energy-limited apparatus) 내부의 회로 및 부품이 에너지 제한 개념에 따라 제조된 전기기기 3.8.3 관련 에너지 제한 기기(associated energy-limited apparatus) 에너지 제한회로와 비에너지 제한회로가 모두 포함되어 있고, 비에너지 제한회로가 에너지 제한회로 에 악영향을 미치지 아니하도록 제작된 전기기기 3.9 유입방폭구조 "o"(oil-immersion "o") 전기기기 또는 전기기기의 부품(parts of the electrical equipment)을 보호 액체에 담가 액체의 상부 또 는 용기의 외부에 존재할 수 있는 폭발성 가스 분위기가 발화되지 않도록 하는 방폭구조 3.10 충전방폭구조 "q"(powder filling "q") 폭발성 가스 분위기를 발화시킬 수 있는 부품을 고정하고 그 주위를 충전재로 완전히 둘러쌈으로써 외부 폭발성 가스 분위기의 발화를 방지하기 위한 방폭구조 비고 이 방폭구조는 주위의 폭발성 가스 분위기가 기기 및 부품에 침투하여 회로에 의해 발화되는 것을 차단하지 못할 수 있다. 그러나 충전재 빈 공간의 체적이 작고 충전재의 경로를 통해 전 파되며 화염이 냉각(quenching of a flame)되어 외부 폭발을 방지한다. 3.11 몰드방폭구조 "m"(encapsulation "m") 스파크나 열로 인해 폭발성 분위기를 발화시킬수 있는 부품(parts)이 작동 또는 설치 조건에서 분진 층이나 폭발성 분위기의 발화를 방지하기 위해 콤파운드나 기타 비금속 용기로 점착하여 완전히 둘 러싸인 방폭구조 3.12 분진방폭구조(protection by enclosure "t") 분진층 또는 분진운에 의한 발화를 회피하기 위해서 용기에 의해 보호되는 전기기기의 방폭구조 8 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
d6c4df75-c866-4406-8b24-bee701f83106 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 3.13 전기 공급 시스템 3.13.1 보호특별저전압 시스템(protective extra-low voltage system) PELV 다음과 같은 조건에서 특별저전압을 초과 하지 아니하는 전기시스템 정상상태 단일고장 조건(다른 전기회로에서 발생하는 지락고장은 제외) [출처: IEC 60050-826:2004, 826-12-32] 3.13.2 안전특별저전압 시스템(safety extra-low voltage system) SELV 다음과 같은 조건에서 특별저전압을 초과 하지 아니하는 전기시스템 정상상태 단일고장 조건(다른 전기회로에서 발생하는 지락고장 포함) [출처: IEC 60050-826:2004, 826-12-31] 3.14 기기 3.14.1 고정형 기기(fixed equipment) 지지대에 고정된 기기 또는 통전 시 특정 위치에 고정된 기기 3.14.2 이동형 기기(transportable equipment) 작동 중에 사람이 휴대하지 않거나 고정 설치를 의도하지 않은 기기 3.14.3 휴대형 기기(portable equipment) 작동 중에 사람이 휴대하는 기기 3.14.4 (개인)착용형 기기(personal equipment) 작동 중에 인체에 접촉하여 착용하는 기기 3.15 무선 주파수 식별(radio frequency identification, RFID) 데이터 저장을 위하여 전기 태그를 이용하는 데이터 수집 기술 비고 "전자 라벨", "위성중계기" 또는 "형식판"이라고도 하는 이 태그는 안테나에 부착된 RFID 칩으로 구성된다. kHz, MHz 및 GHz 범위에서 송신하는 태그는 배터리로 전력을 공급받거나 리더기로 부터 받는 RF 파로부터 전력을 받을 수 있다. 9 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f9f38456-7488-48e1-8e16-bd88b4886da1 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 4 일반사항 4.1 일반 요구사항 전기설비의 적절한 선정 및 설계를 위하여 폭발위험장소를 가스, 증기의 경우 KS C IEC 60079-10-1 에 따라 0 종, 1 종 및 2 종 장소로, 분진의 경우 KS C IEC 60079-10-2 에 따라 20 종, 21 종 및 22 종 장소 로 분류한다. 전기기기는 가능한 한 비폭발위험장소에 설치하는 것을 원칙으로 하되 이것이 불가능할 경우에는 폭 발성 분위기가 발생할 가능성이 가장 낮은 장소에 설치해야 한다. 폭발위험장소의 전기설비는 비폭발위험장소의 전기설비에 대한 적절한 요구사항도 함께 준수해야 한 다. 그러나 비폭발위험장소에 대한 요구사항은 폭발위험장소에 적용하기에 충분하지 않다. 예를 들어, 물의 침투 및 부식에 대한 보호와 같은 다른 환경 조건을 만족시키기 위하여 추가적인 보호가 요구되는 경우, 해당 보호 수단이 기기의 건전성에 악영향을 미치지 않아야 한다. 전기기기 및 재료는 전력, 전압, 전류, 주파수, 용도, 그 밖에 준수하지 않을 경우 해당 기기의 안전성에 영향 을 줄 수 있는 특성 측면에서 해당 기기의 전기 정격을 준수하여 설치 및 사용해야 한다. 특히, 해당 기기의 전압과 주파수가 기기와 함께 사용되는 전기 공급 시스템에 적합해야 하며, 정격 전압, 주파 수 및 기타 파라미터에 대한 온도등급을 설정해야 한다. 폭발위험장소에서 사용하는 제품은 IEC 60038 에 따른 IEC 표준 전압으로 설계되어 있다. 만약 공급 전압이 이 표준 전압 범위가 아닌 경우에는 기기는 특별하게 선택되고 인증받아야 한다. 폭발위험장소에서 사용되는 기기는 5 절 ~ 13 절의 기본 요구사항과 14 절 ~ 23 절의 방폭구조 구조별 추가요구사항을 준수하여 선정 및 설치되어야 한다. 검사와 정비 시 접근이 쉽도록 설치 방식을 설계하고 기기 및 재료를 설치해야 한다(KS C IEC 60079-17). 연구개발, 방폭기기를 사용할 수 없는 파일럿플랜트(pilot plant)와 같이 예외적인 환경에서 사용되는 전기기기 및 설비는 적격기관의 감독하에 있고 다음 중 한 가지 이상의 조건을 만족할 경우 이 표준 의 요구사항을 만족시킬 필요가 없다. 폭발성 분위기가 형성되지 않음을 보증할 수 있는 조치 강구 폭발성 분위기 형성 시 기기의 전원이 차단되고 가열된 부분이 점화원이 되지 않음을 보증할 수 있는 조치 강구 - 시험기기의 화재 또는 폭발이 사람 및 환경에 위험하지 않음을 보증할 수 있는 조치 강구 추가로 적격기관은 관련 조치 또는 조건, 제어 방법 등을 문서화하여야 한다. 적격기관은 다음과 같 아야 한다. 폭발위험장소에서 사용되는 전기기기나 시스템에 관한 이 표준 또는 다른 관련 표준 및 규격에 대하여 익숙하여야 한다. 평가를 수행하는 데 필요한 모든 정보에 접근 가능하여야 한다. 4.2 문서화 10 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
8a9c1761-54eb-4db3-b554-db60a1d062ff | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 모든 기기가 해당 기기에 적용되는 기기 인증서(5 절 참조)뿐만 아니라 이 표준 및 기기를 설치하려는 공장에 적용되는 그 밖의 요구사항을 준수하는지 확인해야 한다. 이를 위해 모든 설치에 대해 검증 문서를 작성하고 사업장 내 또는 다른 장소에 보관해야 한다. 문서를 사업장 외의 장소에 보관한 경 우, 기기의 소유자가 누구인지(소유자가 복수인 경우 복수의 소유자 명시), 해당 문서가 보관되어 있 는 장소가 어디인지를 기록한 문서를 사업장에 비치하고 필요한 경우 사본을 제공할 수 있어야 한다. 비고 검증문서는 인쇄본 또는 전자 포맷으로 보관될 수 있다. 문서의 적법성을 확보하기 위해서는 각 국가의 법률에 의해 허용되는 방식을 준수해야 한다. 올바른 방식으로 기기를 새로 설치하거나 기존 기기를 확장하기 위해서는 비폭발 장소에 요구되는 정보 외에 다음과 같은 정보를 검증문서에 추가해야 한다. 현장 위험장소의 종별(분진폭발위험장소의 경우 최대허용 분진층 두께 포함)을 포함한 위험장소 분류 및 범위를 보여주는 도면이 첨부된 폭발위험장소 분류 문서(KS C IEC 60079-10-1, KS C IEC 60079-10-2 참조) 발화 시 발생하는 피해에 대한 평가(선택사항) (5.3 참조) 해당되는 경우, 전기기기의 그룹 또는 하위 그룹에 적용되는 가스, 증기 또는 분진의 분류 온도등급 또는 가스 또는 증기의 최저발화온도 해당되는 경우, 전기 저항률, 분진운의 최저발화온도, 분진층의 최저발화온도 및 분진운의 최저 - 발화에너지를 포함한 재료 특성 외부 영향 및 주위온도(5.9 참조) 기기 선정, 설치 및 최초 검사에 관한 제조자의 사용설명서 특정사용조건이 명시되어 있는 전기기기 문서, 예를 들어 인증번호에 접미어 "X"가 있는 기기 본질안전시스템에 대한 시스템 기술문서(16.2.4.2 참조) - 기기 또는 분석실의 퍼징률 등과 같은 필요한 계산 값의 세부 내용 제조자/적격자의 확인서(4.4.2 참조) KS C IEC 60079-17 및 IEC 60079-19 의 요구사항을 각각 만족하기 위하여 유지보수 및 수리에 대한 정보를 수집하는 것에 대해 고려하여야 한다. [참고] IEC 60079-19 에 대한 KS C IEC 60079-19 로 준비 중이며, 제정 후 해당하는 KS 표준을 참조 한다. 설치 설치를 담당하는 사람에게 적합한 형태로 제공된, 기기의 올바른 설치를 보장하기 위해 필요한 정보[KS C IEC 60079-0, 사용설명서(Instructions) 참조] 설치 지역 및 환경에 대한 기기의 적합성 관련 기술문서(온도등급, 방폭구조, IP 등급, 내부식성 등) 배선 시스템의 유형과 세부 사항을 표시한 도면 11 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
fbc92b3d-4f6c-42c3-b7ba-5bf11a13128e | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 특정 방폭구조의 요구사항을 준수하는 케이블 인입 시스템 선정 기준에 관한 기록 회로 식별 관련 도면 및 계획서 최초 검사 기록(부속서 C) 설치자/적격자의 확인서(4.5 참조) 비고 조립품 또는 사전 설치된 품목에 대한 검사 기록은 최초 검사 기록의 일부로 인정될 수 있다. 4.3 최초 검사 기기는 해당 기기에 적용되는 문서를 준수하여 설치하여야 한다. 교체 가능한 부품은 올바른 방폭구 조와 정격을 준수하는지 확인해야 한다. 설치를 완료하고 처음 사용하기 전에 기기 및 설치에 대한 최초 검사는 KS C IEC 60079-17 의 정밀 검사 등급을 기반으로 하는 부속서 C 에 따라 수행되어야 한 다. 비고 최초 검사와 관련된 추가적인 정보는 KS C IEC 60079-17 에서 제공된다. 4.4 기기 적합성 보증 4.4.1 KS c IEC 표준에 따른 인증서 보유 기기 4.4.1.1 일반사항 KS C IEC 60079 시리즈 또는 KS C IEC 61241 시리즈에 따른 인증서를 보유한 기기를 이 표준에 따 라 선정 및 설치하면 폭발위험장소에 대한 요구사항을 만족시킬 수 있다. 4.4.1.2 KS C IEC 표준 이 표준에 규정된 요구사항은 KS C IEC 60079 시리즈 최신판의 KS C IEC 표준을 기반으로 한다. 기 기가 KS C IEC 60079 의 최신판에 따라 인증되지 않은 경우, 이 표준에서 제공하는 요구사항에 부합 하지 않을 수 있으며, 안전한 사용을 위한 추가적인 조치가 필요할 수 있다. 비고 제품 안전 또는 폭발위험이 있는 기기에 관한 최신 KS C IEC 표준 정보는 관련 웹 사이트에 서 찾을 수 있다. 기존 연판 대비 변경 사항에 관한 정보는 이 표준의 머리말에서 제공된다. 4.4.2 KS C IEC 표준에 따른 인증서 미보유 기기 본질안전회로가 사용된 단순기기가 아닌 한 인증서가 없거나 인증서가 있지만 4.4.1 에 명시된 표준 중 하나를 따르지 않는 기기는 적합한 인증서를 획득할 수 없는 경우에만 폭발위험장소에서 사용할 수 있다. 이 경우 사용자, 제조자 또는 제 3 자가 해당 기기를 안전하게 사용할 수 있다는 것을 입증해 야 하며, 그 사실을 검증문서에 기록해야 한다. 이 경우에는 이 표준의 이후 요구사항이 적용되지 않 을 수 있다. 4.4.3 수리, 중고 또는 기존 기기의 선정 다음과 같은 경우에만 기존, 중고 또는 수리된 기기를 신규 기기 내에 설치할 수 있다. 기기가 변경되지 않았으며, (수리 및 오버홀을 포함하여) 최초 인증 내용을 만족하는 상태에 있는 것을 확인할 수 있는 경우. 기기의 변경 여부가 불확실할 때는 원 제조자에게 변경 여부를 확인 12 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
04f80b06-b353-4b87-b102-ab7fafe475ca | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 해야 한다. 해당 품목에 적용되는 기기 표준의 어떤 변경 사항도 추가적인 안전조치사항을 요구하는 것으로 간주되지 않는 경우 해당 제품의 인증에 사용된 기준이 이 표준에 규정된 요구사항과 충돌하지 않는 경우 기존 기기와 동일하지 않은 사양의 기기를 도입할 경우 "신규" 설치로 간주될 수 있다. 다중 인증을 받은 기기의 경우(예를 들면 본질안전방폭구조 기기 인증을 받고 별도로 내압방폭구조 인증을 받은 경우), 새로 설치할 위치에 사용되는 방폭구조에 영향을 미치지 않도록 설치 및 유지 관 리해야 한다. 방폭 구조가 다르면 그에 따라 유지보수 요구사항도 달라진다. 상기의 예에서 원래 내 압방폭구조로 설치된 기기는 내압방폭구조로만 사용되어야 하며, 그렇지 않을 경우 해당 기기의 안 전을 확보해주는 본질안전회로 내의 안전 부품들이 손상되지 않았다는 사실을 검증해야 한다. 예를 들어 공급 단자에 과전압이 걸리지 않는지 검증해야 하며, 기존에 본질안전방폭구조로 설치된 기기 의 경우 내압방폭구조로 사용하기 전에 화염 접합면에 손상이 없다는 것을 검증해야 한다. 4.5 담당자 적격성 이 표준이 적용되는 설비의 설계, 기기의 선정 및 설치는 다양한 방폭구조 및 설치 실무, 관련 규정, 규제, 폭발위험장소 구분의 일반 원칙에 관한 교육 및 훈련을 받은 자에 의해 수행되어야 한다. 담당 자는 수행할 작업의 유형에 맞는 전문성을 갖춰야 한다(부속서 A 참조). 담당자는 정기적으로 필요한 교육, 훈련을 받아야 한다. 비고 국가별 규정, 표준, 사용자 요구사항에 따른 교육훈련 및 평가 체계를 통해 전문성을 입증할 수 있다. 5 기기의 선정 5.1 정보 요구사항 폭발위험장소 내의 전기기기를 적합하게 선정하기 위해서는 다음과 같은 자료가 필요하다. 기기보호등급 요구사항을 포함한 폭발위험장소의 구분 해당되는 경우 전기기기 그룹 또는 세부 그룹에 적용되는 가스, 증기 등급 구분 관련된 가스나 증기의 온도등급 또는 최저발화온도 분진운의 최저발화온도, 분진층의 최저발화온도 기기의 용도 외부 영향 및 주위온도 폭발위험장소 구분도에 기기보호등급(EPL) 요구사항을 기록할 것을 권장한다. 피해결과 에 대한 위험 성 평가가 시행되지 않은 경우에도 마찬가지이다(5.3 참조). 5.2 장소 폭발위험장소는 종별 등급에 따라 분류된다. 장소 종별 분류 시 폭발로 인해 발생할 수 있는 피해는 고려하지 않는다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 13 | {}
762ccd70-f3e1-43c9-8c46-ba474bc06860 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 비고 IEC 60079-14:2007(4 판) 이전에 발표된 이 표준의 이전 연판은 폭발성 분위기가 조성될 확률 이 높을 수록 발화 가능성이 있는 대상에 보다 높은 수준의 안전을 요구하는 통계적인 방식으 로 장소별 필요한 방폭구조를 배정했다. 5.3 기기보호등급(EPL)과 폭발위험장소 분류와 의 관계 폭발위험장소 구분 문서에 종별 분류만 명시되어 있는 경우, 표 1 에 따른 기기보호등급을 준수해야 한다. 표 1 - 종별 분류만 할당되어 있는 경우 적용되는 기기보호등급(EPL) ¦ 종별 장소 ¦ 기기보호등급(EPL) ¦ ¦ --- ¦ --- ¦ ¦ 0 ¦ "Ga" ¦ ¦ 1 ¦ "Ga" 또는 "Gb" ¦ ¦ 2 ¦ "Ga" , "Gb" 또는 "Gc" ¦ ¦ 20 ¦ "Da" ¦ ¦ 21 ¦ "Da" 또는 "Db" ¦ ¦ 22 ¦ "Da", "Db" 또는 "Dc" ¦ 폭발위험장소 구분 문서에 기기보호등급이 명시되어 있는 경우, 그에 따른 기기 선정 요구사항을 준 수해야 한다. 표 1 의 장소 분류별 기기보호등급을 대신하여 위험 기반 방식, 즉 발화로 인한 피해 수준을 고려한 방식으로 기기보호등급을 결정할 수 있다. 주어진 상황에 따라 이런 방식으로 결정된 기기보호등급 은 표 1 의 기기보호등급보다 높은 수준의 기기보호등급을 요구할 수도 있고 그보다 낮은 수준의 기 기보호등급을 허용할 수도 있다. 이와 관련하여 KS C IEC 60079-10-1, KS C IEC 60079-10-2 를 참고할 수 있다. 5.4 기기보호등급(EPL)에 따른 기기 선정 5.4.1 일반사항 신규 설치 또는 기기 사용 시에는 4.4 에 따라 기기의 적합성을 검증해야 한다. 5.4.2 기기보호등급과 방폭구조 KS C IEC 표준에 따른 방폭구조별 기본 기기보호등급은 표 2 와 같다. 기기에 표시된 방폭 기호와 기 기보호등급이 표 2 와 다를 경우, 기기에 표시된 내용이 우선된다. 14 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
bc5c2ed0-fa7e-4ec7-8f24-435b82eb53a3 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 표 2 - 방폭구조와 기기보호등급의 기본 관계 ¦ EPL ¦ 방폭구조 ¦ 기호 ¦ 근거 표준 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ "Ga" ¦ 본질안전 ¦ "ia" ¦ KS C IEC 60079-11 ¦ ¦ "Ga" ¦ 몰드 ¦ "ma" ¦ KS C IEC 60079-18 ¦ ¦ "Ga" ¦ 각기 EPL "Gb"에 맞는 두 가지 독립 된 보호구조 ¦ ¦ KS C IEC 60079-26 ¦ ¦ "Ga" ¦ 광방사를 사용하는 기기와 송신시스 템의 보호 ¦ "op is" ¦ KS C IEC 60079-28 ¦ ¦ "Ga" ¦ 특수 방폭구조 ¦ "sa" ¦ IEC 60079-33 ¦ ¦ "Gb" ¦ 내압용기 ¦ "d" ¦ KS C IEC 60079-1 ¦ ¦ "Gb" ¦ 안전증 ¦ "e" ¦ KS C IEC 60079-7 ¦ ¦ "Gb" ¦ 본질안전 ¦ "ib" ¦ KS C IEC 60079-11 ¦ ¦ "Gb" ¦ 몰드 ¦ "m" "mb" ¦ KS C IEC 60079-18 ¦ ¦ "Gb" ¦ 유입 ¦ "⌀" ¦ KS C IEC 60079-6 ¦ ¦ "Gb" ¦ 압력 ¦ "p", "px", "py", "pxb" 또는 "pyb" ¦ KS C IEC 60079-2 ¦ ¦ "Gb" ¦ 충전 ¦ "q" ¦ KS C IEC 60079-5 ¦ ¦ "Gb" ¦ 필드버스 본질안전 개념(FISCO) ¦ ¦ KS C IEC 60079-27 ¦ ¦ "Gb" ¦ 광방사를 사용하는 기기와 송신시스 템의 보호 ¦ "op is" "op sh" "op pr" ¦ KS C IEC 60079-28 ¦ ¦ "Gb" ¦ 특수 방폭구조 ¦ "sb" ¦ IEC 60079-33 ¦ ¦ "Gc" ¦ 본질안전 ¦ "ic" ¦ KS C IEC 60079-11 ¦ ¦ "Gc" ¦ 몰드 ¦ "mc" ¦ KS C IEC 60079-18 ¦ ¦ "Gc" ¦ 비점화 ¦ "n" 또는 "nA" ¦ KS C IEC 60079-15 ¦ ¦ "Gc" ¦ 통기제한 ¦ "nR" ¦ KS C IEC 60079-15 ¦ ¦ "Gc" ¦ 에너지 제한 ¦ "nL" ¦ KS C IEC 60079-15 ¦ ¦ "Gc" ¦ 스파크기기 ¦ "nC" ¦ KS C IEC 60079-15 ¦ ¦ "Gc" ¦ 압력 ¦ "pz" 또는 "pzc" ¦ KS C IEC 60079-2 ¦ ¦ "Gc" ¦ 광방사를 사용하는 기기와 송신시스 템의 보호 ¦ "op is" "op sh" "op pr" ¦ KS C IEC 60079-28 ¦ ¦ "Gc" ¦ 특수 방폭구조 ¦ "sc" ¦ IEC 60079-33 ¦ ¦ "Da" ¦ 몰드 ¦ "ma" ¦ KS C IEC 60079-18 ¦ ¦ "Da" ¦ 보호용기 ¦ "ta" ¦ KS C IEC 60079-31 ¦ ¦ "Da" ¦ 본질안전 ¦ "ia" 또는 "iaD" ¦ KS C IEC 60079-11 또는 KS C IEC 61241-11 ¦ ¦ "Da" ¦ 특수 방폭구조 ¦ "sa" ¦ IEC 60079-33 ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 15 | {}
716adc42-0ce4-4d09-9c5b-a4659d0428cd | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 표 2 - 방폭구조와 기기보호등급의 기본 관계(계속) ¦ EPL ¦ 방폭구조 ¦ 기호 ¦ 근거 표준 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ "Db" ¦ 몰드 ¦ "mb" ¦ KS C IEC 60079-18 ¦ ¦ "Db" ¦ 보호용기 ¦ "tb" 또는 "tD" ¦ KS C IEC 60079-31 KS C IEC 60079-1 ¦ ¦ "Db" ¦ 압력 ¦ "pD" ¦ IEC 61241-4 ¦ ¦ "Db" ¦ 본질안전 ¦ "ib" 또는 "ibD" ¦ KS C IEC 60079-11 또는 KS C IEC 61241-11 ¦ ¦ "Db" ¦ 특수 방폭구조 ¦ "sb" ¦ IEC 60079-33 ¦ ¦ "Dc" ¦ 몰드 ¦ "mc" ¦ KS C IEC 60079-18 ¦ ¦ "Dc" ¦ 보호용기 ¦ "tc" 또는 "tD" ¦ KS C IEC 60079-31 KS C IEC 61241-1 ¦ ¦ "Dc" ¦ 압력 ¦ "pD" ¦ IEC 61241-4 ¦ ¦ "Dc" ¦ 본질안전 ¦ "ic" ¦ KS C IEC 60079-11 ¦ ¦ "Dc" ¦ 특수 방폭구조 ¦ "sc" ¦ IEC 60079-33 ¦ ¦ 비고 향후 새로운 표시 기호와 그에 따른 기기보호등급이 도입될 수 있음. ¦ 비고 향후 새로운 표시 기호와 그에 따른 기기보호등급이 도입될 수 있음. ¦ 비고 향후 새로운 표시 기호와 그에 따른 기기보호등급이 도입될 수 있음. ¦ 비고 향후 새로운 표시 기호와 그에 따른 기기보호등급이 도입될 수 있음. ¦ 5.4.3 기기보호등급(EPL) "Ga" 또는 "Da"가 요구되는 장소에 사용되는 기기 EPL "Ga" 또는 "Da"를 요구하는 장소에서 사용할 수 있는 전기기기나 회로는 EPL "Ga" 또는 "Da"로 표시되어 있는 기기 또는 EPL "Ga" 또는 "Da" 각각의 요구사항을 만족하는 것으로서 표 2 의 방폭구 조를 가진 기기여야 한다. 기기는 해당 방폭구조에 관한 이 표준의 요구사항에 따라 설치해야 한다. 조합 방폭구조(combined types of protection) 기기에 KS C IEC 60079-26 에 따른 "Ga"가 표시되어 있는 경우, 해당 방폭구조에 관한 이 표준의 요구사항도 함께 준수하여 설치해야 한다. 5.4.4 기기보호등급(EPL) "Gb" 또는 "Db"가 요구되는 장소에 사용되는 기기 EPL "Gb", 또는 "Db"를 요구하는 장소에서 사용할 수 있는 전기기기나 회로는 EPL "Gb" 또는 "Db"로 표시되어 있는 기기 또는 EPL "Gb" 또는 "Db" 각각의 요구사항을 만족하는 것으로서 표 2 의 방폭구 조를 가진 기기여야 한다. 기기는 해당 방폭구조에 관한 이 표준의 요구사항에 따라 설치해야 한다. EPL "Ga" 또는 "Da"의 요구사항을 만족하는 기기를 EPL "Gb" 또는 "Db" 기기만을 요구하는 장소에 설치하는 경우, 개별 보호기술에 따른 추가 요구사항으로 인해 방폭구조의 요구사항이 변경되는 경 우가 아니라면 해당 방폭구조의 모든 요구사항을 만족해야 한다. 5.4.5 기기보호등급(EPL) "Gc" 또는 "Dc"가 요구되는 장소에 사용되는 기기 EPL "Gc" 또는 "Dc"를 요구하는 장소에서 사용할 수 있는 전기기기나 회로는 EPL "Ga", "Gb" 또는 "Gc" 그리고 "Da", "Db" 또는 "Dc"로 각각 표시되어 있는 기기 또는 표 2 의 방폭구조를 가진 기기여 야 한다. 기기는 해당 방폭구조에 관한 이 표준의 요구사항에 따라 설치해야 한다. EPL "Ga" 또는 "Gb", "Da" 또는 "Db"의 각 요구사항을 만족하는 기기를 EPL "Gc" 또는 "Dc" 기기만을 요구하는 장소에 설치하는 경우, 개별 보호기술에 따른 추가요구사항으로 인해 방폭구조의 요구사항 이 변경되는 경우가 아니라면 해당 방폭구조의 모든 요구사항을 만족해야 한다. 16 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
42ee2304-7d6b-4efa-a3bf-eb32854fc44a | KSCIEC60079-14_KR | KS CIEC 60079-14:2013 5.5 기기 그룹에 따른 선정 전기기기는 표 3 에 따라 선정해야 한다. 표 3 - 기기 그룹과 가스, 증기 또는 분진 간의 관계 ¦ 가스, 증기 또는 분진 분류 장소 ¦ 허용 기기 그룹 ¦ ¦ --- ¦ --- ¦ ¦ IIA ¦ II, IIA, IIB 또는 IIC ¦ ¦ IIB ¦ II, IIB 또는 IIC ¦ ¦ IIC ¦ II 또는 IIC ¦ ¦ IIIA ¦ IIIA, IIIB 또는 IIIC ¦ ¦ IIIB ¦ IIIB 또는 IIIC ¦ ¦ IIIC ¦ IIIC ¦ 특정 가스나 증기 또는 분진에 적합한 전기기기를 다른 가스, 증기 또는 분진에서 사용하기 위해서 는 적격기관에 의한 위험성 평가를 거쳐 해당 장소에서 사용하기에 적합하다는 평가를 받아야 한다. 5.6 가스, 증기, 분진의 발화온도 또는 주위온도에 따른 선정 5.6.1 일반사항 전기기기의 최고표면온도가 해당 장소에 존재할 가능성이 있는 가스, 증기의 발화온도에 도달하지 않는 전기기기를 선정해야 한다. 전기기기에 주위온도범위가 표시되어 있지 않은 경우, 해당 기기는 -20 °C 부터 40 °C 범위 내에서 사 용하도록 설계된 것이다. 주위온도가 별도로 표시되어 있는 전기기기는 해당 범위 내에서 사용해야 한다. 주위온도가 정해진 범위를 벗어나거나 다른 요인(예: 공정 온도, 태양광 방사 등)에 의해 온도가 영향 을 받는 경우, 기기에 미치는 영향을 고려해야 하며 그에 대한 조치를 문서화해야 한다. 일반적으로 케이블글랜드에는 온도등급이나 사용 주위온도 범위가 표시되어 있지 않지만, 정격 서비 스온도는 지정되어 있으며, 별도의 표시가 없는 한 서비스온도는 기본적으로 -20 °C ~ 80 °C 이다. 이 범위를 벗어나는 온도에서 사용하고자 하는 경우, 케이블글랜드와 관련 부속품이 해당 장소에 적합 한지 주의 를 기울여 확인해야 한다. 5.6.2 가스 또는 증기 전기기기에 표시되는 온도등급 구분 기호의 의미는 표 4 와 같다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 17 | {}
fb43d7fb-5aa2-4865-8678-b040afe752df | KSCIEC60079-14_KR | KS CIEC 60079-14:2013 표 4 - 가스 또는 증기 발화온도와 기기 온도등급 간의 관계 ¦ 폭발위험장소 구분에 따라 요구되는 온도등급 ¦ 가스 또는 증기의 발화온도(°C) ¦ 사용 가능한 기기 온도등급 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ T1 ¦ > 450 ¦ T1 - T6 ¦ ¦ T2 ¦ > 300 ¦ T2- T6 ¦ ¦ T3 ¦ > 200 ¦ T3- T6 ¦ ¦ T4 ¦ > 135 ¦ T4 - T6 ¦ ¦ T5 ¦ > 100 ¦ T5- T6 ¦ ¦ T6 ¦ > 85 ¦ T6 ¦ 5.6.3 분진 5.6.3.1 일반사항 분진층의 두께가 증가하면 최저발화온도가 낮아지고 단열효과 가 증가하는 두 가지 특성이 나타난다. 기기의 최고 허용표면온도는 KS C IEC 61241-2-1(ISO/IEC 80079-20-2, 검토 중)에 따른 시험방법으로 분진운과 분진층 양쪽 모두에 대해 도출된 해당 분진의 최저발화온도에서 안전율(safety margin)을 뺀 값으로 결정된다. 분진층 두께가 5 mm 를 초과 하는 장소에 설치되는 기기의 최고표면온도는 층 두께와 사용되는 재료 의 모든 특성을 고려하여 결정해야 한다. 과도하게 두꺼운 분진층의 예는 부속서 L 에서 제공된다. 5.6.3.2 분진운으로 인한 온도 제한 KS C IEC 60079-0 에 따른 분진 적용없이 시험했을 때 기기의 최고표면온도가 해당 분진/공기 혼합물 의 최저발화온도(°C)의 2/3 를 초과 해서는 안 된다. Tmax ≤2/3 TCL 여기에서, TCL 은 분진운의 최저발화온도를 의미한다. 5.6.3.3 분진층으로 인한 온도 제한 기기에 T 등급의 일부로 분진층 두께가 표시되어 있지 않은 경우에는 분진층 두께를 고려하여 안전 계수를 적용해야 한다. 두께 5mm 이하 KS C IEC 60079-0 에 따른 분진 적용없이 시험했을 때 기기의 최고표면온도가 해당 분진의 5 mm 층 두께의 최저발화온도에서 75 °C 를 뺀 값을 초과 해서는 안 된다. Tmax≤T5mm - 75 °C 여기에서 T5mm 는 두께 5 mm 분진층의 최저발화온도이다. 두께 5 mm 초과 50 mm 이하 18 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
83a87199-33a4-4a87-b3c5-8e875b808d3c | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 기기에 5 mm 를 초과 하는 분진층이 형성될 가능성이 있는 경우, 최고 허용표면온도를 낮춰야 한 다. 참고로 5 mm 층에 대해 250 °C 를 초과 하는 최저발화온도를 갖는 분진이 있는 곳에서 사용되 는 기기에 적용되는 최고 허용표면온도 감소의 예는 다음 그림 1 의 그래프와 같다. 50 mm 이상의 분진층에 대해서는 5.6.3.4 를 참조한다. 그림 1 의 정보를 적용하기 전에 KS C IEC 61241-2-1 을 참조해야 한다. ![image](/image/placeholder) CO 400 표궁번표 300 용 18 파 200 5 mm 분진층에서 발화온도 기기의 400°C≤T5mm 100 320°C≤T5mm<400°C 250°C≤T5mm<320°C 0 0 10 20 30 40 50 분진층 두께(mm) 그림 1 - 최고 허용표면온도와 분진층 깊이 간의 상관관계 5 mm 분진층의 발화온도가 250 °C 미만이거나 그래프의 적용에 대한 확신이 없을 경우, 해당 기기에 대한 실험에 의한 검증을 거쳐야 한다(5.6.3.4 참조). 5.6.3.4 불가피한 분진 층 기기의 측면과 하단 주변에 분진층이 형성되거나 기기가 분진에 완전히 잠기는 것이 불가피할 경우, 단열 효과 로 인해 훨씬 낮은 표면 온도를 적용할 필요가 있다. 이런 환경에서 기기보호등급 "Da"가 필요한 경우, 기기보호등급 "Da"의 모든 구체적인 요구사항들이 만족되어야 한다. 분진층 깊이가 50 mm 를 초과 하는 장소에 설치된 기기의 경우, 허용되는 층 깊이를 기준으로 기기의 최고표면온도가 TL 로 표시될 수 있다. 기기에 층 깊이에 대한 TL 이 표시되어 있는 경우, T5 mm 대신 층 깊이 L 에서의 분진 발화온도를 적용해야 한다. TL 이 표시되어 있는 기기의 최고표면온도는 층 깊 이 L 에서의 분진 발화온도보다 최소 75 °C 이상 낮아야 한다. 과도하게 두꺼운 분진층의 예는 부속서 L 에서 제공된다. 5.7 방사기기 선정 5.7.1 일반사항 기기보호등급 "Ga", "Gb" 또는 "Da", "Db"의 레이저 또는 전기기기의 기타 연속파원 출력 파라미터는 다음 값을 초과 하지 않아야 한다. 연속파 레이저 및 기타 연속파원인 경우 5mW/mm2 또는 35 mW 19 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
216a7cbc-efba-4918-915a-8cd5fbf1f424 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 - 최소 5 초의 펄스 간격을 갖는 펄스 레이저 또는 펄스 광원인 경우 0.1 mJ/mm2 기기보호등급 "Gc" 또는 "Dc"의 레이저 또는 전기기기의 기타 연속파원 출력 파라미터는 다음 값을 초과 하지 않아야 한다. 연속파 레이저 및 기타 연속파원인 경우 10 mW/mm2 또는 35 mW 펄스 레이저 또는 펄스 광원인 경우 0.5mJ/mm2 비고 1 펄스 간격이 5 초 미만인 방사선원은 연속파원으로 간주된다. 비고 2 상기의 값은 KS C IEC 60079-0 에서 발췌하였다. 폭발위험장소 외부에 설치되어 있으나 폭발위험장소 내부로 방사하는 기기의 경우, 5.7.1 의 요구사항 을 적용해야 한다. 폭발위험장소 외부에 있거나, 이 요구사항이 명시되어 있지 않은 연판의 KS C IEC 60079-0 또는 KS C IEC 60079-28 에 따른 인증을 받은 기기의 경우, 해당 기기 제조자를 통해 이 값을 확인할 수 있다. 5.7.2 점화 과정 광 스펙트럼 범위의 방사, 특히 특정 지점에 집중되는(in the case of focusing) 방사는 점화원이 될 수 있다. 예를 들어, 햇빛으로 물체에 광학 방사를 집중시키면 발화될 수 있다(예: 오목 거울, 렌즈 등). 섬광전구(photo flash lamp) 또는 일부 LED 와 같은 고밀도(high intensity) 광원들로부터의 방사는 특정 상황에서 입자에 의해 흡수될 수 있으며, 이로 인해 해당 입자가 점화원이 될 수 있다. 비고 발산형 연속 광원 조명 기기는 일반적으로 위험하지 않은 것으로 간주된다. 레이저 방사(신호, 원격 측정, 측량, 거리 측정기 등)의 경우, 원거리에서 방사되는 초점이 맞지 않는 빔도 에너지 또는 출력 밀도가 너무 높을 경우 대상 물체를 점화시킬 수 있다. 이 경우에도 레이저 빔이 분진층에 영향을 미치거나 대기 중의 입자에 흡수되어 가열이 발생된다. 특히 초점이 집중된 경우, 해당 지점의 온도가 1 000 °C 를 훨씬 초과 할 수도 있다. 광학 방사를 생성하는 기기 자체(예를 들어 등기구, 전기 아크, 레이저 등)가 점화원이 될 수 있는 가 능성에 대해서도 고려해야 한다. 5.8 초음파 기기 선정 5.8.1 일반사항 폭발위험장소에 설치되거나, 외부에 설치되어 있지만 폭발위험장소로 방사하는 기기의 경우, 기기보 호등급 "Ga", "Gb", "Gc", "Da", "Db" 또는 "Dc" 기기로부터의 초음파원의 출력 파라미터가 다음 값을 초과 하지 않아야 한다. · 연속파원의 경우 0.1 W/cm2, 10 MHz · 펄스파원의 경우 평균 출력 밀도 0.1 W/cm2, 2 mJ/cm2 20 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
ba460f5e-479a-412a-9d57-3a84e81d0218 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 비고 상기의 값은 KS C IEC 60079-0 에서 발췌하였다. 폭발위험장소 외부에 있거나, 이 요구사항이 명시되어 있지 않은 연판의 KS C IEC 60079-0 에 따른 인증을 받은 기기의 경우, 해당 기기 제조자를 통해 이 값을 확인할 수 있다. 5.8.2 점화 과정 초음파가 방사되면 음파발생기에 의해 방출되는 에너지의 많은 부분이 고체 또는 액체 물질에 의해 흡수된다. 이로 인해 초음파의 영향을 받은 물질이 가열될 수 있으며, 극단적인 경우 최저발화온도 이상으로 가열될 수 있다. 5.9 외부 요인을 고려한 기기 선정 전기기기는 방폭성능에 악영향을 미칠 수 있는 다음과 같은 외부 요인으로부터 보호될 수 있도록 선 정 및 설치해야 한다. 극저온 또는 고온 태양 복사 압력 조건 부식성 분위기 진동, 기계적 충격, 마찰 또는 마모 바람 도장 공정 화학물질 물, 습기 분진 식물, 동물, 곤충 기기의 선정 및 설치 설계 시 이런 외부 요인을 파악해야 하며, 해당 외부 요인을 통제하기 위해 사 용된 조치를 문서화하여 검증문서에 포함시켜야 한다. 비고 1 보다 자세한 내용은 KS C IEC 60364-5-51 에서 제공된다. 기기가 방폭구조에 영향을 줄 수 있는 습기 또는 수증기 응축이 발생할 수 있는 온도 변화에 장기간 노출되는 경우, 응축 방지 또는 응축수 배수를 위한 적절한 조치를 취해야 한다. 환기 조건에 영향을 미치지 않는 범위 내에서, 수직으로 회전하는 전기기기의 환기구를 통해 이물질 이 수직으로 유입되는 것을 방지하기 위한 조치를 취해야 한다. 전기기기가 의도된 온도 또는 압력 조건에서 벗어나 작동될 경우 문제가 발생할 수 있다. 이런 경우 추가적인 조치를 취해야 한다(5.6 참조). 기기로 유입되는 고압 공정 유체로 인해 위험이 발생할 수 있는 경우[예: 압력 스위치 또는 밀봉 (canned) 전동기 펌프], 고장 발생 시[예: 다이어프램 또는 밀봉부(can) 파손] 유체는 다음의 일부 또 는 전부를 초래할 수 있다. 기기 용기 파열 즉각적인 점화 위험 21 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
36ae655a-aba1-44fd-9f2f-d55b02ade09b | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 - 케이블 또는 전선관 내부를 따라 유체 침투 폭발위험장소에서 사용되는 기기 선정 시 공정 유체의 유입을 확실하게 막을 수 있는 기기를 선정해 야 한다(예: 주 공정 접촉부에 대한 1 차 밀봉, 1 차 밀봉 파손 시를 대비한 기기 내부 2 차 밀봉). 그렇 지 못할 경우, (적절하게 폭발로부터 보호되는 배기구, 배수 또는 통기 장치를 통해) 충분한 배기가 이루어지도록 하거나, 유체 유입을 막을 수 있도록 배선 시스템을 충분히 밀봉해야 하며, 필요한 경 우 두 가지 조치를 모두 취해야 한다. 가시적인 누출이나 기기의 자체 식별 가능한 고장, 경보, 전자 식 탐지 등의 방법으로 1 차 밀봉의 파손이 식별되어야 한다. 케이블 배선시스템을 다음과 같은 방법으로 밀봉해야 한다: 특수한 밀봉 접합부의 사용, 개별 도체를 밀봉하는 케이블글랜드 사용, 무기질 절연 금속 피복(MIMS, mineral-insulated metal-sheathed) 케이블, "에폭시" 밀봉 사용. 단, 케이블 밀봉 장치의 사용이 단순히 습기 침투 속도를 늦추는 역할만 할 수도 있으므로 추가적인 대책이 필요할 수도 있다. 누출 발생 사실을 명확하게 식별할 수 있도록 배기 시 스템을 배치해야 한다. 전기기기를 위한 공정 밀봉에 관한 IEC 표준이 없는 경우, KS C IEC 61010-1 과 같은 국가 표준 또는 기타 적용 가능한 표준을 따라야 한다. KS C IEC 61010-1 에서 공정 밀봉과 관련된 몇 가지 정보를 찾아볼 수 있다. 비고 2 공정 밀봉에 관하여 IEC TS 60079-40 을 참고할 수 있다. (유해한 환경에 보다 적합한 용기를 선택하기 위해) 방폭구조에서 요구되는 것보다 높은 수준의 방수 방진(IP) 등급을 가진 용기를 선택하는 경우, 용기의 IP 등급을 해당 장소에 적합한 IP 등급 또는 방 폭구조에 따라 요구되는 IP 등급 중 높은 쪽으로 유지시켜야 한다. 해당 기기에 지정된 IP 등급이 유 지되지 않은 경우, 그 사실을 검증문서에 명시해야 한다. 5.10 이동형, 휴대형 및 (개인)착용형 기기 선정 5.10.1 일반사항 이동형, 휴대형, (개인)착용형 기기는 다양한 용도로 유연하게 사용할 수 있기 때문에 서로 다른 위험 장소에서의 사용이 요구될 수 있다. 별도의 보호 수단 없이는 기기보호등급이 낮은 기기를 높은 기 기보호등급을 요구하는 장소로 반입할 수 없다. 그러나 특히 휴대형 또는 (개인)착용형 기기의 경우 현실적으로 이런 제한을 적용하기 어려울 수 있 다. 따라서 해당 장소에 노출되는 모든 기기는 해당 장소에서 요구하는 가장 높은 수준의 기기보호 등급을 따르도록 하는 것이 권장된다. 마찬가지로 기기 그룹 및 온도등급도 해당 기기가 사용될 수 있는 모든 가스, 증기, 분진 환경에 적합해야 한다. 적절한 예방 조치가 취해지지 않는 한, 여분의 배터리를 폭발위험장소로 반입해서는 안 된다. 기기에 전지 또는 배터리가 장착되어 있는 경우, 사용자는 배터리함 또는 용기의 빈 공간 중 수소가 차지하는 부피가 2 %를 초과 하지 않는지 또는 모든 전지의 가스배출 개구부(degassing apertures) 배 치를 통해서 배출 가스가 전기, 전자 부품 또는 연결부를 포함하고 있는 기기의 용기 내부로 배출되 지 않도록 되어 있는지 제조자와 함께 확인해야 한다. 단, 기기가 기기 그룹 IIC 에 적용되는 요구사 항을 만족시키는 경우, 가스배출 개구부 또는 수소 농도 제한 요건이 적용되지 않는다. 비고 1 전지의 유형을 불문하고 가스 발생 시 수소가 발생될 위험이 있으며, 이로 인해 작은 용기 내에서 폭발 조건이 조성될 수 있기 때문에 적절한 배기에 대한 조치가 필요하다. 이 요구사 22 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c439aa0c-9200-4c0b-bdaa-d47bb2009943 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 항은 휴대형 등기구, 멀티미터, 휴대형 가스 감지기 및 이와 유사한 기기에 적용된다. 비고 2 위 내용은 KS C IEC 60079-11 에서 인용되었다. 5.10.2 이동형, 휴대형 기기 영구적으로 설치된 기기와 는 달리 이동형, 휴대용 기기는 폭발위험장소에 일시적으로 설치될 수 있 다. 비상 발전기, 전기 아크 용접기, 산업용 리프트(포크) 트럭, 공기 압축기, 동력 환기 팬 또는 송풍 기, 휴대형 전동 공구, 특정 형식의 시험 및 검사 기기가 이런 경우에 해당된다. 폭발위험장소로 운송되거나 반입될 수 있는 기기는 적절한 기기보호등급을 유지해야 한다. 일반적으 로 요구되는 기기보호등급을 달성할 수 없는 이동형 또는 휴대형 기기를 폭발위험장소에서 사용할 필요가 있는 경우, 문서화된 위험 관리 프로그램을 수행해야 한다. 이 프로그램에는 적절한 훈련, 절 차 및 관리 조치가 포함되어 있어야 한다. 해당 기기의 사용으로 인해 발생될 수 있는 점화 위험에 적합한 안전 작업 허가서를 발급해야 한다(부속서 B 참조). 폭발위험장소 내에 있는 플러그나 소켓도 해당 장소에 적합한 기기보호등급에 적합하여야 한다. 그 렇지 않을 경우, 안전작업절차(부속서 B 참조)하에서만 전원을 공급하거나 접속되어야 한다. 5.10.3 (개인)착용형 기기 배터리나 태양광으로 작동되는 (개인)착용형 기기를 소지한 사람이 실수로 폭발위험장소에 해당 기기 를 반입하는 경우가 있다. 기본적인 전자 손목시계는 과거 및 현행 기기보호등급 요구사항에 따라 폭발위험장소에서 사용할 수 있는 기기로 독립적으로 평가받은 저전압 전자기기의 한 예이다. 그 밖의 모든 배터리 또는 태양광 작동 (개인)착용형 기기(다른 장치가 장착되어 있는 전자 손목시계 포함)는 다음 중 하나에 해당되어야 한다. a) 기기보호등급, 가스/분진 그룹 및 온도등급 요구사항에 적합한 것으로 인정된 방폭구조 준수 b) 위험성 평가 수행 c) 안전작업절차에 따라 폭발위험장소로 반입 비고 (개인)착용형 전자 기기에 전원을 공급하는 리튬 배터리가 특히 위험성이 높다. 5.11 회전 전기기기 5.11.1 일반사항 회전 전기기기 선정 시에는 5.1 ~ 5.10 의 요구사항 외에 추가적으로 최소한 다음 사항들을 고려해야 한다. 듀티 형식(duty type) (KS C IEC 60034-1 분류 기준 S1 ~ S10) 공급 전압 및 주파수 범위 구동되는 장치(예를 들면 펌프)로부터 열전달 23 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
962d0a52-f188-409e-8c3d-65d8f6fd3b2a | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 베어링 및 윤활유 수명 절연 등급 케이블 연결 및 케이블 인입 건전성에 영향을 줄 수 있는 진동 및 기타 요인에 영향을 받는 전동기 는 추가적으로 다음 사항에 대해 주의 해야 한다. 접속 불량으로 인한 과도한 발열을 피하기 위하여 단자대의 나사 및 너트가 단단히 조여 있는지 확인 글랜드와 케이블 장력 완화에 사용되는 부품이 케이블 접속부에 응력을 가하지 않고 글랜드의 건 전성을 유지할 수 있도록 단단히 조여져 있는지 확인 5.11.2 회전 전기기기 설치 시 고려해야 하는 환경 요인 전동기 및 발전기는 냉각을 위하여 대량의 청정 공기를 필요로 하며, 냉각에 영향을 미치는 다음과 같은 환경 요인을 고려해야 한다. 깨끗하고 환기가 잘되는 장소 - 기계 외함이 위치, 환경 및 주위 조건에 적합해야 함. 설치 장소에 분진이나 입자가 존재하는 경우 공기 필터가 제공되거나 심한 경우 해당 기계는 밀 폐되어야 함. 다른 기기, 벽, 건물 등으로 인해 기계 환기나 환기 순환이 방해받지 않아야 함. · 일상적인 유지보수를 위하여 기계 주변에 충분한 공간 확보 · 상부 덮개를 분리할 수 있도록 기계 상부에 충분한 공간 확보 · 부식성(산 및 염기) 가스 및 액체가 없는 환경 분진 점화 방지 컬렉터 링 하우징, 부속 장치 또는 전선관 박스가 함께 제공된 기계의 경우, 해체 및 재조립 중에 흠(nick)이나 버(burr)가 발생하면 폭발 방지 또는 분진 점화 방지 기능이 손상될 수 있 으므로 특히 세심한 주의 가 필요하다. 5.11.3 전원 및 부속 장치 연결, 접지 관련 설치 및 사용설명서와 국내외 규정을 준수해야 한다. 접속은 유효한 안전 규정에 따라 전문가 에 의해서만 수행되어야 한다. 전원 연결은 다음과 같이 제조자 설명서에 따라 이뤄져야 한다. 표시된 정격의 준수; 전류, 주 전압 및 주파수 형식비교; 보호 스위치 설정을 위한 정격 전류 준 수; 단자 박스의 배선도에 따라 전동기 연결; 공칭 전류, 케이블 길이 및 주위온도에 따라 케이블 크기 결정 케이블글랜드의 방폭구조, 케이블의 허용 최고온도 준수 배선망의 접지 조건. 전동기 접지는 접지 단자를 통해 제공되며, 이 접지 단자는 설치 배치에 따 라 플랜지 엔드 실드(flange end shield)의 프레임에 위치될 수도 있다. 또한 모든 전동기에는 단자 박스 내부에 보호 도체 단자가 있다. 명판에 명시된 바에 따라 특정 전기기기에는 다음 부속품이 포함될 수 있다. 24 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
ec6d0a01-258a-4824-ad32-d7220d498a95 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 고정자 권선 저항 온도 감지기(슬롯 검출기, HV) 권선 시스템(LV)에 내장된 온도센서 베어링 온도 감지기, 선택: 저항 또는 열전대, 판독 기능, 경보 및 전원차단 접점 기능 자체 온도등급을 가진 스페이스 히터 진동 센서 회전 속도계 베어링 오일 저장용기용 추가 히터 공기 필터의 과도한 압력 강하를 위한 제어장치 추가 기기는 다양한 방폭구조, 온도등급, 가스/분진 그룹을 포함한 자체적인 요구사항을 준수해야 한 다. 분진 및 습기 유입을 막기 위해 단자 박스의 사용하지 않은 케이블 인입구는 KS C IEC 60079 에 따 른 블랭킹 엘리먼트(blanking element)로 밀봉해야 하며 비틀림 방지 밀봉(torsion proof seal)을 해야 한다. 과도한 전달 저항을 피하기 위해 모든 단자의 나사 및 너트를 단단히 조여야 한다. 케이블을 단자 박스에 인입한 후, 글랜드 및 응력 완화에 사용되는 부품을 케이블글랜드 제조자의 사양에 따 른 토크값으로 조여야 한다. 5.11.4 컨버터로부터 전력을 공급받는 전동기 컨버터에 의해 가변 주파수 및 가변 전압을 공급받는 전동기의 선정 및 설치 시에는 전동기 단자에 서 전압을 감소시킬 수 있는 요인을 고려한다. 또한 그 밖의 위험 요인들도 고려해야 한다. 비고 1 컨버터 출력 필터가 전동기 단자에서 전압 강하를 일으킬 수 있다. 전압이 감소되면 전동기 전류 및 슬립을 증가시키며, 이로 인해 전동기의 고정자 및 회전자 온도가 높아진다. 이러한 온도 상승은 일정한 정격 부하 조건에서 가장 두드러지게 나타난다. 비고 2 컨버터로부터 전력을 공급받는 전동기 사용에 관한 추가 정보는 IEC/TS 60034-17 및 IEC/TS 60034-25 에서 제공된다. 이 표준들은 전압과 전류의 주파수 스펙트럼과 추가 손실, 과전압 효과, 베어링 전류 및 고주파 접지에 대해 다루고 있다. 5.11.5 1 kV 초과 개폐용 전동기 5.11.5.1 일반사항 진공 차단기 또는 진공 접촉기를 사용할 경우 개폐 과전압이 발생할 수 있으며, 고전압 전동기가 꺼 질 때 다중 재점호(multiple restrikes)라고도 하는 개폐 과도현상(switching transients)이 발생할 수 있 다. 이러한 과도현상은 다음과 같은 다양한 설치 시스템 및 설계 요소에 따라 다르게 나타난다. 접촉기 또는 스위치의 아크 소호(arc-extinguishing) 원리 전동기의 크기 - 전원 공급 케이블의 길이 시스템 정전용량 및 기타 요인 25 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
413fe69c-1f9a-4456-8c47-db4ac04e723f | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 경우에 따라 다중 재점호로 인해 전동기 고정자 권선의 절연체에 너무 높은 스위칭 과전압이 발생하 여 절연체 손상 및 점화성 스파크가 발생할 수 있다. 스위칭 과전압은 일반적으로 600 A 를 초과(IA > 600 A) 하는 기동전류를 가지는 고전압 전동기가 기동, 실속 또는 과부하로 전원이 차단될 때 발 생한다. 스위치기어 내부의 회로 차단기와 전동기 케이브 단자 사이에는 3 개의 도체 각각에 대해 대지와 연 결되는 과도전압 제한장치가 설치되어야 한다. 피크전압은 권선 절연체에 손상을 줄 수 있으며, 이는 절연체 손상 및 점화성 스파크를 유발할 수 있다. 전동기 개폐에 진공 회로 차단기 또는 진공 접촉기를 사용하는 경우, 전동기 설계 시 스파크 갭이 있는 산화 아연 바리스터(varistor)와 같은 적절한 과도전압 제한장치의 사용을 고려해야 한다. 비고 이 기동 전류 한계는 전동기 기동 시 기동 전류 IA 와 정격 전류 IN 사이의 관계 및 전압 강하 (최대 약 20 %)에 따른 다음과 같은 상한 전력 한계에 따라 결정된다. 최대 3.0 kV 까지 공급되는 전동기의 경우 약 750 kW 최대 6.0 kV 까지 공급되는 전동기의 경우 약 1 500 kW 최대 10.0 kV 까지 공급되는 전동기의 경우 약 2 500 kW 5.11.5.2 개폐 동작으로 인한 과전압 전동기 크기와 사용되는 스위치의 아크 소화 원리와 관계없이(즉, 무오일, SF6 또는 에어브레이크 스 위치의 경우에도) 3 kV ~ 13.8 kV 의 고전압 전동기 및 그 개폐장치를 시운전할 때는 다음 사항에 주의 해야 한다. 기동 중에 전동기를 정지하면 과전압이 발생할 수 있다. 이로 인해 전동기가 손상되고 전동기 외함 및 주 단자 박스 내부에서 스파크가 발생할 수 있다. 따라서 기동 제어의 오류를 점검하거나 보호 설정이 과도하게 민감하게 설정되어 있지 않은지 점검하는 등 기동 중에 전동기가 꺼지지 않도록 하 기 위한 예방 조치를 취해야 한다. 회전 방향 확인 또는 다른 시험을 실시하기 위한 기동 중 정지는 최소한으로만 실시해야 한다. 5.12 등기구 등기구 선정 시 다른 소비전력의 램프를 사용할 수 있는 경우, 온도등급 변화 가능성을 고려해야 한다. 일부 등기구는 사용되는 램프의 형식 또는 정격에 따라 온도등급이 달라질 수 있다. 요구되는 온도 등급에 따라 사용할 램프구의 형식 또는 정격을 선택해야 한다. 램프 교체식 등기구를 선정하는 경우 추가 설치부품 없이 개조되지 않은 표준 램프만 사용 가능한 형식이어야 한다. 저압 나트륨 램프의 경우, 램프가 깨지면서 발생하는 나트륨 누출로 인한 점화 위험성이 있으므로, 이를 방지하기 위한 대책을 마련하지 않고서는 폭발위험장소에 반입할 수 없다. 비고 일부 램프는(예: HO 형 형광등) 노화 과정에서 점화원이 될 수 있는 고온부(hot spot)가 생성될 수 있다. 26 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
2fab36c2-541b-4fdf-9f4c-683f07b9657b | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 5.13 플러그 및 소켓 5.13.1 일반사항 EPL "Ga" 또는 "Da"가 요구되는 장소에서는 플러그 및 소켓을 사용할 수 없다. 비고 Ex"i" 방폭구조에 사용되는 커넥터는 플러그 및 소켓으로 분류되지 않는다. 5.13.2 폭발성 분진 환경에 대한 요구사항 기기보호등급 "Db" 및 "Dc"가 요구되는 장소에서 사용하는 소켓은 플러그 연결 여부와 무관하게 분 진이 유입되지 않도록 설치해야 한다. 의도치 않게 뚜껑이 열린 경우에도 분진 유입을 최소화하기 위해서는 수직 방향 대비 60° 이하의 각도로, 개구부가 아래쪽으로 향하도록 소켓을 설치해야 한다. 폭발성 분진 분위기의 위험이 있는 장소에서 결합기(coupler)를 사용하는 경우, 분리된 결합기에 분진 이 들어가지 않도록 주의 해야 한다. 5.13.3 위치 소켓은 IEC 60364-4-41 에서 요구되는 고장 발생 시 차단 시간을 만족시키기 위하여 필요한 가요 코 드의 길이가 최소화될 수 있는 곳에 설치해야 한다. 5.14 전지 및 배터리 5.14.1 2 차 전지 및 배터리의 충전 전지 및 배터리는 인증서 및 제조자의 사용설명서에 폭발위험장소 내에서의 충전을 허용하는 경우가 아닌 한 비폭발위험장소에서만 충전해야 한다. 비고 1 Ex "d" 용기 내부 전지의 충전도 포함한다. 전기기기를 폭발위험장소로 다시 반입하기 전에 다음과 같은 사항을 확인해야 한다. · 온도가 표시된 온도등급보다 낮은지 여부 · 충전 시 발생한 가스가 용기 내부에 잔류하고 있는지 여부 비고 2 관련 국가 표준 또는 지역 표준(예를 들면 IEC 62485-2)을 준수하는 배터리실(battery room)은 일반적으로 안전한 장소로 간주된다. 5.14.2 환기 용기에 배터리 환기용 개구부가 존재하는 경우, 설치로 인하여 개구부가 영향을 받지 않아야 한다. 5.15 RFID 태그 5.15.1 일반사항 고전류 전기 분해 공장 등에서와 같이 1 A/m 또는 3 V/m 의 실훗값(RMS)을 초과 하는 높은 전자기장 이 존재하는 환경에서는 RFID 태그를 사용할 수 없다. 27 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b754d729-684f-4767-a365-3f048d168633 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 5.15.2 수동형 RFID 태그 배터리 구동형이 아니고 RF 판독기를 통해서만 전력을 공급받는 수동형 RFID 태그는 그 구성이 단 순 기기 요구사항을 만족한다면 인증을 받을 필요가 없다. 수동 RFID 태그는 제조자가 별도로 지정하지 않은 한 주위온도 Tamb ≤ 40 °C 에서는 온도등급 T6, 주 위온도 Tamb ≤ 60 °C 에서는 온도등급 T5 인 것으로 간주된다. 5.15.3 RFID 태그 부착 태그 용기는 6.5 의 요구사항을 따라야 한다. 기기보호등급 "Ga" 또는 "Da"가 요구되는 장소의 경우, 기기와 함께 인증된 RFID 만 사용할 수 있다. 기기보호등급 "Gb" 또는 "Db"가 요구되는 장소의 경우, 다른 기기의 연면거리 및 공간거리가 줄어드 는 것을 방지하기 위해 예상 가능한 실수(예를 들어 태그를 떨어뜨림)를 방지할 수 있는 특별한 예방 조치를 취해야 한다. 태그 부착으로 인해 태그 자체의 특성이 손상되지 않아야 하며, 부착된 기기의 방폭구조에 부정적인 영향을 미쳐서는 안 된다. 접착제를 사용할 경우 최고 작동온도를 고려해야 한다. 설치로 인하여 연면거리 및 공간거리가 영향을 받으면 안 된다. 손상된 RFID 태그는 폭발위험장소로 반입할 수 없다. 5.16 가스 감지기 이 표준의 다른 요구사항을 만족시키지 않는 전기기기를 폭발위험장소에서 사용하기 위해 필요한 통 제 수단의 일환으로 가스 감지를 사용할 수 있다(4.1 참조). 가스 감지기는 KS C IEC 60079-29-1 ~ IEC 60079-29-4 에 규정된 모든 관련 요구사항을 준수해야 한다. 6 위험한(점화성) 스파크로부터의 보호 6.1 구조용 재료로서의 경금속 금속 설치 자재(예: 케이블 트레이, 설치판, 내환경 자재 및 용기 등)의 재료 조성은 다음과 같은 요 구사항을 준수해야 한다. 기기보호등급에 따라 그룹 II 로 분류되는 기기의 설치에 사용되는 재료는 질량 기준으로 다음을 초과 할 수 없다. 기기보호등급 "Ga"의 경우 알루미늄, 마그네슘, 티타늄 및 지르코늄 총량 기준 10 % 이하 마그네슘, 티타늄 및 지르코늄 총량 기준 7.5 % 이하 기기보호등급 "Gb"의 경우 마그네슘, 티타늄 및 지르코늄 총량 기준 7.5 % 이하 28 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
22709b3a-84c5-459e-bb4c-33357b9cef18 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 기기보호등급 "Gc"의 경우 요구사항 없음. 기기보호등급에 따라 그룹 III 으로 분류되는 기기의 설치에 사용되는 재료는 질량 기준으로 다음을 초과 할 수 없다. · 기기보호등급 "Da"의 경우 마그네슘, 티타늄 및 지르코늄 총량 기준 7.5 % 이하 기기보호등급 "Db"의 경우 마그네슘, 티타늄 및 지르코늄의 총량 기준 7.5 % 이하 기기보호등급 "Dc"의 경우 요구사항 없음. 외부 구조에 경금속이 사용되는 기기의 경우 마찰 접촉 조건에서 스파크를 일으키는 것으로 알려져 있으므로 이러한 기기가 설치된 위치에서는 특별한 주의 를 기울여야 한다. 비고 위 값은 KS C IEC 60079-0 에서 발췌되었다. 6.2 통전부로 인한 위험 폭발성 분위기를 점화시킬 수 있는 스파크 형성을 방지하기 위하여, 단독의 본질안전 부품 또는 에 너지 제한 부품(energy-limited parts)을 제외한 나도체와 부주의 한 접촉을 회피하여야 한다. 비고 동시에 두 개 이상의 본질안전회로가 접촉되면서 발생하는 스파크는 점화원으로 작용할 수 있 다. 6.3 노출 및 외부 도전부로 인한 위험 6.3.1 일반사항 안전을 위해 반드시 구조물(frameworks) 또는 용기의 지락전류를 제한하고(크기 및/또는 시간), 등전 위 본딩 도체의 전위 상승을 방지해야 한다. 가능한 모든 전력 시스템에 적용하는 것은 현실적으로 어렵지만, 본질안전회로와 에너지 제한회로를 제외한 교류 1 000 V 직류 1 500 V 이하의 전력시스템에는 다음과 같은 기준이 적용된다. 6.3.2 TN 시스템 접지 TN 시스템 접지를 사용하는 경우, 폭발위험장소에서 중성선(N)과 접지선(PE)이 분리된 TN-S 방식을 사용해야 한다. 즉, 폭발위험장소 내에서는 중성선과 접지선을 서로 연결시키거나 단일 도체로 병합 해서는 안 된다(combined in a single conductor). TN-C 에서 TN-S 로 변경되는 지점에서 보호 도체를 비 폭발위험장소의 등전위 본딩 시스템과 접속하여야 한다. 6.3.3 TT 시스템 접지 TT 시스템 접지를 사용하는 경우(전력시스템과 노출 도전부의 접지가 분리된 경우) 누전차단기 (residual current device)에 의해 보호되어야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 29 | {}
007ca216-fad1-4cd5-9c87-2397237e43dd | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 비고 대지 저항률이 높은 경우에는 이러한 시스템이 허용되지 않을 수 있다. 6.3.4 IT 시스템 접지 IT 시스템 접지를 사용하는 경우(중성점이 접지되어 있지 않거나, 충분한 고임피던스로 접지된 경우), 1 차 지락사고를 감지하기 위한 절연 감시 장치(insulation monitoring device)를 설치해야 한다. 비고 1 1 차 고장이 제거되지 않으면 동일 상의 후속 고장이 감지되지 않아 위험한 상황이 발생할 수 있다. 비고 2 추가 등전위 본딩이라고도 하는 국소 본딩이 필요할 수 있다(IEC 60364-4-41 참조). 6.3.5 SELV 및 PELV 시스템 안전특별저전압(SELV) 시스템은 IEC 60364-4-41:2005 의 414 를 준수해야 한다. SELV 의 통전부를 접 지하거나 또는 타 통전부나 다른 회로를 구성하는 보호도체 등에 접속해서는 안 된다. 노출된 도전 부는 접지를 하거나 하지 않을 수 있다(예를 들어 전자파 적합성을 위해). 보호특별저전압(PELV) 시스템은 IEC 60364-4-41:2005 의 414 를 준수해야 한다. 모든 노출된 도전부는 공통 접지(및 등전위) 시스템에 연결해야 한다. SELV 및 PELV 용 안전 절연 변압기는 KS C IEC 61558-2-6 을 준수해야 한다. 6.3.6 전기적인 분리 전기적인 분리는 기기의 한 품목에 대한 전원을 공급하기 위해 IEC 60364-4-41:2005 의 413 에 따라야 한다. 6.3.7 폭발위험장소 상부의 비 방폭전기기기 점화원이 될 가능성이 있거나 고온 입자 또는 고온 표면을 생성할 수 있는 비방폭전기기기 및 전기 회로 연결부가 폭발위험장소 상부에 존재하는 경우 특별한 주의 가 필요하다. 이런 경우 해당 기기를 완전히 밀폐시키거나 적절한 보호 또는 차폐 조치를 통해 해당 기기 또는 고온 입자가 폭발위험장소 로 낙하하지 않도록 해야 한다. 위험성 평가 시 기기 또는 전기회로 연결부를 포함한 해당 부품의 손상 또는 고장으로 폭발위험장소 로 낙하하여 점화원을 발생시킬 가능성을 고려해야 한다. 비고 해당 품목은 다음과 같다. · 아크, 스파크 또는 고온 입자를 생성할 수 있는 퓨즈 · 아크, 스파크 또는 고온 입자를 생성할 수 있는 스위치, 플러그 및 소켓 · 미끄럼 접촉 또는 브러시가 있는 전동기 또는 발전기 · 아크, 스파크 또는 고온 입자를 생성할 수 있는 히터, 발열체 또는 기타 기기 · 모든 형태의 방전 등기구용 안정기, 커패시터 및 시동 스위치와 같은 보조 기기 · 모든 노출된 램프 · 지지되지 않는 모든 케이블 저압 나트륨 방전 램프는 폭발위험장소 상부에 설치할 수 없다. 30 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
aed85a58-b49b-4698-8100-ea57d85d8c1a | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 6.4 등전위 6.4.1 일반사항 폭발위험장소 내의 설치에는 등전위가 요구된다. TN, TT 및 IT 시스템의 경우 모든 노출된 도전부를 등전위 본딩 시스템에 연결해야 한다. 본딩 시스템은 보호 도체, 금속 전선관, 금속 케이블 피복, 강 선외장 및 구조물의 금속부 등을 포함하나 중성선은 포함하지 않는다. 연결부는 스스로 풀리지 않도 록 단단히 결속시켜야 하며, 연결 효율성을 감소시킬 수 있는 부식 위험을 최소화해야 한다. 예를 들어 별도의 개별 접지 태그를 사용하지 않고 금속 케이블글랜드를 사용할 수 있도록 내부 접 지 연속판을 설치할 수 있다. 접지 연속판의 소재 및 치수는 예상되는 고장 전류에 적합하여야 한다. 케이블 외장 또는 스크린이 폭발위험장소 외부(예를 들면 제어실)에서만 접지되는 경우, 해당 접지 지점도 폭발위험장소의 등전위 시스템에 포함되어야 한다. 케이블 외장 또는 스크린이 TN 시스템에서 폭발위험장소 외부에서만 접지되는 경우, 폭발위험장소의 아머 또는 스크린 끝부분에서 위험한 스파크가 발생할 수 있다. 따라서 이런 외장이나 스크린은 사 용하지 않은 심선(cores)처럼 취급해야 한다(9.6.3 참조). 노출된 도전부가 등전위 본딩 시스템에 접속되어 있는 구조물 또는 배관에 확실하게 전기적으로 연 결되었다면, 등전위 본딩 시스템에 별도로 접속할 필요가 없다. 문틀이나 창틀과 같이 전기기기 또는 구조물의 일부가 아닌 시스템 외 도전부의 경우, 전위차에 의한 위험이 없다면 등전위 본딩 시스템 에 접속할 필요가 없다. 케이블의 브레이드나 외장을 고정시키는 클램핑 장치가 포함된 케이블글랜드는 등전위 본딩에 사용 할 수 있다. 보호 레일과 의 주 연결을 위한 본딩 도체의 최소 크기는 6 mm2 여야 하고 보조 연결부는 최소 4 mm2 이상이어야 한다. 기계적 강도를 확보하기 위해 더 큰 도체를 사용하는 것도 고려해야 한다. 본질안전 또는 에너지 제한 기기의 금속 용기는 해당 기기의 관련 문서에서 별도로 요구하거나 정전 기 축적을 방지하기 위해 특별히 필요한 경우가 아니라면 등전위 본딩 시스템에 접속할 필요가 없다. 음극방식을 위해 특별히 설계된 등전위 본딩 시스템이 아닌 한, 음극방식이 되어 있는 기기를 본딩 시스템에 접속하지 않아야 한다. 이동용 차량(vehicles)과 고정 설치물 사이의 등전위는 특별한 조치가 필요할 수 있다(예를 들어 파이 프 라인을 연결하기 위하여 절연된 플랜지가 사용). 6.4.2 임시 본딩 임시 본딩은 정전기를 제어하거나 등전위를 확보하기 위해서 드럼, 이동용 차량(vehicle), 휴대형 기 기 등과 같은 이동 가능한 기기를 접지하는 것을 포함한다. 임시 본딩의 최종 접속은 다음 중 한 가지 방식을 사용할 것을 권장한다. · 비폭발위험장소에서 접속 · 해당 장소의 기기보호등급 요구사항을 만족하는 접속방법 사용 · 스파크 발생 위험성을 허용 가능한 수준으로 줄일 수 있는 문서화된 절차 사용 31 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
805fafd2-8c29-4e10-a06b-5849eae73a45 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 임시 본딩 시 금속부들 사이의 저항은 1 MO 보다 작아야 한다. 이 저항값을 측정 또는 모니터링하여 확보하여야 한다. 도체와 접속부는 내구성이 높고 유연하며, 정상 작동 중의 움직임을 견딜 수 있는 충분한 기계적 강도를 가져야 한다. 도체의 기계적 강도는 적어도 4 mm2 구리와 동등한 수준이거나 모니터링 및 제어 시스템이 포함된 가요 배선 시스템의 일부여야 한다. 연결 시스템의 저항이 항상 1 M� 미만임을 확인하기 위한 영구 모니터링 시스템의 사용도 고려해야 한다. 6.5 정전기 6.5.1 일반사항 6.5.1 의 요구사항은 인증된 기기의 일부가 아닌 설치 또는 보호 목적으로 사용되는 외부 비금속 재료 에 적용된다[예를 들어 플라스틱 덮개가 달린 케이블 트레이, 플라스틱 설치판, 플라스틱 내환경 보 호부(weather protection) 및 용기 등]. 비고 1 금속부의 외부 표면에 사용되는 비금속 페인트, 필름, 포일 및 판(plate)은 일반적으로 추가적 인 내환경 성능을 제공하기 위해서 사용된다. 이러한 부분의 정전기 충전은 6.5 에 언급된다. 비고 2 일반적으로 유리에는 정전기가 잘 축적되지 않는다. 비고 3 추가적인 정보는 IEC TS 60079-32-1 및 IEC 60079-32-2 에서 제공된다. 6.5.2 기기보호등급 "Ga" , "Gb" 및 "Gc"가 요구되는 장소에서 사용되는 설치부 또는 보호부의 정 전기 방지 설치부 및 보호부는 정상 사용 및 유지보수, 청소 시 정전기로 인한 점화 위험을 방지할 수 있도록 설계해야 한다. 이 요구사항은 다음 중 한 가지 방법으로 만족되어야 한다. a) KS C IEC 60079-0 에 따라 측정한 최대 표면 저항이 다음과 같은 기준 중 하나를 만족시킬 수 있는 적절한 재료 선택 (50±5)% 상대습도에서 측정 시 109 � (30±5)% 상대습도에서 측정 시 1011 � b) 표 5 에 따른 비금속부의 표면적 제한 표면적은 다음과 같이 정의 된다. 판재의 경우, 노출된(충전 가능한) 면적 곡면이 있는 경우, 면적을 최대로 하는 투영면적 개별 비금속부의 경우, 도전성 접지 프레임으로 분리된 경우 개별적으로 평가 비금속 재료의 노출면이 접지된 도전성 프레임에 의해 둘러싸여 접촉되어 있는 경우 표면적 값이 4 배 늘어날 수 있다. 튜브, 막대, 로프 등과 같이 비금속 표면이 있는 긴 부재의 경우, 그 지름 또 는 너비가 표 6 의 기준치를 초과 하지 않아야 한다. 외부 회로 연결용 케이블에는 이 요구사항이 적용되지 않는다. c) 도전성 표면에 본딩된 비금속층의 두께 제한. 비금속층의 두께가 표 7 의 기준값을 초과 하지 않거나 32 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
7272ec61-8328-413d-b8ed-b83f5fa4c1cb | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 (KS C IEC 60243-1 에 따라 절연재 두께에 걸쳐 측정한) 절연파괴 전압이 4 kV 이하이어야 한다. d) 정전기 방전 위험을 최소화하는 방식으로 설치부 및 보호부가 사용된 경우, 해당 부에 다음과 같 은 경고 라벨을 부착해야 한다. 경고 - 정전기 위험(WARNING - POTENTIAL ELECTROSTATIC CHARGING HAZARD) 표 5 - 표면적 제한 ¦ 설치 및 보호부(mm2) ¦ 설치 및 보호부(mm2) ¦ 설치 및 보호부(mm2) ¦ 설치 및 보호부(mm2) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 필요한 기기보호등급 ¦ 그룹 IIA ¦ 그룹 IIB ¦ 그룹 IIC ¦ ¦ EPL Ga ¦ 5 000 ¦ 2 500 ¦ 400 ¦ ¦ EPL Gb ¦ 10 000 ¦ 10 000 ¦ 2 000 ¦ ¦ EPL Gc ¦ 10 000 ¦ 10 000 ¦ 2 000 ¦ 표 6 - 최대 지름 또는 너비 ¦ 설치 및 보호부(mm) ¦ 설치 및 보호부(mm) ¦ 설치 및 보호부(mm) ¦ 설치 및 보호부(mm) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 필요한 기기보호등급 ¦ 그룹 IIA ¦ 그룹 IIB ¦ 그룹 IIC ¦ ¦ EPL Ga ¦ 3 ¦ 3 ¦ 1 ¦ ¦ EPL Gb ¦ 30 ¦ 30 ¦ 20 ¦ ¦ EPL Gc ¦ 30 ¦ 30 ¦ 20 ¦ 표 7 - 비금속층 두께 제한 ¦ 설치 및 보호부(mm) ¦ 설치 및 보호부(mm) ¦ 설치 및 보호부(mm) ¦ 설치 및 보호부(mm) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 필요한 기기보호등급 ¦ 그룹 IIA ¦ 그룹 IIB ¦ 그룹 IIC ¦ ¦ EPL Ga ¦ 2 ¦ 2 ¦ 0.2 ¦ ¦ EPL Gb ¦ 2 ¦ 2 ¦ 0.2 ¦ ¦ EPL Gc ¦ 2 ¦ 2 ¦ 0.2 ¦ ¦ 이 두께 제한은 표면저항이 109 � 또는 1011 요 미만인 비금속층에는 적 용되지 않는다. KS C IEC 60079-0 를 참조한다. 두께 제한을 두는 중요한 이유 중 하나는 최대 두께의 비금속층이 접 지된 절연재를 통해 정전기를 소모(dissipation)시킬 수 있기 때문이다. 이를 통해 정전기가 점화 가능 수준 이상으로 축적되는 것을 방지할 수 있다. ¦ 이 두께 제한은 표면저항이 109 � 또는 1011 요 미만인 비금속층에는 적 용되지 않는다. KS C IEC 60079-0 를 참조한다. 두께 제한을 두는 중요한 이유 중 하나는 최대 두께의 비금속층이 접 지된 절연재를 통해 정전기를 소모(dissipation)시킬 수 있기 때문이다. 이를 통해 정전기가 점화 가능 수준 이상으로 축적되는 것을 방지할 수 있다. ¦ 이 두께 제한은 표면저항이 109 � 또는 1011 요 미만인 비금속층에는 적 용되지 않는다. KS C IEC 60079-0 를 참조한다. 두께 제한을 두는 중요한 이유 중 하나는 최대 두께의 비금속층이 접 지된 절연재를 통해 정전기를 소모(dissipation)시킬 수 있기 때문이다. 이를 통해 정전기가 점화 가능 수준 이상으로 축적되는 것을 방지할 수 있다. ¦ 이 두께 제한은 표면저항이 109 � 또는 1011 요 미만인 비금속층에는 적 용되지 않는다. KS C IEC 60079-0 를 참조한다. 두께 제한을 두는 중요한 이유 중 하나는 최대 두께의 비금속층이 접 지된 절연재를 통해 정전기를 소모(dissipation)시킬 수 있기 때문이다. 이를 통해 정전기가 점화 가능 수준 이상으로 축적되는 것을 방지할 수 있다. ¦ 6.5.3 기기보호등급 "Da", "Db" 및 "Dc"가 요구되는 장소에서 사용되는 설치부 및 보호부의 정전 기 방지 도색 또는 코팅된 금속 및 플라스틱 재질의 설치부 및 보호부는 정상 사용 조건에서 전파 브러시 방 전(propagating brush discharge)으로 인한 점화 위험을 방지하도록 설계하여야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 33 | {}
a28dd824-0731-415d-abec-af3d91b42625 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 500 mm2 를 초과 하는 표면적을 가진 플라스틱을 도전성 재료를 덮는 용도로 사용하는 경우, 다음 중 한 가지 이상의 특성을 가진 플라스틱을 사용해야 한다. a) 표면 저항이 KS C IEC 60079-0 에 규정된 제한 기준 이하인 재료 b) 절연파괴 전압 ≤ 4 kV(KS C IEC 60243-1 에 따라 절연재 두께에 걸쳐 측정) c) 정전기 방전 위험을 최소화하는 방식으로 설치부 및 보호부가 사용된 경우, 해당 부품에 다음과 같은 경고 라벨을 부착해야 한다. 경고 - 정전기 위험(WARNING - POTENTIAL ELECTROSTATIC CHARGING HAZARD) 케이블이 마찰 효과 및 분진의 통과 로 인한 정전기 축적에 노출되지 않도록 케이블 라우팅을 해야 한다. 케이블 표면에 정전기가 축적되지 않도록 예방조치를 취해야 한다. 6.6 낙뢰 보호 전기설비 설치작업의 계획 수립 시 단계별로 낙뢰의 영향을 안전 수준 이하로 줄이기 위한 조치를 취해야 한다(IEC 62305-3:2010, 부속서 D 참조). 기기보호등급 "Ga"를 요구하는 장소에 설치되는 Ex "ia" 기기에 대한 낙뢰 보호에 관한 세부 사항은 16.3 에 따른다. 6.7 전자기 방사 6.7.1 일반사항 전기설비 설치작업의 계획 수립 시 전자기 방사의 영향을 안전한 수준으로 줄이기 위한 조치를 취해 야 한다. 6.7.2 폭발위험장소에서 수신된 무선 주파수 폭발위험장소에 설치된 구조물과 안테나는 폭발위험장소 외부에서 들어오는 무선 주파수의 전송을 수신하는 수신기 역할을 할 수 있다. 연속전송 및 펄스지속시간이 열 개시 시간을 초과 하는 펄스전 송에 대하여 폭발위험장소에서 수신되는 무선 주파수(9 kHz ~ 60 GHz)의 임계 출력은 표 8(무선 주 파수 출력 임계값)의 임계값을 초과 하지 않아야 한다. 사용자가 직접 설정할 수 있는 프로그램 또는 소프트웨어 제어는 허용되지 않는다. 비고 1 표 8 의 값은 폭발위험장소 근처에 있는 고출력 송신기에 적용된다. 플랜트로부터 장거리에 위치한 고출력 방사원에 대한 추가적인 정보는 CLC/TR 50427 에서 제공된다. TR 결과 는 원거 리장 조건(far field conditions)을 기준으로 한다. 34 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
48f598e9-a659-4b5e-8da6-da7add0be093 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 표 8 - 무선 주파수 출력 임계값 ¦ 기기 그룹 ¦ 임계 출력 W ¦ 열 개시 시간 us ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 그룹 IIA ¦ 6 ¦ 100 ¦ ¦ 그룹 IIB ¦ 3.5 ¦ 80 ¦ ¦ 그룹 IIC ¦ 2 ¦ 20 ¦ ¦ 그룹 III ¦ 6 ¦ 200 ¦ 열 개시 시간과 비교하여 펄스가 짧은 펄스 레이더 및 그 밖의 전송의 경우, 임계에너지 값 Zth 가 표 9 의 임계값을 초과 하지 않아야 한다. 표 9 - 무선 주파수 에너지 임계값 ¦ 기기 ¦ 임계 에너지 Zth uJ ¦ ¦ --- ¦ --- ¦ ¦ 그룹 IIA ¦ 950 ¦ ¦ 그룹 IIB ¦ 250 ¦ ¦ 그룹 IIC ¦ 50 ¦ ¦ 그룹 III ¦ 1 500 ¦ 비고 2 큰 안전계수가 적용되었기 때문에 표 8 과 표 9 는 "Ga" , "Gb". , "Gc". "Da" , "Db" , "Dc" 기기에 동 일한 값을 적용한다. 비고 3 표 8 및 표 9 의 값은 기기 사용자가 임의 로 기기를 보다 높은 값으로 조정할 수 없는 정상 작동 조건을 상정한 것이다. 비고 4 이 요구사항은 KS C IEC 60079-0 에서 발췌되었다. 6.8 금속부의 음극방식 폭발위험장소 내에 설치된 음극방식 금속부는 시스템 외의 통전 도전체이며, [특히, 외부전원에 의한 방식시스템(impressed current system)이 설치된 경우] 낮은 음(-) 전위에도 불구하고 위험한 전위로 간주해야 한다. 음극방식을 위한 특별한 설계가 되어 있지 않는 한, 기기보호등급 "Ga" 또는 "Da"를 요구하는 장소에 설치하는 금속부에는 음극방식을 해서는 안 된다. 파이프나 트랙에서 사용되는 절연부(insulating element)의 예와 같이, 음극방식에 필요한 절연부는 가 능한 한 폭발위험장소의 외부에 위치해야 한다. 음극방식에 관한 IEC 기준이 없기 때문에 국내 또는 기타 표준을 준수해야 한다. 6.9 광학 방사에 의한 점화 광학기기 설치작업의 계획 수립 시 5.7 에 따라 방사로 인한 영향을 안전한 수준으로 줄이기 위한 조 치를 취해야 한다. 비고 통신, 감시, 감지 및 측정 용도로 램프, 레이저, LED, 광섬유 등과 같은 광학기기가 점점 더 많 이 사용되고 있다. 소재 공정에도 높은 조도의 광학 방사가 사용되는 경우가 있다. 기기가 폭 35 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
3f4f4963-dcf2-4877-a231-a1399b0ff0ab | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 발성 분위기 내부 또는 가까이에 있는 경우가 많으며, 이 경우 기기로부터 나오는 광학 방사 가 폭발 성분위기를 통과 할 수 있다. 이 경우 방사 특성에 따라 주위 폭발성 분위기가 점화될 수도 있다. 추가적인 방사에너지 흡수체의 존재 여부도 점화에 영향을 준다. 7 전기적 보호 이 항의 요구사항은 본질안전 및 에너지 제한회로에는 적용되지 않는다. 전기회로 및 기기는 단락, 과부하, 지락으로 인한 위험한 영향으로부터 보호되어야 한다. 보호장치는 고장 조건에서 자동으로 다시 닫히지 않아야 한다. 기기보호등급 "Ga", "Gb" 또는 "Da", "Db"가 필요한 장소에서는 IEC 60364-4-41 에 규정된 것보다 더 짧은 차단 시간이 요구될 수 있다. 사용 중 과부하가 불가피할 경우 전기기기에 대한 과부하 보호가 필요하다. 하나 이상의 결상으로 인해 과열이 발생할 수 있는 다상 전기기기의 경우 상 손상 시 작동을 방지하 기 위한 예방 조치를 취해야 한다. 전기기기의 자동 차단이 점화로 인해 발생할 수 있는 위험보다 기기 안전을 더 크게 저해하는 위험 을 초래할 수 있는 경우, 자동 차단 대신 경보를 사용할 수 있다. 단 이러한 경우 신속한 조치를 취 할 수 있도록 경보는 즉각적이고 명확해야 한다. 8 전기 차단(switch-off) 및 전기적 분리 8.1 일반사항 8 절의 요구사항은 본질안전 및 에너지 제한회로에 적용되지 않는다. 8.2 전기 차단 기능상 또는 비상시 목적을 위하여 적절한 위치(필요한 경우 복수의 위치)에 폭발위험장소로의 전기 공급을 차단하는 조치가 제공되어야 한다. 추가적인 위험을 방지하기 위해 지속적으로 작동되어야 하는 전기기기는 전기 차단에 포함되지 않아 야 하며 별도의 회로로 구성되어야 한다. 비고 일반적인 스위치기어 내부에 설치된 개폐 장치는 전기 차단 시설로 충분하다. 전기 차단 시 중성선을 포함한 모든 전원 공급 도체의 차단을 고려하여야 한다. 현장 배전, 현장 인력 및 현장 운영의 특성을 고려하여 전기 차단 위치를 선정해야 한다. 8.3 전기적 분리 전기 작업을 안전하게 수행할 수 있도록 중성선을 포함한 모든 통전 도체를 전기적으로 분리할 수 있는 조치가 제공되어야 한다. 단일 장치로 모든 통전 도체를 분리할 수 없는 경우에는 남은 도체를 분리할 수 있는 조치를 명확하게 제공하여야 한다. 36 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
e01289c4-e6a5-4818-8215-16240202592b | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 모든 관련 도체를 동시에 분리시킬 수 있는 단일 장치를 사용하는 것이 가장 바람직하다. 전기적 분 리 조치는 관련되는 경우 퓨즈나 중성선 링크(neutral link)를 포함할 수 있다. 각 분리 장치마다 라벨을 부착하여 해당 분리 장치에 의해 분리되는 회로 또는 회로 그룹을 즉시 식 별할 수 있도록 해야 한다. 보호되지 않은 통전부가 폭발성 분위기에 노출되어 있는 상태에서 전기기기에 전원이 재공급되는 것 을 방지하기 위한 효과 적인 수단 또는 절차가 제공되어야 한다. 9 케이블 및 배선시스템 9.1 일반사항 케이블 및 배선 시스템은 9 절의 관련 요구사항을 준수해야 한다. 9.2 알루미늄 도체 도체 재료로 알루미늄을 사용하는 경우 적합한 접속부를 사용해야 하며, 본질안전 및 에너지 제한 기기를 제외하고 최소 16 mm2 의 단면적을 가져야 한다. 알루미늄 도체 연결을 위해 필요한 추가적인 연결부가 필요한 연면거리 및 공간거리를 감소시켜서는 안 된다. 최소 연면거리 및 공간거리는 전압 수준 및/또는 방폭구조 요구사항에 따라 결정할 수 있다. 전식 예방조치가 고려되어야 한다. 9.3 케이블 9.3.1 일반사항 내부 또는 외부 피복(sheath)의 인장강도가 8.5 MPa 미만인 케이블을 사용하면 안 된다. 비고 8.5 MPa 미만의 인장강도를 갖는 케이블은 통상 "쉽게 찢어지는(easy tear)" 케이블로 알려져 있다. 9.3.2 고정 설치용 케이블 폭발위험장소 내 고정 설치되어 사용되는 케이블은 사용 환경에 적합해야 하며, 다음 중 한 가지 케 이블을 사용해야 한다. a) 열가소성, 열경화성 또는 탄성 재료로 피복된 케이블. 원형이고 치밀하여야(compact) 함. 베딩(bed ding)이나 피복은 압출되어야 함. 필러(filler)가 사용되는 경우 비흡습성이어야 함. b) 무기질 절연 금속 피복 케이블(mineral insulated metal sheathed) c) 특수 케이블. 예를 들어 적절한 케이블글랜드가 사용된 평면 케이블. 치밀해야 하며 베딩이나 피 복은 압출되어야 함. 필러가 사용되는 경우 비흡습성이어야 함. 37 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
4c226f6a-7bbc-4fcf-b561-a7aaad2b8ca5 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 개별 심선 사이의 틈새를 통해 가스 또는 증기가 유입될 가능성이 있고, 케이블이 비폭발위험장소로 연결되거나 서로 다른 종별 장소 사이를 연결하는 경우, 그에 맞는 구조 및 특성을 가진 케이블을 사용해야 한다. 또한 이런 문제를 완화시킬 수 있는 대책을 고려해야 한다(부속서 E 참조). 케이블의 각 심선 사이의 틈새를 통해 화염 전파가 발생할 가능성이 있는 경우, 이 문제도 함께 고 려해야 한다. 무기질 절연 케이블은 밀봉되어야 한다. 비고 이 요구사항은 공정 밀봉을 위한 기기 선정에는 적용되지 않는다. 9.3.3 고정형 기기에 사용되는 가요 케이블(본질안전회로 제외) 폭발위험장소의 가요 케이블은 다음 중에서 선정해야 한다. a) 보통의 경질고무 피복 가요 케이블(ordinary tough rubber sheathed flexible cables) b) 보통의 폴리클로로프렌 피복 가요 케이블(ordinary polychloroprene sheathed flexible cables) c) 강 경질고무 피복 가요 케이블(heavy tough rubber sheathed flexible cables) d) 강 폴리클로로프렌 피복 가요 케이블(heavy polychloroprene sheath flexible cables) e) 강 경질고무 피복 가요 케이블과 동등 이상의 강도를 가진 플라스틱 절연 케이블(plastic insulated cables) IEC 케이블 표준이 없는 경우에는 국가 또는 기타 표준을 준수해야 한다. 가끔씩 짧은 거리를 움직이는 고정형 기기(예를 들어 슬라이드 레일의 전동기)와 연결하는 케이블의 경우, 기기가 움직일 때 케이블이 손상되지 않도록 케이블을 배치하거나 이동형 기기에 적합한 종류 의 케이블을 사용해야 한다. 고정 배선만 사용할 경우 필요한 움직임에 적합하지 않다면 고정 배선 과 기기 배선이 연결되는, 적절하게 보호된 터미널 박스를 사용해야 한다. 가요 튜브를 사용하는 경 우, 기기의 움직임으로 인해 케이블이 손상되지 않도록 가요 튜브 및 접속부품을 설치해야 한다. 적 절한 접지 또는 본딩을 유지해야 하며, 가요 튜브가 유일한 접지 수단이어서는 안 된다. 가요 튜브는 먼지가 유입되지 않아야 하며, 가요 튜브 사용으로 인해 가요 튜브가 연결된 기기 용기의 건전성이 훼손되어서는 안 된다. 9.3.4 이동형 및 휴대형 기기에 사용되는 가요 케이블(본질안전회로 제외) 이동형 및 휴대형 전기기기에는 강 폴리클로로프렌(heavy poly chloroprene) 케이블 또는 그와 동등한 합성고무 피복(synthetic elastomeric sheath) 케이블, 강 경질고무 피복(heavy tough rubber sheath) 케 이블 또는 그에 상응하는 강도를 가진 케이블을 사용해야 한다. 심선의 굵기는 최소 1.0 mm2 이상이 어야 하며 연선(stranded cable)이어야 한다. 보호접지선이 필요할 경우에는 다른 도체와 유사한 방법 으로 분리 절연시켜 전원 공급 케이블 내부에 포함되어야 한다. 이동형 및 휴대형 전기기기에 금속 가요 외장 또는 스크린(screen)이 사용된 경우, 해당 금속 가요 외장 또는 스크린이 유일한 보호 도체여서는 안 된다. 케이블은 회로보호 조치에 적합해야 하는데, 가령 접지 모니터링이 사용되는 경우 접지 모니터링에 필요한 도체의 수량을 포함해야 한다. 기기를 접지할 필요가 있는 경우, 케이블의 보호접지(PE) 도체에 추가하여 접지된 가요 금속 스크린(earthed flexible metallic screen)을 포함할 수 있다. 38 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
6570205c-1a44-4fa1-95b6-9b9cc7770cea | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 정격전류 6A, 대지전압 250 V 이하인 휴대형 전기기기에는 다음과 같은 케이블을 사용할 수 있다: 보통의 폴리클로로프렌 또는 그와 동등한 합성고무 피복 케이블 보통의 경질고무 피복(ordinary tough rubber sheath) 케이블 그와 동등한 강도를 가진 케이블 이런 케이블들은 손전등, 발판 스위치, 배럴 펌프 등과 같이 높은 수준의 기계적 응력이 가해지는 휴 대형 전기기기에는 사용할 수 없다. 9.3.5 단일 절연 전선(본질안전회로 제외) 단일 절연 전선은 배전반, 용기 또는 전선관 시스템 내부에 설치된 경우가 아니라면 통전 도체로 사 용할 수 없다. 9.3.6 가공 선로 폭발위험장소에 전력 또는 통신 서비스를 제공하기 위하여 비절연 도체를 가공 배선으로 사용하는 경우에는 배선 터미널이 비폭발위험장소에서 끝나도록 해야 하며, 케이블 또는 전선관을 통하여 폭 발위험장소로 이어지게 한다. 절연되지 않은 도체를 폭발위험장소 상부에 설치해서는 안 된다. 비고 부분적으로 절연된 크레인용 도체 레일 시스템이나 저전압 및 특별저전압 트랙 시스템과 같은 기기도 절연되지 않은 도체에 포함된다. 9.3.7 손상 방지 케이블 시스템과 부속품은 가능한 한 기계적 손상, 부식, (용매 등으로 인한) 화학적 작용, 열, 자외선 등의 영향을 받지 않는 위치에 설치해야 한다(단, 본질안전회로에 대해서는 16.2.2.5 참조). 이러한 노출이 불가피하다면 보호 전선관 내부에 설치 등과 같은 보호조치을 마련하거나 해당 조건 에 적합한 케이블을 선택해야 한다(예를 들면 기계적 손상을 최소화하기 위해 외장, 스크린, 이음매 없는 알루미늄 외장, 무기질 절연 금속 피복 또는 반-강체외장(semi-rigid sheathed) 케이블을 사용할 수 있다). 진동 또는 지속적인 휩과 같은 외부 조건에 영향을 받는 경우, 손상 없이 그런 영향을 견딜 수 있도 록 설계된 케이블을 사용해야 한다. 영하 5 °C 이하인 곳에 케이블을 설치하는 경우, 피복이나 절연재에 발생할 수 있는 손상을 방지하기 위한 조치를 취해야 한다. 케이블이 기기 또는 케이블 트레이에 고정되어 있는 경우, 케이블 손상을 방지하기 위해 제조자의 사양을 따르거나 케이블 지름의 최소 8 배 이상인 곡률반지름을 유지해야 한다. 케이블의 굴곡은 케 이블글랜드 말단으로부터 최소 25 mm 이상 떨어진 곳에서부터 시작되어야 한다. 9.3.8 케이블 표면 온도 케이블의 표면온도는 해당 설치에서의 온도등급을 초과 하지 않아야 한다. 39 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
3be2ff3c-5839-4c2c-8ba9-f271eb8ee376 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 비고 케이블의 작동온도가 높은 경우(예를 들어 105 °C)에도 이 온도는 케이블 피복이 아닌 구리 부 분의 온도를 의미한다. 따라서 방열을 고려하면 케이블 온도가 T6 을 초과 하는 상황은 쉽게 발 생하지 않는다. 9.3.9 화염전파에 대한 내성 고정 설치용 케이블은 다음 중 하나에 해당하여야 한다. a) KS C IEC 60332-1-2 또는 KS C IEC 60332-3-22 에 따른 시험을 견딜 수 있는 화염 전파 특성 (비고 참고) b) 화염 전파에 대한 그 밖의 보호 수단(예를 들어 모래가 채워진 트렌치에 매설) c) 폭발위험장소에 진입하는 케이블에는 비폭발위험장소에서 폭발위험장소로의 화염 전파를 차단하 기 위한 배리어를 설치 비고 KS C IEC 60332-1-2 는 일반적인 시험에 1 kW 의 사전 혼합(pre-mixed) 화염을 사용하도록 규정 하고 있다. 단, 시험이 완료되기 전에 도체가 녹아버리는, 총단면적이 0.5 mm2 미만인 소형 단 일 절연 도체나 시험이 완료되기 전에 케이블이 절단되는 소형 광섬유 케이블에는 이 시험 절 차를 사용할 수 없다. 이 경우에는 KS C IEC 60332-3-22 의 시험 절차를 사용한다. 화염 전파를 지연시키고 KS C IEC 60332-1-2 의 권장 요구사항을 준수하는 절연 도체 또는 케이블을 사용하는 것만으로는 모든 설치 조건하에서 화염 전파를 방지하기에 충분하지 않을 수 있기 때문에 수직 방향으로 긴 케이블 다발을 설치해야 하는 경우와 같이 화염 전파 위험이 높은 경우에는 케이 블 설치 시 특별한 예방 조치를 취해야 한다. 케이블 시료가 KS C IEC 60332-1-2 에서 권장하는 성능 요구사항을 준수한다고 해서 케이블 다발도 비슷한 성능을 가질 것이라고 가정해서는 안 된다. 이런 경우 KS C IEC 60332-3 에 따라 수직으로 장착된 배선 또는 케이블 다발에 대한 수직 화염 전파 시험 을 통해 성능을 검증할 수 있다. 9.4 전선관 시스템 폭발위험장소에서 비폭발위험장소로 가스 또는 액체가 유입되는 것을 방지하기 위해 전선관이 폭발 위험장소로 진입하는 또는 나오는 부분에는 전선관 밀봉장치를 설치해야 한다. 밀봉장치와 폭발위험 장소의 경계 사이에는 유니언, 커플링 또는 그 밖의 접속부품이 없어야 한다. 전선관 밀봉장치는 케이블이 효과 적으로 채워진 경우에는 외부 피복을 밀봉하거나 전선관 내부에서 개별 심선 단위로 밀봉해야 한다. 밀봉재는 경화 시 수축되지 않아야 하며 폭발위험장소에서 존재하 는 화학물질로 인해 손상되거나 영향을 받지 않아야 한다. 전선관이 설치되는 용기가 보호등급(예를 들어 IP54)을 유지해야 할 경우, 용기에 근접하여 전선관 밀봉장치가 제공되어야 한다. 전선관의 모든 나사로 된 접속부는 렌치로 확실하게 조여야 한다. 전선관 시스템이 보호접지 도체로 사용되는 경우, 나사산 접합부는 퓨즈나 회로 차단기로 보호될 때 해당 회로에 흐르는 고장전류에 적합해야 한다. 전선관이 부식성 장소에 설치되어 있는 경우, 전선관 소재로 내부식성 소재를 사용하거나 전선관 자 체를 부식으로부터 충분히 보호해야 한다. 40 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
7310c455-76d9-4d0c-9607-85126171267b | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 갈바닉 부식을 일으킬 수 있는 금속 조합은 피해야 한다. 보호피복이 없는 절연된 단심 또는 다심의 케이블은 전선관 내부에 사용될 수 있다. 단, 전선관에 3 개 이상의 케이블이 들어가는 경우, 절연재를 포함한 케이블 전체의 총단면적이 전선관 단면적의 40 % 를 초과 해서는 안 된다. 전선관의 길이가 긴 경우에는 응축수를 배출시킬 수 있는 적절한 배수장치를 설치해야 하며, 추가적 으로 케이블은 적절한 내수성을 가져야 한다. 용기의 보호등급을 준수하기 위해 필요한 경우, 전선관 밀봉장치 외에 전선관과 용기 사이에 추가로 밀봉 조치(예를 들어 밀봉 와셔 또는 비경화성 그리스)가 필요할 수도 있다. 전선관만으로 접지의 연속성을 유지하는 경우, 밀봉 조치로 인해 접지 경로의 효과 성을 저하시키지 않아야 한다. 기계적 보호 목적으로만 사용되는 전선관[일반적으로 "개방형(open)" 전선관 시스템이라고 함.]은 9.4 의 요구사항을 만족시킬 필요가 없다. 그러나 이 경우에도 전선관을 통해 폭발성 분위기가 이동하는 것을 방지하기 위해 전선관이 폭발위험장소로 들어가거나 나가는 부분에 적절한 전선관 밀봉장치를 설치하여 밀봉 조치를 취해야 한다. 전선관이 전선관 인입장치를 통해 용기와 연결되는 경우, 전선관 및 전선관 인입장치에서의 연결부 에서도 IP 등급, 기계적 성능 등의 건전성을 유지하여야 한다. 전선관 시스템은 추가적으로 국가 표준, 그 밖의 관련 표준을 준수해야 한다. 9.5 추가 요구사항 각 방폭구조에 적용되는 케이블 및 전선관 시스템에 대한 추가 요구사항은 14 절 ~ 23 절에 규정되어 있다. 전선관 내 케이블, 필요한 보호 기술과 설치되는 장소에 따라 선택되는 접속부품은 국가 기관의 승 인 대상이 될 수 있다. KS C IEC 60079-26 에 따른 다른 방폭구조에 사용되는 케이블 및 전선관 시스템에 대한 추가 요구사 항은 문서에서 요구하는 보호개념에 적합하여야 한다. 9.6 설치 요구사항 9.6.1 폭발위험장소를 가로지르는 회로 비폭발위험장소에서 시작되고 끝나는 회로가 중간에 폭발위험장소를 가로지르는 경우, 폭발위험장소 를 지나는 배선 시스템은 기기보호등급의 요구사항을 준수해야 한다. 9.6.2 접속부 접속은 종류, 방폭구조, 제조자 설명서에 부합하는 방식으로 이루어져야 하며, 접속부에 과도한 응력 이 가해져서는 안 된다. 다심 연선, 특히 미세 연선을 사용하는 경우에는 케이블 러그, 심선 엔드 슬리브(core end sleeve) 또 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 41 | {}
ed9d329b-2313-4d41-af77-f269b94c2f4b | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 는 단자대 형식에 의해서 연선의 끝단이 분리되지 않도록 하여야 한다. 연선의 끝단이 분리되지 않 게 하기 위해서 납땜에만 의존해서는 안 된다. 도체가 단자에 접속되는 방식으로 인해 기기의 방폭구조에서 필요로 하는 연면거리 및 공간거리가 감소해서는 안 된다. 9.6.3 미사용 심선 다심 케이블의 폭발위험장소 내 미사용 심선은 접지시키거나, 방폭구조에 적합한 단말처리 방식으로 절연시켜야 한다. 테이프에만 의존한 절연 방법은 사용할 수 없다. 본질안전 및 에너지제한회로의 다심 케이블에서 미사용 심선에 대해서는 다른 요구사항이 적용된다 (16.2.2.5.3 참조). 9.6.4 벽 개구부 서로 다른 폭발위험장소 사이 또는 폭발위험장소와 비폭발위험장소 사이를 연결하는 케이블이나 전 선관 벽의 개구부를 모래 밀봉 또는 몰타르 밀봉과 같은 방식으로 충분히 밀봉하여 종별 장소 구분 을 유지해야 한다. 9.6.5 인화성 물질 통과 및 축적 케이블 배선을 위해 트렁킹, 덕트, 파이프 또는 트렌치를 사용하는 경우, 인화성 가스, 증기 또는 액 체가 해당 장치를 통해 다른 장소로 이동하는 것을 방지하고 인화성 가스, 증기 또는 액체가 해당 장치의 내부에 축적되는 것을 방지하기 위한 예방 조치를 취해야 한다. 이런 예방조치 방법 중 하나는 트렁킹, 덕트 또는 파이프를 밀봉하는 것이며, 트렌치의 경우에는 배 기 또는 모래 충진을 사용할 수 있다. 전선관의 경우 액체 또는 가스의 이동을 방지하기 위해 전선 관 그리고 필요한 경우(예를 들어 차압이 존재하는 경우)에는 케이블을 반드시 밀봉해야 한다(9.3.2 참조). 9.6.6 분진 축적 케이블에 분진층이 최소한으로 축적되도록 하면서도 청소를 위한 접근 공간을 확보할 수 있는 방식 으로 케이블 배선을 배치해야 한다. 트렁킹, 덕트 또는 파이프 또는 트렌치를 사용하는 경우, 해당 장소가 분진이 이동하는 경로나 축적되는 장소가 되지 않도록 예방 조치를 취해야 한다. 케이블에 분진층이 형성되어 자유로운 공기 순환을 방해할 우려가 있는 경우, 특히 최저발화온도가 낮은 분진 이 존재하는 경우, 케이블의 전류 용량을 낮출 것을 검토해야 한다. 10 케이블 인입 시스템 및 블랭킹 엘리먼트 10.1 일반사항 케이블글랜드가 -20 °C ~ 40 °C 범위에서 벗어나는 주위온도 및/또는 작동온도가 80 °C 를 초과 하는 조 건에서 사용되는 경우에는 인증 문서에 해당 내용이 포함되어야 한다. 10.2 케이블글랜드의 선정 케이블 지름에 적합한 케이블글랜드를 선정해야 한다. 케이블의 지름을 케이블글랜드에 맞추기 위해 42 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
62843911-6f42-4ad9-8cd3-7ff5c589e1b2 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 밀봉 테이프, 열수축튜브, 기타 재료를 사용해서는 안 된다. 케이블의 "콜드플로(coldflow) 특성"으로 인한 영향을 감소시킬 수 있는 케이블과 케이블글랜드를 선 정해야 한다. 비고 1 케이블에 "콜드플로" 현상을 발생시 키는 재료가 사용될 수 있다. "콜드플로"란 밀봉부품에 의 한 압축력이 케이블 피복의 변형에 대응하는 저항력보다 커서 케이블글랜드 내의 밀봉부품의 변형으로 발생한 압축력이 케이블 피복을 변형시키는 현상을 의미한다. "콜드플로"로 인하여 케이블의 절연저항이 감소될 수 있다. 특히 저연성(low smoke) 또는 내화성 케이블에서 "콜드 플로 특성"이 잘 나타난다. 케이블글랜드는 KS C IEC 60079-0 을 준수해야 하며, 표 10 의 방폭구조 요구사항을 유지할 수 있도록 선정해야 한다. 표 10 - 용기의 방폭구조에 따른 글랜드, 어댑터, 블랭킹 엘리먼트의 방폭구조 선정 ¦ 기기 방폭구조 ¦ 글랜드, 어댑터, 블랭킹 엘리먼트 방폭구조 ¦ 글랜드, 어댑터, 블랭킹 엘리먼트 방폭구조 ¦ 글랜드, 어댑터, 블랭킹 엘리먼트 방폭구조 ¦ 글랜드, 어댑터, 블랭킹 엘리먼트 방폭구조 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ Ex "d" 10.6 참조 ¦ Ex"e" 10.4 참조 ¦ Ex "n" 10.4 참조 ¦ Ex"t" 10.7 참조 ¦ ¦ Ex "d" ¦ X ¦ ¦ ¦ ¦ ¦ Ex "e" ¦ X ¦ X ¦ ¦ ¦ ¦ Ex "i", Ex"nL" - 그룹 II a ¦ X ¦ X ¦ X - 16.5 참조 ¦ ¦ ¦ Ex "i" - 그룹 III a ¦ ¦ ¦ ¦ X - 16.5 참조 ¦ Ex ¦ "m" ¦ 일반적으로 Ex "m"은 배선 접속부에 적용하지 않는다. 연결부의 방폭 구조는 사용된 배선 시스템에 적합해야 한다. ¦ ¦ --- ¦ --- ¦ ¦ Ex "n"(Ex "nL" 제외) Ex "nR"는 10.8 참조 ¦ X ¦ X ¦ X ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Ex"o" ¦ 일반적으로 Ex "0"는 배선 연결부에 적용하지 않는다. 연결부의 방폭 구조는 사용된 배선 시스템에 적합해야 한다. ¦ 일반적으로 Ex "0"는 배선 연결부에 적용하지 않는다. 연결부의 방폭 구조는 사용된 배선 시스템에 적합해야 한다. ¦ 일반적으로 Ex "0"는 배선 연결부에 적용하지 않는다. 연결부의 방폭 구조는 사용된 배선 시스템에 적합해야 한다. ¦ 일반적으로 Ex "0"는 배선 연결부에 적용하지 않는다. 연결부의 방폭 구조는 사용된 배선 시스템에 적합해야 한다. ¦ ¦ Ex "p", 모든 유형 ¦ X ¦ X ¦ Xb ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Ex "pD" ¦ ¦ ¦ ¦ X ¦ ¦ Ex"q" ¦ 일반적으로 Ex "q"는 배선 연결부에 적용하지 않는다. 연결부의 방폭 구조는 사용된 배선 시스템에 적합해야 한다. ¦ 일반적으로 Ex "q"는 배선 연결부에 적용하지 않는다. 연결부의 방폭 구조는 사용된 배선 시스템에 적합해야 한다. ¦ 일반적으로 Ex "q"는 배선 연결부에 적용하지 않는다. 연결부의 방폭 구조는 사용된 배선 시스템에 적합해야 한다. ¦ 일반적으로 Ex "q"는 배선 연결부에 적용하지 않는다. 연결부의 방폭 구조는 사용된 배선 시스템에 적합해야 한다. ¦ ¦ Ex"s" ¦ 인증서상의 조건에 의해서 허용된 방식으로만 가능하다. ¦ 인증서상의 조건에 의해서 허용된 방식으로만 가능하다. ¦ 인증서상의 조건에 의해서 허용된 방식으로만 가능하다. ¦ 인증서상의 조건에 의해서 허용된 방식으로만 가능하다. ¦ ¦ Ex "t" ¦ ¦ ¦ ¦ X ¦ ¦ X ¦ 허용됨. ¦ ¦ --- ¦ --- ¦ ¦ a b ¦ 단일 본질안전회로만 사용하는 경우 케이블글랜드에 대한 별도의 요구사항이 없음. 기기보호등급 "Gc"에만 허용됨. ¦ 용기의 보호등급을 만족시키기 위해 케이블글랜드, 어댑터 및 블랭킹 엘리먼트와 용기 사이에 밀봉 조치를 해야 할 수 있다(예를 들어 밀봉 와셔 또는 나사산 밀봉재). 비고 2 케이블 인입장치의 축이 케이블 인입부 설치판 또는 용기의 외부 표면과 수직이고, 나사식 케이블 인입장치를 두께가 6mm 이상인 나사식 케이블 인입부 설치판 또는 용기에 장착하는 경우에는 케이블 인입장치와 인입부 설치판 또는 용기 사이에 IP54 의 최소 요구사항을 만족 시키기 위한 추가적인 밀봉이 불필요하다. 무기질 절연 금속 피복 케이블(mineral-insulated metal sheathed cable)을 사용하는 경우에는 인증된 43 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
59ce83bb-c225-4fda-8c85-41268823eea3 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 무기질 절연 케이블 밀봉 장치를 사용하여 연면거리 요구사항을 준수해야 한다. 10.3 기기와 케이블의 연결 케이블글랜드는 일단 설치되면 공구를 사용하지 않고는 해체하거나 분해할 수 없도록 설치되어야 한다. 케이블의 당김 및 비틀림이 용기 내부의 도체 단말부로 전달되는 것을 방지하기 위해 케이블에 추가 적인 클램핑이 요구되는 경우, 가능한 한 글랜드에 가까운 곳에 클램프를 설치해야 한다. 비고 1 케이블 클램프는 케이블글랜드 종단에서 300mm 이내에 설치하는 것이 바람직하다. 케이블글랜드 내의 밀봉부품을 손상시킬 수 있는 측면 장력을 회피하기 위해서, 케이블이 케이블글 랜드로부터 직선으로 인출되도록 배치하여야 한다. 나사산이 없는 글랜드 설치판이 있는 용기에 테이퍼 나사를 사용하는 케이블글랜드, 블랭킹 엘리먼 트, 어댑터를 설치하는 경우, 용기의 건전성이 손상되지 않도록 적절한 접속부품을 사용해야 한다. 비고 2 테이퍼 나사에는 NPT 나사도 포함된다. 편조 케이블(braided cable) 또는 외장 케이블(armoured cable)이 케이블글랜드 내에서 단말처리되는 경우, 공구를 사용하지 않고는 케이블의 편조 또는 외장을 고정하는 부품을 풀거나 열 수 없도록 해 야 한다. 전기기기에 케이블을 연결할 때에는 케이블 종류에 적합한 케이블글랜드를 사용해야 하며, 관련 방 폭구조의 건전성을 침해하지 않아야 한다. 나사 크기 또는 구멍 크기가 케이블글랜드의 크기와 다른 경우 표 10 에 따른 나사 어댑터를 장착해 야 한다. 10.4 Ex "d", Ex "t" 또는 Ex "nR" 이외의 인입부에 적용되는 추가 요구사항 Ex "d", Ex "t" 또는 Ex "nR" 이외의 방폭구조에 추가 케이블 인입구가 필요한 경우 다음과 같은 기준 을 준수하여 인입구를 가공해야 한다. · 인입구의 면적, 크기, 개수가 제조자 기준을 준수해야 한다. · 일반 인입구(plain hole) 또는 나사산 인입구(threaded hole)는 제조자의 공차를 준수해야 한다. 플라스틱 용기의 나사 인입구는 용기의 표면과 직각을 이루어야 한다[플라스틱 용기의 제작 방식에 따라 용기 벽에 구배(draw angle)가 있을 수 있기 때문이다]. 용기 표면이 기울어져 있는 경우 글랜드 와 관련 설치부품이 표면과 밀착될 수 없으며, 그에 따라 밀봉 효과 가 감소될 수 있다. 테이퍼 나사를 사용해서 밀봉할 경우 높은 응력이 발생하여 플라스틱 용기 벽이 파손될 수 있으므로 플라스틱 용기에 테이퍼 나사를 사용하는 것은 권장하지 않는다. 10.5 미사용 개구부 하나의 본질안전회로만 포함하는 용기가 아닌 한, 용기의 미사용 개구부를 표 10 에 따른 블랭킹 엘 리먼트를 사용해서 밀봉해야 하며, IP54 또는 설치된 장소에서 요구하는 IP 등급 중 더 높은 쪽을 유 지해야 한다. 블랭킹 엘리먼트는 공구를 사용하지 않고는 제거할 수 없는 종류이어야 한다. 44 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
3ac09225-55a2-4727-acad-5b75c1ee8dd9 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 내압방폭구조 용기의 경우 어댑터를 블랭킹 엘리먼트와 함께 사용해서는 안 된다. 10.6 내압방폭구조 "d"에 적용되는 추가 요구사항 10.6.1 일반사항 케이블이 내압방폭기기의 용기 벽을 통과 하는 내압방폭 부싱을 거쳐 기기로 인입되는 경우(간접 인 입), 부싱의 내압방폭용기 외부에 노출되어 있는 부분은 KS C IEC 60079-0 에 따른 방폭구조 중 하나 를 사용하여 보호해야 한다. 예를 들어, 부싱의 노출된 부분을 다른 내압방폭구조 용기 또는 안전증 방폭구조 "e"의 단자 설치부 내에 위치시킬 수 있다. 밀봉 링(압착식) 형식으로 클램핑되는 Ex "d" 글랜드가 편조 케이블(braided cable) 또는 외장 케이블 (armoured cable)과 함께 사용하는 경우, 편조 또는 외장이 글랜드 안에서 단말되도록 하고, 압착은 내부 케이블 피복에 가해지는 형식이어야 한다. 편조 지름이 0.15mm 미만이고 압착력의 최소 70 % 가 외부 피복에 부과 되는 미세 편조 케이블만 허용된다. 비고 1 일반적인 연선 사이 또는 케이블 심선 사이의 간극을 통해 화염이 전파될 수 있다. 특수한 케이블의 구조를 통해서 이러한 화염전파을 막을 수 있다. 예를 들어 빈 공간이 없는 연선, 개별 연선을 밀봉, 압출 베딩(extruded bedding) 등이 있다. 추가 정보는 부속서 E 에 제공된 다. 평행 나사산이 있는 내압방폭구조의 케이블글랜드, 어댑터 또는 블랭킹 엘리먼트의 경우, 인입장치와 내압방폭용기 사이에 밀봉 와셔(sealing washer)를 설치할 수 있다. 이 경우 와셔를 설치한 후에도 나 사 맞물림이 적어도 5 산 이상을 가져야 한다. 인입장치와 내압방폭용기 사이에, 필요한 경우 접지가 유지된다면 비경화성, 비금속성, 비연소성을 가진 적합한 그리스를 사용해서 밀봉할 수 있다. 테이퍼 나사가 사용되는 경우, 연결부를 렌치로 조여야 한다. 용기에 인입구를 추가하거나 기존의 나사산 형태를 변경하고자 하는 경우 인증문서를 준수해야 하며, 제조자를 통하거나 인증된 작업장에서 작업을 수행해야 한다. 나사산 인입부 또는 구멍의 크기가 케 이블글랜드의 크기와 다른 경우, KS C IEC 60079-1 에 따른 내압방폭구조의 어댑터를 위에서 기술한 나사산 맞물림 요구사항이 만족되도록 설치한다. 미사용 케이블 인입부는 KS C IEC 60079-1 에 따른 내압방폭구조의 블랭킹 엘리먼트로 밀봉하되 어댑터를 함께 사용할 수 없으며, 위에서 기술한 나사 산 맞물림 요구사항이 만족되도록 설치한다. 블랭킹 엘리먼트는 설치 후 풀림이 발생하지 않도록 조 여야 한다. 비고 2 비나사식 케이블글랜드는 기기와 함께 인증을 받았거나 별도의 기기로서 인증을 받은 경우에 만 사용할 수 있다. 10.6.2 케이블랜드의 선정 케이블 인입 시스템은 다음 중 하나의 방법을 따라야 한다. a) KS C IEC 60079-1 에 따라 경화성 컴파운드로 밀봉되고(배리어 케이블글랜드) 별도의 기기로서 인증을 받은 케이블글랜드 b) 다음의 모든 기준을 준수하는 케이블 및 글랜드 - KS C IEC 60079-1 의 기준에 따라 별도 기기로서 인증 받은 케이블글랜드 45 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
9d42f30e-fd26-43c9-92c5-c214814585a2 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 사용된 케이블이 9.3.2 a)를 준수 연결된 케이블의 길이가 최소 3 m 이상 c) 부싱이 사용된 내압방폭구조 용기와 안전증방폭구조 단자 박스가 함께 사용된 간접 케이블 인입부 d) KS C IEC 60079-1 에 따른 내압방폭구조의 케이블글랜드와 함께 사용되는 무기질 절연 금속 피 복 케이블(플라스틱 외부 커버 존재 여부는 무관) e) 기기의 기술문서 또는 KS C IEC 60079-1 에 따라 제작되고, 사용 케이블에 적합한 케이블글랜드 가 부착되어 있는 내압방폭 밀봉장치(예: 밀봉 챔버). 밀봉장치는 개별 심선 주변를 밀봉할 수 있 는 컴파운드나 밀봉재를 포함하여야 한다. 밀봉장치는 기기의 케이블 인입 지점에 설치해야 한다. 비고 1 케이블의 최소 길이는 케이블을 통한 화염전파 가능성을 최소화하기 위함이다(부속서 E 참조). 비고 2 케이블글랜드 및 사용된 케이블이 기기(용기)의 일부로 함께 인증 받은 경우 10.6.2 를 준수할 필요가 없다. 10.7 분진방폭구조 "t"에 적용되는 추가 요구사항 표 11 에 따른 용기의 보호등급을 가져야 한다. 표 11 - 보호등급, 기기 그룹 및 용기 보호등급의 관계 ¦ 보호등급 ¦ IIIC 그룹 ¦ IIIB 그룹 ¦ IIIA 그룹 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ "ta" ¦ IP6X ¦ IP6X ¦ IP6X ¦ ¦ "tb" ¦ IP6X ¦ IP6X ¦ IP5X ¦ ¦ "tc" ¦ IP6X ¦ IP5X ¦ IP5X ¦ 평행 나사산이 있는 Ex "t" 글랜드, 어댑터 또는 블랭킹 엘리먼트는 인입장치와 "t" 용기 사이에 설치 되는 밀봉 와셔와 함께 사용할 수 있다. 와셔를 사용하지 않는 경우 최소 5 산 이상의 나사산 결합이 이뤄져야 한다. 추가적인 밀봉이나 개스킷 없이 테이퍼 나사 결합을 사용할 경우 3 1/2 산 이상의 나 사산 결합이 이뤄져야 한다. 10.8 통기 제한 방폭구조 "nR"에 적용되는 추가 요구사항 통기 제한 "nR" 용기 밀봉 시에는 용기의 통기 제한 특성이 유지되어야 한다. 인증서 및 사용설명서에 명시하지 않은 케이블을 사용하고 해당 케이블이 효과 적으로 밀봉처리 되지 않은 경우에는, 용기로부터의 누설을 방지하기 위해서 개별 도체를 밀봉하는 케이블글랜드 또는 그 밖의 수단(예: 에폭시 조인트, 수축 튜브)을 사용할 수도 있다. 케이블글랜드와 용기 사이에 적절한 밀봉 와셔를 사용해야 한다. 전선관 또는 테이퍼 나사를 사용하 는 경우에는 나사산 밀봉재(thread sealant)를 함께 사용할 수도 있다(9 절 참조). 46 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
67df5f1c-080b-42bc-a8be-81478b9323ce | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 11 회전 전기기기 11.1 일반사항 회전 전기기기는 허용 가능한 발열 범위 내에서, 정격전압 및 정격 주파수에서 기동전류를 연속적으 로 견딜 수 있거나 발전기의 경우에는 단락전류를 견딜 수 있는 경우가 아닌 한 과부하로부터 추가 적으로 보호해야 한다. 과부하 보호장치는 다음 중 하나를 만족시켜야 한다. a) 회전 전기기기의 정격전류를 초과 하지 않도록 설정되어 있는, 3 상을 모두 모니터링하는 전류의 존 시간지연 보호장치. 설정전류의 1.2 배에서는 2 시간 이내에 작동해야 하며, 설정전류의 1.05 배에서 는 2 시간 이내에 작동하지 않아야 한다. b) 내장형 온도센서를 사용하는 직접적인 온도 제어장치 c) 이에 상응하는 그 밖의 장치 11.2 내압방폭구조 "d" 전동기 11.2.1 컨버터로부터 전원을 공급받는 전동기 컨버터로부터 가변 주파수와 전압을 공급받는 전동기는 다음 중 한 가지 기준을 만족시켜야 한다. a) KS C IEC 60079-0 에 따른 기술문서(descriptive documents)에 명시된 컨버터 및 보호장치와 함께 하나의 단위로서 듀티(duty)에 대하여 형식시험을 거친 전동기 b) 컨버터와 함께 하나의 단위로 형식시험을 거치지 않은 전동기의 경우, 전동기 기술문서에 명시된 내장 온도센서를 통해 직접 온도를 제어할 수 있는 수단(또는 기기)이 마련되어 있거나, 전동기 외부 표면온도를 제한할 수 있는 그 밖의 효율적인 수단이 마련되어 있어야 한다. 온도 제어의 효 율성은 전력, 속도 범위, 토크, 듀티 주파수(frequency for the duty)를 고려하여 결정해야 하며, 검 증을 거쳐 문서화해야 한다. 보호장치가 작동되면 전동기가 전기적으로 차단되어야 한다. 비고 1 경우에 따라 전동기 축에서 가장 높은 표면 온도가 나타날 수 있다. 비고 2 (11.1 에 따라) 전류의 존 시간지연 보호장치는 "다른 효과 적인 수단"으로 간주되지 않는다. 방폭구조 "e" 단자 박스가 사용된 전동기의 경우, 출력에 고주파 펄스가 있는 컨버터를 사용할 때 단 자 박스에서 과전압 스파이크(overvoltage spike) 및 고온이 발생할 수 있음을 고려해야 한다. 11.2.2 소프트 스타트[감압기동(soft starting)] 소프트 스타트 기능이 있는 전동기는 다음 중 한 가지 기준을 만족시켜야 한다. a) 기술문서에 명시된 소프트 스타트 장치 및 보호장치와 함께 하나의 단위로 형식시험을 거친 전동기 b) 소프트 스타트 장치와 함께 하나의 단위로 형식시험을 거치지 않은 전동기의 경우, 전동기 설명서 에 명시된 내장 온도센서를 통해 직접 온도를 제어할 수 있는 수단(또는 기기)이 마련되어 있거나, 전동기의 외부 표면온도를 제한할 수 있는 (11.1 에 따른) 그 밖의 효율적인 수단이 마련되어 있어 야 하며, 그렇지 않을 경우 속도 제어장치를 통해 표면온도가 초과 되지 않도록 제어할 수 있어야 한다. 온도 제어 또는 속도 제어의 효율성은 검증을 거쳐 문서화해야 한다. 보호장치가 작동되면 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 47 | {}
1f01ea7f-278c-48ca-8262-84d4eae4e3bf | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 전동기가 전기적으로 차단되어야 한다. 비고 소프트 스타트는 짧은 시간 동안만 사용되는 것으로 간주된다. 방폭구조 "e" 단자 박스가 사용된 전동기의 경우, 출력에 고주파 펄스가 있는 컨버터를 사용할 때 단 자 박스에서 과전압 스파이크 및 고온이 발생할 수 있음을 고려해야 한다. 11.3 안전증방폭구조 "e" 전동기 11.3.1 주전원 작동 11.1 의 기준을 만족시키기 위해서는 반한시 지연(inverse-time delay) 과부하 보호장치가 전동기 전류 를 모니터링할 뿐만 아니라 구속된 전동기가 시간 tE 이내에 차단될 수 있도록 해야 한다. 사용자는 기동전류비 IA/IN 의 함수인 복귀(release) 또는 과부하 계전기의 지연 시간을 제공하는 전류-시간 특 성 곡선을 소지하여야 한다. 이 곡선은 주위온도 20 °C 관련된 저온 상태(cold state)로부터 및 최소 3 ~ 8 의 기동전류비의 범위에 대한 지연 시간의 값을 나타내야 한다. 안전장치의 작동 시간(tripping time)은 지연 시간 ±20 %의 값 과 같아야 한다. 특히 1 상 손실 시 델타결선(delta wound) 전동기의 특성이 구체적으로 기술되어야 한다. 성형결선 (star wound) 전동기와 는 달리 델타결선 전동기의 경우(특히 전동기가 작동하는 동안) 1 상이 손상되더 라도 이를 발견하지 못할 수 있으며, 이로 인한 전동기 인입 선로의 전류 불평형으로 전동기가 가열 될 수 있다. 기동 시 낮은 토크가 걸리는 델타결선 전동기의 경우 권선이 고장 나더라도 기동이 가 능할 수 있어, 권선이 고장 난 상태를 장기간 인지하지 못할 수 있다. 따라서 델타결선 전동기에는 전동기가 과도하게 가열되기 전에 전동기의 전류 불평형을 감지할 수 있도록 상 불평형 보호장치를 설치해야 한다. 일반적으로 상당한 추가 발열을 발생시키지 않으면서 쉽고 드물게 기동하는 전동기를 포함하여 연속 적으로 작동하는 전동기는 반한시 지연 과부하 보호가 허용된다. 가혹한 기동 조건(arduous starting conditions) 또는 빈번한 기동을 하는 전동기는 제한 온도를 초과 하지 않도록 보장하는 적절한 보호 장치가 있어야만 허용된다. 위에서 기술한 기준에 따라 적절하게 선정된 반한시 지연 과부하 보호장치에 의하여 정격속도에 도 달하기 전에 전동기를 차단하는 경우가 발생한다면 가혹한 기동조건이 존재한다고 고려할 수 있다. 이런 조건은 일반적으로 총 기동시간이 tE 의 1.7 배를 초과 하는 경우에 발생한다. 운전: 전동기의 듀티가 S1(정부하에서의 연속운전)이 아닌 경우, 사용자가 정해진 운전 조건에 적합 한지 여부를 판단하기 위한 파라미터를 입수하여야 한다. 기동: 전동기 보호장치가 기동 중 전동기 작동을 중단시키지 않도록 하기 위해 전동기의 직접 온라 인(direct on-line) 기동시간이 tE 미만인 것이 바람직하다. 기동시간이 tE 시간의 80 %를 초과 하는 경 우, 전동기 사용설명서에 규정된 운전 상태에서의 기동에 대한 제한사항을 전동기 제조자를 통해 확 인해야 한다. 전원의 자동 재투입(자동 재기동)은 재투입 동안 회전자 또는 절연 시스템에 스파크를 발생시킬 위험 을 높일 수 있기 때문에 권장하지 않는다. 전동기가 반드시 자동으로 재기동되어야 한다면 상 일치 를 위한 특정 시한 재투입, 압력방폭구조 Ex "p" 및 과도전압 제한장치 등과 같은 추가적인 보호조치 를 고려하여야 한다. 48 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
9e135517-826b-4c08-9f31-4d8aa394a4cb | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 직접 온라인 기동 시 전압이 강하하면 기동 전류는 감소하고 기동시간(run-up time)은 증가한다. 비록 이러한 효과 가 다소의 전압강하를 상쇄하겠지만, 만약 정격전압(UN) 대비 85 % 미만의 전압이 발생 한다면 제조자는 기동에 관련된 제한사항을 기술하여야 한다. 전동기의 기동 시도는 제조자에 의해서 일정한 횟수로 제한될 수 있다. 방폭구조 "e"에 따른 회전 전기기계의 보호 계전기는 11.1 의 요구사항 외에도 다음과 같은 기준을 만 족시켜야 한다. a) 각 상에서 전류를 모니터링 b) 전동기의 전부하 조건에 근접하는 과부하 보호를 제공 기동이 쉽고 기동 횟수가 많지 않은 S1 듀티 형식의 전동기에는 반한시 지연 과부하 보호 계전기를 사용할 수 있다. 기동 듀티가 가혹하거나(arduous) 빈번하게 기동하는 전동기의 경우, 주어진 전동기 의 운전 파라미터하에서 제한 온도를 초과 하지 않도록 해주는 보호장치를 사용해야 한다. 기동시간 이 tE 의 1.7 배를 초과 하면 반한시 계전기가 기동 중에 전동기를 차단시킬 수 있다. 비고 듀티 유형이 S1 이 아닌 전동기와 같이 특정한 조건에서는 온도 감지 및 보호 기능과 전동기를 함께 인증 받을 수 있다. 이런 경우에는 tE 를 따로 파악할 필요가 없다. 11.3.2 권선 온도센서 11.1 의 기준을 만족시키기 위해서는 보호장치로 사용되는 권선 온도센서가 전동기가 구속된 경우에 도 전동기를 과열로부터 보호할 수 있어야 한다. 내장된 온도센서를 사용하는 전동기의 온도 제한 방식은 전동기 기술문서에 해당 방식이 명시되어 있는 경우에만 허용된다. 시간 tA 는 온도 감지기의 응답시간을 의미하며, 이 값은 실제로 검증되어야 한다. 비고 1 내장형 온도센서 및 관련 보호장치의 유형은 전동기에 표시되어 있다. 비고 2 사용자는 보호장치에 대한 시험을 통해 시간 tA(부속서 C, KS C IEC 60079-17 참조)를 검증할 수 있다. 11.3.3 정격 전압이 1 kV 를 초과 하는 회전 전기기기 정격 전압이 1 kV 를 초과 하는 회전 전기기기는 표 G.1 의 값을 반영하여 선정해야 한다. 위험요소의 총합이 6 보다 큰 경우에는 결로 방지용 스페이스 히터를 사용해야 하며, 기동 시에 용기에 폭발성 가스 분위기가 없도록 하기 위한 별도의 조치를 취해야 한다. 비고 1 회전 전기기기가 "특수 조치"하에서 작동하도록 의도된 경우, KS C IEC 60079-0 에 따라 인증 서에 기호 "X"가 표시된다. 비고 2 특수 조치에는 기동 전 환기, 기계 내부에 고정식 가스 탐지기 설치, 제조자의 설명서에 명시 된 다른 수단이 포함된다. 비고 3 최신 KS C IEC 60079-7 에 따라 제작된 1 kV 이상의 모든 Ex "e" 전동기는 고정자에 대한 폭 발성가스 분위기 내의 형식시험이 실시되며 결로 방지용 스페이스 히터가 장착된다. - 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 49 | {}
c234f047-5fee-4137-9cb6-be324637fcdd | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 11.3.4 컨버터로부터 전원을 공급받는 전동기 컨버터로 가변 주파수 및 전압을 공급받는 전동기는 컨버터 및 보호장치와 함께 해당 듀티(duty)에 대해서 형식시험을 거쳐야 한다. 전동기는 정격 범위 내에서 사용해야 하며, 컨버터의 설정은 주파수 범위, 최소 반송 주파수, 기타 지정된 파라미터 등의 전동기 정격 정보에 부합되도록 설정해야 한다. 컨버터는 파라미터를 조정할 수 있는 구조이어야 한다. 비고 영구자석 전동기는 전원이 차단된 후에도 타력운전(coasting)을 하며 발전기로 작동한다. 전압 이 정격전압을 초과 할 가능성이 있는 Ex "eb" 전동기의 경우, 전동기-컨버터 시스템이 타력운 전으로 인해 발생하는 전압에 적합해야 한다. 11.3.5 소프트 스타크(감압 기동) 소프트 스타트 기능이 있는 전동기는 다음 중 한 가지 기준을 만족시켜야 한다. a) 기술문서에 명시된 소프트 스타트 장치 및 보호장치와 함께 하나의 단위로 형식시험을 거친 전동기 b) 소프트 스타트 장치와 함께 하나의 단위로 형식시험을 거치지 않은 전동기의 경우, 전동기 설명서 에 명시된 내장 온도센서를 통해 직접 온도를 제어할 수 있는 수단(또는 기기)이 마련되어 있거나 전동기의 온도를 제한할 수 있는 그 밖의 효율적인 수단이 마련되어 있어야 하며, 그렇지 않을 경우 속도 제어장치를 통해 온도가 초과 되지 않도록 제어할 수 있어야 한다. 온도 제어 또는 속도 제어의 효율성은 검증을 거쳐 문서화해야 한다. 보호장치가 작동되면 전동기가 전기적으로 차단 되어야 한다. 비고 소프트 스타트는 짧은 시간 동안만 사용되는 것으로 간주된다. 출력에 고주파 펄스가 발생하는 소프트 스타트 장치를 사용할 때에는 단자 박스에서 과전압 스파이 크 및 고온이 발생할 수 있음을 고려해야 한다. 11.4 압력방폭구조 "p" 및 분진압력방폭구조 "pD" 전동기 11.4.1 컨버터로부터 전원을 공급받는 전동기 컨버터로부터 가변 주파수와 전압을 공급받는 전동기는 다음 중 한 가지 기준을 만족시켜야 한다. a) KS C IEC 60079-0 에 따른 기술문서에 명시된 컨버터 및 보호장치와 함께 하나의 단위로서 해당 듀티에 대하여 형식시험을 거친 전동기 b) 컨버터와 함께 하나의 단위로 형식시험을 거치지 않은 전동기의 경우, 전동기 기술문서에 명시된 내장 온도센서를 통해 직접 온도를 제어할 수 있는 수단(또는 기기)이 마련되어 있거나, 전동기 외부 표면온도를 제한할 수 있는 그 밖의 효율적인 수단이 마련되어 있어야 한다. 온도 제어의 효 율성은 전력, 속도 범위, 토크, 듀티 주파수를 고려하여 결정해야 하며, 검증을 거쳐 문서화해야 한다. 보호장치가 작동되면 전동기가 전기적으로 차단되어야 한다. 비고 1 경우에 따라 전동기 축에서 가장 높은 표면 온도가 나타날 수 있다. 비고 2 (11.1 에 따라) 전류의 존 시간지연 보호장치는 "다른 효과 적인 수단"으로 간주되지 않는다. 방폭구조 "e" 또는 "n" 단자 박스가 사용된 전동기의 경우, 출력에 고주파 펄스가 있는 컨버터를 사용 50 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
340ee9df-1f1c-4f0b-9a15-2defb60ada2a | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 할 때 단자 박스에서 과전압 스파이크 및 고온이 발생할 수 있음을 고려해야 한다. 11.4.2 소프트 스타크(감압 기동) 소프트 스타트 기능이 있는 전동기는 다음 중 한 가지 기준을 만족시켜야 한다. a) 기술문서에 명시된 소프트 스타트 장치 및 보호장치와 함께 하나의 단위로 형식시험을 거친 전동기 b) 소프트 스타트 장치와 함께 하나의 단위로 형식시험을 거치지 않은 전동기의 경우, 전동기 설명서 에 명시된 내장 온도센서를 통해 직접 온도를 제어할 수 있는 수단(또는 기기)이 마련되어 있거나 전동기의 외부 표면온도를 제한할 수 있는 그 밖의 효율적인 수단이 마련되어 있어야 하며, 그렇 지 않을 경우 속도 제어장치를 통해 온도가 초과 되지 않도록 제어할 수 있어야 한다. 온도 제어 또는 속도 제어의 효율성은 검증을 거쳐 문서화해야 한다. 보호장치가 작동되면 전동기가 전기적 으로 차단되어야 한다. 비고 소프트 스타트는 짧은 시간 동안만 사용되는 것으로 간주된다. 출력에 고주파 펄스가 발생하는 소프트 스타트 장치를 사용할 때 단자 박스에서 과전압 스파이크 및 고온이 발생할 수 있음을 고려해야 한다. 11.5 분진방폭구조 "t" 전동기 11.5.1 컨버터로부터 전원을 공급받는 전동기 컨버터로부터 가변 주파수와 전압을 공급받는 전동기는 다음 중 한 가지 기준을 만족시켜야 한다. a) KS C IEC 60079-0 에 따른 기술문서에 명시된 컨버터 및 보호장치와 함께 하나의 단위로서 해당 듀티에 대하여 형식시험을 거친 전동기 b) 컨버터와 함께 하나의 단위로 형식시험을 거치지 않은 전동기의 경우, 전동기 기술문서에 명시된 내장 온도센서를 통해 직접 온도를 제어할 수 있는 수단(또는 기기)이 마련되어 있거나, 전동기 외부 표면온도를 제한할 수 있는 그 밖의 효율적인 수단이 마련되어 있어야 한다. 온도 제어의 효 율성은 전력, 속도 범위, 토크, 듀티 주파수를 고려하여 결정해야 하며, 검증을 거쳐 문서화해야 한다. 보호장치가 작동되면 전동기가 전기적으로 차단되어야 한다. 비고 1 경우에 따라 전동기 축에서 가장 높은 표면 온도가 나타날 수 있다. 비고 2 (11.1 에 따라) 전류의 존 시간지연 보호장치는 "다른 효과 적인 수단"으로 간주되지 않는다. 단자 박스에서 과전압 스파이크 및 고온이 발생할 수 있음을 고려해야 한다. 11.5.2 소프트 스타트(감압 기동) 소프트 스타트 기능이 있는 전동기는 다음 중 한 가지 기준을 만족시켜야 한다. a) 기술문서에 명시된 소프트 스타트 장치 및 보호장치와 함께 하나의 단위로 형식시험을 거친 전동 기 b) 소프트 스타트 장치와 함께 하나의 단위로 형식시험을 거치지 않은 전동기의 경우, 전동기 설명서 51 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
a7b0f103-cfce-4393-bc31-ab5e91bf99bd | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 에 명시된 내장 온도센서를 통해 직접 온도를 제어할 수 있는 수단(또는 기기)이 마련되어 있거나 전동기의 외부 표면온도를 제한할 수 있는 그 밖의 효율적인 수단이 마련되어 있어야 하며, 그렇 지 않을 경우 속도 제어장치를 통해 온도가 초과 되지 않도록 제어할 수 있어야 한다. 온도 제어 또는 속도 제어의 효율성은 검증을 거쳐 문서화해야 한다. 보호장치가 작동되면 전동기가 전기적 으로 차단되어야 한다. 비고 소프트 스타트는 짧은 시간 동안만 사용되는 것으로 간주된다. 출력에 고주파 펄스가 발생하는 소프트 스타트 장치를 사용할 때 단자 박스에서 과전압 스파이크 및 고온이 발생할 수 있음을 고려해야 한다. 11.6 비점화방폭구조 "nA" 전동기 11.6.1 컨버터로부터 전원을 공급받는 전동기 컨버터로부터 가변 주파수와 전압을 공급받는 전동기는 다음 중 한 가지 기준을 만족시켜야 한다. a) 특정 컨버터 또는 출력 전압과 전류 사양 측면에서 호환 가능한 컨버터와 함께 KS C IEC 60079- 15 에 따라 형식시험을 거친 전동기 b) 컨버터와 함께 하나의 단위로 형식시험을 거치지 않은 전동기의 경우, 전동기 기술문서에 명시된 내장 온도센서를 통해 직접 온도를 제어할 수 있는 수단(또는 기기)이 마련되어 있거나 전동기 외 부 표면온도를 제한할 수 있는 그 밖의 효율적인 수단이 마련되어 있어야 한다. 온도 제어의 효율 성은 전력, 속도 범위, 토크, 듀티 주파수를 고려하여 결정해야 하며, 검증을 거쳐 문서화해야 한 다. 보호장치가 작동되면 전동기가 전기적으로 차단되어야 한다. 그렇지 않은 경우 KS C IEC 60 079-15 에 따라 계산된 온도등급을 가지고 있어야 한다. 11.6.2 감압 기동(소프트 스타트) 소프트 스타트 기능이 있는 전동기는 다음 중 한 가지 기준을 만족시켜야 한다. a) 기술문서에 명시된 소프트 스타트 장치 및 보호장치와 함께 하나의 단위로 형식시험을 거친 전동기 b) 소프트 스타트 장치와 함께 하나의 단위로 형식시험을 거치지 않은 전동기의 경우, 전동기 설명서 에 명시된 내장 온도센서를 통해 직접 온도를 제어할 수 있는 수단(또는 기기)이 마련되어 있거나 전동기의 외부 표면온도를 제한할 수 있는 그 밖의 효율적인 수단이 마련되어 있어야 하며, 그렇 지 않을 경우 속도 제어장치를 통해 온도가 초과 되지 않도록 제어할 수 있어야 한다. 온도 제어 또는 속도 제어의 효율성은 검증을 거쳐 문서화해야 한다. 보호장치가 작동되면 전동기가 전기적 으로 차단되어야 한다. 비고 소프트 스타트는 짧은 시간 동안만 사용되는 것으로 간주된다. 11.6.3 정격전압이 1 kV 를 초과 하는 기계 정격 전압이 1 kV 를 초과 하는 회전 전기기기는 표 G.1 의 값을 반영하여 선정해야 한다. 위험요소의 총합이 6 보다 큰 경우에는 결로 방지용 스페이스 히터를 사용하거나, 기동 시에 용기에 폭발성 가스 분위기가 없도록 하기 위한 별도의 조치를 취해야 한다. 비고 1 회전 전기기기가 "특수 조치"하에서 작동하도록 의도된 경우, KS C IEC 60079-0 에 따라 인증 52 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c6045da3-9616-4f26-a092-7ca55ce923c3 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 서에 기호 "X"가 표시된다. 비고 2 특수 조치에는 기동전 환기, 기계 내부에 고정식 가스 탐지기 설치, 제조자의 설명서에 명시 된 다른 수단이 포함된다. 12 등기구 형광등 및 전자식 안정기가 사용된 방폭구조 "e" 또는 "nA" 형식의 등기구는 온도등급 T5 또는 T6 이 요구되거나 주변 온도가 60 °C 를 초과 하는 곳에서는 사용할 수 없다. 비고 1 이 제한 규정은 램프가 수명이 다한 시점(End oflife, EOL)에서의 위험을 최소화한다. 핀이 있는 램프의 경우, 핀의 소재가 황동이어야 한다. 도전성 코팅이 된 비도전성 재료(예를 들면 바이-핀, 텅스텐 램프의 나사 연결부)가 사용된 등기구는 기기와 함께 시험되지 않는 한 사용할 수 없다. 비고 2 이 제한 규정은 핀 또는 엔드 캡(end caps)이 도전성 필름으로 코팅된 플라스틱이나 세라믹 으로 만든 램프에 적용하기 위함이다. 13 전기 가열 시스템 13.1 일반사항 부품으로 인증받은 전기 가열 시스템 부품, 즉 "U" 표시가 되어 있는 부품은 부품 조립체(이하 기기) 내에서만 사용할 수 있으며, 기기의 인증서상에 해당 부품의 사용이 허용되어야 한다. 기기의 인증서 에는 "X" 표시를 포함할 수 있으며, 해당 기기의 라벨에는 온도등급을 포함하여 전체 방폭 기호를 표 시하여야 한다. 히터가 별도로 인증 받은 조립체의 일부로 설치된 경우(예를 들어, 전동기 결로방지 히터 등)가 아닌 한 과전류 보호 외에 다음과 같은 보호기능이 있어야 한다. a) 7 절에서 요구하는 보호기능 외에 추가로, 지락사고 및 대지 누설 전류로 인한 가열 효과 를 제한하 기 위해 TT 또는 TN 유형 시스템에 다음과 같은 추가적인 보호기능이 제공되어야 한다. 정격 감 도전류가 100 mA 를 초과 하지 않는 누전차단기(RCD)를 사용해야 한다. 정격감도전류가 30mA 인 누전차단기를 사용할 것을 권장한다. 비고 누전차단기에 대한 추가 정보는 KS C IEC 61008-1 에서 제공된다. b) IT 시스템의 경우, 절연저항이 정격전압의 50 �/V 보다 크지 않을 때 전원을 차단하기 위해 절연 감시장치(insulation monitoring device)를 사용해야 한다. 단락 회로 계산(short-circuit calculation)을 위해서 전체 트레이스 히팅 회로(trace heating circuit)의 부하 전류를 고려해야 한다. 13.2 온도 모니터링 온도 보호장치를 설치해야 하는 경우, 다른 운전온도 제어장치로부터 독립되어 있어야 하며, 직접 또 53 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
0db28d10-6ec5-401c-b7db-ebb51af6d6b4 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 는 간접적으로 전기 가열 시스템의 전원을 차단할 수 있어야 한다. 보호장치 재설정은 수동으로만 가능해야 한다. 온도 모니터링 시스템에 적용되는 요구사항은 표 12 와 같다. 표 12 - 온도 모니터링 시스템 요구사항 ¦ 전기 기계식 고온 스위치 ¦ 프로세서 제어 고온 스위치 ¦ ¦ --- ¦ --- ¦ ¦ 도구를 사용해야 재설정 가능 ¦ 사용자 코드가 있어야 재설정 가능 ¦ ¦ 수동 재설정 ¦ 제어장치에 대한 접근 권한이 있는 사람에 의해 서만 재설정 가능 ¦ ¦ 정상 작동 조건에서만 재설정 가능 ¦ 정상 작동 조건에서만 재설정 가능 ¦ ¦ 설정 접근 제한 ¦ 하드 와이어드 점퍼 (hard wired jumper) 및 제조 자 코드가 있어야 온도등급 설정 가능 ¦ ¦ 컨트롤러와 는 독립적 ¦ 컨트롤러와 는 독립적 ¦ ¦ 감지기 페일세이프(fail-safe) 기능(예를 들면 모 세관 튜브 파열) ¦ 100 % 센서 모니터링 ¦ 13.3 온도 제한 저항가열장치 또는 유닛은 통전 중 제한 온도를 초과 하지 않아야 한다. 이는 다음 방법 중 어느 하나에 의해 보장되어야 한다. a) 저항가열장치의 자체 온도제한 특성(temperature self-limiting characteristic)을 이용한 안정화 설계 b) (특정 사용 조건에서) 가열 시스템의 안정화 설계 비고 1 기기보호등급 "Gb" 또는 "Gc"에 사용되는 안정화 설계는 일반적으로 과도한 온도에 대한 추가적인 보호를 필요로 하지 않는다. c) 13.4 에 따른 안전장치 저항가열장치의 온도에 영향을 주는 관계에 관한 필요 데이터는 KS C IEC 60079-0 에 따라 준비된 문 서를 통해 제조자가 제공하여야 한다. 비고 2 b)와 c)에서, 저항가열장치의 온도는 아래의 다양한 파라미터 사이의 관계에 따르지만, 다음 의 사항으로만 제한하지 않는다. 주위온도 범위 매체의 입구 및 출구 온도 또는 가열 대상물(workpiece)의 온도 가열되는 매체의 종류, 물리적 특성(열전도도, 비열 용량, 동점도, 프란틀 수, 상대밀도) 온도등급 열 출력 매체의 물리적 특성, 유속, 공급 전압, 허용 표면온도에 따라 달라지는 열 유속 가열 유닛의 형상(개별 가열 요소의 배열, 입사각, 열전달) 54 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
222c4563-ffb8-4c5e-ae2f-a96fbef68b4f | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 13.4 안전장치 안전장치에 의한 보호는 다음을 감지(sensing)하여야 한다. a) 저항가열장치의 온도 또는 해당되는 경우 바로 인접한 주위의 온도 b) 저항가열장치의 온도 또는 주변 온도 및 하나 이상의 다른 파라미터 비고 b)에서 기술하는 그 밖의 파라미터의 예는 다음과 같다. 액체의 경우, 레벨을 모니터링하여 가열장치가 액면 아래 50 mm 이상 유지됨을 보장(액면 위로 노출되어 운전되는 것을 보호) 가스 및 공기와 같은 유동 매체의 경우, 유량 모니터링을 통해 최소 처리량을 보장 - 대상물의 가열을 위해 가열장치를 고정하거나 보조제(열전도성 시멘트)를 사용하여 열전달을 보장 기기보호등급 "Gb" 또는 "Db"가 요구되는 장소의 안전장치는 다음과 같은 기능을 가져야 한다. - 저항가열장치 또는 유닛의 전원을 직접 또는 간접적으로 차단 기기보호등급 "Gc" 또는 "Dc"가 요구되는 장소의 안전장치는 다음 중 한 가지 기능을 가져야 한다. - 저항가열장치 또는 유닛의 전원을 직접 또는 간접적으로 차단 항상 사람이 있는 장소에서 확인할 수 있는 경보용 출력을 제공 안전장치로부터의 정보가 지속적으로 모니터링되는 경우를 제외하고, 안전장치 재설정은 앞서 설정 된 공정 조건으로 복귀된 이후 수작업으로만 가능해야 한다. 센서가 고장을 일으킨 경우에는 제한 온도에 도달하기 전에 가열장치의 전원이 차단되어야 한다. 안전장치의 조정(adjustment)은 잠금 및 밀봉되어야 하며 사용 중 변경될 수 없어야 한다. 열 퓨즈(thermal fuse) 교체 시에는 반드시 제조자가 지정한 부품만 사용해야 한다. 안전장치는 비정상 조건에서만 작동해야 하고, 정상 조건에서 작동상의 이유로 필요할 수 있는 조절 장치에 부가적이고 기능상으로는 독립적이어야 한다. 13.5 전기 트레이스 히터 시스템 트레이스 히터 시스템의 외부 금속 커버, 금속 브레이드 또는 기타 그와 동등한 도전성 물질은 효과 적인 접지 경로를 제공하기 위하여 접지 시스템에 연결되어야 한다. 주 접지 경로가 금속 커버, 금속 브레이드 또는 기타 그와 동등한 도전성 물질에 의존하는 기기에서 부식성 증기 또는 액체에 노출될 우려가 있는 경우, 재료의 내화학성을 고려해야 한다. 스테인리스강 형식의 브레이드 및 피복은 일반적으로 저항이 높으며 효과 적인 접지 경로를 제공하지 못할 수 있다. 이런 경우 대체 접지 수단 또는 접지 보호를 위한 보완 수단을 고려해야 한다. 전기 트레이스 히터 시스템에 대한 추가요구사항은 부속서 F 에서 제공된다. 55 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
1cd790fe-3ede-4909-9709-c8262675cd70 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 14 내압방폭구조 "d"에 적용되는 추가 요구사항 14.1 일반사항 Ex "d"로 완전하게 인증을 받은 기기만 설치할 수 있다. 부품으로 인증 받은 Ex "d" 용기 및 부품, 즉 "U" 표시가 되어 있는 부품은 부품 조립체(이하 기기)의 부분품으로서만 폭발위험장소 내에서 사용할 수 있으며, 기기의 인증서상에 이 부품의 사용이 허용 되어야 한다. 기기의 인증서에는 "X" 표시를 포함할 수 있으며, 해당 기기의 라벨에는 온도등급을 포 함하여 전체 방폭 기호를 표시하여야 한다. 내압방폭용기 Ex "d"에 인입구 추가 또는 개조는 제조자를 통하거나 인증된 작업장에서만 수행해야 한다. 기기 내부의 부품 변경은 의도치 않은 압력 중첩(pressure piling), 온도등급 변경, 기타 인증서를 무효 화할 수 있는 문제를 초래할 수 있기 때문에 기기 재평가 없이는 허용되지 않는다. 특정 가스가 표시되어 있거나 기기 그룹과 함께 특정 가스가 표시가 되어 있는 기기가 해당 특정 가 스 분위기에서 사용될 때에는 해당 특정 가스가 속한 기기 그룹에 적용되는 요구사항에 따라 설치되 어야 한다. 예를 들어, "IIB + H2"라고 표시된 기기를 수소 분위기에서 사용할 경우에는 IIC 기기로 설 치해야 한다. 알루미늄 도체가 평면 접합면에 인접하여 심각한 아크를 발생시키는 고장을 초래할 수 있는 경우에 는 "d" 방폭구조의 용기 내부에서 알루미늄 도체의 사용을 회피하여야 한다. 고장의 발생을 방지할 수 있는 도체 및 단자절연을 제공하거나, 마개 또는 나사 접합면을 사용하는 용기를 사용할 수도 있 다. 14.2 고체 장애물 전기기기의 설치 시에는 철재, 벽, 환경 보호 가드, 설치 브라켓, 파이프 및 다른 전기기기 등 해당 기기의 일부가 아닌 고체 장애물과 플랜지 접합면 사이의 거리가 표 13 에 규정된 값 이내로 접근하 지 않도록 유의 해야 한다. 단, 시험을 통해 이 값보다 짧은 거리에서 사용해도 안전하다고 확인된 경 우에는 예외로 한다. 표 13 - 가스 그룹에 따른 내압방폭 평면 접합면과 장애물과 의 최소 거리 ¦ 가스 그룹 ¦ 최소 거리(mm) ¦ ¦ --- ¦ --- ¦ ¦ IIA ¦ 10 ¦ ¦ IIB ¦ 30 ¦ ¦ IIC ¦ 40 ¦ 14.3 내압 접합면의 보호 제조자 기술문서에 따라 내압 접합면의 부식 방지를 유지해야 한다. 개스킷의 사용은 제조자 기술문 서에 명시된 경우에만 허용된다. 내압 접합면을 페인트로 도장해서는 안 된다. 56 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
5ab91e02-bbbb-4c19-832e-0459a6fef3d5 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 6.5.2 에 따라 정전기를 회피할 수 있다면, 조립이 완료된 후에 용기를 (사용자가) 페인트로 도장할 수 있다. 내압 접합면에 그리스를 도포하면 틈새로 유입되는 페인트의 양을 줄일 수는 있지만 완전히 막을 수는 없다. 페인트가 용기의 온도등급에 미치는 영향을 고려해야 한다. 도색이 표시의 가독성을 해쳐서는 안 된다. 제조자의 기술문서에 그리스 사용과 같은 내압 접합면 접합부 보호방법이 명시되어 있지 않은 경우 에는 조립 전에 페트롤리움 젤리(petroleum jelly), 비누처럼 굳어진 광물유(soap-thickened mineral oil) 등과 같은 내부식성 그리스(corrosion inhibiting grease)만을 접합면에 도포할 수 있다. 그리스를 도포 할 경우, 시간이 지나도 경화되지 않고 휘발성 용제를 함유하고 있지 않으며, 접합면을 부식시키지 않는 종류를 사용해야 한다. 또한 비고착 특성(non-setting characteristic)이 유지되어 추후 접합면을 분리할 수 있어야 한다. 비고 1 그리스의 적합성을 확인할 책임은 사용자에게 있다. 비고 2 실리콘 계열 그리스를 사용할 경우, 일부 형식의 가스 검출기에 영향을 줄 수 있다(KS C IEC 60079-29 참조). 용기가 그룹 IIC 에 해당하는 가스와 함께 사용되는 경우, 테이프를 사용해서는 안 된다. 비경화성 그리스를 함유하는 섬유 테이프는 다음의 조건에서 평면 접합부의 외측에 사용할 수 있다. 용기가 IIA 에 해당하는 가스에 사용되는 경우, 평면 접합부의 모든 둘레에 한 겹으로 적용하고 겹 치는 부분을 짧게 한다. 기존에 붙여진 테이프가 손상된 경우 새 테이프로 교체해야 한다. 용기가 IIB 에 해당하는 가스에 사용되는 경우, 평면 접합부의 길이와 무관하게 접합면 틈새가 0.1 mm 를 초과 해서는 안 된다. 평면 접합부의 모든 둘레에 한 겹으로 적용하고 겹치는 부분을 짧게 한다. 기존에 붙여진 테이프가 손상된 경우 새 테이프로 교체해야 한다. 14.4 전선관 시스템 전선관에 사용하는 전선관 밀봉장치는 다음 중 하나를 만족시켜야 한다. a) 기기와 함께 제공되고 기기의 기술문서에 세부적으로 명시되어 있는 밀봉장치 b) 기기의 기술문서에 명시되어 있는 밀봉장치 c) KS C IEC 60079-1 을 만족하는 밀봉장치 전선관 밀봉장치는 내압방폭구조 용기의 일부이거나 용기 인입부 인접 또는 가능한 한 가까운 곳에 최소한의 접속부품을 사용하여 설치해야 한다. 비고 1 인증 받은 조립체로 제조자가 제공한 경우가 아닌 경우에, 위 요구사항은 인접하게 결합된 용기들 간의 밀봉에도 적용된다. 평행나사를 가진 전선관 밀봉장치와 내압방폭구조의 용기 사이에는 밀봉 와셔를 장착할 수 있다. 이 경우 와셔를 설치한 후에도 적용 가능한 나사 맞물림 요구사항을 만족해야 하고 나사의 맞물림은 적 어도 5 산 이상이어야 한다. 그리스가 밀봉장치와 내압방폭구조 용기 사이에, 필요한 경우 접지를 유 57 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b4f46c14-105c-42bd-a925-6bb00d8e6415 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 지시킬 수 있고 비경화성이라면 사용할 수 있다. 전선관 밀봉장치를 용기에 직접 설치하거나 제조자의 지침에 따른 접속부품을 사용하여 설치하는 경 우 그 위치는 내압방폭용기의 인입부에 인접한다고 볼 수 있다. 용기에 가장 근접한 밀봉재의 면 (face of seal)과 용기의 외부 벽 사이의 거리는 가능한 한 가까워야 하며, 전선관의 크기 또는 50 mm 중 더 작은 값을 초과 할 수 없다. 비고 2 일반적인 연선 사이 또는 케이블 심선 사이의 간극을 통해 가스 또는 증기가 누설되거나 화 염이 전파될 수 있다. 누설과 화염전파를 감소시키기 위한 조치로서 특수한 구조가 사용될 수 있다. 가령 빈 공간이 없는 연선, 개별 연선의 밀봉, 압출 베딩(extruded bedding) 등이 있 다(9.3.2 를 참조할 수 있다). 15 안전증방폭구조 "e"의 추가 요구사항 15.1 일반사항 Ex "e"로 완전하게 인증 받은 기기만 설치할 수 있다. 부품으로 인증 받은 Ex "e" 용기 및 부품, 즉 "U" 표시가 되어 있는 부품은 부품 조립체(이하 기기)의 부분품으로만 폭발위험장소 내에서 사용할 수 있으며, 기기의 인증서상에 이 부품의 사용이 허용되 어야 한다. 기기의 인증서에는 "X" 표시를 포함할 수 있으며, 해당 기기의 라벨에는 온도등급을 포함 하여 전체 방폭 기호를 표시하여야 한다. 15.2 단자 박스의 최대 소비전력 용기 내 전력 손실에 의해 발산되는 열로 인하여 요구되는 기기 온도등급을 초과 하지 않도록 해야 한다. 다음과 같은 방법을 통해 이를 달성할 수 있다. a) 허용 단자 수, 도체 크기 및 최대 전류에 관한 제조자 사양 준수 b) 제조자가 지정한 파라미터를 사용하여 계산된 손실 전력이 정격 최대 소비전력보다 작은지 확인 형식시험 및 계산 시 도체의 길이가 용기 대각선 길이의 절반이라고 가정하기 때문에, 도체의 길이 가 가능한 한 짧아야 한다. 도체를 짧게 하면 도체의 길이가 평균적으로 형식시험의 기준을 초과 하 지 않도록 할 수 있다. 최대 허용전류가 흐르는 용기 내부의 도체 길이가 길어지면 온도등급을 초과 하는 내부 온도를 발생시킬 수 있다. 6 개 이상의 도체를 묶는 경우에도 T6 을 초과 하는 고온 발생 또는 절연 손상을 초래할 수 있기 때문 에 이를 피해야 한다. 제조자의 기술문서에 개별 단자의 크기, 허용되는 단자 수, 도체 크기, 최대 전류가 명시되어 있어야 한다(표 14 의 예 참조). 인증서에 달리 명시되지 않는 한 다음을 따른다. 단자 박스 용기 내부에는 Ex"e" 단자만 사용해야 한다. - 다른 부품은 허용되지 않는다. 하나의 연결점당 하나의 도체만 허용된다. 58 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
2da29bb1-7369-448d-9682-6024fb9dc8ff | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 15.3 도체 단말처리 슬롯 형식과 같은 일부 단자는 둘 이상의 도체 인입을 허용할 수 있다. 하나의 단자에 둘 이상의 도 체를 연결한 경우, 각각의 도체가 충분히 클램핑되도록 주의 해야 한다. 제조자 기술문서에서 허용할 때만 단면이 서로 다른 두 도체를 하나의 단자에 연결할 수 있는데, 이 경우에도 먼저 단일 압착형 페룰(ferrule) 또는 그 밖에 제조자가 지정한 방법으로 도체들을 고정시켜 야 한다. 단자대에 인접한 도체 사이의 단락 위험을 피하기 위해 단자의 금속부까지 개별 도체의 절연을 유지 해야 한다. 단일 도체에 단일 나사식 새들 클램프(saddle clamp)를 사용하는 경우, 기기와 함께 제공된 기술문서 에서 달리 허용하지 않는 한 나사 주위의 도체 끝부분이 "U"자 형태가 되도록 해야 한다. 15.4 단면적 및 연속 허용전류에 따른 최대 도체 수 한 가지 이상의 조합이 허용되는 경우, 제조자는 표로써 정보를 제공할 수 있다. 서로 다른 전류값 및/또는 단면적을 조합해서 사용하는 경우, 설치자가 표를 사용해서 계산해야 한다. 다음 표 14 는 계 산의 예시이다. 모든 단자를 동시에 사용하는 것이 아니라면 계산에 부하율을 적용할 수 있다. 표 14 - 단자/도체 배치의 예 - 단면적 및 연속 허용 전류에 따른 최대 도체 수 Chart Title: 단면적(mm2)에 따른 도체 수 Chart Type: bar 1.5 mm2 2.5 mm2 4 mm2 6 mm2 10 mm2 16 mm2 20 mm2 25 mm 35 mm 50 mm 63 mm item_01 2.5mm2 1.5mm2 2.5mm2 4mm2 6mm2 10mm2 13mm2 20mm2 25mm2 35mm2 50mm2 비고 모든 인입 도체(incoming conductor) 및 내부 링크(link)는 도체로 계산되며, 접지연결은 계산되지 않는다. 이 표를 사용하면서 KS C IEC 61439 에 따른 부등률(diversity factor) 또는 정격 부하율을 고려할 수 있다. 표 의 값을 각각의 비율로 사용하면 단면적 및 전류가 다른 회로를 가진 도체의 혼합된 크기가 가능하다. a 추가적인 임의 의 값 b (열 상승 계산을 포함하여) 제조자가 결정할 수치 59 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
8fa08218-0c66-4cea-a0e4-d7537f87d6bc | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 ¦ 단면적 (mm2) ¦ 전류 (A) ¦ 사용수량 ¦ = ¦ 사용률 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1.5 ¦ 10 ¦ 20 개(40 개 중) ¦ = ¦ 50 % ¦ ¦ 2.5 ¦ 20 ¦ 5 개(15 개 중) ¦ = ¦ 33.3 % ¦ ¦ 4 ¦ 25 ¦ 2 개(17 개 중) ¦ = ¦ 11.7 % ¦ ¦ ¦ ¦ 합계 < 100 % ¦ = ¦ 95.0 % ¦ 16 본질 안전방폭구조 "i"의 추가 요구사항 16.1 일반사항 본질안전회로 설치 시에는 근본적으로 다른 종류의 보호개념이 적용되어야 한다. 본질안전회로는 회 로의 차단 · 단락 또는 지락사고 시에도 다른 전원으로부터 에너지가 유입되지 않도록 회로를 보호하 고 회로의 안전한 에너지 제한값을 초과 하지 않도록 함으로써 그 건전성을 유지한다. 이 원칙은 달 리 명시하지 않는 한 그룹 II, 그룹 III 본질안전방폭구조 기기 및 관련기기의 본질안전회로에도 동일 하게 적용된다. 관련기기는 폭발위험장소 외부에 위치하는 것이 바람직하며, 폭발위험장소 내부에 위치한 경우에는 5 절에 따른 다른 적절한 방폭구조를 갖춰야 한다. 습기 또는 먼지의 유입이나 도전부로의 접근으로부터 회로의 본질안전 특성이 손상되는 것을 방지하 고 허용되지 않은 간섭 및 손상으로부터 회로를 보호하기 위해, 본질안전기기 및 관련기기(예를 들면 배리어)의 부품 및 내부 배선을 적합한 용기 내부에 설치해야 한다. 간섭 및 손상에 대해 동등한 수 준의 건전성을 보장할 수 있는 대체 설치 방법을 사용할 수 있다. 이런 원칙하에서 본질안전회로 설치 요구사항의 목적은 보호 대상 회로를 다른 회로로부터 격리시키 고 그 상태를 유지하는 것이다. 달리 규정되어 있지 않은 한 본질안전회로에 적용되는 요구사항은 모든 보호등급("ia", "ib", "ic")에 동일하게 적용한다. 에너지제한회로 "nL" 설치 시 본질안전회로 "ic"에 적용되는 모든 요구사항을 준수해야 한다. 16.2 기기보호등급(EPL) "Gb". "Gc" 및 "Db", "Dc"의 요구사항에 따른 설치 , 16.2.1 기기 기기보호등급 "Gb"의 요구사항을 만족하기 위해서는 본질안전기기와 관련기기의 본질안전 부품이 최 소 "ib" 보호등급 이상으로 KS C IEC 60079-11 을 준수해야 한다. 기기보호등급 "Gc"의 요구사항을 만족하기 위해서는 본질안전기기와 관련기기의 본질안전 부품이 최 소 "ic" 보호등급 이상으로 KS C IEC 60079-11 을 준수해야 한다. 기기보호등급 "Db"의 요구사항을 만족하기 위해서는 본질안전기기와 관련기기의 본질안전 부품이 기 기 그룹 III 에 대한 최소 "ib" 보호등급 이상으로 KS C IEC 60079-11 을 준수해야 한다. 기기보호등급 "Dc"의 요구사항을 만족하기 위해서는 본질안전기기와 관련기기의 본질안전 부품이 기 기 그룹 III 에 대한 최소 "ic" 보호등급 이상으로 KS C IEC 60079-11 을 준수해야 한다. 관련기기의 비본질안전 단자에 접속된 전기기기에는 해당 관련기기의 라벨에 표시된 Um 을 초과 하는 전압을 공급할 수 없으며, 예상단락전류 값이 1 500 A 를 넘을 수 없다. 60 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
822a67c1-39b5-4fa0-b690-1ec797929561 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 높은 수준의 고장이 존재할 경우, 공급측에서의 적절한 퓨즈 또는 보호를 통해서 예상단락전류를 제 한할 수 있다. 관련기기의 라벨에 표기된 Um 이 250 V 보다 낮을 경우 다음 중 한 가지 방법으로 설치해야 한다. a) Um 이 50 V a.c.나 120 V d.c.를 초과 하지 않을 경우 SELV 시스템 또는 PELV 시스템 b) KS C IEC 61558-2-6 이나 그 밖에 기술적으로 동등한 표준을 따르는 안전 절연변압기를 통해 설치 c) KS C IEC 60950, KS C IEC 61010-1 또는 그와 기술적으로 동등한 표준을 따르는 기기에 직접 연결 d) 전지 또는 배터리로부터 직접 전원공급 본질안전 시스템의 일부를 구성하는 모든 기기에 대해, 합리적으로 실행 가능한 범위 내에서 본질안 전 시스템의 일부라는 사실을 식별할 수 있는 표시를 해야 한다. 케이블 표시에 대해서는 16.2.2.6 에 기술한다. 16.2.2 케이블 16.2.2.1 일반사항 본질안전회로 전압의 두 배 또는 500 V r.m.s.(700 V d.c.) 중 큰 값에 해당하는 전압을 견딜 수 있는 절연성능을 가진 케이블만 본질안전회로에 사용하여야 한다. 폭발위험장소 내에서 사용되는 심선이나 연선의 지름은 0.1 mm 보다 작아서는 안 된다. 16.2.2.2 케이블의 전기 파라미터 본질안전회로에 사용되는 모든 케이블의 전기 파라미터(Cc 와 Lc 또는 Cc 와 LdRc)는 다음 중 하나에 따라 결정되어야 한다. a) 케이블 제조자가 제공한 가장 가혹한 경우를 가정한 전기 파라미터 b) 표본 측정에 의해 결정된 전기 파라미터 비고 관련 파라미터를 결정하는 세부적인 방법에 대해서는 부속서 H 에 제공된다. c) (스크린의 유무에 관계없이) 일반 구조의 케이블의 2 심 또는 3 심이 상호 접속된 경우, 200 pF/m 그리고 1 �H/m 또는 30 �H/� FISCO 또는 FNICO 시스템이 사용된 경우, 케이블 파라미터 요구사항은 KS C IEC 60079-25 를 준수 해야 한다. 16.2.2.3 도전성 스크린의 접지 스크린이 필요한 경우, 다음 a)부터 c)의 경우를 제외하고 스크린은 한 지점, 주로 비폭발위험장소에 있는 회로 말단에서만 접지되어야 한다. 이는 접지가 가능한 접속점 사이의 국부적인 대지전위차로 인해 스크린에 점화 수준의 순환 전류가 흐르는 것을 방지하기 위한 것이다. 61 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
dc5357ba-0e7a-4380-b645-7d2b03fa669e | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 접지된 본질안전회로가 스크린된 케이블 내에 있는 경우, 해당 회로의 스크린은 그 스크린이 차폐하 는 본질안전회로와 같은 지점에서 접지해야 한다. 접지되지 않은 본질안전회로 또는 부속회로가 스크린 케이블 내부에 있는 경우, 스크린은 한 점에서 등전위 본딩 시스템에 접속되어야 한다. 특수한 경우: a) 특수한 이유(스크린의 저항이 높거나 유도간섭을 방지하기 위한 스크린이 추가적으로 요구되는 경 우 등)로 인해 스크린의 여러 곳에 접지 접속점이 있는 경우, 다음과 같은 조건하에서 그림 2 의 배치를 사용할 수 있다. 견고한 구조의 절연된 접지도체(일반적으로 최소 굵기 4 mm2 이상. 클램프형 접속에서는 16 mm2 이 더 적합함.) 다른 도체 및 케이블 외장으로부터 500 V a.c. 또는 700 V d.c. 절연시험을 견딜 수 있도록 절 연된 접지도체와 스크린을 사용한 케이블 절연된 접지도체와 스크린이 동일한 지점(일반적으로 비폭발위험장소 쪽에 있는 케이블 말단) 에서 접지된 경우 9.3.7 에 적합하게 절연된 접지도체 절연된 접지도체와 함께 설치된 케이블의 인덕턴스 대 저항의 비(L/R)가 확정되고 16.2.2.5 의 요구사항에 적합 b) 기기가 회로 양 끝단 사이(즉 폭발위험장소와 비폭발위험장소 사이)의 등전위가 보장되도록 효과 적으로 설치 및 유지관리되고 있다면 요구될 경우 케이블의 양 끝단 모두를 접지할 수 있으며, 필 요에 따라 임의 의 중간 지점에서도 접지할 수 있다. c) 소용량 커패시터(예를 들어 1 nF, 1 500 V 세라믹)를 사용한 다중 접지는 전체 정전용량이 10 nF 를 넘지 않는 경우에 한하여 사용할 수 있다. 62 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
dc8e5185-2cf6-4f87-bf3e-097fb843da46 | KSCIEC60079-14_KR | KS CIEC 60079-14:2013 ![image](/image/placeholder) 폭발위험장소 비폭발위험장소 케이블 외장 스크린 기기 제어반 신호 절연된 접속부 「절연된 접지선 I 필요한 경우, 추가 접지 계통 스크린 접지 (16.2.2.3 참고) 그림 2 - 도전성 스크린 접지 16.2.2.4 케이블 외장 본딩 케이블 외장은 케이블의 각 말단에서 케이블 인입장치 또는 그와 동등한 장치를 통해 등전위 본딩시 스템에 본딩해야 한다. 중간에 정션박스(interposing junction box) 또는 다른 기기가 있는 경우, 일반적 으로 이러한 지점들에서도 케이블 외장을 비슷한 방식으로 등전위 본딩시스템에 본딩한다. 케이블 외장을 중간 지점에서 등전위 본딩시스템에 본딩하지 않도록 요구하는 케이블은, 케이블의 전체에 걸쳐 말단에서 반대 측 말단까지 외장의 전기적 연속성이 유지되도록 주의 를 기울여야 한다. 케이블 인입점에서 외장을 본딩하는 것이 현실적으로 어렵거나 설계상 불가능할 경우, 외장과 등전 위 본딩시스템 사이에서 발생하는 전위차로 인해 점화성 스파크가 발생하지 않도록 주의 해야 한다. 어떤 경우에도 등전위 본딩시스템과 외장 사이에 최소 한 곳 이상에서 전기적인 본딩이 이뤄져야 한 다. 케이블 외장을 접지와 분리시키기 위한 케이블 인입장치는 비폭발위험장소 또는 기기보호등급 "Gc" 또는 "Dc"를 요구하는 장소에 설치해야 한다. 16.2.2.5 케이블 및 배선의 설치 16.2.2.5.1 일반사항 본질안전회로는 본질안전 특성이 근접한 고전류 전송 단심 케이블(heavy current-carrying single core cable)과 같은 외부의 전기장 또는 자기장에 의해 영향을 받지 않도록 설치해야 한다. 스크린 또는 꼬인 심선을 사용하거나 전기장 또는 자기장 발생원으로부터 적절한 거리를 유지하는 방법 등을 통 해 이를 달성할 수 있다. 폭발위험장소 및 비폭발위험장소에서 설치되는 케이블의 경우, 9.3.7 의 케이블 요구사항 외에 추가적 으로 본질안전회로 케이블을 부주의 하게 비본질안전회로 케이블에 연결하지 않아야 한다. 다음과 같 은 방법으로 이를 달성할 수 있다. 63 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
68d43dee-a22e-4b35-bf71-82222b0d3600 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 a) 서로 다른 형식의 회로 케이블을 분리시킨다. b) 케이블이 기계적 손상으로부터 보호받을 수 있도록 설치한다(9.3.7 참조). c) 적어도 하나의 회로 유형에는 외장, 금속 피복 또는 스크린을 사용한 케이블을 사용한다(예를 들 어 모든 비본질안전회로에 외장 케이블 사용하거나 모든 본질안전회로에 외장 케이블을 사용). 16.2.2.5.2 도체 16.6 에 따라 허용되는 경우가 아닌 한 본질안전회로의 도체와 비본질안전회로의 도체가 하나의 케이 블 내에 존재해서는 안 된다. 16.2.2.7 에 따라 허용되는 경우가 아닌 한 절연성 재질의 중간층(intermediate layer) 또는 접지된 금속 칸막이(metal partition)로 서로 분리시키지 않고서는 본질안전회로 도체와 비본질안전회로의 도체가 동일한 번들(bundle) 또는 덕트에 존재해서는 안 된다. 본질안전회로 또는 비본질안전회로에 금속 피 복 또는 스크린을 사용한 경우에는 분리하지 않을 수 있다. 16.2.2.5.3 케이블의 미사용 심선 케이블의 미사용 심선은 다음 중 한 가지 방법으로 처리해야 한다. a) 적합한 단말처리를 사용하여 양쪽 끝단을 각 심선 및 접지로부터 충분히 절연시킨다. b) 케이블 내의 다른 회로가 (예를 들어 관련기기를 통하여) 접지에 연결되어 있다면, 한쪽은 동일 케이블 내의 본질안전회로 접지에 사용된 접지점에 연결하고, 그 반대쪽 끝은 적합한 단말처리를 사용하여 각 심선 및 접지로부터 충분히 절연시킨다. 비고 열 수축 튜브를 사용하거나 미사용 심선을 적절한 단자에 단말 처리하는 것은 16.2.2.5.3 의 요 구사항을 만족시킨다. 16.2.2.6 케이블의 표시 본질안전회로를 포함하는 케이블은 본질안전회로의 일부분임을 식별할 수 있는 표시를 해야 한다(다 음의 경우는 제외). 색으로 구별되는 피복이나 커버를 사용할 경우에는 본질안전회로가 포함된 케이 블에 밝은 청색을 사용해야 한다. 본질안전회로를 밝은 청색 케이블 피복으로 구분하는 경우, 본질안 전회로 식별에 혼란이나 혼동을 일으키지 않도록 본질안전회로가 들어 있지 않은 케이블에는 밝은 청색을 사용해서는 안 된다. 만약 모든 본질안전회로 케이블 또는 모든 비본질안전회로 케이블에 외장, 금속 피복 또는 스크린을 사용한 경우, 본질안전회로 케이블 표시를 하지 않을 수 있다. 청색 중성선이 있는 곳에서 본질안전회로와 비본질안전회로 케이블 사이에 혼동을 일으킬 우려가 있 는 계측 및 제어 캐비닛, 스위치기어, 배전반 등에는 다음과 같은 다른 표시 방식을 사용해야 한다. 공통의 밝은 청색 하네스 내에서 심선을 통합 라벨 부착 명확한 배치 및 공간 분리 64 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
240b3b12-e7f3-4e2c-8dc0-315ac9d98454 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 16.2.2.7 하나 이상의 본질안전회로를 포함하는 케이블 이 요구사항은 16.2.2.1 ~ 16.2.2.6 에 더해 추가적으로 적용한다. 케이블에 하나 이상의 본질안전회로가 포함될 수 있다. 비본질안전회로는 16.6 에서 규정하고 있는 예 외에 해당되지 않는 한 본질안전회로와 함께 하나의 케이블에 포함되어서는 안 된다. 본질안전 "ic" 회로가 16.2.2.8 에서 규정하는 A 형 또는 B 형 케이블에 포함될 경우에는 본질안전 "ia" 및 "ib" 회로와 함께 하나의 케이블에 포함시킬 수 있다. 도체 절연의 반지름 두께는 도체 지름과 절연의 특성에 적합해야 한다. 최소 반지름 두께는 0.2 mm 이상이어야 한다. 케이블의 절연은 최소한 다음의 절연내력 시험에 견딜 수 있는 형식이어야 한다. 외장 또는 스크린을 묶은 그룹과 모든 도체들을 묶은 그룹 간에 500 V r.m.s. a.c. 또는 750 V d.c. 케이블 도체 절반을 함께 묶은 것(bundle)과 나머지 케이블 도체 절반의 묶은 것(bundle) 사이에 교류 1 000 V r.m.s. a.c. 또는 직류 1 400 V d.c.로 절연내력 시험 실시. 각각의 회로를 스크린으로 차폐하여 한 개 이상의 본질안전회로를 구성하는 케이블에는 이 시험을 적용하지 않는다. 절연내력시험은 해당 케이블 표준에 규정된 방법에 따라 실시해야 한다. 정해진 방법이 없는 경우, KS C IEC 60079-11 에 규정된 절연내력시험에 방법에 따라 실시한다. 비고 케이블 공급자, 제조자 또는 설치자가 제공하는 검사 결과 로 위의 요구사항을 만족시킬 수 있다. 16.2.2.8 하나 이상의 본질안전회로를 포함하는 케이블의 형식과 적용가능한 고장 고려사항 본질안전 시스템에 사용되는 하나 이상의 본질안전회로를 포함하는 케이블에서 고려해야 하는 고장 은 사용되는 케이블의 형식에 따라 다르다. A 형 16.2.2.7 의 요구사항을 만족시키며, 추가적으로 도전성 스크린을 통해 각 본질안전회로마다 개별 적인 보호를 제공하여 이러한 회로들이 서로 연결되는 것을 방지함. 또한 케이블의 스크린은 표면 적의 60 %를 최소한 커버하여야 함. 이러한 케이블의 경우 회로 사이의 고장은 고려하지 않는다. B 형 고정 설치되어 있고 손상으로부터 효과 적으로 보호되며, 16.2.2.7 의 요구사항을 만족시킴. 추가적 으로 케이블 내의 어떤 회로도 최대출력전압 Uo 가 60 V 를 초과 하지 않음. 이러한 케이블의 경우 회로 사이의 고장은 고려하지 않는다. C 형 16.2.2.7 의 요구사항을 만족시키지만 A 형 또는 B 형의 추가 요구사항을 만족하지 않는 케이블의 경우, "ia" 또는 "ib" 회로에서 도체 사이의 최대 2 개의 단락 그리고 동시에 최대 4 개의 개방을 고 려해야 한다. 동일한 회로들의 경우에는 "ia" 및 "ib"에서 요구되는 값보다 4 배 높은 스파크 점화 파라미터 안전율을 가진 케이블을 사용할 경우 고장을 고려할 필요가 없다. 16.2.3 본질안전회로의 접지 본질안전회로는 다음 중 하나에 적합하여야 한다. 65 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
4fbad5de-fd3d-47b8-b09d-6b7b31a55463 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 a) 대지로부터 격리 b) 본질안전회로가 설치된 영역 전체에 걸쳐 등전위 본딩 시스템이 존재하는 경우, 등전위본딩 시스 템의 한 지점에 연결 본질안전회로의 설치 방법은 회로의 기능적 요구사항과 제조자 설명서에 따라 선택해야 한다. 회로가 한 지점만 접지된 각각의 보조회로로 전기적으로 분리될 경우, 해당 회로에 하나 이상의 접 지접속이 허용된다. 접지와 분리되어 있는 본질안전회로의 경우 정전기 축적에 주의 해야 한다. 정전기 제거 등을 목적으 로 0.2 M�을 초과 하는 저항을 통해 접지에 연결하는 경우에는 접지가 된 것으로 보지 않는다. 전기적으로 분리되지 않은 안전배리어가 있는 기기의 경우와 같이 안전을 위해 필요하다면 본질안전 회로를 접지해야 한다. 용접된 열전대와 같이 기능적인 이유로 필요한 경우에도 본질안전회로를 접 지할 수 있다. 본질안전기기가 KS C IEC 60079-11 에 따른 최소 500 V a.c. r.m.s.의 절연내력시험을 견딜 수 없다면 해당 기기는 접지된 것으로 간주된다. (사용된 설치 방식 등으로) 기기가 접지되어 있고 기기와 관련기기의 접지접속점 사이에 본딩도체가 사용된 경우, 위의 a) 또는 b)를 따를 필요가 없다. 이런 경우 순환 고장 전류로 인한 위험을 피하기 위해 전문가의 검토가 필요하다. 기기보호등급 "Ga" 기기 요구사항을 준수해야 하는 경우 특히 주의 가 필요하다. 본딩도체를 사용할 경우 사용 조건에 적합해야 하고, 단면적인 4 mm2 이상인 구리 도 체여야 하고, 플러그나 소켓을 사용하지 않고 영구적으로 설치되어야 하고, 적절한 기계적 보호를 받 아야 하며, IP 등급을 제외한 방폭구조 "e"의 요구사항을 준수하는 단자가 있어야 한다. 본질안전회로에서 [제너 배리어(Zener Barriers)와 같은] 갈바닉 절연이 되어 있지 않은 안전배리어의 접지단자는 다음 중 한 가지 방식을 따라야 한다. 1) 가능한 한 최단거리로 등전위 본딩 시스템에 접속 2) TN-S 시스템의 경우, 연결지점과 주전원시스템 접지지점 사이의 임피던스가 1� 미만이 되는 접 지지점에 접속. 스위치룸의 접지봉 또는 별도의 접지봉에 연결함으로써 이를 달성할 수 있다. 도체와 접촉할 수도 있는 금속부분(예를 들어 제어반 프레임)을 통해 흐르는 고장전류가 접지로 전달 되지 않도록 해당 도체를 절연해야 한다. 손상 위험성이 높은 장소에서는 기계적 보호도 제공되어야 한다. 접지도체의 단면적은 다음 중 하나에 따라야 한다. 최대허용전류(maximum possible current)를 연속으로 흘릴 수 있는 정격을 가진 개별 단면적이 1. 5 mm2 이상인 구리 도체 2 개 이상 단면적이 4 mm2 이상인 구리 도체 1 개 이상 시험이 용이하도록 두 개의 도체를 제공하는 것이 바람직하다. 배리어 입력단자에 접속된 공급시스템의 예상 단락전류를 접지접속부가 수용할 수 없는 경우에는 그 에 따라 접지부의 단면적을 증가시키거나 도체를 추가해야 한다. 접지접속에 정션 박스를 사용하는 경우, 연속적인 접지 건전성을 유지하기 위한 특별한 주의 가 필요 하다. 66 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
cd7b3996-fbcd-423c-ab4e-f0766e4b392b | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 16.2.4 본질안전회로의 검증 16.2.4.1 일반사항 본질안전시스템 전체에 적용되는 파라미터를 정의 하는 인증서가 있지 않는 한 16.2.4 전체를 적용해 야 한다. 케이블을 포함한 본질안전회로 설치 시에는 최대 허용인덕턴스 및 커패시턴스 또는 L/R 비 및 최고 표면온도를 초과 해서는 안 된다. 허용값은 해당 기기의 기술문서나 명판으로부터 제공받아야 한다. 폭발위험장소에 설치하는 기기의 온도등급은 해당 기기의 라벨 또는 기술문서로부터 결정해야 한다. 전기기기의 사용 조건에 따라 온도등급이 달라질 수도 있다(일반적으로 주위온도 또는 입력 파라미 터 U, /, P 에 따라 결정된다). 16.2.4.2 시스템 기술문서 시스템 설계자는 서로 연결된 배선을 포함하여 전기기기의 품목, 시스템의 전기적 파라미터가 기술 되어 있는 시스템 기술문서를 작성해야 한다. 안전을 확보하기 위해 요구되는 시스템 기술문서의 작성양식은 명확하게 특정되어 있지는 않지만, 가령 도면, 적용계획, 유지보수 매뉴얼 또는 이와 비슷한 문서를 통해 기술할 수 있다. 시스템 기술 문서는 특정 설치에 관련된 정보에 쉽게 접근할 수 있는 방식으로 준비되고 유지되어야 한다. 비고 예시는 KS C IEC 60079-25 에서 찾을 수 있다. 16.2.4.3 단일 전원 본질안전회로 각 본질안전기기의 최대입력전압 Ui, 최대입력전류 /i, 최대입력전력 Pi 값은 각 전원의 최대출력전압 U。, 최대출력전류 10, 최대출력전력 Po 보다 크거나 같아야 한다. 본질안전회로의 기기 그룹은 그 본질안전회로를 구성하는 기기의 그룹 중 가장 낮은 그룹과 동일하 다(예를 들어 기기 그룹이 IIB 와 IIC 인 전기기기로 구성된 회로의 기기 그룹은 IIB 이다). 본질안전회로의 보호등급은 그 본질안전회로를 구성하는 기기의 보호등급 중 가장 낮은 보호등급이 다(예를 들어 "ib"와 "ic"인 기기로 구성된 회로의 보호등급은 "ic"이다). 시스템에 포함된 모든 기기의 인덕턴스, 커패시턴스와 모든 케이블의 인덕턴스, 커패시턴스의 총합은 전원의 L。 및 C。와 같거나 작아야 한다. 케이블을 제외하고 연결된 모든 기기의 전체 인덕턴스와 커패시턴스 합이 전원의 L。와 C。의 1 %를 각각 초과 하는 경우, L。 및 C。의 허용값을 반으로 줄여야 하고 이에 따라 허용 가능한 케이블의 인턱 턴스와 커패시턴스를 조정하여야 한다. 어떠한 경우에도 이 규칙에 따른 최대 외부 커패시턴스 C。는 그룹 IIB 에서 최대 1 �F 이며 그룹 IIC 에서는 600 nF 으로 제한된다. 추가적인 정보는 KS C IEC 60079- 25 에 제공된다. 비고 1 그룹 IIA 에 대한 추가 제한사항은 없다. 비고 2 연결된 모든 전기기기에는 제조자가 Li 및 Ci 값을 표기하지 않은 단순기기도 포함된다. 전원 은 관련기기 또는 다른 본질안전 전기기기일 수 있다. 67 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
3186699d-517c-43dd-b220-10f3a647fbba | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 연결된 모든 기기의 총 인덕턴스가 L。의 1 %보다 큰 경우가 아니라면 전원의 Lo 를 사용하여 평가하 는 대신 Lo/Ro 비를 사용할 수 있다. 연결된 모든 기기의 총 인덕턴스가 L。의 1 %보다 큰 경우에는 KS C IEC 60079-25 에 따라 허용되는 케이블의 L/R 비를 다시 계산해야 한다. 제한 L/R 비가 결정되면 케이블의 L/R 비가 그 제한 비보다 작야야 하며, C。도 여전히 연결된 기기 및 케이블에 적용해야 한다. 전원 관련 기술문서에 Lo/Ro 비가 포함되어 있지 않은 경우, 케이블에 대한 L/R 비의 평가를 사용할 수 없다. 케이블 파라미터 결정에 관한 사항은 16.2.2.2 에 제공된다. 16.2.4.4 하나 이상의 관련기기가 있는 본질안전회로 본질안전회로가 하나 이상의 관련기기를 포함하거나 둘 이상의 본질안전회로가 서로 연결되어 있는 경우, KS C IEC 60079-11 및 KS C IEC 60079-25 에 따른 이론적인 계산 또는 스파크 점화 시험을 통 해 전체 시스템의 본질안전관련 안전성을 확인하여야 한다. 기기 그룹, 온도등급, 보호등급도 결정해 야 한다. 나머지 회로로부터 관련기기로 전압 및 전류가 유입되어 발생할 수 있는 위험을 고려해야 한다. 다 른 관련기기의 U。 및 10 를 적절히 조합함으로써 관련기기 내부의 전압 및 전류 제한 소자의 정격이 초과 되지 않도록 해야 한다. 비고 1 선형 전류/전압 특성을 가진 관련기기의 경우, 부속서 I 에 계산의 근거를 제공한다. 비선형 전류/전압 특성을 가진 관련기기의 경우, KS C IEC 60079-25 의 비선형 및 선형 본질안전회로 연결 지침을 적용하거나 전문가의 평가를 참고한다. 비고 2 고려 중인 본질안전회로 관련기기의 내부 저항 Ri = UJI 가 알려져 있는 경우(KS C IEC 60079-25 에 따른 선형 특성), KS C IEC 60079-25 에 규정된 하나 이상의 전원을 가진 회로의 평가 방법을 대신 적용할 수 있다. 16.3 기기보호등급(EPL) "Ga" 또는 "Da" 요구사항을 만족하는 설치 본질안전회로는 다음과 같은 특수한 요구사항에 따라 수정되는 경우를 제외하면 16.2 에 따라 설치해 야 한다. 기기보호등급 "Ga"가 요구되는 장소에 본질안전회로를 설치하는 경우, 본질안전기기 및 관련기기가 KS C IEC 60079-11 의 보호등급 "ia"를 만족해야 한다. (모든 단순기기, 본질안전기기, 관련기기 및 연 결 케이블의 최대 허용 전기 파라미터를 포함한) 회로의 보호등급은 "ia"이어야 한다. 기기보호등급 "Da"가 요구되는 장소에 본질안전회로를 설치하는 경우, 본질안전기기 및 관련기기가 KS C IEC 60079-11 에 따른 그룹 III 의 보호등급 "ia"를 만족해야 한다. 본질안전회로와 비본질안전회로가 갈바닉 절연된 관련기기를 사용하는 것이 바람직하다. 등전위 본딩 시스템의 경우 하나의 고장만으로도 점화 위험이 발생할 수 있기 때문에, 16.2.3 b)에 따 라 접지가 되어 있고, 안전 지역의 단자에 연결된 모든 주전원 기기가 2 중권선 변압기(double wound transformer)에 의해 주전원으로부터 절연되어 있는 경우에만 갈바닉 절연이 되어 있지 않은 관련기 기를 사용할 수 있다. 이 경우 변압기의 1 차 권선은 적절한 차단용량을 가진 퓨즈로 보호되어야 한다. 68 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
e8da9455-f90b-4c3f-8f48-191150adbc89 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 본질안전회로가 부속회로들로 나뉘어 있는 경우, 중 갈바닉 절연 소자를 포함하여 기기보호등급 "Ga" 부속회로가 요구되는 장소의 보호등급은 "ia"이어야 한다. "Ga"가 요구되는 장소가 아닌 경우 부속회 로들의 기기보호등급은 "ib" 또는 "ic"이다. 비고 1 갈바닉 절연은 관련기기를 통해 달성하거나 기기보호등급 Gb, Db, Gc, Dc 또는 비폭발위험장 소에 위치하는 본질안전회로 내 전기적 절연 기기를 통해 달성할 수 있다. 기능상의 이유로 회로를 접지해야 하는 경우, 접지연결은 기기보호등급 "Ga" 또는 "Da"가 요구되는 장소 외부에서 해야 하며, 기기보호등급 "Ga" 또는 "Da"인 전기기기에 가능한 한 근접해야 한다. 회로가 작동하는 데 접지가 필수적인 경우에는(예를 들어 접지된 팁 열전대 또는 전도도 측정 프로 브), 하나 이상의 접지 연결점이 있어도 고장이 발생하지 않는다는 것이 입증되지 않은 한 해당 접지 가 유일한 접지여야 한다. 본질안전회로의 일부가 기기보호등급 "Ga" 또는 "Da"가 요구되는 장소에 설치되어 있고 해당 기기 및 관련기기가 예를 들어 대기전기(atmospheric electricity) 등으로 인해 위험한 전위차를 발생시킬 우 려가 있는 경우, 케이블의 비접지 심선과 구조물 사이에, 기기보호등급 "Ga" 또는 "Da"가 요구되는 장소에서 가능한 한 가까운 지점(1m 이내가 가장 바람직함.)에 서지 보호장치를 설치해야 한다. 이러 한 장소의 예로 인화성 액체 보관 탱크, 폐수처리 플랜트, 석유화학 공정의 증류탑 등이 있다. 가장 큰 전위차의 위험이 발생하는 곳은 주로 넓게 분포된 플랜트 또는 옥외로 노출된 기기가 있는 장소 인데, 이런 경우에는 단순히 케이블 또는 탱크를 매설을 통해 설치하는 것만으로 위험이 경감되지 않는다. 서지 보호장치는 10 kA(KS C IEC 60060-1 에 따라 8/20 �s 임펄스, 10 회)의 최소 피크방전전류를 우회 시킬 수 있어야 한다. 서지 보호장치와 구조물 사이 연결도체의 단면적은 최소 4 mm2 의 구리와 동등 한 수준이어야 한다. 서지 보호장치의 방전개시전압(spark-over voltage)은 사용자와 설치 전문가가 결정해야 한다. 본질안전회로에 하나 또는 그 이상의 저전압 서지 보호장치를 사용하는 경우 해당 회로에서 고려된 접지방식이 변경될 수 있다. 본질안전 시스템의 설계 시 이 점을 고려해야 한다. 비고 2 서지 보호장치 사용에 관한 추가적인 정보는 KS C IEC 60079-25 에 제공된다. 기기보호등급 "Ga" 또는 "Da"가 요구되는 장소의 본질안전기기와 서지 보호장치 사이에 설치되는 케 이블은 낙뢰로부터 보호되도록 설치해야 한다. 16.4 단순 기기 단순기기에는 기기보호등급이 적용되지 않는다. 단순기기에는 단순기기임을 식별할 수 있는 내구성 있는 라벨을 부착해야 한다. 제조자, 설치자를 포함하여 누구든지 단순기기에 라벨을 부착할 수 있으며, 단순기기임을 명확하게 식별할 수 있다면 설치에 적합한 어떤 표시 또는 코드도 사용할 수 있다. 계기루프번호와 같이 단순기기 식별에 도움이 되는 추가 정보도 라벨에 표시할 수 있다. 단순기기에 대한 정의 는 3.5.5 의 정의 를 따른다. 다음과 같은 기기가 단순기기에 포함된다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 69 | {}
a87df86d-6175-4e0b-9614-22969a959db2 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 a) 스위치, 정션 박스, 저항 및 단순 반도체 부품 등 수동 부품 b) 커패시터 또는 인덕터와 같이 (시스템의 전반적인 안전을 결정할 때 고려해야 하는) 파라미터가 명확하고, 회로가 단순하며, 단일 부품으로 구성되어 있는 에너지 저장원 c) 열전대, 광전지 등과 같이 1.5V, 100 mA, 25 mW 이상을 발생시키지 않는 에너지 발생원 단순기기도 KS C IEC 60079-11 의 관련 요구사항을 만족해야 한다. 비고 1 KS C IEC 60079-11 은 단순기기를 방폭기기 표시 대상에서 제외한다. 단순기기의 경우 온도등급을 얻기 위해서 전원의 P。 값으로부터 최고표면온도를 결정할 수 있다. 최고표면온도는 다음 식에 따라 계산되어야 한다. T=PoRth + Tamb 여기에서 ¦ T ¦ : 표면온도 ¦ ¦ --- ¦ --- ¦ ¦ Po ¦ : 관련기기에 표시된 최대출력전력 ¦ ¦ Rth ¦ : 표면온도상승(KW)(설치 조건에 따라 제조자에 의해 정해짐.) ¦ ¦ Tamb ¦ : 단순기기가 설치되는 지점에서의 주위온도(가령 온도센서) ¦ 총 표면적이 20 mm2 이상인 단순기기는 주위온도에 따라 공급받는 최대 전력이 표 15 의 기준값을 초과 하지 않으면 온도등급을 T4 로 지정할 수 있다. 표 15 - 기기그룹 II 의 주위온도에 따른 최대 소비전력 ¦ 최대 주변 온도 ¦ °C ¦ 40 ¦ 50 ¦ 60 ¦ 70 ¦ 80 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 최대 소비 전력 ¦ W ¦ 1.3 ¦ 1.25 ¦ 1.2 ¦ 1.1 ¦ 1.0 ¦ 소형 부품은 다음과 같은 제한 조건하에서 온도등급 T4 또는 T5 로 지정할 수 있다. a) 표면적이 20 mm2(리드선 제외)보다 작은 부품은 표면 온도가 275 °C 를 초과 하지 않으면 T4 로 분 류할 수 있다. b) 표면적이 20 mm2 초과 1 000 mm2 미만인 부품(리드선 제외)은 표면 온도가 200 °C 를 초과 하지 않으면 T4 로 분류할 수 있다. c) 표면적이 1 000 mm2 보다 작은 부품(리드선 제외)은 표면 온도가 150 °C 를 초과 하지 않으면 T5 로 분류할 수 있다. 비고 2 단순기기에 대해 최대전력의 제한값을 조정하는 것은 그룹 III 에는 적용할 수 없다. 단순기기가 본질안전회로 접지와 의 절연을 유지할 필요가 있는 경우에는 500 V a.c. r.m.s. 또는 700 V d.c. 또는 본질안전회로의 전압의 두 배 중 가장 큰 값의 시험전압에 견딜 수 있어야 한다. 단자는 비본질안전 단자 또는 접속부로부터 최소 50 mm 이상 이격되어야 하며, 그렇지 않을 경우 KS C IEC 60079-11 에 따른 별도의 이격 조치가 필요하다. 70 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
612ad664-7942-4a7b-9653-5f63ceb57399 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 단순기기는 기술문서에서 명시적으로 허용하지 않는 한 본질안전회로와 연결되면 안 된다. 비고 3 단자의 절연 및 이격에 대한 요구사항은 KS C IEC 60079-11 에서 인용된 것이다. 본질안전회로의 단자 박스 및 스위치는 온도 상승이 40 K 미만인 것으로 고려한다. 따라서 주위온도 가 40 °C 를 초과 하지 않는 경우에는 T6, 55 °C 를 초과 하지 않는 경우에는 T5, 80 °C 를 초과 하지 않는 경우에는 T4 의 온도등급을 가질 수 있다. 16.5 단자 박스 16.5.1 일반사항 습기 또는 분진의 유입이나 도전부로의 접근에 의하여 분리된 본질안전회로의 특성을 손상시키거나 평가받지 않은 본질안전회로의 조합을 초래할 경우, 분리 상태가 손상되지 않도록 회로를 설치해야 한다. 간섭이나 손상에 대해 동등한 수준의 보호를 제공할 수 있는 다른 설치 방법도 사용할 수 있 다. 사용된 단자 박스는 설치된 환경에 적합해야 한다. 일반적으로 최소 IP54 이상의 용기를 사용하는 것이 바람직하다. 케이블 인입장치는 용기의 보호등급을 유지하여야 한다. 본질안전 배선 단자들은 접지부로부터 최소 3mm 이상 이격되어야 한다. 단자 박스에는 "경고 - 본질안전회로(WARNING - Intrinsically safe circuits)" 또는 기술적으로 동등 한 문구를 표시해야 한다. 비고 안전증 용기에 적절하게 인증을 받은 안전증 단자를 사용하면 16.5.2 및 16.5.3 의 요구사항을 만족시킬 수 있다. 16.5.2 하나의 본질안전회로만 설치된 단자 박스 이 경우에는 추가로 적용되는 요구사항이 없다. 16.5.3 하나 이상의 본질안전회로가 설치된 단자 박스 본질안전회로 조합에 대한 평가를 통해 본질안전회로 조합의 본질안전 특성이 손상되지 않았다는 사 실이 입증된 경우가 아닌 한 단자 박스가 다음과 같은 최소 요구사항에 적합해야 본질안전 요구사항 을 만족할 수 있다. 16.5.1 의 용기 요구사항 외에 추가적으로, 용기의 재료에 따라 KS C IEC 60079-0 의 비금속 용기 및 비금속부 요구사항, 금속 용기 및 금속부 요구사항을 만족해야 한다. 비고 비금속 용기 및 비금속부에 적용되는 KS C IEC 60079-0 의 요구사항에는 내충격성, 내광성, 인 위적 노화시험 등이 포함된다. 금속 용기 및 금속부에 적용되는 KS C IEC 60079-0 의 요구사항 에는 내충격성, 합금에 사용된 경금속의 양 등이 포함된다. 접속부의 나도체 사이의 절연공간거리는 각각의 본질안전회로 간 최소 6 mm 이어야 한다. 16.5.4 비본질안전회로 및 본질안전회로가 함께 설치된 단자 박스 본질안전회로 및 비본질안전회로가 모두 포함되어 있는 단자 박스는 16.5.3 의 요구사항 외에 추가적 71 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
42c0de51-394c-4420-8ac1-a6f3784dca18 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 으로 다음과 같은 최소 요구사항을 만족해야 한다. a) 단자 박스가 폭발위험장소에 설치되는 경우, 용기와 비본질안전 부품은 적절한 방폭구조에 적합하 여야 한다. b) 본질안전회로의 나도체와 비본질안전회로 사이의 절연공간거리는 적어도 50 mm 또는 KS C IEC 60079-11 에서 요구하는 거리에 적합하여야 한다. c) 통전중인 비본질안전회로에 접근할 수 있는 용기 커버에는 "경고 - 통전 중 개방하지 마시오(WA RNING DO NOT OPEN WHEN ENERGIZED")라는 문구가 표시된 라벨을 부착하거나 d) 방폭구조 "i"에 의해 보호되지 않는 모든 나도체는, 용기가 열려 있을 때, 최소 IP30 을 제공할 수 있는 별도의 내부 커버를 가지고 있어야 한다. 또한 내부 커버에는 "경고 - IP30 내부 커버로 보 호되는 비본질안전회로(WARNING - NON-INTRINSICALLY SAFE CIRCUITS PROTECTED BY I NTERNAL IP30 COVER)"라는 문구가 표시된 라벨을 부착해야 한다. 비고 내부 커버의 목적은 본질안전회로 유지보수를 위해 용기를 잠시 열었을 때 통전 중인 비본질 안전회로에 대한 접근을 방지하기 위한 최소한의 허용 가능한 보호등급을 제공하는 것이다. 커버는 전기적 충격(감전)으로부터 보호를 제공하기 위한 것이 아니다. 본질안전회로 단자는 비본질안전회로의 단자와 명확하게 구분되도록 표시를 해야 한다. 색을 사용해서 본질안전회로 단자를 구분할 수 있으며, 이 경우 밝은 청색을 사용해야 한다. 16.5.5 외부 연결용 플러그 및 소켓 외부의 본질안전회로 접속에 사용되는 플러그 및 소켓은 비본질안전회로의 플러그 및 소켓과 구분되 어야 하며, 교차 사용이 불가능해야 한다. 기기에 하나 이상의 플러그 및 소켓이 장착되어 있고, 교 차 사용 시 방폭구조에 악영향을 미칠 수 있는 경우, 해당 플러그 및 소켓을 교차 사용하는 것이 불 가능해야 한다. 이를 위해 키를 사용하거나(keying) 색상 또는 표시로 구분하여 교차 사용을 명백하 게 인지시킴으로써 결합할 수 있는 플러그와 소켓이 구분되어야 한다. 연결부가 접지된 회로를 포함하고 있고 방폭구조가 이 접지의 연결에 의존하는 경우에는 KS C IEC 60079-11 의 접지 도체, 연결 및 단자의 요구사항에 따라 당 연결부가 구성되어야 한다. 16.6 특수 용도 전원 케이블의 모니터링과 같은 특수 용도로 사용되는 경우, 본질안전의 원리가 적용되는 회로를 전 원 회로와 동일한 케이블에 포함시킬 수 있다. 이러한 설치에는 그에 따른 위험성에 대한 별도의 분 석이 필요하다. 특수한 용도로 사용되는 경우, 본질안전회로가 비본질안전회로를 포함하는 동일한 플러그 및 소켓 내에서도 허용된다. 이때에는 해당 회로가 KS C IEC 60079-11 의 요구사항을 만족시키고, 비본질안전 회로는 KS C IEC 60079 의 관련 방폭구조의 요구사항을 만족시키며, 다른 회로가 통전 중일 때 본질 안전이 요구되지 않아야 한다. 72 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
d6698df2-b839-40d6-9cb8-811e7df40cf8 | KSCIEC60079-14_KR | KS CIEC 60079-14:2013 17 압력방폭용기에 적용되는 추가 요구사항 17.1 일반사항 Ex "p"로 완전하게 인증을 받은 기기만 설치할 수 있다. 부품으로 인증받은 Ex "p" 용기 및 부품, 즉 인증서에 "U" 표시만 되어 있는 용기 및 부품은 폭발위 험장소에 설치할 수 없다. 인증 받지 않은 용기(산업용 용기)를 인증 받은 제어/퍼지 장치와 함께 설치할 수 없다. 언제나 전체 유닛, 제어/퍼징 장치, 관련기기를 하나의 단위로 인증 받아야 한다. 부품으로 인증 받은 압력방폭용기 및 부품, 즉 "U" 표시가 되어 있는 부품은 부품 조립체(이하 기기) 의 부분품으로만 폭발위험장소 내에서 사용할 수 있으며, 기기의 인증서상에 이 부품의 사용이 허용 되어야 한다. 기기의 인증서에는 "X" 표시를 포함할 수 있으며, 해당 기기의 라벨에는 온도등급을 포 함하여 전체 방폭 기호를 표시하여야 한다. 17.2 압력방폭구조 "p" 17.2.1 일반사항 기기 전체를 하나의 단위로 평가를 받은 경우가 아니라면 전체 기기에 대해 기술문서 및 이 표준의 요구사항에 대한 적합성을 확인해야 한다. 해당 장소의 기기보호등급 요구사항 및 표 16 에 따라 "Gc"를 만족하지 않는 기기가 용기에 포함되어 있는지 여부에 따라 "pxb", "pyb", "pzc" 중에서 필요한 보호등급을 결정해야 한다. 표 16 - 보호등급의 결정 (용기 내에 인화성 가스의 누출원이 존재하지 않는 경우) ¦ 기기보호등급(EPL) ¦ EPL "Gc"의 요구사항을 만족하지 않는 기기가 들어 있는 용기 ¦ EPL "Gc"의 요구사항을 만족하는 기기가 들어 있는 용기 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ "Gb" ¦ "pxb" ¦ "pyb" ¦ ¦ "Gc" ¦ "pxb" 또는 "pzc" ¦ 가압 불필요 ¦ KS C IEC 60079-2 에 따르면 보호등급 "py"가 적용된 기기는 방폭구조 "d," "e", "i", "m", "nA", "nC", "O" "q"만 포함할 수 있다. 17.2.2 덕트 모든 덕트 및 덕트 연결부는 다음 중 어느 하나의 기준에 따른 압력 또는 200 Pa(2 mbar)에 견딜 수 있어야 한다. a) 압력방폭 기기의 제조자에 의해 규정된 정상 작동 중 최대 양압의 1.5 배 b) 압력방폭 기기의 제조자에 의하여 가압기기의 압력원(예를 들어 팬)이 지정되어 있는 경우, 모든 배출구를 닫은 상태에서 가압기기에 의하여 도달할 수 있는 최대 양압 덕트 및 덕트 연결부의 재료는 사용되는 보호가스, 인화성 가스 또는 증기에 의해 악영향을 받지 않 73 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
be90c5e0-a7a3-43a8-aa05-a16f6c546482 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 아야 한다. 실린더 공급식을 제외하고 보호가스가 공급 덕트로 들어가는 지점은 비폭발위험장소에 위치해야 한다. 덕트는 가능한 한 비폭발위험장소에 위치해야 한다. 덕트가 폭발위험장소를 통과 하고 보호가스의 압 력이 대기압보다 낮은 경우에는 덕트에 누설이 없어야 한다. 보호가스 배기 덕트의 출구는 비폭발위험장소 내에 위치하는 것이 바람직하다. 그렇지 않을 경우 표 17 과 같이 점화 가능성이 있는 스파크 또는 입자의 방출을 방지할 수 있는 불꽃 및 입자 배리어의 설치를 고려해야 한다. 비고 퍼지를 하는 동안 덕트 출구에 소규모 폭발위험장소가 형성될 수 있다. 표 17 - 불꽃 및 입자 배리어 ¦ 배기 덕트 출구 위치에 대한 기기보호등급 요구사항 ¦ 기기 ¦ 기기 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 배기 덕트 출구 위치에 대한 기기보호등급 요구사항 ¦ A ¦ B ¦ ¦ "Gb" ¦ 필요 a ¦ 필요 a ¦ ¦ "Gc" ¦ 필요 ¦ 불필요 ¦ ¦ A: 정상 작동 중 점화성 스파크나 입자를 발생시킬 수 있는 기기 B: 정상 작동 중 점화성 스파크나 입자를 발생시키지 않는 기기 ¦ A: 정상 작동 중 점화성 스파크나 입자를 발생시킬 수 있는 기기 B: 정상 작동 중 점화성 스파크나 입자를 발생시키지 않는 기기 ¦ A: 정상 작동 중 점화성 스파크나 입자를 발생시킬 수 있는 기기 B: 정상 작동 중 점화성 스파크나 입자를 발생시키지 않는 기기 ¦ ¦ a 가압 고장 시 용기 내부 기기의 온도가 위험 수준에 도달할 수 있는 경우, 압력방폭용기 내부로 주위의 분위기가 급속히 유입되는 것을 방지하기 위한 장치를 제공해야 한다. ¦ a 가압 고장 시 용기 내부 기기의 온도가 위험 수준에 도달할 수 있는 경우, 압력방폭용기 내부로 주위의 분위기가 급속히 유입되는 것을 방지하기 위한 장치를 제공해야 한다. ¦ a 가압 고장 시 용기 내부 기기의 온도가 위험 수준에 도달할 수 있는 경우, 압력방폭용기 내부로 주위의 분위기가 급속히 유입되는 것을 방지하기 위한 장치를 제공해야 한다. ¦ 송풍기 또는 압축기와 같이 보호가스 공급용으로 사용되는 가압용 기기는 가능한 한 비폭발위험장소 에 설치해야 한다. 구동 전동기 또는 그 제어장치가 공급 덕트 내에 있거나 불가피하게 폭발위험장 소 내의 설치할 경우, 가압용 기기를 적절하게 보호해야 한다. 17.2.3 가압 실패 시의 조치 17.2.3.1 일반사항 가압시스템에는 비가압 상태(예를 들어 용기가 개방된 상태)에서도 통전을 유지하기 위한 오버라이드 장치(override device) 또는 "정비 스위치"가 때때로 설치된다. 이런 장치는 사용 중 해당 장소에 인화성 가스 또는 증기가 존재하지 않는다는 것이 확인된 경우 ("gas-free" 상황)에만 폭발위험장소에서 사용할 수 있다. 해당 용기는 인화성 가스가 감지되면 즉시 전원이 차단되어야 하며 재작동 전에 다시 퍼지시켜야 한다. 가압이 재개된 이후에는 퍼지가 불필요한데, 만약 수동 오버라이드의 사용 중에 인화성 가스가 감지 된 경우라면 재퍼지를 실시할 필요가 있다. 17.2.3.2 내부 누출원이 없는 기기 17.2.3.2.1 일반사항 내부에 누출원이 없는 전기기기로 구성된 압력방폭용기는 보호가스 압력유지 실패 시 표 18 을 따라 야 한다. 74 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f2084509-7dd8-4c80-9d02-767db6375367 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 정적가압에 의해 보호되는 압력방폭용기가 압력을 상실한 경우, 비폭발위험장소로 이동시켜서 재가 압을 해야 한다. 정적가압에 의해 보호되는 압력방폭용기가 압력을 상실한 경우, 압력 모니터링 장치를 잠가야 하며 (lock out), 보호가스를 재주입하고 압력이 복구된 이후에만 재설정하여야 한다. 표 18 - 내부 누출원이 없는 압력방폭용기에 적용되는 보호 요구사항 ¦ EPL 요구사항 ¦ 비가압상태에서 기기보호등급 "Gc"의 요구사항을 만족하지 못하는 기기가 설치된 용기 ¦ 비가압상태에서 기기보호등급 "Gc"의 요구사항을 만족하는 기기가 설치된 용기 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ "Gb" ¦ 경보 및 전원차단 a (17.2.3.2.2, 17.2.3.2.3 적용) ¦ 경보 b (17.2.3.2.3 적용) ¦ ¦ "Gc" ¦ 경 보 b (17.2.3.2.3 적용) ¦ 가압 불필요 ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ ¦ 가능한 한 신속하게 가압을 복구시키되, 24 시간 이내이어야 ¦ 한다. 가압이 작동하지 않는 동안에 용 ¦ ¦ 기 내부로 인화성 물질이 유입되지 않도록 해야 한다. 가압 실패 시 압력방폭기기의 전원이 자동으로 꺼지도록 되어 있는 경우에는 안전을 위한 경보장 치가 추가로 필요하지 않을 수 있으며, 이는 기기보호등급 "Gb"가 요구되는 장소의 경우에도 동일 하다. 기기보호등급 "Gc"가 요구되는 장소에서처럼 압력방폭기기의 전원이 자동으로 꺼지지 않는 경우에는 작업자가 즉시 압력을 복구하거나 기기의 전원을 차단하는 조치가 뒤따른다면 최소한의 조치로서 경보장치를 사용할 것을 권장한다. 압력방폭용기 내의 기기가 용기가 설치된 외부 장소에서 요구하는 기기보호등급에 적합한 경우, 가압 실패 시에도 해당 기기의 전원을 차단할 필요가 없다. 그러나 점화성 스파크를 발생시킬 수 있는 작업을 할 수도 있으므로 압력방폭용기 내부의 기기 내측으로부터 새어나올 수 있는 인화성 물질이 기기 내측에 축적되지 않도록 주의 하여야 한다. ¦ 기 내부로 인화성 물질이 유입되지 않도록 해야 한다. 가압 실패 시 압력방폭기기의 전원이 자동으로 꺼지도록 되어 있는 경우에는 안전을 위한 경보장 치가 추가로 필요하지 않을 수 있으며, 이는 기기보호등급 "Gb"가 요구되는 장소의 경우에도 동일 하다. 기기보호등급 "Gc"가 요구되는 장소에서처럼 압력방폭기기의 전원이 자동으로 꺼지지 않는 경우에는 작업자가 즉시 압력을 복구하거나 기기의 전원을 차단하는 조치가 뒤따른다면 최소한의 조치로서 경보장치를 사용할 것을 권장한다. 압력방폭용기 내의 기기가 용기가 설치된 외부 장소에서 요구하는 기기보호등급에 적합한 경우, 가압 실패 시에도 해당 기기의 전원을 차단할 필요가 없다. 그러나 점화성 스파크를 발생시킬 수 있는 작업을 할 수도 있으므로 압력방폭용기 내부의 기기 내측으로부터 새어나올 수 있는 인화성 물질이 기기 내측에 축적되지 않도록 주의 하여야 한다. ¦ ¦ ¦ ¦ ¦ a 전원의 자동차단이 오히려 더 위험한 상황을 초래할 수 있는 경우, 이중 보호가스 공급과 같은 다른 예방조치를 취해야 한다. b 경보가 발생할 경우, 시스템의 압력방폭구조 복구와 같은 즉각적인 조치가 취해져야 한다. ¦ a 전원의 자동차단이 오히려 더 위험한 상황을 초래할 수 있는 경우, 이중 보호가스 공급과 같은 다른 예방조치를 취해야 한다. b 경보가 발생할 경우, 시스템의 압력방폭구조 복구와 같은 즉각적인 조치가 취해져야 한다. ¦ 17.2.3.2.2 자동 전원차단 양압 또는 보호가스 유량이 미리 설정한 기준값 이하로 감소하는 경우, 기기에 대한 전기공급을 차 단하는 자동 전원차단 장치가 제공되어야 한다. 추가적으로, 시각 또는 청각 경보 장치가 필요할 수 있다. 자동 전원차단 시 기기의 안전에 문제를 초래할 수 있고 만약 다른 방법으로 안전이 보장되는 경우에는 정해진 시간이 경과 한 후에 전원이 차단되는 장치와 함께 압력이 복구되거나 다른 적절한 조치가 취해질 때까지 지속적으로 작동하는 시각 또는 청각 경보 장치를 제공해야 한다. 자동으로 전원을 차단할 경우 더 위험한 상황을 초래한다면 이중 보호가스 공급 장치 등과 같은 다 른 예방 조치를 취해야 한다. 압력방폭용기 내의 기기가 용기가 설치된 외부 장소에서 요구하는 기기보호등급에 적합한 경우, 가 압 실패 시에도 해당 기기의 전원을 차단할 필요가 없다. 그러나 점화성 스파크를 발생시킬 수 있는 작업을 할 수도 있으므로 압력방폭용기 내부의 기기 내측으로부터 새어나올 수 있는 인화성 물질이 기기 내측에 축적되지 않도록 주의 하여야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 75 | {}
4916c6d2-2964-47e8-8a03-b7ef99b0c950 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 17.2.3.2.3 경보 양압 또는 보호가스 유량이 최소 기준값 이하로 떨어지면 운전자가 즉시 볼 수 있는 신호를 통해 그 사실을 경고해야 한다. 가능한 한 빠른 시간 내에 가압 시스템을 복구시키거나 수동으로 전원을 차 단해야 한다. 17.2.3.3 내부 누출원이 있는 기기 내부에 누출원이 있는 기기는 제조자가 제공한 사용설명서에 따라 설치해야 한다. 특히 안전을 위해 유량 제한장치(sample flow limiters), 압력조절기 또는 화염방지기와 같은 컨테인먼 트 시스템(containment system) 안전장치가 필요함에도 이런 장치가 제공되지 않은 경우, 사용자가 이를 설치해야 한다. 압력방폭용기에 공정 유체 또는 가스의 내부 유입을 허용하는 내부 컨테인먼트 시스템이 설치되어 있는 경우에는 공정 시스템으로 보호가스가 유입될 가능성과 그로 인한 영향을 고려해야 한다. 예를 들어 컨테인먼트 시스템 내의 저압 공정 가스가 가압 가스보다 압력이 낮은 경우, 컨테인먼트 시스 템 내의 누출 경로를 통해 가스가 공정 시스템으로 유입되어 공정 시스템에 악영향을 미치거나 위험 을 초래할 수 있다. 보호가스 공급 불량 시 경보가 작동되어야 하며 시스템의 안전성을 유지하기 위한 조치가 취해져야 한다. 사용자는 최소한 다음과 같은 사항을 고려하여 압력 또는 유량에 문제가 발생할 때 취해야 하는 조 치를 결정해야 한다. a) 제조자의 권고 b) 컨테인먼트 시스템에서 발생하는 누출의 특성(예: "없음", "제한적" 또는 "무제한" 등) c) 내부 누출의 조성(예: 액체 또는 가스, 그 인화범위 등) d) 압력/유량 문제 발생 시 인화성 물질의 공급이 자동 차단되는지 여부 e) 용기 내부의 기기 특성. 예를 들어 점화성, 기기보호등급 "Gb" 또는 기기보호등급 "Gc"를 요구하 는 장소에 대한 적합성, 누출원과 의 근접성 등 f) 외부의 기기보호등급 요구사항. 예를 들어 "Gb" 또는 "Gc" g) 사용되는 보호가스의 종류, 예를 들어 공기 또는 불활성 가스. 후자의 경우, 용기의 압력이 상실되 었을 때 반드시 다시 퍼지하여 충분한 보호 수준을 유지할 수 있도록 필요한 불활성 가스 농도로 복구시켜야 한다(동시에 산소 농도를 필요한 수준까지 낮춰야 한다). h) 예고되지 않은 기기의 자동 전원차단으로 인해 발생할 수 있는 결과 가스의 인화상한(UEL)이 높거나(예: 80 % 이상), 산화에틸렌과 같이 공기가 없는 경우에도 발열 반응 을 일으킬 수 있는 가스일 경우, 불활성 가스로 용기를 보호하는 "누설보상(leakage compensation)" 기법을 사용할 수 없다. 인화하한(LEL)의 25 % 이하 또는 분해가 발생할 수 없는 수준 이하로 누출 농도를 낮출 수 있을 만큼 보호가스의 유량이 충분한 경우, 공기 또는 불활성 가스를 사용하는 "연속 76 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
4f78af00-b57b-4ef7-8626-7520846158bf | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 희석(continuous flow)" 기법을 사용하는 것이 바람직하다. 17.2.4 공통 안전장치가 사용되는 복수의 용기 하나의 보호가스 공급원을 복수의 용기에 사용할 경우, 결과 적인 보호조치가 전체 조합체의 가장 불 리한 조건을 고려한 경우라면 안전장치를 이들 용기에 공통적으로 사용할 수 있다. 공통 안전장치를 설치했을 때, 아래의 조건을 만족하는 경우에는 문 또는 커버의 열림으로 인해 모 든 압력방폭용기 내부의 전기기기 전원을 차단하거나 경보를 작동시킬 필요는 없다. 적절한 방폭구조로 보호되는 기기를 제외하고 문 또는 커버의 개방 전에 해당 특정 압력방폭용기 로의 전원 공급을 차단하는 경우 공통 안전장치가 그룹 내 모든 다른 압력방폭용기의 압력을 지속적으로 모니터링하는 경우 17.2.5 퍼징 제조자가 명시한 압력방폭용기의 최소 퍼지시간에 제조자가 명시한 덕트의 단위 체적당 최소 추가퍼 지시간과 체적을 곱한 시간만큼을 추가해야 한다. 기기보호등급 "Gc"를 요구하는 장소에서, 용기 및 관련 덕트 내부의 인화성 물질 농도가 인화하한 보 다 현저히 낮은 경우에는(예: LEL 의 25 % 이하) 퍼지를 생략할 수 있다. 또한 압력방폭용기 내부의 가스가 인화성이 있는지를 확인하기 위해 가스 감지기를 사용할 수 있다. 17.2.6 보호가스 퍼지, 가압 및 연속희석용으로 사용하는 보호가스는 비가연성이고 무독성이어야 한다. 보호가스에는 기기의 정상 작동 및 건전성 유지에 위험이나 악영향을 줄 수 있는 습기, 유분, 분진, 섬유소, 화학물 질, 가연성 물질 및 기타 오염물질 등이 함유되어 있지 않아야 한다. 보호가스로 주로 공기가 사용되 지만 특히 내부에 인화성 물질 누출원이 있을 때는 불활성 가스가 사용되기도 한다. 보호가스에는 부피를 기준으로 대기 중에 일반적으로 존재하는 비율 이상의 산소가 함유되어서는 안 된다. 공기를 보호가스로 사용하는 경우 공급원을 비폭발위험장소 내 오염 위험이 낮은 곳에 설치해야 한 다. 주변 구조물이 공기 흐름에 미치는 영향과 풍향 및 풍속의 변화가 미치는 영향을 고려해야 한다. 용기의 입구에서 보호가스의 온도가 40 °C 를 넘어서는 안 된다. 특별한 경우 높은 온도가 허용되거나 더 낮은 온도가 필요할 수 있으며, 이러한 경우 용기에 온도를 표시하여야 한다. 특히 대형 용기의 경우, 불활성 가스를 보호가스로 사용한다면 질식 위험 방지를 위한 조치가 필요 하다. 불활성 가스를 보호가스로 사용하는 용기에는 예를 들어 다음과 같은 위험 경고를 표시해야 한다. "경고 - 이 용기에는 불활성 가스가 들어 있어 질식 위험이 있음. 이 용기는 또한 공기에 노출되면 인화 한계에 달할 수 있는 가연성 물질이 들어 있음." 17.3 분진압력방폭구조 "pD" 17.3.1 보호가스 공급원 기기의 작동을 상시적으로 유지해야 할 필요가 있는 경우와 같은 특정 상황에서는 두 개의 보호 가 77 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
63e2e97f-aa0e-4560-8537-7a5d5899f0b9 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 스 공급원을 준비하여 하나가 고장 났을 때 대체 공급원을 통해 계속 보호가스가 공급되도록 하는 것이 바람직하다. 각 공급원은 요구되는 수준의 압력 또는 보호가스의 유량을 독립적으로 유지할 수 있어야 한다. 용기 내부의 기기 중 폭발성 분진 분위기에 적합하지 않은 기기가 있는 경우, 압력 상실 시 표 19 를 따라야 한다. 표 19 - 용기 보호 요구사항 ¦ EPL ¦ 용기 내 기기의 형식 ¦ 용기 내 기기의 형식 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ EPL ¦ 점화가능기기 ¦ 정상 작동 중 점화원이 없는 기기 ¦ ¦ Db ¦ 자동 전원차단 (17.3.2 적용) ¦ 경보 (17.3.3 적용) ¦ ¦ Dc ¦ 경보 (17.3.3 적용) ¦ 가압 불필요 ¦ 17.3.2 자동 전원차단 양압 또는 보호가스 유량이 지정된 최소 기준값 이하로 감소하는 경우 기기에 대한 전기공급을 차단 하고, 시각 또는 청각 경보를 발생시키는 자동 장치가 제공되어야 한다. 전원차단 시 기기의 안전에 문제를 초래할 수 있고, 만약 다른 방법으로 안전이 보장되는 경우에는 정해진 시간이 경과 한 후에 전원이 차단되는 장치와 함께 압력이 복구되거나 다른 적절한 조치가 취해질 때까지 지속적으로 작 동하는 시각 또는 청각 경보 장치를 제공해야 한다. 17.3.3 경보 양압 또는 보호가스 유량이 최소 기준값 이하로 떨어지면 운전자가 즉시 확인할 수 있는 신호를 통 해 그 사실을 경고해야 한다. 가능한 한 빠른 시간 내에 가압시스템을 복구시키거나 수동으로 전원 을 차단해야 한다. 17.3.4 공통 보호가스 공급원 하나의 보호가스 공급원을 복수의 용기에 사용할 경우, 결과 적인 보호조치가 전체 조합체의 가장 불 리한 조건을 고려한 경우라면 안전장치를 이들 용기에 공통적으로 사용할 수 있다. 공통 안전장치를 설치했을 때, 아래의 조건을 만족하는 경우에는 문 또는 커버의 열림으로 인해 모 든 압력방폭용기 내부의 전기기기 전원을 차단하거나 경보를 작동시킬 필요는 없다. 적절한 방폭구조로 보호되는 기기를 제외하고 문 또는 커버의 개방 전에 해당 특정 압력방폭용기 로의 전원 공급을 차단하는 경우 공통 안전장치가 그룹 내 모든 다른 압력방폭용기의 압력을 지속적으로 모니터링하는 경우 해당 기기에 대한 전원 공급을 재개하기 전에 적용 가능한 분진제거(청소) 절차를 거치는 경우 17.3.5 전원 공급 분진압력방폭구조의 용기에 대한 퍼지는 허용되지 않는다. 시운전 시 또는 셧다운 후 기기의 전원 공급장치를 켜기 전에 분진 폭발위험을 일으킬 수 있는 농도 이상의 분진이 용기 또는 그와 연결된 덕트에 침투하지 않았는지 검증해야 한다. 검증 시 다음과 같은 요소를 고려해야 한다. 78 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
411471a5-3fa7-451f-a9df-c367ecc85704 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 1) 상당한 수준의 안전여유를 둘 필요성 2) 위험을 발생시킬 수 있는 공기 중 폭발성 분진 농도 3) 해당되는 경우, 발열로 인해 연소될 가능성이 있는 분진층의 두께 도구를 사용하지 않고 열 수 있는 도어와 커버의 경우, 해당 도어와 커버가 열리면 다른 방법으로 보호되지 않는 모든 부품에 대한 전원 공급이 자동으로 차단되도록 해야 한다. 도어와 커버가 다시 닫히기 전에는 전원이 다시 공급되는 것을 방지하여야 한다. 17.4 폭발성 가스 분위기를 위한 룸(room) 17.4.1 양압실 "룸(room)"이라는 용어는 사람의 전신이 완전히 접근할 수 있는 하나 또는 복수의 공간 또는 건물을 의미한다. "px", "py", "pz", "pxb", "pyb", "pzc" 및 "pv" 방폭구조가 적용된다(IEC 60079-13 참조). "px" 및 "pxb" 방폭구조는 내부의 압력을 유지하고 내부에 누출원이 있을 경우, 희석을 통하여 양압 실 내의 기기보호등급 "Gb" 또는 "Db"를 비방폭기기를 사용할 수 있는 등급으로 완화시킨다. 따라서 가압에 필요한 안전장치를 제외한 방폭구조로 보호되지 않는 기기를 양압실 내부에 설치할 수 있다. 비고 "px" 및 "pxb" 방폭구조는 기기보호등급을 비방폭 수준으로 낮추므로 인터록, 경보 등을 적용 하는 데 있어서 보다 엄격한 조건이 요구된다. "py" 및 "pyb" 방폭구조는 내부의 압력을 유지하고 내부에 누출원이 있을 경우, 희석을 통하여 양압 실 내의 기기보호등급 "Gb"를 기기보호등급 "Gc"로 완화시킨다. 따라서 가압에 필요한 안전장치를 제 외한 기기보호등급 "Gc"를 양압실 내부에 설치할 수 있다. "pz" 및 "pzc" 방폭구조는 내부의 압력을 유지하고 내부에 누출원이 있을 경우, 희석을 통하여 양압실 내의 기기보호등급 "Gc" 또는 "Dc"를 비방폭기기를 사용할 수 있는 등급으로 완화시킨다. 따라서 가 압에 필요한 안전장치를 제외한 방폭구조로 보호되지 않는 기기를 양압실 내부에 설치할 수 있다. "pv" 방폭구조는 본질상 희석에 의한 보호이며, 비폭발위험장소에 위치한 양압실에 하나의 내부 누출 원만 존재할 경우, 양압실 내의 기기보호등급 "Gb" 또는 "Gc"를 비방폭기기를 사용할 수 있는 등급으 로 완화시킨다. 17.4.2 분석실 분석실의 전기설비 설치에 대한 요구사항은 IEC TR 60079-16 및 KS C IEC 61285 에서 제공된다. 18 비점화방폭구조 "n"형에 적용되는 추가 요구사항 18.1 일반사항 Ex "n"으로 완전하게 인증을 받은 기기만 설치할 수 있다. 부품으로 인증 받은 Ex "n" 용기 및 부품, 즉 "U" 표시가 되어 있는 부품은 부품 조립체(이하 기기)의 부분품으로만 폭발위험장소 내에서 사용할 수 있으며, 기기의 인증서상에 이 부품의 사용이 허용되 어야 한다. 기기의 인증서에는 "X" 표시를 포함할 수 있으며, 해당 기기의 라벨에는 온도등급을 포함 하여 전체 방폭 기호를 표시하여야 한다. 79 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
6d7a06b9-38d9-4c01-a6a5-a38334699d1e | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 비점화방폭구조 "n"은 다음과 같이 세 가지 세부 형식으로 분류된다. ¦ "nA" ¦ 스파크를 발생하지 않는 기기 ¦ ¦ --- ¦ --- ¦ ¦ "nC" ¦ 스파크를 발생하는 기기 내부의 접점이 통기제한용기 또는 에너지 제한 이외의 방법으로 적절 히 보호되는 기기 ¦ ¦ "nR" ¦ 통기제한용기 ¦ 비고 "nL"에 대해서는 16 절을 참고한다. 18.2 "nR" 기기 "nR" 기기는 모든 시험 포트에 쉽게 접근할 수 있도록 설치해야 한다. "nR" 기기는 설치 후 및 유지보수 시에 통기제한 특성을 시험할 수 있도록 시험 포트가 제공되어야 한다. 보다 자세한 내용은 KS C IEC 60079-15 에 제공된다. 비고 일부 등기구에 대한 시험 포트 면제는 KS C IEC 60079-15 에 제공된다. 기기와 함께 제공되는 설치 설명서에 따라 케이블글랜드와 케이블 또는 전선관 인입장치를 선정하여 사용하여야 한다. 직사광선 등과 같은 가열원 또는 냉각원이 용기에 미치는 영향을 고려해야 한다. 높은 내부 온도가 기기 전원이 차단시 냉각에 따라 용기 외부의 폭발성 분위기를 내부로 유입시킬 수 있는 경우에는 점화를 일으킬 수 있는 접점에 대한 보호 목적으로 통기제한 용기를 사용하는 것 은 바람직하지 않다. 기기 전원 차단 시 용기 주위에 인화성 가스 또는 증기가 존재할 가능성이 높 기 때문에 이런 유형의 전기기기의 경우에는 듀티 사이클(duty cycle)도 고려해야 한다. 18.3 단자 및 도체의 조합 용기 내 발산되는 열로 인하여 요구되는 기기 온도등급을 초과 하는 온도가 발생하지 않아야 한다. 다음과 같은 방법을 통해 이를 달성할 수 있다. a) 허용 단자 수, 도체 크기 및 최대 전류에 관한 제조자 사양 준수 b) 제조자가 지정한 파라미터를 사용하여 계산된 소비전력이 정격 최대 소비전력보다 작은지 확인 용기 내 도체의 길이는 용기 대각선 길이를 초과 하지 않아야 하는데, 이는 형식시험 및 계산이 이와 같은 가정에 근거하기 때문이다. 최대 허용전류가 흐르는 용기 내부의 도체 길이가 길어지면 온도등 급을 초과 하는 내부 온도를 발생시킬 수 있다. 6 개 이상의 도체를 묶는 경우에도 T6 을 초과 하는 고온 발생 및/또는 절연 손상을 초래할 수 있기 때 문에 이를 피해야 한다. 18.4 도체 단말처리 슬롯 형식과 같은 일부 단자는 둘 이상의 도체 인입을 허용할 수 있다. 하나의 단자에 둘 이상의 도 체를 연결한 경우, 각각의 도체가 충분히 클램핑되도록 주의 해야 한다. 80 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f5552d43-70a8-443f-8538-9c83a007b64e | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 제조자 기술문서에서 허용할 때에만 단면이 서로 다른 두 도체를 하나의 단자에 연결할 수 있는데, 이 경우에도 먼저 단일 압착형 페룰 또는 그 밖에 제조자가 지정한 방법으로 도체들을 고정시켜야 한다. 단자대에 인접한 도체 사이의 단락 위험을 피하기 위해 단자의 금속부까지 개별 도체의 절연을 유지 해야 한다. 단일 도체에 단일 나사식 새들 클램프를 사용하는 경우, 기기와 함께 제공된 기술문서에서 달리 허 용하지 않는 한 나사 주위의 도체 끝 부분이 "U" 자 형태가 되도록 해야 한다. 19 유입방폭구조 "o"의 추가 요구사항 19.1 일반사항 Ex"o"로 완전하게 인증을 받은 기기만 설치할 수 있다. 부품으로 인증 받은 Ex "⌀" 용기 및 부품, 즉 "U" 표시가 되어 있는 부품은 부품 조립체(이하 기기)의 부분품으로만 폭발위험장소 내에서 사용할 수 있으며, 기기의 인증서상에 이 부품의 사용이 허용되 어야 한다. 기기의 인증서에는 "X" 표시를 포함할 수 있으며, 해당 기기의 라벨에는 온도등급을 포함 하여 전체 방폭 기호를 표시하여야 한다. 유입방폭구조 기기는 제조자의 기술문서에 따라 설치해야 한다. 비고 이와 관련된 세부 사항은 KS C IEC 60079-6 에 기술하고 있다. 19.2 외부 연결 외부 연결(현장 배선)은 해당 장소의 기기보호등급 요구사항을 만족하는 방폭구조로 보호되어야 한다. 20 충전방폭구조 "q"의 추가 요구사항 Ex"q"로 완전하게 인증을 받은 기기만 설치할 수 있다. 부품으로 인증 받은 Ex "q" 용기 및 부품, 즉 "U" 표시가 되어 있는 부품은 부품 조립체(이하 기기) 의 부분품으로만 폭발위험장소 내에서 사용할 수 있으며, 기기의 인증서상에 이 부품의 사용이 허용 되어야 한다. 기기의 인증서에는 "X" 표시를 포함할 수 있으며, 해당 기기의 라벨에는 온도등급을 포 함하여 전체 방폭 기호를 표시하여야 한다. 충전방폭구조 기기는 제조자의 기술문서에 따라 설치해야 한다. 21 몰드방폭구조 "m"의 추가 요구사항 Ex "m"으로 완전하게 인증을 받은 기기만 설치할 수 있다. 부품으로 인증 받은 Ex "m" 용기 및 부품, 즉 "U" 표시가 되어 있는 부품은 부품 조립체(이하 기기) 의 부분품으로만 폭발위험장소 내에서 사용할 수 있으며, 기기의 인증서상에 이 부품의 사용이 허용 되어야 한다. 기기의 인증서에는 "X" 표시를 포함할 수 있으며, 해당 기기의 라벨에는 온도등급을 포 함하여 전체 방폭 기호를 표시하여야 한다. 81 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
0060f31d-b42b-4b41-a4b7-0901fe5c54dd | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 몰드방폭구조 기기는 제조자의 기술문서에 따라 설치해야 한다. 22 광학 방사 기기 "op"의 추가 요구사항 Ex"op"로 완전하게 인증을 받은 기기만 설치할 수 있다. 부품으로 인증 받은 Ex "op" 장치 및 부품, 즉 "U" 표시가 되어 있는 부품은 부품 조립체(이하 기기) 의 부분품으로만 폭발위험장소 내에서 사용할 수 있으며, 기기의 인증서상에 이 부품의 사용이 허용 되어야 한다. 기기의 인증서에는 "X" 표시를 포함할 수 있으며, 해당 기기의 라벨에는 온도등급을 포 함하여 전체 방폭 기호를 표시하여야 한다. 광학 방사 기기는 제조자의 기술문서 및 부속서 K 에 따라 설치해야 한다. 23 용기 "t"에 의한 분진방폭구조의 추가 요구사항 Ex "t"로 완전하게 인증을 받은 기기만 설치할 수 있다. 부품으로 인증 받은 Ex "t" 용기 및 부품, 즉 "U" 표시가 되어 있는 부품은 부품 조립체(이하 기기)의 부분품으로만 폭발위험장소 내에서 사용할 수 있으며, 기기의 인증서상에 이 부품의 사용이 허용되 어야 한다. 기기의 인증서에는 "X" 표시를 포함할 수 있으며, 해당 기기의 라벨에는 온도등급을 포함 하여 전체 방폭 기호를 표시하여야 한다. 용기 "t"에 의한 분진방폭구조 기기는 제조자의 기술문서 및 부속서 L 에 따라 설치해야 한다. 82 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
6180ad61-9970-423f-b1e7-a95a5a7365c6 | KSCIEC60079-14_KR | KS CIEC 60079-14:2013 부속서 A (규정) 책임자, 운용자/기술자, 설계자의 지식, 기술 및 적격성 A.1 범위 부속서 A 에는 이 표준에서 언급한 인원들의 지식, 기술 및 적격성에 대하여 기술한다. A.2 지식 및 기술 A.2.1 책임자 방폭기기의 설계, 선정 및 설치에 대한 책임을 지는 책임자는 적어도 다음의 지식 및 기술을 보유하 여야 한다. a) 관련 전기공학에 대한 일반적인 이해 b) 공학도면을 이해 및 평가할 수 있는 능력 c) 방폭원리 및 기술에 대한 실무적 이해 d) 방폭 관련 표준에 대한 실무지식 및 이해 e) 품질 보증에 대한 기본지식(예: 감사, 문서화, 측정의 소급성, 측정기기의 교정 등) 위와 같은 능력을 보유한 자의 역할은 방폭기기 선정 및 설치 의무를 지는 운용자/기술자를 관리하 는 데 국한되어야 하며, 최소한 아래 A.2.2 의 요구사항에 부합하는 실무 기술을 가진 경우가 아닌 한 실무에 직접 참여해서는 안 된다. A.2.2 운용자/기술자(선정 및 설치) 운용자/기술자는 업무를 수행하기 위해 다음의 지식 및 기술을 보유하여야 한다. a) 일반 방폭원리에 대한 이해 b) 방폭구조 및 표시에 관한 일반 원리에 대한 이해 c) 방폭성능에 영향을 미치는 측면에서의 방폭기기에 대한 이해 d) 인증서 및 이 표준의 관련 내용에 대한 이해 e) KS C IEC 60079-17 의 검사 및 유지보수에 대한 일반적인 이해 f) 이 표준에 명시된, 방폭기기를 선정 및 설치하는 데 적용되는 특정 기술에 관한 친숙도 g) 방폭에 관련된 작업허가 절차와 안전 격리(분리)의 중요성에 대한 이해 A.2.3 설계자(설계 및 선정) 설계자는 업무를 수행하기 위해 다음의 지식 및 기술을 보유하여야 한다. 83 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
576afb19-0273-47a9-9d86-22264b66c8d3 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 a) 일반 방폭원리에 대한 세부 지식 b) 방폭구조 및 표시의 일반 원리에 대한 세부 지식 c) 방폭성능에 영향을 미치는 측면에서의 방폭기기에 대한 세부 지식 d) 인증서 및 이 표준의 관련 내용에 대한 세부 지식 e) 방폭구조별 기기의 준비 및 설치에 관한 실무기술의 이해 f) 방폭과 관련된 작업허가 절차와 안전 격리(분리)의 중요성에 대한 세부 지식 g) 이 표준에 명시된, 방폭기기를 선정 및 설치하는 데 사용되는 특정 기술에 관한 세부 지식 h) KS C IEC 60079-17 의 검사 및 유지보수에 대한 일반적인 이해 A.3 적격성 A.3.1 일반사항 적격성은 해당 인원의 업무에 관련된 방폭구조별로 적용된다. 예를 들어, Ex "i" 기기의 선정 및 설치 에 관한 적격성을 보유한 인원이 Ex "d" 스위치기어 또는 Ex "e" 전동기에 대한 적격성을 보유하지 않을 수 있다. 이런 내용은 인원에 대한 문서화 시스템을 통해 명확하게 관리하여야 한다. A.3.2 책임자 책임자는 방폭구조별 및 기기별로 A.2.1 에서 요구하고 있는 지식 및 기술 요구사항에 대한 적격성을 보유하였음을 실증할 수 있어야 하고 또한 증거를 제공할 수 있어야 한다. A.3.3 운용자/기술자 운용자/기술자는 방폭구조별 및 기기별로 A.2.2 에서 요구하고 있는 지식 및 기술 요구사항에 대한 적 격성을 보유하였음을 실증할 수 있어야 하고 또한 증거를 제공할 수 있어야 한다. 운용자/기술자는 문서화된 증거를 통해 다음에 대한 적격성을 실증할 수 있어야 한다. a) 4.2 에 관련된 문서의 사용 b) 사용자에게 4.2 에 관련된 보고서(예를 들어, 검사 보고서)를 생성 c) 관련 방폭구조의 준비 및 설치를 위해 필요한 실무 기술 d) 4.2 에 관련된 설치 보고서의 사용 및 생성 A.3.4 설계자 설계자는 방폭구조별 및 기기별로 A.2.3 에서 요구하고 있는 지식 및 기술 요구사항에 대한 적격성을 보유하였음을 실증할 수 있어야 하고 또한 증거를 제공할 수 있어야 한다. 설계자는 문서화된 증거를 통해 다음에 대한 적격성을 실증할 수 있어야 한다. a) 4.2 에 관련된 문서의 생성 b) 사용자에게 4.2 에 관련된 설계자 인증서를 생성 84 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
7b9d28d2-f996-4aff-ba4e-b599a82eb347 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 c) 관련 방폭구조 및 시스템에 대한 상세 설계를 준비하고 취합하는 데 필요한 실무 기술 d) 4.2 에 관련된 설치 기록의 갱신 및 생성 A.4 평가 국가 규정, 표준 또는 사용자가 요구하는 주기로 책임자, 운용자/기술자, 설계자의 다음과 같은 적격 성을 검증해야 한다. a) 업무 범위 내에서 필요한 기술을 보유하고 있는지 여부 b) 업무 범위에 걸쳐 적격성을 가지고 활동할 수 있는지 여부 c) 적격성을 뒷받침하는 관련 지식과 이해를 가지고 있는지 여부 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 85 | {}
21f129cb-b0d0-41b9-8b3e-8256153a3e7f | KSCIEC60079-14_KR | KS CIEC 60079-14:2013 부속서 B (참고) 폭발성 가스 분위기에서의 안전작업절차 지침 안전작업절차는 규정된 조건을 만족할 경우 폭발위험장소 내에서 점화원을 사용할 수 있도록 승인하 기 위해서 사용된다. 안전작업 허가는 특정 시간 동안 특정 장소에서 인화성 농도를 발생시킬 수 있는 양의 가스나 증기 가 존재하지 않거나 존재하지 않을 것으로 평가되었을 때 발행한다. 허가는 연속 또는 주기적인 가 스 모니터링에 대한 요구사항, 누출이 발생하였을 때의 상세 조치를 규정할 수 있다. 안전작업 허가를 발행하기 위하여 고려할 사항은 다음과 같다. a) 허가의 시작일 및 시간 기술 b) 작업하는 장소의 지정 c) 허용된 작업(예: 디젤 발전기, 굴착)의 기술 d) 인화성 가스 또는 증기가 점화 가능한 농도로 존재하지 않음을 확인하기 위한 측정 및 측정의 기록 e) 인화성 가스 또는 증기가 지속적으로 존재하지 않음을 확인하기 위한 샘플링 요구사항 f) 인화성 가스 또는 액체의 누출원 관리 g) 비상상황을 대비한 긴급조치의 기술 h) 허가의 종료일 및 시간의 기술 비고 안전작업 허가의 효과 적인 적용을 위한 문서화, 훈련, 관리, 사용에 관련된 중요한 측면들은 이 표준의 범위를 벗어난다. 86 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b4df8bac-b486-48a5-8549-e7365590e79f | KSCIEC60079-14_KR | KS CIEC 60079-14:2013 부속서 C (규정) 최초 검사 - 기기별 검사 계획 비고 최초 검사는 KS C IEC 60079-17 의 정밀 검사에서 도출되었다. 표 C.1, 표 C.2 및 표 C.3 은 기기별 검사 계획이다. 표 C.1 - Ex "d", Ex"e", Ex "n", Ex"t"의 검사 계획 ¦ 점검 사항 ¦ 점검 사항 ¦ Ex"d" ¦ Ex"e" ¦ Ex"n", Ex"t" ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 점검 사항 ¦ 점검 사항 ¦ 검사 등급: 상세 ¦ 검사 등급: 상세 ¦ 검사 등급: 상세 ¦ ¦ A ¦ 일반사항(모든 기기) ¦ ¦ ¦ ¦ ¦ 1 ¦ 방폭기기는 해당 위치의 기기보호등급(EPL)/종별 장소 요 구사항에 적합한가? ¦ X ¦ X ¦ X ¦ ¦ 2 ¦ 기기 그룹이 맞는가? ¦ X ¦ X ¦ X ¦ ¦ 3 ¦ 기기 온도등급이 맞는가?(가스만 해당) ¦ X ¦ X ¦ n ¦ ¦ 4 ¦ 기기 최고표면온도가 맞는가? ¦ ¦ ¦ t ¦ ¦ 5 ¦ 방폭기기의 용기 보호등급(IP 등급)은 보호/그룹/도전성 수 준에 적합한가? ¦ X ¦ X ¦ X ¦ ¦ 6 ¦ 방폭기기 회로 식별이 올바른가? ¦ X ¦ X ¦ X ¦ ¦ 7 ¦ 방폭기기 회로 식별이 가능한가? ¦ X ¦ X ¦ X ¦ ¦ 8 ¦ 용기, 유리 부품 및 유리 대 금속 실링 개스킷 및/또는 컴 파운드가 만족스러운가? ¦ X ¦ X ¦ X ¦ ¦ 9 ¦ 손상이나 허가받지 않은 수정은 없는가? ¦ X ¦ X ¦ X ¦ ¦ 10 ¦ 허가받지 않은 수정의 증거는 없는가? ¦ ¦ ¦ ¦ ¦ 11 ¦ 볼트, 케이블 입입장치(직접 및 간접) 및 블랭킹 엘리먼트 는 적합한 형식이며 완전하고 견고하게 고정되었는가? ¦ ¦ ¦ ¦ ¦ 11 ¦ - 물리적 검사 ¦ X ¦ X ¦ X ¦ ¦ 12 ¦ 용기의 나사산 커버는 적합한 형식이며 풀림이 없고 견고 하게 고정되어 있는가? ¦ ¦ ¦ ¦ ¦ 12 ¦ - 물리적 검사 ¦ X ¦ ¦ ¦ ¦ 13 ¦ 접합면이 깨끗하고 손상되지 않았으며, 개스킷이 있다면 만족스럽고 올바르게 위치되었는가? ¦ X ¦ ¦ ¦ ¦ 14 ¦ 용기 개스킷의 상태는 만족스러운가? ¦ X ¦ X ¦ X ¦ ¦ 15 ¦ IP 등급에 따라 용기에 물이나 분진이 침입한 흔적이 없 는가? ¦ X ¦ X ¦ X ¦ ¦ 16 ¦ 평면 접합면의 틈새 치수는 다음 어느 하나와 같은가? - 제조자의 문서에 따른 범위 내에 있는가? - 설치 시점에서 관련 설계 표준에서 허용하는 최댓값 이내에 있는가? - 현장 문서에서 허용하는 최댓값 이내에 있는가? ¦ X ¦ ¦ ¦ ¦ 17 ¦ 전기 접속이 견고한가? ¦ ¦ X ¦ X ¦ ¦ 18 ¦ 사용되지 않는 단자는 조여져 있는가? ¦ ¦ X ¦ n ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 87 | {}
c7405b86-7ced-4082-a6f4-37cbe3ca21e1 | KSCIEC60079-14_KR | KS CIEC 60079-14:2013 표 C.1 - Ex "d", Ex "e" , Ex "n", Ex"t"의 검사 계획(계속) ¦ 점검 사항 ¦ 점검 사항 ¦ Ex"d" ¦ Ex"e" ¦ Ex "n", Ex"t" ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 점검 사항 ¦ 점검 사항 ¦ 검사 등급: 상세 ¦ 검사 등급: 상세 ¦ 검사 등급: 상세 ¦ ¦ 19 ¦ 내압차단 장치 및 용융밀봉 장치는 손상되지 않았는가? ¦ ¦ ¦ n ¦ ¦ 20 ¦ 몰드 부품은 손상되지 않았는가? ¦ ¦ X ¦ n ¦ ¦ 21 ¦ 내압방폭구조 부품이 손상되지 않았는가? ¦ ¦ X ¦ n ¦ ¦ 22 ¦ 통기제한 용기가 만족스러운가? ("nR" 형식만 해당) ¦ ¦ ¦ n ¦ ¦ 23 ¦ 시험 포트가 장착된 경우 작동하는가? ("nR" 형식만 해당) ¦ ¦ ¦ n ¦ ¦ 24 ¦ 통기 작동이 만족스러운가? ("nR" 형식만 해당) ¦ X ¦ X ¦ n ¦ ¦ 25 ¦ 통기 및 배수 장치가 만족스러운가? ¦ X ¦ X ¦ n ¦ ¦ ¦ 특정 기기(조명) ¦ ¦ ¦ ¦ ¦ 26 ¦ 형광등이 EOL 효과 를 나타내지 않는가? ¦ ¦ X ¦ X ¦ ¦ 27 ¦ HID 램프가 EOL 효과 를 나타내지 않는가? ¦ X ¦ X ¦ X ¦ ¦ 28 ¦ 램프 형식, 정격, 핀 구성 및 위치가 맞는가? ¦ X ¦ X ¦ X ¦ ¦ ¦ 특정 기기(전동기) ¦ ¦ ¦ ¦ ¦ 29 ¦ 전동기 팬은 용기 및/또는 커버와 충분한 틈새가 있으며, 냉각 시스템은 손상되지 않았으며, 전동기 기반은 패인 곳 이나 균열이 없는가? ¦ X ¦ X ¦ X ¦ ¦ 30 ¦ 환기를 위한 공기 흐름이 방해받지 않는가? ¦ X ¦ X ¦ X ¦ ¦ 31 ¦ 전동기 권선의 절연저항(IR)은 만족스러운가? ¦ X ¦ X ¦ X ¦ ¦ B ¦ 설치 - 일반사항 ¦ ¦ ¦ ¦ ¦ 1 ¦ 케이블 형식이 적절한가? ¦ X ¦ X ¦ X ¦ ¦ 2 ¦ 케이블에 명백한 손상이 없는가? ¦ X ¦ X ¦ X ¦ ¦ 3 ¦ 트렁킹, 덕트, 파이프 및/또는 전선관의 밀봉은 만족스러운가? ¦ X ¦ X ¦ X ¦ ¦ 4 ¦ 스톱핑 박스 및 케이블 박스가 올바르게 채워져 있는가? ¦ X ¦ ¦ ¦ ¦ 5 ¦ 전선관 시스템의 건전성 및 복합 시스템과 의 인터페이스 는 유지되고 있는가? ¦ X ¦ X ¦ X ¦ ¦ 6 ¦ 보조 접지 본딩을 포함하여 모든 접지 연결이 만족스러운 가? (예: 체결이 견고하고 도체가 충분한 단면적을 가지고 있음.) ¦ ¦ ¦ ¦ ¦ 6 ¦ - 물리적 검사 ¦ X ¦ X ¦ X ¦ ¦ 7 ¦ 고장 루프 임피던스(TN 시스템) 또는 접지 저항(IT 시스 템)이 만족스러운가? ¦ X ¦ X ¦ X ¦ ¦ 8 ¦ 자동 전기 보호장치가 올바르게 설정되었는가? (자동 재설 정 불가) ¦ X ¦ X ¦ X ¦ ¦ 9 ¦ 자동 전기 보호장치가 허용 범위 내에서 작동하는가? ¦ X ¦ X ¦ X ¦ ¦ 10 ¦ 특정사용조건(해당되는 경우)은 준수하고 있는가? ¦ X ¦ X ¦ X ¦ ¦ 11 ¦ 사용하지 않는 케이블은 올바르게 말단되었는가? ¦ X ¦ X ¦ X ¦ ¦ 12 ¦ 내압방폭구조의 평면 접합면에 인접한 장애물은 KS C IEC 60079-14 에 따르는가? ¦ X ¦ ¦ ¦ ¦ 13 ¦ 가변 전압/주파수 설치는 문서를 준수하는가? ¦ X ¦ X ¦ X ¦ ¦ ¦ 설치 - 가열 시스템 ¦ ¦ ¦ ¦ ¦ 14 ¦ 온도센서는 제조자의 문서에 따라 작동하는가? ¦ X ¦ X ¦ t ¦ ¦ 15 ¦ 안전 차단장치는 제조자의 문서에 따라 작동하는가? ¦ X ¦ X ¦ to ¦ ¦ 16 ¦ 안전 차단 설정이 봉인되었는가? ¦ X ¦ X ¦ ¦ 88 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
d1978655-ecbd-4d1d-a91b-5ad0ea0dc09a | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 표 C.1 - Ex "d" , Ex "e" , Ex "n", Ex "t"의 검사 계획(계속) ¦ 점검 사항 ¦ 점검 사항 ¦ Ex"d" ¦ Ex"e" ¦ Ex "n", Ex"t" ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 점검 사항 ¦ 점검 사항 ¦ 검사 등급: 상세 ¦ 검사 등급: 상세 ¦ 검사 등급: 상세 ¦ ¦ 17 ¦ 도구를 사용해야만 가열 시스템의 안전 차단 재설정이 가 능한가? ¦ X ¦ X ¦ ¦ ¦ 18 ¦ 자동 재설정은 불가능한가? ¦ X ¦ X ¦ ¦ ¦ 19 ¦ 고장 조건에서 안전 차단장치의 재설정이 방지되어 있는가? ¦ X ¦ X ¦ ¦ ¦ 20 ¦ 안전 차단장치는 제어 시스템과 독립적인가? ¦ X ¦ X ¦ ¦ ¦ 21 ¦ 필요한 경우 레벨 스위치가 설치되고 올바르게 설정되었 는가? ¦ X ¦ X ¦ ¦ ¦ 22 ¦ 필요한 경우 유량 스위치가 설치되고 올바르게 설정되었 는가? ¦ X ¦ X ¦ ¦ ¦ ¦ 설치 - 전동기 ¦ ¦ ¦ ¦ ¦ 23 ¦ 전동기 보호장치가 허용되는 tE 또는 tA 시간 내에 작동하 는가? ¦ ¦ X ¦ ¦ ¦ C ¦ 환경 ¦ ¦ ¦ ¦ ¦ 1 ¦ 기기는 부식, 환경, 진동 및 기타 가혹한 조건으로부터 적 절하게 보호되는가? ¦ X ¦ X ¦ X ¦ ¦ 2 ¦ 분진과 먼지의 과도한 축적은 없는가? ¦ X ¦ X ¦ X ¦ ¦ 3 ¦ 전기 절연은 깨끗하고 건조한가? ¦ ¦ X ¦ X ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 89 | {}
b40a8c8e-e6a6-4b71-9de7-17d37ab6d1fd | KSCIEC60079-14_KR | KS CIEC 60079-14:2013 표 C.2 - Ex "i"의 검사 계획 ¦ 점검사항 ¦ 점검사항 ¦ 검사 등급: 상세 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ A ¦ 기기 ¦ ¦ ¦ 1 ¦ 회로 및/또는 기기 문서는 기기보호등급(EPL)/종별 장소에 적합한가? ¦ X ¦ ¦ 2 ¦ 설치된 기기는 문서에 명시된 기기인가? ¦ X ¦ ¦ 3 ¦ 회로 및/또는 기기의 범주 및 그룹은 맞는가? ¦ X ¦ ¦ 4 ¦ 기기의 IP 등급은 현재 존재하는 그룹 III 물질에 적합한가? ¦ X ¦ ¦ 5 ¦ 기기의 온도등급은 맞는가? ¦ X ¦ ¦ 6 ¦ 기기의 주위온도 범위가 설치에 적합한가? ¦ X ¦ ¦ 7 ¦ 기기의 서비스온도 범위가 설치에 적합한가? ¦ X ¦ ¦ 8 ¦ 설치가 명확하게 표식되어 있는가? ¦ X ¦ ¦ 9 ¦ 용기, 유리 부품 및 유리 대 금속 실링 개스킷 및/또는 컴파운드가 만족스 러운가? ¦ X ¦ ¦ 10 ¦ 케이블글랜드와 블랭킹 엘리먼트는 적합한 형식이며 완전하고 견고하게 고 정되었는가? - 물리적 검사 ¦ X ¦ ¦ 11 ¦ 허가받지 않은 수정은 없는가? ¦ X ¦ ¦ 12 ¦ 허가받지 않은 수정의 증거는 없는가? ¦ X ¦ ¦ 13 ¦ 다이오드 안전 배리어, 갈바닉 아이솔레이터, 릴레이 및 기타 에너지 제한 기기는 승인된 형식으로 인증 요구사항에 따라 설치되고 필요한 경우 안전 하게 접지되는가? ¦ X ¦ ¦ 14 ¦ 용기 개스킷의 상태는 만족스러운가? ¦ X ¦ ¦ 15 ¦ 전기 접속은 견고한가? ¦ X ¦ ¦ 16 ¦ 인쇄회로기관은 깨끗하고 손상되지 않았는가? ¦ X ¦ ¦ 17 ¦ 관련기기의 최대 전압 Um 이 초과 되지 않았는가? ¦ X ¦ ¦ B ¦ 설치 ¦ ¦ ¦ 1 ¦ 케이블은 문서에 따라 설치되었는가? ¦ X ¦ ¦ 2 ¦ 케이블 스크린은 문서에 따라 접지되어 있는가? ¦ X ¦ ¦ 3 ¦ 케이블에 명백한 손상이 없는가? ¦ X ¦ ¦ 4 ¦ 트렁킹, 덕트, 파이프 및/또는 전선관의 밀봉은 만족스러운가? ¦ X ¦ ¦ 5 ¦ 포인트 투 포인트 연결(point-to-point connection)이 모두 맞는가? ¦ X ¦ ¦ 6 ¦ 갈바닉 절연되지 않은 회로에 대해서는 접지 연속성이 만족스러운가? (예: 체결이 견고하고 도체가 충분한 단면적을 가짐.) ¦ X ¦ ¦ 7 ¦ 접지 연결은 방폭구조의 건전성을 유지하는가? ¦ X ¦ ¦ 8 ¦ 본질안전회로의 접지가 만족스러운가? ¦ X ¦ ¦ 9 ¦ 절연저항이 만족스러운가? ¦ X ¦ ¦ 10 ¦ 공통 배전함 또는 계전기 큐비클(relay cubicle)에서 본질안전 및 비본질안 전회로 간의 분리가 유지되는가? ¦ X ¦ ¦ 11 ¦ 전원 공급 장치의 단락 회로 보호는 문서와 일치하는가? ¦ X ¦ ¦ 12 ¦ 특정사용조건(해당되는 경우)은 준수하고 있는가? ¦ X ¦ ¦ 13 ¦ 사용하지 않는 케이블은 올바르게 말단되었는가? ¦ X ¦ ¦ C ¦ 환경 ¦ ¦ ¦ 1 ¦ 기기는 부식, 환경, 진동 및 기타 가혹한 조건으로부터 적절하게 보호되는가? ¦ X ¦ ¦ 2 ¦ 분진 및 먼지의 과도한 외부 축적은 없는가? ¦ X ¦ 90 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
061a81db-8be8-4030-b156-562f37fafc27 | KSCIEC60079-14_KR | KS CIEC 60079-14:2013 표 C.3 - Ex"p", "pD"의 검사 계획 ¦ 점검사항 ¦ 점검사항 ¦ 검사 등급: 상세 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ A ¦ 기기 ¦ ¦ ¦ 1 ¦ 기기는 해당 위치의 기기보호등급(EPL)/종별 장소 요구사항에 적합한가? ¦ X ¦ ¦ 2 ¦ 기기 그룹이 맞는가? ¦ X ¦ ¦ 3 ¦ 기기 온도등급 또는 표면온도가 맞는가? ¦ X ¦ ¦ 4 ¦ 기기 회로 식별이 맞는가? ¦ X ¦ ¦ 5 ¦ 기기 회로 식별이 가능한가? ¦ X ¦ ¦ 6 ¦ 용기, 유리 및 유리 대 금속 실링 개스킷 및/또는 컴파운드가 만족스러운가? ¦ X ¦ ¦ 7 ¦ 허가받지 않은 수정이 없는가? ¦ X ¦ ¦ 8 ¦ 허가받지 않은 수정의 증거는 없는가? ¦ X ¦ ¦ 9 ¦ 램프 형식, 정격 및 위치가 맞는가? ¦ X ¦ ¦ B ¦ 설치 ¦ ¦ ¦ 1 ¦ 케이블 형식이 적절한가? ¦ X ¦ ¦ 2 ¦ 케이블에 명백한 손상이 없는가? ¦ X ¦ ¦ 3 ¦ 보조 접지 본딩을 포함한 접지 연결은 만족스러운가? 예를 들어 체결이 견 고하고 도체의 단면적은 충분한가? - 물리적 검사 ¦ X ¦ ¦ 4 ¦ 고장 루프 임피던스(TN 시스템) 또는 접지 저항(IT 시스템)이 만족스러운가? ¦ X ¦ ¦ 5 ¦ 자동 전기 보호장치는 허용 범위 내에서 작동하는가? ¦ X ¦ ¦ 6 ¦ 자동 전기 보호장치는 올바르게 설정되었는가? ¦ X ¦ ¦ 7 ¦ 보호가스의 유입구 온도가 지정된 최대 온도보다 낮은가? ¦ X ¦ ¦ 8 ¦ 덕트, 파이프 및 용기는 양호한 상태인가? ¦ X ¦ ¦ 9 ¦ 보호가스에는 오염 물질이 실질적으로 없는가? ¦ X ¦ ¦ 10 ¦ 보호가스 압력 및/또는 유량이 적당한가? ¦ X ¦ ¦ 11 ¦ 압력 및/또는 유량 표시기, 경보 및 인터록 장치가 올바르게 작동하는가? ¦ X ¦ ¦ 12 ¦ 폭발위험장소에서 보호가스를 배출하기 위한 덕트의 불꽃 및 입자 배리어 조건은 만족스러운가? ¦ X ¦ ¦ 13 ¦ 특정사용조건(해당되는 경우)을 준수하고 있는가? ¦ X ¦ ¦ c ¦ 환경 ¦ ¦ ¦ 1 ¦ 기기는 부식, 환경, 진동 및 기타 가혹한 조건으로부터 적절하게 보호되는가? ¦ X ¦ ¦ 2 ¦ 분진 및 먼지의 과도한 축적은 없는가? ¦ X ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 91 | {}
625d1e0d-8a03-4433-bbd3-04944506c066 | KSCIEC60079-14_KR | KS CIEC 60079-14:2013 부속서 D (참고) 매우 낮은 온도에서의 전기설비 D.1 일반사항 극한의 기후에서 사용하기 위한 기기를 선정할 때에는 매우 낮은 온도로 인하여 특별한 조치가 필요 하다. 비고 1 표준 주위온도 범위는 -20 °C ~ 40 °C 이다. 표준 주위온도 범위를 벗어난 곳에서 사용하는 기 기는 그에 따라 설계, 시험, 인증 및 표시된다. 비고 2 이 부속서의 목적은 주위온도가 낮은 곳에서 사용되는 기기의 적절한 설계, 선정 및 설치에 대한 지침을 제공하는 것이다. D.2 케이블 고정 설치용 케이블을 선택할 때에는 매우 낮은 온도에서 절연 재료의 특성에 주의 하여야 한다. 이 러한 낮은 온도에서는 케이블의 서비스온도 및 최소 굽힘 반지름에 대해 특별한 예방 조치를 취해야 한다. 케이블의 설치는 적절한 주위온도 범위에서 수행해야 한다. D.3 전기 트레이스 히팅 시스템 낮은 온도에서는 전기저항식 트레이스 히터의 돌입전류(inrush current), 서비스온도, 최소 굽힘 반지 름 및 절연 특성에 대해 특별한 예방 조치를 취해야 한다. D.4 조명 시스템 D.4.1 일반사항 등기구를 선택하는 경우 모든 유형의 램프가 이러한 온도에서 작동하지 않는다는 사실을 고려해야 한다. D.4.2 비상 조명 비상 조명을 선택할 때에는 이러한 온도에서 일부 배터리(예: NiCd 배터리)를 충전할 수 없다는 점을 고려해야 한다. D.5 회전 전기기기 회전 전기기기를 선정할 때는 이러한 저온에 적합한 유형을 고려해야 한다. 92 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
5e4caf65-6888-4552-bbf0-129047bb7912 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 부속서 E (참고) 케이블의 통기제한 시험 E.1 시험절차 5 L (± 0.2 L)의 밀폐된 용기에 설치하여 길이 0.5 m 의 케이블을 일정한 온도 조건에서 시험해야 한다. 최소 0.3 kPa(30 mm 수주압력계)의 내부 양압이 0.15 kPa(15 mm 수주압력계)까지 떨어지는 데 필요 한 시간이 5 초 이상이면 케이블은 허용 가능한 것으로 간주한다. 용기의 틈새를 통해 압력 손실이 발생할 수도 있으므로 용기는 완전하게 조여야 한다. 93 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
d4a27dc7-31be-4683-aab1-39d2c49e4bec | KSCIEC60079-14_KR | KS CIEC 60079-14:2013 부속서 F (참고) 전기 트레이스 히팅 시스템의 설치 F.1 일반사항 각 전기 트레이스 히팅 시스템들은 특별한 공정 및 플랜트의 요구사항을 만족하기 위하여 고안되었 다. 각 시스템들이 현장에서 조립되는 상당한 구성품으로 구성되어 있기 때문에 트레이스 히팅 시스 템이 설치될 때 유효성을 근거로 한 플랜트 파라미터를 보증하는 것이 필요하다. 적절한 시험 및 유 지보수는 만족스러운 성능과 안전을 보증하기 위하여 필수적이다. F.2 정의 F.2.1 전기 트레이스 히팅 시스템 전기 트레이스 히팅 시스템은 일반적으로 기기 외부에 적용되며 주로 배관, 탱크 및 고용용기의 내 용물 온도를 유지하는 기능을 한다. 폭발위험장소에서 트레이스 히팅 시스템의 전기 부품은 인증을 받아야 하며 점화원이 될 수 있는 고온이 발생하지 않도록 전체 시스템을 설계, 설치 및 검사한다. 시스템은 또한 KS C IEC 60079-30-1 및 시스템 문서(명판, 태그, 작동 설명서, 설계 문서, 인증서, 기 타 등)에 따른 적절한 표시를 포함하고 있어야 한다. F.2.2 시스템 구성품 시스템 구성품은 전기 트레이스 히팅 시스템의 사용에 대한 의도된 안전에 요구되는 모든 구성품으 로 구성된다. 완전한 전기 트레이스 히팅 시스템은 전형적으로 다음과 같은 것들로 구성되어 있다. 전기 저항 트레이스 히터 유닛(가열 케이블, 패드) 단자 박스, 커넥터 및 전선 접속기구(splice kit)와 같은 설치 부속품 온도 조절장치 및/또는 제한장치 단열재 및 내환경재(피복재) 전기 구성품은 독립된 인증서가 있거나 가열 시스템의 인증에 포함되어야 한다. F.2.3 현장조립 트레이스 히터 현장 조립 트레이스 히터는 현장에서 작업할 수 있도록 인증되었다면 허용 가능하다. 이러한 경우는 다음과 같다. 제조자가 제공한 설치 설명서에서 현장조립을 허용한다. 설치 인원은 요구되는 기술분야에서 적격성을 보유하고 있다. 트레이스 히터는 KS C IEC 60079-30-1:2007 과 부속서 D 에 의한 현장(현장 작업) 시험을 통과 해야 한다. 94 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
2a3d85b5-6c75-4e18-95b1-47cff36c0eaa | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 트레이스 히터는 KS C IEC 60079-0 및 KS C IEC 60079-30-1 에 의한 표시를 해야 한다. F.2.4 센서의 위치 센서의 수 및 위치는 공정설계 기준의 요구사항들에 따라 결정된다. 센서의 부정확한 적용 및/또는 설치는 전체적인 트레이스 히팅 시스템 작업에 직접적인 영향을 미친다. 만약 제공된 회로 정보가 명확하지 않고 또한 설치에 적합하지 않다면 명확한 정보를 얻기 위해서 회로정보 제공자와 연락하 여야 한다. F.2.5 단열재 단열재 설치는 전기 트레이스 히팅 시스템 작업에 중요한 요소로 작용한다. 단열 시스템의 올바르지 못한 적용 및/또는 설치는 전체적인 트레이스 히팅 시스템의 성능에 직접적인 영향을 미친다. 이는 온도 감지 센서 및 제어에 대한 영향을 포함한다. 단열재의 종류 및 두께와 단열 배리어의 형태 또는 커버는 규정된 설계 기술문서에 따라 확인해야 한다. F.2.6 인원 측면 트레이스 히팅 시스템의 설치, 검사에 관여하는 인원은 요구되는 모든 기술에 대하여 적합하게 교육 을 받아야 한다. 설치는 폭발성 분위기에서 전기 트레이스 히팅 시스템의 사용에 관한 추가적인 교 육을 받은 적합한 감독자의 감독하에 수행되어야 한다. 교육을 받은 인원만 접속부 설치 및 단말처 리와 같은 주요 업무를 수행하여야 한다. 설치자는 제조자가 제공하는 설치 설명서에서 기술하는 기술/자격 요구사항을 충분하게 갖춰야 한다. F.3 일반적인 요구사항 온도등급, 최고표면온도 등 전기 트레이스 히팅 시스템의 안전 관련 특성은 트레이시 히팅 시스템의 설계 및 설치에 부분적으로 의존한다. KS C IEC 60079-30-1 에서 트레이스 히팅 시스템에 관한 설계, 시험, 인증 관련 요구사항을 기술하고 있으며, 추가 권고사항들은 KS C IEC 60079-30-2 를 참고할 수 있다. 트레이스 히터의 온도등급 분류 또는 최고표면온도는 제조자에 의해서 특정된다. 만약 명판이 제공되면 제조자 문서에 따라 설치자에 의해 전기 트레이스 히팅 시스템에 부착되어야 한다. 전기 트레이스 히팅 시스템의 방폭 요구사항은 기기보호등급, 기기 그룹, 온도등급 또는 최고 표면온도에 의존한다. KS C IEC 60079-30-1 은 기기보호등급 "Ga" 또는 "Da"에서 전기 트레이스 히팅 시스템의 설치를 허용 하지 않는다. 사용되는 전기 트레이스 히팅 시스템의 유형 및 설치 조건에 따라서 온도는 변할 수 있으며 각각의 시스템은 개별적으로 다뤄져야 한다. 인증서에서 주어진 제한사항 및 요구사항은 고려되어야 하며 설치를 하는 동안 관련된 요구사항들은 이행되어야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 95 | {}
fcf3c006-43a9-4072-8fe7-f183d1612bce | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 F.4 기기보호등급 "Gb" , "Gc" , "Db" 및 "Dc"에 대한 요구사항 F.4.1 일반사항 KS C IEC 60079-30-1 에 따라 "안정화 설계(stabilized design)"와 "제어 설계(controlled design)"를 구별 할 필요가 있다. F.4.2 안정화 설계 F.4.2.1 일반사항 전기 트레이스 히팅 시스템은 합리적으로 예상 가능한 조건하에서 그 표면온도가 온도등급 또는 최 고표면온도가 200 °C 이하일 때에는 이보다 5 K 낮은 온도, 온도등급 또는 최고표면온도가 200 °C 를 초과 할 때는 이보다 10K 낮은 온도를 초과 하면 안 된다. 비고 여기서 제품의 분류 또는 시스템 접근방식이 적용된다. 따라서 인증은 온도등급과 최고표면온 도를 명시할 수 있다. 제조자는 히팅 시스템 부품과 함께 사용설명서, 설계 문서 및 명판을 제 공할 것이다. F.4.2.2 PTC 특성 온도가 증가함에 따라 출력이 낮아지는 트레이스 히터는 시험에 의해 온도등급을 지정할 수 있다. 많은 적용 분야에서 만약 트레이스 히터의 온도등급이 설치에서 지정하는 것보다 더 낮은 온도일 경 우 추가적인 온도 제어 조치는 불필요하다. 그럼에도 불구하고 공정온도의 보다 좁은 범위에서 시스 템을 작동시키기 위해서 제한장치 및 안정화 설계가 적용될 수 있다. F.4.2.3 지정된 조건 안정화 설계는 최악의 조건 조합에서 가열 대상물(workpiece) 및 트레이스 히터의 최고표면온도를 결 정한다는 원칙에 기초한다. 이것은 열 입력이 열 손실과 같을 때 발생하는 평형 조건에서의 계산이 다. 최악의 조건 조합은 다음을 포함한다. · 최고 주위온도, 달리 명시되지 않았다면 통상 40 °C 로 규정 · 바람 없음(평온한 대기). · 단열재의 열전도도는 보수적인 값 또는 최솟값을 사용 · 설계에 따른 온도 제어 또는 온도 제어장치의 고장을 모사할 수 있는 온도 제어가 없음. · 트레이스 히터는 지정된 작동 전압보다 10 % 높은 전압에서 작동함. · 트레이스 히터는 제조 공차의 상한에서 작동하거나 직렬 트레이스 히터의 최소 저항에서 작동하 는 것으로 가정함. F.4.3 제어 설계 제어 설계는 최고표면온도의 제한을 위해서 온도 제어장치를 필요로 한다. 온도 제어장치는 온도 조 정기와 는 독립적으로 작동한다. 온도 제한장치와 같은 보호장치는 필요시 시스템으로 입력되는 전원 을 차단하고, 관련 온도가 허용된 최고표면온도를 초과 하는 것을 방지한다. 센서에 고장이나 손상이 발생할 경우에는 결함이 발생한 기기를 교체하기 위해서 전원이 차단된다. 96 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
9ff61520-3a9e-465b-8388-6ad71c980fb8 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 비고 1 전기 트레이스 히팅 시스템의 온도등급이나 최고표면온도는 시스템 배치(가령, 모니터링 장 치의 정해진 설정값)나 올바른 설치가 되었는지 여부(가령, 고온부의 정의 및 온도센서의 올 바른 위치선정)와 독립적이다. 제조자는 설계, 설치 및 설치 작업자의 적격성에 대한 정확한 지침을 제공하여야 한다. 만약 온도 모니터링이 올바르게 적용되지 않은 경우에는 안전하다는 잘못된 추정을 초래할 수 있다. 온도 안전장치는 관련 안전율을 적용하여 해당 폭발위험지역의 온도등급에 해당하는 최고 온도보다 더 낮은 제한온도로 설정되어야 한다. 이 오프셋 값은 보통 상당하며 다음에 의존한다. 전기 저항 트레이스 히터의 기하학적 구조 또는 위치에 관련된 센서의 위치 - 시스템 내의 센서 위치 보호장치의 이력 현상(hysteresis) 또는 제어 대역(control band) 전기 저항 트레이스 히터, 센서, 가열 대상물 및 환경 사이의 열전달 비고 2 인증서상의 온도등급 또는 최고표면온도는 제한장치와 실제 최고표면온도의 오프셋 값을 예 측하는 제조자의 설계 계산값을 검증한 후 이를 근거로 한다. 이 경우 최고표면온도는 센서 의 올바른 설치, 센서의 적합한 장소, 센서의 적합한 위치 및 안전장치에 온도 오프셋을 포함 했는지 여부에 의존한다. F.5 설계 정보 F.5.1 설계 정보 도면 및 문서 운용가능한 전기 트레이스 히팅 시스템의 설계를 위해서는 최신 배관 정보와 전기 트레이스 히팅 시 스템과 관련된 품목이나 도면의 모든 변경 사항을 설계자에게 제공하여야 한다. 특정 설치에 적용할 수 있는 다음의 정보들이 트레이스 히팅 시스템의 설계에 사용된다. a) 열역학적 설계 파라미터 b) 시스템 흐름도 c) 기기 배치도(설계도, 단면도 등) d) 배관 도면(설계도, 등축도, 배관 리스트 등) e) 배관 사양 f) 단열 사양 g) 기기 상세 도면(펌프, 밸브, 여과 기 등) h) 전기 도면(단선도, 기능 배선도 등) i) 물질 목록 j) 전기기기 사양 k) 기기 설치 설명서 및 지침서 I) 기기 세부사항 m) 단열 계획 97 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
60451aeb-332c-4012-a0fe-261c59133596 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 n) 폭발위험장소 구분도 o) 관련 가스 또는 증기의 온도등급 또는 분진 관련 최고표면온도 p) 배관 온도를 상승시킬 수 있는 공정 과정(가령, 수증기 배출 또는 발열반응) F.5.2 등축도 또는 히터 배치 목록 및 부하 차트 각 히터 회로의 도면에는 물리적 위치, 배치, 히팅 장치의 관련 정보 및 배관 시스템이 표현되어야 한다. 도면 및/또는 설계 정보는 다음을 포함하여야 한다. a) 배관 시스템 명시 b) 배관 크기 및 재료 c) 배관 위치 또는 배관라인 번호 d) 히팅 장치 명시 또는 회로 번호 e) 전원 연결부 위치, 밀봉 말단, 적용될 경우 온도센서 f) 히팅 장치 번호 g) 다음과 같은 히팅 장치의 특성 1) 유지되는 온도 2) 최고 공정 온도 3) 최고 주위온도 4) 적용될 경우, 최고 노출 온도 5) 요구될 경우, 최고 피복 온도 6) 요구될 경우, 가열 파라미터 7) 배관 길이 8) 배관 길이당 전기 저항 트레이스 히터의 트레이스 비율 9) 밸브, 배관 지지대 및 기타 히트싱크(heat sink)에 적용되는 전기 저항 트레이스 히터의 추가 길이 10) 전기 저항 트레이스 히터의 길이 11) 작동 전압 12) 희망 유지 온도에서 전기 저항 트레이스 히터의 단위 길이당 출력 13) 희망 유지 온도에서 단위 배관 길이당 열손실 14) 총 출력 15) 회로 전류 h) 단열 유형, 공칭 크기, 두께 및 k 값(k-factor) i) 적용 가능할 경우, 각 장소마다 온도등급 또는 최고표면온도를 포함하는 폭발위험장소 구분 j) 물질 목록 k) 열전달 보조물 98 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
6cb12ff5-90d1-4142-84b7-6405778c98e1 | KSCIEC60079-14_KR | KS CIEC 60079-14:2013 I) 전원 배전반의 태그번호 또는 명시 m) 경보, 제어기기 명시 및 설정값(명시된 오프셋 포함) F.6 인수 검사 F.6.1 재료 인수 트레이스 히팅 시스템의 부품을 인수하면 재료의 형식 및 수량, 문서를 포함하는 일반적인 검사를 수행해야 한다. 모든 트레이스 히터는 제품 형식, 제품 및 포장 표시, 전력 정격, 전압 정격, 수량 및 특성을 검증하기 위해서 확인하여야 한다. 추가적으로 요구될 경우, 설치 지침서 및 인증서의 인수도 확인하여야 한다. 트레이스 히팅 시스템의 공급자는 트레이스 히터에 대한 상세 지침과 다양한 시스템 부품을 공급하 여야 한다. 시스템의 건전성을 유지하고 기기보호등급 및 온도등급 요구사항을 만족시키기 위해 이 러한 지침은 명백하게 준수되어야 한다. F.6.2 설치 전 시험 설치 전에 다음과 같은 시험을 수행하고 표 F.1 과 유사한 설치 전 체크리스트 및 기록에 따라 문서 화하여야 한다. a) 손상에 대한 육안 검사. 연속성 및 절연 검사는 최종 검사로 수행해야 한다. 절연저항은 F.6.4 에 따라 측정해야 한다. b) 설계 문서에 따라 올바른 기기가 제공되었는지 확인하기 위해서 각각의 온도 제어장치를 확인한 다. 추가적으로 설정값도 확인한다. c) 공급처가 제조하고 조립한 제어반과 문서에 대한 일반적인 검사를 실시하여 배선, 배치 및 기능은 적합한지 여부와 시험은 실시되었는지 여부를 확인한다. 또한 현장으로의 이동 중에 손상이 발생 하였는지 확인한다. F.6.3 육안 검사 트레이스 히터는 물리적 손상이 완벽하게 없어야 한다. 공장에서 미리 조립된 접속부는 설치 중에 일반적으로 예상되는 조건을 견딜 수 있도록 충분히 강인해야 한다. F.6.4 절연저항 시험 절연저항은 최소 500 V d.c. 시험전압에서 트레이스 히터 도체와 도전성 커버 사이에서 측정한다. 하 지만 이보다 더 높은 시험전압이 사용될 것을 추천한다. 무기질 절연 트레이스 히터는 1 000 V d.c 에 서 시험하되 이를 초과 하면 안 된다. 폴리머 절연 트레이스 히터는 2 500 V d.c.에서 시험한다. 측정 된 절연저항은 20 MO 보다 작으면 안 된다. F.6.5 부품 교체 부품 교체는 다음의 제한사항을 포함한다. a) 공급자의 설치 또는 유지보수 지침에서 목록으로 특정하는 부품은 교체하고자 하는 부품이 인증 의 일부가 아닐 경우, 유사한 부품으로 교체해서는 안 된다. 99 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
ca1f88c2-2810-468f-b54a-0f3b31d4cb66 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 b) 공급자의 설치 또는 유지보수 지침에서 기술하고 있는 다른 부품들은 적절한 정격의 부품과 교체 될 수 있다. c) 트레이스 히터에 전원을 공급하는 배선 시스템의 구성 부품은 결정권을 가진 책임자의 승인하에 적절한 정격의 부품과 교체될 수 있다. F.6.6 전원 공급 위치 전원 공급 위치는 트레이스 히터의 설치 이전에 결정되고 지정되어야 한다. 정션박스를 설치할 때에 는 트레이스 히터가 단열재로부터 드러나는 지점부터 정션박스로 들어가는 인입부까지 그 사이에서 손상이 발생하지 않도록 주의 하여야 한다. 표 F.1 - 설치 전 체크리스트 ¦ 점검 사항 ¦ 점검 사항 ¦ 비고 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ 가열 대상물은 완전히 설치되고 시험되었으 며, 임시 지지대는 제거되었는가? 가열 대상 물의 표면은 날카로운 모서리, 용접 스패터 및 거친 부위가 없는가? ¦ 트레이스 히터가 설치된 후에 가열 대상물에 용접이나 압력시험을 수행할 경우, 트레이스 히터의 장치에 손상을 초래할 수 있다. ¦ ¦ 2 ¦ 트레이스 히터가 부착될 표면은 통상의 강재 또는 비금속인가? ¦ 만약 표면이 광택처리된 스테인리스강이거나, 두께가 매우 얇거나 또는 비금속 재질이라면 특별한 예방조치가 필요할 수 있다. ¦ ¦ 3 ¦ 가열될 품목이 설계 시의 크기나 위치 등에 일치하는가? ¦ 때때로 맞는 가열 대상물이 가열되는지 확신 하기 어렵다. 적절한 식별 시스템이 도움이 될 수 있다. ¦ ¦ 4 ¦ 트레이스 히터의 부착 이전에 금속 포일의 설치가 지정되었는가? ¦ 이것은 열의 분포에 도움을 줄 수 있다. ¦ ¦ 5 ¦ 트레이스 히터의 설치 이후에 금속 포일의 설치가 지정되었는가? ¦ 이것은 단열재가 트레이스 히터를 둘러싸는 것을 막을 수 있고, 또는 열 분포에 도움을 줄 수 있다. ¦ ¦ 6 ¦ 정상조건 또는 비정상조건에서 제품(유체)의 흐름이 트레이스 히터가 견딜 수 있는 온도 이상으로 상승할 수 있는가? ¦ 통상 이것은 설계 단계에서 다루어진다. 하지 만 현장에서 관련 인원과 의 협의 를 통해 혹 시 부정확하거나 예전의 정보가 사용되었는 지 확인할 수 있다. ¦ ¦ 7 ¦ 트레이스 히팅 시스템의 가장 최신 문서(작업 도면, 설계, 지침 등)가 가용한가? ¦ 안전한 사용을 위해서는 신중한 계산이 필요 하므로 트레이스 히팅 시스템 문서의 검토 없이는 변경이 고려되어서는 안 된다. ¦ ¦ 8 ¦ 배관이나 표면이 팽창 또는 수축하여 트레이 스 히팅 시스템의 어떤 부품에라도 응력을 가할 수 있는가? ¦ 이러한 경우 손상을 피하기 위해서 예방조치 는 필수적이다. ¦ ¦ 9 ¦ 온도 조절기의 센서가 외부의 영향을 받는 가? ¦ 인접한 가열 회로들은 센서에 영향을 미칠 수 있다. ¦ ¦ 10 ¦ 트레이스 히터는 설계에 따라 나선 모양이거 나 지그재그 형태인가? ¦ 나선 모양 또는 지그재그 형태가 필요한지 결정하기 위해서 배관의 단위 길이당 설계부 하를 확인해야 한다. ¦ ¦ 11 ¦ 냉도선(cold lead)은 설치되었을 때 가열된 표 면과 의 접촉에 적합한가? ¦ 만약 냉도선이 단열재 아래 매립될 경우에 냉도선은 해당 온도를 견디어야 한다. ¦ ¦ 12 ¦ 배관이 배관랙으로부터 걸쳐 나와 있는가? ¦ 이 경우 매단 지점에서 단열재의 내환경 보 호를 위한 조치가 필요하다. ¦ 100 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
16fbaaae-4f6f-4bb9-9ab2-ac74de350275 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 표 F.1 - 설치 전 체크리스트 (계속) ¦ 점검 사항 ¦ 점검 사항 ¦ 비고 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 13 ¦ 배관은 완전한 지지 보충을 받고 있는가? ¦ 이후 단계에서 중간 지지부를 추가할 경우에 는 히팅 시스템에 손상을 초래할 수 있다. ¦ ¦ 14 ¦ 도면에 없는 샘플링 배관 또는 블리드 배관 이 현장에 있는가? ¦ 이것은 트레이스 히터의 설치를 막거나 장애 로 작용할 수 있다. 또한 트레이스 히팅 시스 템 문서의 검토가 필요할 수 있다. ¦ ¦ 15 ¦ 기기의 설계에 사용된 다른 파라미터(가령, 배관 지지부)가 설계문서에 기술되어 있는가? ¦ ¦ ¦ 16 ¦ 히터, 제어장치, 정션박스, 스위치, 케이블글 랜드 등이 폭발성 가스 분위기나 환경 조건 에 적합한가? 또한 이 부품들이 부식, 액체나 특정 매질의 침투로부터 보호받고 있는가? ¦ ¦ F.7 트레이스 히터의 설치 F.7.1 일반사항 설치 시에는 공급자의 최소 굽힘 반지름과 겹침 또는 교차설치 등과 같은 설치 제한사항에 주의 하여 야 한다. 트레이스 히팅 시스템의 설치 시에는 원래의 부품만 사용하여야 한다. 그렇지 않을 경우 시스템의 인증은 유효하지 않다. 표 F.2 에서 제공하는 설치 기록은 작성하여 보관하여야 한다. F.7.2 연결 및 단말 F.7.2.1 일반사항 모든 형식의 트레이스 히터는 적절하게 단말처리되어야 한다. 현장에서 완결되는 연결부와 단말부는 공급자의 지침에 따라 신중하게 작업하여야 한다. 공장에서 단말처리된 기기는 해당 단말처리가 완 전하고, 적절하게 인식표가 부착되어 있으며 KS C IEC 60079-0 및 KS C IEC 60079-30-1 에 따라 표시 되어 있는지 확인하여야 한다. 설치자는 인증서, 연결부와 단말부의 온도 정격, 작동 조건에 대한 적 합성을 검토하여야 한다. 현장 단말용의 직렬 저항 트레이스 히터는 설치될 길이가 설계 길이 및 부하에 일치하는지 설치 전 에 확인하여야 한다. 무기질 절연 트레이스 히터를 작업 현장에서 단말처리할 때에는 수분의 침입을 방지하기 위해서 절단된 끝단을 즉시 밀봉하여야 한다. 병렬 트레이스 히터의 경우, 총 회로 길이는 공급자가 권고하는 것보다 초과 하면 안 된다. F.7.2.2 접속 기구(connection kit) 트레이스 히터의 접속 기구는 공급자의 지침에 따라 견고하게 고정되어야 하고, 물리적 손상으로부 터 보호되어야 하며, 기타 사용성이나 적합성에 불리한 영향을 끼칠 수 있는 물 또는 오염물질로부 터 보호되어야 한다. 101 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
dca493db-d4d5-4292-a38d-3a8ce3706227 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 F.7.2.3 정션박스 트레이스 히터의 회로는 적절한 보호방식에 대해 인증을 받았으며 적합한 보호등급(IP 등급)을 가지 고 있는 박스 내에서 연결되어야 한다. 정션박스는 트레이스 히터 출구 측에 가능한 한 가깝게 위치 해야 하며 가열 대상물의 팽창을 수용할 수 있어야 한다. 어떤 때에라도 정션박스는 열린 채로 두어 서는 안 된다. F.7.2.4 냉도선(Cold leads) 적용될 경우 연결부는 방수가 되는지, 접지에 대한 연결은 유효한지를 확인하여야 한다. 냉도선이 사 용될 경우에는 물이나 다른 오염물질의 침입이 불가능하도록 항상 둘러싸고 있는 단열재로부터 노출 되어야 한다. 냉도선은 공급자의 지침이나 인증서상의 사용 조건을 엄격히 준수하여 현장에서 고정되거나 수정되 어야 한다. 냉도선이 금속 피복된 트레이스 히터와 솔더링 또는 브레이징으로 접속된 경우에는 접속 점 부근에서 트레이스 히터나 냉도선을 구부려서는 안 된다. F.7.2.5 트레이스 히터 인입부 및 글랜드 도체의 단말(F.7.3 참조)은 모든 다른 연결부 및 말단이 조립되고 해당 회로의 절연저항 시험(F.6.4 참조)이 수행된 이후에만 완료할 수 있다. F.7.2.6 접속, 선의 결속(splicing) 및 수정 트레이스 히터의 접속, 선의 결속 및 수정은 공급자의 지침을 엄격히 준수하여 현장에서 수행하여야 한다. 트레이스 히터에 대한 이런 종류의 작업은 인증을 무효화할 수도 있다. 이것은 트레이스 히터 의 출력밀도를 변경시키거나 피복 온도에 영향을 줄 수 있는 모든 종류의 수정작업에도 적용된다. 수정 관련 사항은 시스템 문서에 기록되어야 한다. F.7.2.7 말단부의 단말처리 트레이스 히터의 말단부에 대한 단말처리는 공급자의 지침에 따라 견고하게 고정되어야 하고, 물리 적 손상으로부터 보호되어야 하며, 기타 사용성이나 적합성에 불리한 영향을 끼칠 수 있는 물 또는 오염물질로부터 보호되어야 한다. F.7.3 도체의 단말처리 터미널은 단선 또는 연선 또는 포일 형식의 도체를 수용할 수 있는 적절한 크기와 정격을 가지고 있 어야 한다. 도체의 절연피복을 벗겨낼 때에는 도체에 손상이 가지 않도록 주의 하여야 한다. 크림프(crimp) 또는 압착 형태의 커넥터 및 페룰의 크기는 관련 도체에 적합해야 하고 승인된 형식이 어야 한다. 압착 도구는 해당 결합부품에 적합해야 하고 양호하게 관리되어야 한다. 설치되었지만 단말처리 되지 않은 트레이스 히터는 습기의 침입으로부터 보호하기 위해 밀폐하여야 하고, 단말처리가 완료될 때까지 손상으로부터 보호하여야 한다. 102 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
6680f1cc-b8e0-4bca-a7a0-8cf1f820f6a6 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 F.8 제어 및 모니터링 기기의 설치 F.8.1 기기 적합성 검증 선정된 제한장치, 조절기, 서모스태트, 센서 및 관련 장치는 서비스온도, IP 등급 및 보호방식의 측면 에서 전체 시스템의 요구사항을 만족하여야 한다. 트레이스 히팅 시스템의 인증은 특정 부품의 사용 을 지정할 수도 있다. 이런 경우에는 제조자가 지정한 부품만을 사용하여야 한다. F.8.2 센서 고려사항 F.8.2.1 일반적인 센서 설치 센서는 공급자의 지침에 따라 설치하고 위치시켜야 한다. 제어 센서는 외부 열의 방사, 태양광 방사, 공정 열원 또는 건물의 열원이 존재하는 장소에 위치해서는 안 된다. 센서는 트레이스 히터가 가열 하는 구간 내에서 온도를 측정해야 하고, 배관의 끝단이나 배관의 지지부로부터 떨어져 있어야 한다. 주위온도를 감지하는 제어장치는 해당 설치에서 노출이 가장 잘된 장소에 위치하여야 한다. 센서는 가열 대상물 또는 기기와 열접촉이 잘되도록 밀착시켜야 하고, 센서와 가열 표면 사이에 단 열재가 침입하지 못하도록 보호하여야 한다. 교정 오차가 발생할 수도 있으므로 모세관 튜브, 열전대 또는 RTD 인출선이 손상되지 않도록 주의 하여야 한다. 매질(물질)에 대한 직접적인 온도 감지가 필요한 경우에 해당 센서는 적절한 위치(가령, 폐기물 용기 내 예상 액위의 상부)에서 서모웰(thermowell)을 통해 설치하여야 한다. 전체 길이가 1 m 를 초과 하지 않는다면 여분의 모세관 튜브를 단열재 내측에 설치할 수 있다. 하지만 이러한 경우에는 모세관의 부피가 교정에 악영향을 미칠 수 있다. 모세관 튜브, 열전대 또는 RTD 인출선이 단열재로부터 드러나는 구간에서는 습기의 침투가 발생하 지 않도록 주의 하여야 한다. 많은 경우, 센서의 위치는 시스템의 설계 단계에서 정의 된다. 센서의 위치선정에 대한 고려사항은 F.8.2 에서 기술하고 있다. F.8.2.2 부터 F.8.3 까지는 특정 설치 방법에 대한 설치 고려사항을 기술하고 있다. F.8.2.2 온도 제어장치를 위한 센서의 설치 온도 제어장치를 위한 센서는 전체 회로를 대표하는 온도를 제공할 수 있는 위치에서 가열 대상물 또는 기기의 표면 상에 설치하여야 한다. 그림 F.1 에서와 같이 센서는 트레이스 히터의 온도나 히트 싱크, 태양광과 같은 다른 요소로부터 영향을 받지 않도록 설치하여야 한다. F.8.2.3 온도 제한장치를 위한 센서의 설치 온도 제한장치를 위한 센서는 전체 회로를 대표하는 온도를 제공할 수 있는 위치에서 가열 대상물 또는 기기의 표면상에 설치하여야 한다. 이를 통해 온도 제한장치가 트레이스 히터의 최고 피복 온 도에 정확하게 반응할 수 있어야 한다. 센서의 위치, 부착 방법 및 설정값에 특히 주의 하여야 한다. 센서의 설치방식은 주어진 출력에서 기기 온도와 히터 피복 온도 사이의 알려진 관계에 근거한다. 그림 F.1 은 전형적인 온도 제한장치의 설치를 보여준다. 제한장치는 히터 피복 온도가 최악의 조건(가령, 전압의 110 %에서 작동, 제조자의 출력범위 중 상한 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 103 | {}
247c2b0d-5d13-419b-b386-2876ad20de76 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 값, 히터가 가열 대상물 또는 기기로부터 분리, 높은 주위온도, 외부 대류 없음 등)에서 최고 제한온 도를 초과 하지 않도록 설정해야 한다. 트레이스 히터 회로가 전압 제어장치와 사용되도록 설계된 경우에는, F.8.2.3, F.8.2.4 및 F.8.2.5 의 방 법을 사용하여 센서를 설치하는 것이 필요할 수도 있다. 해당 방법을 통해 전압 제어장치의 고장으 로 인한 히터 피복 온도의 급격한 변화에 신속하게 반응할 수 있다. ![image](/image/placeholder) 그림 F.1 - 제어 센서와 온도제한용 센서의 전형적인 설치 F.8.2.4 트레이스 히터 피복 상에 센서가 있는 온도 제한장치 그림 F.2 에서는 온도센서가 트레이스 히터에 직접적으로 설치되어 있고, 트레이스 히터는 가열되고 있는 표면에 직접 접촉하고 있다. 트레이스 히터와 센서 간의 정확한 열적 결합(thermal coupling)을 확보하기 위해서는 센서를 금속 포일 테이프나 열전달 컴파운드를 사용하여 설치할 필요가 있다. 설치 지점은 최고 고온부를 대표할 수 있는 위치인지 검증하여야 한다. 시간의 경과 나 온도에의 노 출에도 풀리지 않고 미래의 유지보수 작업 시에도 풀리지 않는 방식을 사용하여 센서를 히터에 설치 하여야 한다. 이러한 센서 설치방식은 트레이스 히터의 최고 고온부를 측정하는 것은 아니다(최고 고온부는 기기 와 접촉하지 않는 지점에서 발생할 개연성이 크다). 따라서 이 방식은 최고 제한온도보다 낮은 제어 장치 설정에만 사용되어야 한다. 104 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
602f9884-5932-4d17-a0de-d153acef8615 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 ![image](/image/placeholder) 그림 F.2 - 트레이스 히터의 피복상에 설치되는 센서가 있는 제한장치 F.8.2.5 인공적인 고온부가 있는 온도 제한장치 그림 F.3 에서는, 센서가 트레이스 히터의 최고 고온부를 대표하도록 의도적으로 설치한 인공 고온부 를 측정하도록 위치하고 있다. F.8.2.4 의 방식이 시스템의 최악의 경우에서의 피복 온도를 제어하는 데 있어서 신뢰성 있게 사용될 수 없다면, 인공적인 고온부가 약간의 추가적인 안전여유를 제공할 수 있다. 이 경우에는 단열재가 트레이스 히터와 가열되는 표면 사이에 삽입된다. 그런 다음에 온도 제한장치를 위한 센서를 트레이 스 히터와 직접 접촉하도록 설치한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 105 | {}
bb137eeb-f5b5-42de-b7fd-4297b02c2c83 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 ![image](/image/placeholder) C D S H A B 온도 A>B> C 식별부호 ¦ H: 트레이스 히터 ¦ B: 측정 지점의 온도 ¦ ¦ --- ¦ --- ¦ ¦ S: 온도 센서 ¦ C: 미흡한 열적 결합 지점(고온부) ¦ ¦ A: 인공적인 고온부의 ¦ 온도 D: 트레이스 히터와 가열되는 표면 사이의 단열재 ¦ 그림 F.3 - 인공적인 고온부에 센서가 있는 제한장치 인공적인 고온부에서의 온도(온도 C)가 미흡한 열적 결합 지점에서의 온도보다 높도록 보장하기 위 해서 단열재는 센서보다 2 배 정도 길다. B 에서의 측정 온도는 C 보다는 높지만 센서에서의 불가피한 열손실 때문에 실제 고온부인 A 보다는 낮다. 이 차이는 센서와 트레이스 히터 간의 질량비와 단위 열용량(W/m)의 함수인데, 제한장치의 온도 설정에 고려되어야 한다. 이 방식의 장점은 오작동(가령, 제어장치의 고장, 전압 제어장치의 고장, 과전압 등)에 대한 매우 빠 른 응답시간을 제공한다는 것이다. 어떤 경우에는 복잡한 회로를 개별 온도 제한장치를 가진 복수의 회로로 나누는 것이 필요하다. F.8.3 제어장치의 운전, 교정 및 접근 온도 제어장치와 온도 제한장치의 설정은 시운전 중에 검토하여야 한다. 온도 제한장치에서 제공하 는 설정 가능성 여부에 따라서 제한장치는 임의 변경으로부터 봉인되어야 한다. 온도 제어장치와 센서 루프는 시운전 단계에서 교정되어야 한다. 제어장치는 요구되는 온도로 설정 되어야 하고, 필요할 경우 공장설정으로부터 재교정되어야 한다. 기능 검사도 수행해야 하는데, 이는 온도 설정을 조정하면서 해당 제어장치가 트레이스 히터에 전원을 공급하는지 살펴보면서 확인할 수 있다. 모든 측정된 자료는 문서화해야 한다. 106 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
7fe916a4-3f36-47d8-92ae-5c69d1f1449f | KSCIEC60079-14_KR | KS CIEC 60079-14:2013 F.9 단열 시스템의 설치 F.9.1 일반사항 단열재의 선택과 적용은 전기 트레이스 히팅 시스템의 설치에 있어서 매우 중요한 요소이다. 단열재 는 통상 히팅 시스템에서 발생하는 열손실을 보상하도록 설계된다. 결과 적으로 단열 문제는 전체 시 스템의 성능에 직접적인 영향을 미친다. 에너지 발산을 최소화함으로써 운영비용을 줄이고 시스템 특성을 향상시킬 수 있으며, 시스템의 가열용량을 증대시킬 수 있다. 단열재의 설치는 적용 가능한 국가 표준이나 지역 규제를 만족하여야 한다. F.9.2 예비 작업 트레이스 히터는 트레이스 히터가 설치된 이후부터 단열재를 설치하기 이전까지 기계적 손상이나 습 기의 침투로부터 보호되도록 조치를 취해야 한다. 단열재의 설치를 시작하기 이전에 현장에서 트레 이스 히터 설치자와 단열재 작업자 사이에 연락체계를 구축하여 트레이스 히터의 설치 및 시험 직후 바로 단열재가 설치될 수 있도록 하는 것이 바람직하다. 설치된 트레이스 히팅 시스템은 F.6.2 에 따 라 시험이 완료되어 있어야 한다. 다음과 같은 점검 및 절차를 확인해야 한다. a) 형식, 내부 지름, 두께가 트레이스 히터의 선정에서 사용된 값과 일치하는지 확인한다. 만일 단열 재의 두께가 사양과 다르다면 특정된 설계 온도가 달성될 수 없다. b) 단열재를 보관하고 취급하고 설치하는 동안에는 보호 코팅이나 자켓 내부로 습기가 침투할 위험 이 있으므로 임시 내환경 조치를 제공하여야 한다. F.10 배선의 설치와 분기회로의 배치 F.10.1 일반사항 각 트레이스 히터 회로의 분기회로 배선은 과전류 보호장치를 필요로 한다. 분배 배선의 크기와 형 식, 분기회로 보호장치의 정격은 트레이스 히터가 겪게 될 최저 온도에서의 히터 개시전류(start-up current)와 개시전류의 지속시간에 의존한다. F.10.2 표식/식별 KS C IEC 60079-30-1 의 요구사항은 각각의 정션박스에 다음을 포함하는 영구적인 표식 및 식별을 포 함한다. a) 회로 식별 b) 모니터링 및 경보용 기기 c) 트레이스 히터의 전원 연결 d) 회로 번호 및 각 온도 제어장치의 설정값 107 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
0e8278ff-3940-4617-a7ff-f49aa54ea337 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 F.11 최종 설치 검토 F.11.1 필요한 수정 트레이스 히팅 시스템은 최고 피복 온도를 확인하여야 한다. 만약 측정된 온도가 허용된 피복 온도 또는 설계 값에서 벗어나는 경우에는 수정조치를 취하고 필요시 다시 검증하여야 한다. F.11.2 현장에서의 회로 절연저항 시험 모든 트레이스 히터 회로는 설치 후에 F.6.2 에 따른 시험을 수행해야 하는데, 측정된 절연저항은 5 MO 보다 작아서는 안 된다. F.11.3 육안 검사 육안 검사는 다음을 확인하여야 한다. a) 내환경 조치(내환경 부재의 겹침 또는 고정 비딩)의 결과 로서 수분이 단열재 내부로 침투하면 안 된다. b) 내환경 부재의 유연 연결부(sliding conection or the like)는 열 팽창 움직임을 흡수할 만큼 충분히 유연해야 한다. c) 내환경 부재를 고정하는 조임나사는 트레이스 히터나 온도센서를 손상시키지 않도록 충분히 짧다. d) 트레이스 히터나 온도센서를 인입하기 위해 내환경 부재에 구멍을 가공할 경우에는 접촉이 불가 능하도록 크기를 선정하여야 한다. 특히 분기회로의 경우에는 구멍이 충분히 넓어야 한다. e) 내환경 부재의 연결부 및 단열재의 인입부는 탄성을 가진 비경화성 밀봉재로 밀봉하여야 한다. 해 당 밀봉재는 내화학성 및 내부식성을 가져야 하고 치수 측면에서 안정적이어야 한다. F.12 시운전 F.12.1 시운전 사전 점검 표 F.1 에 따라 시운전 사전 체크리스트를 작성하고 보관하여야 한다. F.12.2 기능 검사 및 최종 문서화 F.12.2.1 일반사항 단열재가 설치되고 전원 배전이 완료되면 트레이스 히팅 시스템에 대한 시운전이 수행되어야 한다. F.12.2.2 기능 검사 다음의 기능 검사를 수행하여야 한다. a) 모든 분기회로를 닫고 적절한 전류를 확인한다. 온도 제어장치를 위해서 임시 바이패스가 필요할 수도 있다. b) 모니터링 또는 경보 회로가 작동 가능한지 확인한다. 현장 접점에서 바이패스가 필요할 수 있다. c) 각 회로에 대해서 표 F.2 의 트레이스 히터 시운전 기록을 작성한다. 모든 시험 및 시운전 정보를 문서화한다. 108 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
160ef538-a0af-4b1e-a482-317f0d1ff21e | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 d) F.6.4 에 따라 시험을 수행하고 각각의 측정에 대한 절연저항값을 기록한다. e) 전원을 공급하고 5 분 후에 적용된 전압 및 결과 전류값을 기록한다. 필요할 경우 가열 대상물의 온도도 기록한다. f) 경보와 모니터링 부품이 의도한 대로 작동하는지 확인한다. g) 온도 제어장치의 설정값에서 교정이 수행되었는지 여부와 온도 제어장치가 이 설정값으로 설정되 어 있는지를 확인한다. F.12.2.3 최종 문서화 전기 트레이스 히터 회로에 대한 적절하고 균질한 문서화는 해당 기기의 경제적인 유지보수를 위한 사전조건으로 고려되어야 한다. 이것은 특히 회로에 문제가 발생하였을 때 빠른 문제해결을 위해 매 우 중요하다. 또한 전문가를 통해서 시스템을 변경하거나 확장할 때 더 간단하고 빠르면서 경제적으 로 처리할 수 있다. 폭발성 가스 분위기에서 사용하는 전기 트레이스 히팅 시스템을 고려해 볼 때 프로젝트 문서는 주로 각 시스템 문서 내에서 상세히 기술되고 있다. 트레이스 히팅 시스템의 각 히터 회로의 문서는 다음을 포함하여야 한다. a) 설계 및 시험 문서 1) 목차 제한 2) 트레이스 히터 회로, 전원의 접속 위치, 연결부, 도체 결속, 티(tee), 단말처리, 제어장치나 장치를 위한 온도센서 등이 포함된 배관도 3) 용기(vessel): 트레이스 히터 회로의 배치 4) 가열 대상물 및 단열 목록 5) 트레이스 히터의 각 회로 길이 6) 계산 및 치수 자료 7) 물질 목록 8) 트레이스 히터 설치 지침 9) 히터 케이블 설치 계획 10) 온도센서의 사양 및 설치 지침 11) 전기 트레이스 히팅 시스템의 설치 기록(표 F.2) 12) 온도 분포 측정 13) 설치 인증서 b) 회로도 또는 목록 1) 배선 및 회로도 또는 목록 2) 단자 연결도, 부품 목록이 있는 스위치기어 3) 설치 지침 c) 기타 사항 1) 각 개별 기기의 기술사양 및 사용설명서 109 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
7e231183-a90a-417f-af23-7da131e3911e | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 2) 설계 엔지니어와 협의 된 기능 다이어그램 3) 방폭기기에 대한 인증서 표 F.2 - 전기 트레이스 히팅 시스템 설치 기록 - 예시 ¦ 위치 ¦ 시스템 ¦ 프로젝트 번호 ¦ 참조 도면 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 라인 번호 ¦ 트레이스 히터 번호 ¦ 종별 장소 ¦ 온도등급 ¦ ¦ 패널 번호 ¦ 위치 ¦ 회로 번호 ¦ 회로 전류/전압 ¦ ¦ 트레이스 히터 제조자 ¦ 트레이스 히터 모델 ¦ 단위 길이/전압 정격 당 ¦ 트레이스 히터 출력 ¦ ¦ 인증 표시 확인 ¦ 인증 표시 확인 ¦ 인증 표시 확인 ¦ 인증 표시 확인 ¦ ¦ 절연저항계 제조자/모델 전압 설정 ¦ 절연저항계 제조자/모델 전압 설정 ¦ 절연저항계 제조자/모델 전압 설정 ¦ 정확도/측정 범위 ¦ ¦ 절연저항계 최종 교정일 ¦ 절연저항계 최종 교정일 ¦ 절연저항계 최종 교정일 ¦ 절연저항계 최종 교정일 ¦ ¦ 멀티미터 제조자/모델 ¦ 저항 설정 ¦ 저항 설정 ¦ 정확도/측정 범위 ¦ ¦ 트레이스 히터 시험 ¦ 시험값/비고 ¦ 날짜 ¦ 머리글자 ¦ ¦ 개방 또는 단락 회로에서만 사용되는 자기 제어식 트레이스 히터(self-regulating trace heater)의 연 속성 시험(continuity test) 최소 절연저항은 20 M�일 것(단, MI 트레이스 히터의 경우 5 M�). 최소 시험전압은 500 V d.c.임 (단, MI 트레이스 히터의 경우 1 000 V d.c., 폴리머 트레이스 히터의 경우 2 500 V d.c.를 권고). ¦ 개방 또는 단락 회로에서만 사용되는 자기 제어식 트레이스 히터(self-regulating trace heater)의 연 속성 시험(continuity test) 최소 절연저항은 20 M�일 것(단, MI 트레이스 히터의 경우 5 M�). 최소 시험전압은 500 V d.c.임 (단, MI 트레이스 히터의 경우 1 000 V d.c., 폴리머 트레이스 히터의 경우 2 500 V d.c.를 권고). ¦ 개방 또는 단락 회로에서만 사용되는 자기 제어식 트레이스 히터(self-regulating trace heater)의 연 속성 시험(continuity test) 최소 절연저항은 20 M�일 것(단, MI 트레이스 히터의 경우 5 M�). 최소 시험전압은 500 V d.c.임 (단, MI 트레이스 히터의 경우 1 000 V d.c., 폴리머 트레이스 히터의 경우 2 500 V d.c.를 권고). ¦ 개방 또는 단락 회로에서만 사용되는 자기 제어식 트레이스 히터(self-regulating trace heater)의 연 속성 시험(continuity test) 최소 절연저항은 20 M�일 것(단, MI 트레이스 히터의 경우 5 M�). 최소 시험전압은 500 V d.c.임 (단, MI 트레이스 히터의 경우 1 000 V d.c., 폴리머 트레이스 히터의 경우 2 500 V d.c.를 권고). ¦ ¦ 1 릴에 대한 자료의 인수 ¦ 1 릴에 대한 자료의 인수 ¦ 1 릴에 대한 자료의 인수 ¦ 1 릴에 대한 자료의 인수 ¦ ¦ 릴의 연속성 시험 ¦ 릴의 연속성 시험 ¦ ¦ ¦ ¦ 릴의 절연저항 시험 ¦ 릴의 절연저항 시험 ¦ ¦ ¦ ¦ 2 배관 완성 여부(트레이스 히터의 설치 개시 승인) ¦ 2 배관 완성 여부(트레이스 히터의 설치 개시 승인) ¦ 2 배관 완성 여부(트레이스 히터의 설치 개시 승인) ¦ 2 배관 완성 여부(트레이스 히터의 설치 개시 승인) ¦ ¦ 3 트레이스 히터의 설치 여부(단열재 설치 개시 승인) ¦ 3 트레이스 히터의 설치 여부(단열재 설치 개시 승인) ¦ 3 트레이스 히터의 설치 여부(단열재 설치 개시 승인) ¦ 3 트레이스 히터의 설치 여부(단열재 설치 개시 승인) ¦ ¦ 트레이스 히터는 배관, 용기 또는 기기에 올바르게 설치됨. ¦ 트레이스 히터는 배관, 용기 또는 기기에 올바르게 설치됨. ¦ ¦ ¦ ¦ 트레이스 히터는 밸브, 배관 지지부, 다른 히트싱크 에 올바르게 설치됨. ¦ 트레이스 히터는 밸브, 배관 지지부, 다른 히트싱크 에 올바르게 설치됨. ¦ ¦ ¦ ¦ 부품이 올바르게 설치되고 단말됨(전원, 티-말단 밀봉). ¦ 부품이 올바르게 설치되고 단말됨(전원, 티-말단 밀봉). ¦ ¦ ¦ ¦ 설치는 제조자의 지침과 회로 설계를 준수함. ¦ 설치는 제조자의 지침과 회로 설계를 준수함. ¦ ¦ ¦ ¦ 4 단열재 설치 완료 ¦ 4 단열재 설치 완료 ¦ 4 단열재 설치 완료 ¦ 4 단열재 설치 완료 ¦ ¦ 연속성 시험 ¦ 연속성 시험 ¦ ¦ ¦ ¦ 절연저항 시험 ¦ 절연저항 시험 ¦ ¦ ¦ ¦ 시스템 검사 ¦ 시스템 검사 ¦ 시스템 검사 ¦ 시스템 검사 ¦ ¦ 5 표시, 표식(tagging) 및 식별 완료 (KS CIEC60079-30-1, 6 절 참조) ¦ 5 표시, 표식(tagging) 및 식별 완료 (KS CIEC60079-30-1, 6 절 참조) ¦ ¦ ¦ ¦ 6 트레이스 히터가 효과 적으로 접지되었는지 여부 ¦ 6 트레이스 히터가 효과 적으로 접지되었는지 여부 ¦ ¦ ¦ ¦ 7 온도 제어장치는 적절하게 설치되었고 설정값은 검증되었는지 여부 ¦ 7 온도 제어장치는 적절하게 설치되었고 설정값은 검증되었는지 여부 ¦ ¦ ¦ ¦ 8 정션박스는 인증받았고 닫혀 있는지 여부 ¦ 8 정션박스는 인증받았고 닫혀 있는지 여부 ¦ ¦ ¦ ¦ 9 단열재의 내환경성(모든 침투로부터 밀봉되었는 지 여부) ¦ 9 단열재의 내환경성(모든 침투로부터 밀봉되었는 지 여부) ¦ ¦ ¦ ¦ 10 말단은 밀봉되었고 도선 결속부(splice)의 외부 절연 표면에 표시가 되어있는지 여부 ¦ 10 말단은 밀봉되었고 도선 결속부(splice)의 외부 절연 표면에 표시가 되어있는지 여부 ¦ ¦ ¦ ¦ 11 도면 및 문서화 여부 ¦ 11 도면 및 문서화 여부 ¦ ¦ ¦ ¦ 수행: ¦ 수행: ¦ 회사 ¦ 날짜 ¦ ¦ 관찰: ¦ 관찰: ¦ 회사 ¦ 날짜 ¦ ¦ 수령: ¦ 수령: ¦ 회사 ¦ 날짜 ¦ ¦ 승인: ¦ 승인: ¦ 회사 ¦ 날짜 ¦ 110 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b33a0f3a-4f6e-43c7-b594-76a25461cd44 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 부속서 G (규정) 고정자 권선의 잠재적 방전 위험성 평가 - 점화위험인자 표 G.1 - 발화위험점수 ¦ 특성 ¦ 값 ¦ 인자 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 정격 전압 ¦ > 11 kV ¦ 6 ¦ ¦ 정격 전압 ¦ > 6.6 kV 에서 11 kV ¦ 4 ¦ ¦ 정격 전압 ¦ > 3.3 kV 에서 6.6 kV ¦ 2 ¦ ¦ 정격 전압 ¦ > 1 kV 에서 3.3 kV ¦ 0 ¦ ¦ 사용 중 평균 기동 횟수 ¦ > 1 회/시간 ¦ 3 ¦ ¦ 사용 중 평균 기동 횟수 ¦ > 1 회/일 ¦ 2 ¦ ¦ 사용 중 평균 기동 횟수 ¦ > 1 회/주 ¦ 1 ¦ ¦ 사용 중 평균 기동 횟수 ¦ ≤ 1 회/주 ¦ 0 ¦ ¦ 권선의 해체, 청소, 검사 사이의 주기 ¦ > 10 년 ¦ 3 ¦ ¦ 권선의 해체, 청소, 검사 사이의 주기 ¦ > 5 년에서 10 년 ¦ 2 ¦ ¦ 권선의 해체, 청소, 검사 사이의 주기 ¦ > 2 년에서 5 년 ¦ 1 ¦ ¦ 권선의 해체, 청소, 검사 사이의 주기 ¦ < 2 년 ¦ 0 ¦ ¦ 보호등급(IP) ¦ < IP44 a ¦ 3 ¦ ¦ 보호등급(IP) ¦ IP44 및 IP54 ¦ 2 ¦ ¦ 보호등급(IP) ¦ IP55 ¦ 1 ¦ ¦ 보호등급(IP) ¦ > IP55 ¦ 0 ¦ ¦ 환경 조건 ¦ 매우 더럽고 습함. b ¦ 4 ¦ ¦ 환경 조건 ¦ 해변 실외 C ¦ 3 ¦ ¦ 환경 조건 ¦ 실외 ¦ 1 ¦ ¦ 환경 조건 ¦ 청결 및 건조한 실내 ¦ 0 ¦ a 청결한 환경에 한하며, 훈련된 인원에 의해 주기적으로 관리되어야 함. b 살수시스템(deluge system)이나 연안 장소에서 열린 갑판을 포함하는 "매우 더럽 고 습한" 장소 C 염분을 함유하는 분위기에 노출된 장소 111 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
0edd837f-7d51-40fb-8919-b7c1d57cc17e | KSCIEC60079-14_KR | KS CIEC 60079-14:2013 부속서 H (규정) 선형 전류/전압 특성을 갖는 하나 이상의 관련기기로 구성된 본질안전회로의 검증 H.1 일반사항 본질안전회로 시스템의 커패시턴스 및 인덕턴스 파라미터는 고장조건 및 시스템의 각 지점에서 U。 및 10 의 시스템 값을 사용하여 KS C IEC 60079-11 의 점화 곡선으로부터 결정해야 한다. KS C IEC 60079-11 에 따른 고장은 전기기기의 각 품목이 아닌 엔터티로서 전기 시스템에 적용되어야 한다. 위의 요구사항은 다음 계산 절차를 사용하여 만족시킬 수 있다. H.2 보호등급이 "ib"인 본질안전 모든 관련기기의 보호등급이 "ia"이더라도 보호등급은 "ib"로 간주된다. 비고 시험을 실시하지 않고 단지 계산에 의해 평가되었으므로 보호등급의 감소가 발생한다. a) 관련기기에 명시된 U。 및 % 값을 사용하여 시스템에서의 최고 전압 및 전류를 결정한다(부속서 I 참조). b) 최대 시스템 전류(�)에 안전계수 1.5 를 곱한 값이, 최대 시스템 전압(U。)에 대한 KS C IEC 60079-11 의 해당 기기 그룹의 저항성 회로 점화곡선에서 얻은 전류를 초과 하지 않는지를 확인한다. c) 최대 허용 인덕턴스(Lo)는 최고 시스템 전류(�)에 안전계수 1.5 를 곱한 값을 사용하여 KS C IEC 60079-11 의 해당 기기 그룹에 대한 유도성 회로의 점화곡선으로부터 구한다. d) 최대 허용 커패시턴스(Co)는 최고 시스템 전압(U。)에 안전계수 1.5 를 곱한 값을 사용하여 KS C I EC 60079-11 의 용량성 회로의 점화곡선으로부터 구한다. e) C。 및 L。의 최대 허용값이 16.2.4.3 의 요구사항을 만족하는지 확인한다. f) U。, 10 및 Po(Po = loUd4)가 16.2.4.3 의 요구사항을 만족하는지 확인한다. g) 사용된 점화곡선의 기기 그룹을 고려하여 16.2.4.3 에 따라 시스템의 기기 그룹을 결정한다. h) 16.2.4.3 에 따라(Po = I。U。/4) 시스템의 온도등급을 결정한다. H.3 보호등급이 "ic"인 본질안전 유사한 계산 방법이 "ic" 회로에 사용될 수 있다. 안전계수는 1 이어야 한다. 112 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b4d8aa72-07a2-4c96-8e43-af218daa2aff | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 부속서 I (참고) 선형 전류/전압 특성을 갖는 하나 이상의 관련기기가 있는 본질안전회로 에서의 최대 시스템 전압 및 전류의 결정 방법(부속서 H 에 요구에 따라) I.1 선형 전류/전압 특성을 갖는 본질안전회로 본질안전회로에서 둘 이상의 관련기기가 있는 경우(16.2.4.4 참조), 문서 또는 명판에서 취한 각 관련 기기의 U。 및 10 값을 사용하여 본질안전회로의 고장조건하에서 새로운 최대 시스템 전압 및 전류를 결정하는 데 다음의 실용적인 방법을 사용할 수 있다. 관련기기의 본질안전 단자에서의 연결방식에 따라 다음을 고려하여 정상 작동 및 고장조건에서 U。 및 10 값을 결정할 수 있다. 전압만의 합산 - 전류만의 합산 전류 및 전압 모두 합산 본질안전회로와 비본질안전회로 사이에 갈바닉 절연된 관련기기가 직렬로 연결된 경우에는(그림 I.1 참조) 회로의 극성과 관계없이 전압의 합산만 가능하다. 전원의 양극을 병렬로 연결한 경우에는 전류의 합산만 필요하다(그림 1.2 참조). 전원의 극이 서로 연결 가능한(그림 I.3 참조) 다른 모든 경우에서는 고려하는 고장에 따라 직렬 또 는 병렬 연결이 고려되어야 한다. 이러한 경우에는 전압의 합산 및 전류의 합산 모두를 각각 고려해 야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 113 | {}
e16def32-9574-4baa-bb3c-5579a304a1bc | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 ![image](/image/placeholder) 폭발위험장소 관련기기 1 종 장소 Io1 U01 Ex ib 보안 기기 Io2 Uo2 I 계통의 최대 신규 값 U。= � Uoi= U01 + Uo2 10 = max.(/oi) 그림 I.1 - 직렬 연결(전압 합산) ![image](/image/placeholder) 폭발위험장소 관련기기 1 종 장소 Io1 U01 보안 기기 Exib Io2 Uo2 최대 신규 값 U。 = max.(Uoi) 계통의 10 = � /oi= /01 + /o2 그림 1.2 - 병렬 연결(전류 합산) 114 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
0b81e131-e47e-47a3-bd26-b5d2f3cb68f6 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 ![image](/image/placeholder) 폭발위험장소 관련기기 1 종 장소 Io1 U01 Exib 보안 기기 Io2 Uo2 I 계통의 최대 신규 값 U。= � Uoi = U01 + Uo2 U。 = max.(Uoi) 또는 10 = max.(/oi) /⌀= � /oi = /01 + /o2 그림 I.3 - 직렬 및 병렬 연결(전압 및 전류 합산) 1.2 비선형 전류/전압 특성을 갖는 본질안전회로 둘 이상의 관련기기가 연결되어 있고, 이 중 하나 이상의 관련기기가 비선형 출력을 갖고 있다면 특 별한 주의 가 필요하다. 이러한 상황은 해당 분야의 전문가에 의해 고려되어야 한다. 추가 정보는 KS C IEC 60079-25 를 참조한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 115 | {}
d733e080-f32f-4231-a4d9-b36f3b1d32bb | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 부속서 J (참고) 케이블 파라미터의 결정 J.1 측정 케이블의 인덕턴스 및 정전용량은 주파수 1 kHz 土 0.1 kHz 에서 정확도 ±1 %인 기기를 사용하여 측정 하고, 케이블의 저항은 정확도 ±1%인 직류기기를 사용하여 측정한다. 최소 10m 이상의 케이블 샘플 로부터 측정한 결과 가 허용 가능하다. 측정은 주위온도 20 °C ~30 °C 에서 실시한다. 인덕턴스 측정용 기기는 유의 미한 값을 가진 저항에서 저 인덕턴스를 측정할 때 만족스럽게 작동할 수 있어야 한다. 현실적으로 가능할 경우, 케이블의 끝단에서 개방회로 또는 단락회로를 구성함으로써 심선의 가능한 조합들을 만들어낼 수 있다. 커패시턴스, 인덕턴스 및 L/R 비의 최대 측정값이 케이블 파라미터로 사 용되어야 한다. 많은 양의 심선이 있는 경우에는 인덕턴스 및 커패시턴스의 최댓값을 만들어내는 대 표적인 심선 조합의 샘플을 사용해서 측정해야 한다. 케이블의 최대 커패시턴스는 케이블 양 끝단을 개방회로로 두고 측정해야 하며, 최댓값을 나타내는 전선과 스크린의 조합에서 측정해야 한다. 가령 트윈패어 스크린 케이블(twin-pair screened cable)을 측정할 때에는 통상 하나의 심선은 스크린에 연결한 채로 다른 심선 사이에서 측정할 때 최댓값을 나타낸다. 이 값이 최댓값임을 확정하기 위해서는 심선과 스크린의 다른 조합도 측정해서 비교하여 야 한다. 최대 인덕턴스는 서로 공간적으로 가장 멀리 떨어져 있는 두 심선의 끝을 연결하여 측정하여야 한다. 이 경로의 직류 저항은 케이블의 L/R 비를 계산하는 데 사용되는 저항이다. 느슨한 구조의 케이블에서 최소 10 회 이상 구부리거나 감은 케이블의 파라미터는 2 % 이상 변화하 지 않는다. 이 측정의 목적상 각 도체들이 직렬로 연결될 수 있는 고장조건의 조합은 고려되지 않았는데, 이러 한 고장은 케이블의 길이를 증가시키는 효과 를 가져온다. 커패시턴스를 측정할 때에는 스크린이나 사용하지 않는 심선은 서로 묶고, 측정되는 회로의 한쪽 끝단에 연결되어야 한다. J.2 하나 이상의 본질안전회로를 포함하는 케이블 J.2.1 일반사항 특정 본질안전 또는 에너지 제한회로에 의해 사용되는 도체가 하나 이상의 본질안전회로를 포함하는 케이블 내에서 쉽게 식별될 수 있는 경우, 특정 도체와 관련된 케이블 파라미터만 고려해야 한다. J.2.2 A 형 케이블 회로에서 사용되는 모든 도체가 하나의 스크린 내에 있는 경우, 스크린 내의 도체 간 연결 또는 도 체와 스크린과 의 연결만 고려하여야 한다. 하나 이상의 스크린 내에 도체가 있는 경우에는 관련 스 116 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f5270470-bac0-4a9b-acad-0d62915db916 | KSCIEC60079-14_KR | KS CIEC 60079-14:2013 크린 내의 모든 관련 도체들을 사용하여 측정하여야 한다. J.2.3 B 형 케이블 특정 회로에 사용되는 도체가 확실하게 구별되는 경우, 측정은 해당 도체에서만 실시한다. 확실하게 구별할 수 없는 경우에는 특정 본질안전회로에 사용되는 도체의 모든 가능한 조합을 고려해야 한다. J.2.4 C 형 케이블 두 개의 단락 고장에 의해 서로 연결될 수 있는, 본질안전회로와 관련된 모든 도체와 모든 스크린에 대해서 측정하여야 한다. 관련된 도체를 확실하게 구별할 수 없는 경우에는, 세 개의 서로 연결된 회로에 관련된 도체 및 스 크린의 총 수량에 대해 가능한 조합까지 시험이 확대되어야 한다. J.3 FISCO 버스 케이블의 유효 커패시턴스는 두 도체 사이의 커패시턴스에 대한 미터당 커패시턴스 C'로부터 도출된다. 만약 케이블이 스크린을 포함하고 있다면 미터당 추가 커패시턴스가 고려되어야 한다. 커패시턴스의 계산은 버스 케이블과 스크린의 전기적 연결에 의존한다. 만약 버스 회로가 접지된 스 크린으로부터 격리되어 있거나 스크린이 전원 공급 유닛의 플러스 및 마이너스 사이에 대칭적으로 배치되어 있다면(그라운드에 대해 밸런스된 필드버스), 도체/도체 간 커패시턴스뿐만 아니라 도체/스 크린 및 스크린/도체로부터의 시리즈 커패시턴스도 고려되어야 한다. 다음이 얻어질 수 있다. C' = C'도체/도체 + 0.5C'도체/스크린 만약 스크린이 공급 유닛의 한 극과 연결되어 있다면 아래의 관계가 성립한다. C' = C'도체/도체 + C'도체/스크린 117 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
adfe872e-7ea4-4a5b-82c5-c19272881d36 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 부속서 K (규정) 광학 방사 기기 "op"의 추가 요구사항 K.1 일반사항 용기에 광 송신부가 장착된 경우 용기에서 방출되는 모든 광학 방사는 "op is"이어야 한다. K.2 본질안전 광학 방사 "op is" K.2.1 일반사항 본질안전 광학 방사는 정상 작동 또는 특정 고장조건에서 특정 폭발성 분위기를 점화시킬 수 있는 충분한 에너지를 공급할 수 없는 방사를 의미한다. 이 개념은 빔 강도를 점화에 필요한 강도보다 낮 도록 제한하는 것이다. 공기 중에서 광학적으로 조사된 입자가 점화를 일으키기 위해서는 입자에 의해서 흡수되는 얼마간의 에너지, 광파워 또는 조도가 필요하다. 본질안전 광학 방사의 개념은 제한되지 않은 방사 또는 광학 기기 내의 방사에 적용된다. K.2.2 단면적의 변화 설치 시 사용되는 광케이블의 단면적 감소는 허용되지 않는다. K.2.3 커플러(coupler) 광 커플러에서의 광케이블의 접속은 추가적인 에너지가 광섬유에 유입될 수 없는 방식이어야 한다. K.3 보호 광학 방사 "op pr" K.3.1 일반사항 이 개념은 광학 방사를 광섬유 또는 다른 전송 매체 내부에 가두고 전송 매체로부터 광학 방사의 방 출이 없다는 가정에 근거한다. 이 경우 전송 매체의 성능이 시스템의 안전 수준을 결정한다. 위험 분석은 가정된 조건(고장조건 또는 정상 작동)을 근거로 안전 요구사항을 제공한다. 광섬유는 외력으로부터 보호 배리어의 파손이 발생할 수 있다는 가정을 하지 않는 곳에서도 사용할 수 있다. 외력이 정상 작동 또는 비정상 작동 중에 보호 배리어를 파손할 수 있는 경우에는 추가 보 호 수단(예: 견고한 케이블, 전선관 또는 보호배관)을 사용해야 한다. 위험 분석은 파손이나 광학 방 사의 방출을 방지하기 위한 조치들을 기술한다. 비고 광섬유는 정상 작동 조건에서 대기로의 광학 방사의 방출을 방지한다. 예측 가능한 오작동에 대비하여 부가적인 외장, 전선관, 케이블 트레이 또는 보호배관을 제공할 수 있다. 118 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
9a3bef75-91f9-41b4-b72e-0912c9ed5ed7 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 K.3.2 용기 내부에서의 방사 내압방폭구조 "d", 압력방폭구조 "p" 또는 통기제한용기 "nR"와 같이 용기 내부에 점화원을 수용할 수 있는 방폭구조의 경우, 용기 내부에 점화성 방사가 허용된다. K.4 인터록된 광학 방사 "op sh" 이 보호 형태는 방사가 본질적으로 안전하지 않고 만약 광학 방사의 제한(confinement)이 실패할 경 우 전송차단을 위한 인터록을 사용할 경우 적용할 수 있다. 차단은 점화 지연 시간(ignition delay time) 보다 짧은 시간 내에 발생해야 한다. 위의 개념은 KS C IEC 60079-28 에 적합해야 한다. 119 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
81385eb7-b5bb-4b11-bcaa-3c3d3f5388b5 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 부속서 L (참고) 과도한 두께의 분진층의 예 과도하게 두꺼운 분진층의 예는 다음과 같다(그림 L.1 참조). ¦ 50 mm ¦ 그림 L.1a - 기기 상측의 과도한 층 ¦ ¦ --- ¦ --- ¦ ¦ T5mm < 250 °C > 5 mm ↑ ¦ 그림 L.1b - 분진의 낮은 발화온도에 기인한 기 기 상측의 과도한 층 ¦ ¦ ↕> 5mm ¦ 그림 L.1c 기기 측면의 과도한 층 ¦ ¦ > [ > b > s > s ¦ 그림 L.1d 완전히 잠긴 기기 실험실 분석에 의해 치수 b, s 및 t 가 제한되어야 함. ¦ 그림 L.1 - 과도한 두께의 분진층의 예 120 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
a65c9003-effb-4b6a-b54d-b670ac500394 | KSCIEC60079-14_KR | 부속서 M (참고) KS C IEC 60079-14:2013 하이브리드 혼합물 M.1 일반사항 하이브리드 혼합물은 인화성 가스 또는 증기와 가연성 분진 또는 부유물이 섞인 혼합물이다. 이러한 하이브리드 혼합물은 개개의 가스, 증기 또는 분진과 는 다른 행태를 보인다. 산업에서 발생할 수 있 는 상황의 수는 매우 다양할 수 있으므로 구체적인 지침을 제공하는 것은 현실적이지 않다. 그러나 이 부속서는 혼합물이 있을 때 고려해야 할 사항에 대한 지침을 제공한다. M.2 농도 한계 하이브리드 혼합물은 각각의 가스, 증기의 인화한계 또는 분진의 폭발농도 밖에서도 폭발성 분위기 를 조성할 수 있다. 추가적 자료가 제공되지 않는 한 하이브리드 혼합물은 가스, 증기의 농도가 폭발 하한(LEL)의 25 % 또는 분진의 농도가 MEC 의 25 %가 넘으면 폭발성 물질로 고려하는 것이 바람직 하다. M.3 에너지/온도 제한 하이브리드 혼합물이 존재하는 경우, 가스, 증기의 MIE 및 자연발화온도 또는 분진운의 최저발화온 도 같은 최저발화 매개변수는 혼합물 구성물질의 그 어떠한 매개변수보다 낮을 수 있다. 다른 추가 정보가 없는 경우, 매개변수는 혼합물 내의 파라미터 중 가장 낮은 것이어야 한다. M.4 기기 선정 최소한 해당 가스, 증기와 분진의 요구사항을 모두 만족시키는 기기를 선정해야 한다. 분진층은 통상 가스, 증기 그 자체만으로 평가된 온도보다 기기의 온도를 증가시키므로 기기의 온도등급을 평가할 때에는 주의 를 기울여야 한다. 온도 상승은 표면온도의 상승일 수도 있고, 내부 부품의 온도 상승일 수도 있다. 가스, 증기와 분진 양쪽에 대한 온도 정격을 가진 가스, 증기 온도등급은 해당 기기가 분 진층에 노출될 때 더는 유효하지 않다. M.5 내압방폭기기의 사용 하이브리드 혼합물 내에서 내압방폭기기를 사용할 때에는 화염전파가 외부의 폭발성 분진 분위기에 서는 검증되지 않았다는 사실을 인지해야 한다. 또한 화염접합면에 존재할 수 있는 분진에 의해 고 온입자가 외부로 방출될 수 있으므로 내압방폭의 보호원리가 훼손될 수 있다. M.6 정전기 위험 분진 조건이 정전기 위험을 초래할 수 있으므로 정전기에 관련된 경고가 표시된 기기에는 주의 를 기 울여야 한다. 121 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
d69bf4aa-839b-4829-a4b6-0be12d38e53a | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 M.7 설치 요구사항 케이블, 케이블글랜드, 전기적 보호 및 기타 설치 사항은 가스, 증기 및 분진 관련 양쪽의 요구사항 을 모두 만족해야 한다. 122 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
82529875-cd99-4ea9-b302-10ac8962024f | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 참고문헌 KS C IEC 60034-5, 회전기기 - 제 5 부: 회전기기 외함의 보호등급 분류(IP 코드) KS C IEC 60034-17, 회전 전기기기 - 제 17 부: 컨버터 구동 농형 유도 전동기 - 적용 지침 KS C IEC 60050(모든 부), 국제 전기기술 용어 (available at <http://www.electropedia.org>) KS C IEC 60079-2, 폭발성 분위기 - 제 2 부: 압력방폭용기 "p"에 의한 기기 보호 KS C IEC 60079-5, 폭발성 분위기 - 제 5 부: 충전 방폭구조 "q"에 의한 기기 보호 KS C IEC 60079-29-2, 폭발성 분위기 - 제 29-2 부: 가스 감지기 - 가연성 가스 및 산소용 감지기의 선정, 설치, 사용 및 유지보수 KS C IEC 60079-30-2, 방폭 전기기계 · 기구 - 제 30-2 부: 전기저항 트레이스 히터 - 설계, 시공 및 유지를 위한 응용 가이드 KS C IEC 60079-31, 폭발성 분위기 - 제 31 부: 용기 "t"에 의한 기기의 분진 점화 보호 KS C IEC 60332-2-2, 화재 조건에서의 전기/광섬유 케이블 시험 - 제 2-2 부: 단심 소형 절연 전선 또 는 케이블 수직 불꽃 전파 시험 - 확산 불꽃 시험 절차 KS C IEC 60332-3(모든 부), 화재조건에서의 전기 및 광섬유 케이블 시험 KS C IEC 60529, 외함의 밀폐 보호등급 구분(IP 코드) KS C IEC 60614-2-1, 전선관 - 제 2-1 부: 금속제 전선관의 개별규정 KS C IEC 60614-2-5, 전선관 - 제 2-5 부: 가요 전선관(플렉시블)의 개별규정 KS C IEC 61008-1, 주택용 및 이와 유사한 용도의 과전류 보호장치가 없는 누전차단기(RCCBs) - 제 1 부: 일반 요구사항 KS C IEC 61241(모든 부), 분진 방폭 전기 기계 · 기구 KS C IEC 61241-1, 분진 방폭 전기 기계 · 기구 - 제 1 부: 내압방폭구조 KS C IEC 61241-2-1, 분진방폭 전기기계 · 기구 - 제 201 부: 분진의 최소점화온도 시험방법 KS C IEC 61241-11, 분진 방폭 전기 기계 · 기구 - 제 11 부: 본질안전 방폭구조 "iD" KS C IEC 61439-1, 저압 배전반 및 제어반 - 제 1 부: 통칙 IEC TS 60034-25, Rotating electrical machines - Part 25: AC electrical machines used in power drive systems - Application guide IEC 60742, Isolating transformers and safety isolating transformers Requirements IEC 60755, General requirements for residual current operated protective devices IEC 61024-1, Protection of structures against lightning - Part 1: General principles IEC 61241-4, Electrical apparatus for combustible dust atmospheres - Part 4: Type of protection0 "pD" ISO 10807, Pipework - Corrugated flexible metallic hose assemblies for the protection of electric cables in explosive atmospheres CENELEC/EN 50272-2, Safety requirements for secondary batteries and battery installations - Part 2: Stationary batteries 123 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
016146e5-6d20-4e88-bd58-7fb541c67b6d | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 CLC/TR 50427, Assessment of inadvertent ignition of flammable atmospheres by radiofrequency radiation Guide CENELEC/TR 50404, Electrostatics Code of practice for the avoidance of hazards due to static electricity 124 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
7e64a974-9d5f-4bd9-a108-4376fce0a251 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 KS C IEC 60079-14:2013 해 설 이 해설은 본체 및 부속서(규정)에 규정한 사항, 부속서(참고)에 기재한 사항 및 이들과 관련된 사항 을 설명하는 것으로 표준의 일부는 아니다. 1 개정 취지 이 표준은 2013 년 제 5 판으로 발행된 IEC 60079-14, Explosive atmospheres - Part 14: Electrical installations design, selection and erection, COR1(2016), ISH1(2017) 및 ISH2(2020)를 기초로 기술적 내용 및 대응국제표준의 구성을 변경하지 않고 작성한 한국산업표준이다. 2 개정 내용 기존 KS C IEC 60079-14:2002(2017 확인)에서 현 KS C IEC 60079-14:2013 으로의 변경 사항은 다음과 같다. ¦ 주요 변경 사항 ¦ 조항 ¦ 변경 유형 ¦ 변경 유형 ¦ 변경 유형 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 주요 변경 사항 ¦ 조항 ¦ 사소한 내용, 편집 수정 ¦ 확장 ¦ 중요한 기 술적 변경 ¦ ¦ 최초 검사 신설 ¦ 적용범위 ¦ ¦ X ¦ ¦ ¦ "전기기기" 정의 신설 ¦ 3.1.3 ¦ X ¦ ¦ ¦ ¦ "하이브리드 혼합물" 정의 신설 ¦ 3.2.4 ¦ ¦ X ¦ ¦ ¦ "관련기기" 정의 에 주석 추가 ¦ 3.5.2 ¦ X ¦ ¦ ¦ ¦ "무선 주파수 식별" 정의 신설 ¦ 3.15 ¦ X ¦ ¦ ¦ ¦ 문서 목록 개선, 확대: 현장, 기기, 설치, 담당자 ¦ 4.2 ¦ X ¦ ¦ ¦ ¦ 최초 검사 항목 신설 ¦ 4.3 ¦ ¦ X ¦ ¦ ¦ KS C IEC 60079 의 최신 연판 KS C IEC 표준에 근거한 구체적 요구사항 ¦ 4.4.1.2 ¦ X ¦ ¦ ¦ ¦ KS C IEC 60079-0 에 따른 새로운 방사기기 선정 기준 ¦ 5.7 ¦ ¦ X ¦ ¦ ¦ KS C IEC 60079-0 에 따른 새로운 초음파 기기 선정 기준 ¦ 5.8 ¦ ¦ X ¦ ¦ ¦ KS C IEC 60079-11 에 따른 이동형, 휴대형, (개 인)착용형 기기에 사용되는 전지 및 배터리에 적용되는 구체적 요구사항 ¦ 5.10 ¦ ¦ ¦ C1 ¦ ¦ 새로운 회전 전기기기 선정 기준 ¦ 5.11 ¦ X ¦ ¦ ¦ ¦ 새로운 전지 및 배터리 선정 기준 ¦ 5.14 ¦ ¦ X ¦ ¦ ¦ 새로운 무선 주파수 인식 태그 선정 기준 ¦ 5.15 ¦ ¦ X ¦ ¦ ¦ 새로운 가스 감지기기 선정 기준 ¦ 5.16 ¦ ¦ X ¦ ¦ ¦ KS C IEC 60079-0 의 경금속 요구사항에 따른 금 속 설치 자재 소재 구성 요구사항 ¦ 6.1 ¦ ¦ X ¦ ¦ ¦ 폭발위험장소 상부 3.5m 제한 규정 삭제 ¦ 6.3.7 ¦ X ¦ ¦ ¦ ¦ KS C IEC 60079-0 에 따른, 새로운 구조의 정전 기 요구사항 추가 ¦ 6.5 ¦ ¦ X ¦ ¦ 125 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
cb485949-ac7a-437e-a155-06e017802b46 | KSCIEC60079-14_KR | KS CIEC 60079-14:2013 ¦ 주요 변경 사항 ¦ 조항 ¦ 변경 유형 ¦ 변경 유형 ¦ 변경 유형 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 주요 변경 사항 ¦ 조항 ¦ 사소한 내용, 편집 수정 ¦ 확장 ¦ 중요한 기 술적 변경 ¦ ¦ KS C IEC 60079-0 에 따른, 전자기 방사 요구사 항 신설 ¦ 6.7 ¦ ¦ X ¦ ¦ ¦ 가독성 향상을 위한 케이블, 고정 기기에 사용되 는 고정/가요 케이블 관련 문구 개선 ¦ 9.3.1 9.3.2 9.3.3 ¦ X ¦ ¦ ¦ ¦ 케이블 인입 시스템, 블랭킹 커버에 적용되는 새 로운 구조의 요구사항 일반사항 기기에 대한 케이블 연결 케이블글랜드 선정(표 10 새로 추가) Ex "d", Ex "t", Ex "nR"가 아닌 케이블글랜드 관련 추가 요구사항 Ex "d"에 적용되는 추가 요구사항 Ex "t"에 적용되는 추가 요구사항 Ex "nR"에 적용되는 추가 요구사항 ¦ 10 절 10.1 10.2 10.3 10.4 10.5 10.6 10.7 10.8 ¦ ¦ X ¦ ¦ ¦ 모든 방폭유형에 적용되는 새로운 구조의 회전 전기기기 요구사항 ¦ 11 절 ¦ ¦ X ¦ ¦ ¦ 온도 계측, 온도 제한, 안전장치를 포함한 전기 가열 시스템에 적용되는 새로운 구조의 요구사 항, 전기 트레이스 가열 시스템에 적용되는 추가 적인 요구사항 ¦ 13 절 ¦ ¦ X ¦ ¦ ¦ 단면적과 허용 연속 전류의 사이의 관계와 연선 의 수의 함수로 표시한 단자함 전력 소비를 제 한하는 조항 신설, 예시 추가 ¦ 15.4 ¦ ¦ X ¦ ¦ ¦ 단순기기의 정의, 제한, 주위온도에 근거한 최대 전력 소비 변화, 최대 표면 온도 계산을 위한 대 체 공식 문구 수정 ¦ 16.4 ¦ ¦ X ¦ ¦ ¦ 둘 이상의 본질안전회로가 포함된 단자함의 각 각의 독립된 본질안전회로 사이의 단락을 피하 기 위한 새로운 요구사항 신설 ¦ 16.5 ¦ ¦ ¦ C2 ¦ ¦ 비본질안전회로 및 본질안전회로가 포함된 단자 함에 관한 문구 수정 ¦ 16.5.4 ¦ X ¦ ¦ ¦ ¦ 양압실 및 분석실 조항 신설 ¦ 17.4 ¦ ¦ X ¦ ¦ ¦ 광학 방사 조항 신설 ¦ 22 절 ¦ ¦ X ¦ ¦ ¦ 모든 형식의 방폭구조에 대한 특정 기기 최초 검사에 관한 부록 신설 ¦ 부속서 C ¦ ¦ X ¦ ¦ ¦ 매우 낮은 온도에서의 전기설비에 관한 부속서 신설 ¦ 부속서 D ¦ ¦ X ¦ ¦ ¦ 케이블 통기제한에 관한 부속서 신설 ¦ 부속서 E ¦ ¦ X ¦ ¦ ¦ 전기 트레이스 가열 시스템 설치에 관한 부속서 신설 ¦ 부속서 F ¦ ¦ X ¦ ¦ ¦ 광학방폭구조 "op"형에 적용되는 요구사항에 관 한 부속서 신설 ¦ 부속서 K ¦ ¦ X ¦ ¦ ¦ 하이브리드 혼합물에 관한 부속서 신설 ¦ 부속서 M ¦ ¦ X ¦ ¦ 126 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
221e2ab6-c219-47d3-8ed3-efd95c8dd9c4 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 3 INTERPRETATION SHEET(ISH1, ISH2) ISH1 다음은 2016 년 프랑크푸르트에서 개최된 SC 31J 의 IEC 60079-14:2013 의 해석에 관한 결정사항으로 서, 컨버터 전원공급 또는 감소된 전압으로 기동하는 전기 모터의 설치 관련 이슈사항을 명확히 하 기 위한 해설이다. 세부사항: 11.2.1 b), 11.2.2 b), 11.3.5b), 11.4.1 b) 11.4.2 b), 11.5.1 b), 11.5.2 b), 11.6.1 b) 및 11.6.2 b)에서 컨버 터 전원공급 및 감압 기동에 대한 해설 컨버터와 함께 하나의 단위로 형식시험을 거치지 않은 전동기의 경우, 전동기 기술문서에 명시된 내 장 온도센서를 통해 직접 온도를 제어할 수 있는 수단(또는 기기)이 마련되어 있거나, 전동기 외부 표면온도를 제한할 수 있는 그 밖의 효율적인 수단이 마련되어 있어야 한다. 온도 제어의 효율성은 전력, 속도 범위, 토크, 듀티 주파수(frequency for the duty)를 고려하여 결정해야 하며, 검증을 거쳐 문서화해야 한다. 보호장치가 작동되면 전동기가 전기적으로 차단되어야 한다. 질문사항 이 요구사항을 충족시키기 위하여 스위치(회로 차단기) 또는 접점과 같은 물리적 차단장지가 요구되 는가? 해설 이 요구사항은 표면온도 초과 로부터 기기를 보호하기 위함이다. 모터 제어회로 내에서 이루어지는 다음 중 한 가지 조치가 이 요구사항에서 의도하는 것을 충족하는 것으로 본다. · 모터쪽으로 출력 전압을 차단하는 직접 물리적 차단 · 주파수 변조를 정지시키는 것이 중재 제어회로(control circuit intervention)가 모터의 동작을 차단 비고 이 경우에서 모터 측에 전압이 존재할 수 있어도 모터는 동작하지 않는다. ISH2 배경 KS C IEC 60079 시리즈의 방폭구조가 변경됨에 따라 현 KS C IEC 60079-14 에서 여러 방폭구조 표기 법이 포함되지 않았다. 이것은 사용자의 혼선을 유도하여 올바른 기기 적용에 혼선을 초래할 수도 있다. 질문사항 새로운 방폭구조는 KS C IEC 60079-14 에 따라 어떻게 기기에 표기되어야 하는가? 해설 새로운 방폭구조가 표기된 기기는 아래 사항 및 KS C IEC 60079-14:2013 의 표 2 를 기준으로 하여 KS C IEC 60079-14 에 따라 적용되어야 한다. 127 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
0ab7cb0d-bfb9-4c6b-bd6d-06bc669bd5d5 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 · · . . · Ex "eb"는 Ex "e"와 동등한 것으로 간주된다. Ex "ec"는 Ex"nA"와 동등한 것으로 간주된다. Ex "db"는 Ex "d"와 동등한 것으로 간주된다. Ex "dc"의 요구사항은 Ex"d" 요구사항에 근거하였지만 기기보호등급 Gc 에만 적합하다. Ex "ob"는 Ex"o"와 동등한 것으로 간주된다. Ex "oc"의 요구사항은 Ex"o" 요구사항에 근거하였지만 기기보호등급 Gc 에만 적합하다. · ¦ 중요한 변경 사항의 유형에 대한 설명 ¦ 중요한 변경 사항의 유형에 대한 설명 ¦ ¦ --- ¦ --- ¦ ¦ A) 정의 ¦ A) 정의 ¦ ¦ 1 사소한 내용, 편집 수정: ¦ - 문구를 명확하게 수정 - 기술 요구사항 완화 - 사소한 기술적 변경 - 교정 ¦ ¦ 이 변경 사항은 편집 또는 사소한 기술적 사항 변경을 의미한다. 기술적 변경 사항 없이 관련 문 구만 보다 명확하게 수정하거나 기존 요구사항을 완화하는 경우가 여기에 포함된다. ¦ 이 변경 사항은 편집 또는 사소한 기술적 사항 변경을 의미한다. 기술적 변경 사항 없이 관련 문 구만 보다 명확하게 수정하거나 기존 요구사항을 완화하는 경우가 여기에 포함된다. ¦ ¦ 2 확장: ¦ - 기술적 대안 추가 ¦ ¦ 이 변경 사항은 새로운 대안을 제시하지만, 기존 표준에 완전히 부합되는 기존 기기의 설계, 선정, 설치 요구사항을 강화하지는 않는, 기술 요구사항 신설 또는 수정을 의미한다. 따라서 이전 연판의 표준을 준수하는 기존 시설은 이 변경 사항과 무관하다. ¦ 이 변경 사항은 새로운 대안을 제시하지만, 기존 표준에 완전히 부합되는 기존 기기의 설계, 선정, 설치 요구사항을 강화하지는 않는, 기술 요구사항 신설 또는 수정을 의미한다. 따라서 이전 연판의 표준을 준수하는 기존 시설은 이 변경 사항과 무관하다. ¦ ¦ 3 중요한 기술적 변경: ¦ - 기술 요구사항 추가 - 기술 요구사항 강화 ¦ ¦ 중요한 변경 사항의 유형에 대한 설명 ¦ 중요한 변경 사항의 유형에 대한 설명 ¦ ¦ 이 변경 사항은 기존 표준에 완전히 부합되는 기존 기기에 새롭게 적용될 수 있는 기술 요구사항 의 변경(추가, 강화, 삭제)을 의미한다. 이전 연판의 표준을 준수하는 기존 시설도 이 변경 사항을 고려해야 한다. 이에 대한 추가적인 정보는 아래 B)에서 제공된다. 이 변경 사항은 최신 기술 변화를 반영한 것이다. 그러나 이 변경 사항은 일반적으로 기존 기기에 대해서는 영향을 미치지 않는다. ¦ 이 변경 사항은 기존 표준에 완전히 부합되는 기존 기기에 새롭게 적용될 수 있는 기술 요구사항 의 변경(추가, 강화, 삭제)을 의미한다. 이전 연판의 표준을 준수하는 기존 시설도 이 변경 사항을 고려해야 한다. 이에 대한 추가적인 정보는 아래 B)에서 제공된다. 이 변경 사항은 최신 기술 변화를 반영한 것이다. 그러나 이 변경 사항은 일반적으로 기존 기기에 대해서는 영향을 미치지 않는다. ¦ ¦ B) "중요한 기술적 변경"의 배경 ¦ B) "중요한 기술적 변경"의 배경 ¦ ¦ C1 전지의 유형과 무관하게 수소 가스 발생 위험이 있으며, 이로 인해 소형 외함 내에 폭발성 분 위기가 조성될 수 있기 때문에 환기를 시킬 필요가 있다. 토치, 멀티미터, 포켓 가스 감지기 및 이 와 유사한 기기에서 이런 문제가 발생할 수 있다. 단, 기기 그룹 IIC 의 요구사항을 준수하는 기기 의 경우는 탈기 구멍 또는 수소 농도 제한 요구사항이 적용되지 않는다. C2 개별 본질안전회로는 단락 조건에서도 안전성이 유지된다. 2 개의 독립된 본질회로 사이의 단락 은 고려하지 않는다. 따라서 단자함은 최악의 조건에서도 외함의 건전성을 유지하기 위해 IP 등급 과 기계적 충격에 관한 추가적인 요구사항을 준수해야 한다. ¦ C1 전지의 유형과 무관하게 수소 가스 발생 위험이 있으며, 이로 인해 소형 외함 내에 폭발성 분 위기가 조성될 수 있기 때문에 환기를 시킬 필요가 있다. 토치, 멀티미터, 포켓 가스 감지기 및 이 와 유사한 기기에서 이런 문제가 발생할 수 있다. 단, 기기 그룹 IIC 의 요구사항을 준수하는 기기 의 경우는 탈기 구멍 또는 수소 농도 제한 요구사항이 적용되지 않는다. C2 개별 본질안전회로는 단락 조건에서도 안전성이 유지된다. 2 개의 독립된 본질회로 사이의 단락 은 고려하지 않는다. 따라서 단자함은 최악의 조건에서도 외함의 건전성을 유지하기 위해 IP 등급 과 기계적 충격에 관한 추가적인 요구사항을 준수해야 한다. ¦ 4 기타 이 표준은 KS A 0001:2015(표준의 서식과 작성방법)에 따라 작성하였다. 128 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
fb48b75b-aa8f-411b-9f4f-5e9b93f9a46c | KSCIEC60079-14_KR | 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
223b0dfd-12ed-4807-aaf4-14bfc8f39027 | KSCIEC60079-14_KR | KS C IEC 60079-14:2013 KSKSKS KSKSK KSKS KSK KS KSK KSKS KSKSK KSKSKS ¦ Explosive atmospheres ¦ ¦ --- ¦ ¦ Part 14: Electrical installations ¦ ¦ design, selection and erection ¦ ¦ ICS 29.260.20 ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
a0774e11-8991-4dc2-b92b-f4bd9db4ef1a | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | SK ecoplant SPECIFICATION FOR HVAC & PLUMBING SYSTEM - 급수·급탕 배관공사 - ¦ DOC No. ¦ : 21036D-IC-M16G00-HV-A00-00141 ¦ ¦ --- ¦ --- ¦ ¦ DISCIPLINE ¦ : HVAC ¦ ¦ PROJECT No. ¦ : 21036D ¦ ¦ PROJECT TITLE ¦ : M16 Ph2 Project ¦ ¦ CLIENT ¦ : SK hynix ¦ ¦ LOCATION ¦ : Icheon city, Gyeonggi-do, Korea ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 0 ¦ 2022.01.25 ¦ APPROVED FOR CONSTRUCTION ¦ T.G.YU ¦ J.H. YANG ¦ Y.T.OH ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ REV. ¦ DATE ¦ DESCRIPTION ¦ PRPD ¦ CHKD ¦ APPD ¦ 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. | {}
4d577e9e-9847-42c3-a51c-75f66f719202 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 1 of 41 ¦ 1. 일반사항 1.1 적용범위 1.1.1 요약 (1) 이 절은 급수(CTW) 및 급탕(DHWS/R) 및 재활용수(NPW) 배관에 적용한다. (2) 설계도서, 관계법규 또는 별도로 정한 규정에 의한 것을 제외하고는 모두 본 시방에 준한다. (3) 이 시방서에 기재되지 않은 사항은 국토교통부 제정 "기계설비공사 표준 시방서" 및, '1.3 항 참조표준'을 적용할 수 있다. 단 본 시방서와 상이한 내용은 본 시방서를 우선하여 적용한다. (4) 이 시방서에 특별한 명기가 없는 사항 중 건축, 전기에 관한 사항은 해당 시방서에 따른다. (5) 시방서, 설계도면 및 내역서 중 어느 한 도서에라도 표기되어 있는 사항은 시공하여야 한다. (6) 산업안전보건법에서 규정한 법규에 의해서 시공하여야 한다. 1.1.2 적용 및 우선 (1) 모든 공사는 설계도면 및 시방서에 준하여 시공하며, 설계도면과 시방이 상이한 경우에는 설 계도면을 우선하되 발주 담당자와 협의 하여 정한다. (2) 본 시방서, 설계도면 또는 표준 시방이 정한 공법, 자재 및 제품 등의 내용이 현실적으로 이 (3) 행하기 불가능할 경우에는 반드시 발주 담당자에게 서면으로 보고하고 대안에 대한 승인을 득한 후 시공한다. 1.1.3 주요내용 (1) 배관 재료 및 배관 부속품 (2) 접합재료 (3) 지지철물 (4) 계측기 및 기타 (5) 관의 접합 (6) 배관 용접 (7) 시험 및 검사 1.2 관련 시방 1.2.1 일반공통사항 1.2.2 보온공사 1.2.3 도장 · 방청 및 부식공사 1.2.4. 플랜지체결공사 1.3 참조 표준 1.3.1 한국산업표준 SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. SK ecoplant | {}
bb8b0ac4-6bd4-4ec3-83f3-dab424a55bb2 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ ENGINEERING DESIGN SPECIFICATION ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 Page 2 of 41 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ KS B 0052 ¦ 용접 기호 ¦ ¦ --- ¦ --- ¦ ¦ KS B 0106 ¦ 용접 용어 ¦ ¦ KS B 0222 ¦ 관용 테이퍼 나사 ¦ ¦ KS B 0816 ¦ 침투 탐상 시험방법 및 지시모양의 분류 ¦ ¦ KS B 0845 ¦ 강 용접 이음부의 방사선 투과 시험방법 ¦ ¦ KS B 0885 ¦ 수동용접 기술검점에 있어서의 시험방법 및 판정기준 ¦ ¦ KS B 0888 ¦ 배관 용접부의 비파괴 시험방법 ¦ ¦ KS B 0896 ¦ 강 용접부의 초음파 탐상 시험방법 및 시험결과 의 등급 분류 방법 ¦ ¦ KS B 1501 ¦ 철강제 관 플랜지의 압력 단계 ¦ ¦ KS B 1503 ¦ 강제 용접식 관 플랜지 ¦ ¦ KS B 1506 ¦ 스테인리스 강제 용접식 플랜지 ¦ ¦ KS B 1511 ¦ 철강제 관 플랜지의 기본 치수 및 치수 허용차 ¦ ¦ KS B 1519 ¦ 관 플랜지의 개스킷 자리 치수 ¦ ¦ KS B 1531 ¦ 나사식 가단 주철제 관 이음쇠 ¦ ¦ KS B 1533 ¦ 나사식 강관제 관 이음쇠 ¦ ¦ KS B 1536 ¦ 벨로스형 신축관 이음 ¦ ¦ KS B 1543 ¦ 맞대기 용접식 관 이음쇠 ¦ ¦ KS B 1546 ¦ 폴리에틸렌 관 이음쇠 ¦ ¦ KS B 2301 ¦ 청동 밸브 ¦ ¦ KS B 2308 ¦ 볼 밸브 ¦ ¦ KS B 2332 ¦ 수도용 제수 밸브 ¦ ¦ KS B 2333 ¦ 버터플라이 밸브 ¦ ¦ KS B 2350 ¦ 주철 밸브 ¦ ¦ KS B 2361 ¦ 주강 플랜지형 밸브 ¦ ¦ KS B 2373 ¦ 물용 자동 공기 배출 밸브 ¦ ¦ KS B 2813 ¦ 웨이퍼형 고무붙이 버터플라이 밸브 ¦ ¦ KS B 5302 ¦ 유리제 온도계(전체 담금) ¦ ¦ KS B 5305 ¦ 부르동관 압력계 ¦ ¦ KS C 9602 ¦ 교류 아크 용접기 ¦ ¦ KS C 9605 ¦ 정류기식 직류 아크 용접기 ¦ ¦ KS C 9607 ¦ 용접봉 홀더 ¦ ¦ KS D 0237 ¦ 스테인리스강 용접부의 방사선 투과 검사방법 ¦ ¦ KS D 3507 ¦ 일반 배관용 탄소 강관 ¦ ¦ KS D 3515 ¦ 용접 구조용 압연 강재 ¦ ¦ KS D 3562 ¦ 압력 배관용 탄소 강관 ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
5cc554cf-e44e-4b05-b642-c8f606e7964b | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ ENGINEERING DESIGN SPECIFICATION ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 Page 3 of 41 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ KS D 3576 ¦ 배관용 스테인리스 강관 ¦ ¦ --- ¦ --- ¦ ¦ KS D 3583 ¦ 배관용 아크 용접 탄소강 강관 ¦ ¦ KS D 3595 ¦ 일반 배관용 스테인리스 강관 ¦ ¦ KS D 3696 ¦ 용접용 스테인리스강 선재 ¦ ¦ KS D 7004 ¦ 연강용 피복 아크 용접봉 ¦ ¦ KS D 7006 ¦ 고장력 강용 피복 아크 용접봉 ¦ ¦ KS M 6617 ¦ 방진 고무용 고무 재료 ¦ 1.4 제출물 1.4.1 자재 공급 전 제출물 시공자는 다음의 사항을 자재공급 전에 발주 담당자에게 제출하여 승인을 받아야 한다. (1) 주요 기자재공급원 승인요청서 ① KS 규격 인증서 또는 ISO 품질인증서 ② 공급자의 사업자 등록증명원 (단, 외산자재인 경우 납품 회사 분) ③ 국세 및 지방세 완납증명서 (유효기관 확인) ④ 납품실적증명서 (유효기관 확인) ⑤ 품질검사 전문기관 및 국·공립검사기관의 시험성과 표 ⑥ 품질보증각서 : KS 비인증제품, 공인기관 시험 불가제품, 해외제품(시험성적서 제출)등 (2) 필요 시 재료에 대한 견본품을 제출하여야 한다. 1.4.2 자재 입고 검사 요청서 자재(외부 제작 배관 등 포함) 반입 시 자재 입고 검사 요청서를 발주 담당자에게 제출하여 확인을 받는다. 1.4.3 검측 요청서 시공 담당자가 검측 요청서를 작성하여 건설사업관리기술인에게 확인을 받은 후 발주 담당자에 게 제출 한다. 1.5 품질보증 1.5.1 용접공의 자격 (1) 용접공은 관재의 각종 재료에 관련된 시공사의 용접사 기량 확인 시험에 합격한 자로 한다. (2) 시공자는 용접작업지침서를 제출하여 발주 담당자의 승인을 받아야 한다. (3) 용접사 기량 확인 시험은 체크시트에 의거하여 자체 육안검사(Visual Test)를 진행하여 합·불 SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. SK ecoplant | {}
f3cf6a0a-ee55-44bb-ad66-7216c9ef61c7 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 4 of 41 ¦ 판정을 한다. (4) 합격된 시편에 한하여 방사선투과 검사(Radiographic Test)를 의뢰하며, 결과 를 발주 담당자에 게 보고한다. (5) 용접사 기량 확인 시험 방법 1 차 용접사 테스트를 실시하여 자격요건을 확인한다. 테스트 항목은 아래와 같다. -. BEAD 검사 -. UNDERCUT 검사 -. OVERLAP 상태 검사 -. BACK BEAD 검사 : 용입부족 검사 -. 용접 후 배관 각도 검사 -. CRACK 검사 1 차 용접사 테스트 합격자에 한하여 방사선투과 검사를 의뢰하고, 합격자에 한하여 용접작업 에 투입될 수 있도록 한다 (6) 판정 판정은 당 프로젝트 시공사 용접기술자가 방사선투과 검사 결과 를 근거로 판정하고 합격자에 게는 CERTIFICATE 를 발급하여 인정토록 하며, 관리대장을 정리하여 관리한다. 1.5.2 환경조건 (1) 용접 전 모재 온도가 영상 10°C 미만일 경우에는 반드시 영상 10°C 이상으로 예열한다. (모재의 가열범위는 배관 양 끝에서 각각 50mm 이상 용접 시작부위에 예열한다.) (2) 용접중에는 예열하지 않으며 용접 작업 중단 후 재용접 시에는 배관의 온도를 측정하여 10°C 이하일 경우 추가 예열 후 작업한다. (3) 비 또는 눈이 내리는 곳이나 바람이 (10m/s 이상 강하게) 부는 곳에서 용접을 하여서는 안된 다. 단, 날씨 등의 영향을 받지 않도록 충분한 보호시설을 하였을 경우에는 발주 담당자의 승 인을 득한 후 용접할 수 있다. 1.6 운반, 저장 및 취급 1.6.1 모든 재료는 옥내에 보관한다. 1.6.2 보관, 운반, 상하차 및 시공할 때에는 충격 등으로 관이 손상되지 않도록 하며, 적재·보관 시 주변 하중으로 관의 변형이 발생하지 않도록 하여야 한다. SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
a9450261-fbf3-4385-82f3-2b41ef34c9d7 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ ENGINEERING DESIGN SPECIFICATION ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 Page 5 of 41 ¦ ¦ --- ¦ --- ¦ --- ¦ 1.6.3 운반, 저장 및 취급기간 동안 현장제작 또는 공장제작된 배관, SPOOL, 부속기기 및 구매된 제품이 손상되지 않도록 보호해야 한다. 1.6.4 모서리와 끝부분의 손상을 방지하고 배관, SPOOL 및 부속기기의 표면에 이물질이 묻거나 내부에 습기가 차지 않도록 하여야 한다. 1.7 보온공사 '18154D-CJ-G00-HV-A00-00150 보온공사' 기준에 따른다. 1.8 도장 · 방청 및 부식공사 '18154D-CJ-G00-HV-A00-00160 도장 · 방청 및 부식공사' 기준에 따른다. 2. 재료 2.1 일반사항 배관재료는 KS 규격에 적합한 제품으로 하고, KS 제품이 없는 품목에 대해서는 중소기업청이 승인한 표준화규격에 인정된 제품 또는 기능과 성능이 보장 될 수 있는 제품에 한하여 발주 담당자와 협의 하여 사용 할 수 있다. 2.2 배관재료 2.2.1 유체별 배관 사양 ¦ 분 류 ¦ 급수(CTW), 급탕(DHWS/R), 재활용수( NPW) ¦ 급수(CTW), 급탕(DHWS/R), 재활용수( NPW) ¦ 급수(CTW), 급탕(DHWS/R), 재활용수( NPW) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 압 력 ¦ 10 kg/cm2.G 이하 ¦ 10 kg/cm2.G 이하 ¦ 10 kg/cm2.G 이하 ¦ ¦ 온 도 ¦ 100°C 이하 ¦ 100°C 이하 ¦ 100°C 이하 ¦ ¦ 크 기 ¦ 15A ~ 40A ¦ 50A ~ 300A ¦ 300A above ¦ ¦ PIPE ¦ STS304 TP-AP, KS D 3576, ERW, PE, SCH10S STS304 TPD, KS D 3595, Joint Type (화장실,탕비실) ¦ STS304 TP-AP, KS D 3576, ERW, BE, SCH10S STS304 TPD, KS D 3595, Joint Type (화장실,탕비실) ¦ STS304 TPY, KS D 3588, ERW, BE, SCH10S ¦ ¦ FITTINGS ¦ STS304, KS B 1543, ERW, BE, SCH10S ¦ STS304, KS B 1543, ERW, BE, SCH10S ¦ STS304, KS B 1543, ERW, BE, SCH10S ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
81b5d15e-56bb-41ca-940a-567cbdbdc64b | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 6 of 41 ¦ ¦ ¦ STS304,Joint Type (화장실,탕비실) ¦ STS304,Joint Type (화장실,탕비실) ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ FLANGE ¦ KS 10K, STSF304, KS B 1506, SO, FF ¦ KS 10K, STSF304, KS B 1506, SO, FF ¦ KS 10K, STSF304, KS B 1506, SO, FF ¦ ¦ GASKET ¦ KS 10K, Spiral Wound(Graphite Filler/SS304 Outerring), FF, 3.2THK KS 10K, 3.5THK, PTFE Cushion, FF ¦ KS 10K, Spiral Wound(Graphite Filler/SS304 Outerring), FF, 3.2THK KS 10K, 3.5THK, PTFE Cushion, FF ¦ KS 10K, Spiral Wound(Graphite Filler/SS304 Outerring), FF, 3.2THK KS 10K, 3.5THK, PTFE Cushion, FF ¦ ¦ GATE VALVE ¦ API 800LB, STSF304/TYPE304, SW, BB. OS&Y ¦ KS 10K, SSC13/TYPE304, FLG'D, FF, BB. OS&Y ¦ KS 10K, SSC13/TYPE304, FLG'D, FF, BB. OS&Y ¦ ¦ BUTTERFLY VALVE ¦ - ¦ KS 10K, SCPH2/Cr13, +METAL, WAFER TYPE, GEAR OPER. ¦ KS 10K, SCPH2/Cr13, +METAL, WAFER TYPE, GEAR OPER. ¦ ¦ GLOBE VALVE ¦ API 800LB, STSF304/TYPE304, SW, BB. OS&Y ¦ KS 10K, SSC13/TYPE304, FLG'D, FF, BB. OS&Y ¦ KS 10K, SSC13/TYPE304, FLG'D, FF, BB. OS&Y ¦ ¦ CHECK VALVE ¦ API 800LB, STSF304/TYPE304,SW, BC. LIFT ¦ KS 10K, SSC13/TYPE304, FLG'D, FF, BC. SWING ¦ KS 10K, SSC13/TYPE304, FLG'D, FF, BC. SWING ¦ ¦ BALL VALVE ¦ KS 10K, KS B 2308, SCR'D, STS304 ¦ ¦ ¦ ¦ Y-TYPE STRAINER ¦ KS 10K, STSF304/SS304 SCR'D ¦ KS 10K, SSC13/SS304, FLG'D, FF ¦ KS 10K, SSC13/SS304, FLG'D, FF ¦ * 옥외배관의 Butterfly Valve : Keystone Valve 규격의 동등품 이상 적용. 2.2.4 수격방지기 (1) 본체는 수압에 충분히 결딜 수 있는 두꺼운 판 구조의 것으로 하고, 공기보급의 경우에 상하에 콕 및 밸브를 설치하는 것으로 한다. (2) 벨로스나 고무 등을 사용하는 것은 내구성이 있고 동시에 수질에 해를 끼치지 않는 것 으로 한다. 2.2.5 공기빼기밸브 자동적으로 공기를 배제하는 기능을 가지며 작동이 확실하고 최고사용압력에 견딜 수 있는 것으로 한다. 2.2.6 감압밸브 2 차측 압력은 1 차측 압력의 변동에 영향을 받지 않고 작동이 확실한 것으로 한다. hynix SK SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
b0837f3e-e75e-4484-8240-97305f9d250b | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 7 of 41 ¦ 2.2.7 플로팅 밸브(볼탭) KS B 2330 제품으로 하며, KS 의 적용범위 이외의 것에 대해서는 KS 에 준하는 재료 및 구조로 하 고, 최고사용압력에 견디는 것으로 한다. 단, 볼의 재질은 내식성 금속재료 또는 합성수지로 한다. 2.2.8 슬리브(SLEEVE) (1) 슬리브 구경은 원칙적으로 관의 외경(보온된 것은 보온피복 외경) 보다 2 단계 큰 사이즈로 하고 이종관의 접촉 또는 연결 부속에 절연 조치를 한다. (2) 벽, 바닥 등을 관통하는 곳에 KS D 3507(일반배관용탄소강관), KS D 3506(용융아연도금강판및강대) 재질의 슬리브를 설치 한다. 2.3 접합재료 2.3.1 접합재료의 종류 및 규격은 다음 표에 따른다. ¦ 종 류 ¦ 명 칭 ¦ 적 용 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 플랜지 접합 ¦ 가스켓 ¦ '2.2.1 유체별 배관 사양' GASKET 기준에 따른다. ¦ ¦ 용접 접합 ¦ 용접봉 ¦ 스테인리스 강관의(TIG 용접)은 용도에 적합한 것으로 한다. ¦ 2.3.2 볼트, 너트 및 와셔 (1) 볼트, 너트 및 와셔의 재료는 KS D 3503(일반구조용 압연강재) 및 스테인리스강제의 제품 으로 한다. (2) 볼트 및 너트는 다음의 제품으로 한다. KS B 1002(6 각 볼트) KS B 1012(6 각 너트 및 6 각 낮은너트) (3) 와셔는 KS B 1326(평와 셔) 제품으로 한다. (4) 앵커 볼트의 나사는 KS B 1002(6 각 볼트)의 나사에 준한다. (5) 고장력 볼트, 너트 및 평와 셔의 세트는 KS B 1010(마찰접합용 고장력 6 각볼트, 6 각너트, 평와 셔의 세트), TS 볼트, 너트는 KS B 2819(구조물용 토크 전단형 고장력 볼트, 6 각너트, 평와 셔의 세트)의 제품으로 한다. (6) 옥상/옥외 설비 체결부(STS 강관, 탄소 강관 및 장비)의 고정용으로 사용하는 볼트, 너트는 재질에 따라 STS 볼트/너트, GEOMET 볼트/너트를 사용한다 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
5889c640-6aa2-4bf8-bea6-1c096108f7c5 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 8 of 41 ¦ 2.3.3 용접기 (1) 용접전원은 필요한 전류용량과 용접에 적합한 전기적 특성을 가지며, 또한 출력을 원활히 조 절할 수 있는 것이어야 한다. (2) 용접기는 안정된 아크를 발생시키고 필요한 전류를 간단, 정확, 연속적으로 조정할 수 있으며 양호한 용접을 할 수 있는 것이어야 한다. (3) 용접기에는 사고방지를 위한 전격 방지장치를 부착하여야 한다. 2.3.4 용접봉 홀더 용접기 홀더는 KS C 9607(용접봉 홀더)에 적합한 것이어야 하며, 불량한 홀더 사용으로 감전 및 용접봉과 의 접촉불량을 유발하여 홀더가 과열되는 일이 있어서는 안된다. 2.3.5 용접봉 (1) 용접봉은 용접조건(강재의 종류, 관두께 및 종류 등)에 따라 적합한 것을 사용하여야 한다. (2) 이물질이 묻어 있거나 손상된 용접봉을 사용하여서는 안된다. (3) 용접봉의 종류 및 규격은 용접작업지침서에 명기하여 발주담당자의 승인을 받아야 한다. 2.4 지지철물 2.4.1 일반사항 (1) 관의 신축, 동요 및 하중 등에 견딜 수 있는 것으로 관경 또는 관의 재질에 따라 지지강도를 갖는 것으로 하고, 진동 전달을 막을 필요가 있을 때는 방진재가 붙은 것으로 한다. (2) SUPPORT 부재의 재질은 KS D 3503(일반 구조용 압연강재)을 사용하며, 배관의 TRUNNION 부재는 받쳐지는 배관과 동일한 재질을 사용한다. (3) 모든 BOLT 및 NUT 는 KS B 1002 및 KS B 1012 의 HEXAGON TYPE 을 사용한다. 2.4.2 행거 철물 및 입상관 지지 철물 행거 지지철물은 KS B 1527(파이프 서포트) 규격에 적합한 철제품으로 하고 관의 지지 간격에 따른 관, 내용물 및 피복의 전 하중을 지지할 수 있는 구조 및 강도가 있는 것으로 한다. 2.4.3 관 고정 철물 관경에 적합한 철제품으로 하고 배관의 신축에 따라 생기는 응력 또는 수격 등으로 인해 진동이 발생하지 않고, 관이 어느 방향으로도 움직이지 않는 강도를 가진 구조로 한다. 2.4.4 관 공통 지지 철물 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
69564fbc-f8cc-4d15-8c16-2f91fa203219 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 9 of 41 ¦ 다수의 배관이 병렬로 놓여 있을 때에 사용되는 공통 지지 철물은 관과 내용물 및 피복의 전 중 량을 지지하는데 충분한 구조 및 강도를 갖는 것으로 한다. 2.4.5 방진 지지 철물 진동전달을 방지할 필요가 있는 곳에 사용하는 지지철물은 행거철물 및 지지 철물에 방진고무 등을 넣어 충분한 방진성과 강도가 있는 KS B 1561(방진 스프링 행거), KS B 1562(방진고무 마운 트), KS B 1563(방진스프링 마운트) 규격에 적합한 것으로 한다. 2.5 계측 및 기타 2.5.1 압력계, 진공계 (1) 압력계, 진공계는 KS B 5305(부르동관 압력계)에 따르며, 측정하는 유체의 종류 및 설치 장소 에 적합한 것으로 하고 도면에 표기된 위치에 설치한다. 설치 전에 시공상세도면으로 발주자 와 설치 위치를 협의 한다. (2) 증기용은 콕 부착 위치에 사이폰관을 부착하여, 사이폰관 전단에 블록밸브를 설치한다. (3) 최고 눈금은 최고 사용압력의 1.5 배 이상, 진공측 눈금은 0.1MPa 로 한다. 2.5.2 온도계 KS B 5235(증기압식 지시온도계)에 의한 부르동관 팽창식 원형 지시계 및 KS B 5302(유리제 온도계[전체담금]) 또는 KS B ISO 1771(유리제 일반용 온도계)에 준하는 재료, 구조 및 성능을 가진 원형 온도계로 하고, 최고 눈금은 최고 사용온도의 1.5 배로 한다. 또한 정밀도를 요하지 않으면 온도계 교체를 위해 온도계용 웰을 사용한다. 3. 시공 3.1 공통사항 3.1.1 일반사항 (1) 관은 배관길이를 정확히 측정한 후 관경을 축소시키지 않는 공구를 사용하며, 관축에 대하여 직각으로 절단하고 관 내·외면의 덧살 및 그을 음 등이 없도록 다듬질한다. (2) 관을 잇기 전에 내부를 점검하여 이물질이 없는지를 확인한 후 금속칩 및 먼지를 깨끗이 닦 아낸다. (3) 이종금속이 접합 및 접촉되는 부분은 별도의 표기가 없더라도 항상 절연을 하여야 한다. (4) 절연플랜지 및 절연유니온은 피복부 등의 절연재가 손상되지 않도록 하여야 한다. (5) 모든 배관은 이경관을 접속할 때 레듀서를 사용하여야 하고, 수평 주관에는 편심레듀서를 사 용하여 공기 및 응축수가 정체되지 않도록 시공하여야 한다. SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
a70c4a3a-63c6-4ccb-b488-1212def69359 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 10 of 41 ¦ (6) 배관, 연결부위 및 연결된 장비에 응력을 주지 않고 배관이 팽창 수축할 수 있도록 펌프 흡입 및 토출측 입상배관 등을 지지하여야 한다. (7) 모든 배관공사는 보온 작업, 밸브 및 배관 이음쇠에 접근, 보수작업 등에 지장이 없도록 여유 공간을 두고 배관하여야 한다. (8) 배관은 질서정연하게 배열하고 공기빼기, 배수 등을 고려하여 기울기를 주어야 한다. (9) 밸브는 스템(Stem)이 아래로 향하지 않고 위 또는 수평으로 향하도록 설치하여야 한다. (밸브 조작 및 개폐여부 확인이 어려운 경우에는 CAT WALK 설치 또는 체인타입 등을 발주 담당자와 협의 하여 유지관리에 지장이 없도록 설치한다.) (10)모든 배관공사는 보온 작업, 밸브 및 배관 이음쇠에 접근, 보수작업등에 지장이 없도록 여유 공간을 300mm 두고 작업 한다. ![image](/image/placeholder) 300 300 300 8 3.1.2 배관 준비 (1) 위치의 결정 시공에 앞서 모든 배관에 대하여 다른 배관과 의 병렬 및 교차의 최소간격, 필요 기울기, 슬리 브의 위치, 향후 보수 및 배관교체 등 기타 관련 사항들을 고려하여 배관 위치를 정확히 결정 한다. (2) 배관 피트, 거푸집 및 슬리브의 고정 콘크리트의 바닥 및 벽 등에 매설할 배관 또는 관통하는 배관에 대해서는 콘크리트 타설전에 충분히 강도가 있는 거푸집 또는 슬리브 등을 소정의 위치에 장착하여 CORE(구멍뚫기)공사는 가급적 피하도록 한다. (3) 지지철물의 고정 천장 및 벽에 고정하는 인서트 및 지지철물은 건축공사의 진행에 따라 지체없이 소정의 위치 에 정확하게 부착되도록 한다. 3.1.3 배관 설치 기준 (1) 도면상의 누락이나 불분명한 사항 혹은 변경사항은 반드시 발주 담당자의 사전승인 및 지시 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
9edc6fae-4e29-42e4-a5c7-e65757cdcbde | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 11 of 41 ¦ 를 받아 시공하여야 한다. (2) 밸브의 사용구분에 대해서는 설계도면 또는 '2.2 배관재료'에 따른다. (3) 배관에 FLANGE 를 붙이는 것은 최소한으로 줄이고 도면에 기입되지 않은 것이 배관공사상 FLANGE 설치를 필요로 생각되는 경우는 발주 담당자와 협의 하여 FLANGE 설치 여부를 결정 토록 한다. (4) 배관 LINE 의 내압기밀 TEST 를 장치마다 행할 경우는 BLIND PATCH(맹판)를 사용해야 한다. (5) 내압 TEST 에 사용한 GASKET 은 TEST 이외에 재사용하여서는 안된다. (6) 매설배관과 지상배관과 의 경계는 지상높이 30cm 부분을 경계로 구분한다. (7) 맞대기 용접(BUTT WELD) 연결이 요구되는 자재는 BEVEL END 로 공급하여야 하며, BEVEL END 로 공급되지 않거나 PIPE 등을 절단하여 사용할 때는 절단면을 현장에서 BEVELING 하여야 한다. (8) 내화구조의 인정 및 관리기준(국토교통부고시 제 2018-772 호)에 따른 내화충전구조로 인증된 방법 및 재료로 충진한다. (9) 방화구획 관통부에서 배관 용접부를 1m 이상 이격하여야 한다. (단, 1m 이내에 용접부가 불가피할 경우 발주 담당자의 승인을 받아야 한다.) (10)수배관은 유체흐름 방향으로 균등한 기울기 또는 상향기울기로 시공하며, 역기울기 및 공기 차기 등 순환을 저해 할 우려가 없도록 시공하여야 한다. (11)진동이 있는 기기의 드레인 배관은 배수관에 연결 시 진동이 차단되도록 시공하여야 한다. (12)배관의 플랜지, 용접 접합부는 용접 및 유지보수에 지장이 없도록 PIPE RACK 으로부터 이격하 여야 한다. (13)상시 드레인이 필요한 배관은 집수정 및 FLOOR DRAIN 으로 유도하여야 한다. (14)배관 접합 시 각 배관의 seam 은 90° 이상 엇갈리게 접합한다. (15) 압력계, 온도계 등의 계기류는 점검자의 동선에서 확인이 가능 하도록 한다. (16)Flexible Joint 설치방법은 첨부-3 의 기준을 적용한다. 3.1.4 금긋기 작업 흠집을 내면 못쓰게 되는 재료에는 정, 각인, 센터 펀치 등을 사용해서는 안된다. 3.1.5 배관 설치 기준 (1) 관의 절단 ① 관의 배관 길이를 정확하게 잰 후 축선에 직각이 되도록 절단하고, 절단 시 관경이 축소되 거나 도금 또는 도복강재의 칠이 벗겨질 수 있는 절단기기 및 공구류 등은 사용하지 않는다. ② 주관과 일정한 각도를 가지고 접합하는 관 끝은 절단 각도에 주의 해서 절단한다. ③ 소재의 절단면은 지정한 것 이외에는 축과 수직으로 한다. ④ 절단면에 요철, 홈, 슬래그의 부착 등이 있을 때에는 수정하거나 떨어내어야 한다. SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
65b27ce2-a063-49ec-9401-67b448f0ce12 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 12 of 41 ¦ ⑤ PIPE 는 지정된 PIPE CUTTER 를 사용하여야 하며, 절단 내면을 깨끗이 처리하여야 한다. (2) 절단부위의 처리 모든 관의 절단부위는 매끈하게 축선과 직각으로 평면이 되도록 다듬질한다. 3.1.6 나사내기 (1) PIPE 에 가공하는 나사는 PT(Pipe Threaded)나사로 한다. 필요 할 경우 발주 담당자의 승인을 받아 KS B 0203 관용 TAPER 나사로 할 수도 있다. (2) 나사접속은 원칙적으로 SEAL TAPE 을 사용하여야 한다. (3) 나사접속 후 SEAL 용접을 행하는 것은 윤활재, SEAL TAPE 을 사용하지 말 것. (4) SCREWED FITTING 의 끼우는 길이는 규정된 길이로 하고, 나사접속 후 나사부에 여분의 나사 가 2 산 또는 3 산으로 한다. (5) 싸이폰밸브와 압력게이지 설치시 싸이폰밸브 파손 우려가 있어, 육안으로 확인하여 Leak 가 없도록 조여야한다. 3.1.7 교정작업 소재 또는 조립된 부재의 변형은 각 공정에서 재질을 손상하지 않도록 교정한다. 3.1.8 볼트 이음 (1) 조립 작업 ① 마찰면을 보호하기 위한 주의 를 요하며 녹, 기름, 도료, 먼지 등 마찰력을 저하시키는 이물질 을 제거한다. ② 이음부는 먼저 마찰면을 밀착시킨 후 볼트로 조인다. ③ 가조립 후 볼트구멍이 서로 맞지 않을 때에는 수정하고 이음부에 부착된 찌꺼기 등은 깨끗 하게 제거한 후 조립한다. ④ 수직배관 볼트 체결 시에는 볼트 머리가 아래쪽으로 향하도록 체결하고, 수평배관의 경우 유 체의 흐름 반대방향으로 볼트 머리가 향하도록 한다. (단, 시공이 부득이한 경우에는 시공이 가능한 방향으로 체결한다.) (2) 볼트 조이기 ① 플랜지체결은 '18154D-CJ-G00-HV-A00-00170 플랜지체결공사'에 의한다. ② 나사산 완전체결 후 여장길이는 최소 3 산~체결 BOLT 지름의 1.5 이하로 한다. ③ 같은 플랜지에 체결되는 볼트/너트는 동일한 볼트/너트를 사용하여야 하며 같은 여장길이를 가져야 한다. ④ 스터드 볼트의 경우 동일한 플랜지에 양쪽으로 볼트의 길이가 동일한 길이가 나오도록 체결 하여야 한다. ⑤ 볼트의 I 마킹대상 및 기준은 '18154D-CJ-G00-HV-A00-00170 플랜지체결공사'를 참조한다. SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
6d31d110-b5e0-4370-8be0-09ffef4e0ce1 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 13 of 41 ¦ 3.1.9 배관 BRANCH 적용 및 FITTING 사용 (1) 300A(12") 이하의 구경에서 SHORT RADIUS ELBOW 를 사용할 시 발주 담당자의 승인을 받고 사용하여야 한다. (2) 유체 수송용 50A(2") 이상 배관의 VENT 혹은 DRAIN POCKET 부분은 VENT 및 DRAIN VALVE 를 설치하여야 한다. 기체 수송용 배관에도 필요할 경우 DRAIN 을 설치한다. (3) 각종 구동체에 접속되어 있는 저온(-20°C~-80°C) 배관에는 KS M 6617(방진고무용 고무재료) 로 성형한 네오프렌재질의 FLEXIBLE CONNECTOR 및 금속 FLEXIBLE CONNECTOR 를 설치하며, 고온(MAX 220°C)의 배관에는 금속 FLEXIBLE CONNECTOR 를 설치한다. (성상, 온도, 압력조건 등에 따른 재질 및 타입은 설계도면에 따른다.) (4) FLEXIBLE CONNECTOR 는 운전 시 발생되는 순간 가진력에 의해 큰 변위가 발생되므로 CON- ROL ROD 와 BRACKET 을 설치하며, 진동에 의한 CONTROL ROD NUT 의 풀림을 방지하여 위하 여 풀림방지너트 또는 이중 너트를 적용한다. 3.1.10 관내의 점검, 청소 및 배관 끝의 보호 (1) 모든 관은 접합하기 전 관 내부를 점검하고 이물질이 없는가를 확인한 후, 금속 부스러기 등 이물질을 제거한다. (2) 배관작업을 마쳤을 때 또는 일시 배관작업을 중지할 때에는 배관 끝을 플러그 및 캡 등으로 완전히 막아 이물질이 들어가지 않도록 한다. (3) 수압시험 후 관의 내부를 FLUSHING 하여야 한다. 3.2 관의 접합 3.2.1 동종관의 접합 (1) 스테인리스 강관 ① 나사이음 접합용 나사는 KS B 0222 에 준한다. 접합할 때의 숫나사부에 사용하는 밀봉테이프 또는 충전 재료 등은 가능한 소량으로 하고 굳은 페인트 및 퍼티 등은 사용하지 않는다. 플랜지 접합 Gasket 은 두께 3.5mm 이하(Spiral Wound Gasket 은 5.0mm 이하)의 것을 사용하고, 관 내경과 일치하도록 플랜지 사이에 놓고 볼트를 균등하게 조인다. Gasket 의 양면에 소량의 충진제를 균등하게 얇게 바르는 것은 허용되나, 굳은 페인트 및 퍼티 등을 사용해서는 안된다. 3.2.2 이종관의 접합 이종관의 접합은 절연유니온, 절연플랜지를 사용하여 접합하여야 한다. hynix SK SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
24306897-8cc7-417d-b891-8e9d32a05034 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 14 of 41 ¦ 3.3 용접 공사 3.3.1 일반사항 시공자는 용접 공사와 관련된 사항에 대해 용접작업지침서의 작성 후 발주 담당자의 승인을 받아 진행 하도록 한다. 3.3.2 재료 준비 (1) 끝가공 모양은 재질, 모양 또는 사용방법에 의해 정하는 것으로 한다. (2) 끝가공은 원칙적으로 기계가공으로 한다. 끝가공면을 매끈하고 정확하게 마감하고 끝가공면 에 부착해 있는 슬래그는 완전히 제거하여야 한다. (3) 용접재료는 조심스럽게 취급하고 파손, 변질 및 녹이 발생한 것을 사용해서는 안된다. 3.3.3 모재의 청소 모재의 용접면은 용접하기 전에 녹, 스케일, 물기, 기름기, 슬래그, 도료 등 용접에 지장이 있는 것들을 제거한다. 3.3.4 용접 시공 요령 용접의 일반적 사양 및 요령은 설계도면에 특별한 지시가 없는 한 다음에 따른다. (1) 용접 후 용접부위의 위치를 시공도면에 반영한다. (2) 용접봉의 재질에 따른 물질안전보건자료(MSDS)를 용접봉 보관함에 부착한다. (3) 용접시 가접 POINT 는 최소한 3~4 개 이상으로 하며 각 POINT 간의 최소거리는 10mm 이상이 되게 실시한다. (4) 용접부간 최소거리(양쪽비드 내부)는 50mm 이상(소구경 부속의 경우 부품길이) 이격하여 열영 향부가 중복되지 않도록 하며, 중간에 단관이 설치되어서는 안되고 부득이하게 설치가 필요한 경우 발주 담당자와 협의 후 진행하여야 한다. (5) 현장내 모든 용접은 TIG 용접을 원칙으로 한다. (6) 용접기와 그 부속기구는 주어진 용접조건에 알맞은 구조 및 기능을 갖고 안전하게 용접할 수 있어야 한다. (7) 용접부는 결함이 없고 표면이 매끈하여야 한다. (8) 용접순서는 용접에 의한 변형 및 잔류응력이 작아지도록 정한다. (9) 용접작업 중에는 누전, 전격(��), 아크광 등에 의한 사고 또는 용융금속 아크 등에 의한 화 재 등을 방지하도록 조치하여야 한다. (10) 용접으로 유독가스가 발생할 우려가 있는 곳은 환기장치를 하여야 한다. (11)어스선은 직접 피용접물에 나사 CLAMP 등으로 확실하게 설치하여야 하며, 용접 모재 1m 이내 2 개소 체결을 원칙으로 한다 (12)용접부의 초층(Root Pass) 용접 시 반드시 Back Bead 가 형성되어야 한다. SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. SK ecoplant | {}
3fc4bc94-6b5e-45ff-acc4-639501d27e5d | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 15 of 41 ¦ (13)우천, 강풍 등 때문에 용접에 지장이 있다고 볼 경우 원칙적으로 용접을 해서는 안된다. 단, 충분한 보호조치를 하였을 경우에는 발주 담당자의 승인을 득한 후 용접할 수 있다. (14)용접부위는 충분히 청소를 행하여 녹, PAINT, 수분, 토사 등의 부착이 없도록 한다. (15)케이블이나 전력공급에 변화를 주는 경우 용접기 전원을 차단한다. (16)시공자는 전격쇼크의 위험이 있으므로 용접을 시행하고 있는 모재에 일정한 간격을 유지하여 개인안전에 주의 해야 한다. (17)용접 시 발생되는 아크나 자외선으로부터 몸을 보호할 수 있도록 개인 안전장구를 착용한 후 작업을 실시한다. (18)배관 정렬작업 시 어긋남이 발생하지 않도록 고정하며, 관의 각면을 수평계를 이용하여 골고 루 맞춘다. 비틀림 발생 시 고무망치와 지그를 이용하여 정렬하며, 가접전에 PURGE 를 실시한 다. (19)배관의 FITTING 부 내부는 특히 용접보의 떨어짐 등이 없도록 주의 하여 시공하고, 발생한 부 착물은 가능한 제거해야 한다. (20) 전기 및 계장 CABLE TRAY 부근에서 용접 또는 화기 작업 시에는 CABLE 을 손상하지 않도록 보호한 후 시행해야 한다. (21)특수한 배관(수지계, 고무, 유기 등의 배관 및 라이닝관) 또는 방폭지역 내에서 용접 및 화기 작업 시에는 반드시 발주 담당자의 승인을 득한 후 화기, 충격 등에 대한 충분한 준비를 갖추 고 시행하여야 한다. (22)배관 가공 및 종료 후 PURGE 하지 않을 경우는 먼지 및 오염물을 최소화하기 위해 끝단에 CAP 처리를 한다. (23)모재 온도가 영상 10°C 미만일때는 용접 부위를 10°C 이상으로 예열 처리를 하여야 한다. (24)보관용 용접 홀더는 PVC 케이스를 사용 한다. 3.3.5 홈내기 가공 (1) 홈내기 가공은 원칙적으로 기계가공으로 한다. 홈내기 면은 매끈하게 마무리하고 홈내기면에 부착되어 있는 찌꺼기는 완전하게 제거한다. (2) 용접작업에는 모재의 베벨각과 루트패스 간격 등에 현저한 오차가 없도록 하여야 한다. (3) 베벨각과 루트패스 간격 등의 기준은 용접작업지침서에 규정하여 발주담당자의 승인을 받는다. 3.3.6 용접공사의 종류 (1) 스테인리스 강관 용접 ① TIG Manual Welding -, 스테인리스 강관의 용접은 불활성 가스 용접 방식인 TIG 용접을 행하며, 내면을 불활성 가 스로 충전시켜 대기의 영향을 받지 않도록 한다. SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
8a55895a-c89c-4d24-800f-936c6fbdf080 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 16 of 41 ¦ -. 원칙적으로 TIG 용접은 GAP 을 벌려 용접한다. 스테인리스 강관의 용접은 전극을 마이너스(-)에 접속하여야 한다. - PURGE GAS 는 Ar, N2 둘 다 사용 가능하며, 사전에 발주 담당자와 현장여건에 맞는 가스 및 순도를 협의 하여 사용한다. 3.3.7 용접 후의 검사 (1) 용접부의 외관은 표면의 슬래그가 확실하게 제거되어야 하고 용접부의 외관은 목측(또는 필 요 시 측정공구에 의해서 측정)으로 보아 결과 는 다음과 같아야 한다. 관경두께의 차이에 의한 관외면의 엇갈림 -. h ≤ 0.5t, 최대 4mm 이하 ![image](/image/placeholder) UNDERCUTTING : 두께의 1/4T 이하 또는 1.0mm 이하 UNDERCUT 은 허용범위 내의 수치로 되어도 NOTCH 가 잔존하지 않도록 그라인더 등으로 평탄하게 사상 할 것. -. 사상 후에 관두께가 최저 두께 이하로 되지 않도록 할 것. OVERLAP : 90° 이하 (배관과 용접 BEAD 의 각) WELDING RREINFORCEMENT(용접 덧살) 두께 ¦ 6mm ¦ 이하 ¦ : 3.0mm 이하 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 6mm ~ ¦ 13mm : 3.0mm ¦ 이하 ¦ ¦ 13mm ~ 25mm ¦ : 4.0mm ¦ 이하 ¦ ¦ 25mm ¦ 이상 : 5.0mm ¦ 이하 ¦ 3.4 지지 및 고정 3.4.1 U-BOLT 및 HANGER ROD 규격 (스테인리스 강관) 、 15A ~ 100A : M9 125A ~ 600A : M12 3.4.2 배관의 SUPPORT 배관의 SUPPORT 는 될 수 있는대로 공동 PIPE RACK 을 만들어 사용하며, 이는 STEEL STRUCTURE DWG.를 기준 한다. 공동 PIPE RACK 에서 벗어나는 배관은 KS B 1527(파이프 서포트) 규격에 적합 한 밴드형 파이프 행거로 HANGING 또는 바닥에서 TRUNNION 을 사용하여 받쳐 주도록 한다. 이때 CONTROL VALVE 등 추후 MAINTENANCE 로 해체가 필요한 부위는 TRUNNION PIPE 사이 hynix SK SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
0bc14e84-544d-4887-9549-3af34d575efc | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 17 of 41 ¦ 에 FLANGE PLATE 를 만들어 해체에 대비하며, FLANGE 사이에 NEOPRENE PAD(20t)를 설치하고 FLANGE 까지 보온한다. (1) 배관의 지지 간격 * 지상층 배관 행거 고정 시 반드시 12m 이내에 1 개소 이상 �형강, L 형강 보강 할 것. 배관의 지지 간격은 공동 PIPE RACK 에서는 최소거리를 기준하여 설치하도록 하며, 간격 및 개소는 설계도면에 명시되어 있지 않으면 아래의 표를 따른다. ¦ 구 분 ¦ 배관 종류 및 관경 ¦ 최대 지지간격(mm) ¦ 비 고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 입상배관 ¦ 탄소 강관 및 스테인리스 강관 100A 이하 125A ~ 150A 200A ~ 250A ~ 450A 300A 500A 이상 ¦ 층별 2 개소 지지 6M 이상 8M 이상 10M 이상 12M 이상 14M 이상 단, 층당 최소 1 개소는 배관지지가 되어야 함 ¦ ¦ ¦ 횡주배관 ¦ 스테인리스 강관(KS D 3576) 20A (3/4") 이하 25A (1") ~ 40A (1.1/2") 50A (2") ~ 80A (3") 100A(4") ~ 150A (6") 200A (8") 이상 ¦ 1,800 2,000 3,000 4,000 5,000 ¦ ¦ ¦ 횡주배관 ¦ 스테인리스 강관(KS D 3595) 20A (3/4") 이하 25A (1") ~ 40A (1.1/2") 50A (2") 65A(2.1/2") ~ 100A (4") 125A (5") 이상 ¦ 1,000 1,500 2,000 2,500 3,000 ¦ 화장실 적용 ¦ * 배관 SHAFT 등과 같이 수평배관에서 입상배관으로 바뀌는 ELBOW 부위는 입상배관 자중에 의한 처짐을 방지하기 위해 지지간격과 별도의 추가보강을 하여야 한다. * 공통 PIPE RACK 배관 중 지지간격을 벗어나는 관은 중간보강을 하여야 하며 현장여견을 반영한 시공상세도를 제출하여 발주 담당자의 승인을 득한 후 시공하여야 한다. SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
c4785f55-1801-4d40-a9bd-c716dfa5fa2c | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 18 of 41 ¦ * 지상층 배관 행거 고정 시 반드시 12m 이내에 1 개소 이상 �형강, L 형강 보강 할 것. (내진 설계 Guide Line 기준에 따른다.) (2) TRUNNION 의 규격 장비에서 나와 입상하는 배관이나 밸브류 하부에는 방진 지지대 또는 TRUNNION 을 설치하 여야 한다. ¦ PIPE SIZE (mm) ¦ TRUNNION SIZE (mm) ¦ PIPE SIZE (mm) ¦ TRUNNION SIZE (mm) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 50 ¦ 40 ¦ 350 ¦ 200 ¦ ¦ 65 ¦ 50 ¦ 400 ¦ 200 ¦ ¦ 80 ¦ 50 ¦ 450 ¦ 200 ¦ ¦ 100 ¦ 80 ¦ 500 ¦ 250 ¦ ¦ 125 ¦ 100 ¦ 550 ¦ 250 ¦ ¦ 150 ¦ 150 ¦ 600 ¦ 300 ¦ ¦ 200 ¦ 150 ¦ 650 ¦ 300 ¦ ¦ 250 ¦ 150 ¦ 700 ¦ 350 ¦ ¦ 300 ¦ 150 ¦ 750 ¦ 400 ¦ * 상기 표에서 벗어나는 SIZE 는 발주 담당자의 확인을 받은 후 작업한다. * PLATE 의 두께는 12mm 이상으로 적용한다. Chart Type: line Min. 50 Min. 25 item_01 0Minutes 25Minutes [그림] FLANGE PLATE, BASE PLATE 제작도 * MAINTENANCE 를 필요로 하는 부위의 TRUNNION FLANGE PLATE 설치는 아래의 그림 참조 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
7f01b7ba-9be0-42f9-aec6-b5262cdf9cc2 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 19 of 41 ¦ ![image](/image/placeholder) 20K 밸브/플랜지 ST'L PLATE � FLANGE PLATE TRUNNION 등 0 NEOPRENE PAD BASE PLATE SETTING BOLT MIN. 10⌀ 음 RUBBER PAD 3.4.3 배관 방진 (1) 공동 PIPE RACK 은 진동이 건축 구조물에 전달되어서는 안되는 지역에서는 방진을 사용하여 PIPE RACK 과 건축 구조물의 진동 전달을 방지하여야 한다. ![image](/image/placeholder) INSULATION PIPE PIPE SHOE SPRING RUBBER MOUNT ST'L BEAM or CHANNEL [그림] PIPE RACK 및 방진 설치 상세도 - 수평배관 SK hynix SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
9ab59f08-d09b-452f-ac4c-102e282e89d3 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ ENGINEERING DESIGN SPECIFICATION ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 Page 20 of 41 ¦ ¦ --- ¦ --- ¦ --- ¦ ![image](/image/placeholder) 입상배관 입상배관 방진 CLAMP 방진 CLAMP 입상관 방진 SPRING MOUNT 방진 ANCHOR �-형강 or H-BEAM �-형강 or H-BEAM [그림] PIPE RACK 및 방진 설치 상세도 - 입상배관 (1) 방진은 전문 업체에 의뢰하여 계산·선정하며, 발주 담당자의 승인을 득한 후 설치하여야 한다. 3.4.4 PIPE SHOE (1) 보온 및 보냉이 필요한 배관에는 KS B 1527(파이프 서포트) 규격의 슬라이더형 PIPE SHOE 를 사용하며, 그 적용범위나 방법은 첨부 - 2 의 기준으로 적용 한다. 3.5 배관의 변위 흡수장치 3.5.1 신축이음부를 통과 하는 배관 등은 쌍방의 건물에 생기는 최대 상대변위량을 흡수할 수 있는 배관의 횡성을 이용, 또는 변위 흡수관 이음쇠를 사용한다. 3.5.2 지반의 형상이 불안정하고 건축물과 지반 사이에 변위가 생길 우려가 있는 건축물 인입부의 배관 등에는 변위 흡수 조치를 행한다. 3.6 배관 SLEEVE 설치 공사 콘크리트 구조물을 통과 하는 배관에는 SLEEVE 를 시공하여야 하며, SLEEVE 는 콘크리트 타설 전에 설 치하여야 한다. 특히 기밀이 요구되는 콘크리트 수조 등의 펌프 흡입배관 등 LEAK 우려가 있는 부 분 등에는 SLEEVE 의 FIXED PLATE 와 콘크리트 속의 철근과 사전에 용접 시공되어야 하므로 필히 선 작업되어야 한다. (단, 변경 등으로 인하여 후시공 하는 경우 일반형 콘크리트 관통형에 한하여 구조 물 외부에 FIXED PLATE 를 설치하여 SLEEVE 와 용접하여 ANCHOR 로 고정한다.) 또한 SLEEVE 의 설치 후 개구부 철판 막음 등 안전 관리 방안을 수립, 적용하여 SLEEVE 개구부를 관리 토록 한다. (첨부-1 기준 적용) hynix SK SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
25caa4a8-bda5-4342-a856-723bacca426e | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 21 of 41 ¦ 3.6.1 배관 매입형-수조 등( SLEEVE 및 FIXED PLATE 의 재질은 설계도면에 따름 - 사각 or 원형) ![image](/image/placeholder) WELDING 필요시 용접연결 BOLT 체결 TOOL SPACE 필요 타 방수층 FIXED PLATE 콘크리트 MIN. 50 VAL. MIN. 50 L Chart Type: line O.D B A item_01 2.5Not specified 1.5Not specified 0.5Not specified ¦ PIPE SIZE (mm) ¦ FIXED PLATE "A" X THK ¦ "B" (mm) ¦ PIPE SIZE (mm) ¦ FIXED PLATE "A" X THK ¦ "B" (mm) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 50 ¦ 210 X 4.5t ¦ 75 ¦ 300 ¦ 525 X 4.5t ¦ 100 ¦ ¦ 65 ¦ 225 X 4.5t ¦ 75 ¦ 350 ¦ 605 X 4.5t ¦ 125 ¦ ¦ 80 ¦ 240 X 4.5t ¦ 75 ¦ 400 ¦ 655 X 4.5t ¦ 125 ¦ ¦ 100 ¦ 265 X 4.5t ¦ 75 ¦ 450 ¦ 710 X 4.5t ¦ 125 ¦ ¦ 125 ¦ 340 X 4.5t ¦ 100 ¦ 500 ¦ 760 X 4.5t ¦ 125 ¦ ¦ 150 ¦ 370 X 4.5t ¦ 100 ¦ 550 ¦ 860 X 4.5t ¦ 150 ¦ ¦ 200 ¦ 420 X 4.5t ¦ 100 ¦ 600 ¦ 910 X 4.5t ¦ 150 ¦ ¦ 250 ¦ 475 X 4.5t ¦ 100 ¦ 650 ¦ 960 X 4.5t ¦ 150 ¦ hynix SK SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
deac69b3-43a5-4f8e-95fb-597836498e22 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 22 of 41 ¦ 3.6.2 일반형 (콘크리트 관통형) ![image](/image/placeholder) WELDING SEALANT SEALANT FIXED PLATE 콘크리트 MIN. 50 VAL. MIN. 50 L [ 콘크리트 타설 전 시공 ] ![image](/image/placeholder) FIXED PLATE SEALANT WELDING SEALANT SEALANT 콘크리트 ANCHOR MIN. 50 VAL. MIN. 50 L [ 콘크리트 타설 후 시공 ] ¦ PIPE SIZE (mm) ¦ SLEEVE SIZE (mm) ¦ FIXED PLATE "A" X THK ¦ "B" (mm) ¦ PIPE SIZE (mm) ¦ SLEEVE SIZE (mm) ¦ FIXED PLATE "A" X THK ¦ "B" (mm) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 50 ¦ 65~80 ¦ 225 X 4.5t ¦ 75 ¦ 300 ¦ 350 ¦ 605 X 4.5t ¦ 100 ¦ ¦ 65 ¦ 80~100 ¦ 240 X 4.5t ¦ 75 ¦ 350 ¦ 400 ¦ 655 X 4.5t ¦ 125 ¦ ¦ 80 ¦ 100~125 ¦ 265 X 4.5t ¦ 75 ¦ 400 ¦ 450 ¦ 710 X 4.5t ¦ 125 ¦ ¦ 100 ¦ 125~150 ¦ 340 X 4.5t ¦ 75 ¦ 450 ¦ 500 ¦ 760 X 4.5t ¦ 125 ¦ ¦ 125 ¦ 150~200 ¦ 370 X 4.5t ¦ 100 ¦ 500 ¦ 550 ¦ 860 X 4.5t ¦ 125 ¦ ¦ 150 ¦ 200 ¦ 420 X 4.5t ¦ 100 ¦ 550 ¦ 600 ¦ 910 X 4.5t ¦ 150 ¦ ¦ 200 ¦ 250 ¦ 475 X 4.5t ¦ 100 ¦ 600 ¦ 650 ¦ 960 X 4.5t ¦ 150 ¦ ¦ 250 ¦ 300 ¦ 525 X 4.5t ¦ 100 ¦ 650 ¦ 700 ¦ 1,010 X 4.5t ¦ 150 ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
1c55aed6-ff25-4a83-a936-3e686aeda795 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 23 of 41 ¦ 3.7 배관 부식방지 3.7.1 배관 · 장비 · 구조물 등을 고정 · 조립 할 경우 전위부식방지를 위하여 동일한 재질의 재료를 사용하여야 하고, 최대한 이종금속 사용을 배제하여야 하며 꼭 이종금속을 사용해야 하는 경우 는 전위부식방지를 위해 절연플랜지 또는 절연 볼트/ 너트/ 와셔등을 사용하는 적정한 조치를 취하여야 한다. 3.7.2 콘크리트 등 바닥위에 구조물 또는 장비를 설치할 경우에는 구조물 또는 장비의 부식방지를 위하여 콘크리트 등 바닥 구조물 또는 장비 사이에 RUBBER PAD 를 설치하여 시공한다. 3.7.3 부식방지를 위하여 볼팅을 하거나 나사못과 같은 것으로 조립작업 등을 할 경우 나사못 또는 이와 유사한 것과 철판 등의 피조립물 등 사이에 RUBBER PAD 를 설치한다. 3.7.4 장비 또는 구조물 등을 콘크리트 등 바닥에 고정할 경우 SET ANCHOR 등 고정물과 구조물 또는 장비는 같은 재질의 볼트와 너트를 사용하여 부식을 방지한다. 3.7.5 용접부위는 특히 부식에 취약하므로 충분한 조치를 하여 부식을 방지하도록 한다. 3.8 시공 허용오차 3.8.1 현장 시공오차 최소화방안 (1) 배관 시공 시 정확한 시공을 위해 시공 기준선(레이져, 먹선 등)을 활용한다. (2) 설계도면(Shop 도면)과 현장시공 오차 ¦ 구 분 t ¦ 구 분 t ¦ 오차 한� ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ F02 P ¦ F02 P ¦ 土 5 ¦ ¦ E03 ¦ F04 CI IR 드 ¦ 7 ¦ 3.9 배관 세척공사 3.9.1 세척 방법의 선정 세척 방법은 관내의 유체 종별, 관 재료 및 내면상태를 고려하여 발주 담당자와 협의 한다. 3.9.2 물 세척 방법 (1) 세척 용수 물 세척은 원칙적으로 상수 또는 잡용수(공업용수 등)를 사용하여 행하고 해수를 사용하지 말 것. SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
9d3387b3-f82e-41f4-b9b6-1129af821b71 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 24 of 41 ¦ (2) 세척 횟수 ① 전체 세척 : 1 회 이상 ② 부분 세척 : 2 회 이상 (3) 세척 요령 ① 물의 압력 및 햄머링을 병행하여 유출 시키거나, 관에 물을 채워 일시에 배출 시킬 것. ② 부분 세척은 배관을 적당히 분할하여 제작한 PIECE 로 적용하고, 전체 물 세척이 부적당한 부분은 압축공기를 불어 넣어 관 내부를 청소 할 것. ③ 전체 물세척 시 배관중 자동제어 기기가 있는 경우는 원칙적으로 자동제어 기기를 떼어내고 대신 단관을 붙여 행할 것. ④ 세척은 스트레이너에 이물질이 부착하지 않는 상태가 될 때까지 시행할 것. ⑤ 세척 후 관내는 압축공기에 의한 건조 또는 자연 건조를 행할 것. 3.10 시험(TEST) 및 검사 3.10.1 배관 압력 기밀 시험 (1) TEST 용 유체 내압 TEST - TEST 용 유체는 원칙적으로 물을 사용하며, 이 경우 공업용수 또는 상수로 한다. -. 0°C 이하의 기온조건에서는 원칙적으로 물을 사용해서는 안된다. 또한, GAS(공기, 질소 등), OIL, 후레온 등을 사용하는 경우는 발주 담당자와 협의 하여야 한다. 기밀 TEST ~ 기밀 TEST 의 최고 사용압력은 배관 기기(VALVE, FLANGE) 압력 RATING 이하로 하며 각 부분의 TEST 압력은 첨부-4 TEST 압력 기준을 적용한다. (2) TEST 범위 일반사항 -. TEST 를 할 배관 LINE 이 BATTERY LIMIT 외의 배관과 연결되어 있는 경우에는 VALVE 또 는 BLIND PLATE,CAP 으로 완전히 차단 할 것. -. TEST 를 할 배관 LINE 과 차단하는 것이 부적당한 경우에는 TEST 조건을 발주 담당자와 협의 하여 결정 한다. (3) TEST 준비 안전한 TEST 를 위해 할 일 1. 열팽창에 대해 고려 할 것. : TEST 지역을 구획 할 것. -. Hanger and Support 확인 할 것. ~ 기.수압 TEST 시 Relief Valve 를 설치 할 것. hynix SK SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
160fc661-cbca-4fe9-b90a-2ca961e495bb | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 25 of 41 ¦ ② 기기와 연결된 배관은 기기와 분리하여 TEST 하는 경우 개방된 배관의 부분에 그 배관의 압력 RATING 에 일치하는 BLIND FLANGE 를 설치한다. 배관을 FLANGE 접속 개소에서 분리하여 TEST 하는 경우는 그 FLANGE 접속사이에 BLIND PATCH 를 삽입한다. (BLIND PATCH 의 최소 두께는 발주 담당자의 승인을 득한 후 시행하여 야 한다.) TEST 용에 사용하는 삽입 BLIND PATCH 에는 필히 외측에 손잡이를 달고 적색도료를 칠하여 그 외의 BLIND PATCH 와 확실히 식별가능 하도록 할 것. TEST 용에 사용된 일체의 BLIND PATCH 및 BLIND FLANGE 의 LIST 를 작성하여 START-UP 에 앞서 제거하였는가를 확인 할 것. SUPPORT 및 HANGER ~ 운전 시 배관의 내압 TEST 를 위해 지지가 필요한 경우에는 임시 SUPPORT 를 설치한다. -. SPRING HANGER 로 지지하여 있는 배관은 SPRING 의 NECK 이 SET 되어 있는가를 확인한다. ⑥ VENT ~ 일체의 배관 및 기기에는 공기를 완전히 제거하기 위한 VENT 를 적절하게 설치 할 것. -, VENT 의 위치는 그 LINE 의 최고부분에 공기 VENT, 최저부에 DRAIN 을 설치 할 것. 압력계 -. 압력계 사용기준은 기.수압 TEST 시 해당 압력의 1.5~2 배의 압력 눈금의 게이지를 사용하 여야 하며, 예비 기,수압 게이지도 본 기.수압 기준과 동일하게 적용한다. -. TEST 용 압력계 설치 시 발주 담당자의 승인 후 설치한다. -. 압력계는 검교정을 받은 압력계를 사용하되 해당성적서를 제출 한다. - 게이지 설치위치는 가능한 배관 TEST 부분의 최고부와 최저부 2 개소에 설치하고 배관 최 대 압력이 걸리지 않는 곳으로 할 것. 단, 10m 미만의 배관에 대해서는 1 개소에 설치한다. 기,수압 테스트는 고압용 호스 및 이탈 방지와 이어로 체결 한다. 기타 - TEST 시 가압용 장비, 안전밸브, VENT, DRAIN 밸브 등이 설치된 곳은 안전구역으로 설정 하여 일반인의 출입을 통제하여야 한다. -. 기.수압 TEST 구간에 자재 및 구성품(VALVE 및 FLANGE 등)이 있을 경우에는 자재 및 구 성품의 설계압력 이하로 기.수압 TEST 를 시행한다. -. 긴 시간 동안 수압 TEST 를 하는 경우 온도 변화를 고려해야 한다. 예를 들어 차가운 시수 를 이용할 경우 배관 안에 물이 따뜻해져서 생기는 열팽창을 고려하거나, 수압 TEST 전에 차가운 시수가 주변온도까지 상승 할 때 까지 기다린 후 TEST 한다. -. CHECK VALVE 가 있는 배관은 압력원을 그 전단에 설치 할 것. -. LEAK TEST 시 반드시 압력을 나타내는 게이지가 표시된 사진을 촬영하여 제출 할 것. 、 TEST 완료 후에는 인체에 위험을 가져오거나 기기에 손상을 입히지 않도록 VALVE 를 서서 히 열어 감압 시킬 것. 、 TEST 완료 후 일체의 배관 및 기기로부터 완전히 배출(기체, 액체) 시킬 것. SK hynix SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
3ee4b1ea-3f8a-4ca1-8103-fccbfe307488 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 26 of 41 ¦ -. 기압시험 후에는 해당 배관의 세척을 실시하여야 한다. 一, 배관 세척 후에는 습기에 의한 내부 부식방지를 위하여 발주 담당자가 지정하는 유체로 PURGE 하여야 한다. - 기타 특수한 현장 여건상 발생되는 제반 문제는 발주 담당자의 지시에 따른다. -. AIR TEST 에서 사용압보다 10% 크거나, TEST 압 + 3.5kgcm2 중 적은 값으로 SETTING 된 RELIEF VALVE 를 설치해야 한다. 단, 안전을 위해 AIR TEST 이후 반드시 RELIEF VALVE 를 제거하여야 한다. -. TEST 압력이 규정압력 이상으로 승압되지 않도록 필히 압력 정지용의 VENT 를 설치 할 것 3.10.2 기록 TEST 기록은 TEST 기간 중 일체의 TEST LINE 에 관해 주의 하여 기록, 보관 할 것. (1) TEST 기록의 기재 항목 TEST 의 적용범위와 사양 ② 승압 방법 및 사용 기준 ③ TEST 압력 및 유지시간 ④ TEST 유체 성분 ⑤ TEST 일자 ⑥ TEST 의 시공 책임자명 3.10.3 검사 검사는 배관 공사의 각 사양의 내용에 기준하여 각각의 기준서에 따른다. 3.11 배관 표식 '18154D-CJ-G00-HV-A00-00191 APPENDIX- I (눈 관리 STICKER)' 참조 - End of Document - SK hynix SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
c9b2071c-3423-42e3-a12d-129f15333666 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 27 of 41 ¦ ¦ 첨부-1 ¦ 공종명 ¦ 공조배관공사 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 슬리브 막음 설치기준 ¦ 슬리브 막음 설치기준 ¦ 슬리브 막음 설치기준 ¦ ¦ 구 분 ¦ 상부 보양 + 내부 보강 적용(안) ¦ 상부 보양 + 내부 보강 적용(안) ¦ 상부 보양 + 내부 보강 적용(안) ¦ 상부 보양 + 내부 보강 적용(안) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 100A 이하 미적용 ¦ * Sleeve 제작 : 강관 (KS D3507) * 상부 보양 : PVC 배관 캡 * 내부 보강 : 미적용 미적용 ¦ 125A 물 250A 이적을 ¦ ¦ 이상 괴정지점 ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ * Sleeve 제작 : 2.0t 이상 강판 (SS400) or 강관 (KS D3507) + 내부 보강 (규격별) [* KS 기준 강관 적용 시 보강 제외 / 3.0t 이상, 900A 이상 보감 적용] * 상부 보양 : 2.0t 이상 강판 (SS400) + 상부 보강 (규격별) [* 3.0t 이상 강판 적용 시 600A 이상 적용] * 적용 상부철판 (솔리브의 정+00mm-20mm) 철근 10mm 규 격 이상 ⌀H ⌀H ¦ ¦ 125A 이상 ¦ ¦ ¦ ¦ ¦ ¦ 125A 이상 ¦ ¦ ¦ ¦ ¦ ¦ 125A 이상 ¦ ¦ ¦ ¦ ¦ ¦ 125A 이상 ¦ 상부 보강 (A) [상부 보강 예시] 300A M SSDA 철근 10mm 400A - 850A ¦ ¦ 내부 보강 (B) 미적용 ¦ ¦ ¦ 125A 이상 ¦ 상부 보강 (A) [상부 보강 예시] 300A M SSDA 철근 10mm 400A - 850A ¦ ¦ ¦ ¦ ¦ 125A 이상 ¦ 상부 보강 (A) [상부 보강 예시] 300A M SSDA 철근 10mm 400A - 850A ¦ ¦ ¦ ¦ ¦ 125A 이상 ¦ 900A M 1500A B ¦ 156 - 200 구경 시 적정배치 ¦ 3 줄 ¦ ¦ ¦ 125A 이상 ¦ 900A M 1500A B ¦ ¦ ¦ ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
90f0134c-2969-40e8-9bff-f80bb514f94e | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 28 of 41 ¦ ¦ 첨부-2 ¦ 공종명 ¦ 공조배관공사 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 증기, 증기응축수(SS,SR,PSR FAB) SHOE ¦ 증기, 증기응축수(SS,SR,PSR FAB) SHOE ¦ 증기, 증기응축수(SS,SR,PSR FAB) SHOE ¦ ¦ 관경 (A) ¦ 가이드슈 ¦ 앙카슈 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ ~ 100A ¦ 해법 상품명 Gt 단속옮김 (다프행정) 배관과 SHOE 의 �김한 단속출입으로 실시하며 출판길이는 30mm 이탈, 올립관리한 50mm 이하로 하되 * L1 은 부제폭+ 100 이상 SHOE 땡꿀 부위 融合 바깥쪽 름이 명도록 한다. PLATE (6T) 10DA 이하 하) 6t X L1 ¦ ●접 STEEL PLATE R PLATE (BT) ¦ ¦ 125A ~ 150A ¦ STEEL PLATE 혈 수 가이드 6t ⑥ 단속종합 (다르엘괴) 御 배관과 SHOE 의 동일은 단속종법으로 실시하며 충법길비는 30mm 떠날, 충법관리한 50mm 삐하로 하되 SHOE 일곤 부위 출입한 바깥쪽 종이 명도록 한다. * L1 촌 부가목+100 극장 PLATE (9T) 125 ~ 150A 하) 9t X L1 ¦ PLATE 9t STEEL PLATE (9T) ¦ ¦ ¦ ¦ ¦ ¦ 300A ~ 550A ¦ STEEL PLATE GL: 단속용법 (다프홍집) STEEL PLATE 9t 종접 . ⌀ 배관과 SHDE 의 충잡은 단속중입으로 김치하며 올집길이는 30mm 떠달, 출입관리한 50mm 이하로 하되 SHOE 열곱 부위 銀 바깥쪽 쯤이 명도록 한다. L1 촌 부제목+100 이창 PLATE 상) 6t X L1 300 rv 550A � 월 하) 9t X L1 ¦ STEEL PLATE 秋 STEEL PLATE 9t 해법 PLATE ¦ ¦ 600A ~ 750A ¦ STEEL PLATE 81 단속용법 (다프콜리) STEEL PLATE 12t 캘리 비 배관과 SHOE 의 � 단속중입으로 집시하며 흥법길비는 30mm 파장, 흥법관객관 50mm 피해도 하되 ¦ STEEL PLATE 8 STEEL PLATE 12t 창업 具 8 ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
5fd2e0b6-4e77-4c6e-9a99-cb8b155afdfc | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 29 of 41 ¦ ¦ 첨부-2 ¦ 공종명 ¦ 공조배관공사 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 냉수 (CHS, CHR FAB) SHOE 1 ¦ 냉수 (CHS, CHR FAB) SHOE 1 ¦ 냉수 (CHS, CHR FAB) SHOE 1 ¦ ¦ 관경 (A) ¦ 가이드슈 ¦ 앙카슈 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ ~ 100A ¦ STEEL BAND 3.2t STEEL BAND 3TCUB,FAB 피하대 해당) 볼트(9mm) ·니호프렌 20t (CUBFAB 지하에 해당) 네오프린 20t STEEL PLATE 3.24, 왕(구의 EPDM 9t(그외) 병원 # L2 는 부재 사이즈 이상열 몇. PUNTE 円 실) 3.2t X L2 100A 이하 하) 6t X L2 ¦ STEEL PLATE 6t 용접 준비전학적,200) ※ 3.00 주세관만하되 PLATE (6T) ¦ ¦ 125A ~ 150A ¦ BAND 3.21 THE SUBJICUB,FAB 지하에 해당) 널드(9mm) 네오프렌 20t {CUB,FAB 피하에 해당) EPON 맑(그외) EPCM 명(구역) STEEL PLATE 4.5t -STEEL PLATE 9t 서울 기업드 6L ■ l 는 부패 사이즈 이상열 것. PLATE (91) 상) 4.5t x L2 125 ~ 150A 하) 9t x L2 ¦ STEEL PLATE 0t 非目 보존재 손박점짜리 ,200 냉수비 광단해요 PLATE (91) 12 ¦ ¦ ¦ -5TEEL BAND 3.2t WWW.YOUBUELFAB 피하의 해당) 볼트(9mm) EPDM 9t(그외) 네오프렌 20t (CUB,FAB 지하데 해당) EPDW 9t/그외 STEEL PLATE 4.5t STEEL PLATE 康 ¦ STEEL PLATE R ¦ ¦ 300A ~ 550A ¦ STEEL BAND 3.2t 客 TCUB,FAB 지하에 해당) 3. 않는 네오프렌 20t (CUB,FAB 지하에 해당) 볼트(9mm) EPON 알고의 EPQM 91(그역) 내오프렌 20t CUB,FAB 지하에 해당) EPOM 20t[ 그의 네오프렌 20t (CUB,FAB 피하에 해당) STEEL PLATE 찰 STEEL PLATE 91 EPON 20t(그외 수 가이드 Bt E * L2 는 부재 사이즈 이상열 것. PLATE (9T) 삶> 6t X L2 300 ~ 550A 하) 9t X L2 ¦ STEEL PLATE 하 STEEL PLATE 9t 발포 보존재 출진 (복수배관만해당) -홍집 보존재(은바김지식,20t) (냉수비권만해당) PLATE (9T) ¦ ¦ 600A ~ 750A ¦ STEEL BAND 3.2t CCUB,FAB 지하에 해당) 내오프린 20t (CUB,FAB 지하데 해당) EPON St(그의) 설트(9mm) EPDM 9t(그외) 네오프린 20t (CUB,FAB 지하에 허용) EPDM 20t(그의) 네오프렌 20t (CUB,FAB 피하의 해당) STEEL PLATE 81 STEEL PLATE 12t EPOM 20t(그외) A 가벼드 6L ¦ 難 野 Bt STEEL PLATE 121 별모 해법 (봉수배관민해당) 보훈제(은바라틱틱 .20t) (내소비과 메디) ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
b8718e7c-3014-4574-9771-534ad7498bca | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 30 of 41 ¦ ¦ 첨부-2 ¦ 공종명 ¦ 공조배관공사 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 냉수 (CHS, CHR FAB) SHOE 2 ¦ 냉수 (CHS, CHR FAB) SHOE 2 ¦ 냉수 (CHS, CHR FAB) SHOE 2 ¦ ¦ 800A ¦ 네로프린 20t (CUB,FAB 피하에 해당) EPDM 20t(그의 STEEL BAND 9t BAND 9t 네오프린 20t (CUB,FAB 피하에 해당) STEEL EPCM 20t(그의) N16 � STEEL PLATE 121- STEEL PLATE 12t 내호프런 20t (CUB,FAB 피하헤 해당) EPCM 20t(그외) STEEL PLATE 12t CUIDE 12t not Mack orral PLATE (12T) * L2 는 부재 시미즈 이상열 것. ¦ ① 융합 STEELPLATE-12+ STEEL PLATE 12t 물건 (봉수비관민해당) (전액일약식,40t) (냉수배관민해당) nce ammer⌀i PLATE (12) ¦ ¦ 900A ¦ STEEL BAND 9t 내오프렌 20t (CUB,FAB 지하해 해당)↘ EPOM 20t(그의 STEEL BAND 9t- 네오프렌 20t (CUB,FAB 지하에 해당) EPDM 20t(그외) M16 교 STEEL PLATE 12ト STEEL PLATE 12t 너오프렌 20t (CUB,FAB STEL 12t- EPON 201(그의) □ GUIDE 12t ¦ 山 충전 PLATE 12)- STEEL 중인 STEEL PLATE 12t : (보수배관민해당) 용접 -보존재(선택접학식,40) (냉수배관한해당) ¦ ¦ 1,000A ¦ 니오프렌 20t (CUBFAB 지하해 해당) STEEL BAND 9t EPON 201(그외) STEEL BAND 9t. 세오프맨 20t (CUB,FAB 지하에 해당) EPDM 20t(그외) M16 STEEL PLATE 121- STEEL PLATE 12t 네일프렌 20k 피하에 해당) EPDM 201⌀5g GUB, FAB QJ GUIDE 12t STEEL PLATE 12t- ind⌀ater and PLATE (12T) · L2 는 부패 사비즈 의창열 것. ¦ ① 입원 민족들의 121 STEEL PLATE 12t 보은재 (봉수배관단해당) 보존재(존박점식 4,401) (냉수배관단해당) NO - PLATE (12T) 의 ¦ SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant SK | {}
c0b11c64-bd39-49b5-9048-a7dda01f94b4 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 31 of 41 ¦ 첨부-2 공종명 공조배관공사 ¦ ¦ 냉수 (CHS, CHR FAB) SHOE 3 ¦ ¦ --- ¦ --- ¦ ¦ 네오프렌 201 (CUB,FAB 피하의 해당) BAND � EPDM 20t(그외 STEEL BAND 9t ·내오프렌 20t (CUB,FAB/ 지하여 해당) EPDM 20t(그외) M16 STEEL PLATE 12t STEEL PLATE 12t 1,100A 네오프렌 20t 피하레 해당) EPDM 20103GUB,FAB STEEL PLATE 12t □ GUIDE 12t BACK - (12T) ¦ STEEL 용접 STEEL PLATE 12L 발모 보존재 촉진 STEEL PLATE 121 (실수배관민해당)용접 보존재(완벽김지식,40%) (냉수배관안해당) MOXINAGOVIAN PLATE * L2 는 부패 시미즈 이상의 것. FRE 120 ¦ ¦ 1,200A ¦ 내오프벤 20t (CUB,FAB 지하에 해당) EPDW 20t(그역) STEEL BAND 91- STEEL BAND 네오프린 20t (CUB,FAB/피하에 해당) EPOM 20t(그의 M16 4 용접 STEEL PLATE 12)- STEEL PLATE 12t P 노래시티 12t- STEEL PLATE 12L (냉수세관만해당) � 네오프렌 20t (CUB,FAB 피하데 해당) AURE 1 차 보존계(한색접착식,40%) - 1 로 EPIPM 20t(그외) STEEL PLATE 12I- ¦ ¦ 1,300A ¦ 네호프면 20t (CUB,FAB 기하해 해당) EPCM 20%(그의) STEEL BAND 91- 내오므렌 20t 지하해 해당) STEEL BAND 9t EPDW 20L/20/SUBLFAB/ M16 19 康 종접 STEEL PLATE 1 차 STEEL PLATE 12t- -STEEL PLATE 12t 발포 보존재 충전 STEEL PLATE 121 (냉수배관단배당)옮김 내용관련 201CK CUBJFAB 지하에 해당) STEEL PLATE 12t M GUIDE 12t 보훈제(은바법칙칙,40t) (내수세권판해당) mack ⌀thersod to of BACK (SMINK YOOK12:00 * L2 는 부찌 사이즈 이상열 것. 미 ATE (12T) PLATE (12门 ¦ SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. SK ecoplant | {}
4d64cb6b-c5e0-4533-9f9c-11fa8e8ad6ce | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 32 of 41 ¦ ![image](/image/placeholder) 첨부-2 공종명 공조배관공사 냉수(CHS, CHR FAB) SHOE 4 내호프렌 20t (CUB,FAB 지하데 해당)- EPON 20%(그외) STEEL BAND/9t STEEL BAND 9t ·내오브랜 20t (CUB/FAB 피하에 해당) EPDM 20t(그외) M16 종별 1,500A STEEL PLATE 12t- STEEL PLATE 121- STEEL PLATE 12t 필포 보완해 홍진 STEEL PLATE 12t 남주 배관민해당 내오므렌 20t (CUB,FAB 지하예 해당) 접 EPOW 20t(그외) STEEL PLATE 12t GUIDE 12t 보존재(완익흡학식,40t 住 1 월 (보수배관민해당) PHOKORDOM:134201 MC - U+ HAIT AI·LAI 네호프렌 20t 지하해 해당) EPCM 2000L/SUBFAB STEEL BAND STEEL BAND 9t 네오프렌 201 (CUB,FAB 피하해 해당) EPDM 20t(그외) M16 1,600A STEEL PLATE 12t. STELPLATE 1 같힌 STEEL PLATE 12t STEEL PLATE 12 (봉수배관민해당) 네포프렌 20t (CUB,FAI 네오프렌 20t 지하에 해당) EPDM 201/5g FAB STEEL PLATE 12H 전기 20t(그외 보존재(연택접피식,40t) GUIDE 12t (영수배관안마당) RACK:57003300mm:3mm BACE OFFICTION TRACED - SK hynix SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
240e4117-781a-4893-b30b-6aafde7fec2c | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 33 of 41 ¦ ¦ 첨부-2 ¦ 공종명 ¦ 공조배관공사 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 폐열회수(RHWS, RHWR) SHOE ¦ 폐열회수(RHWS, RHWR) SHOE ¦ 폐열회수(RHWS, RHWR) SHOE ¦ ¦ 관경 (A) ¦ 가이드슈 ¦ 앙카슈 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ ~ 100A ¦ STEEL BAND 3.2t STEEL BAND 321 볼트(9mm) ·니호프렌 20t (CUB,FAB 지하에 해당) 네오프린 20t (CUB,FAB 피하대 해당) EPDM 91(그의) STEEL PLATE 3.24, 0 알(금외) STEE 6L # L2 는 부재 사이즈 이상일 몇. PATE(IT) 상) 3.2t x L2 100A 이하 하) 6t X L2 ¦ STEEL PLATE 6t 똥집 진 학적,20t) 냉주세관만하되 PLATE (6T) ¦ ¦ 125A ~ 150A ¦ STEEL BAND 3.21 THE SUBICUB,FAB 지하에 해당) 널드(9mm) 917-0UB,FAB 지하에 해당) EPON 맑(그외) 네오프렌 20t EPDM 0 STEEL PLATE 4.5t STEEL PLATE 9t 역 최우 ■ 8 12 는 부패 사이즈 이상열 것 PLATE (9T) 상) 4.5t x L2 125 ~ 150A 하) 9t x L2 ¦ STEEL PLATE Bt #집 보존재 손박점착칙,201) 냉수배경단에요) PLATE (91) 12 ¦ ¦ ¦ -STEEL BAND 3.2t WWW.YOUBLFAB 피하에 해당) 볼트(9mm) EPQM 9t(그외) ·네오프렌 20t (CUB,FAB 지하데 해당) EPDM 9t(그외 STEEL PLATE 4.5t STEEL PLATE gt ¦ STEEL PLATE 9 ¦ ¦ 300A N 550A ¦ ·STEEL BAND 3.2t 3. (CUB,FAB 지하에 하유) 않는 20% 네오프렌 20t (CUB,FAB 지하에 해당) 블트(9mm) EPQM %(구역) EPON 알고의 내오프렌 20t CUB,FAB 지하의 해당) EPOM 20t(그의) 네오프렌 20t (CUB,FAB 피하에 해당) STEEL PLATE 찰 STEEL PLATE 91 EPOW 20t(그외) ■ 수 가이드 Et -⌀ * L2 는 부재 사이즈 이창열 것. PLATE (9T) #> 6t x L2 300 ~ 550A 하) 9t x L2 ¦ STEEL PLATE Bt STEEL PLATE 또 발포 보존재 충진 (복수배관말하당) 옮김 보존재(은복점 1 일,20t) (냉수비관만해당) PLATE (9T) ¦ ¦ 600A ~ 750A ¦ -STEEL BAND 3.2t 또는 37CUB,FAB 지하에 해당) 내코므렌 20t (CUB,FAB 지하데 해당) EPON 맑(그의) 월드(9mm) EPDM 9t(그외) 네오프린 20t (CUB,FAB 지하에 해당) EPCM 20t(그의 네오프린 20t (CUB,FAB 피하에 해당) STEEL PLATE 81 STEEL PLATE 12t EPDM 20t(그외) ■ 좀 가벼드 61 ¦ 출입 입문제 PLATE Bt STEEL PLATE 12L 발모 2 용접 (봉수배관민해당) 보온제(은바리믹직,20t) MAH 리메디) ¦ SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. SK ecoplant | {}
879852f6-56c3-409d-ae62-9fcb3dbdb612 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 34 of 41 ¦ 첨부-2 공종명 공조배관공사 ¦ 급탕 환탕 (DHWS, DHWR) SHOE ¦ 급탕 환탕 (DHWS, DHWR) SHOE ¦ 급탕 환탕 (DHWS, DHWR) SHOE ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 관경 (A) ¦ 가이드슈 ¦ 앙카슈 ¦ ¦ ~ 100A ¦ ·STEEL BAND 3.2t ·내오프렌 20t (CUB,FAB 지하에 해당) STEEL BAND 3.2t 볼트(9mm) EPOM %(그의) 네오프렌 20t (CUB,FAB 지하에 해당) EPDM 9t(그외) STEEL PLATE 3.2t- -STEEL PLATE 6t 수 가이드 타 록 0 용접 * L2 는 부재 사이즈 이상열 것. PLATE (6T) 상) 3.2t X L2 100A 이하 하) 6t X L2 ¦ STS PLATE 3.2t 절연볼트(9mm) 용접 네오프린 20t 지하에 해당] 3L/그회(CUB,FAB STEEL PLATE 3.2t- EPDM STEEL PLATE 6t t 의 PLATE (6T) ¦ ¦ 125A ~ 150A ¦ STEEL BAND 3.2t STELBAND 37CUB,FAB 지하에 해당) 볼트(9mm) 네오프렌 20t (CUB,FAB 지하에 해당) EPDM 9t(그외) EPDM 91(그외 STEEL PLATE 4.5t STEELPLATE 9t 6t 응집 ¦ STS PLATE 3.2t 응집 PLATECINSCUB,FAB 피하에 해당) 절연볼트(9mm) 네오프렌 20t STEEL PLATE 4.5t EPOM STEEL 용접 ¦ SK hynix SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
c3fd6497-a734-4654-8053-a13afd790426 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 35 of 41 ¦ ¦ 첨부-2 ¦ 공종명 ¦ 공조배관공사 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 시수,정수 등(CW, IW,NPW,PCW, CD,WSS) SHOE ¦ 시수,정수 등(CW, IW,NPW,PCW, CD,WSS) SHOE ¦ 시수,정수 등(CW, IW,NPW,PCW, CD,WSS) SHOE ¦ ¦ 관경 (A) ¦ 가이드슈 ¦ 앙카슈 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ ~ 100A ¦ STEEL BAND 3.2t -STEEL BAND 321 볼트(9mm) 니호프렌 20t (CUBFAB 지하에 해당) 네오프린 20t (CUB,FAB 피하대 해당) EPDM 9t(그외) STEEL PLATE 3.2 앞□의 병원 GL ■ # L2 는 부재 사이즈 이상열 몇. PUNTE 円 상) 3.2t X L2 100A 이하 하) 6t X L2 ¦ STEEL PLATE 6t 용접 준비전학적,200) ※ 3.00 냉주세관만하되 PLATE (6T) ¦ ¦ 125A ~ 150A ¦ BAND 3.21 발생 3. CUB,FAB 지하에 해당) 널드(9mm) ·네오프렌 20t {CUB,FAB 피하에 해당) EPON 맑(그외) EPCM 9(구역) STEEL PLATE 4.5t -STEEL PLATE 9t 기회드 61 최우 ■ l 12 는 부패 사이즈 이상열 것 PLATE (9T) 상) 4.5t x L2 125 ~ 150A 하) 9t x L2 ¦ STEEL PLATE 0t 番目 (손녁점지식,201) 보존재 배광안에요 PLATE (91) 12 ¦ ¦ ¦ -5TEEL BAND 3.2t WWW.YOUBLFAB 피하에 해당) 볼트(9mm) EPOM 9t(그외) 네오프렌 20t (CUB,FAB 지하에 해당) EPDW 9t/그외 STEEL PLATE 4.5t STEEL PLATE 항 ¦ STEEL PLATE R ¦ ¦ 300A ~ 550A ¦ STEEL BAND 3.2t 8 37CUB,FAB 지하에 해당) 네오프렌 20t (CUB,FAB 지하에 해당) 볼트(9mm) EPDM 「명(그역) EPDN �고의 내오프렌 20t CUB,FAB 지하에 해당) EPOM 20t[ 금액 네오프린 20t (CUB,FAB 피하에 해당) STEEL PLATE な STEEL PLATE 91 EPON 20t(그외) [ ⌀ 수 가이드 Bt E · L2 는 부재 사이즈 이상열 것. PLATE (9T) 상) 6t X L2 300 ~ 550A 하) 9t X L2 ¦ STEEL PLATE it STEEL PLATE 9t 발포 보존재 출진 (복수배관만해당) 콩집 보존재(은바김지식,20t) (냉수비권만해당 PLATE (9T) ¦ ¦ 600A ~ 750A ¦ STEEL BAND 3.2t Not 7CUB,FAB 지하에 해당) 내오프렌 20t (CUB,FAB 지하데 해당) EPON 앞(그의) 설트(9mm) EPOM 9t(그외) 네오프린 20t (CUB,FAB 지하에 허용) EPDM 20t(그의 네오프렌 20t (CUB,FAB 피하의 해당) STEEL PLATE 히 STEEL PLATE 12t EPOM 20t(그외) 가벼드 61 ¦ 출범 입찰해 PATE Bt. STEEL PLATE 121 별모 용법 (봉수배관민해당) 보은제(은바리 학칙 .20t) (내소비과 메디) ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
738bd1e5-8ac6-47d0-86b9-af416f984717 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client SK hynix Date : 25.JAN. 2022 ¦ ENGINEERING DESIGN SPECIFICATION ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 Page 36 of 41 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 첨부-3 ¦ 공종명 ¦ 공조배관공사 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Flexible Joint 설치기준 ¦ Flexible Joint 설치기준 ¦ Flexible Joint 설치기준 ¦ ● Flexible 종류 및 특성 ¦ 구분 ¦ Rubber Flexible joint ¦ SRJ(Rubber Pump Connector) ¦ TPC (Tied Pump Conector) ¦ FJT (Flexible Hose pump Connector) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Image ¦ ¦ ¦ ¦ ¦ ¦ 배관재질 ¦ PE&PVC 배관 ¦ PE 배관 ¦ Steel(STS,SPP)배관 ¦ STS 배관 ¦ ¦ 사용처 ¦ UPW,Water ¦ 폐수 ¦ 냉각수,냉수,PCW ¦ ¦ ¦ 허용온도 ¦ 80°C ¦ 80°C ¦ 220°C ¦ 220°C ¦ ¦ 특징 ¦ 고무 재질로 방지,방음 효과 가 우수 신장,압축 편심 허용량이 크다 Tie-Rod 사용으로 추력 손상방지 ¦ 고무 재질로 방지,방음 효과 가 우수 신장,압축 편심 허용량이 크다 Tie-Rod 사용으로 추력 손상방지 ¦ 多겹 벨로우즈 사용하여 내구성 우수 Barid 미 사용으로 진동 차단 효과 우수 Tie-Rod 사용으로 추력 손상 방지 비금속 Washer 사용 마 찰 소음 최소화 ¦ Matal Bellows 사용으로 내구성 우수 Barid 사용을 추력에 의 한 벨로우즈 손상방지 ¦ · Rubber Flexible Joint Tie Rod 설치방법 ![image](/image/placeholder) oa ①인장 상단부는 인장부와 압축부를 �압축 설치 값으로 맞추고 너트를 DETAIL 고정한다. い K 고정 하단부는 풀림방지 조치한다 8 2 (편심 x) (편각 a) SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
7110a740-cb06-4eb3-a457-61247a2cbe70 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 37 of 41 ¦ ¦ 첨부-3 ¦ 공종명 ¦ 공조배관공사 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Flexible Joint 설치기준 ¦ Flexible Joint 설치기준 ¦ Flexible Joint 설치기준 ¦ SRJ(Rubber Pump Connector) Tie Rod 설치 방법 ![image](/image/placeholder) PIPING 육각너트 COUNTER FLANGE 절대로 풀지 마십시오. TIE ROD HOLDER 육각너트 저대균 표 TI 미시시오 배관죽의 직진도가 맞지 않은 싱 를 설치할 경우에는 펌프 콘넥터 수명이 감소 TPC(Tied Pump Conector) Tie Rod 설치 방법 ![image](/image/placeholder) 0 & 0 0 ( (0 Flange Bolt Hose 를 정확히 및 콘넥터에 비틀림이 발생하여 수 ![image](/image/placeholder) Q ⑤ ![image](/image/placeholder) PIPING COUNTERFLANGE 풀림방지너트 셋트클립 플리스틱 별 셋트바 TIERO 플라스틱 제품설치 제품설치후 (운전하기전) 배관축의 직진도가 맞지 않은 상태에서 Flexible 를 설치할 경우 Flexible 에 편심이 발생하여 수명 감소 ![image](/image/placeholder) 폴랑방지네트 절대로 풀지 마십시오. 제품설치전,후 (운전하기전) ![image](/image/placeholder) ① ���� 0 0 Q 0 SK hynix Flange Bolt Hose 를 정확히 및 Flexible 에 비틀림이 발생하여 ![image](/image/placeholder) 0 S 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. SK ecoplant | {}
ff50ddab-c4cd-4439-8bad-6520df2d0830 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 38 of 41 ¦ ¦ 첨부-4 ¦ 공종명 ¦ 공조배관공사 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 설비배관 기,수압 기준 ¦ 설비배관 기,수압 기준 ¦ 설비배관 기,수압 기준 ¦ ¦ 기수압기준 ¦ 기수압기준 ¦ 기수압기준 ¦ 기수압기준 ¦ 기수압기준 ¦ 기수압기준 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 공종 ¦ Item(구분) ¦ Utility ¦ 적용기준 ¦ 적용기준 ¦ 적용기준 ¦ ¦ 공종 ¦ Item(구분) ¦ Utility ¦ 기압 ¦ 기압 ¦ ¦ ¦ 공종 ¦ Item(구분) ¦ Utility ¦ 압력(kgf/cm2) ¦ 시간(hr) ¦ 압력 ¦ ¦ 공조배관 ¦ 냉수 ¦ CHS/R ¦ 3 ¦ 0.5 ¦ 8 ¦ ¦ 공조배관 ¦ 냉각수 ¦ CWS/R ¦ 3 ¦ 0.5 ¦ 8 ¦ ¦ 공조배관 ¦ 온수 ¦ HWS/R ¦ 3 ¦ 0.5 ¦ 8 ¦ ¦ 공조배관 ¦ 시수 ¦ CTW ¦ 3 ¦ 0.5 ¦ 8 ¦ ¦ 공조배관 ¦ 급탕 ¦ DHWS/R ¦ 3 ¦ 0.5 ¦ 8 ¦ ¦ 공조배관 ¦ 공정냉각수 ¦ PCWS/R ¦ 3 ¦ 0.5 ¦ 8 ¦ ¦ 공조배관 ¦ DCC 냉수 ¦ DCWS/R ¦ 3 ¦ 0.5 ¦ 8 ¦ ¦ 공조배관 ¦ 증기/응축수 ¦ SS/SR(3 kgf/cm2 이상) ¦ 1.1 X 사용압력 ¦ 6 ¦ ¦ ¦ 공조배관 ¦ 증기/응축수 ¦ SS/SR(3 kgf/cm2 미만) ¦ 4 ¦ 6 ¦ ¦ ¦ 공조배관 ¦ 보일러 보급수 ¦ BFW ¦ 3 ¦ 0.5 ¦ 8 ¦ ¦ 공조배관 ¦ 공업용수 ¦ IW ¦ 3 ¦ 0.5 ¦ 8 ¦ ¦ 공조배관 ¦ 중수 ¦ NPW ¦ 3 ¦ 0.5 ¦ 8 ¦ ¦ 공조배관 ¦ 폐열회수 ¦ RHWS/R ¦ 3 ¦ 0.5 ¦ 8 ¦ ¦ 공조배관 ¦ 장비배수 ¦ CD ¦ ¦ ¦ ー ¦ SK hynix SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
d22907cf-b3b2-4628-9076-fb72a1d94c42 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 39 of 41 ¦ ¦ 첨부-5 ¦ 공종명 ¦ 공조배관공사 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 설비배관 배관재질 ¦ 설비배관 배관재질 ¦ 설비배관 배관재질 ¦ ¦ 종류 ¦ 규격 ¦ 사용구분 ¦ 사용구분 ¦ 비고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 종류 ¦ 규격 ¦ 냉수(CHS/R), 냉각수(CWS/R), 온수(HWS/R), 공업용수(IW), 공업용수(IPW) to UPW, 장비배수(CD), 재활용수(NPW), 폐열회수(RHWS/R), 팽창(E) ¦ 증기(SS), 증기응축수(SR) ¦ 비고 ¦ ¦ 탄소강관 ¦ KS D 3507 ¦ 15A ~ 600A (SPP+GALV.) ¦ 5kg/cm2 이하(SPP) ¦ SPW 400, KS D 3583, SAW BE, GALV. 650A 이하 ST'D 700A ~1,200A : 9.5T 1,300A 1,500A : 12.7T 1,600A~1,800A : 16.0T ¦ ¦ 탄소강관 ¦ KS D 3562 ¦ - ¦ 6~10kg/cm2 (SPPS380) ¦ SPW 400, KS D 3583, SAW BE, GALV. 650A 이하 ST'D 700A ~1,200A : 9.5T 1,300A 1,500A : 12.7T 1,600A~1,800A : 16.0T ¦ ¦ 탄소강관 ¦ KS D 3583 ¦ 600A above (SPW400+GALV.) ¦ 600A above (SPW400) ¦ SPW 400, KS D 3583, SAW BE, GALV. 650A 이하 ST'D 700A ~1,200A : 9.5T 1,300A 1,500A : 12.7T 1,600A~1,800A : 16.0T ¦ ¦ 도복장강관 ¦ KS D 3565 ¦ - ¦ - ¦ ¦ ¦ 스테인리스강관 ¦ KS D 3576 ¦ - ¦ - ¦ ¦ ¦ 스테인리스강관 ¦ KS D 3588 ¦ 、 ¦ - ¦ ¦ ¦ 폴리에틸렌 피복강관 ¦ KS D 3589 ¦ - ¦ - ¦ ¦ ¦ 가스용 강관 ¦ KS D 3631 ¦ - ¦ - ¦ ¦ ¦ 가스용 폴리에틸렌 관 ¦ KS M 3514 ¦ - ¦ - ¦ ¦ ¦ 수도용 폴리에틸렌 관 ¦ KS M 3408 ¦ - ¦ - ¦ ¦ ¦ 고밀도 폴리에틸렌 관 ¦ - ¦ 냉수(CHS/R), 공업용수(IW) 지중 매설 ¦ - ¦ ¦ ¦ 단열 이중보온관 ¦ - ¦ - ¦ - ¦ ¦ ¦ 일반용 경질 폴리염화비닐관 ¦ KS M 3404 ¦ - ¦ - ¦ ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
28d65b8b-6191-4a06-987e-2b3c915a3ce8 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 40 of 41 ¦ ¦ 첨부-5 ¦ 공종명 ¦ 공조배관공사 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 설비배관 배관재질 ¦ 설비배관 배관재질 ¦ 설비배관 배관재질 ¦ ¦ 종류 ¦ 규격 ¦ 사용구분 ¦ 사용구분 ¦ 사용구분 ¦ 비고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 종류 ¦ 규격 ¦ 공정냉각수(PCWS/R), 급수(CTW), 급탕(DHWS/R) ¦ 오수(S), 배수(D), 통기(V) ¦ 광역상수도 ¦ 비고 ¦ ¦ 탄소강관 ¦ KS D 3507 ¦ - ¦ - ¦ - ¦ SPW 400, KS D 3583, SAW BE, GALV. 650A 이하 ST'D 700A ~1,200A : 9.5T 1,300A 1,500A : 12.7T 1,600A~1,800A : 16.0T ¦ ¦ 탄소강관 ¦ KS D 3562 ¦ - ¦ - ¦ - ¦ SPW 400, KS D 3583, SAW BE, GALV. 650A 이하 ST'D 700A ~1,200A : 9.5T 1,300A 1,500A : 12.7T 1,600A~1,800A : 16.0T ¦ ¦ 탄소강관 ¦ KS D 3583 ¦ ¦ - ¦ - ¦ SPW 400, KS D 3583, SAW BE, GALV. 650A 이하 ST'D 700A ~1,200A : 9.5T 1,300A 1,500A : 12.7T 1,600A~1,800A : 16.0T ¦ ¦ 도복장강관 ¦ KS D 3565 ¦ - ¦ - ¦ STWW ¦ ¦ ¦ 스테인리스강관 ¦ KS D 3576 ¦ 15A ~ 300A (STS304 TP)- ¦ - ¦ - ¦ ¦ ¦ 스테인리스강관 ¦ KS D 3588 ¦ 300A above (STS304 TPY)) ¦ - ¦ - ¦ ¦ ¦ 폴리에틸렌 피복강관 ¦ KS D 3589 ¦ - ¦ - ¦ - ¦ ¦ ¦ 가스용 강관 ¦ KS D 3631 ¦ - ¦ - ¦ - ¦ ¦ ¦ 가스용 폴리에틸렌 관 ¦ KS M 3514 ¦ 、 ¦ 一 ¦ - ¦ ¦ ¦ 수도용 폴리에틸렌 관 ¦ KS M 3408 ¦ - ¦ - ¦ - ¦ ¦ ¦ 고밀도 폴리에틸렌 관 ¦ - ¦ 급수(CW) 지중 매설 ¦ - ¦ - ¦ ¦ ¦ 단열 이중보온관 ¦ - ¦ - ¦ - ¦ 내관:STWW / 외관:AL. ¦ ¦ ¦ 일반용 경질 폴리염화비닐관 ¦ KS M 3404 ¦ ¦ PVC VG1 ¦ ¦ ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
ad841b6b-8679-4c38-a7f2-f60a47f26272 | 21036D-IC-M16G00-HV-A00-00141 M16_Ph-2 시방서-급수·급탕 배관공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix ¦ ENGINEERING DESIGN ¦ 21036D-IC-M16G00-HV-A00-00141 Rev. 0 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Date : 25.JAN. 2022 ¦ SPECIFICATION ¦ Page 41 of 41 ¦ ¦ 첨부-5 ¦ 공종명 ¦ 공조배관공사 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 설비배관 배관재질 ¦ 설비배관 배관재질 ¦ 설비배관 배관재질 ¦ ¦ 종류 ¦ 규격 ¦ 사용구분 ¦ 사용구분 ¦ 사용구분 ¦ 사용구분 ¦ 비고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 종류 ¦ 규격 ¦ NG (도시가스) ¦ 재이용수 (RW) -WWT~ 저수조 ¦ 폐수(WASTE WATER) -DUCT(SOLVENT) DRAIN ¦ 폐수 (WASTE WATER) -SCR. & DUCT(HF) DRAIN ¦ 비고 ¦ ¦ 탄소강관 ¦ KS D 3507 ¦ - ¦ - ¦ - ¦ - ¦ SPW 400, KS D 3583, SAW BE, GALV. 650A 이하 ST'D 700A ~1,200A : 9.5T 1,300A 1,500A : 12.7T 1,600A~1,800A : 16.0T ¦ ¦ 탄소강관 ¦ KS D 3562 ¦ - ¦ - ¦ - ¦ - ¦ SPW 400, KS D 3583, SAW BE, GALV. 650A 이하 ST'D 700A ~1,200A : 9.5T 1,300A 1,500A : 12.7T 1,600A~1,800A : 16.0T ¦ ¦ 탄소강관 ¦ KS D 3583 ¦ ¦ ¦ ¦ - ¦ SPW 400, KS D 3583, SAW BE, GALV. 650A 이하 ST'D 700A ~1,200A : 9.5T 1,300A 1,500A : 12.7T 1,600A~1,800A : 16.0T ¦ ¦ 도복장강관 ¦ KS D 3565 ¦ - ¦ - ¦ - ¦ - ¦ ¦ ¦ 스테인리스강관 ¦ KS D 3576 ¦ - ¦ - ¦ STS304 TP ¦ - ¦ ¦ ¦ 스테인리스강관 ¦ KS D 3588 ¦ - ¦ - ¦ - ¦ - ¦ ¦ ¦ 폴리에틸렌 피복강관 ¦ KS D 3589 ¦ 중압 지중 매설 ¦ - ¦ - ¦ - ¦ ¦ ¦ 가스용 강관 ¦ KS D 3631 ¦ 노출배관 ¦ - ¦ - ¦ - ¦ ¦ ¦ 가스용 폴리에틸렌 관 ¦ KS M 3514 ¦ 저압 지중 매설 ¦ - ¦ - ¦ - ¦ ¦ ¦ 수도용 폴리에틸렌 관 ¦ KS M 3408 ¦ - ¦ PE ¦ ¦ PVC VG1(SUB), PE(MAIN) ¦ ¦ ¦ 고밀도 폴리에틸렌 관 ¦ - ¦ - ¦ ¦ - ¦ - ¦ ¦ ¦ 단열 이중보온관 ¦ - ¦ - ¦ - ¦ ¦ ¦ ¦ ¦ 일반용 경질 폴리염화비닐관 ¦ KS M 3404 ¦ - ¦ - ¦ - ¦ ¦ ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
e61aac23-df4b-4aa4-833f-d2926520d5ab | KSCIEC60364-5-52_KR | KSKSKSKS KS C IEC 60364-5-52 KSKSKSK KSKSKS KSKSK KSKS KSK K KS 저압 전기설비 - 제 5-52 부: 전기기기의 선정 및 설치 - 배선설비 KS C IEC 60364-5-52:2009 산 업 표 준 심 의 회 2024 년 7 월 31 일 개정 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
d7f4df1d-61f8-4d63-bdb5-e36fc5f3c522 | KSCIEC60364-5-52_KR | KSCIEC 60364-5-52:2009 심 의 : 전력기기 기술심의 회 성 명 근 무 처 직 위 (회 장) 홍 순 찬 단국대학교 교 수 (위 원) 김 재 철 숭실대학교 교 수 서 호 선 KR 지식재산법률사무소 대 표 심 대 섭 (주)정인시스템 연 구 소 장 이 주 철 (주)건일이엔지 연 구 소 장 전 기 중 (주)피디엔에스 전 무 박 현 주 한국전력공사 전력연구원 책 임 안 상 필 한국전기연구원 본 부 장 채 경 수 한국스마트의 료기기산업진흥재단 연 구 위 원 (간 사) 이 승 훈 국가기술표준원 표준정책국 전기전자정보표준과 공업사무관 원안작성협력 : 저압전기설비 전문위원회 성 명 근 무 처 직 위 (대표전문위원) 김 재 철 숭실대학교 교 수 (위 원) 민 찬 식 한국폴리텍대학(성남캠퍼스) 교 수 김 진 만 (주)한길이앤씨 소 장 송 인 권 슈나이더일렉트릭코리아 팀 장 주 강 필 SK 에코플랜트 프 로 안 준 호 서울대학교 전력연구소 책 임 김 영 석 한국전기안전공사 전기안전연구원 책 임 정 종 욱 CJ 이엔지 대 표 이 주 철 (주)건일이엔지 연 구 소 장 박 원 석 ABB 코리아 수 석 팀 장 신 성 수 대한전기협회 팀 장 (간 사) 이 준 선 대한전기협회 과 장 표준열람 : e 나라표준인증(http://www.srandiand.go.kr) 제 정 자 : 산업표준심의 회 위원장 담당부처 : 산업통상자원부 국가기술표준원 제 정 : 2002 년 10 월 29 일 개 정 : 2024 년 7 월 31 일 심 의 : 산업표준심의 회 전력기기 기술심의 회 원안작성협력 : 저압전기설비 전문위원회 이 표준에 대한 의견 또는 질문은 e 나라표준인증 웹사이트를 이용하여 주십시오. 이 표준은 산업표준화법 제 10 조의 규정에 따라 매 5 년마다 산업표준심의 회에서 심의 되어 확인, 개정 또는 폐지됩니다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
339d2f5a-76e4-4190-8e65-6427bc9b4a3a | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 목 차 머 리 말 .................................... III 개 요 ....................................... IV 520 개요 ................................... 1 520.1 적용범위 .................... 1 520.2 인용표준 ................. 1 520.3 용어와 정의 ................. 520.4 일반사항 ...................... 521 배선방식의 종류 ...................................... ························ 2 521.4 버스바트렁킹 시스템과 파워트랙 시스템 .................................3 521.5 교류회로 - 전기자기적 영향(맴돌이 전류 방지) ············· ····················· ······· ............ 3 521.6 전선관 시스템, 케이블덕팅 시스템, 케이블트렁킹 시스템, 케이블트레이 시스템 및 케이블래더 시스템 ·······················/ 521.7 하나의 다심케이블 속의 복수회로 ..................... 521.8 회로 구성 ................. 521.9 유연성 케이블 또는 코드의 사용 ................... 521.10 케이블의 설치 ................... 522 배선설비의 선정과 설치에 고려할 외적 영향 ............................ 522.1 주위온도(AA) .............. 522.2 외부 열원 .................. 522.3 물의 존재(AD) 또는 높은 습도(AB) ......................6 522.4 침입 고형물의 존재 (AE) ------- 522.5 부식 또는 오염 물질의 존재(AF) ................... 522.6 충격(AG) ·················· 6 522.7 진동(AH) ................. 6 522.8 그 밖의 기계적 응력(AJ) -------- 6 522.9 식물과 곰팡이의 ⌀ - - - - - 8 522.10 동물의 존재(AL) ............ ..... 522.11 태양 방사(AN) 및 자외선 MESSERVES 522.12 지진의 영향(AP) ······· 8 522.13 바람(AR) ............ ................. 522.14 가공물질 또는 보관자재의 ( 1861 - - - - - - - - 522.15 건축물의 설계(CB) ----- 523 허용전류 ....... 9 523.5 복수회로로 포설된 그룹 ---------- 10 523.6 부하 도체의 수 ······· 10 523.7 병렬도체 ------- 10 523.8 경로 중 시설조건 변화 ........ 11 523.9 금속 피복된 단심케이블 -------- 11 524 도체의 단면적 - 11 524.2 중성선의 단면적 ----- 12 -i- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단배포를 금합니다. | {}
4dd8b855-3416-479b-89e8-d94c5f2077cb | KSCIEC60364-5-52_KR | KS CIEC 60364-5-52:2009 525 수용자설비에서의 전압강하 --- 13 526 전기적 접속 -------- 13 526.8 다중선, 세선, 극세선 ターシー 14 527 화재 확산을 최소화하기 위한 배선설비의 선정과 시공 -------------------------------- 14 527.1 방화구획 내부에서의 주의 사항 ···················· 14 527.2 배선설비 관통부의 밀봉 ---------- 15 528 배선설비와 다른 공급설비와 의 접근 ····················· 16 528.1 다른 전기 공급설비와 의 ---------- 16 528.2 통신 케이블과 의 접근 ------- 16 17 528.3 다른 공급설비와 의 중국인화학생협검사무료비자기초등록번호가 529 청소 등 정비를 고려한 배선설비 선정과 설치....................... 17 부속서 A(규정) 설치 방법 ----- 18 부속서 B (참고) 허용전류 -------- 25 부속서 C (참고) 523 절 표의 간략화(예) ...........) 부속서 D (참고) 허용전류를 구하는 방식 .............. 부속서 E(규정) 고조파 전류가 평형 3 상 계통에 미치는 영향 .........................................53 부속서 F (참고) 전선관 선정 ...... 부속서 G(참고) 수용가설비에서의 전압강하 ..................2 부속서 H (참고) 병렬 케이블 배치 예 ················ 64 부속서 I (참고) 특정 국가에 해당되는 사항 ...................... 67 참고문헌 ························ -------- 72 KS CIEC 60364-5-52:2009 해 (- - -) -ii- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
e060ec58-3fb4-45c8-99e8-17d5ff6fd7dd | KSCIEC60364-5-52_KR | KS CIEC 60364-5-52:2009 머 리 말 이 표준은 산업표준화법 관련 규정에 따라 산업표준심의 회의 심의 를 거쳐 개정한 한국산업표준이다. 이에 따라 KS C IEC 60364-5-52:2009(2022 년 발행)는 개정되어 이 표준으로 바뀌었다. 이 표준의 내용 일부 또는 전부는 저작권법에 따른 보호대상이 되는 저작물이 될 수 있다. 이 표준의 내용 일부 또는 전부가 ISO · IEC 등에서 제정한 표준을 참고하여 제정 또는 개정된 경우, 해당 표준의 저작권을 보유하고 있는 ISO · IEC 등의 저작권 보호 규정 등에 따라 보호되어야 한다. 이 표준의 일부가 기술적 성질을 가진 특허권, 출원공개 이후의 특허출원, 실용신안권 또는 출원공개 후의 실용신안등록출원에 저촉될 가능성이 있다는 것에 주의 를 환기한다. 관계 중앙행정기관의 장과 산업표준심의 회는 이러한 기술적 성질을 가진 특허권, 출원공개 이후의 특허출원, 실용신안권 또는 출원공개 후의 실용신안등록출원에 관계되는 확인에 대하여 책임을 지지 않는다. KS C IEC 60364 시리즈는 "저압 전기설비"라는 공통 제목을 가지며, 모든 부의 목록은 IEC 웹사이트 에서 찾을 수 있다. -iii- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
d324bffa-e8e3-4ec2-a189-34aa92911291 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 개 요 이 표준은 2009 년 제 3 판으로 발행된 IEC 60364-5-52, Low-voltage electrical installations - Part 5-52: Selection and erection of electrical equipment - Wiring systems 를 기초로 기술적 내용 및 대응국제표 준의 구성을 변경하지 않고 작성한 한국산업표준이다. - iv - 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
50909933-eaed-4718-a3ea-8403c3f494dc | KSCIEC60364-5-52_KR | 한국산업표준 KS C IEC 60364-5-52:2009 저압 전기설비 - 제 5-52 부: 전기기기의 선정 및 설치 - 배선설비 Low-voltage electrical installations - Part 5-52: Selection and erection of electrical equipment - Wiring systems 520 개요 520.1 적용범위 이 표준은 배선설비의 선정 및 설치를 다루고 있다. 비고 1 이 표준은 일반적으로 보호도체에도 적용하지만 보호도체에 대한 자세한 요구사항은 KS C IEC 60364-5-54 에 기술되어 있다. 비고 2 이 표준에 관한 권장 지침(Guidance)은 KS C IEC 61200-52 에 실려 있다. 520.2 인용표준 다음의 인용표준은 전체 또는 부분적으로 이 표준의 적용을 위해 필수적이다. 발행연도가 표기된 인 용표준은 인용된 판만을 적용한다. 발행연도가 표기되지 않은 인용표준은 최신판(모든 추록을 포함) 을 적용한다. KS C IEC 60228, 절연 케이블용 도체 KS C IEC 60287-2-1, 전기 케이블-전류정격 계산 - 제 2-1 부: 열 저항 - 열 저항 계산 KS C IEC 60287-3-1, 전기 케이블 - 정격 전류의 계산 - 제 3-1 부: 동작 조건 - 표준 동작 조건과 케이블 유형의 선정 KS C IEC 60332-1-1, 화재 조건에서 전기/광섬유 케이블 시험 - 제 1-1 부: 단심 절연 전선 또는 케이 블 수직 불꽃 전파 시험 - 시험장치 KS C IEC 60332-1-2, 화재 조건에서 전기/광섬유 케이블 시험 - 제 1-2 부: 단심 절연 전선 또는 케이 블 수직 불꽃 전파 시험 - 1 kW 혼합 불꽃 시험 절차 KS C IEC 60364-1:2005, 저압 전기설비 - 제 1 부: 기본 원칙, 일반 특성평가 및 용어 정의 KS C IEC 60364-4-41:2005, 저압 전기설비 - 제 4-41 부: 안전을 위한 보호 - 감전에 대한 보호 KS C IEC 60364-4-42, 저압 전기설비 - 제 4-42 부: 안전을 위한 보호 - 열 영향에 대한 보호 KS C IEC 60364-5-54, 저압 전기설비 - 제 5-54 부: 전기기기의 선정 및 설치 - 접지설비 및 보호도 체 및 결합도체 KS C IEC 60439-2, 저전압 개폐장치 및 제어장치 부속품 - 제 2 부: 버스바트렁킹 시스템의 개별 요구 사항 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. 1 | {}
4181979d-16d3-4dff-b773-9fedb9dbaf37 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 KS C IEC 60449, 건축전기설비의 전압밴드 KS C IEC 60502(모든 부), 정격전압 1 kV~30 kV 압출성형 절연 전력케이블 및 그 부속품 KS C IEC 60529, 외함의 밀폐 보호등급 구분(IP 코드) KS C IEC 60570, 등기구 전원공급용 트랙 시스템 KS C IEC 60998(모든 부), 가정용 및 이와 유사한 용도의 저전압용 접속기구 KS C IEC 61084(모든 부), 전기설비용 케이블 트렁킹 및 덕트시스템 KS C IEC 61386(모든 부), 전기설비용 전선관 시스템 KS C IEC 61537, 케이블 관리 - 케이블 트레이 시스템 및 케이블 래더 시스템 IEC 60287(all parts), Electric cables Calculation of the current rating IEC 60702(all parts), Mineral insulated cables and their terminations with a rated voltage not exceeding 750 V IEC 60947-7(all parts), Low-voltage switchgear and controlgear Part 7: Ancillary equipment IEC 61534(all parts), Powertrack systems ISO 834(all parts), Fire-resistance tests Elements of building construction 520.3 용어와 정의 이 표준의 목적을 위하여 다음의 용어와 정의 를 적용한다. 520.3.1 배선설비(wiring system) 나도체 또는 절연전선이나 케이블, 버스바와 필요한 경우 케이블 및 버스바를 안전하게 밀폐한 부품 들로 구성된 집합체 520.3.2 버스바(busbar) 여러 개의 전기회로를 분리하여 접속시킬 수 있는 저임피던스 도체 [IEV 605-02-01] 520.4 일반사항 다음 사항을 적용할 경우, KS C IEC 60364-1 의 기본원칙이 적용되어야 한다. 케이블 및 도체 케이블 및 도체의 단말처리 또는 접속 케이블 및 도체에 관련된 지지물과 현수지지물 외적 영향에 대한 외함 또는 보호방법 521 배선방식의 종류 521.1 사용하는 전선 또는 케이블의 종류와 관련한 배선설비의 설치방법은(521.4 에서 다루는 배선 설비는 제외) 522 절에 따른 외적 영향을 고려하여 표 A.52.1 을 따라야 한다. 521.2 시설상태에 따른 배선설비의 설치방법(521.4 에서 다루는 배선설비는 제외)은 표 A.52.2 를 따 2 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
e9beb27a-a66b-4485-9413-f86d69e01cfd | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 른다. 표 A.52.2 에 포함되지 않은 케이블, 전선, 버스바의 다른 설치방법은 이 표준 규정의 요건을 충 족시킬 경우 허용된다. 521.3 허용전류를 구하기 위해 사용되는 설치방법의 참조사항과 더불어 배선설비의 예(521.4 에 규 정된 배선설비는 제외)를 표 A.52.3 에 나타내었다. 비고 표 A.52.3 은 동일한 허용전류의 안전한 사용이 고려되는 장소에서의 배선설비의 참조방법을 제공한다. 모든 국가의 법규에서 이들 항목이 모두 승인된다는 의미는 아니며, 기타 설치방법 이 금지된다는 의미는 아니다. 521.4 버스바트렁킹 시스템과 파워트랙 시스템 버스바트렁킹 시스템은 KS C IEC 60439-2, 파워트랙 시스템은 IEC 61534 시리즈에 적합해야 한다. 버 스바트렁킹 시스템 및 파워트랙 시스템은 외적 영향을 고려한 제조자의 설명서에 따라 선정하고 설 치한다. 521.5 교류회로 - 전기자기적 영향(맴돌이 전류 방지) 521.5.1 강자성 외함 안에 설치된 교류회로는 보호도체를 포함하여 각 회로의 모든 도체가 동일한 외함 안에 들어가도록 배치해야 한다. 그러한 도체가 강자성 외함 안에 들어갈 경우, 도체가 집합적 으로 강자성 물질에 둘러싸이도록 배치해야 한다. 521.5.2 강선이나 강대 외장의 단심케이블은 교류회로에 사용하지 않는다. 비고 단심케이블의 강선 또는 강대 외장은 강자성 외함으로 간주한다. 단심 외장강선 케이블에 대해 서는 알루미늄 외장의 사용을 권장한다. 521.6 전선관 시스템, 케이블덕팅 시스템, 케이블트렁킹 시스템, 케이블트레이 시스템 및 케이블래더 시스템 모든 도체가 현재 최대 공칭전압에 대해 절연된 경우, 동일한 전선관, 구획된 케이블덕트 시스템 또 는 케이블트렁킹 시스템 내에는 복수회로 설치가 허용된다. 전선관은 KS C IEC 61386 시리즈에 적합해야 하며, 케이블트렁킹 또는 케이블덕트는 KS C IEC 61084 시리즈에 적합해야 하고, 케이블 트레이, 케이블 래더는 KS C IEC 61537 에 적합해야 한다. 비고 전선관의 선정에 관한 지침은 부속서 F 에 있다. 521.7 하나의 다심케이블 속의 복수회로 모든 도체가 최대 공칭전압에 대해 절연되어 있는 경우, 동일한 케이블에 복수의 회로를 구성할 수 있다. 521.8 회로 구성 521.8.1 한 회로의 여러 도체는 다른 다심케이블, 다른 전선관, 다른 케이블덕팅 시스템 또는 다른 케이블트렁킹 시스템을 통해 분산 배선해서는 안 된다. 이것은 1 회로를 구성하는 다심케이블이 병렬 로 시설되는 것은 바람직하지 않기 때문이다. 다심케이블을 병렬로 시설하는 경우 각 케이블은 각 상의 1 가닥의 도체와 중성선이 있다면 중성선도 포함해야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 3 | {}
fc6af85e-9909-45e7-b55d-789258bd4447 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 521.8.2 여러 개의 주회로에 공통 중성선을 사용하는 것은 허용되지 않는다. 왜냐하면, 단상 교류 분기회로는 회로 구성으로 1 가닥의 중성선만 있는 1 개의 다상 교류회로의 1 가닥의 선도체와 중성선 으로 구성해야 하기 때문이다. 이 다상 회로는 모든 선도체를 단로하도록 한 KS C IEC 60364-5-53 의 536.2.2 에 따른 단로장치에 의해 단로해야 한다. 비고 복수의 회로에 대한 공통 보호도체의 배치에 대해서는 KS C IEC 60364-5-54 를 참조 521.8.3 여러 회로가 하나의 접속 상자에서 단자 접속되는 경우, 각 회로에 대한 단자는 KS C IEC 60998 시리즈에 따른 접속기 및 IEC 60947-7 에 따른 단자블록에 관한 것을 제외하고 절연 격벽으로 분리해야 한다. 521.9 유연성 케이블 또는 코드의 사용 521.9.1 유연성 케이블이 이 표준의 규정에 충족되는 경우, 고정배선으로 사용될 수 있다. 521.9.2 이동용 전기기기는 접촉전선(트롤리선)에서 전력을 공급하는 기기를 제외하고 유연성 케이 블 또는 코드에 연결해야 한다. 521.9.3 조리도구(cookers) 또는 이중 마루에 수평매입 설치한 기기와 같이 접속, 청소 등의 목적으 로 일시적으로 움직이는 고정식 기기는 유연성 케이블이나 코드로 접속해야 한다. 521.9.4 유연성 전선관 시스템은 유연성 절연전선을 보호하기 위해 사용할 수 있다. 521.10 케이블의 설치 고정배선용 시스 없는 절연전선은 전선관, 케이블덕트, 또는 케이블트렁킹 시스템 안에 수납되어야 한다. 이 요건은 KS C IEC 60364-5-54 에 적합한 보호도체에는 적용되지 않는다. 522 배선설비의 선정과 설치에 고려할 외적 영향 배선설비의 모든 해당부분에서 예상되는 외적 영향에 대한 보호조치가 확실한 설치방법을 선정해야 한다. 방향이 바뀌는 부분과 배선이 기기 안으로 들어가는 곳에서 특히 주의 를 기울여야 한다. 비고 KS C IEC 60364-5-51 의 표 51A 의 외적 영향 중 배선설비에 있어 중요한 것만을 이 절에서 규정 했다. 522.1 주위온도(AA) 522.1.1 배선설비는 최대주위온도와 최저주위온도 사이의 어떠한 온도에서도 적합하고, 정상운전과 고장 시에도 온도상승한도(표 52.1 참조)를 초과 하지 않도록 선정 및 시설되어야 한다. 비고 "온도상승한도"는 최대 연속운전온도를 의미한다. 522.1.2 케이블과 배선 기구류 등을 포함하는 배선설비의 구성부품은 해당 제품 표준 또는 제조자가 제시하는 제한 온도 내에서만 시설 또는 취급해야 한다. 522.2 외부 열원 4 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
ab2ee59c-a419-434f-8741-7e7ddab321cf | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 522.2.1 외부 열원으로부터의 악영향을 피하기 위해 다음 대책 중의 하나 또는 이와 동등한 유효 조치를 사용하여 배선설비를 보호해야 한다. 차폐 열원으로부터의 충분한 이격 추가적인 온도 상승이 발생할 가능성을 고려하여 배선설비부품을 선정 절연 재료의 국부적 보강. 예: 열 절연슬리브접속 비고 외부 열원으로부터의 열은 다음으로부터의 복사, 대류 또는 전도에 의해 전달된다. 온수 시스템으로부터 설비 (plant), 기기와 조명으로부터 생산 공정으로부터 열전도 재료를 통해 배선 시설 또는 그 주위의 매체가 받는 태양열로부터 522.3 물의 존재(AD) 또는 높은 습도(AB) 522.3.1 배선설비는 결로와 침입에 의한 손상이 없도록 선정과 시공을 해야 한다. 완성한 배선설비 는 개별 장소에 맞는 IP 보호등급에 적합해야 한다. 비고 일반적으로 고정 설비에서의 케이블 외장과 절연체는 그대로의 상태로는 습기의 침입에 대해 내성이 있다고 간주할 수 있다. 빈번히 물이 튀거나 흩어지는 곳, 침입 또는 물에 잠길 가능성 이 있는 케이블은 특별한 고려를 해야 한다. 522.3.2 배선설비 내에 물의 고임 또는 응결될 우려가 있는 경우는 그것을 배출하기 위한 조치를 마 련해야 한다. 522.3.3 배선설비가 파도에 영향을 받을 우려가 있는 경우(AD6)는 기계적 손상에 대해 보호하기 위 해 522.6, 522.7 및 522.8 의 조치 중 한 가지 이상을 강구해야 한다. 522.4 침입 고형물의 존재(AE) 522.4.1 배선설비는 고형물의 침입으로 인해 일어날 수 있는 위험을 최소화할 수 있도록 선정하고 설치해야 한다. 완성한 배선설비는 개별 장소에 맞는 IP 보호등급에 적합해야 한다. 522.4.2 영향을 미칠 수 있는 정도의 먼지가 존재하는 장소(AE4)는 추가 예방 조치를 마련하여 배선 설비의 열 발산을 저해할 수 있는 먼지나 기타의 물질이 쌓이는 것을 방지해야 한다. 비고 배선설비는 쉽게 먼지를 제거할 수 있어야 한다(529 절 참조). 522.5 부식 또는 오염 물질의 존재(AF) 522.5.1 물을 포함하여 부식 또는 오염 물질의 존재가 부식이나 성능 저하를 일으킬 우려가 있는 경 우는 그 영향을 받을 위험이 있는 배선설비 부분을 적당히 보호하거나 이들 물질에 견딜 수 있는 재 료로 제조해야 한다. 비고 설치 시에 적용할 적절한 보호 방식에는 보호 테이프, 도장 또는 그리스 도포 등이 포함될 수 있다. 이들 방식은 제조자에 문의 하여 조정하여야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 5 | {}
8d9d8858-25c0-4229-ae04-3b34ffbd54fe | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 522.5.2 전해작용을 발생시킬 우려가 있는 서로 다른 금속은 상호 접촉에 의한 영향을 피할 수 있는 특별 조치를 마련한 경우를 제외하고 상호 접촉하지 않도록 배치해야 한다. 522.5.3 재료가 상호 작용에 의해서나 개별적으로 성능 저하 또는 위험한 상태가 될 우려가 있는 경 우는 이들을 상호 접속시키지 않도록 배치해야 한다. 522.6 충격(AG) 522.6.1 배선설비는, 예를 들어 사용 중 또는 유지 보수 중 충격, 관통, 압축 등의 기계적 응력에 의 해 발생하는 손상을 최소화하도록 선정하고 설치해야 한다. 522.6.2 고정 설비에 있어 중간 가혹도의 충격(AG2) 또는 높은 가혹도의 충격(AG3)이 발생할 수 있 는 경우는 다음 중 하나의 방법으로 보호되어야 한다. 배선설비의 기계적 특성 장소의 선정 부분적 또는 전체적으로 실시하는 추가적인 기계적 보호 조치 위의 경우에 대한 조합 비고 1 예를 들면 관통이 쉬운 바닥이나 지게차 트럭이 사용되는 구역 비고 2 적절한 케이블트렁킹, 덕팅 또는 전선관을 사용함으로써 기계적 보호 조치를 추가할 수 있다. 522.6.3 바닥 밑 또는 천장 위에 설치된 케이블은 바닥이나 천장, 또는 고정장치와 접촉하여 손상을 입지 않는 위치에 설치해야 한다. 522.6.4 케이블과 도체의 설치 후에도 전기기기의 보호등급이 유지되어야 한다. 522.7 진동(AH) 522.7.1 중간 가혹도의 진동(AH2) 또는 높은 가혹도의 진동(AH3)을 받는 기기의 구조체에 고정되거 나 그 구조체로 지지되는 배선설비는 그러한 조건에 적절히 대비해야 하고, 특히 케이블 및 그 접속 부와 관련되는 경우라면 더욱 그렇다. 비고 진동 기기에의 접속에는 특별한 주의 를 기울여야 할 것이다. 부분적으로 유연성 배선설비를 채 택할 수도 있다. 522.7.2 조명 기구 등 현수형 전기 사용 기기의 고정형 설비는 유연성 심선을 갖는 케이블로 접속해 야 한다. 진동이나 이동이 예상되지 않는 경우는 비유연성 심선의 케이블을 사용하는 것이 가능하다. 522.8 그 밖의 기계적 응력(AJ) 522.8.1 배선설비는 설치, 사용 또는 보수 시에 케이블과 절연전선의 외장이나 절연물과 그 단말부 에 손상을 주지 않도록 선정과 시공을 해야 한다. 전선관 시스템, 덕팅시스템, 트렁킹시스템, 트레이 및 래더시스템에 케이블 및 도체를 입선하기 위해 실리콘유를 함유한 윤활유를 사용해서는 안 된다. 6 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
87912148-af02-4533-a9ac-3344b1dfed9d | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 522.8.2 구조체에 매입하는 전선관 시스템, 케이블덕팅 시스템, 그 밖에 설비를 위해 특별히 설계된 전선관 조립품은 절연전선 또는 케이블을 입선하기 전에 그 연결구간이 완전하게 시공되어야 한다. 522.8.3 배선설비의 모든 굴곡부는 전선과 케이블이 손상을 받지 않으며 단말부가 응력을 받지 않는 반지름을 가져야 한다. 522.8.4 전선과 케이블이 설치 방식에 의해 연속적으로 지지되지 않는 경우는 적절한 간격마다 알맞 은 방법으로 지지하여 전선과 케이블이 그 자체 무게로 인한 손상을 받거나 단락전류로 인한 전자력 에 의해 손상을 받지 않도록 해야 한다. 비고 단락전류로 인한 전자역학적 힘에 대한 예방 조치는 단면적이 50mm2 를 넘는 단심케이블에 대해서만 필요하다. 522.8.5 배선설비가 영구적인 인장 응력을 받는 경우(예를 들어 수직 포설에서의 자기 중량에 의한 인장 응력)는 적당한 단면적을 갖는 적합한 종류의 케이블이나 전선을 적절한 방식으로 설치하여 전 선과 케이블이 수용할 수 없는 인장 응력으로 손상을 받지 않도록 해야 한다. 522.8.6 전선 또는 케이블을 입선 또는 인출이 가능하도록 의도된 배선설비는 이 작업을 위해 설비 에 접근할 수 있는 적절한 방법을 갖추고 있어야 한다. 522.8.7 바닥 내에 매입한 배선설비는 바닥 용도에 맞는 사용에 의해 발생하는 손상을 방지하기 위 해 충분히 보호해야 한다. 522.8.8 벽 내에 견고하게 고정하고 매입하는 배선설비는 수직 또는 수평이거나 방의 가장자리 선과 평행이 되게 포설해야 한다. 천장이나 바닥의 배선설비는 실용적인 최단 경로를 취할 수 있다. 522.8.9 배선설비는 전선과 접속부에 기계적 응력이 가해지지 않도록 설치해야 한다. 522.8.10 지중에 매설되는 케이블, 전선관 또는 덕팅시스템 등은 기계적인 손상으로부터 보호조치 가 되어 있거나 그러한 손상 위험을 최소화할 수 있는 깊이로 매설해야 한다. 매설 케이블은 케이블 덮개 또는 적당한 표시 테이프로 표시를 해야 한다. 매설 전선관과 덕트는 적절한 표식 조치를 해야 한다. 비고 1 KS C IEC 61386-24 는 매설 지중 전선관에 대한 규정이다. 비고 2 KS C IEC 61386-24 에 따라 지중에 매설한 전선관이나 외장 케이블 또는 덮개 판과 같은 그 밖의 적절한 방법이 기계적 보호조치가 될 수 있다. 522.8.11 케이블 지지 장치와 외함에는 케이블이나 절연선에 손상을 줄 수 있는 날카로운 가장자리 가 있어서는 안 된다. 522.8.12 케이블과 전선은 고정방법에 의해 손상을 받아서는 안 된다. 522.8.13 신축 이음부를 지나는 케이블, 버스바 및 그 밖의 전기적 도체는, 예를 들어 유연성 배선 설비를 사용하는 등의 조치를 취하여, 예상되는 움직임으로 인해 전기기기에 손상이 가지 않도록 선 정하고 설치해야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. 7 | {}
41645284-6432-49fa-a989-665691bba2bd | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 522.8.14 배선이 고정된 구획을 관통하는 경우에는, 예를 들면 금속 시스 또는 외장 케이블이나 전 선관 또는 그로미트를 사용하여 기계적 손상을 받지 않게 보호해야 한다. 비고 배선설비는 하중을 견디는 용도의 건축 구조 부재가 관통해서는 안 된다. 다만, 관통 후에도 그 부재가 하중에 견딘다는 것을 보증할 수 있는 경우는 제외한다. 522.9 식물과 곰팡이의 존재(AK) 522.9.1 경험 또는 예측을 통해 위험 조건(AK2)이 구성되는 경우, 이에 대응하는 배선설비를 선정하 거나 특별한 보호 조치를 마련해야 한다. 비고 1 식물이나 곰팡이의 제거가 용이한 설치 방법이 필요할 수도 있다(529 절 참조). 비고 2 가능한 보호 조치로는 폐쇄형 설치법(전선관, 케이블덕트 또는 케이블트렁킹), 식물과 의 거리 유지, 관련 배선설비의 주기적인 청소 등이 있다. 522.10 동물의 존재(AL) 경험 또는 예측을 통해 위험 조건(AL2)이 구성되는 경우, 이에 대응하는 배선설비를 선정하거나 특별 한 보호 조치를 마련해야 한다. 예를 들면 다음과 같다. 배선설비의 기계적 특성 장소의 선정 부분적 또는 전체적인 기계적 보호조치 추가 위의 경우에 대한 조합 522.11 태양 방사(AN) 및 자외선 방사 영향을 줄 만한 양의 태양 방사(AN2)를 경험하거나 예측되는 경우는 이러한 조건에 맞는 배선설비를 선정, 시공하거나 적절한 차폐를 해야 한다. 이온 방사선이 있는 경우, 기기에 특별한 예방 조치가 필요할 수도 있다. 비고 온도 상승을 다룬 522.2.1 도 참조할 것. 522.12 지진의 영향(AP) 522.12.1 해당 시설이 위치하는 장소의 지진 위험을 고려하여 배선설비를 선정하고 설치해야 한다. 522.12.2 경험으로 볼 때 지진 위험도가 낮은 위험도(AP2) 이상인 경우, 특히 다음 사항에 주의 를 기울여야 한다. 배선설비를 건축물 구조에 고정 예를 들어 안전설비(safety services) 등 모든 중요한 기기와 고정 배선 사이의 접속은 유연성을 고 려하여 선정해야 한다. 522.13 바람(AR) 8 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
2f60b421-bec6-4c5a-a756-815f33e0b287 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 522.13.1 522.7 의 진동의 영향(AH)과 522.8 의 기타 기계적 응력(AJ) 참조 522.14 가공물질 또는 보관자재의 특성(BE) 422 절의 화재 예방 조치, 527 절의 화재의 확대를 최소화하기 위한 배선설비 선정과 시공 참조 522.15 건축물의 설계(CB) 522.15.1 구조체의 움직임에 의한 위험이 존재(CB3)하는 경우, 그 상호 변위를 허용하는 케이블 지 지와 보호 방식을 채택하여 전선과 케이블에 과도한 기계적 응력이 가해지지 않도록 해야 한다. 522.15.2 유연성 구조체 또는 움직이도록 의도된 구조체(CB4)에 대해서는 유연성 배선방식을 채용 해야 한다. 523 허용전류 523.1 정상적인 사용상태에서 내용기간 중에 도체에 흘러야 할 전류는 절연물의 온도상승한도를 넘지 않아야 한다. 이 요건은 표 52.1 에 주어진 대로 절연물의 종류에 따라 충족되어야 한다. 전류 값은 523.2 에 따라 선정하거나 523.3 에 따라 결정해야 한다. 표 52.1 절연 형태별 최고사용온도 ¦ 절연물의 종류 ¦ 허용 온도 a,d °C ¦ ¦ --- ¦ --- ¦ ¦ 열가소성 물질[염화 비닐(PVC)] 열경화성 물질[가교 폴리에틸렌(XLPE) 또는 에틸렌프로필렌 고무 혼합물 (EPR)] 무기물(PVC 피복 또는 나도체로 사람이 접촉할 우려가 있는 것.) 무기물(접촉에 노출되지 않고 가연성 물질과 접촉할 우려가 없는 나도체) ¦ 70(도체) 90(도체)b 70(시스) 105(시스) b,c ¦ ¦ 비고 1 이 표는 모든 형태의 케이블을 포함하고 있지는 않다. 비고 2 이 표는 KS C IEC 60439-2 와 파워트랙 시스템 IEC 61534-1 에 따라 제조자가 허용전류를 제 공해야 하는 버스바트렁킹 시스템, 파워트랙 시스템 또는 라이팅트랙 시스템에는 적용되지 않는다. 비고 3 다른 절연 형태에 대한 허용 온도에 대해서는 케이블 표준을 참조하거나 제조자에 문의 한다. ¦ 비고 1 이 표는 모든 형태의 케이블을 포함하고 있지는 않다. 비고 2 이 표는 KS C IEC 60439-2 와 파워트랙 시스템 IEC 61534-1 에 따라 제조자가 허용전류를 제 공해야 하는 버스바트렁킹 시스템, 파워트랙 시스템 또는 라이팅트랙 시스템에는 적용되지 않는다. 비고 3 다른 절연 형태에 대한 허용 온도에 대해서는 케이블 표준을 참조하거나 제조자에 문의 한다. ¦ ¦ a 부속서 A 에 나타낸 허용전류표의 기초가 되는 표 52.1 의 최고 허용 도체온도는 KS C IEC 60502 및 IEC 60702 에서 발췌한 것이며 이들 표에 나타냈다. b 도체가 70 C 를 초과 하는 온도에서 사용될 경우, 이 도체에 접속된 기기는 접속 후의 온도에 적 합한지 확인이 되어 있어야 한다. C 무기물 절연 케이블(mineral insulated cable)에 대해서는 케이블의 온도 정격, 그 단말 처리, 주위 환경조건과 기타 외적 영향에 따라 더 높은 사용온도가 허용될 수도 있다. d 공인 인증을 받았을 경우, 도체 또는 케이블은 제조자 규격에 따라 최고사용온도 허용치를 가질 수도 있다. ¦ a 부속서 A 에 나타낸 허용전류표의 기초가 되는 표 52.1 의 최고 허용 도체온도는 KS C IEC 60502 및 IEC 60702 에서 발췌한 것이며 이들 표에 나타냈다. b 도체가 70 C 를 초과 하는 온도에서 사용될 경우, 이 도체에 접속된 기기는 접속 후의 온도에 적 합한지 확인이 되어 있어야 한다. C 무기물 절연 케이블(mineral insulated cable)에 대해서는 케이블의 온도 정격, 그 단말 처리, 주위 환경조건과 기타 외적 영향에 따라 더 높은 사용온도가 허용될 수도 있다. d 공인 인증을 받았을 경우, 도체 또는 케이블은 제조자 규격에 따라 최고사용온도 허용치를 가질 수도 있다. ¦ 523.2 절연전선 및 비외장형 케이블의 전류가 부속서 B 의 필요한 보정계수를 적용하고 부속서 B 와 표 A.52.3 에서 선정된 적절한 값을 넘지 않는다면, 523.1 의 요건을 충족하는 것으로 간주한다. 부속서 B 에 주어진 허용전류는 권장 지침이다. 비고 1 각 국가위원회는 자국 규정에 맞는 간략화된 형태의 부속서 B 의 표를 채택할 수 있다. 간략 화의 한 예를 부속서 C 에 나타내었다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 9 | {}
6ac1d7a6-4870-4280-a5e7-7d2455fd973b | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 비고 2 환경조건 및 케이블의 정확한 구조에 따라 허용전류에 어느 정도 허용오차가 있을 수 있다. 523.3 허용전류의 적정 값은 IEC 60287 에서 규정하는 대로 또는 시험이나 인증된 방법을 이용한 계산을 통해 정할 수도 있다. 적절한 경우, 부하의 특성을 고려하고 매설 케이블에 대해서는 토양 열 저항의 영향을 고려한다. 523.4 주위온도는 해당 케이블 또는 전선에 부하가 걸려 있지 않을 때의 주위 매체의 온도이다. 523.5 복수회로로 포설된 그룹 그룹저감계수(group reduction factors)(표 B.52.17~표 B.52.21)는 동일한 최고사용온도를 가진 절연전 선이나 케이블 그룹에 적용한다. 최고사용온도가 서로 다른 케이블이나 절연전선을 포함한 그룹인 경우, 해당 그룹 내의 모든 케이블 이나 절연전선의 허용전류는 적절한 그룹 저감 계수와 함께 그룹 중 가장 낮은 최고사용온도에 기초 해야 한다. 알려진 사용 조건 때문에 케이블이나 절연전선이 그것이 속한 그룹의 정격의 30% 이하 전류가 예 상될 경우, 그룹의 나머지에 대한 저감 계수를 구하는 데 있어 무시해도 된다. 523.6 부하 도체의 수 523.6.1 회로에서 고려해야 할 사항은 부하전류가 통전되는 도체의 수이다. 다상 회로 도체의 전류 가 평형 상태로 예상되는 경우, 그 중성선을 고려할 필요는 없다. 이러한 조건에서는 4 심 케이블의 허용전류는 각 선로도체에 대해 동일한 도체 단면적을 갖는 3 심 케이블과 같다. 4 심, 5 심 케이블은 3 심에만 부하가 걸렸을 때 더 높은 허용전류 용량을 가질 수 있다. THDi(총고조파왜율)가 15 %를 넘는 제 3 고조파나 3 배수 고조파 전류가 존재할 경우, 이런 가정이 유효하지 않다. 523.6.2 다심케이블에서 선전류의 불균형으로 인해 중성선에 전류가 흐르는 경우, 중성선 전류에 의한 온도 상승은 하나 또는 그 이상의 선도체에서 발생하는 열이 감소됨으로써 상쇄된다. 이 경우, 중성선 사이즈는 가장 높은 선전류를 기초로 선택해야 한다. 어떤 경우이든, 중성선은 523.1 에 적합한 단면적을 가져야 한다. 523.6.3 중성선이 선도체의 부하에 상응하는 감소 없이 전류를 흘릴 경우, 회로의 정격을 고려할 때 중성선도 도체 수에 포함시켜야 한다. 이러한 전류는 삼상 회로의 현저한 3 배수 고조파 전류가 원인이 될 수 있다. 고조파 전류의 크기가 기본 선전류의 15 %를 넘는 경우, 그 중성선의 사이즈는 선도체 사이즈 이상이어야 한다. 3 배수 고조파 전류 또는 제 3 고조파의 존재로 인한 열적 영향과 그에 대응하는 더 높은 고조파 전류에 대한 저감 계수는 부속서 E 에 나타내었다. 523.6.4 보호도체로만 사용되는 전선(PE 도체)은 고려하지 않는다. PEN 도체는 중선선과 같은 방법 으로 취급한다. 523.7 병렬도체 두 개 이상의 선도체 또는 PEN 도체가 병렬로 접속된 경우, 다음의 a) 또는 b)에 따른다. a) 부하전류가 균등하게 배분될 수 있도록 조치를 취한다. 10 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
9ba82caf-2118-481e-b25b-73904ac14d86 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 전선이 같은 재질, 같은 단면적을 가지고, 거의 길이가 같고, 그 전체 길이에서 분기 회로가 없으 며 다음 어느 하나일 경우 이 요건을 충족한 것으로 본다. 병렬 전선이 다심케이블 또는 꼬인 단심케이블 또는 절연전선임 병렬 전선이 꼬이지 않은 단심케이블 또는 삼각배치 또는 수평배치의 절연전선으로서 단면적 이 동선은 50mm2, 알루미늄선은 70mm2 이하임 병렬 전선이 꼬이지 않은 단심케이블 또는 삼각배치 혹은 수평의 절연전선으로서 단면적이 동 선은 50 mm2, 알루미늄선은 70 mm2 를 초과 하고 이러한 구성에 필요한 특수한 배치 법을 적용 함. 특수한 배치 법은 서로 다른 상 또는 극을 적절하게 그룹 짓고 간격을 두는 것으로 이루 어진다(부속서 H 참조). b) 523.1 의 요건을 충족시키도록 부하전류를 배분하는 데 특별히 주의 한다. 이 절은 쥐꼬리접속(spur connection)이 있거나 없는 다른 링 분기회로의 사용을 배제하지 않는다. 전류가 적절히 분배되지 않거나 넷 이상의 도체가 병렬로 연결되어야 하는 경우, 버스바트렁킹 시스 템의 사용을 고려한다. 523.8 경로 중 시설조건 변화 경로 중 일부에서 다른 부분과 냉각 조건이 다를 경우, 경로 중 가장 나쁜 조건의 부분에 적합하도 록 허용전류를 결정해야 한다. 비고 배선이 벽을 통해 가는 길이가 0.35 m 미만일 때에만 냉각 조건이 다르다면 이 요건은 통상적 으로 무시할 수 있다. 523.9 금속 피복된 단심케이블 동일한 회로의 단심케이블의 금속 시스 또는 비자성 외장은 양쪽 끝에서 함께 연결되어야 한다. 또 는 허용전류를 늘리기 위해서 단면적이 50 mm2 를 넘는 도체를 가진 그러한 케이블의 시스나 외장 및 비전도성 외장은 한 지점에서 서로 연결하고 연결되지 않은 다른 끝은 적절한 절연조치를 해도 된다. 이때 연결점으로부터의 케이블 길이는 시스 또는 외장에서 접지까지의 전압이 다음과 같도록 제한해야 한다. a) 예를 들어 최대 전압을 25 V 로 제한하는 등으로 케이블에 최대부하의 전류가 흘렀을 때 부식을 일으키지 않을 것. b) 케이블에 단락전류가 발생했을 때 재산 피해나 위험을 초래하지 않을 것. 524 도체의 단면적 524.1 기계적인 이유로, 교류회로의 선도체와 직류 회로의 선도체의 단면적은 표 52.2 에 나타낸 값 이상이어야 한다. 11 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
92755cab-e2a7-45eb-9be9-9760df0ff55d | KSCIEC60364-5-52_KR | KS CIEC 60364-5-52:2009 표 52.2 - 도체의 최소 단면적 ¦ 배선설비의 종류 ¦ 배선설비의 종류 ¦ 회로 용도 ¦ 도체 ¦ 도체 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 배선설비의 종류 ¦ 배선설비의 종류 ¦ 회로 용도 ¦ 재료 ¦ 단면적 mm2 ¦ ¦ 고정 설비 ¦ 케이블 및 절연전선 ¦ 전력 및 조명 회로 ¦ 구리 ¦ 1.5 ¦ ¦ 고정 설비 ¦ 케이블 및 절연전선 ¦ 전력 및 조명 회로 ¦ 알루미늄 ¦ 케이블 표준 KS C IEC 60228 에 맞게 조치(10 mm2)(비고 1 참조) ¦ ¦ 고정 설비 ¦ 케이블 및 절연전선 ¦ 신호 및 제어 회로 ¦ 구리 ¦ 0.5(비고 2 참조) ¦ ¦ 고정 설비 ¦ 나도체 ¦ 전력 회로 ¦ 구리 ¦ 10 ¦ ¦ 고정 설비 ¦ 나도체 ¦ 전력 회로 ¦ 알루미늄 ¦ 16 ¦ ¦ 고정 설비 ¦ 나도체 ¦ 신호 및 제어 회로 ¦ 구리 ¦ 4 ¦ ¦ 절연전선 및 케이블의 가요 접속 ¦ 절연전선 및 케이블의 가요 접속 ¦ 특정 기기용 ¦ 구리 ¦ 관련 IEC 표준에 의함. ¦ ¦ 절연전선 및 케이블의 가요 접속 ¦ 절연전선 및 케이블의 가요 접속 ¦ 기타 적용 ¦ 구리 ¦ 0.75 a ¦ ¦ 절연전선 및 케이블의 가요 접속 ¦ 절연전선 및 케이블의 가요 접속 ¦ 특수 용도를 위한 특별 저압 회로 ¦ 구리 ¦ 0.75 ¦ ¦ 비고 1 ¦ 알루미늄 도체의 단말 처리에 사용하는 커넥터는 이 용도에 대해 시험 승인된 것이어야 한다. ¦ ¦ --- ¦ --- ¦ ¦ 비고 2 ¦ 전자 기기용으로 이용하는 신호 및 제어 회로에서는 최소 단면적을 0.1 mm2 로 할 수 있다. ¦ ¦ 비고 3 ¦ 특별저전압 조명용 특수 요건에 대해서는 KS C IEC 60364-7-715 참조 ¦ ¦ 비고 4 ¦ 영국에서는 조명 회로용으로 1.0 mm2 케이블이 허용된다. ¦ ¦ 비고 5 ¦ 영국에서는 전력 및 조명용 회로에 케이블과 절연전선을 사용한 고정 설비에 대해서 1.0 mm2 구리 케이블이 허용된다. ¦ ¦ a 7 심 ¦ 이상의 다심 유연성 케이블에서는 비고 2 를 적용한다. ¦ 524.2 중성선의 단면적 정확한 정보가 없을 경우, 다음을 적용한다. 524.2.1 중성선의 단면적은 다음의 경우에 최소한 선도체의 단면적 이상이어야 한다. 단상 2 선식 회로, 어떤 것이든 중성선의 단면적 다상 회로에서 선도체의 단면적이 동선 16mm2, 알루미늄선 25 mm2 이하일 경우 3 상 회로에서 제 3 고조파 및 제 3 고조파의 홀수배수의 고조파 전류가 흐를 가능성이 높고 총 고조 파 왜형률이 15 %~33 %인 경우 비고 예를 들면 형광등과 같은 방전램프를 비롯한 조명회로에서 그러한 고조파 수치가 나타난다. 524.2.2 제 3 고조파 전류 및 제 3 고조파 전류의 홀수배수 총 고조파 왜형률이 33 %를 초과 하는 경우, 중성선의 단면적을 증가해야 할 수도 있다(523.6.3 및 부속서 E 참조). 비고 1 이러한 값의 적용은, 예를 들면 IT 전용 회로에서 이루어진다. a) 다심케이블에 대해서는 선도체의 단면적이 중성선의 단면적과 같아야 하며, 이 단면적은 선도체 의 1.45 x /B 가 흐르는 중성점에 대해 선택한다. 12 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
0334082e-0d62-43e6-8dc1-443b547542b6 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 b) 단심케이블에 대해서는 선도체의 단면적이 중성선 단면적보다 작을 수도 있다. 계산은 다음과 같다. - 선: /B 에서 중성점: 선의 1.45 IB 와 같은 전류에서 비고 2 IB 의 설명은 KS C IEC 60364-4-43:2008 의 433.1 참조 524.2.3 다상 회로의 각 선도체 단면적이 동선 16mm2 또는 알루미늄선 25 mm2 를 초과 하는 경우, 다음 조건을 모두 충족한다면 그 중성선의 단면적을 선도체 단면적보다 작게 해도 된다. 통상적인 사용 시에 상과 제 3 고조파 전류 간에 회로 부하가 균형을 이루고 있고 제 3 고조파 전류 의 홀수배수 전류가 선도체 전류의 15 %를 넘지 않는다. 비고 보통 중성선 단면적을 선도체 단면적의 50 % 미만으로 하지는 않는다. 중성선은 431.2 의 규정에 따라 과전류 보호된다. 중성선의 단면적은 동선 16 mm2, 알루미늄선 25 mm2 이상이다. 525 수용자설비에서의 전압강하 다른 조건을 고려하지 않는다면 사용자 설비의 인입구로부터 기기까지의 전압강하는 표 G.52.1 에 주 어진 값을 초과 해서는 안 된다. 비고 다른 고려할 사항으로 돌입 전류가 높은 기기 및 전동기의 가동시간이 포함된다. 비정상 사용 으로 인한 전압 변동과 과도전압 등과 같은 일시적 조건은 무시할 수 있다. 526 전기적 접속 526.1 도체 간, 도체와 그 밖의 다른 기기 간의 접속은 내구성 있는 전기적 연속성이 있어야 하며 기계적 강도 및 보호가 충분해야 한다. 비고 KS C IEC 61200-52 참조 526.2 접속 방법은 다음에 적합한 것을 고려해 선정한다. 도체와 그 절연물의 재료 도체를 구성하는 배선의 수와 형태 도체의 단면적 함께 접속되는 도체의 수 비고 1 통신 회로를 제외하고는 땜납접속은 피해야 한다. 만약 사용하는 경우, 크리프와 기계적 응력 및 고장 시 온도 상승을 고려하여 설계해야 한다(522.6, 522.7, 522.8 참조). 비고 2 적용 표준에는 KS C IEC 60998, IEC 60947(Part 7 전체), IEC 61535 가 있다. 비고 3 "r"(강체 도체에만), "f"(유연성 도체에만), "s" 또는 "sol"(단선 도체에만) 표시가 없는 단말부는 모든 종류의 도체 접속에 적합하다. 526.3 다음의 경우를 제외한 모든 접속 부분은 검사, 시험과 보수를 위해 접근이 가능해야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. 13 | {}
70a7f4a3-e81d-41ed-9e77-f06f86fe5674 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 매설 케이블의 접속부 충진재를 채운 부위 또는 몰드 내의 접속부 천정가열(ceiling heating), 마루가열(floor heating), 열선가열(trace heating) 시스템에서 발열체와 비 발열선단부(cold tail)와의 접속부 용접, 납땜, 경납땜(brazing) 또는 적절한 압착 도구로 만든 접합부 기기의 일부를 구성하는 접합부로 해당되는 제품 표준에 적합할 경우 비고 화합물 충진 접합부의 예를 들면 수지 충진 접합부 등이다. 526.4 필요한 경우, 통상적인 사용에서 접속에 의한 온도 상승으로 접속부에 연결되거나 접속부를 지지하는 도체의 절연 효과 가 저해되지 않도록 예방 조치를 마련해야 한다. 526.5 도체 접속은 (단말부뿐 아니라 중간 연결부도) 접속함, 인출함, 또는 제조자가 이 용도를 위 해 공간을 제공해 놓은 경우, 기기 내부 등 적당한 외함 안에 수납되어야 한다. 기기 안에 수납할 경 우, 기기에 고정 접속 장비가 있거나 접속 장비 설치를 위한 조치가 마련되어 있어야 한다. 회로 도 선 단말부는 외함 안에서 끝나야 한다. 526.6 케이블과 도선의 접속점과 연결점은 기계적 응력이 미치지 않아야 한다. 스트레스 완화장치 는 케이블이나 도선에 기계적인 손상이 가지 않도록 압력 완화 장비를 설계되어야 한다. 526.7 접속부가 외함 내에 수납될 경우, 외함은 관련 외적 영향으로부터의 보호 조치와 기계적인 보호조치가 되어 있어야 한다. 526.8 다중선, 세선, 극세선 접속 526.8.1 다중선, 세선, 극세선의 소선이 분리되거나 분산되는 것을 막기 위해서 적합한 단말부를 사 용하거나 도선 끝을 적당히 처리하여야 한다. 526.8.2 적당한 단말부를 사용한다면 다중선, 세선, 극세선의 전체 도선 말단을 납땜하는 것이 허용 된다. 526.8.3 사용 중 도선의 납땜한 부위와 납땜하지 않은 부위의 상대적인 변위가 있게 되는 연결점에 서는 세선 및 극세선 도선의 말단을 납땜하는 것이 허용되지 않는다. 비고 세선과 극세선은 KS C IEC 60228 의 클래스 5 와 6 의 표준에 따른다. 526.9 전선관, 덕트 또는 트렁킹 말단에서 외피가 벗겨지거나 외피가 피복되지 않은 케이블의 심 선은 526.5 의 요건대로 외함 안에 수납해야 한다. 527 화재 확산을 최소화하기 위한 배선설비의 선정과 시공 527.1 방화구획 내부에서의 주의 사항 527.1.1 화재의 확산 위험을 최소화하도록 적절한 재료를 선정하고 527 절에 따라 설치해야 한다. 527.1.2 배선설비는 건축 구조물의 일반 성능과 화재 안정성을 저해시키지 않도록 설치한다. 14 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f9d8cfe9-7f28-4266-8ab0-6365d7c7e009 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 527.1.3 적어도 KS C IEC 60332-1-2 에 적합한 케이블 및 자소성을 인정받은 제품은 특별한 예방 조 치 없이 설치할 수 있다. 비고 특별한 위험이 있는 것으로 인식되는 설비에서는 IEC 60332-3 에서 규정하는 집합 케이블에 대 한 보다 엄격한 검사에 적합한 케이블을 필요로 할 수도 있다. 527.1.4 KS C IEC 60332-1-2 화염 전파 저항 요건에 적합하지 않은 케이블을 사용하는 경우, 영구적 배선설비에 기기를 접속시키기 위한 용도로 짧은 길이만을 사용하는 것으로 제한해야 하며, 어떤 경 우에도 한 방화구획에서 다른 구획으로 통과 시켜서는 안 된다. 527.1.5 KS C IEC 60439-2, KS C IEC 61537, KS C IEC 61084 시리즈, KS C IEC 61386 시리즈, IEC 61534 시리즈에 규정된 자소성으로 분류되는 제품은 특별한 예방조치 없이 설치할 수 있다. 내화성 에 관한 비슷한 요건을 가진 표준에 적합한 다른 제품도 특별한 예방조치 없이 설치할 수 있다. 527.1.6 KS C IEC 60439-2, KS C IEC 60570, KSCIEC 61537, KS C IEC 61084 시리즈, KS C IEC 61386 시리즈, IEC 61534 시리즈에서 자소성(non-flame propagating)으로 분류되지는 않지만 각각의 제품 표 준 요건의 모든 다른 면을 충족시키는 부품이 들어간 배선설비를 사용하는 경우, 적절한 불연성 건 축 재료 안에 완전하게 수납해야 한다. 527.2 배선설비 관통부의 밀봉 527.2.1 배선설비가 바닥, 벽, 지붕, 천장, 칸막이, 중공벽 등 건축 구조부를 관통하는 경우, 배선설 비가 통과 한 후에 남는 개구부를 관통 전의 건축 구조 각 부재에 규정된 내화 등급에 따라 밀폐해야 한다(ISO 834 시리즈 참조). 비고 1 배선설비를 설치하는 동안 임시 밀폐 조치가 필요할 수도 있다. 비고 2 개조 작업 시에 밀폐는 가능한 한 신속하게 회복시키는 것이 바람직하다. 527.2.2 내화 성능이 규정된 건축 구조부를 관통하는 배선설비는 527.2.1 요건대로 외부를 밀폐할 뿐 아니라 관통 전의 각 부분의 내화 등급 수준까지 내부도 밀폐해야 한다. 527.2.3 관련 제품 표준에 따라 자소성으로 분류되고 최대 내부 단면적이 710 mm2 이하인 전선관, 케이블트렁킹, 케이블덕팅 시스템은 다음과 같은 경우라면 내부적으로 밀폐하지 않아도 된다. KS C IEC 60529 의 IP33 검사를 충족시키는 설비 관통하는 건축 구조체에 의해 분리되는 하나의 격실 내에 수납된 배선설비의 단말이 KS C IEC 60529 IP33 검사를 충족시키는 경우 527.2.4 배선설비는 그 용도가 하중을 받는 건축 구조 부재를 관통해서는 안 된다. 다만, 관통 후에 도 그 부재가 하중에 견딘다는 것을 보증할 수 있는 경우는 제외한다(ISO 834 시리즈 참조). 527.2.5 527.2.1 또는 527.2.2 를 충족시킬 의도로 배치된 밀폐 조치는 그 밀폐가 사용되는 배선설비 와 동일한 수준으로 외적 영향에 대한 내성이 있어야 하며, 다음 요건을 모두 충족시켜야 한다. 연소 생성물에 대해서 관통하는 건축 구조부와 같은 수준의 내성을 지닌다. 물의 침투에 대해 설치되는 건축 구조부에 요구되는 것과 동등한 수준으로 보호 조치를 갖춘다. 밀폐 및 배선설비는 밀폐에 사용된 모든 재료가 최종적으로 결합 조립되었을 때 내습성이 있는 15 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
542a171a-d1ac-47e5-a4fd-075a35650279 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 경우가 아닌 한, 배선설비를 따라 이동하거나 밀폐 주위에 모일 수 있는 물방울로부터의 보호 조 치를 갖춘다. 비고 1 이들 요건은 IEC 의 제품 표준이 정비되면 그 표준으로 옮겨질 수 있다. 접촉하는 배선설비의 재료와 양립될 수 있는 것이어야 한다. 밀폐 성능을 감소시키지 않고 배선설비의 열의 이동이 가능한 것이어야 한다. 화재 시에 배선설비의 지지재가 손상되어 발생할 우려가 있는 스트레스를 견딜 수 있는 정도의 충분한 기계적 내구성을 가져야 한다. 비고 2 다음의 어느 한 경우라면 527.2.5 요건이 충족될 수 있을 것이다. 케이블 클리트, 케이블 타이 또는 케이블 지지재는 밀폐부로부터 750 mm 이내에 설치하 며, 밀폐부의 불에 탄 쪽 지지재가 붕괴되었을 때 예상되는 기계적 부하를 밀폐부에 변형 이 가해지지 않는 정도로 견딜 수 있다. 밀폐 방식의 설계 자체가 충분한 지지 기능을 갖는다. 528 배선설비와 다른 공급설비와 의 접근 528.1 다른 전기 공급설비와 의 접근 KS C IEC 60449 에 따른 밴드 I 과 밴드 II 전압 회로는 다음 중 어느 한 방법을 채택하지 않는 한 같 은 배선설비 내에 수납하지 않는다. 모든 케이블 또는 도체가 존재하는 최고 전압에 대해 절연되어 있다. 다심케이블의 각 도체가 케이블에 존재하는 최고 전압에 대해 절연되어 있다. 케이블이 계통전압에 대해 절연되어 있으며 케이블들이 케이블덕트 또는 케이블트렁킹의 다른 격 실에 설치되어 있다. 케이블이 격벽을 써서 물리적으로 분리되는 케이블트레이 시스템에 설치되어 있다. 각각의 전선관, 트렁킹, 덕트를 이용한다. SELV 및 PELV 설비에 대해서는 414 절의 요건이 적용된다. 비고 1 통신 회로, 데이터 전송 회로 등과 같은 종류에 대해서는 전자기적 간섭과 정전기적 간섭 모 두를 특별히 고려해야 할 수도 있다. 비고 2 배선설비와 피뢰 설비가 근접해 있는 경우, KS C IEC 62305 시리즈를 고려해야 한다. 528.2 통신 케이블과 의 접근 지중 통신 케이블과 지중 전력 케이블을 가로지르거나 이에 근접할 경우, 최소 100 mm 간격을 유지 하거나, a) 또는 b) 요건을 충족해야 한다. a) 케이블 사이에, 예를 들면 벽돌, 케이블 보호캡(찰흙, 콘크리트), 성형블록(콘크리트) 등과 같은 발 화지연 장벽을 갖추거나, 발화지연물질로 만든 트로프나 케이블 전선관 등으로 보호 조치를 추가 한다. b) 교차부에 대해서는 케이블 사이에 케이블 전선관, 콘크리트 케이블 보호캡, 형상 블록(shaped block) 등과 같은 기계적인 보호 조치를 갖춘다. 16 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f4c730c6-dcec-443c-b817-5bfa5ba06b7f | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 528.3 다른 공급설비와 의 접근 528.3.1 배선설비는 배선에 해로울 가능성이 높은 열이나 연기, 증기를 발산하는 설비 근처에 설치 하지 않는다. 다만, 배선으로부터의 열 발산에 영향을 주지 않도록 조치된 차폐물을 써서 해로운 외 적 영향으로부터 적절하게 보호한 경우는 예외로 한다. 각종 설비의 통로나 빈 곳(service shaft, cavity) 등과 같이 특별히 케이블 설치를 위해 설계된 구역이 아닌 곳에서는 케이블이 인접 설비(가스, 수도선, 증기배관 등)의 정상 운전에 의한 해로운 영향에 노 출되지 않도록 배치한다. 528.3.2 배선설비가 응축을 초래할 가능성이 높은 설비(예를 들어 물, 증기 또는 가스 공급 설비)의 밑으로 지나갈 때는 배선설비에 해로운 영향이 미치지 않도록 예방 조치를 취한다. 528.3.3 전기 공급설비가 다른 공급설비와 근접하여 설치된 경우, 다른 공급설비에서 예상할 수 있 는 어떠한 운전을 하더라도 전기공급설비에 손상을 주거나 그 반대의 경우가 되지 않도록 전기공급 설비를 배치한다. 비고 다음과 같이 함으로써 위의 요건이 충족될 수도 있다. 설비 간에 적절한 간격을 둔다. 기계적 또는 열적 차폐물을 사용한다. 528.3.4 전기 공급 설비가 다른 공급설비와 매우 근접하여 설치된 경우, 다음 두 조건을 충족시키 도록 한다. 다른 공급설비의 정상 사용으로 초래될 우려가 있는 위험에 대해 배선설비를 적절히 보호한다. 금속제의 다른 공급설비는 계통 외 도전부로 간주하고 KS C IEC 60364-4-41:2005 의 413 절 요건에 따른 고장보호를 한다. 528.3.5 배선설비가 승강기(또는 인양기) 설비의 일부를 구성하지 않는 한, 배선설비가 승강기(또는 인양기) 통로를 지나서는 안 된다. 529 청소 등 정비를 고려한 배선설비 선정과 설치 529.1 정비와 관련해서는 KS C IEC 60364-1:2005 의 34 절을 참조한다. 529.2 보수 활동을 위해 어떤 보호 조치를 제거할 필요가 있는 경우, 원래 의도했던 보호등급을 저 하시키지 않으면서 그 보호 조치를 회복할 수 있는 조치를 마련해야 한다. 529.3 보수가 필요하다고 여겨지는 배선설비의 모든 부분을 안전하고 적절하게 접근할 수 있는 조 치가 되어 있어야 한다. 비고 상황에 따라서는 사다리, 통로 등 영구적 접근 수단의 설치가 필요할 수도 있다. 17 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
69cd8641-b449-4be1-b2be-c5a35939a249 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 부속서 A (규정) 설치 방법 표 A.52.1 - 도체 및 케이블과 관련한 설치방법 ¦ 도체와 케이블 ¦ 도체와 케이블 ¦ 설치방법 ¦ 설치방법 ¦ 설치방법 ¦ 설치방법 ¦ 설치방법 ¦ 설치방법 ¦ 설치방법 ¦ 설치방법 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도체와 케이블 ¦ 도체와 케이블 ¦ 비고정 ¦ 직접 고정 ¦ 전선관 ¦ 케이블트렁킹 (몰드형, 바닥 매입형을 포함) ¦ 케이블 덕팅 시스템 ¦ 케이블 래더, 케이블 트레이, 케이블 브래킷 ¦ 애자 사용 ¦ 지지선 ¦ ¦ 나도체 ¦ 나도체 ¦ - ¦ - ¦ - ¦ - ¦ - ¦ - ¦ + ¦ - ¦ ¦ 절연전선 b ¦ 절연전선 b ¦ - ¦ - ¦ + ¦ + a ¦ + ¦ - ¦ + ¦ - ¦ ¦ 외장케이블 (외장 및 무기질 절연물을 포함) ¦ 다심 ¦ + ¦ + ¦ + ¦ + ¦ + ¦ + ¦ 0 ¦ + ¦ ¦ 외장케이블 (외장 및 무기질 절연물을 포함) ¦ 단심 ¦ 0 ¦ + ¦ + ¦ + ¦ + ¦ + ¦ 0 ¦ + ¦ ¦ + - ¦ : 사용할 수 있다. : 사용할 수 없다. ¦ ¦ --- ¦ --- ¦ ¦ 0 ¦ : 적용할 수 없거나 실용상 일반적으로 사용할 수 없다. ¦ ¦ a b ¦ 케이블트렁킹이 적어도 IP4X 또는 IPXXD 급의 보호를 제공하고 도구를 사용하거나 의도적인 행 동을 했을 때만 덮개를 제거할 수 있는 경우 절연전선을 사용할 수 있다. 보호 도체 또는 보호 본딩도체로 사용되는 절연전선은 절연을 위해 적절한 어떤 방법이든 사용 할 수 있고 전선관, 트렁킹 또는 덕트에 배치할 필요는 없다. ¦ 표 A.52.2 - 배선설비의 설치 ¦ 시설 상황 ¦ 시설 상황 ¦ 설치방법 ¦ 설치방법 ¦ 설치방법 ¦ 설치방법 ¦ 설치방법 ¦ 설치방법 ¦ 설치방법 ¦ 설치방법 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 시설 상황 ¦ 시설 상황 ¦ 고정하지 않음 ¦ 직접 고정 ¦ 전선관 ¦ 케이블트렁킹 (몰드형, 바닥 매입형을 포함) ¦ 케이블 덕트 ¦ 케이블 래더, 케이블 트레이, 케이블 지지대 ¦ 애자 사용 ¦ 지지선 ¦ ¦ 건물의 빈 공간 ¦ 접근 가능 ¦ 40 ¦ 33 ¦ 41, 42 ¦ 6,7,8,9, 12 ¦ 43, 44 ¦ 30,31,32, 33,34 ¦ - ¦ 0 ¦ ¦ 건물의 빈 공간 ¦ 접근 불가 ¦ 40 ¦ 0 ¦ 41, 42 ¦ 0 ¦ 43 ¦ 0 ¦ 0 ¦ 0 ¦ ¦ 케이블 채널 ¦ 케이블 채널 ¦ 56 ¦ 56 ¦ 54, 55 ¦ 0 ¦ ¦ 30,31,32, 34 ¦ - ¦ - ¦ ¦ 지중매설 ¦ 지중매설 ¦ 72, 73 ¦ 0 ¦ 70, 71 ¦ - ¦ 70, 71 ¦ 0 ¦ - ¦ - ¦ ¦ 구조체 매설 ¦ 구조체 매설 ¦ 57, 58 ¦ 3 ¦ 1,2,59,60 ¦ 50, 51, 52, 53 ¦ 46, 45 ¦ 0 ¦ - ¦ - ¦ ¦ 노출부착 ¦ 노출부착 ¦ - ¦ 20,21, 22,23,33 ¦ 4, 5 ¦ 6, 7, 8,9, 12 ¦ 6,7, 8,9 ¦ 30,31,32, 34 ¦ 36 ¦ ¦ ¦ 가공/기중 ¦ 가공/기중 ¦ - ¦ 33 ¦ 0 ¦ 10, 11 ¦ 10, 11 ¦ 30,31,32, 34 ¦ 36 ¦ 35 ¦ ¦ 창틀 ¦ 창틀 ¦ 16 ¦ 0 ¦ 16 ¦ 0 ¦ 0 ¦ 0 ¦ - ¦ - ¦ 18 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c73ba8ca-502d-4574-8e6e-f6a92a0978a2 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 A.52.2 - 배선설비의 설치(계속) ¦ 시설 상황 ¦ 설치방법 ¦ 설치방법 ¦ 설치방법 ¦ 설치방법 ¦ 설치방법 ¦ 설치방법 ¦ 설치방법 ¦ 설치방법 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 시설 상황 ¦ 고정하지 않음 ¦ 직접 고정 ¦ 전선관 ¦ 케이블트렁킹 (몰드형, 바닥 매입형을 포함) ¦ 케이블 덕트 ¦ 케이블 래더, 케이블 트레이, 케이블 지지대 ¦ 애자 사용 ¦ 지지선 ¦ ¦ 처마도리(건물의 가장자리의 기둥이나 벽 위에, 서까래를 받치기 위해 가로지르는 나무) ¦ 15 ¦ 0 ¦ 15 ¦ 0 ¦ 0 ¦ 0 ¦ - ¦ - ¦ ¦ 수중 1 ¦ + ¦ + ¦ + ¦ - ¦ + ¦ 0 ¦ - ¦ - ¦ ¦ - : 사용할 수 없다. 0 : 적용할 수 없거나 실용상 일반적으로 사용할 수 없다. + : 제조자 지침을 따른다. ¦ - : 사용할 수 없다. 0 : 적용할 수 없거나 실용상 일반적으로 사용할 수 없다. + : 제조자 지침을 따른다. ¦ - : 사용할 수 없다. 0 : 적용할 수 없거나 실용상 일반적으로 사용할 수 없다. + : 제조자 지침을 따른다. ¦ - : 사용할 수 없다. 0 : 적용할 수 없거나 실용상 일반적으로 사용할 수 없다. + : 제조자 지침을 따른다. ¦ - : 사용할 수 없다. 0 : 적용할 수 없거나 실용상 일반적으로 사용할 수 없다. + : 제조자 지침을 따른다. ¦ - : 사용할 수 없다. 0 : 적용할 수 없거나 실용상 일반적으로 사용할 수 없다. + : 제조자 지침을 따른다. ¦ - : 사용할 수 없다. 0 : 적용할 수 없거나 실용상 일반적으로 사용할 수 없다. + : 제조자 지침을 따른다. ¦ - : 사용할 수 없다. 0 : 적용할 수 없거나 실용상 일반적으로 사용할 수 없다. + : 제조자 지침을 따른다. ¦ - : 사용할 수 없다. 0 : 적용할 수 없거나 실용상 일반적으로 사용할 수 없다. + : 제조자 지침을 따른다. ¦ 비고 40, 46 등 표 중의 번호는 표 A.52.3 의 설치방법 인용 번호이다. 표 A.52.3 - 전류 용량 확보를 위한 설치방법의 예 ¦ 항목 번호 ¦ 설치 방법 ¦ 설명 ¦ ¦ 전류 용량 확보를 위한 표준 설치방법 (부속서 B 참조) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ ¦ 옥내 ¦ 단열벽 속에 매입한 전선관 내부의 절연 전선 또는 단심케이블 a,c ¦ A1 ¦ ¦ 2 ¦ ¦ 옥내 ¦ 단열벽 속에 매입한 전선관 내부의 다심케이블 a,c ¦ A2 ¦ ¦ 3 ¦ ¦ 옥내 ¦ 단열벽 속에 직접 매입한 다심케이 블 a,c ¦ A1 ¦ ¦ 4 ¦ ¦ ¦ 목재 벽면 또는 석재 벽면에 직접 접촉하였거나 벽에서 전선관 지름 의 0.3 배 미만의 거리에 배관된 전 선관 내의 절연 전선 또는 단심케 이블 C ¦ B1 ¦ ¦ 5 ¦ ¦ ¦ 목재 벽면 또는 석재 벽면에 직접 접촉하였거나 벽에서 전선관 지름 의 0.3 배 미만의 거리에 배관된 전 선관 내의 다심케이블 c ¦ B2 ¦ ¦ 비고 1 이 ¦ 그림은 실제 제품 또는 ¦ 설치 예를 나타낸 것이 ¦ ¦ ¦ 아니라 설명한 ¦ 설치방법을 나타낸 것이다. ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 비고 2 a,b ¦ 등의 주는 표 ¦ A.52.3 의 ¦ 마지막 페이지에 ¦ ¦ 기술되어 있다. ¦ ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 19 | {}
9a44edf0-caa7-4ba9-9013-dba8404a6098 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 A.52.3 전류 용량 확보를 위한 설치방법의 예(계속) ¦ 항목 번호 ¦ 설치 방법 ¦ 설명 ¦ 전류 용량 확보를 위한 표준 설치방법 (부속서 B 참조) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 6 7 ¦ 6 7 ¦ 목재 벽면 또는 석재 벽면에 직접 접촉한 케이블 트렁킹(다중 격실 트렁킹 포함) 내의 절연전선 또는 단심케이블 수평 배관 b - 수직 배관 b,c ¦ B1 ¦ ¦ 8 9 ¦ 8 9 ¦ 목재 벽면 또는 석재 벽면에 직접 접촉한 케이블 트렁킹(다중격실 트 렁킹 포함) 내의 다심케이블 - 수평 포설 b - 수직 포설 b,c ¦ 검토 중 d B2 를 사용할 수 있음. ¦ ¦ 10 ¦ ¦ 현수형 케이블 트렁킹 내부의 절연 전선 또는 단심케이블 b ¦ B1 ¦ ¦ 11 ¦ 10 11 ¦ 현수형 케이블 트렁킹 내부의 다심 케이블 b ¦ B2 ¦ ¦ 12 ¦ ¦ 몰딩 내부의 절연전선 또는 단심케 이블 c,e ¦ A1 ¦ ¦ 15 ¦ ¦ 전선관 내부의 절연전선 또는 문틀 (architrave) 내의 단심케이블이나 다심케이블 c,f ¦ A1 ¦ ¦ 16 ¦ ¦ 전선관 내부의 절연전선 또는 창틀 (window frames) 내부의 단심케이 블이나 다심케이블 c,f ¦ A1 ¦ ¦ 20 ¦ ¦ 단심케이블 또는 다심케이블 목재 벽 또는 석재 벽에 고정되 어 있거나 벽과 의 거리가 케이 블 지름의 0.3 배 이내인 경우 C ¦ C ¦ ¦ 21 ¦ ¦ 단심 또는 다심케이블: 목재 또는 석재 천장에 직접 고 정된 경우 ¦ C, 표 B.52.17 의 항목 3 ¦ ¦ 22 ¦ ¦ 단심 또는 다심케이블: 천장과 거리를 두고 설치된 경우 ¦ 검토 중. 방법 E 를 쓰는 것이 가능 ¦ 20 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
422bd1cf-daf8-4ade-ad90-4626c36ea2ae | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 A.52.3 전류 용량 확보를 위한 설치방법의 예(계속) ¦ 항목 번호 ¦ 설치 방법 ¦ 설명 ¦ 전류 용량 확보를 위한 표준 설치방법 (부속서 B 참조) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 23 ¦ ¦ 현수형 전류 사용 기기의 고정 설비 ¦ C, 표 B.52.17 의 항목 3 ¦ ¦ 30 ¦ +20.3De ≥ 0.3De ¦ 단심 또는 다심케이블: 수직 또는 수평으로 배치되는 비천 공 트레이에 포설 c,h ¦ C, 표 B.52.17 의 항목 2 ¦ ¦ 31 ¦ - -≥0.3De ≥ 0.3De ¦ 단심 또는 다심케이블: 수직 또는 수평으로 배치되는 천공 형 트레이에 포설 c,h 비고 설명은 B.52.6.2 참조 ¦ E 또는 F ¦ ¦ 32 ¦ ~≥0.3De - ≥0.3De ¦ 단심 또는 다심케이블: 수직 또는 수평으로 배치되는 케이 블 지지대 또는 와이어 메시 트레 이에 포설 c,h ¦ E 또는 F ¦ ¦ 33 ¦ ¦ 단심 또는 다심케이블: 벽과 의 거리가 케이블 지름의 0.3 배 이상인 경우 ¦ E 또는 F 또는 방법 G g ¦ ¦ 34 ¦ ¦ 단심 또는 다심케이블: 케이블 래더에 포설 C ¦ E 또는 F ¦ ¦ 35 ¦ ¦ 조가선 또는 고정벨트(harness)에 매달려 있거나 일체로 된 단심 또 는 다심케이블 ¦ E 또는 F ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 21 | {}
ada6d7f2-63a4-4a74-8280-6c5a9f0fbc3f | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 A.52.3 전류 용량 확보를 위한 설치방법의 예(계속) ¦ 항목 번호 ¦ 설치 방법 ¦ 설명 ¦ 전류 용량 확보를 위한 표준 설치방법 (부속서 B 참조) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 36 ¦ ¦ 애자 위의 나선 또는 절연전선 ¦ G ¦ ¦ 40 ¦ De ¦ 건물 내 빈 공간(building void)의 단 심 또는 다심케이블 c,h,i ¦ 1.5 De ≤ V < 5 De B2 5 De ≤ V < 20 De B1 ¦ ¦ 41 ¦ ↑ De ¦ 건물 내 빈 공간에 설치된 전선관 c, i, j,k 의 절연전선 ¦ 1.5 De≤ V<20 De B2 V≥20 De B1 ¦ ¦ 42 ¦ ¦ 건물 내 빈 공간에 설치된 전선관 내의 단심 또는 다심케이블 c,k ¦ 검토 중. 다음을 사용할 수 있다. 1.5 De ≤ V < 20 De B2 V≥ 20 De B1 ¦ ¦ 43 ¦ De ¦ 건물 내 빈 공간에 설치된 케이블 덕트 내의 절연전선 c, i, j,k ¦ 1.5 De ≤ V < 20 De B2 V≥ 20 De B1 ¦ ¦ 44 ¦ De ¦ 건물 내 빈 공간에 설치된 케이블 덕트의 다심 또는 단심케이블 c,k ¦ 검토 중 다음을 사용할 수 있다. 1.5 De ≤ V < 20 De B2 V≥ 20 De B1 ¦ ¦ 45 ¦ ¦ 열저항률이 2K · m/W 이하인 석 재 내부에 설치된 케이블덕트 내의 절연전선 c,h,i ¦ 1.5 De ≤ V < 5 De B2 5 De ≤ V < 50 De B1 ¦ ¦ 46 ¦ V De] ¦ 열저항률이 2K · m/W 이하인 석 재 내부에 설치된 케이블덕트 내의 단심 또는 다심케이블 C ¦ 검토 중 다음을 사용할 수 있다. 1.5 De ≤ V < 20 De B2 V≥ 20 De B1 ¦ ¦ 47 ¦ V D ¦ 단심 또는 다심케이블 천장의 빈 공간에 설치된 경우 이중바닥에 설치된 경우 h,i ¦ 1.5 De ≤ V < 5 De B2 5 De ≤ V < 50 De B1 ¦ ¦ 50 ¦ ¦ 바닥면과 수평인 케이블트렁킹 내 의 절연전선 또는 단심케이블 ¦ B1 ¦ 22 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
911dfac7-bbb3-453e-a3af-04689112d3b7 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 A.52.3 전류 용량 확보를 위한 설치방법의 예(계속) ¦ 항목 번호 ¦ 설치 방법 ¦ 설명 ¦ 전류 용량 확보를 위한 표준 설치방법 (부속서 B 참조) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 51 ¦ ¦ 바닥면과 수평인 케이블트렁킹 내 의 다심케이블 ¦ B2 ¦ ¦ 52 ¦ TV TV ICT ICT ⑧⊙⊙ 52 53 ¦ 벽면과 평평하게 설치된 케이블 트 렁킹 내부의 절연전선 또는 단심케 이블 C ¦ B1 ¦ ¦ 53 ¦ TV TV ICT ICT ⑧⊙⊙ 52 53 ¦ 벽면과 평평하게 설치된 트렁킹 내 부의 다심케이블 c ¦ B2 ¦ ¦ 54 ¦ ↑ De ¦ 수평 또는 수직으로 설치된 비천공 형 케이블 채널 내 전선관의 절연 전선 또는 단심케이블 c,i,l,n ¦ 1.5 De ≤ V < 20 De B2 V≥ 20De B1 ¦ ¦ 55 ¦ ¦ 바닥에 설치된 개방 또는 환기 케이블 채널 내 전선관의 절연전 선 m,n ¦ B1 ¦ ¦ 56 ¦ ¦ 수평 또는 수직으로 설치된 개방 또는 환기 케이블 채널 내 외장 단 심 또는 다심케이블 n ¦ B1 ¦ ¦ 57 ¦ ¦ 열저항률이 2K · m/W 이하인 석 재 내부에 직접 설치된 단심 또는 다심케이블 기계적 손상에 대한 추가 보호 장 치가 없는 경우 o,p ¦ C ¦ ¦ 58 ¦ ¦ 열저항률이 2K · m/W 이하인 석 재 내부에 직접 설치된 단심 또는 다심케이블 기계적 손상에 대한 추가 보호 장 치가 있는 경우 o,p ¦ C ¦ ¦ 59 ¦ ¦ 석재 내부에 설치된 전선관 내의 절연전선 또는 단심케이블 p ¦ B1 ¦ ¦ 60 ¦ ¦ 석재 내부에 설치된 전선관 내의 다심케이블 p ¦ B2 ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 23 | {}
ca25824e-f683-4fdd-9c14-687875cdbcf5 | KSCIEC60364-5-52_KR | KS CIEC 60364-5-52:2009 표 A.52.3 전류 용량 확보를 위한 설치방법의 예(계속) ¦ 항목 번호 ¦ 설치 방법 ¦ 설명 ¦ 전류 용량 확보를 위한 표준 설치방법 (부속서 B 참조) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 70 ¦ ¦ 지중 매설한 전선관 또는 케이블덕 트 내의 다심케이블 ¦ D1 ¦ ¦ 71 ¦ ¦ 지중 매설한 전선관 또는 케이블덕 트 내의 단심케이블 ¦ D1 ¦ ¦ 72 ¦ ¦ 지중에 직접 매설한 단심 또는 다 심 외장 케이블 - 기계적 추가 보호가 없는 경우 q ¦ D2 ¦ ¦ 73 ¦ ¦ 지중에 직접 매설한 단심 또는 다 심 외장 케이블 - 기계적 추가 보호가 있는 경우 q ¦ D2 ¦ ¦ a 벽 내면의 열전도율은 10 W/m2 · K 이상이어야 한다. b 부속서 B 의 설치 방법 B1, B2 에서 해당 수치는 단일 회로에 관한 것이다. 트렁킹 안에 하나 이 상의 회로가 있는 경우, 표 B.52.17 의 그룹 저감 계수를 적용할 수 있다. 이때 내부 격벽의 존재 여부는 무관하다. C 케이블이 수직으로 설치되어 있고 환기가 제한적인 경우 주의 를 요한다. 수직부 상단의 주변 온 도가 상당히 높아질 수 있다. 이 부분은 검토 중이다. d 설치방법 B2 의 수치를 이용할 수 있다. e 건축 자재와 공극을 고려하여 외함의 열저항률은 좋지 못한 것으로 가정한다. 열저항률이 설치 방법 6 또는 7 과 대등한 경우, 참조 설치방법 B1 을 사용하는 것이 가능하다. f 건축 자재와 공극을 고려하여 외함의 열저항률은 좋지 못한 것으로 가정한다. 열저항률이 설치 방법 6, 7,8 또는 9 와 대등한 경우, 참조 설치방법 B1 또는 B2 를 사용하는 것이 가능하다. g 표 B.52.17 의 계수 또한 사용할 수 있다. h De = 다심케이블의 바깥지름 단심케이블이 삼각배치로 결합되어 있는 경우, 케이블 지름의 2.2 배 - 단심케이블이 수평으로 놓여 있는 경우, 케이블 지름의 3 배 V= 석재 덕트 또는 공간의 크기 또는 지름 중 작은 것 또는 사각형 덕트, 바닥 또는 천장 공간 또는 통로의 수직 깊이. 통로의 깊이가 폭보다 중요하다. De = 전선관의 바깥지름 또는 케이블덕트의 수직 깊이 ¦ a 벽 내면의 열전도율은 10 W/m2 · K 이상이어야 한다. b 부속서 B 의 설치 방법 B1, B2 에서 해당 수치는 단일 회로에 관한 것이다. 트렁킹 안에 하나 이 상의 회로가 있는 경우, 표 B.52.17 의 그룹 저감 계수를 적용할 수 있다. 이때 내부 격벽의 존재 여부는 무관하다. C 케이블이 수직으로 설치되어 있고 환기가 제한적인 경우 주의 를 요한다. 수직부 상단의 주변 온 도가 상당히 높아질 수 있다. 이 부분은 검토 중이다. d 설치방법 B2 의 수치를 이용할 수 있다. e 건축 자재와 공극을 고려하여 외함의 열저항률은 좋지 못한 것으로 가정한다. 열저항률이 설치 방법 6 또는 7 과 대등한 경우, 참조 설치방법 B1 을 사용하는 것이 가능하다. f 건축 자재와 공극을 고려하여 외함의 열저항률은 좋지 못한 것으로 가정한다. 열저항률이 설치 방법 6, 7,8 또는 9 와 대등한 경우, 참조 설치방법 B1 또는 B2 를 사용하는 것이 가능하다. g 표 B.52.17 의 계수 또한 사용할 수 있다. h De = 다심케이블의 바깥지름 단심케이블이 삼각배치로 결합되어 있는 경우, 케이블 지름의 2.2 배 - 단심케이블이 수평으로 놓여 있는 경우, 케이블 지름의 3 배 V= 석재 덕트 또는 공간의 크기 또는 지름 중 작은 것 또는 사각형 덕트, 바닥 또는 천장 공간 또는 통로의 수직 깊이. 통로의 깊이가 폭보다 중요하다. De = 전선관의 바깥지름 또는 케이블덕트의 수직 깊이 ¦ a 벽 내면의 열전도율은 10 W/m2 · K 이상이어야 한다. b 부속서 B 의 설치 방법 B1, B2 에서 해당 수치는 단일 회로에 관한 것이다. 트렁킹 안에 하나 이 상의 회로가 있는 경우, 표 B.52.17 의 그룹 저감 계수를 적용할 수 있다. 이때 내부 격벽의 존재 여부는 무관하다. C 케이블이 수직으로 설치되어 있고 환기가 제한적인 경우 주의 를 요한다. 수직부 상단의 주변 온 도가 상당히 높아질 수 있다. 이 부분은 검토 중이다. d 설치방법 B2 의 수치를 이용할 수 있다. e 건축 자재와 공극을 고려하여 외함의 열저항률은 좋지 못한 것으로 가정한다. 열저항률이 설치 방법 6 또는 7 과 대등한 경우, 참조 설치방법 B1 을 사용하는 것이 가능하다. f 건축 자재와 공극을 고려하여 외함의 열저항률은 좋지 못한 것으로 가정한다. 열저항률이 설치 방법 6, 7,8 또는 9 와 대등한 경우, 참조 설치방법 B1 또는 B2 를 사용하는 것이 가능하다. g 표 B.52.17 의 계수 또한 사용할 수 있다. h De = 다심케이블의 바깥지름 단심케이블이 삼각배치로 결합되어 있는 경우, 케이블 지름의 2.2 배 - 단심케이블이 수평으로 놓여 있는 경우, 케이블 지름의 3 배 V= 석재 덕트 또는 공간의 크기 또는 지름 중 작은 것 또는 사각형 덕트, 바닥 또는 천장 공간 또는 통로의 수직 깊이. 통로의 깊이가 폭보다 중요하다. De = 전선관의 바깥지름 또는 케이블덕트의 수직 깊이 ¦ a 벽 내면의 열전도율은 10 W/m2 · K 이상이어야 한다. b 부속서 B 의 설치 방법 B1, B2 에서 해당 수치는 단일 회로에 관한 것이다. 트렁킹 안에 하나 이 상의 회로가 있는 경우, 표 B.52.17 의 그룹 저감 계수를 적용할 수 있다. 이때 내부 격벽의 존재 여부는 무관하다. C 케이블이 수직으로 설치되어 있고 환기가 제한적인 경우 주의 를 요한다. 수직부 상단의 주변 온 도가 상당히 높아질 수 있다. 이 부분은 검토 중이다. d 설치방법 B2 의 수치를 이용할 수 있다. e 건축 자재와 공극을 고려하여 외함의 열저항률은 좋지 못한 것으로 가정한다. 열저항률이 설치 방법 6 또는 7 과 대등한 경우, 참조 설치방법 B1 을 사용하는 것이 가능하다. f 건축 자재와 공극을 고려하여 외함의 열저항률은 좋지 못한 것으로 가정한다. 열저항률이 설치 방법 6, 7,8 또는 9 와 대등한 경우, 참조 설치방법 B1 또는 B2 를 사용하는 것이 가능하다. g 표 B.52.17 의 계수 또한 사용할 수 있다. h De = 다심케이블의 바깥지름 단심케이블이 삼각배치로 결합되어 있는 경우, 케이블 지름의 2.2 배 - 단심케이블이 수평으로 놓여 있는 경우, 케이블 지름의 3 배 V= 석재 덕트 또는 공간의 크기 또는 지름 중 작은 것 또는 사각형 덕트, 바닥 또는 천장 공간 또는 통로의 수직 깊이. 통로의 깊이가 폭보다 중요하다. De = 전선관의 바깥지름 또는 케이블덕트의 수직 깊이 ¦ ¦ ¦ ¦ ¦ ¦ ¦ I ¦ I ¦ I ¦ I ¦ ¦ j I ¦ j I ¦ j I ¦ j I ¦ ¦ De = 전선관의 바깥지름 ¦ De = 전선관의 바깥지름 ¦ De = 전선관의 바깥지름 ¦ De = 전선관의 바깥지름 ¦ ¦ m 설치 방법 55 에 따라 설치된 다심케이블의 경우, 참조 방법 B2 의 허용전류 등급을 적용한다. n ¦ m 설치 방법 55 에 따라 설치된 다심케이블의 경우, 참조 방법 B2 의 허용전류 등급을 적용한다. n ¦ m 설치 방법 55 에 따라 설치된 다심케이블의 경우, 참조 방법 B2 의 허용전류 등급을 적용한다. n ¦ m 설치 방법 55 에 따라 설치된 다심케이블의 경우, 참조 방법 B2 의 허용전류 등급을 적용한다. n ¦ ¦ 이 설치 방법은 부스러기 등의 축적으로 인한 화재 위험 및 전류 용량 감소를 막을 수 있도록 관계자외 출입 제한 조치가 취해진 지역에 한해 권장한다. ¦ 이 설치 방법은 부스러기 등의 축적으로 인한 화재 위험 및 전류 용량 감소를 막을 수 있도록 관계자외 출입 제한 조치가 취해진 지역에 한해 권장한다. ¦ 이 설치 방법은 부스러기 등의 축적으로 인한 화재 위험 및 전류 용량 감소를 막을 수 있도록 관계자외 출입 제한 조치가 취해진 지역에 한해 권장한다. ¦ 이 설치 방법은 부스러기 등의 축적으로 인한 화재 위험 및 전류 용량 감소를 막을 수 있도록 관계자외 출입 제한 조치가 취해진 지역에 한해 권장한다. ¦ ¦ 0 도체 단면적이 16 mm2 이하인 케이블의 경우, 전류 용량이 더 높을 수 있다. 열저항률은 2K m/W 이하이다. "석재"라 함은 벽돌, 콘크리트, 석고 등의 종류(단열 물 ¦ 0 도체 단면적이 16 mm2 이하인 케이블의 경우, 전류 용량이 더 높을 수 있다. 열저항률은 2K m/W 이하이다. "석재"라 함은 벽돌, 콘크리트, 석고 등의 종류(단열 물 ¦ 0 도체 단면적이 16 mm2 이하인 케이블의 경우, 전류 용량이 더 높을 수 있다. 열저항률은 2K m/W 이하이다. "석재"라 함은 벽돌, 콘크리트, 석고 등의 종류(단열 물 ¦ 0 도체 단면적이 16 mm2 이하인 케이블의 경우, 전류 용량이 더 높을 수 있다. 열저항률은 2K m/W 이하이다. "석재"라 함은 벽돌, 콘크리트, 석고 등의 종류(단열 물 ¦ ¦ p 석재의 · 질이 아닌)를 포함하는 것으로 본다. ¦ p 석재의 · 질이 아닌)를 포함하는 것으로 본다. ¦ p 석재의 · 질이 아닌)를 포함하는 것으로 본다. ¦ p 석재의 · 질이 아닌)를 포함하는 것으로 본다. ¦ ¦ q 토양의 열저항률이 2.5K · m/W 정도인 경우, 직접 매설된 케이블도 이 기준에 적용이 된다. 토 양의 열저항률이 이보다 낮은 경우, 직접 매설된 케이블의 전류 용량은 덕트 내의 케이블보다 훨씬 커지게 된다. ¦ q 토양의 열저항률이 2.5K · m/W 정도인 경우, 직접 매설된 케이블도 이 기준에 적용이 된다. 토 양의 열저항률이 이보다 낮은 경우, 직접 매설된 케이블의 전류 용량은 덕트 내의 케이블보다 훨씬 커지게 된다. ¦ q 토양의 열저항률이 2.5K · m/W 정도인 경우, 직접 매설된 케이블도 이 기준에 적용이 된다. 토 양의 열저항률이 이보다 낮은 경우, 직접 매설된 케이블의 전류 용량은 덕트 내의 케이블보다 훨씬 커지게 된다. ¦ q 토양의 열저항률이 2.5K · m/W 정도인 경우, 직접 매설된 케이블도 이 기준에 적용이 된다. 토 양의 열저항률이 이보다 낮은 경우, 직접 매설된 케이블의 전류 용량은 덕트 내의 케이블보다 훨씬 커지게 된다. ¦ 24 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
0bda1319-e81d-4e2c-b3e8-9b0b51ea25ab | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 부속서 B (참고) 허용전류 B.52.1 머리말 이 부속서의 권장 사항의 목적은 통상적인 사용 시 상당 기간 동안 통과 전류의 열효과 를 받는 도체 와 절연물에 대해 충분한 수명을 부여하는 데 있다. 그 외에 도체 단면적 선정에 있어서 고려하여야 할 사항은 감전 보호(KS C IEC 60364-4-41), 열적 영향에 대한 보호(KS C IEC 60364-4-42), 과전류 보 호(KS C IEC 60364-4-43), 전압강하(이 표준의 525 절), 전선이 접속되는 기기 단자의 제한 온도(이 표 준의 526 절) 등이 있다. 현시점에서, 이 부속서는 공칭 전압 교류 1kV 또는 직류 1.5kV 이하의 비외장형 케이블(non- armoured cables)이나 절연전선에만 적용한다. 이 부속서 내용은 외장형 다심케이블에는 적용할 수 있지만, 표준은 외장형 단심케이블에는 적용하지 않는다. 비고 1 외장형(armored) 단심케이블이 사용되는 경우, 이 표준에 나타낸 허용전류 용량을 상당히 감 소시켜야 한다. 케이블 제조자의 자문을 구함이 좋다. 이것은 싱글웨이 금속 덕트(single way metallic ducts) 내의 비외장형 단심케이블에도 적용할 수 있다(521.5 참조). 비고 2 외장형 다심케이블이 사용되는 경우, 이 부속서에 주어진 값은 안전한 범위에 들 것이다. 비고 3 절연전선의 허용전류는 단심케이블의 허용전류와 동일하다. 표 B.52.2~B.52.13 값은 비외장 케이블에 적용하며 KS C IEC 60502 에 규정된 사이즈와 KS C IEC 60228 에 규정된 도체의 저항을 사용해 IEC 60287 시리즈에 나타낸 방법으로 산출하였다. 케이블 구 조(예를 들면 도체의 형상)는 실제적으로 매우 다양하고 제조상의 허용오차도 존재하여 결과 적으로는 가능한 케이블 사이즈의 범위가 매우 넓다. 따라서 가능한 허용전류의 범위 또한 넓어지게 된다. 표 시된 허용전류는 이 폭에 대해 안전한 범위의 값을 고려하면서 도체 단면적에 대한 도표로 나타내었 을 때 완만한 곡선 위에 있도록 선정했다. 단면적 25 mm2 이상인 도체의 다심케이블은 원형 또는 성형 도체 중 어느 쪽에도 적용할 수 있다. 표시된 값은 성형 도체에 적합한 사이즈로부터 산출하였다. B.52.2 주위온도 B.52.2.1 이 부속서의 표에 실린 허용전류 값은 기준 주위온도를 다음과 같이 가정한 것이다. 공기 중의 절연전선 및 케이블에 대해서는 설치방법과 상관없이: 30 °C 매설 케이블에 대해서는 토양에 직접 또는 지중 덕트 내에 설치 시: 20 °C B.52.2.2 전선 또는 케이블의 사용 장소의 주위온도가 기준 주위온도와 다른 경우는 표 B.52.14 및 표 B.52.15 에 나타낸 적절한 보정계수를 표 B.52.2~표 B.52.13 의 허용전류 값에 적용해야 한다. 다 만 매설 케이블의 경우, 토양의 온도가 기준 주위온도로부터 5K 범위를 초과 하는 기간이 연간 몇 주간 밖에 되지 않을 때에는 보정이 필요 없다. 25 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
b50a8dd8-e397-4107-83af-b7c9f7f3c188 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 비고 공기 중의 케이블과 전선의 경우, 주위온도가 가끔 기준 주위온도를 넘을 때 표의 허용전류 값 을 보정 없이 사용할 가능성에 대해서는 검토 중이다. B.52.2.3 표 B.52.14 및 표 B.52.15 의 보정계수는 태양 또는 기타 적외선 방사로 인한 온도 상승에 대하여는 고려하지 않는다. 케이블 또는 전선이 이러한 방사를 받는 경우, 허용전류는 IEC 60287 시 리즈에서 규정하는 방법으로 산출할 수 있다. B.52.3 토양의 열저항률 지중 케이블에 대해 이 부속서에서 표시한 허용전류는 토양의 열저항률로 2.5 K · m/W 를 채택하고 있다. 토질 및 지리적인 위치가 지정되어 있지 않은 상황에서 세계 어느 곳에서나 이 값을 사용하는 데는 주의 가 필요하다(KS C IEC 60287-3-1 참조). 실제의 토양열 저항률이 2.5 K · m/W 보다 큰 장소에서는 허용전류를 적절히 감소시키든가, 케이블 바 로 주위의 토양을 보다 적절한 재료로 치환해야 한다. 보통 매우 건조한 토양 조건인 경우에 이런 경우가 인정될 수 있다. 토양의 열저항률이 2.5 K · m/W 와 다른 경우에 대한 보정계수를 표 B.52.16 에 실었다. 비고 지중 케이블에 대해서 이 부속서에서 표시한 허용전류는 건축물의 내부 및 주위에 포설한 경 우만을 대상으로 하고 있다. 기타 설비에 대해서는 조사를 통해 실제 통전 용량에 적합한 열 저항률의 정확한 값을 얻을 수 있는 경우, 허용전류 값은 IEC 60287 시리즈의 계산 방법을 통 해 산출하거나 케이블 제조자로부터 구해도 된다. B.52.4 복수회로로 포설된 그룹 B.52.4.1 표 B.52.1 의 A~D 형 설비 표 B.52.2~표 B.52.7 에 나타낸 허용전류는 다음의 전선 개수로 구성된 단일 회로에 적용한다. 2 개의 절연전선 혹은 2 개의 단심케이블 또는 한 개의 2 심 케이블 3 개의 절연전선 혹은 3 개의 단심케이블 또는 한 개의 3 심 케이블 이 이상의 전선 또는 케이블을 동일 그룹으로서 포설한 경우는 접촉이 되지 않도록 포설된 나도체 무기질 절연 케이블을 제외하고는 표 B.52.17~ 표 B.52.19 에서 규정하는 보정계수를 적용한다. 비고 집합 보정계수는 모든 선도체가 부하율 100 %로 연속 정상 운전하는 것을 기초로 하여 계산 하고 있다. 설비의 운전 조건에 의해 부하가 100 % 미만이 되는 경우, 이 보정계수는 더 커도 좋다. B.52.4.2 표 B.52.1 의 E 형, F 형 설비 표 B.52.8~ 표 B.52.13 의 허용전류는 기준 설치방법에 따라 적용한다. 천공형 케이블 트레이, 클리트 등과 같은 설비에 대해 단일 회로와 집합 회로의 허용전류는 모두 표 B.52.8~표 B.52.13 에 나타낸 대로, 개방 기중의 관련 절연전선이나 케이블 배선에 대한 전류 값을 곱하고 표 B.52.20 및 표 B.52.21 에 주어진 설비 및 집합 보정계수를 통해 얻는다. 접촉이 되지 않도 록 포설된 나도체 무기질 절연 케이블에 대해서는 그룹 보정계수가 필요하지 않다. 표 B.52.7 및 표 B.52.9 참조 26 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
834d1ab4-2687-4bbd-a4eb-035117917011 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 다음 비고는 B.52.4.1 과 B.52.4.2 에 관련된 것이다. 비고 1 집합 저감 계수는 대상으로 삼은 도체 사이즈의 범위, 케이블의 종류와 설치 조건에 대한 평 균으로 계산하고 있다. 일부 사례에서는 보다 정확하게 계산하는 것이 바람직할 수 있다. 비고 2 집합 저감 계수는 유사한 동등 부하(similar equally loaded)의 절연전선이나 케이블로 구성된 집합을 기본으로 계산한다. 사이즈가 다른 케이블이나 절연전선으로 구성된 집합일 경우, 작 은 쪽의 케이블에 걸쳐 있는 전류에 주의 를 기울여야 한다(B.52.5 참조). B.52.5 다른 사이즈를 포함한 그룹 표에 나타낸 그룹 저감 계수는 거의 유사한 동등 부하 케이블로 구성된 그룹에 적용할 수 있다. 다 른 사이즈의 유사한 동등 부하 절연전선이나 케이블을 포함한 그룹의 저감 계수 계산은 그룹 전체 수와 사이즈의 혼합에 따라 달라진다. 그러한 저감 계수는 표로 만들 수는 없고 각 그룹별로 계산해 야 한다. 이 계수의 계산 방법은 이 표준의 범위 밖이다. 권장할 만한 몇 가지 예를 아래에 나타낸다. 비고 전선단면적이 세 개 이상의 인접 표준 단면적 전선이 모인 그룹인 경우, 다른 사이즈를 포함한 그룹으로 간주할 수 있다. 유사한 케이블 그룹은 모든 케이블의 허용 전류량이 동일한 최대 허 용 도체 온도를 기본으로 하고 그룹 내 전선 단면적의 범위가 세 개 이하의 인접한 표준 단면 적으로 구성된 경우, 하나의 그룹으로 간주한다. B.52.5.1 전선관, 케이블트렁킹 또는 케이블덕트의 그룹 전선관, 케이블트렁킹 또는 케이블덕트에서 다른 사이즈의 절연전선이나 케이블이 포함된 그룹의 경 우, 안전한 범위의 그룹 저감 계수는 다음과 같다. 1 F= Vn 여기에서 F : 그룹 저감 계수 n : 그룹 내의 다심케이블 또는 회로 수 이 방정식으로 구한 그룹 저감 계수는 더 작은 사이즈의 도체나 케이블의 과부하 위험을 줄일 수 있 으나 더 큰 단면적의 도체나 케이블 사용에 있어서는 비효율적일 수 있다. 이러한 비효율성은 동일 그룹 내에서 큰 사이즈와 작은 사이즈의 케이블이나 절연전선을 혼용하지 않으면 피할 수 있다. 전선관, 케이블트렁킹 또는 케이블덕트 내에 사이즈가 다른 절연전선이나 케이블을 포함한 그룹에 맞는 계산 방법을 이용하면 보다 정확한 그룹 저감 계수를 구할 수 있다. 이 문제는 검토 중에 있다. B.52.5.2 트레이 그룹 한 그룹에 사이즈가 서로 다른 케이블이 포함되어 있는 경우, 사이즈가 작은 쪽의 부하전류에 주의 한다. 다른 사이즈의 케이블을 포함한 그룹용의 계산 방법을 사용하는 것이 바람직하다. B.52.5.1 에 따라 구한 그룹 저감 계수는 안전한 쪽의 값을 나타낸다. 이 문제는 검토 중에 있다. 27 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
8600405e-eef0-40e4-a1a6-c6a115e6ef6b | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 B.52.6 설치방법 B.52.6.1 참조 방법 참조 방법이란 시험이나 계산으로 결정된 허용전류 용량에 대한 설치방법이다. a) 참조 방법 A1, 표 A.52.3 항목 1(단열 처리된 벽 내 전선관의 절연전선) 및 A2, 표 A.52.3 항목 2 (단 열 처리된 벽 내 전선관의 다심케이블): 외벽이 내후성이고, 내벽은 목재나 최소 10 W/m2 · K 이상 의 열전도율을 가진 목재성 재질로 구성한다. 전선관은 내벽에 가깝게, 그러나 꼭 접촉할 필요는 없이 고정시킨다. 케이블에서 발생한 열은 내벽만을 통과 하는 것으로 간주한다. 전선관은 금속 또 는 플라스틱 소재로 할 수 있다. b) 참조 방법 B1, 표 A.52.3 항목 4(목재 벽면 전선관의 절연전선) 및 B2, 표 A.52.3 항목 5(목재 벽 면 전선관의 다심케이블): 전선관과 벽면 사이의 간격이 전선관 지름의 0.3 배 미만이 되도록 목재 벽면에 설치한 전선관으로 금속 또는 플라스틱으로 할 수 있다. 전선관이 석조벽에 고정된 경우, 케이블이나 절연전선의 허용전류 용량은 더 높을 수 있다. 이 문제는 검토 중에 있다. c) 참조 방법 C, 표 A.52.3 항목 20(목재 벽면에 설치한 단심 또는 다심케이블): 케이블과 벽면 사이 의 간격이 케이블 지름의 0.3 배 미만이 되도록 목재 벽면에 설치한 케이블. 케이블이 석조 벽면에 고정 또는 매입된 경우, 허용전류 용량이 더 높을 수 있다. 이 문제는 검토 중에 있다. 비고 1 "석조"란 벽돌, 콘크리트, 석고 등을 포함하는 것으로 본다. d) 참조 방법 D1, 표 A.52.3 항목 70(지중 내 덕트의 다심케이블) 및 D2(지중에 직접 매설하도록 설계 된 다심케이블-제조자 지시에 따른다): 열저항률이 2.5K · m/W 이고 깊이가 0.7 m 인 토양과 직접 접촉시켜 설치한 지름 100 mm 의 플라스틱, 도기 또는 금속제 덕트에 인입한 케이블(B.52.3 도 참 조). 열저항률이 2.5 K · m/W 이고 깊이가 0.7 m 인 토양과 직접 접촉시켜 설치한 케이블(B.52.3 도 참조) 비고 2 지중에 설치한 케이블에서는 시스의 온도를 제한하는 것이 중요하다. 시스의 열이 토양을 건조시키면 열저항률이 증가하여 케이블이 과부하될 수 있다. 가열을 피하는 한 가지 방법 은 90 °C 용으로 설계된 케이블일지라도 70 °C 전선 온도에 해당하는 표를 적용하는 것이다. e) 참조 방법 E, F, G, 표 A.52.3 항목 32, 33(기중의 단심 또는 다심케이블): 모든 열 방사가 방해받지 않도록 지지된 케이블. 태양 방사와 기타 열원에 의한 가열을 고려한다. 공기의 자유 대류가 방해 받지 않도록 주의 한다. 실제로 케이블과 인접물 표면과 의 간격이 다심케이블의 경우 케이블 바깥 지름의 0.3 배 이상이거나 단심케이블에 대해서는 케이블 지름 이상이라면 공기 중 개방 조건에 적합한 허용전류로 사용하기에 충분하다. B.52.6.2 기타 방법 a) 바닥면 설치 또는 천장 아래에 매입 케이블: 참조 방법 C 와 유사하나 천장 아래 설치 케이블 정격 은 공기의 자유 대류 감소 때문에 벽이나 바닥에 대한 값보다 약간 감소한다(표 B.52.17 참조). b) 케이블 트레이 시스템: 통풍형 케이블 트레이는 케이블 부착용 나사를 쉽게 사용할 수 있도록 규 칙적으로 배열된 구멍을 갖고 있다. 통풍형 케이블 트레이의 허용전류는 표면적의 30 %가 되는 트레이를 사용한 시험에서 얻어진 값이다. 구멍이 차지하는 비율이 표면적의 30 % 미만을 차지하 는 경우, 그 트레이는 비천공으로 본다. 이는 참조방법 C 와 유사하다. c) 케이블 래더 시스템: 이 설비는 케이블 주위의 공기의 대류저항이 최소가 되는 구조를 취한다. 즉, 케이블이 지지하는 금속 부분이 설계 면적의 10 % 미만이 되도록 한다. 28 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c4bb74d3-88f1-41d7-8357-e0ac58a6c230 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 d) 케이블 클리트, 케이블 타이: 케이블을 케이블 트레이에 고정하거나 여러 케이블을 한데 묶어 주 는 장치 e) 케이블 행거: 케이블을 길이 방향으로 일정 간격마다 잡아 주고 케이블 주변에 상당히 자유로운 공기 흐름을 허용하는 케이블 지지 장치 표 B.52.1 ~표 B.52.21 에 대한 일반적 비고 비고 3 고정 전기 설비에 일반적으로 사용되는 절연전선, 케이블의 종류와 설치방법에 대한 허용 전류를 표시하였다. 표의 전류 값은 공칭 주파수가 50 Hz 또는 60 Hz 인 교류 또는 직류 에 대한 연속 정상 통전(100 %의 부하율)의 경우에 적용한다. 비고 4 표 B.52.1 은 허용전류 표에서 인용하는 참조 설치방법으로 항목을 나누었다. 모든 국가의 국내 규정에서 이들 모든 항목을 반드시 인정한 것으로 보는 것은 아니다. 비고 5 설비 설계에 컴퓨터 지원 시스템을 사용하는 경우의 편의 를 위해, 표 B.52.2~표 B.52.13 의 허용전류는 전선 사이즈에 관한 간단한 식으로 나타낼 수 있다. 이 식과 필요한 계수 는 부속서 D 에 기술하였다. f) 천장에 매입한 케이블: 참조 방법 A 와 유사하다. 천장에 매입된 단자함 내지 그와 유사한 장치 내 의 주위온도가 높을 수 있기 때문에 보정계수 적용이 필요할 수도 있다. 비고 6 천장에 설치한 단자 함이 조명 공급을 위해 쓰일 경우, 조명으로부터의 열 발산으로 표 B.52.2~B.52.5 의 값보다 주위온도가 높아질 수 있다. 또한 522.2.1 도 참조한다. 온도는 40 °C ~50 °C 범위가 될 수 있고, 표 B.52.14 에 따른 보정계수를 적용해야 한다. 표 B.52.1 - 허용전류 표의 기초가 되는 참조 설치방법 ¦ 설치방법 ¦ 설치방법 ¦ 설치방법 ¦ 표와 세로줄 ¦ 표와 세로줄 ¦ 표와 세로줄 ¦ 표와 세로줄 ¦ 표와 세로줄 ¦ 표와 세로줄 ¦ 표와 세로줄 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 설치방법 ¦ 설치방법 ¦ 설치방법 ¦ 단일 회로에 대한 허용전류 용량 ¦ 단일 회로에 대한 허용전류 용량 ¦ 단일 회로에 대한 허용전류 용량 ¦ 단일 회로에 대한 허용전류 용량 ¦ 단일 회로에 대한 허용전류 용량 ¦ 주위 온도 계수 ¦ 집합 저감 계수 ¦ ¦ 설치방법 ¦ 설치방법 ¦ 설치방법 ¦ 열가소성 절연물질 ¦ 열가소성 절연물질 ¦ 열경화성 물질절연 ¦ 열경화성 물질절연 ¦ 무기질 절연물 ¦ 주위 온도 계수 ¦ 집합 저감 계수 ¦ ¦ 설치방법 ¦ 설치방법 ¦ 설치방법 ¦ 심 개수 ¦ 심 개수 ¦ 심 개수 ¦ 심 개수 ¦ 심 개수 ¦ 주위 온도 계수 ¦ 집합 저감 계수 ¦ ¦ 설치방법 ¦ 설치방법 ¦ 설치방법 ¦ 2 ¦ 3 ¦ 2 ¦ 3 ¦ 2,3 ¦ 주위 온도 계수 ¦ 집합 저감 계수 ¦ ¦ 1 ¦ 1 ¦ 2 ¦ 3 ¦ 4 ¦ 5 ¦ 6 ¦ 7 ¦ 8 ¦ 9 ¦ ¦ ¦ 단열벽 속의 전 선관에 설치한 방 절연전선(단심케 이블) ¦ A1 ¦ B.52.2 Col. 2 ¦ B.52.4 Col.2 ¦ B.52.3 Col.2 ¦ B.52.5 Col.2 ¦ - ¦ B.52.14 ¦ B.52.17 ¦ ¦ ¦ 단열벽 속의 전 방 선관에 설치한 다심케이블 ¦ A2 ¦ B.52.2 Col.3 ¦ B.52.4 Col.3 ¦ B.52.3 Col.3 ¦ B.52.5 Col.3 ¦ - ¦ B.52.14 ¦ B.52.17, D 제외 (표 B.52.19 적용) ¦ ¦ 목재 벽면의 전 선관에 설치한 절연도체(단심케 이블) ¦ 목재 벽면의 전 선관에 설치한 절연도체(단심케 이블) ¦ B1 ¦ B.52.2 Col.4 ¦ B.52.4 Col.4 ¦ B.52.3 Col.4 ¦ B.52.5 Col.4 ¦ - ¦ B.52.14 ¦ B.52.17 ¦ ¦ 목재 벽면의 전 선관에 설치한 다심케이블 ¦ 목재 벽면의 전 선관에 설치한 다심케이블 ¦ B2 ¦ B.52.2 Col.5 ¦ B.52.4 Col.5 ¦ B.52.3 Col.5 ¦ B.52.5 Col.5 ¦ - ¦ B.52.14 ¦ B.52.17 ¦ 29 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
674c90d2-a528-481f-a4e1-be71dbf981c3 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 B.52.1 허용전류 표의 기초가 되는 참조 설치방법(계속) ¦ 설치방법 ¦ 설치방법 ¦ 표와 세로줄 ¦ 표와 세로줄 ¦ 표와 세로줄 ¦ 표와 세로줄 ¦ 표와 세로줄 ¦ 표와 세로줄 ¦ 표와 세로줄 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 설치방법 ¦ 설치방법 ¦ 단일 회로에 대한 허용전류 용량 ¦ 단일 회로에 대한 허용전류 용량 ¦ 단일 회로에 대한 허용전류 용량 ¦ 단일 회로에 대한 허용전류 용량 ¦ 단일 회로에 대한 허용전류 용량 ¦ 주위 온도 계수 ¦ 집합 저감 계수 ¦ ¦ 설치방법 ¦ 설치방법 ¦ 열가소성 절연물질 ¦ 열가소성 절연물질 ¦ 열경화성 물질절연 ¦ 열경화성 물질절연 ¦ 무기질 절연물 ¦ 주위 온도 계수 ¦ 집합 저감 계수 ¦ ¦ 설치방법 ¦ 설치방법 ¦ 심 개수 ¦ 심 개수 ¦ 심 개수 ¦ 심 개수 ¦ 심 개수 ¦ 주위 온도 계수 ¦ 집합 저감 계수 ¦ ¦ 설치방법 ¦ 설치방법 ¦ 2 ¦ 3 ¦ 2 ¦ 3 ¦ 2,3 ¦ 주위 온도 계수 ¦ 집합 저감 계수 ¦ ¦ 1 ¦ 2 ¦ 3 ¦ 4 ¦ 5 ¦ 6 ¦ 7 ¦ 8 ¦ 9 ¦ ¦ 목재 벽면의 단 심 또는 다심케 이블 ¦ C ¦ B.52.2 Col.6 ¦ B.52.4 Col.6 ¦ B.52.3 Col.6 ¦ B.52.5 Col.6 ¦ 70 °C 시스 B.52.6 105 °C 시스 B.52.7 ¦ B.52.14 ¦ B.52.17 ¦ ¦ 지중의 덕트 내 설치한 다심 케이블 ¦ 에 D1 ¦ B.52.2 Col.7 ¦ B.52.4 Col.7 ¦ B.52.3 Col.7 ¦ B.52.5 Col.7 ¦ ¦ B.52.15 ¦ B.52.19 ¦ ¦ 지중에 직접 매 설한 외장 단심 또는 다심케이블 ¦ D2 ¦ Col.8 ¦ Col.8 ¦ Col.8 ¦ Col.8 ¦ Col.8 ¦ Col.8 ¦ Col.8 ¦ ¦ 자유 공기 중의 다심케이블 벽과 의 이격 거리는 케이블 지름의 0.3 배 이상이어야 함. ¦ E ¦ 구리 B.52.10 알루미늄 B.52.11 ¦ 구리 B.52.10 알루미늄 B.52.11 ¦ 구리 B.52.12 알루미늄 B.52.13 ¦ 구리 B.52.12 알루미늄 B.52.13 ¦ 70 °C 외장 B.52.8 105 °C 외장 B.52.9 ¦ B.52.14 ¦ B.52.20 ¦ ¦ 단심케이블로 자 유 공기와 접촉 벽과 의 이격 거리 는 한 케이블 지 름 이상이어야 함. ¦ F ¦ 구리 B.52.10 알루미늄 B.52.11 ¦ 구리 B.52.10 알루미늄 B.52.11 ¦ 구리 B.52.12 알루미늄 B.52.13 ¦ 구리 B.52.12 알루미늄 B.52.13 ¦ 70 °C 외장 B.52.8 105 °C 외장 B.52.9 ¦ B.52.14 ¦ B.52.21 ¦ ¦ 자유 공기 중 단 심케이블 이격 케이블의 지름 이상이어야 함. ¦ G ¦ 구리 B.52.10 알루미늄 B.52.11 ¦ 구리 B.52.10 알루미늄 B.52.11 ¦ 구리 B.52.12 알루미늄 B.52.13 ¦ 구리 B.52.12 알루미늄 B.52.13 ¦ 70 °C 외장 B.52.8 105 °C 외장 B.52.9 ¦ B.52.14 ¦ - ¦ 30 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
22e0d7cd-9aa2-4cb0-9451-3f0b01770c9a | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 B.52.2 - 표 B.52.1 의 설치방법의 허용전류(A) PVC 절연, 2 개 부하 도체, 구리 또는 알루미늄, 도체 온도: 70 °C, 주위온도: 기중 30 °C, 지중 20 °C ¦ 도체의 공칭 단면적 mm2 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도체의 공칭 단면적 mm2 ¦ A1 ¦ A2 ¦ B1 ¦ B2 ¦ C ¦ D1 ¦ D2 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 1 ¦ 2 ¦ 3 ¦ 4 ¦ 5 ¦ 6 ¦ 7 ¦ 8 ¦ ¦ 구리 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 1.5 ¦ 14.5 ¦ 14 ¦ 17.5 ¦ 16.5 ¦ 19.5 ¦ 22 ¦ 22 ¦ ¦ 2.5 ¦ 19.5 ¦ 18.5 ¦ 24 ¦ 23 ¦ 27 ¦ 29 ¦ 28 ¦ ¦ 4 ¦ 26 ¦ 25 ¦ 32 ¦ 30 ¦ 36 ¦ 37 ¦ 38 ¦ ¦ 6 ¦ 34 ¦ 32 ¦ 41 ¦ 38 ¦ 46 ¦ 46 ¦ 48 ¦ ¦ 10 ¦ 46 ¦ 43 ¦ 57 ¦ 52 ¦ 63 ¦ 60 ¦ 64 ¦ ¦ 16 ¦ 61 ¦ 57 ¦ 76 ¦ 69 ¦ 85 ¦ 78 ¦ 83 ¦ ¦ 25 ¦ 80 ¦ 75 ¦ 101 ¦ 90 ¦ 112 ¦ 99 ¦ 110 ¦ ¦ 35 ¦ 99 ¦ 92 ¦ 125 ¦ 111 ¦ 138 ¦ 119 ¦ 132 ¦ ¦ 50 ¦ 119 ¦ 110 ¦ 151 ¦ 133 ¦ 168 ¦ 140 ¦ 156 ¦ ¦ 70 ¦ 151 ¦ 139 ¦ 192 ¦ 168 ¦ 213 ¦ 173 ¦ 192 ¦ ¦ 95 ¦ 182 ¦ 167 ¦ 232 ¦ 201 ¦ 258 ¦ 204 ¦ 230 ¦ ¦ 120 ¦ 210 ¦ 192 ¦ 269 ¦ 232 ¦ 299 ¦ 231 ¦ 261 ¦ ¦ 150 ¦ 240 ¦ 219 ¦ 300 ¦ 258 ¦ 344 ¦ 261 ¦ 293 ¦ ¦ 185 ¦ 273 ¦ 248 ¦ 341 ¦ 294 ¦ 392 ¦ 292 ¦ 331 ¦ ¦ 240 ¦ 321 ¦ 291 ¦ 400 ¦ 344 ¦ 461 ¦ 336 ¦ 382 ¦ ¦ 300 ¦ 367 ¦ 334 ¦ 458 ¦ 394 ¦ 530 ¦ 379 ¦ 427 ¦ ¦ 알루미늄 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 2.5 ¦ 15 ¦ 14.5 ¦ 18.5 ¦ 17.5 ¦ 21 ¦ 22 ¦ ¦ ¦ 4 ¦ 20 ¦ 19.5 ¦ 25 ¦ 24 ¦ 28 ¦ 29 ¦ ¦ ¦ 6 ¦ 26 ¦ 25 ¦ 32 ¦ 30 ¦ 36 ¦ 36 ¦ ¦ ¦ 10 ¦ 36 ¦ 33 ¦ 44 ¦ 41 ¦ 49 ¦ 47 ¦ ¦ ¦ 16 ¦ 48 ¦ 44 ¦ 60 ¦ 54 ¦ 66 ¦ 61 ¦ 63 ¦ ¦ 25 ¦ 63 ¦ 58 ¦ 79 ¦ 71 ¦ 83 ¦ 77 ¦ 82 ¦ ¦ 35 ¦ 77 ¦ 71 ¦ 97 ¦ 86 ¦ 103 ¦ 93 ¦ 98 ¦ ¦ 50 ¦ 93 ¦ 86 ¦ 118 ¦ 104 ¦ 125 ¦ 109 ¦ 117 ¦ ¦ 70 ¦ 118 ¦ 108 ¦ 150 ¦ 131 ¦ 160 ¦ 135 ¦ 145 ¦ ¦ 95 ¦ 142 ¦ 130 ¦ 181 ¦ 157 ¦ 195 ¦ 159 ¦ 173 ¦ ¦ 120 ¦ 164 ¦ 150 ¦ 210 ¦ 181 ¦ 226 ¦ 180 ¦ 200 ¦ ¦ 150 ¦ 189 ¦ 172 ¦ 234 ¦ 201 ¦ 261 ¦ 204 ¦ 224 ¦ ¦ 185 ¦ 215 ¦ 195 ¦ 266 ¦ 230 ¦ 298 ¦ 228 ¦ 255 ¦ ¦ 240 ¦ 252 ¦ 229 ¦ 312 ¦ 269 ¦ 352 ¦ 262 ¦ 298 ¦ ¦ 300 비고 세로줄 3,5,6, 7, 8 의 도체로 ¦ 289 ¦ 263 경우 면적이 ¦ 358 16 mm2 ¦ 308 이하인 ¦ 406 것은 원형 ¦ 296 간주한다. ¦ 336 단면적이 이를 ¦ 초과 하는 경우에 대한 값은 성형 도체와 관련된 것으로, 이 값은 원형 도체에 대해 안전하게 적용할 수 있다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 31 | {}
eb54c039-9ede-4a9f-9004-86940b20452f | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 B.52.3 - 표 B.52.1 의 설치방법의 허용전류(A) - XLPE 또는 EPR 절연, 2 개 부하 도체, 구리 또는 알루미늄, 도체 온도: 90 °C, 주위온도: 기중 30 °C, 지중 20 °C ¦ 도체의 공칭 단면적 mm2 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도체의 공칭 단면적 mm2 ¦ A1 ¦ A2 ¦ B1 ¦ B2 ¦ C ¦ D1 ¦ D2 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 1 ¦ 2 ¦ 3 ¦ 4 ¦ 5 ¦ 6 ¦ 7 ¦ 8 ¦ ¦ 구리 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 1.5 ¦ 19 ¦ 18.5 ¦ 23 ¦ 22 ¦ 24 ¦ 25 ¦ 27 ¦ ¦ 2.5 ¦ 26 ¦ 25 ¦ 31 ¦ 30 ¦ 33 ¦ 33 ¦ 35 ¦ ¦ 4 ¦ 35 ¦ 33 ¦ 42 ¦ 40 ¦ 45 ¦ 43 ¦ 46 ¦ ¦ 6 ¦ 45 ¦ 42 ¦ 54 ¦ 51 ¦ 58 ¦ 53 ¦ 58 ¦ ¦ 10 ¦ 61 ¦ 57 ¦ 75 ¦ 69 ¦ 80 ¦ 71 ¦ 77 ¦ ¦ 16 ¦ 81 ¦ 76 ¦ 100 ¦ 91 ¦ 107 ¦ 91 ¦ 100 ¦ ¦ 25 ¦ 106 ¦ 99 ¦ 133 ¦ 119 ¦ 138 ¦ 116 ¦ 129 ¦ ¦ 35 ¦ 131 ¦ 121 ¦ 164 ¦ 146 ¦ 171 ¦ 139 ¦ 155 ¦ ¦ 50 ¦ 158 ¦ 145 ¦ 198 ¦ 175 ¦ 209 ¦ 164 ¦ 183 ¦ ¦ 70 ¦ 200 ¦ 183 ¦ 253 ¦ 221 ¦ 269 ¦ 203 ¦ 225 ¦ ¦ 95 ¦ 241 ¦ 220 ¦ 306 ¦ 265 ¦ 328 ¦ 239 ¦ 270 ¦ ¦ 120 ¦ 278 ¦ 253 ¦ 354 ¦ 305 ¦ 382 ¦ 271 ¦ 306 ¦ ¦ 150 ¦ 318 ¦ 290 ¦ 393 ¦ 334 ¦ 441 ¦ 306 ¦ 343 ¦ ¦ 185 ¦ 362 ¦ 329 ¦ 449 ¦ 384 ¦ 506 ¦ 343 ¦ 387 ¦ ¦ 240 ¦ 424 ¦ 386 ¦ 528 ¦ 459 ¦ 599 ¦ 395 ¦ 448 ¦ ¦ 300 ¦ 486 ¦ 442 ¦ 603 ¦ 532 ¦ 693 ¦ 446 ¦ 502 ¦ ¦ 알루미늄 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 2.5 ¦ 20 ¦ 19.5 ¦ 25 ¦ 23 ¦ 26 ¦ 26 ¦ ¦ ¦ 4 ¦ 27 ¦ 26 ¦ 33 ¦ 31 ¦ 35 ¦ 33 ¦ ¦ ¦ 6 ¦ 35 ¦ 33 ¦ 43 ¦ 40 ¦ 45 ¦ 42 ¦ ¦ ¦ 10 ¦ 48 ¦ 45 ¦ 59 ¦ 54 ¦ 62 ¦ 55 ¦ ¦ ¦ 16 ¦ 64 ¦ 60 ¦ 79 ¦ 72 ¦ 84 ¦ 71 ¦ 76 ¦ ¦ 25 ¦ 84 ¦ 78 ¦ 105 ¦ 94 ¦ 101 ¦ 90 ¦ 98 ¦ ¦ 35 ¦ 103 ¦ 96 ¦ 130 ¦ 115 ¦ 126 ¦ 108 ¦ 117 ¦ ¦ 50 ¦ 125 ¦ 115 ¦ 157 ¦ 138 ¦ 154 ¦ 128 ¦ 139 ¦ ¦ 70 ¦ 158 ¦ 145 ¦ 200 ¦ 175 ¦ 198 ¦ 158 ¦ 170 ¦ ¦ 95 ¦ 191 ¦ 175 ¦ 242 ¦ 210 ¦ 241 ¦ 186 ¦ 204 ¦ ¦ 120 ¦ 220 ¦ 201 ¦ 281 ¦ 242 ¦ 280 ¦ 211 ¦ 233 ¦ ¦ 150 ¦ 253 ¦ 230 ¦ 307 ¦ 261 ¦ 324 ¦ 238 ¦ 261 ¦ ¦ 185 ¦ 288 ¦ 262 ¦ 351 ¦ 300 ¦ 371 ¦ 267 ¦ 296 ¦ ¦ 240 ¦ 338 ¦ 307 ¦ 412 ¦ 358 ¦ 439 ¦ 307 ¦ 343 ¦ ¦ 300 비고 세로줄 ¦ 387 3, 5, 6, 7, ¦ 352 8 의 경우, ¦ 471 면적이 16 mm2 ¦ 415 이하인 것은 ¦ 508 원형 도체로 ¦ 346 간주한다. ¦ 386 단면적이 이 ¦ 를 초과 하는 경우에 대한 값은 성형 도체와 관련된 것으로, 이 값은 원형 도체에 대해 안전 하게 적용할 수 있다. 32 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
ed0317a0-22d7-44c2-99c2-16859255cea7 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 B.52.4 표 B.52.1 의 설치방법의 허용전류(A) PVC 절연, 3 개 부하 도체, 구리 또는 알루미늄, 도체 온도: 70 °C, 주위온도: 기중 30 °C, 지중 20 °C ¦ 도체의 공칭 단면적 mm2 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도체의 공칭 단면적 mm2 ¦ A1 ¦ A2 ¦ B1 ¦ B2 ¦ C ¦ D1 ¦ D2 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 1 ¦ 2 ¦ 3 ¦ 4 ¦ 5 ¦ 6 ¦ 7 ¦ 8 ¦ ¦ 구리 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 1.5 ¦ 13.5 ¦ 13 ¦ 15.5 ¦ 15 ¦ 17.5 ¦ 18 ¦ 19 ¦ ¦ 2.5 ¦ 18 ¦ 17.5 ¦ 21 ¦ 20 ¦ 24 ¦ 24 ¦ 24 ¦ ¦ 4 ¦ 24 ¦ 23 ¦ 28 ¦ 27 ¦ 32 ¦ 30 ¦ 33 ¦ ¦ 6 ¦ 31 ¦ 29 ¦ 36 ¦ 34 ¦ 41 ¦ 38 ¦ 41 ¦ ¦ 10 ¦ 42 ¦ 39 ¦ 50 ¦ 46 ¦ 57 ¦ 50 ¦ 54 ¦ ¦ 16 ¦ 56 ¦ 52 ¦ 68 ¦ 62 ¦ 76 ¦ 64 ¦ 70 ¦ ¦ 25 ¦ 73 ¦ 68 ¦ 89 ¦ 80 ¦ 96 ¦ 82 ¦ 92 ¦ ¦ 35 ¦ 89 ¦ 83 ¦ 110 ¦ 99 ¦ 119 ¦ 98 ¦ 110 ¦ ¦ 50 ¦ 108 ¦ 99 ¦ 134 ¦ 118 ¦ 144 ¦ 116 ¦ 130 ¦ ¦ 70 ¦ 136 ¦ 125 ¦ 171 ¦ 149 ¦ 184 ¦ 143 ¦ 162 ¦ ¦ 95 ¦ 164 ¦ 150 ¦ 207 ¦ 179 ¦ 223 ¦ 169 ¦ 193 ¦ ¦ 120 ¦ 188 ¦ 172 ¦ 239 ¦ 206 ¦ 259 ¦ 192 ¦ 220 ¦ ¦ 150 ¦ 216 ¦ 196 ¦ 262 ¦ 225 ¦ 299 ¦ 217 ¦ 246 ¦ ¦ 185 ¦ 245 ¦ 223 ¦ 296 ¦ 255 ¦ 341 ¦ 243 ¦ 278 ¦ ¦ 240 ¦ 286 ¦ 261 ¦ 346 ¦ 297 ¦ 403 ¦ 280 ¦ 320 ¦ ¦ 300 ¦ 328 ¦ 298 ¦ 394 ¦ 339 ¦ 464 ¦ 316 ¦ 359 ¦ ¦ 알루미늄 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 2.5 ¦ 14 ¦ 13.5 ¦ 16.5 ¦ 15.5 ¦ 18.5 ¦ 18.5 ¦ ¦ ¦ 4 ¦ 18.5 ¦ 17.5 ¦ 22 ¦ 21 ¦ 25 ¦ 24 ¦ ¦ ¦ 6 ¦ 24 ¦ 23 ¦ 28 ¦ 27 ¦ 32 ¦ 30 ¦ ¦ ¦ 10 ¦ 32 ¦ 31 ¦ 39 ¦ 36 ¦ 44 ¦ 39 ¦ ¦ ¦ 16 ¦ 43 ¦ 41 ¦ 53 ¦ 48 ¦ 59 ¦ 50 ¦ 53 ¦ ¦ 25 ¦ 57 ¦ 53 ¦ 70 ¦ 62 ¦ 73 ¦ 64 ¦ 69 ¦ ¦ 35 ¦ 70 ¦ 65 ¦ 86 ¦ 77 ¦ 90 ¦ 77 ¦ 83 ¦ ¦ 50 ¦ 84 ¦ 78 ¦ 104 ¦ 92 ¦ 110 ¦ 91 ¦ 99 ¦ ¦ 70 ¦ 107 ¦ 98 ¦ 133 ¦ 116 ¦ 140 ¦ 112 ¦ 122 ¦ ¦ 95 ¦ 129 ¦ 118 ¦ 161 ¦ 139 ¦ 170 ¦ 132 ¦ 148 ¦ ¦ 120 ¦ 149 ¦ 135 ¦ 186 ¦ 160 ¦ 197 ¦ 150 ¦ 169 ¦ ¦ 150 ¦ 170 ¦ 155 ¦ 204 ¦ 176 ¦ 227 ¦ 169 ¦ 189 ¦ ¦ 185 ¦ 194 ¦ 176 ¦ 230 ¦ 199 ¦ 259 ¦ 190 ¦ 214 ¦ ¦ 240 ¦ 227 ¦ 207 ¦ 269 ¦ 232 ¦ 305 ¦ 218 ¦ 250 ¦ ¦ 300 ¦ 261 ¦ 237 ¦ 306 ¦ 265 ¦ 351 ¦ 247 ¦ 282 ¦ 비고 세로줄 3, 5, 6, 7, 8 의 경우, 면적이 16 mm2 이하인 것은 원형 도체로 간주한다. 단면적이 이 를 초과 하는 경우에 대한 값은 성형 도체와 관련된 것으로, 이 값은 원형 도체에 대해 안전 하게 적용할 수 있다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 33 | {}
98dd699c-efc7-498c-aee4-1e9d367aa34e | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 B.52.5 - 표 B.52.1 의 설치방법의 허용전류(A) - XLPE 또는 EPR 절연, 3 개 부하 도체, 구리 또는 알루미늄, 도체 온도: 90 °C, 주위온도: 기중 30 °C, 지중 20 °C ¦ 도체의 공칭 단면적 mm2 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도체의 공칭 단면적 mm2 ¦ A1 ¦ A2 ¦ B1 ¦ B2 ¦ C ¦ D1 ¦ D2 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 1 ¦ 2 ¦ 3 ¦ 4 ¦ 5 ¦ 6 ¦ 7 ¦ 8 ¦ ¦ 구리 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 1.5 ¦ 17 ¦ 16.5 ¦ 20 ¦ 19.5 ¦ 22 ¦ 21 ¦ 23 ¦ ¦ 2.5 ¦ 23 ¦ 22 ¦ 28 ¦ 26 ¦ 30 ¦ 28 ¦ 30 ¦ ¦ 4 ¦ 31 ¦ 30 ¦ 37 ¦ 35 ¦ 40 ¦ 36 ¦ 39 ¦ ¦ 6 ¦ 40 ¦ 38 ¦ 48 ¦ 44 ¦ 52 ¦ 44 ¦ 49 ¦ ¦ 10 ¦ 54 ¦ 51 ¦ 66 ¦ 60 ¦ 71 ¦ 58 ¦ 65 ¦ ¦ 16 ¦ 73 ¦ 68 ¦ 88 ¦ 80 ¦ 96 ¦ 75 ¦ 84 ¦ ¦ 25 ¦ 95 ¦ 89 ¦ 117 ¦ 105 ¦ 119 ¦ 96 ¦ 107 ¦ ¦ 35 ¦ 117 ¦ 109 ¦ 144 ¦ 128 ¦ 147 ¦ 115 ¦ 129 ¦ ¦ 50 ¦ 141 ¦ 130 ¦ 175 ¦ 154 ¦ 179 ¦ 135 ¦ 153 ¦ ¦ 70 ¦ 179 ¦ 164 ¦ 222 ¦ 194 ¦ 229 ¦ 167 ¦ 188 ¦ ¦ 95 ¦ 216 ¦ 197 ¦ 269 ¦ 233 ¦ 278 ¦ 197 ¦ 226 ¦ ¦ 120 ¦ 249 ¦ 227 ¦ 312 ¦ 268 ¦ 322 ¦ 223 ¦ 257 ¦ ¦ 150 ¦ 285 ¦ 259 ¦ 342 ¦ 300 ¦ 371 ¦ 251 ¦ 287 ¦ ¦ 185 ¦ 324 ¦ 295 ¦ 384 ¦ 340 ¦ 424 ¦ 281 ¦ 324 ¦ ¦ 240 ¦ 380 ¦ 346 ¦ 450 ¦ 398 ¦ 500 ¦ 324 ¦ 375 ¦ ¦ 300 ¦ 435 ¦ 396 ¦ 514 ¦ 455 ¦ 576 ¦ 365 ¦ 419 ¦ ¦ 알루미늄 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 2.5 ¦ 19 ¦ 18 ¦ 22 ¦ 21 ¦ 24 ¦ 22 ¦ ¦ ¦ 4 ¦ 25 ¦ 24 ¦ 29 ¦ 28 ¦ 32 ¦ 28 ¦ ¦ ¦ 6 ¦ 32 ¦ 31 ¦ 38 ¦ 35 ¦ 41 ¦ 35 ¦ ¦ ¦ 10 ¦ 44 ¦ 41 ¦ 52 ¦ 48 ¦ 57 ¦ 46 ¦ ¦ ¦ 16 ¦ 58 ¦ 55 ¦ 71 ¦ 64 ¦ 76 ¦ 59 ¦ 64 ¦ ¦ 25 ¦ 76 ¦ 71 ¦ 93 ¦ 84 ¦ 90 ¦ 75 ¦ 82 ¦ ¦ 35 ¦ 94 ¦ 87 ¦ 116 ¦ 103 ¦ 112 ¦ 90 ¦ 98 ¦ ¦ 50 ¦ 113 ¦ 104 ¦ 140 ¦ 124 ¦ 136 ¦ 106 ¦ 117 ¦ ¦ 70 ¦ 142 ¦ 131 ¦ 179 ¦ 156 ¦ 174 ¦ 130 ¦ 144 ¦ ¦ 95 ¦ 171 ¦ 157 ¦ 217 ¦ 188 ¦ 211 ¦ 154 ¦ 172 ¦ ¦ 120 ¦ 197 ¦ 180 ¦ 251 ¦ 216 ¦ 245 ¦ 174 ¦ 197 ¦ ¦ 150 ¦ 226 ¦ 206 ¦ 267 ¦ 240 ¦ 283 ¦ 197 ¦ 220 ¦ ¦ 185 ¦ 256 ¦ 233 ¦ 300 ¦ 272 ¦ 323 ¦ 220 ¦ 250 ¦ ¦ 240 ¦ 300 ¦ 273 ¦ 351 ¦ 318 ¦ 382 ¦ 253 ¦ 290 ¦ ¦ 300 ¦ 344 ¦ 313 ¦ 402 ¦ 364 ¦ 440 ¦ 286 ¦ 326 ¦ 비고 세로줄 3, 5, 6, 7, 8 의 경우, 면적이 16 mm2 이하인 것은 원형 도체로 간주한다. 단면적이 이 를 초과 하는 경우에 대한 값은 성형 도체와 관련된 것으로, 이 값은 원형 도체에 대해 안전 하게 적용할 수 있다. 34 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
0cccc061-122b-4936-9725-7647a78b90d0 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 B.52.6 표 B.52.1 의 설치방법의 허용전류(A) - 무기질절연, 구리 도체, PVC 외피 또는 노출로 접촉 우려 있음(비고 2 참조) - 금속 시스 온도: 70 °C, 기준 주위온도: 30 °C ¦ 도체의 공칭 단면적 mm2 ¦ 표 B.52.1 설치방법 C 에 대한 도체 수와 배치 ¦ 표 B.52.1 설치방법 C 에 대한 도체 수와 배치 ¦ 표 B.52.1 설치방법 C 에 대한 도체 수와 배치 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 2 심 또는 단심의 2 개 부하 도체 ¦ 3 개 부하 도체 ¦ 3 개 부하 도체 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 2 심 또는 단심의 2 개 부하 도체 ¦ 삼각배치 단심 또는 다 심 ¦ 수평 단심 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ ¦ ¦ ¦ ¦ 1 ¦ 2 ¦ 3 ¦ 4 ¦ ¦ 500 V ¦ ¦ ¦ ¦ ¦ 1.5 ¦ 23 ¦ 19 ¦ 21 ¦ ¦ 2.5 ¦ 31 ¦ 26 ¦ 29 ¦ ¦ 4 ¦ 40 ¦ 35 ¦ 38 ¦ ¦ 750 V ¦ ¦ ¦ ¦ ¦ 1.5 ¦ 25 ¦ 21 ¦ 23 ¦ ¦ 2.5 ¦ 34 ¦ 28 ¦ 31 ¦ ¦ 4 ¦ 45 ¦ 37 ¦ 41 ¦ ¦ 6 ¦ 57 ¦ 48 ¦ 52 ¦ ¦ 10 ¦ 77 ¦ 65 ¦ 70 ¦ ¦ 16 ¦ 102 ¦ 86 ¦ 92 ¦ ¦ 25 ¦ 133 ¦ 112 ¦ 120 ¦ ¦ 35 ¦ 163 ¦ 137 ¦ 147 ¦ ¦ 50 ¦ 202 ¦ 169 ¦ 181 ¦ ¦ 70 ¦ 247 ¦ 207 ¦ 221 ¦ ¦ 95 ¦ 296 ¦ 249 ¦ 264 ¦ ¦ 120 ¦ 340 ¦ 286 ¦ 303 ¦ ¦ 150 ¦ 388 ¦ 327 ¦ 346 ¦ ¦ 185 ¦ 440 ¦ 371 ¦ 392 ¦ ¦ 240 ¦ 514 ¦ 434 ¦ 457 ¦ 비고 1 단심케이블인 경우, 회로를 구성하는 케이블의 금속 시스의 그 양단을 접지 한다. 비고 2 노출로 사람이 접촉할 우려가 있는 케이블은 0.9 를 곱한 값으로 한다. 비고 3 500 V 와 750 V 는 케이블의 정격 전압이다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 35 | {}
89e0b8c8-7191-4726-85e9-5b2075822f2e | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 B.52.7 표 B.52.1 의 설치방법 C 의 허용전류(A) - 무기질 절연물, 구리 도체와 구리 시스, 노출로 사람이 접촉할 우려가 없고 가연성 물질과 접촉할 우려가 없는 케이블, 금속온도: 105 °C, 기준 주위온도: 30 °C ¦ 도체의 공칭 단면적 mm2 ¦ 표 B.52.1 설치방법 C 에 대한 도체 수와 배치 ¦ 표 B.52.1 설치방법 C 에 대한 도체 수와 배치 ¦ 표 B.52.1 설치방법 C 에 대한 도체 수와 배치 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 2 심 또는 단심의 2 개 부하 도체 ¦ 3 개 부하 도체 ¦ 3 개 부하 도체 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 2 심 또는 단심의 2 개 부하 도체 ¦ 삼각배치 단심 또는 다 심 ¦ 수평 단심 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ ¦ ¦ · ¦ ¦ 1 ¦ 2 ¦ 3 ¦ 4 ¦ ¦ 500 V ¦ ¦ ¦ ¦ ¦ 1.5 ¦ 28 ¦ 24 ¦ 27 ¦ ¦ 2.5 ¦ 38 ¦ 33 ¦ 36 ¦ ¦ 4 ¦ 51 ¦ 44 ¦ 47 ¦ ¦ 750 V ¦ ¦ ¦ ¦ ¦ 1.5 ¦ 31 ¦ 26 ¦ 30 ¦ ¦ 2.5 ¦ 42 ¦ 35 ¦ 41 ¦ ¦ 4 ¦ 55 ¦ 47 ¦ 53 ¦ ¦ 6 ¦ 70 ¦ 59 ¦ 67 ¦ ¦ 10 ¦ 96 ¦ 81 ¦ 91 ¦ ¦ 16 ¦ 127 ¦ 107 ¦ 119 ¦ ¦ 25 ¦ 166 ¦ 140 ¦ 154 ¦ ¦ 35 ¦ 203 ¦ 171 ¦ 187 ¦ ¦ 50 ¦ 251 ¦ 212 ¦ 230 ¦ ¦ 70 ¦ 307 ¦ 260 ¦ 280 ¦ ¦ 95 ¦ 369 ¦ 312 ¦ 334 ¦ ¦ 120 ¦ 424 ¦ 359 ¦ 383 ¦ ¦ 150 ¦ 485 ¦ 410 ¦ 435 ¦ ¦ 185 240 ¦ 550 643 ¦ 465 544 ¦ 492 572 ¦ 비고 1 단심케이블인 경우, 회로를 구성하는 케이블의 금속 시스의 그 양단을 접지 한다. 비고 2 집합에 대한 보정계수는 적용할 필요 없다. 비고 3 이 표에서 참조 방법 C 는 외장의 높은 온도 때문에 목재 벽을 허용할 수 없어 석조 벽을 언급하였다. 비고 4 500 V 와 750 V 는 케이블의 정격 전압이다. 36 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
61a6467a-e0e8-4c64-a041-772d4d251d3e | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 B.52.8 표 B.52.1 의 설치방법 E, F, G 의 허용전류(A) - 무기질 절연물, 구리 도체와 구리 시스, PVC 피복 또는 노출로 사람이 접촉할 우려가 있는 케이블(비고 2 참조) 금속온도: 70 °C, 기준 주위온도: 30 °C ¦ 도체의 공칭 단면적 mm2 ¦ 표 B.52.1 의 방법 E, F, G 에서 케이블 수와 배치 ¦ 표 B.52.1 의 방법 E, F, G 에서 케이블 수와 배치 ¦ 표 B.52.1 의 방법 E, F, G 에서 케이블 수와 배치 ¦ 표 B.52.1 의 방법 E, F, G 에서 케이블 수와 배치 ¦ 표 B.52.1 의 방법 E, F, G 에서 케이블 수와 배치 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 2 심 또는 단심의 2 개 부하 도체 방법 E 또는 F ¦ 3 개 부하 도체 ¦ 3 개 부하 도체 ¦ 3 개 부하 도체 ¦ 3 개 부하 도체 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 2 심 또는 단심의 2 개 부하 도체 방법 E 또는 F ¦ 삼각배치 단심 또는 다심 방법 E 또는 F ¦ 단심 접촉 방법 F ¦ 수직 이격한 단심 방법 G ¦ 수평 이격한 단심 방법 G ¦ ¦ 도체의 공칭 단면적 mm2 ¦ or ¦ or ¦ ⊙⊙㉧ or ¦ ¦ De ¦ ¦ 1 ¦ 2 ¦ 3 ¦ 4 ¦ 5 ¦ 6 ¦ ¦ 500 V ¦ ¦ ¦ ¦ ¦ ¦ ¦ 1.5 ¦ 25 ¦ 21 ¦ 23 ¦ 26 ¦ 29 ¦ ¦ 2.5 ¦ 33 ¦ 28 ¦ 31 ¦ 34 ¦ 39 ¦ ¦ 4 ¦ 44 ¦ 37 ¦ 41 ¦ 45 ¦ 51 ¦ ¦ 750 V ¦ ¦ ¦ ¦ ¦ ¦ ¦ 1.5 ¦ 26 ¦ 22 ¦ 26 ¦ 28 ¦ 32 ¦ ¦ 2.5 ¦ 36 ¦ 30 ¦ 34 ¦ 37 ¦ 43 ¦ ¦ 4 ¦ 47 ¦ 40 ¦ 45 ¦ 49 ¦ 56 ¦ ¦ 6 ¦ 60 ¦ 51 ¦ 57 ¦ 62 ¦ 71 ¦ ¦ 10 ¦ 82 ¦ 69 ¦ 77 ¦ 84 ¦ 95 ¦ ¦ 16 ¦ 109 ¦ 92 ¦ 102 ¦ 110 ¦ 125 ¦ ¦ 25 ¦ 142 ¦ 120 ¦ 132 ¦ 142 ¦ 162 ¦ ¦ 35 ¦ 174 ¦ 147 ¦ 161 ¦ 173 ¦ 197 ¦ ¦ 50 ¦ 215 ¦ 182 ¦ 198 ¦ 213 ¦ 242 ¦ ¦ 70 ¦ 264 ¦ 223 ¦ 241 ¦ 259 ¦ 294 ¦ ¦ 95 ¦ 317 ¦ 267 ¦ 289 ¦ 309 ¦ 351 ¦ ¦ 120 ¦ 364 ¦ 308 ¦ 331 ¦ 353 ¦ 402 ¦ ¦ 150 ¦ 416 ¦ 352 ¦ 377 ¦ 400 ¦ 454 ¦ ¦ 185 ¦ 472 ¦ 399 ¦ 426 ¦ 446 ¦ 507 ¦ ¦ 240 ¦ 552 ¦ 466 ¦ 496 ¦ 497 ¦ 565 ¦ 비고 1 단심케이블인 경우, 회로를 구성하는 케이블의 금속 시스의 그 양단을 접지한다. 비고 2 노출로 사람이 접촉할 우려가 있는 케이블은 0.9 를 곱한 값으로 한다. 비고 3 De 는 케이블의 바깥지름이다. 비고 4 500 V 와 750 V 는 케이블의 정격 전압이다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 37 | {}
e5e111b3-aa43-431b-8caa-d5667a2b07c6 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 B.52.9 - 표 B.52.1 의 설치방법 E, F, G 의 허용전류(A) - 무기질 절연물, 구리 도체와 구리 시스, 노출로 사람이 접촉할 우려가 없는 케이블(비고 2 참조) 금속온도: 105 °C, 기준 주위온도: 30 °C ¦ 도체의 공칭 단면적 mm2 ¦ 표 B.52.1 의 방법 E, F, G 에서 케이블 수와 배치 ¦ 표 B.52.1 의 방법 E, F, G 에서 케이블 수와 배치 ¦ 표 B.52.1 의 방법 E, F, G 에서 케이블 수와 배치 ¦ 표 B.52.1 의 방법 E, F, G 에서 케이블 수와 배치 ¦ 표 B.52.1 의 방법 E, F, G 에서 케이블 수와 배치 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 2 심 또는 단심의 2 개 부하 도체 방법 E 또는 F ¦ 3 개 부하 도체 ¦ 3 개 부하 도체 ¦ 3 개 부하 도체 ¦ 3 개 부하 도체 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 2 심 또는 단심의 2 개 부하 도체 방법 E 또는 F ¦ 삼각배치 단심 또는 다심 방법 E 또는 F ¦ 단심 접촉 방법 F ¦ 수직 이격한 단심 방법 G ¦ 수평 이격한 단심 방법 G ¦ ¦ 도체의 공칭 단면적 mm2 ¦ or ¦ or ¦ ⊙⊙㉧ or ¦ ¦ De ¦ ¦ 1 ¦ 2 ¦ 3 ¦ 4 ¦ 5 ¦ 6 ¦ ¦ 500 V ¦ ¦ ¦ ¦ ¦ ¦ ¦ 1.5 ¦ 31 ¦ 26 ¦ 29 ¦ 33 ¦ 37 ¦ ¦ 2.5 ¦ 41 ¦ 35 ¦ 39 ¦ 43 ¦ 49 ¦ ¦ 4 ¦ 54 ¦ 46 ¦ 51 ¦ 56 ¦ 64 ¦ ¦ 750 V ¦ ¦ ¦ ¦ ¦ ¦ ¦ 1.5 ¦ 33 ¦ 28 ¦ 32 ¦ 35 ¦ 40 ¦ ¦ 2.5 ¦ 45 ¦ 38 ¦ 43 ¦ 47 ¦ 54 ¦ ¦ 4 ¦ 60 ¦ 50 ¦ 56 ¦ 61 ¦ 70 ¦ ¦ 6 ¦ 76 ¦ 64 ¦ 71 ¦ 78 ¦ 89 ¦ ¦ 10 ¦ 104 ¦ 87 ¦ 96 ¦ 105 ¦ 120 ¦ ¦ 16 ¦ 137 ¦ 115 ¦ 127 ¦ 137 ¦ 157 ¦ ¦ 25 ¦ 179 ¦ 150 ¦ 164 ¦ 178 ¦ 204 ¦ ¦ 35 ¦ 220 ¦ 184 ¦ 200 ¦ 216 ¦ 248 ¦ ¦ 50 ¦ 272 ¦ 228 ¦ 247 ¦ 266 ¦ 304 ¦ ¦ 70 ¦ 333 ¦ 279 ¦ 300 ¦ 323 ¦ 370 ¦ ¦ 95 ¦ 400 ¦ 335 ¦ 359 ¦ 385 ¦ 441 ¦ ¦ 120 ¦ 460 ¦ 385 ¦ 411 ¦ 441 ¦ 505 ¦ ¦ 150 ¦ 526 ¦ 441 ¦ 469 ¦ 498 ¦ 565 ¦ ¦ 185 ¦ 596 ¦ 500 ¦ 530 ¦ 557 ¦ 629 ¦ ¦ 240 ¦ 697 ¦ 584 ¦ 617 ¦ 624 ¦ 704 ¦ 비고 1 단심케이블인 경우, 회로를 구성하는 케이블의 시스를 그 양단에 상호 접속한다. 비고 2 집합에 대한 보정계수는 적용할 필요 없다. 비고 3 De 는 케이블의 바깥지름이다. 비고 4 500 V 와 750 V 는 케이블의 정격 전압이다. 38 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
14acb138-e5a3-4a20-944b-9ce560ee7a07 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 B.52.10 표 B.52.1 의 설치방법 E, F, G 의 허용전류(A) PVC 절연, 구리 도체, 도체 온도: 70 °C, 기준 주위온도: 30 °C ¦ 도체의 공칭 단면적 mm2 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 다심케이블 ¦ 다심케이블 ¦ 단심케이블 ¦ 단심케이블 ¦ 단심케이블 ¦ 단심케이블 ¦ 단심케이블 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 2 개 부하 도체 ¦ 3 개 부하 도체 ¦ 2 개 부하 도체 접촉 ¦ 3 개 부하 도체 삼각배치 ¦ 수평 3 개 부하 도체 ¦ 수평 3 개 부하 도체 ¦ 수평 3 개 부하 도체 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 2 개 부하 도체 ¦ 3 개 부하 도체 ¦ 2 개 부하 도체 접촉 ¦ 3 개 부하 도체 삼각배치 ¦ 밀착 ¦ 이격 방법 ¦ 이격 방법 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 2 개 부하 도체 ¦ 3 개 부하 도체 ¦ 2 개 부하 도체 접촉 ¦ 3 개 부하 도체 삼각배치 ¦ 밀착 ¦ 수평 ¦ 수직 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ ¦ ¦ 。 or ¦ ¦ ○○○ or ¦ ¦ EDe ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 방법 E ¦ 방법 E ¦ 방법 F ¦ 방법 F ¦ 방법 F ¦ 방법 G ¦ 방법 G ¦ ¦ 1 ¦ 2 ¦ 3 ¦ 4 ¦ 5 ¦ 6 ¦ 7 ¦ 8 ¦ ¦ 1.5 ¦ 22 ¦ 18.5 ¦ ¦ ¦ ¦ ¦ ¦ ¦ 2.5 ¦ 30 ¦ 25 ¦ - ¦ - ¦ - ¦ - ¦ - ¦ ¦ 4 ¦ 40 ¦ 34 ¦ - ¦ - ¦ - ¦ - ¦ - ¦ ¦ 6 ¦ 51 ¦ 43 ¦ - ¦ - ¦ - ¦ - ¦ - ¦ ¦ 10 ¦ 70 ¦ 60 ¦ - ¦ - ¦ - ¦ - ¦ - ¦ ¦ 16 ¦ 94 ¦ 80 ¦ - ¦ ¦ - ¦ ¦ ¦ ¦ 25 ¦ 119 ¦ 101 ¦ 131 ¦ 110 ¦ 114 ¦ 146 ¦ 130 ¦ ¦ 35 ¦ 148 ¦ 126 ¦ 162 ¦ 137 ¦ 143 ¦ 181 ¦ 162 ¦ ¦ 50 ¦ 180 ¦ 153 ¦ 196 ¦ 167 ¦ 174 ¦ 219 ¦ 197 ¦ ¦ 70 ¦ 232 ¦ 196 ¦ 251 ¦ 216 ¦ 225 ¦ 281 ¦ 254 ¦ ¦ 95 ¦ 282 ¦ 238 ¦ 304 ¦ 264 ¦ 275 ¦ 341 ¦ 311 ¦ ¦ 120 150 ¦ 328 ¦ 276 ¦ 352 ¦ 308 ¦ 321 372 ¦ 396 456 ¦ 362 419 ¦ ¦ 185 ¦ 379 434 ¦ 319 364 ¦ 406 463 ¦ 356 409 ¦ 427 ¦ 521 ¦ 480 ¦ ¦ 240 ¦ 514 ¦ 430 ¦ 546 ¦ 485 ¦ 507 ¦ 615 ¦ 569 ¦ ¦ 300 ¦ 593 ¦ 497 ¦ 629 ¦ 561 ¦ 587 ¦ 709 ¦ 659 ¦ ¦ ¦ ¦ ¦ 754 ¦ 656 ¦ 689 ¦ 852 ¦ 795 ¦ ¦ 400 ¦ ¦ - ¦ 868 ¦ 749 ¦ 789 ¦ 982 ¦ 920 ¦ ¦ 500 630 ¦ - ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 1 005 ¦ 855 ¦ 905 ¦ 1 138 ¦ 1 070 ¦ ¦ 비고 1 단면적이 16 mm2 이하인 것은 원형 도체로 간주한다. 단면적이 이를 초과 하는 경우에 대 ¦ 비고 1 단면적이 16 mm2 이하인 것은 원형 도체로 간주한다. 단면적이 이를 초과 하는 경우에 대 ¦ 비고 1 단면적이 16 mm2 이하인 것은 원형 도체로 간주한다. 단면적이 이를 초과 하는 경우에 대 ¦ 비고 1 단면적이 16 mm2 이하인 것은 원형 도체로 간주한다. 단면적이 이를 초과 하는 경우에 대 ¦ 비고 1 단면적이 16 mm2 이하인 것은 원형 도체로 간주한다. 단면적이 이를 초과 하는 경우에 대 ¦ 비고 1 단면적이 16 mm2 이하인 것은 원형 도체로 간주한다. 단면적이 이를 초과 하는 경우에 대 ¦ 비고 1 단면적이 16 mm2 이하인 것은 원형 도체로 간주한다. 단면적이 이를 초과 하는 경우에 대 ¦ 비고 1 단면적이 16 mm2 이하인 것은 원형 도체로 간주한다. 단면적이 이를 초과 하는 경우에 대 ¦ 한 값은 성형 도체와 관련된 것으로, 이 값은 원형 도체에 대해 안전하게 적용할 수 있다. 비고 2 De 는 케이블의 바깥지름이다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 39 | {}
ad11b5ba-aa9b-4aa5-a396-e5b65764b50e | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 B.52.11 - 표 B.52.1 의 설치방법 E, F, G 의 허용전류(A) PVC 절연, 알루미늄 도체, 도체 온도: 70 °C, 기준 주위온도: 30 °C ¦ 도체의 공칭 단면적 mm2 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 다심케이블 ¦ 다심케이블 ¦ 단심케이블 ¦ 단심케이블 ¦ 단심케이블 ¦ 단심케이블 ¦ 단심케이블 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 2 개 부하 도체 ¦ 3 개 부하 도체 ¦ 2 개 부하 도체 접촉 ¦ 3 개 부하 도체 삼각배치 ¦ 수평 3 개 부하 도체 ¦ 수평 3 개 부하 도체 ¦ 수평 3 개 부하 도체 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 2 개 부하 도체 ¦ 3 개 부하 도체 ¦ 2 개 부하 도체 접촉 ¦ 3 개 부하 도체 삼각배치 ¦ 밀착 ¦ 이격 방법 ¦ 이격 방법 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 2 개 부하 도체 ¦ 3 개 부하 도체 ¦ 2 개 부하 도체 접촉 ¦ 3 개 부하 도체 삼각배치 ¦ 밀착 ¦ 수평 ¦ 수직 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ ¦ ¦ 。 or ¦ ¦ ooo or xxxxx ¦ ¦ De ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 방법 E ¦ 방법 E ¦ 방법 F ¦ 방법 F ¦ 방법 F ¦ 방법 G ¦ 방법 G ¦ ¦ 1 ¦ 2 ¦ 3 ¦ 4 ¦ 5 ¦ 6 ¦ 7 ¦ 8 ¦ ¦ 2.5 ¦ 23 ¦ 19.5 ¦ - ¦ ¦ ¦ ¦ ¦ ¦ 4 ¦ 31 ¦ 26 ¦ - ¦ - ¦ - ¦ - ¦ - ¦ ¦ 6 ¦ 39 ¦ 33 ¦ - ¦ - ¦ - ¦ - ¦ - ¦ ¦ 10 ¦ 54 ¦ 46 ¦ - ¦ - ¦ - ¦ - ¦ ¦ ¦ 16 ¦ 73 ¦ 61 ¦ ¦ ¦ ¦ ¦ ¦ ¦ 25 ¦ 89 ¦ 78 ¦ 98 ¦ 84 ¦ 87 ¦ 112 ¦ 99 ¦ ¦ 35 ¦ 111 ¦ 96 ¦ 122 ¦ 105 ¦ 109 ¦ 139 ¦ 124 ¦ ¦ 50 ¦ 135 ¦ 117 ¦ 149 ¦ 128 ¦ 133 ¦ 169 ¦ 152 ¦ ¦ 70 ¦ 173 ¦ 150 ¦ 192 ¦ 166 ¦ 173 ¦ 217 ¦ 196 ¦ ¦ 95 ¦ 210 ¦ 183 ¦ 235 ¦ 203 ¦ 212 ¦ 265 ¦ 241 ¦ ¦ 120 ¦ 244 ¦ 212 ¦ 273 ¦ 237 ¦ 247 ¦ 308 ¦ 282 ¦ ¦ 150 ¦ 282 ¦ 245 ¦ 316 ¦ 274 ¦ 287 ¦ 356 ¦ 327 376 ¦ ¦ 185 240 ¦ 322 ¦ 280 ¦ 363 ¦ 315 375 ¦ 330 392 ¦ 407 482 ¦ 447 ¦ ¦ ¦ 380 ¦ 330 ¦ 430 497 ¦ 434 ¦ 455 ¦ 557 ¦ 519 ¦ ¦ 300 ¦ 439 ¦ 381 ¦ ¦ ¦ ¦ ¦ ¦ ¦ 400 ¦ ¦ ¦ 600 ¦ 526 ¦ 552 ¦ 671 ¦ 629 ¦ ¦ 500 ¦ - ¦ - ¦ 694 ¦ 610 ¦ 640 ¦ 775 ¦ 730 ¦ ¦ 630 ¦ ¦ ¦ 808 ¦ 711 ¦ 746 ¦ 900 ¦ 852 ¦ ¦ 비고 1 단면적이 16 mm2 이하인 것은 원형 도체로 간주한다. 단면적이 이를 초과 하는 경우에 대 한 값은 성형 도체와 관련된 것으로, 이 값은 원형 도체에 대해 안전하게 적용할 수 있다. ¦ 비고 1 단면적이 16 mm2 이하인 것은 원형 도체로 간주한다. 단면적이 이를 초과 하는 경우에 대 한 값은 성형 도체와 관련된 것으로, 이 값은 원형 도체에 대해 안전하게 적용할 수 있다. ¦ 비고 1 단면적이 16 mm2 이하인 것은 원형 도체로 간주한다. 단면적이 이를 초과 하는 경우에 대 한 값은 성형 도체와 관련된 것으로, 이 값은 원형 도체에 대해 안전하게 적용할 수 있다. ¦ 비고 1 단면적이 16 mm2 이하인 것은 원형 도체로 간주한다. 단면적이 이를 초과 하는 경우에 대 한 값은 성형 도체와 관련된 것으로, 이 값은 원형 도체에 대해 안전하게 적용할 수 있다. ¦ 비고 1 단면적이 16 mm2 이하인 것은 원형 도체로 간주한다. 단면적이 이를 초과 하는 경우에 대 한 값은 성형 도체와 관련된 것으로, 이 값은 원형 도체에 대해 안전하게 적용할 수 있다. ¦ 비고 1 단면적이 16 mm2 이하인 것은 원형 도체로 간주한다. 단면적이 이를 초과 하는 경우에 대 한 값은 성형 도체와 관련된 것으로, 이 값은 원형 도체에 대해 안전하게 적용할 수 있다. ¦ 비고 1 단면적이 16 mm2 이하인 것은 원형 도체로 간주한다. 단면적이 이를 초과 하는 경우에 대 한 값은 성형 도체와 관련된 것으로, 이 값은 원형 도체에 대해 안전하게 적용할 수 있다. ¦ 비고 1 단면적이 16 mm2 이하인 것은 원형 도체로 간주한다. 단면적이 이를 초과 하는 경우에 대 한 값은 성형 도체와 관련된 것으로, 이 값은 원형 도체에 대해 안전하게 적용할 수 있다. ¦ 비고 2 De 는 케이블의 바깥지름이다. 40 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
69164f63-f1bd-47db-9c6c-eef8ce279364 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 B.52.12 표 B.52.1 의 설치방법 E, F, G 의 허용전류(A) XLPE 또는 EPR 절연, 구리 도체, 도체 온도: 90 °C, 기준 주위온도: 30 °C ¦ 도체의 공칭 단면적 mm2 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 다심케이블 ¦ 다심케이블 ¦ 단심케이블 ¦ 단심케이블 ¦ 단심케이블 ¦ 단심케이블 ¦ 단심케이블 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 2 개 부하 도체 ¦ 3 개 부하 도체 ¦ 2 개 부하 도체 접촉 ¦ 3 개 부하 도체 삼각배치 ¦ 수평 3 개 부하 도체 ¦ 수평 3 개 부하 도체 ¦ 수평 3 개 부하 도체 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 2 개 부하 도체 ¦ 3 개 부하 도체 ¦ 2 개 부하 도체 접촉 ¦ 3 개 부하 도체 삼각배치 ¦ 밀착 ¦ 이격 방법 ¦ 이격 방법 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 2 개 부하 도체 ¦ 3 개 부하 도체 ¦ 2 개 부하 도체 접촉 ¦ 3 개 부하 도체 삼각배치 ¦ 밀착 ¦ 수평 ¦ 수직 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ ¦ ¦ ⊙ or ¦ ¦ ⊙⊙⊙ XXXXXXXX or ¦ ¦ e ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 방법 E ¦ 방법 E ¦ 방법 F ¦ 방법 F ¦ 방법 F ¦ 방법 G ¦ 방법 G ¦ ¦ 1 ¦ 2 ¦ 3 ¦ 4 ¦ 5 ¦ 6 ¦ 7 ¦ 8 ¦ ¦ 1.5 ¦ 26 ¦ 23 ¦ ¦ ¦ ¦ ¦ ¦ ¦ 2.5 ¦ 36 ¦ 32 ¦ - ¦ - ¦ - ¦ - ¦ - ¦ ¦ 4 ¦ 49 ¦ 42 ¦ - ¦ - ¦ - ¦ - ¦ - ¦ ¦ 6 ¦ 63 ¦ 54 ¦ - ¦ - ¦ - ¦ - ¦ - ¦ ¦ 10 ¦ 86 ¦ 75 ¦ - ¦ - ¦ - ¦ - ¦ - ¦ ¦ 16 ¦ 115 ¦ 100 ¦ - ¦ - ¦ ¦ - ¦ ¦ ¦ 25 ¦ 149 ¦ 127 ¦ 161 ¦ 135 ¦ 141 ¦ 182 ¦ 161 ¦ ¦ 35 ¦ 185 ¦ 158 ¦ 200 ¦ 169 ¦ 176 ¦ 226 ¦ 201 ¦ ¦ 50 ¦ 225 ¦ 192 ¦ 242 ¦ 207 ¦ 216 ¦ 275 ¦ 246 ¦ ¦ 70 ¦ 289 ¦ 246 ¦ 310 ¦ 268 328 ¦ 279 342 ¦ 353 430 ¦ 318 389 ¦ ¦ 95 120 ¦ 352 410 ¦ 298 346 ¦ 377 437 ¦ 383 ¦ 400 ¦ 500 ¦ 454 ¦ ¦ 150 ¦ 473 ¦ 399 ¦ 504 ¦ 444 ¦ 464 ¦ 577 ¦ 527 ¦ ¦ 185 ¦ 542 ¦ 456 ¦ 575 ¦ 510 ¦ 533 ¦ 661 ¦ 605 ¦ ¦ 240 ¦ 641 ¦ 538 ¦ 679 ¦ 607 ¦ 634 ¦ 781 ¦ 719 ¦ ¦ 300 ¦ 741 ¦ 621 ¦ 783 ¦ 703 ¦ 736 ¦ 902 ¦ 833 ¦ ¦ 400 ¦ ¦ ¦ 940 ¦ 823 ¦ 868 ¦ 1 085 ¦ 1 008 ¦ ¦ 500 ¦ - ¦ - ¦ 1 083 ¦ 946 ¦ 998 ¦ 1 253 ¦ 1 169 ¦ ¦ 630 1 단면적이 16 단면적이 이를 초과 하는 ¦ mm2 ¦ ¦ 1 254 것은 원형 도체로 ¦ 1 088 ¦ 1 151 ¦ 1 454 ¦ 1 362 경우에 대 ¦ 비고 이하인 간주한다. 한 값은 성형 도체와 관련된 것으로, 이 값은 원형 도체에 대해 안전하게 적용할 수 있다. 비고 2 De 는 케이블의 바깥지름이다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 41 | {}
d5eab53f-b4d5-4193-9dc8-16655ef977b7 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 B.52.13 - 표 B.52.1 의 설치방법 E, F, G 의 허용전류(A) XLPE 또는 EPR 절연, 알루미늄 도체, 도체 온도: 90 °C, 기준 주위온도: 30 °C ¦ 도체의 공칭 단면적 mm2 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ 표 B.52.1 의 설치방법 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 다심케이블 ¦ 다심케이블 ¦ 단심케이블 ¦ 단심케이블 ¦ 단심케이블 ¦ 단심케이블 ¦ 단심케이블 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 2 개 부하 도체 ¦ 3 개 부하 도체 ¦ 2 개 부하 도체 접촉 ¦ 3 개 부하 도체 삼각배치 ¦ 수평 3 개 부하 도체 ¦ 수평 3 개 부하 도체 ¦ 수평 3 개 부하 도체 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 2 개 부하 도체 ¦ 3 개 부하 도체 ¦ 2 개 부하 도체 접촉 ¦ 3 개 부하 도체 삼각배치 ¦ 밀착 ¦ 이격 방법 ¦ 이격 방법 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 2 개 부하 도체 ¦ 3 개 부하 도체 ¦ 2 개 부하 도체 접촉 ¦ 3 개 부하 도체 삼각배치 ¦ 밀착 ¦ 수평 ¦ 수직 ¦ ¦ 도체의 공칭 단면적 mm2 ¦ ¦ ¦ 。 or ¦ ¦ ◎◎◎ or ¦ ¦ ¦ ¦ 도체의 공칭 단면적 mm2 ¦ 방법 E ¦ 방법 E ¦ 방법 F ¦ 방법 F ¦ 방법 F ¦ 방법 G ¦ 방법 G ¦ ¦ 1 ¦ 2 ¦ 3 ¦ 4 ¦ 5 ¦ 6 ¦ 7 ¦ 8 ¦ ¦ 2.5 ¦ 28 ¦ 24 ¦ - ¦ - ¦ - ¦ - ¦ - ¦ ¦ 4 ¦ 38 ¦ 32 ¦ - ¦ - ¦ - ¦ - ¦ - ¦ ¦ 6 ¦ 49 ¦ 42 ¦ - ¦ - ¦ - ¦ - ¦ - ¦ ¦ 10 ¦ 67 ¦ 58 ¦ - ¦ - ¦ - ¦ - ¦ - ¦ ¦ 16 ¦ 91 ¦ 77 ¦ ¦ ¦ ¦ ¦ - ¦ ¦ 25 ¦ 108 ¦ 97 ¦ 121 ¦ 103 ¦ 107 ¦ 138 ¦ 122 ¦ ¦ 35 ¦ 135 ¦ 120 ¦ 150 ¦ 129 ¦ 135 ¦ 172 ¦ 153 ¦ ¦ 50 ¦ 164 ¦ 146 ¦ 184 ¦ 159 ¦ 165 ¦ 210 ¦ 188 ¦ ¦ 70 ¦ 211 ¦ 187 ¦ 237 ¦ 206 ¦ 215 ¦ 271 ¦ 244 ¦ ¦ 95 120 ¦ 257 300 ¦ 227 263 ¦ 289 337 ¦ 253 296 ¦ 264 308 ¦ 332 387 ¦ 300 351 ¦ ¦ 150 ¦ 346 ¦ 304 ¦ 389 ¦ 343 ¦ 358 ¦ 448 ¦ 408 ¦ ¦ 185 ¦ 397 ¦ 347 ¦ 447 ¦ 395 ¦ 413 ¦ 515 ¦ 470 ¦ ¦ 240 ¦ 470 ¦ 409 ¦ 530 ¦ 471 ¦ 492 ¦ 611 ¦ 561 ¦ ¦ 300 ¦ 543 ¦ 471 ¦ 613 ¦ 547 ¦ 571 ¦ 708 ¦ 652 ¦ ¦ 400 ¦ ¦ ¦ 740 ¦ 663 ¦ 694 ¦ 856 ¦ 792 ¦ ¦ 500 ¦ - ¦ - ¦ 856 ¦ 770 ¦ 806 ¦ 991 ¦ 921 ¦ ¦ 630 ¦ ¦ ¦ 996 ¦ 899 ¦ 942 ¦ 1 154 ¦ 1 077 ¦ 비고 1 단면적이 16 mm2 이하인 것은 원형 도체로 간주한다. 단면적이 이를 초과 하는 경우에 대한 값은 성형 도체와 관련된 것으로, 이 값은 원형 도체에 대해 안전하게 적용할 수 있다. 비고 2 De 는 케이블의 바깥지름이다. 42 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
60143a05-839d-4ffb-85da-9068c4c1a69b | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 B.52.14 기중 케이블의 허용전류에 적용되는 기중주위온도가 30 °C 이외인 경우의 보정계수 ¦ 주위온도 a °C ¦ 절연체 ¦ 절연체 ¦ 절연체 ¦ 절연체 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 주위온도 a °C ¦ PVC ¦ XLPE 또는 EPR ¦ 무기 a ¦ 무기 a ¦ ¦ 주위온도 a °C ¦ PVC ¦ XLPE 또는 EPR ¦ PVC 피복 또는 노출로 접촉할 우려가 있는 것 (70 °C) ¦ 노출로 접촉할 우려가 없는 것 (105 °C) ¦ ¦ 10 ¦ 1.22 ¦ 1.15 ¦ 1.26 ¦ 1.14 ¦ ¦ 15 ¦ 1.17 ¦ 1.12 ¦ 1.20 ¦ 1.11 ¦ ¦ 20 ¦ 1.12 ¦ 1.08 ¦ 1.14 ¦ 1.07 ¦ ¦ 25 ¦ 1.06 ¦ 1.04 ¦ 1.07 ¦ 1.04 ¦ ¦ 30 ¦ 1.00 ¦ 1.00 ¦ 1.00 ¦ 1.00 ¦ ¦ 35 ¦ 0.94 ¦ 0.96 ¦ 0.93 ¦ 0.96 ¦ ¦ 40 ¦ 0.87 ¦ 0.91 ¦ 0.85 ¦ 0.92 ¦ ¦ 45 ¦ 0.79 ¦ 0.87 ¦ 0.78 ¦ 0.88 ¦ ¦ 50 ¦ 0.71 ¦ 0.82 ¦ 0.67 ¦ 0.84 ¦ ¦ 55 ¦ 0.61 ¦ 0.76 ¦ 0.57 ¦ 0.80 ¦ ¦ 60 ¦ 0.50 ¦ 0.71 ¦ 0.45 ¦ 0.75 ¦ ¦ 65 ¦ ¦ 0.65 ¦ ¦ 0.70 ¦ ¦ 70 ¦ - ¦ 0.58 ¦ ¦ 0.65 ¦ ¦ 75 ¦ - ¦ 0.50 ¦ - ¦ 0.60 ¦ ¦ 80 ¦ - ¦ 0.41 ¦ - ¦ 0.54 ¦ ¦ 85 ¦ - ¦ ¦ - ¦ 0.47 ¦ ¦ 90 ¦ - ¦ - ¦ - ¦ 0.40 ¦ ¦ 95 ¦ ¦ ¦ - ¦ 0.32 ¦ ¦ a 이 이상의 주위온도에 대해서는 제조자와 협의 한다. ¦ a 이 이상의 주위온도에 대해서는 제조자와 협의 한다. ¦ a 이 이상의 주위온도에 대해서는 제조자와 협의 한다. ¦ a 이 이상의 주위온도에 대해서는 제조자와 협의 한다. ¦ a 이 이상의 주위온도에 대해서는 제조자와 협의 한다. ¦ 표 B.52.15 - 지중 케이블의 허용전류에 적용되는 지중 주위온도가 20 °C 이외인 경우의 보정계수 ¦ 지중 온도 °C ¦ 절연체 ¦ 절연체 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 지중 온도 °C ¦ PVC ¦ XLPE 또는 EPR ¦ ¦ 10 ¦ 1.10 ¦ 1.07 ¦ ¦ 15 ¦ 1.05 ¦ 1.04 ¦ ¦ 20 ¦ 1.00 ¦ 1.00 ¦ ¦ 25 ¦ 0.95 ¦ 0.96 ¦ ¦ 30 ¦ 0.89 ¦ 0.93 ¦ ¦ 35 ¦ 0.84 ¦ 0.89 ¦ ¦ 40 ¦ 0.77 ¦ 0.85 ¦ ¦ 45 ¦ 0.71 ¦ 0.80 ¦ ¦ 50 ¦ 0.63 ¦ 0.76 ¦ ¦ 55 ¦ 0.55 ¦ 0.71 ¦ ¦ 60 ¦ 0.45 ¦ 0.65 ¦ ¦ 65 ¦ ¦ 0.60 ¦ ¦ 70 ¦ - ¦ 0.53 ¦ ¦ 75 ¦ - ¦ 0.46 ¦ ¦ 80 ¦ ¦ 0.38 ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 43 | {}
b34e5bb3-99a7-4e14-b01f-2367ee16f365 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 B.52.16 - 지중에 직접 매설하거나 지중 덕트 내에 시설한 케이블에서 토양의 열 저항률이 2.5 K · m/W 이외인 경우의 보정계수. 참조 방법 D 의 허용전류(A)에 적용 ¦ 열 저항률, K · m/W ¦ 0.5 ¦ 0.7 ¦ 1 ¦ 1.5 ¦ 2 ¦ 2.5 ¦ 3 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 매설 덕트 내 케이블에 대한 보정계수 ¦ 1.28 ¦ 1.20 ¦ 1.18 ¦ 1.1 ¦ 1.05 ¦ 1 ¦ 0.96 ¦ ¦ 직접 매설한 케이블에 대한 보정계수 ¦ 1.88 ¦ 1.62 ¦ 1.5 ¦ 1.28 ¦ 1.12 ¦ 1 ¦ 0.90 ¦ ¦ 비고 1 표에 나타낸 보정계수는 표 B.52.2~표 B.52.5 에 제시된 도체의 사이즈와 설치 형태 범위 에 대한 평균값이다. 보정계수의 정확도는 ±5% 오차 범위 내에 있다. 비고 2 보정계수는 매설된 덕트에 설치한 케이블에 적용할 수 있다. 직접 매설된 케이블에 대해서 는 열저항률이 2.5 K · m/W 미만일 경우 보정계수가 더욱 커진다. 보다 정확한 값이 필요할 경우 IEC 60287 시리즈에서 규정하는 계산 방법으로 계산할 수 있다. 비고 3 보정계수는 매설 깊이가 0.8m 까지인 덕트에 적용할 수 있다. 비고 4 토양의 성질은 균일하다고 가정한다. 케이블 주변 지역의 열저항률을 높일 수 있는 수분 이동 가능성에 대한 허용오차는 주지 않았다. 토양의 부분적인 건조가 예상되는 경우, IEC 60287 시리즈에서 규정한 방법으로부터 허용전류를 구해야 한다. ¦ 비고 1 표에 나타낸 보정계수는 표 B.52.2~표 B.52.5 에 제시된 도체의 사이즈와 설치 형태 범위 에 대한 평균값이다. 보정계수의 정확도는 ±5% 오차 범위 내에 있다. 비고 2 보정계수는 매설된 덕트에 설치한 케이블에 적용할 수 있다. 직접 매설된 케이블에 대해서 는 열저항률이 2.5 K · m/W 미만일 경우 보정계수가 더욱 커진다. 보다 정확한 값이 필요할 경우 IEC 60287 시리즈에서 규정하는 계산 방법으로 계산할 수 있다. 비고 3 보정계수는 매설 깊이가 0.8m 까지인 덕트에 적용할 수 있다. 비고 4 토양의 성질은 균일하다고 가정한다. 케이블 주변 지역의 열저항률을 높일 수 있는 수분 이동 가능성에 대한 허용오차는 주지 않았다. 토양의 부분적인 건조가 예상되는 경우, IEC 60287 시리즈에서 규정한 방법으로부터 허용전류를 구해야 한다. ¦ 비고 1 표에 나타낸 보정계수는 표 B.52.2~표 B.52.5 에 제시된 도체의 사이즈와 설치 형태 범위 에 대한 평균값이다. 보정계수의 정확도는 ±5% 오차 범위 내에 있다. 비고 2 보정계수는 매설된 덕트에 설치한 케이블에 적용할 수 있다. 직접 매설된 케이블에 대해서 는 열저항률이 2.5 K · m/W 미만일 경우 보정계수가 더욱 커진다. 보다 정확한 값이 필요할 경우 IEC 60287 시리즈에서 규정하는 계산 방법으로 계산할 수 있다. 비고 3 보정계수는 매설 깊이가 0.8m 까지인 덕트에 적용할 수 있다. 비고 4 토양의 성질은 균일하다고 가정한다. 케이블 주변 지역의 열저항률을 높일 수 있는 수분 이동 가능성에 대한 허용오차는 주지 않았다. 토양의 부분적인 건조가 예상되는 경우, IEC 60287 시리즈에서 규정한 방법으로부터 허용전류를 구해야 한다. ¦ 비고 1 표에 나타낸 보정계수는 표 B.52.2~표 B.52.5 에 제시된 도체의 사이즈와 설치 형태 범위 에 대한 평균값이다. 보정계수의 정확도는 ±5% 오차 범위 내에 있다. 비고 2 보정계수는 매설된 덕트에 설치한 케이블에 적용할 수 있다. 직접 매설된 케이블에 대해서 는 열저항률이 2.5 K · m/W 미만일 경우 보정계수가 더욱 커진다. 보다 정확한 값이 필요할 경우 IEC 60287 시리즈에서 규정하는 계산 방법으로 계산할 수 있다. 비고 3 보정계수는 매설 깊이가 0.8m 까지인 덕트에 적용할 수 있다. 비고 4 토양의 성질은 균일하다고 가정한다. 케이블 주변 지역의 열저항률을 높일 수 있는 수분 이동 가능성에 대한 허용오차는 주지 않았다. 토양의 부분적인 건조가 예상되는 경우, IEC 60287 시리즈에서 규정한 방법으로부터 허용전류를 구해야 한다. ¦ 비고 1 표에 나타낸 보정계수는 표 B.52.2~표 B.52.5 에 제시된 도체의 사이즈와 설치 형태 범위 에 대한 평균값이다. 보정계수의 정확도는 ±5% 오차 범위 내에 있다. 비고 2 보정계수는 매설된 덕트에 설치한 케이블에 적용할 수 있다. 직접 매설된 케이블에 대해서 는 열저항률이 2.5 K · m/W 미만일 경우 보정계수가 더욱 커진다. 보다 정확한 값이 필요할 경우 IEC 60287 시리즈에서 규정하는 계산 방법으로 계산할 수 있다. 비고 3 보정계수는 매설 깊이가 0.8m 까지인 덕트에 적용할 수 있다. 비고 4 토양의 성질은 균일하다고 가정한다. 케이블 주변 지역의 열저항률을 높일 수 있는 수분 이동 가능성에 대한 허용오차는 주지 않았다. 토양의 부분적인 건조가 예상되는 경우, IEC 60287 시리즈에서 규정한 방법으로부터 허용전류를 구해야 한다. ¦ 비고 1 표에 나타낸 보정계수는 표 B.52.2~표 B.52.5 에 제시된 도체의 사이즈와 설치 형태 범위 에 대한 평균값이다. 보정계수의 정확도는 ±5% 오차 범위 내에 있다. 비고 2 보정계수는 매설된 덕트에 설치한 케이블에 적용할 수 있다. 직접 매설된 케이블에 대해서 는 열저항률이 2.5 K · m/W 미만일 경우 보정계수가 더욱 커진다. 보다 정확한 값이 필요할 경우 IEC 60287 시리즈에서 규정하는 계산 방법으로 계산할 수 있다. 비고 3 보정계수는 매설 깊이가 0.8m 까지인 덕트에 적용할 수 있다. 비고 4 토양의 성질은 균일하다고 가정한다. 케이블 주변 지역의 열저항률을 높일 수 있는 수분 이동 가능성에 대한 허용오차는 주지 않았다. 토양의 부분적인 건조가 예상되는 경우, IEC 60287 시리즈에서 규정한 방법으로부터 허용전류를 구해야 한다. ¦ 비고 1 표에 나타낸 보정계수는 표 B.52.2~표 B.52.5 에 제시된 도체의 사이즈와 설치 형태 범위 에 대한 평균값이다. 보정계수의 정확도는 ±5% 오차 범위 내에 있다. 비고 2 보정계수는 매설된 덕트에 설치한 케이블에 적용할 수 있다. 직접 매설된 케이블에 대해서 는 열저항률이 2.5 K · m/W 미만일 경우 보정계수가 더욱 커진다. 보다 정확한 값이 필요할 경우 IEC 60287 시리즈에서 규정하는 계산 방법으로 계산할 수 있다. 비고 3 보정계수는 매설 깊이가 0.8m 까지인 덕트에 적용할 수 있다. 비고 4 토양의 성질은 균일하다고 가정한다. 케이블 주변 지역의 열저항률을 높일 수 있는 수분 이동 가능성에 대한 허용오차는 주지 않았다. 토양의 부분적인 건조가 예상되는 경우, IEC 60287 시리즈에서 규정한 방법으로부터 허용전류를 구해야 한다. ¦ 비고 1 표에 나타낸 보정계수는 표 B.52.2~표 B.52.5 에 제시된 도체의 사이즈와 설치 형태 범위 에 대한 평균값이다. 보정계수의 정확도는 ±5% 오차 범위 내에 있다. 비고 2 보정계수는 매설된 덕트에 설치한 케이블에 적용할 수 있다. 직접 매설된 케이블에 대해서 는 열저항률이 2.5 K · m/W 미만일 경우 보정계수가 더욱 커진다. 보다 정확한 값이 필요할 경우 IEC 60287 시리즈에서 규정하는 계산 방법으로 계산할 수 있다. 비고 3 보정계수는 매설 깊이가 0.8m 까지인 덕트에 적용할 수 있다. 비고 4 토양의 성질은 균일하다고 가정한다. 케이블 주변 지역의 열저항률을 높일 수 있는 수분 이동 가능성에 대한 허용오차는 주지 않았다. 토양의 부분적인 건조가 예상되는 경우, IEC 60287 시리즈에서 규정한 방법으로부터 허용전류를 구해야 한다. ¦ 표 B.52.17 - 단일 회로 또는 단일 다심케이블 또는 복수회로 또는 복수 다심케이블에 대한 저감 계수. 표 B.52.2~표 B.52.13 의 허용전류를 이용 ¦ 항 ¦ 배치 (케이블 접촉) ¦ 회로 또는 다심케이블의 수 ¦ 회로 또는 다심케이블의 수 ¦ 회로 또는 다심케이블의 수 ¦ 회로 또는 다심케이블의 수 ¦ 회로 또는 다심케이블의 수 ¦ 회로 또는 다심케이블의 수 ¦ 회로 또는 다심케이블의 수 ¦ 회로 또는 다심케이블의 수 ¦ 회로 또는 다심케이블의 수 ¦ 회로 또는 다심케이블의 수 ¦ 회로 또는 다심케이블의 수 ¦ 회로 또는 다심케이블의 수 ¦ 허용전류에 따라 사용 참조 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 항 ¦ 배치 (케이블 접촉) ¦ 1 ¦ 2 ¦ 3 ¦ 4 ¦ 5 ¦ 6 ¦ 7 ¦ 8 ¦ 9 ¦ 12 ¦ 16 ¦ 20 ¦ 허용전류에 따라 사용 참조 ¦ ¦ 1 ¦ 기중이나 벽면에 묶음 설치, 매설 또는 수납 ¦ 1.00 ¦ 0.80 ¦ 0.70 ¦ 0.65 ¦ 0.60 ¦ 0.57 ¦ 0.54 ¦ 0.52 ¦ 0.50 ¦ 0.45 ¦ 0.41 ¦ 0.38 ¦ B.52.2 ~ B.52.13 방법 A~F ¦ ¦ 2 ¦ 벽, 바닥 또는 비천공 케이블 트레이의 단일층 ¦ 1.00 ¦ 0.85 ¦ 0.79 ¦ 0.75 ¦ 0.73 ¦ 0.72 ¦ 0.72 ¦ 0.71 ¦ 0.70 ¦ 9 개 이상의 회로나 다심 케이블인 경우, 더 이상의 저감 계수는 없음. ¦ 9 개 이상의 회로나 다심 케이블인 경우, 더 이상의 저감 계수는 없음. ¦ 9 개 이상의 회로나 다심 케이블인 경우, 더 이상의 저감 계수는 없음. ¦ B.52.2 ~ B.52.7 방법 C ¦ ¦ 3 ¦ 목재 천장면 아래에 직접 고정한 단일층 ¦ 0.95 ¦ 0.81 ¦ 0.72 ¦ 0.68 ¦ 0.66 ¦ 0.64 ¦ 0.63 ¦ 0.62 ¦ 0.61 ¦ 9 개 이상의 회로나 다심 케이블인 경우, 더 이상의 저감 계수는 없음. ¦ 9 개 이상의 회로나 다심 케이블인 경우, 더 이상의 저감 계수는 없음. ¦ 9 개 이상의 회로나 다심 케이블인 경우, 더 이상의 저감 계수는 없음. ¦ B.52.2 ~ B.52.7 방법 C ¦ ¦ 4 ¦ 천공형 수평 또는 수직 케이블 트 레이의 단일층 ¦ 1.00 ¦ 0.88 ¦ 0.82 ¦ 0.77 ¦ 0.75 ¦ 0.73 ¦ 0.73 ¦ 0.72 ¦ 0.72 ¦ 9 개 이상의 회로나 다심 케이블인 경우, 더 이상의 저감 계수는 없음. ¦ 9 개 이상의 회로나 다심 케이블인 경우, 더 이상의 저감 계수는 없음. ¦ 9 개 이상의 회로나 다심 케이블인 경우, 더 이상의 저감 계수는 없음. ¦ B.52.8 ~ B.52.13 방법 E 와 F ¦ ¦ 5 ¦ 케이블래더 단일층 또는 클리트 지지 등 ¦ 1.00 ¦ 0.87 ¦ 0.82 ¦ 0.80 ¦ 0.80 ¦ 0.79 ¦ 0.79 ¦ 0.78 ¦ 0.78 ¦ 9 개 이상의 회로나 다심 케이블인 경우, 더 이상의 저감 계수는 없음. ¦ 9 개 이상의 회로나 다심 케이블인 경우, 더 이상의 저감 계수는 없음. ¦ 9 개 이상의 회로나 다심 케이블인 경우, 더 이상의 저감 계수는 없음. ¦ B.52.8 ~ B.52.13 방법 E 와 F ¦ 비고 1 이 계수는 동일하게 부하가 걸리는 동일 집합에 속한 케이블에 적용할 수 있다. 비고 2 인접 케이블 간의 수평 간격이 케이블 전체 바깥지름의 2 배를 초과 할 경우, 저감 계수를 적 용할 필요는 없다. 비고 3 다음에 같은 계수가 적용된다. · 단심케이블 2 개 또는 3 개의 그룹 · 다심케이블 44 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
83f664e5-5a01-4b2d-87a2-8bced89eaae0 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 B.52.17 - 단일 회로 또는 단일 다심케이블 또는 복수회로 또는 복수 다심케이블에 대한 저감 계수. 표 B.52.2~B.52.13 의 허용전류를 이용(계속) ¦ 비고 4 ¦ 하나의 배선설비가 2 심과 3 심 케이블로 구성된 경우, 전체 케이블 수는 회로 수와 같은 것 으로 간주하고, 그 보정계수는 2 심 케이블에는 2 개 부하 도체의 표를, 3 심 케이블에는 3 개 부하 도체의 표를 적용한다. ¦ ¦ --- ¦ --- ¦ ¦ 비고 5 ¦ 집합이 n 개 단심케이블로 구성된 경우, 2 개 부하 도체의 n/2 개 회로 또는 3 개 부하 도체의 n/3 개 회로로 간주해도 좋다. ¦ ¦ 비고 6 ¦ 이 표에 나타낸 값은 표 B.52.2~표 B.52.13 에 제시된 도체 범위의 설치형태에 대한 평균값 이다. 보정계수의 정확도는 5% 오차 범위 내에 있다. ¦ ¦ 비고 7 ¦ 이 표에 나타내지 않은 다른 설치방법과 일부 설비에 대해서는 특정 경우에 맞는 계수를 사 용하는 것이 바람직하며 표 B.52.20~표 B.52.21 의 예를 참조한다. ¦ 표 B.52.18 - 지중에 직접 시설한 복수회로, 케이블에 대한 저감 계수 표 B.52.2~표 B.52.5 의 설치방법 D2 - 단심 또는 다심케이블 ¦ 회로수 ¦ 케이블간 간격 a ¦ 케이블간 간격 a ¦ 케이블간 간격 a ¦ 케이블간 간격 a ¦ 케이블간 간격 a ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 회로수 ¦ 0 (케이블 접촉) ¦ 1 케이블의 지름 ¦ 0.125 m ¦ 0.25 m ¦ 0.5 m ¦ ¦ 2 ¦ 0.75 ¦ 0.80 ¦ 0.85 ¦ 0.90 ¦ 0.90 ¦ ¦ 3 ¦ 0.65 ¦ 0.70 ¦ 0.75 ¦ 0.80 ¦ 0.85 ¦ ¦ 4 ¦ 0.60 ¦ 0.60 ¦ 0.70 ¦ 0.75 ¦ 0.80 ¦ ¦ 5 ¦ 0.55 ¦ 0.55 ¦ 0.65 ¦ 0.70 ¦ 0.80 ¦ ¦ 6 ¦ 0.50 ¦ 0.55 ¦ 0.60 ¦ 0.70 ¦ 0.80 ¦ ¦ 7 ¦ 0.45 ¦ 0.51 ¦ 0.59 ¦ 0.67 ¦ 0.76 ¦ ¦ 8 ¦ 0.43 ¦ 0.48 ¦ 0.57 ¦ 0.65 ¦ 0.75 ¦ ¦ 9 ¦ 0.41 ¦ 0.46 ¦ 0.55 ¦ 0.63 ¦ 0.74 ¦ ¦ 12 ¦ 0.36 ¦ 0.42 ¦ 0.51 ¦ 0.59 ¦ 0.71 ¦ ¦ 16 ¦ 0.32 ¦ 0.38 ¦ 0.47 ¦ 0.56 ¦ 0.68 ¦ ¦ 20 ¦ 0.29 ¦ 0.35 ¦ 0.44 ¦ 0.53 ¦ 0.66 ¦ ¦ a 다심케이블 a 단심케이블 ¦ oo 品 品 a ⊙⊙ ⊙⊙ 열저항률이 · m/W 인 % 범위의 값을 ¦ oo 品 品 a ⊙⊙ ⊙⊙ 열저항률이 · m/W 인 % 범위의 값을 ¦ oo 品 品 a ⊙⊙ ⊙⊙ 열저항률이 · m/W 인 % 범위의 값을 ¦ oo 品 品 a ⊙⊙ ⊙⊙ 열저항률이 · m/W 인 % 범위의 값을 ¦ oo 品 品 a ⊙⊙ ⊙⊙ 열저항률이 · m/W 인 % 범위의 값을 ¦ ¦ 비고 1 이 값은 매설 깊이가 0.7 m, 토양의 경우에 적용한다. 이 값은 표 B.52.2~ 표 B.52.5 에 제시된 케이블의 사이즈와 설치 형태 범위에 대한 평균값이다. 평 균을 구해 그 값을 반올림하여 ±10 오차 얻을 수 있다(보다 정확한 값이 ¦ 2.5K ¦ 2.5K ¦ 2.5K ¦ 2.5K ¦ 2.5K ¦ 필요할 경우, KS C IEC 60287-2-1 에서 규정하는 방법으로 계산할 수 있다). 비고 2 열저항률이 2.5K · m/W 미만일 경우 일반적으로 보정계수가 증가할 수 있으며, KS C IEC 60287-2-1 에 규정된 방법으로 계산할 수 있다. 비고 3 각 상당 병렬도체 m 개로 구성된 회로가 있다면, 저감계수를 결정하기 위해서는 회로를 m 개 회로로 간주해야 한다. 45 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
5cf096ca-96e4-475e-91b2-8df092888add | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 B.52.19 - 지중 덕트 내에 시설한 복수의 회로, 케이블에 대한 저감 계수 표 B.52.2~표 B.52.5 의 설치방법 D1 ¦ A) 단일 덕트 내의 다심케이블 ¦ A) 단일 덕트 내의 다심케이블 ¦ A) 단일 덕트 내의 다심케이블 ¦ A) 단일 덕트 내의 다심케이블 ¦ A) 단일 덕트 내의 다심케이블 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 케이블 수 ¦ 덕트의 간격 a ¦ 덕트의 간격 a ¦ 덕트의 간격 a ¦ 덕트의 간격 a ¦ ¦ 케이블 수 ¦ 0(덕트 접촉) ¦ 0.25 m ¦ 0.5 m ¦ 1.0 m ¦ ¦ 2 ¦ 0.85 ¦ 0.90 ¦ 0.95 ¦ 0.95 ¦ ¦ 3 ¦ 0.75 ¦ 0.85 ¦ 0.90 ¦ 0.95 ¦ ¦ 4 ¦ 0.70 ¦ 0.80 ¦ 0.85 ¦ 0.90 ¦ ¦ 5 ¦ 0.65 ¦ 0.80 ¦ 0.85 ¦ 0.90 ¦ ¦ 6 ¦ 0.60 ¦ 0.80 ¦ 0.80 ¦ 0.90 ¦ ¦ 7 ¦ 0.57 ¦ 0.76 ¦ 0.80 ¦ 0.88 ¦ ¦ 8 ¦ 0.54 ¦ 0.74 ¦ 0.78 ¦ 0.88 ¦ ¦ 9 ¦ 0.52 ¦ 0.73 ¦ 0.77 ¦ 0.87 ¦ ¦ 10 ¦ 0.49 ¦ 0.72 ¦ 0.76 ¦ 0.86 ¦ ¦ 11 ¦ 0.47 ¦ 0.70 ¦ 0.75 ¦ 0.86 ¦ ¦ 12 ¦ 0.45 ¦ 0.69 ¦ 0.74 ¦ 0.85 ¦ ¦ 13 ¦ 0.44 ¦ 0.68 ¦ 0.73 ¦ 0.85 ¦ ¦ 14 ¦ 0.42 ¦ 0.68 ¦ 0.72 ¦ 0.84 ¦ ¦ 15 ¦ 0.41 ¦ 0.67 ¦ 0.72 ¦ 0.84 ¦ ¦ 16 ¦ 0.39 ¦ 0.66 ¦ 0.71 ¦ 0.83 ¦ ¦ 17 ¦ 0.38 ¦ 0.65 ¦ 0.70 ¦ 0.83 ¦ ¦ 18 ¦ 0.37 ¦ 0.65 ¦ 0.70 ¦ 0.83 ¦ ¦ 19 ¦ 0.35 ¦ 0.64 ¦ 0.69 ¦ 0.82 ¦ ¦ 20 ¦ 0.34 ¦ 0.63 ¦ 0.68 ¦ 0.82 ¦ ¦ B) 비자성 단일(single-way) 덕트 내의 단심케이블 ¦ B) 비자성 단일(single-way) 덕트 내의 단심케이블 ¦ B) 비자성 단일(single-way) 덕트 내의 단심케이블 ¦ B) 비자성 단일(single-way) 덕트 내의 단심케이블 ¦ B) 비자성 단일(single-way) 덕트 내의 단심케이블 ¦ ¦ 단심케이블 2 개 ¦ 덕트의 간격 b ¦ 덕트의 간격 b ¦ 덕트의 간격 b ¦ 덕트의 간격 b ¦ ¦ 또는 3 개로 구성된 회로의 수 ¦ 0(덕트 접촉) ¦ 0.25 m ¦ 0.5 m ¦ 1.0 m ¦ ¦ 2 ¦ 0.80 ¦ 0.90 ¦ 0.90 ¦ 0.95 ¦ ¦ 3 ¦ 0.70 ¦ 0.80 ¦ 0.85 ¦ 0.90 ¦ ¦ 4 ¦ 0.65 ¦ 0.75 ¦ 0.80 ¦ 0.90 ¦ ¦ 5 ¦ 0.60 ¦ 0.70 ¦ 0.80 ¦ 0.90 ¦ ¦ 6 ¦ 0.60 ¦ 0.70 ¦ 0.80 ¦ 0.90 ¦ ¦ 7 ¦ 0.53 ¦ 0.66 ¦ 0.76 ¦ 0.87 ¦ ¦ 8 ¦ 0.50 ¦ 0.63 ¦ 0.74 ¦ 0.87 ¦ ¦ 9 ¦ 0.47 ¦ 0.61 ¦ 0.73 ¦ 0.86 ¦ ¦ 10 ¦ 0.45 ¦ 0.59 ¦ 0.72 ¦ 0.85 ¦ ¦ 11 ¦ 0.43 ¦ 0.57 ¦ 0.70 ¦ 0.85 ¦ ¦ 12 ¦ 0.41 ¦ 0.56 ¦ 0.69 ¦ 0.84 ¦ ¦ 13 ¦ 0.39 ¦ 0.54 ¦ 0.68 ¦ 0.84 ¦ ¦ 14 ¦ 0.37 ¦ 0.53 ¦ 0.68 ¦ 0.83 ¦ ¦ 15 ¦ 0.35 ¦ 0.52 ¦ 0.67 ¦ 0.83 ¦ ¦ 16 ¦ 0.34 ¦ 0.51 ¦ 0.66 ¦ 0.83 ¦ ¦ 17 ¦ 0.33 ¦ 0.50 ¦ 0.65 ¦ 0.82 ¦ ¦ 18 ¦ 0.31 ¦ 0.49 ¦ 0.65 ¦ 0.82 ¦ ¦ 19 ¦ 0.30 ¦ 0.48 ¦ 0.64 ¦ 0.82 ¦ ¦ 20 ¦ 0.29 ¦ 0.47 ¦ 0.63 ¦ 0.81 ¦ 46 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
31bdd160-c66c-4602-9a2e-c44b51559b20 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 B.52.19 - 지중 덕트 내에 시설한 복수의 회로, 케이블에 대한 저감 계수 표 B.52.2~표 B.52.5 의 설치방법 D1(계속) ¦ a 다심케이블 ¦ a ¦ ¦ --- ¦ --- ¦ ¦ b 단심케이블 ¦ a ¦ ¦ 비고 1 이 값은 매설 깊이가 0.7 m, 토양의 열저항률이 2.5 K · m/W 인 경우에 적용한다. 이 값은 표 B.52.2~표 B.52.5 에 제시된 케이블의 사이즈와 설치 형태 범위에 대한 평균값 이다. 평균을 구해 그 값을 반올림하여 ±10 % 오차 범위의 값을 얻을 수 있다. 보다 정확 한 값이 필요할 경우, IEC 60287 시리즈에서 규정하는 방법으로 계산할 수 있다. 비고 2 열저항률이 2.5K · m/W 미만일 경우 일반적으로 보정계수가 증가할 수 있으며, KS C IEC 60287-2-1 에 규정된 방법으로 계산할 수 있다. 비고 3 각 상당 병렬도체 n 개로 구성된 회로가 있다면, 저감계수를 결정하기 위해서는 회로를 n 개 회로로 간주해야 한다. ¦ 비고 1 이 값은 매설 깊이가 0.7 m, 토양의 열저항률이 2.5 K · m/W 인 경우에 적용한다. 이 값은 표 B.52.2~표 B.52.5 에 제시된 케이블의 사이즈와 설치 형태 범위에 대한 평균값 이다. 평균을 구해 그 값을 반올림하여 ±10 % 오차 범위의 값을 얻을 수 있다. 보다 정확 한 값이 필요할 경우, IEC 60287 시리즈에서 규정하는 방법으로 계산할 수 있다. 비고 2 열저항률이 2.5K · m/W 미만일 경우 일반적으로 보정계수가 증가할 수 있으며, KS C IEC 60287-2-1 에 규정된 방법으로 계산할 수 있다. 비고 3 각 상당 병렬도체 n 개로 구성된 회로가 있다면, 저감계수를 결정하기 위해서는 회로를 n 개 회로로 간주해야 한다. ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 47 | {}
ab0acbdd-92fc-4ca9-96fb-89ee0ac0b8e4 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 B.52.20 기중 개방의 다심케이블의 참고허용전류로 적용되는 복수의 다심케이블의 집합에 대한 저감 계수 - 표 B.52.8~표 B.52.13 의 설치방법 E ¦ 표 A.52.3 의 설치방법 ¦ 표 A.52.3 의 설치방법 ¦ 표 A.52.3 의 설치방법 ¦ 트레이 또는 래더 수 ¦ 트레이 또는 래더당 케이블의 수 ¦ 트레이 또는 래더당 케이블의 수 ¦ 트레이 또는 래더당 케이블의 수 ¦ 트레이 또는 래더당 케이블의 수 ¦ 트레이 또는 래더당 케이블의 수 ¦ 트레이 또는 래더당 케이블의 수 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 표 A.52.3 의 설치방법 ¦ 표 A.52.3 의 설치방법 ¦ 표 A.52.3 의 설치방법 ¦ 트레이 또는 래더 수 ¦ 1 ¦ 2 ¦ 3 ¦ 4 ¦ 6 ¦ 9 ¦ ¦ 천공형 트레이 (비고 3) ¦ 31 ¦ 접촉 ≥ 20 mm ≥300 mm ¦ 1 2 3 6 ¦ 1.00 1.00 1.00 1.00 ¦ 0.88 0.87 0.86 0.84 ¦ 0.82 0.80 0.79 0.77 ¦ 0.79 0.77 0.76 0.73 ¦ 0.76 0.73 0.71 0.68 ¦ 0.73 0.68 0.66 0.64 ¦ ¦ 천공형 트레이 (비고 3) ¦ 31 ¦ 이격 De ≥ 20 mm ¦ 1 2 3 ¦ 1.00 1.00 1.00 ¦ 1.00 0.99 0.98 ¦ 0.98 0.96 0.95 ¦ 0.95 0.92 0.91 ¦ 0.91 0.87 0.85 ¦ - - - ¦ ¦ 수직 천공형 트레이 (비고 4) ¦ 31 ¦ 접촉 26 8 。 ≥ 225 mm ¦ 1 2 ¦ 1.00 1.00 ¦ 0.88 0.88 ¦ 0.82 0.81 ¦ 0.78 0.76 ¦ 0.73 0.71 ¦ 0.72 0.70 ¦ ¦ 수직 천공형 트레이 (비고 4) ¦ 31 ¦ 이격 ○ � � ≥ De 。 225 。 mm : ¦ 1 2 ¦ 1.00 1.00 ¦ 0.91 0.91 ¦ 0.89 0.88 ¦ 0.88 0.87 ¦ 0.87 0.85 ¦ - - ¦ ¦ 비천공형 트레이 ¦ 31 ¦ 접촉 ≥20mm ≥300 mm ¦ 1 2 3 6 ¦ 0.97 0.97 0.97 0.97 ¦ 0.84 0.83 0.82 0.81 ¦ 0.78 0.76 0.75 0.73 ¦ 0.75 0.72 0.71 0.69 ¦ 0.71 0.68 0.66 0.63 ¦ 0.68 0.63 0.61 0.58 ¦ ¦ 래더, 브래킷, 클리트 기타 (비고 3) ¦ 32 33 34 ¦ 접촉 ≥20 mm ≥300 mm ¦ 1 2 3 6 ¦ 1.00 1.00 1.00 1.00 ¦ 0.87 0.86 0.85 0.84 ¦ 0.82 0.80 0.79 0.77 ¦ 0.80 0.78 0.76 0.73 ¦ 0.79 0.76 0.73 0.68 ¦ 0.78 0.73 0.70 0.64 ¦ ¦ 래더, 브래킷, 클리트 기타 (비고 3) ¦ 32 33 34 ¦ 이격 밀착 De > 20 mm ¦ 1 2 3 ¦ 1.00 1.00 1.00 ¦ 1.00 0.99 0.98 ¦ 1.00 0.98 0.97 ¦ 1.00 0.97 0.96 ¦ 1.00 0.97 0.93 ¦ - - - ¦ 비고 1 이 표의 값은 표 A.52.8 ~ 표 A.52.13 에서 검토한 케이블 형태와 도체 사이즈 분산 범위에 대한 평균값이다. 이 값의 폭은 일반적으로 5% 이하이다. 비고 2 이 계수는 상기와 같이 단일 층에 설치한 케이블 집합에 적용하고, 상호 접촉하는 2 층 이 상의 케이블 설치에는 적용하지 않는다. 이러한 설치방법에 대한 계수는 상당히 작으며, 적 절한 방법을 통해 결정해야 한다. 비고 3 이 값은 트레이 간의 수직 간격이 300 mm 이고 케이블 트레이와 벽 간 간격은 20 mm 이상 인 경우이다. 이보다 간격이 좁을 경우 계수를 감소시켜야 한다. 비고 4 이 값은 배면 방향으로 부착한 트레이 사이의 수평 간격이 225 mm 인 경우이다. 이보다 간 격이 좁을 경우 계수를 감소시켜야 한다. 48 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b49fde7e-5606-48f9-9ba1-0abde05d7807 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 B.52.21 - 기중 개방의 하나의 단심케이블의 참고허용전류에 적용되는 하나 이상의 단심케이블의 집합에 대한 저감 계수 - 표 B.52.8~표 B.52.13 의 설치방법 F ¦ 표 A.52.3 의 설치방법 ¦ 표 A.52.3 의 설치방법 ¦ 표 A.52.3 의 설치방법 ¦ 트레이 또는 래더 수 ¦ 트레이 또는 래더당 3 상 회로의 수 ¦ 트레이 또는 래더당 3 상 회로의 수 ¦ 트레이 또는 래더당 3 상 회로의 수 ¦ 해당 허용전류에 대한 승수로 사용 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 표 A.52.3 의 설치방법 ¦ 표 A.52.3 의 설치방법 ¦ 표 A.52.3 의 설치방법 ¦ 트레이 또는 래더 수 ¦ 1 ¦ 2 ¦ 3 ¦ 해당 허용전류에 대한 승수로 사용 ¦ ¦ 천공형 트레이 (비고 3) ¦ 31 ¦ 접촉 ⊙ ≥300 mm TV 20 mm ¦ 1 2 3 ¦ 0.98 0.96 0.95 ¦ 0.91 0.87 0.85 ¦ 0.87 0.81 0.78 ¦ 수평 배치한 3 개 케이블 ¦ ¦ 수직 천공형 트레이 (비고 4) ¦ 31 ¦ 접촉 225 mm : ¦ 1 2 ¦ 0.96 0.95 ¦ 0.86 0.84 ¦ - - ¦ 수직 배치한 3 개 케이블 ¦ ¦ 래더, 브래킷, 클리트 기타 (비고 3) ¦ 32 33 34 ¦ 접촉 300 mm ≥ 20 mm ¦ 1 2 3 ¦ 1.00 0.98 0.97 ¦ 0.97 0.93 0.90 ¦ 0.96 0.89 0.86 ¦ 수평 배치한 3 개 케이블 ¦ ¦ 천공형 트레이 (비고 3) ¦ 31 ¦ ≥2De De 。 ≥300 mm ≥20mm ¦ 1 2 3 ¦ 1.00 0.97 0.96 ¦ 0.98 0.93 0.92 ¦ 0.96 0.89 0.86 ¦ 삼각배치의 3 개 케이블 ¦ ¦ 수직 천공형 트레이 (비고 4) ¦ 31 ¦ 이격 ≥2De De 이 ≥ 300 mm ≥20 mm ¦ 1 2 ¦ 1.00 1.00 ¦ 0.91 0.90 ¦ 0.89 0.86 ¦ 삼각배치의 3 개 케이블 ¦ ¦ 래더, 브래킷, 클리트 기타 (비고 3) ¦ 32 33 34 ¦ ≥2De Mr De ≥ 300 mm ≥ 20 mm ¦ 1 2 3 ¦ 1.00 0.97 0.96 ¦ 1.00 0.95 0.94 ¦ 1.00 0.93 0.90 ¦ 삼각배치의 3 개 케이블 ¦ ¦ 비고 1 ¦ 이 표의 값은 표 B.52.8~ 표 B.52.13 에서 검토한 케이블 형태와 도체 사이즈 분산 범위에 대한 평균값이다. 이 값의 폭은 일반적으로 5% 이하이다. ¦ ¦ --- ¦ --- ¦ ¦ 비고 2 ¦ 이 계수는 상기와 같이 단일 층으로 설치한 케이블 집합(또는 삼각배치 집합)에 적용하고, 상호 접촉하여 2 층 이상으로 설치한 케이블에는 적용하지 않는다. 이러한 설치방법에 대한 계수는 상당히 작은 값이 될 수 있으며, 적절한 방법을 통해 결정해야 한다. ¦ ¦ 비고 3 ¦ 이 값은 트레이 간의 수직 간격이 300 mm, 케이블 트레이와 벽의 간격은 20 mm 이상인 경우이다. 이보다 수직 간격이 좁을 경우, 계수를 줄여야 한다. ¦ ¦ 비고 4 ¦ 이 값은 배면 방향으로 부착한 트레이 사이의 수평 간격이 225 mm 인 경우이다. 이보다 간 격이 좁을 경우, 계수를 줄여야 한다. ¦ ¦ 비고 5 ¦ 상마다 복수의 케이블이 병렬로 있는 회로인 경우, 이 표의 적용을 위해 도체의 3 선도체 세트를 하나의 회로로 간주한다. ¦ ¦ 비고 6 ¦ 상당 병렬도체 m 개로 구성된 회로인 경우, 저감 계수를 결정하기 위해서는 이 회로를 m 개 회로로 간주해야 한다. ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 49 | {}
5f2dec02-ea9c-46bf-a4b1-84e3a31f4d70 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 부속서 C (참고) 523 절 표의 간략화(예) 이 부속서는 표 B.52.2~ 표 B.52.5, 표 B.52.10~ 표 B.52.13 및 표 B.52.17~ 표 B.52.21 을 각국의 규 정에서 채용하기 위해 간략화하는 방법의 일례를 나타낸 것이다. 여기 기술한 것 이외의 다른 적절한 방법의 사용을 제외하는 것은 아니다(523.2 의 비고 1 참조). 표 C.52.1 허용전류(A) ¦ 표 B.52.1 의 설치방법 ¦ 절연체의 종류와 부하 도체의 수 ¦ 절연체의 종류와 부하 도체의 수 ¦ 절연체의 종류와 부하 도체의 수 ¦ 절연체의 종류와 부하 도체의 수 ¦ 절연체의 종류와 부하 도체의 수 ¦ 절연체의 종류와 부하 도체의 수 ¦ 절연체의 종류와 부하 도체의 수 ¦ 절연체의 종류와 부하 도체의 수 ¦ 절연체의 종류와 부하 도체의 수 ¦ 절연체의 종류와 부하 도체의 수 ¦ 절연체의 종류와 부하 도체의 수 ¦ 절연체의 종류와 부하 도체의 수 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ A1 ¦ ¦ 3PVC ¦ 2PVC ¦ ¦ 3 XLPE ¦ 2XLPE ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ A2 ¦ 3 PVC ¦ 2PVC ¦ ¦ 3 XLPE ¦ 2 XLPE ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ B1 ¦ ¦ ¦ ¦ 3 PVC ¦ 2PVC ¦ ¦ 3 XLPE ¦ ¦ 2 XLPE ¦ ¦ ¦ ¦ ¦ B2 ¦ ¦ ¦ 3 PVC ¦ 2PVC ¦ ¦ 3 XLPE ¦ 2XLPE ¦ ¦ ¦ ¦ ¦ ¦ ¦ C ¦ ¦ ¦ ¦ ¦ 3PVC ¦ ¦ 2PVC ¦ 3 XLPE ¦ ¦ 2XLPE ¦ ¦ ¦ ¦ E ¦ ¦ ¦ ¦ ¦ ¦ 3PVC ¦ ¦ 2PVC ¦ 3 XPLE ¦ ¦ 2XLPE ¦ ¦ ¦ F ¦ ¦ ¦ ¦ ¦ ¦ ¦ 3 PVC ¦ ¦ 2PVC ¦ 3 XLPE ¦ ¦ 2XLPE ¦ ¦ 1 ¦ 2 ¦ 3 ¦ 4 ¦ 5 ¦ 6 ¦ 7 ¦ 8 ¦ 9 ¦ 10 ¦ 11 ¦ 12 ¦ 13 ¦ ¦ 사이즈(mm2) 구리 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 1.5 ¦ 13 ¦ 13.5 ¦ 14.5 ¦ 15.5 ¦ 17 ¦ 18.5 ¦ 19.5 ¦ 22 ¦ 23 ¦ 24 ¦ 26 ¦ - ¦ ¦ 2.5 ¦ 17.5 ¦ 18 ¦ 19.5 ¦ 21 ¦ 23 ¦ 25 ¦ 27 ¦ 30 ¦ 31 ¦ 33 ¦ 36 ¦ - ¦ ¦ 4 ¦ 23 ¦ 24 ¦ 26 ¦ 28 ¦ 31 ¦ 34 ¦ 36 ¦ 40 ¦ 42 ¦ 45 ¦ 49 ¦ - ¦ ¦ 6 ¦ 29 ¦ 31 ¦ 34 ¦ 36 ¦ 40 ¦ 43 ¦ 46 ¦ 51 ¦ 54 ¦ 58 ¦ 63 ¦ - ¦ ¦ 10 ¦ 39 ¦ 42 ¦ 46 ¦ 50 ¦ 54 ¦ 60 ¦ 63 ¦ 70 ¦ 75 ¦ 80 ¦ 86 ¦ - ¦ ¦ 16 ¦ 52 ¦ 56 ¦ 61 ¦ 68 ¦ 73 ¦ 80 ¦ 85 ¦ 94 ¦ 100 ¦ 107 ¦ 115 ¦ - ¦ ¦ 25 ¦ 68 ¦ 73 ¦ 80 ¦ 89 ¦ 95 ¦ 101 ¦ 110 ¦ 119 ¦ 127 ¦ 135 ¦ 149 ¦ 161 ¦ ¦ 35 ¦ ¦ - ¦ - ¦ 110 ¦ 117 ¦ 126 ¦ 137 ¦ 147 ¦ 158 ¦ 169 ¦ 185 ¦ 200 ¦ ¦ 50 ¦ - ¦ - ¦ - ¦ 134 ¦ 141 ¦ 153 ¦ 167 ¦ 179 ¦ 192 ¦ 207 ¦ 225 ¦ 242 ¦ ¦ 70 ¦ - ¦ - ¦ - ¦ 171 ¦ 179 ¦ 196 ¦ 213 ¦ 229 ¦ 246 ¦ 268 ¦ 289 ¦ 310 ¦ ¦ 95 ¦ - ¦ - ¦ - ¦ 207 ¦ 216 ¦ 238 ¦ 258 ¦ 278 ¦ 298 ¦ 328 ¦ 352 ¦ 377 ¦ ¦ 120 ¦ - ¦ - ¦ - ¦ 239 ¦ 249 ¦ 276 ¦ 299 ¦ 322 ¦ 346 ¦ 382 ¦ 410 ¦ 437 ¦ ¦ 150 ¦ - ¦ - ¦ - ¦ ¦ 285 ¦ 318 ¦ 344 ¦ 371 ¦ 395 ¦ 441 ¦ 473 ¦ 504 ¦ ¦ 185 ¦ - ¦ - ¦ - ¦ - ¦ 324 ¦ 362 ¦ 392 ¦ 424 ¦ 450 ¦ 506 ¦ 542 ¦ 575 ¦ ¦ 240 ¦ - ¦ - ¦ - ¦ - ¦ 380 ¦ 424 ¦ 461 ¦ 500 ¦ 538 ¦ 599 ¦ 641 ¦ 679 ¦ 50 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
6387766d-3145-49a7-a8d3-dff1a58df3b0 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 C.52.1 허용전류(A)(계속) ¦ 표 B.52.1 의 설치방법 ¦ 절연체의 종류와 부하 도체의 수 ¦ 절연체의 종류와 부하 도체의 수 ¦ 절연체의 종류와 부하 도체의 수 ¦ 절연체의 종류와 부하 도체의 수 ¦ 절연체의 종류와 부하 도체의 수 ¦ 절연체의 종류와 부하 도체의 수 ¦ 절연체의 종류와 부하 도체의 수 ¦ 절연체의 종류와 부하 도체의 수 ¦ 절연체의 종류와 부하 도체의 수 ¦ 절연체의 종류와 부하 도체의 수 ¦ 절연체의 종류와 부하 도체의 수 ¦ 절연체의 종류와 부하 도체의 수 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 알루미늄 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 2.5 ¦ 13.5 ¦ 14 ¦ 15 ¦ 16.5 ¦ 18.5 ¦ 19.5 ¦ 21 ¦ 23 ¦ 24 ¦ 26 ¦ 28 ¦ - ¦ ¦ 4 ¦ 17.5 ¦ 18.5 ¦ 20 ¦ 22 ¦ 25 ¦ 26 ¦ 28 ¦ 31 ¦ 32 ¦ 35 ¦ 38 ¦ - ¦ ¦ 6 ¦ 23 ¦ 24 ¦ 26 ¦ 28 ¦ 32 ¦ 33 ¦ 36 ¦ 39 ¦ 42 ¦ 45 ¦ 49 ¦ - ¦ ¦ 10 ¦ 31 ¦ 32 ¦ 36 ¦ 39 ¦ 44 ¦ 46 ¦ 49 ¦ 54 ¦ 58 ¦ 62 ¦ 67 ¦ - ¦ ¦ 16 ¦ 41 ¦ 43 ¦ 48 ¦ 53 ¦ 58 ¦ 61 ¦ 66 ¦ 73 ¦ 77 ¦ 84 ¦ 91 ¦ - ¦ ¦ 25 ¦ 53 ¦ 57 ¦ 63 ¦ 70 ¦ 73 ¦ 78 ¦ 83 ¦ 90 ¦ 97 ¦ 101 ¦ 108 ¦ 121 ¦ ¦ 35 ¦ ¦ ¦ ¦ 86 ¦ 90 ¦ 96 ¦ 103 ¦ 112 ¦ 120 ¦ 126 ¦ 135 ¦ 150 ¦ ¦ 50 ¦ - ¦ - ¦ - ¦ 104 ¦ 110 ¦ 117 ¦ 125 ¦ 136 ¦ 146 ¦ 154 ¦ 164 ¦ 184 ¦ ¦ 70 ¦ - ¦ - ¦ - ¦ 133 ¦ 140 ¦ 150 ¦ 160 ¦ 174 ¦ 187 ¦ 198 ¦ 211 ¦ 237 ¦ ¦ 95 ¦ - ¦ ¦ - ¦ 161 ¦ 170 ¦ 183 ¦ 195 ¦ 211 ¦ 227 ¦ 241 ¦ 257 ¦ 289 ¦ ¦ 120 ¦ - ¦ - ¦ - ¦ 186 ¦ 197 ¦ 212 ¦ 226 ¦ 245 ¦ 263 ¦ 280 ¦ 300 ¦ 337 ¦ ¦ 150 ¦ - ¦ - ¦ - ¦ - ¦ 226 ¦ 245 ¦ 261 ¦ 283 ¦ 304 ¦ 324 ¦ 346 ¦ 389 ¦ ¦ 185 ¦ - ¦ - ¦ - ¦ - ¦ 256 ¦ 280 ¦ 298 ¦ 323 ¦ 347 ¦ 371 ¦ 397 ¦ 447 ¦ ¦ 240 ¦ - ¦ - ¦ - ¦ - ¦ 300 ¦ 330 ¦ 352 ¦ 382 ¦ 409 ¦ 439 ¦ 470 ¦ 530 ¦ 비고 부속서 B 에 실은 적절한 허용전류의 표는 각 설치 방법에 대하여, 상기 허용전류를 적용할 수 있는 도체 사이즈 범위를 결정하는 데 참고해야 한다. 51 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
266273a9-6605-408b-a5a7-ca774bddd706 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 C.52.2 허용전류(A) ¦ 설치방법 ¦ 사이즈 mm2 ¦ 절연체의 종류와 부하 도체의 수 ¦ 절연체의 종류와 부하 도체의 수 ¦ 절연체의 종류와 부하 도체의 수 ¦ 절연체의 종류와 부하 도체의 수 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 설치방법 ¦ 사이즈 mm2 ¦ 2 PVC ¦ 3 PVC ¦ 2 XLPE ¦ 3 XLPE ¦ ¦ D1/D2 ¦ 구리 ¦ ¦ ¦ ¦ ¦ ¦ D1/D2 ¦ 1.5 ¦ 22 ¦ 18 ¦ 26 ¦ 22 ¦ ¦ D1/D2 ¦ 2.5 ¦ 29 ¦ 24 ¦ 34 ¦ 29 ¦ ¦ D1/D2 ¦ 4 ¦ 38 ¦ 31 ¦ 44 ¦ 37 ¦ ¦ D1/D2 ¦ 6 ¦ 47 ¦ 39 ¦ 56 ¦ 46 ¦ ¦ D1/D2 ¦ 10 ¦ 63 ¦ 52 ¦ 73 ¦ 61 ¦ ¦ D1/D2 ¦ 16 ¦ 81 ¦ 67 ¦ 95 ¦ 79 ¦ ¦ D1/D2 ¦ 25 ¦ 104 ¦ 86 ¦ 121 ¦ 101 ¦ ¦ D1/D2 ¦ 35 ¦ 125 ¦ 103 ¦ 146 ¦ 122 ¦ ¦ D1/D2 ¦ 50 ¦ 148 ¦ 122 ¦ 173 ¦ 144 ¦ ¦ D1/D2 ¦ 70 ¦ 183 ¦ 151 ¦ 213 ¦ 178 ¦ ¦ D1/D2 ¦ 95 ¦ 216 ¦ 179 ¦ 252 ¦ 211 ¦ ¦ D1/D2 ¦ 120 ¦ 246 ¦ 203 ¦ 287 ¦ 240 ¦ ¦ D1/D2 ¦ 150 ¦ 278 ¦ 230 ¦ 324 ¦ 271 ¦ ¦ D1/D2 ¦ 185 ¦ 312 ¦ 258 ¦ 363 ¦ 304 ¦ ¦ D1/D2 ¦ 240 ¦ 361 ¦ 297 ¦ 419 ¦ 351 ¦ ¦ D1/D2 ¦ 300 ¦ 408 ¦ 336 ¦ 474 ¦ 396 ¦ ¦ D1/D2 ¦ 알루미늄 ¦ ¦ ¦ ¦ ¦ ¦ D1/D2 ¦ 2.5 ¦ 22 ¦ 18.5 ¦ 26 ¦ 22 ¦ ¦ D1/D2 ¦ 4 ¦ 29 ¦ 24 ¦ 34 ¦ 29 ¦ ¦ D1/D2 ¦ 6 ¦ 36 ¦ 30 ¦ 42 ¦ 36 ¦ ¦ D1/D2 ¦ 10 ¦ 48 ¦ 40 ¦ 56 ¦ 47 ¦ ¦ D1/D2 ¦ 16 ¦ 62 ¦ 52 ¦ 73 ¦ 61 ¦ ¦ D1/D2 ¦ 25 ¦ 80 ¦ 66 ¦ 93 ¦ 78 ¦ ¦ D1/D2 ¦ 35 ¦ 96 ¦ 80 ¦ 112 ¦ 94 ¦ ¦ D1/D2 ¦ 50 ¦ 113 ¦ 94 ¦ 132 ¦ 112 ¦ ¦ D1/D2 ¦ 70 ¦ 140 ¦ 117 ¦ 163 ¦ 138 ¦ ¦ D1/D2 ¦ 95 ¦ 166 ¦ 138 ¦ 193 ¦ 164 ¦ ¦ D1/D2 ¦ 120 ¦ 189 ¦ 157 ¦ 220 ¦ 186 ¦ ¦ D1/D2 ¦ 150 ¦ 213 ¦ 178 ¦ 249 ¦ 210 ¦ ¦ D1/D2 ¦ 185 ¦ 240 ¦ 200 ¦ 279 ¦ 236 ¦ ¦ D1/D2 ¦ 240 ¦ 277 ¦ 230 ¦ 322 ¦ 272 ¦ ¦ D1/D2 ¦ 300 ¦ 313 ¦ 260 ¦ 364 ¦ 308 ¦ 52 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
2b3289cd-b0d8-4548-95f7-2f80a4fbaad5 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 C.52.3 복수회로 또는 복수의 다심케이블의 집합에 대한 저감 계수 (표 C.52.1 의 허용전류에 사용) ¦ 항 ¦ 배치 ¦ 회로 또는 다심케이블의 수 ¦ 회로 또는 다심케이블의 수 ¦ 회로 또는 다심케이블의 수 ¦ 회로 또는 다심케이블의 수 ¦ 회로 또는 다심케이블의 수 ¦ 회로 또는 다심케이블의 수 ¦ 회로 또는 다심케이블의 수 ¦ 회로 또는 다심케이블의 수 ¦ 회로 또는 다심케이블의 수 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 항 ¦ 배치 ¦ 1 ¦ 2 ¦ 3 ¦ 4 ¦ 6 ¦ 9 ¦ 12 ¦ 16 ¦ 20 ¦ ¦ 1 ¦ 기중이나 벽면에 묶음 설치, 매설 또는 수납 ¦ 1.00 ¦ 0.80 ¦ 0.70 ¦ 0.65 ¦ 0.55 ¦ 0.50 ¦ 0.45 ¦ 0.40 ¦ 0.40 ¦ ¦ 2 ¦ 벽, 바닥 또는 비천공 트레이 위로 단일층 ¦ 1.00 ¦ 0.85 ¦ 0.80 ¦ 0.75 ¦ 0.70 ¦ 0.70 ¦ - ¦ - ¦ - ¦ ¦ 3 ¦ 천장에 직접 고정한 단 일층 ¦ 0.95 ¦ 0.80 ¦ 0.70 ¦ 0.70 ¦ 0.65 ¦ 0.60 ¦ - ¦ - ¦ - ¦ ¦ 4 ¦ 천공형 수평 또는 수직 트레이 위로 단일층 ¦ 1.00 ¦ 0.90 ¦ 0.80 ¦ 0.75 ¦ 0.75 ¦ 0.70 ¦ - ¦ - ¦ - ¦ ¦ 5 ¦ 래더, 브래킷 또는 클 리트 등 위의 단일층 ¦ 1.00 ¦ 0.85 ¦ 0.80 ¦ 0.80 ¦ 0.80 ¦ 0.80 ¦ - ¦ - ¦ - ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 53 | {}
3e77a263-1715-4c41-a4a2-30cbfbad02e8 | KSCIEC60364-5-52_KR | KS CIEC 60364-5-52:2009 부속서 D (참고) 허용전류를 구하는 방식 표 B.52.2~ 표 B.52.13 에 제시된 값은 허용전류 대 도체 단면적 곡선상에 위치한다. 허용전류 대 도체 단면적 곡선은 다음 식으로부터 얻을 수 있다. I=axSm-bxS" 여기에서 I : 허용전류(A) S : 도체의 공칭 단면적(mm2)1) a, b : 케이블의 종류와 설치 방법에 따른 계수 m, n : 케이블의 종류와 설치 방법에 따른 지수 계수 값과 지수 값은 이 부속서에 표로 실었다. 허용전류는 20 A 를 넘지 않는 경우 0.5A 단위로, 20 A 를 넘는 경우 1A 단위로 반올림하여 표시한다. 유효 숫자의 개수가 허용전류의 정확도를 의미하는 것은 아니다. 실질적으로 모든 경우에 있어서 첫 번째 항만 적용하면 된다. 두 번째 항은 대형 단심케이블을 사용 하는 8 가지 경우에만 적용하면 된다. 표 B.52.2~표 B.52.13 에 제시된 범위를 벗어나는 도체에 대해서는 위 계수 및 지수 적용을 권장하 지 않는다. 1) 압출 성형 절연된 케이블의 경우, 공칭 단면적이 50 mm2 이면 47.5 mm2 를 적용해야 한다. 다른 모든 표준의 케이블과 모든 표준의 미네랄 절연 케이블의 경우, 공칭 값이 충분히 정확하다. 54 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
03edb9ec-e0bb-404b-9685-8496a64e9ac9 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 D.52.1 계수와 지수 표 ¦ 허용전류 표 ¦ 구분 ¦ 구리 도체 ¦ 구리 도체 ¦ 알루미늄 도체 ¦ 알루미늄 도체 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 허용전류 표 ¦ 구분 ¦ a ¦ m ¦ a ¦ m ¦ ¦ B.52.2 ¦ 2 ¦ 11.2 ¦ 0.611 8 ¦ 8.61 ¦ 0.616 ¦ ¦ B.52.2 ¦ 3(s ≤ 120 mm2) ¦ 10.8 ¦ 0.601 5 ¦ 8.361 ¦ 0.602 5 ¦ ¦ B.52.2 ¦ 3 (s > 120 mm2) ¦ 10.19 ¦ 0.611 8 ¦ 7.84 ¦ 0.616 ¦ ¦ B.52.2 ¦ 4 ¦ 13.5 ¦ 0.625 ¦ 10.51 ¦ 0.625 4 ¦ ¦ B.52.2 ¦ 5 ¦ 13.1 ¦ 0.600 ¦ 10.24 ¦ 0.599 4 ¦ ¦ B.52.2 ¦ 6 ≤ 16 mm2 ¦ 15.0 ¦ 0.625 ¦ 11.6 ¦ 0.625 ¦ ¦ B.52.2 ¦ 6 > 16 mm2 ¦ 15.0 ¦ 0.625 ¦ 10.55 ¦ 0.640 ¦ ¦ B.52.2 ¦ 7 ¦ 17.42 ¦ 0.540 ¦ 13.6 ¦ 0.540 ¦ ¦ B.52.3 ¦ 2 ¦ 14.9 ¦ 0.611 ¦ 11.6 ¦ 0.615 ¦ ¦ B.52.3 ¦ 3(s) ≤ 120 mm2 ¦ 14.46 ¦ 0.598 ¦ 11.26 ¦ 0.602 ¦ ¦ B.52.3 ¦ 3(s) > 120 mm2 ¦ 13.56 ¦ 0.611 ¦ 10.56 ¦ 0.615 ¦ ¦ B.52.3 ¦ 4 ¦ 17.76 ¦ 0.625 0 ¦ 13.95 ¦ 0.627 ¦ ¦ B.52.3 ¦ 5 ¦ 17.25 ¦ 0.600 ¦ 13.5 ¦ 0.603 ¦ ¦ B.52.3 ¦ 6 ≤ 16 mm2 ¦ 18.77 ¦ 0.628 ¦ 14.8 ¦ 0.625 ¦ ¦ B.52.3 ¦ 6 > 16 mm2 ¦ 17.0 ¦ 0.650 ¦ 12.6 ¦ 0.648 ¦ ¦ B.52.3 ¦ 7 ¦ 20.25 ¦ 0.542 ¦ 15.82 ¦ 0.541 ¦ ¦ B.52.4 ¦ 2 ¦ 10.4 ¦ 0.605 ¦ 7.94 ¦ 0.612 ¦ ¦ B.52.4 ¦ 3(s) ≤ 120 mm2 ¦ 10.1 ¦ 0.592 ¦ 7.712 ¦ 0.598 4 ¦ ¦ B.52.4 ¦ 3(s) > 120 mm2 ¦ 9.462 ¦ 0.605 ¦ 7.225 ¦ 0.612 ¦ ¦ B.52.4 ¦ 4 ¦ 11.84 ¦ 0.628 ¦ 9.265 ¦ 0.627 ¦ ¦ B.52.4 ¦ 5 ¦ 11.65 ¦ 0.600 5 ¦ 9.03 ¦ 0.601 ¦ ¦ B.52.4 ¦ 6 ≤ 16 mm2 ¦ 13.5 ¦ 0.625 ¦ 10.5 ¦ 0.625 ¦ ¦ B.52.4 ¦ 6 > 16 mm2 ¦ 12.4 ¦ 0.635 ¦ 9.536 ¦ 0.632 4 ¦ ¦ B.52.4 ¦ 7 ¦ 14.34 ¦ 0.542 ¦ 11.2 ¦ 0.542 ¦ ¦ B.52.5 ¦ 2 ¦ 13.34 ¦ 0.611 ¦ 10.9 ¦ 0.605 ¦ ¦ B.52.5 ¦ 3(s) ≤ 120 mm2 ¦ 12.95 ¦ 0.598 ¦ 10.58 ¦ 0.592 ¦ ¦ B.52.5 ¦ 3(s) > 120 mm2 ¦ 12.14 ¦ 0.611 ¦ 9.92 ¦ 0.605 ¦ ¦ B.52.5 ¦ 4 ¦ 15.62 ¦ 0.625 2 ¦ 12.3 ¦ 0.630 ¦ ¦ B.52.5 ¦ 5 ¦ 15.17 ¦ 0.60 ¦ 11.95 ¦ 0.605 ¦ ¦ B.52.5 ¦ 6 ≤ 16 mm2 ¦ 17.0 ¦ 0.623 ¦ 13.5 ¦ 0.625 ¦ ¦ B.52.5 ¦ 6 > 16 mm2 ¦ 15.4 ¦ 0.635 ¦ 11.5 ¦ 0.639 ¦ ¦ B.52.5 ¦ 7 ¦ 16.88 ¦ 0.539 ¦ 13.2 ¦ 0.539 ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 55 | {}
6f868f1f-346a-480a-81d9-d5aa9632dc97 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 D.52.1 계수와 지수 표(계속) ¦ 허용전류 표 ¦ 구분 ¦ 계수와 지수 ¦ 계수와 지수 ¦ 계수와 지수 ¦ 계수와 지수 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 허용전류 표 ¦ 구분 ¦ a ¦ m ¦ b ¦ n ¦ ¦ B.52.6 ¦ 500 V 2 3 4 750 V 2 3 4 ¦ 18.5 14.9 16.8 19.6 16.24 ¦ 0.56 0.612 0.59 0.596 0.599 5 ¦ - - ¦ - - ¦ ¦ ¦ 500 V 2 3 4 ¦ 18.0 22.0 19.0 21.2 ¦ 0.59 0.60 0.60 ¦ ¦ ¦ ¦ ¦ 750 V 2 3 ¦ 24.0 20.3 ¦ 0.58 0.60 0.60 ¦ ¦ ¦ ¦ ¦ 4 ¦ ¦ 0.579 4 ¦ ¦ ¦ ¦ ¦ 500 V 2 4 5 6 ¦ 20.2 ¦ ¦ ¦ ¦ ¦ B.52.7 비고 b 는 계수이고, n 은 지수이다. ¦ 3 ¦ 23.88 19.5 16.5 18.0 23.0 ¦ 0.58 0.58 0.59 0.58 0.58 ¦ - - ¦ ¦ a, m, 56 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
538f016f-a360-49ad-9760-c93dd362bab3 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 D.52.1 계수와 지수 표(계속) ¦ 허용전류 표 ¦ 구분 ¦ 구리 도체 ¦ 구리 도체 ¦ 알루미늄 도체 ¦ 알루미늄 도체 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 허용전류 표 ¦ 구분 ¦ a ¦ m ¦ a ¦ m ¦ ¦ B.52.8 ¦ 750 V 2 3 4 5 ≤ 120 mm2 5 > 120 mm2 6 ≤ 120 mm2 6 > 120 mm2 500 V 2 ¦ 20.6 17.4 20.15 22.0 22.0 25.17 25.17 ¦ 0.60 0.60 0.584 5 0.58 0.58 0.578 5 0.578 5 ¦ - - 1 x 10~11 - 1.9 x 10-11 ¦ - - 5.25 - 5.15 ¦ ¦ B.52.9 ¦ 3 4 5 6 750 V 2 3 4 5 ≤ 120 mm2 5 > 120 mm2 6 ≤ 120 mm2 6 > 120 mm2 ¦ 24.2 20.5 23.0 26.1 29.0 26.04 21.8 25.0 27.55 27.55 31.58 31.58 ¦ 0.58 0.58 0.57 0.549 0.57 0.599 7 0.60 0.585 0.579 2 0.579 2 0.579 1 0.579 1 ¦ - - - - 1.3 x 10~10 - 1.8 ¦ - - - - - - 4.8 - 3.55 ¦ ¦ ¦ ¦ 14.30 12.9 17.1 ¦ 0.62 ¦ x 10-7 ¦ ¦ ¦ ¦ 2 > 16 mm2 3 ≤ 16 mm2 ¦ 16.8 14.9 ¦ 0.646 0.64 0.632 ¦ - ¦ ¦ ¦ ¦ 2 ≤ 16 mm2 3 > 16 mm2 4 ¦ ¦ 0.62 ¦ - - - ¦ - - - 2.14 - 2.01 ¦ ¦ B.52.10 B.52.11 (알루미늄 도체) ¦ 5 ≤ 300 mm2 5 > 300 mm2 6 ≤ 300 mm2 6 > 300 mm2 7 8 2 ≤ 16 mm2 2 > 16 mm2 3 ≤ 16 mm2 3 > 16 mm2 4 5 6 7 8 ¦ 13.28 13.28 13.75 13.75 18.75 15.8 12.8 11.4 11.0 9.9 12.0 9.9 10.2 13.9 11.5 ¦ 0.656 4 0.656 4 0.658 1 0.658 1 0.637 0.654 0.627 0.64 0.62 0.64 0.653 0.663 0.666 0.647 0.668 ¦ 6 x 10-5 1.2 x 10~4 - - - - - - - ¦ - - - - - - - ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 57 | {}
f94fd939-1303-490d-b73d-41cd3b2513d5 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 표 D.52.1 계수와 지수 표(계속) ¦ 허용전류 표 ¦ 구분 ¦ 구리 도체 ¦ 구리 도체 ¦ 알루미늄 도체 ¦ 알루미늄 도체 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 허용전류 표 ¦ 구분 ¦ a ¦ m ¦ a ¦ m ¦ ¦ B.52.12 ¦ 2 ≤ 16 mm2 2 > 16 mm2 3 ≤ 16 mm2 3 > 16 mm2 4 5 ≤ 300 mm2 5 > 300 mm2 6 ≤ 300 mm2 6 > 300 mm2 7 ¦ 20.5 18.6 17.8 16.4 20.8 16.0 16.0 16.57 16.57 22.9 19.1 ¦ 0.623 0.646 0.623 0.637 0.636 0.663 3 0.663 3 0.665 0.665 0.644 ¦ - - 6 x 10-4 3 x 10-4 ¦ - - - 1,793 - 1.876 ¦ ¦ ¦ 8 2 ≤ 16 mm2 2 > 16 mm2 3 ≤ 16 mm2 ¦ 16.0 13.4 13.7 12.6 ¦ 0.662 0.625 0.649 0.623 ¦ - - ¦ - - ¦ ¦ B.52.13 (알루미늄 도체) ¦ 3 > 16 mm2 4 5 6 7 8 ¦ 14.7 11.9 12.3 16.5 13.8 ¦ 0.635 0.654 0.671 0.673 0.659 0.676 ¦ - - ¦ - - - - - ¦ 58 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
814e2b59-c1a1-438e-9eef-696c30a7ef25 | KSCIEC60364-5-52_KR | KS CIEC 60364-5-52:2009 부속서 E (규정) 고조파 전류가 평형 3 상 계통에 미치는 영향 E.52.1 4 심에 전류가 흐르는 4 심 및 5 심 케이블에서 고조파 전류에 대한 저감 계수 523.6.3 에 의하면, 중성 도체에 부하 감소 없이 전류가 흐르는 경우 회로의 허용전류 결정 시 그 중 성 도체에 흐르는 전류를 고려해야 한다. 이 부속서에서는 3 상 평형 배선의 중성점에 전류가 흐르는 경우를 다룬다. 중성 전류가 흐르는 것은 중성 도체에서 상쇄되지 않는 고조파 성분을 가지는 선전류 때문이다. 중성 전류에서 상쇄되지 않는 가장 중요한 고조파 성분은 보통 제 3 고조파 성분이다. 제 3 고조파 성분에 의한 중성 전류의 크기는 상용주파수 선전류의 크기보다 클 수도 있다. 그런 경우, 중성 전류는 회로 내 케이블의 허용전류에 상당한 영향을 미치게 된다. 이 부속서에 실린 저감 계수는 3 상 평형 회로에 적용된다. 3 상 중 2 상에만 부하가 걸린 경우, 부담 이 더 커지게 된다. 이 경우 중성 도체에는 불평형 전류와 더불어 고조파 전류가 흐르게 되며, 이로 인해 중성 도체에 과부하가 걸릴 수 있다. 형광등 뱅크나 컴퓨터 등의 직류 전원 등은 상당한 고조파 전류를 발생시킬 수 있는 장치이다. 고조 파 간섭에 관한 보다 상세한 내용은 IEC 61000 시리즈를 참조한다. 표 E.52.1 에 제시된 저감 계수는 4 심 또는 5 심 케이블의 중성 도체로서 선로도체와 재질 및 단면적 이 동일한 경우에만 적용된다. 저감 계수는 제 3 고조파 전류를 기준으로 계산한 것이다. 제 9 고조파, 제 12 고조파 등의 상위 고조파 성분이 유효(15% 이상)한 경우, 더 낮은 저감 계수가 적용될 것으로 예상된다. 상 사이에 50 % 이상의 불평형이 있는 경우, 더 낮은 저감 계수가 적용될 수도 있다. 표로 나타낸 저감 계수를 이용하여 3 개의 부하 도체를 갖는 케이블의 허용전류에 적용했을 때, 네 번째 도체의 전류가 고조파 성분에 의한 것인 경우에 4 개 부하 도체를 가진 케이블의 허용전류를 구 할 수 있다. 저감 계수는 선로도체의 고조파 전류에 의한 가열 효과 도 고려한 것이다. 중성 전류가 선전류보다 높을 것으로 예상되는 경우, 중성 전류를 고려하여 케이블의 표준을 정해야 한다. 선전류보다 크게 높지 않은 중성 전류에 근거하여 케이블 표준을 선정하는 경우, 표에 실린 3 개 부 하 도체의 허용전류를 낮출 필요가 있다. 중성 전류가 선전류의 135 %를 넘고 중성 전류를 고려하여 케이블의 표준을 정한 경우, 3 개의 선로 도체는 완전히 부하가 걸리지는 않는다. 선로도체에서 발생하는 열의 감소가 중성 도체에서 발생하 는 열을 상쇄하므로, 3 개의 부하 도체의 허용전류에 저감 계수를 적용하지 않아도 된다. 59 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
df9b54d0-b0fd-4c02-8218-4fadb2e57cb1 | KSCIEC60364-5-52_KR | KS CIEC 60364-5-52:2009 표 E.52.1 4 심 및 5 심 케이블 고조파 전류의 저감 계수 ¦ 선전류의 제 3 고조파 성분 % ¦ 저감 계수 ¦ 저감 계수 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 선전류의 제 3 고조파 성분 % ¦ 선전류를 고려한 표준 결정 ¦ 중성 전류를 고려한 표준 결정 ¦ ¦ 0~15 ¦ 1.0 ¦ ¦ ¦ 15~33 ¦ 0.86 ¦ - ¦ ¦ 33~45 ¦ ¦ 0.86 ¦ ¦ >45 ¦ ¦ 1.0 ¦ ¦ 비고 선전류의 제 3 고조파 성분은 기본파(제 1 고조파)에 대한 제 3 고조파 의 비율이다. ¦ 비고 선전류의 제 3 고조파 성분은 기본파(제 1 고조파)에 대한 제 3 고조파 의 비율이다. ¦ 비고 선전류의 제 3 고조파 성분은 기본파(제 1 고조파)에 대한 제 3 고조파 의 비율이다. ¦ E.52.2 고조파 전류에 대한 저감 계수의 적용 예 39A 의 부하가 걸리도록 설계된 3 상 회로를 4 심 PVC 절연 케이블을 써서 설치방법 C 에 따라 벽에 설치한다고 가정한다. 표 B.52.4 에서 6mm2 구리선 케이블의 허용전류는 41 A 이므로, 회로에 고조파 성분이 없다면 이 케 이블로 충분하다. 제 3 고조파 성분이 20% 존재한다면, 저감 계수 0.86 이 적용되므로 설계 부하는 39 =45 A 0.86 따라서 10 mm2 케이블이 필요하다. 제 3 고조파 성분이 40 %라면, 케이블 표준은 중성 전류에 근거하여 선정된다. 이 중성 전류는 39 x 0.4x3=46.8 A 이고, 환산 계수 0.86 이 적용되므로 설계 부하는 46.8 = 54.4A 0.86 따라서 10 mm2 케이블이 적합하다. 제 3 고조파 성분이 50 %라면 케이블 표준은 중성 전류에 근거하여 선정되는데, 이 중성 전류는 39 x 0.5 x3=58.5 A 이고, 환산 계수 1 이 적용되므로 16 mm2 케이블이 요구된다. 이상의 케이블 표준은 모두 케이블의 허용전류를 기준으로 결정한 것이며, 전압강하나 그 밖의 설계 관련 사항은 고려하지 않은 것이다. 60 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
b85dfd96-f651-4ec3-b141-3122a3ac9c12 | KSCIEC60364-5-52_KR | KS CIEC 60364-5-52:2009 부속서 F (참고) 전선관 선정 전선관 선정을 위한 참고 사항을 표 F.52.1 에 나타냈다. 표 F.52.1 - 권장 전선관 특성(KS C IEC 61386 에 따른 분류) ¦ 시설 상황 ¦ 시설 상황 ¦ 시설 상황 ¦ 압축에 저항 ¦ 충격에 저항 ¦ 최소 사용 온도 ¦ 최대 사용 온도 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 옥외 설치 ¦ 노출 설치 ¦ 노출 설치 ¦ 3 ¦ 3 ¦ 2 ¦ 1 ¦ ¦ 옥내 사용 ¦ 노출 설치 ¦ 노출 설치 ¦ 2 ¦ 2 ¦ 2 ¦ 1 ¦ ¦ 옥내 사용 ¦ 바닥 밑에 설치(floor screed) ¦ 바닥 밑에 설치(floor screed) ¦ 2 ¦ 3 ¦ 2 ¦ 1 ¦ ¦ 옥내 사용 ¦ 매설 ¦ 콘크리트 ¦ 3 ¦ 3 ¦ 2 ¦ 1 ¦ ¦ 옥내 사용 ¦ 매설 ¦ 빈 벽/벽면(불연성 재질) ¦ 2 ¦ 2 ¦ 2 ¦ 1 ¦ ¦ 옥내 사용 ¦ 매설 ¦ 석재 ¦ 2 ¦ 2 ¦ 2 ¦ 1 ¦ ¦ 옥내 사용 ¦ 매설 ¦ 건물의 빈 곳 ¦ 2 ¦ 2 ¦ 2 ¦ 1 ¦ ¦ 옥내 사용 ¦ 매설 ¦ 천장의 빈 곳 ¦ 2 ¦ 2 ¦ 2 ¦ 1 ¦ ¦ 옥내 사용 ¦ 가공(overhead mounting) ¦ 가공(overhead mounting) ¦ 4 ¦ 3 ¦ 3 ¦ 1 ¦ 비고 1 위의 값은 KS C IEC 61386 에 규정한 전선관의 특성에 대한 하나의 견본일 뿐이다. 비고 2 자소성에 따라 주황색의 전선관 시스템은 콘크리트 매설일 경우에만 허용된다. 다른 설치 방법에 대해서는 노랑, 주황, 빨강을 제외하고 모든 색상이 허용된다. 61 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
abf4d097-6f70-4d19-b651-0c96e76e97c8 | KSCIEC60364-5-52_KR | KS CIEC 60364-5-52:2009 부속서 G (참고) 수용가설비에서의 전압강하 전압강하의 최댓값 설비 인입구와 부하점 사이의 전압강하는 설비의 공칭 전압에 대하여 나타낸 표 G.52.1 의 값을 초과 해서는 안 된다. 표 G.52.1 전압강하 ¦ 설치 유형 ¦ 조명 % ¦ 기타 용도 % ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ A- 공공 저압 배전설비에서 직접 공급받는 저압 설비 ¦ 3 ¦ 5 ¦ ¦ B- 수용가 공급설비에서 공급받는 저압 설비 a ¦ 6 ¦ 8 ¦ ¦ a 가능한 한 최종 회로 내 전압강하가 설치 유형 A 에 나타낸 값을 넘지 않도록 하 는 것이 바람직하다. 시설의 주 배선설비가 100 보다 길 경우, 이러한 전압강하가 100 m 를 넘는 배선 의 미터당 0.005 % 증가할 수 있지만, 이러한 증가분은 0.5 %를 넘지 않는다. 전압강하는 해당되는 여러 가지 계수(diversity factor)를 적용하고 전기사용기기의 수요로부터 결정되거나, 회로의 설계 전류 값으로부터 결정된다. ¦ a 가능한 한 최종 회로 내 전압강하가 설치 유형 A 에 나타낸 값을 넘지 않도록 하 는 것이 바람직하다. 시설의 주 배선설비가 100 보다 길 경우, 이러한 전압강하가 100 m 를 넘는 배선 의 미터당 0.005 % 증가할 수 있지만, 이러한 증가분은 0.5 %를 넘지 않는다. 전압강하는 해당되는 여러 가지 계수(diversity factor)를 적용하고 전기사용기기의 수요로부터 결정되거나, 회로의 설계 전류 값으로부터 결정된다. ¦ a 가능한 한 최종 회로 내 전압강하가 설치 유형 A 에 나타낸 값을 넘지 않도록 하 는 것이 바람직하다. 시설의 주 배선설비가 100 보다 길 경우, 이러한 전압강하가 100 m 를 넘는 배선 의 미터당 0.005 % 증가할 수 있지만, 이러한 증가분은 0.5 %를 넘지 않는다. 전압강하는 해당되는 여러 가지 계수(diversity factor)를 적용하고 전기사용기기의 수요로부터 결정되거나, 회로의 설계 전류 값으로부터 결정된다. ¦ 비고 1 다음과 같은 경우, 더 큰 전압강하를 수용할 수 있다. 시동 시간 중의 전동기에 대해서 돌입전류가 높은 기타 기기에 대해서 두 가지 경우 모두에서 전압 변동이 관련 기기 표준에서 정한 기준 값 범위에 머물 경우에 한한다. 비고 2 다음의 일시적인 조건은 배제된다. 과도전압 비정상 사용으로 인한 전압 변동 전압강하는 다음 식을 써서 정할 수 있다. u=b( P1 100000 여기에서 u : 전압강하(V) b : 3 상 회로에 대한 1, 단상 회로에 대한 2 와 동등한 계수 비고 3 중성으로 완전히 불평형인 3 상 회로(단상 부하)는 단상 회로로 간주한다. PI : 통상적인 사용에서 도체의 저항률로, 통상적인 사용 중 온도에서 저항률과 동등한 것 으로 본다. 예를 들면 20 °C 의 저항률의 1.25 배 또는 구리에 대해서는 0.022 5 �mm2/m, 알루미늄에 대해서는 0.036 �mm2/m 62 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
74f5ac8a-009c-4471-a590-dd14ef3194ae | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 ¦ L ¦ : 배선설비의 직선 길이(m) ¦ ¦ --- ¦ --- ¦ ¦ s ¦ : 도체의 단면적(mm2) ¦ ¦ cos⌀ ¦ : 역률. 정확한 사항을 알고 있지 못한 경우, 역률은 0.8 로 본다(sin⌀ = 0.6). ¦ ¦ 2 ¦ : 도체의 단위길이당 리액턴스이며, 다른 자세한 사항을 알고 있지 못한 경우, 0.08 m�/m 로 본다. ¦ ¦ IB ¦ : 설계 전류(A) 관련 전압강하(%) △u = 100 iU。 ¦ ¦ Uo ¦ : 전선과 중성 간 전압(V) ¦ 비고 4 특별저전압 회로에서는 조명 외 용도에 대해서(예를 들면 벨, 제어기, 현관문 개폐장치 등) 해당 기기가 정확하게 작동되는 것을 확인했다면 표 G.1 의 전압강하 제한을 지킬 필요는 없다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 63 | {}
7be9bb88-53d2-4b7c-8696-359fbccfe770 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 부속서 H (참고) 병렬 케이블 배치 예 523.7 에서 말하는 특수한 배치의 예는 다음과 같다. a) 4 개의 3 심 케이블을 위한 연결 계획: L1L2L 3, L1L2L3, L1L2L3, L1L2L3 케이블은 서로 접촉될 수 있다. b) 6 개의 단심 케이블 1) 수평. 그림 H.52.1 참조 2) 케이블 서로 간의 상위 배치. 그림 H.52.2 참조 3) 삼각배치. 그림 H.52.3 참조 c) 9 개의 단심 케이블 1) 수평. 그림 H.52.4 참조 2) 케이블 서로 간의 상위 배치. 그림 H.52.5 참조 3) 삼각배치. 그림 H.52.6 참조 d) 12 개의 단심 케이블 1) 수평. 그림 H.52.7 참조 2) 케이블 서로 간의 상위 배치. 그림 H.52.8 참조 3) 삼각배치. 그림 H.52.9 참조 그림에서 표시한 거리는 유지해야 한다. 비고 가능한 경우, 특수 배치에서 상(phase) 간의 임피던스 차이 또한 제한한다. N 1 L L2 L 3 L 3 L2 L N2 그림 H.52.1 6 병렬 단심케이블의 특수 배치 - 수평(523.7 참조) N 1 L 1 L2 L3 N2 L3 �2 L 1 그림 H.52.2 6 병렬 단심케이블의 특수 배치 -케이블 서로 간의 상위에 배치(523.7 참조) 64 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
0abbe1d8-65fe-4535-a43b-9a3072429fae | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 L3 L3 N1 L1 L2 L2 L1 N2 그림 H.52.3 6 병렬 단심케이블의 특수 배치 - 삼각배 치(523.7 참조) ![image](/image/placeholder) ≥ 2De ≥ 2De L 1 L2 L3 N L3 L2 L1 2 1 L2 L3 비고 De 는 케이블의 바깥지름이다. 그림 H.52.4 9 병렬 단심케이블의 특수 배치 - 수평(523.7 참조) ![image](/image/placeholder) L 1 L2 L3 N1 ≥ 300 mm L3 L2 L1 N2 ≥ 300 mm L1 L2 L3 N3 그림 H.52.5 9 병렬 단심케이블의 특수 배치 -케이블 서로 간의 상위에 배치(523.7 참조) ![image](/image/placeholder) > 2De ≥ 2De L3 L3 L3 L1 �2 N1 L 1 �2 N2 L L2 N3 De 1 비고 De 는 케이블의 바깥지름이다. 그림 H.52.6 9 병렬 단심케이블의 특수 배치 - 삼각배 치(523.7 참조) 65 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
959d6b23-72b4-4ac7-8346-8f4f1df9048f | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 N1 L1 L2 L3 L3 L1 L2 N2 N3 L1 L2 L3 L3 L1 L2 N 2 그림 H.52.7 12 병렬 단심케이블의 특수 배치 -수평(523.7 참조) ![image](/image/placeholder) N1 L1 L2 L3 L3 L2 L1 N2 ≥ 300 mm N3 L1 L2 L3 L3 L2 L1 N 그림 H.52.8 12 병렬 단심케이블의 특수 배치 -케이블 서로간의 상위에 배치(523.7 참조) L3 L3 L3 L3 N1 L1 L2 L2 L1 N2 N3 L1 L2 L2 L1 N 4 그림 H.52.9 12 병렬 단심케이블의 특수 배치 - 삼각배 치(523.7 참조) 66 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
15cd09f6-3a9c-4f55-b91b-6d70823abac0 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 부속서 I (참고) 특정 국가에 해당되는 사항 ¦ 국가 ¦ 절 ¦ 성격(IEC 지침에 따라 영구적 또는 영구성이 덜함) ¦ 근거 (요청 국가의 상세한 근거 설명) ¦ 내용 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 독일 ¦ 521.6 ¦ ¦ ¦ 독일과 네덜란드는 전선관, 케이블트렁킹, 케이블 덕트의 기본 절연전선의 경우에 주회로와 결합된 보조 회로를 포함한 하나의 주회로 도체만이 다 중 채널 트렁킹의 단일 덕트 또는 단일 채널 트 렁킹 또는 전선관 내에 설치될 수 있다. 밀폐 전 기 사용 구역(electrical and enclosed operating areas)은 제외한다. 그러나 복수의 회로로 이루 어진 재단하지 않은 도체(uncut conductor)는 공 통의 스루런 박스(through-run box)를 통해 공급 될 수 있다. ¦ ¦ 독일 ¦ 522 절 ¦ ¦ ¦ 독일은 케이블 터널, 케이블덕트 및 기타 설치 케이블의 밀도가 증가하는 장소에서 열 방출과 연기를 감지하는 화재 감지기 설치를 요구한다. 대규모 배선설비에서는 이동식 소화기를 사용할 수 있어야 한다. 접촉하기 어려운 대규모 배선설비의 경우, 고정 형 소화기 설비 사용을 권한다. 케이블 터널에서는 100 m 마다 내화 구획 역할을 하는 격벽을 설치해야 하고 모든 케이블 통로 (breaking through)는 승인을 받은 적절한 소방 조치로 밀폐해야 한다. 접촉할 수 있는 케이블 터널과 덕트는 소방 활 동을 위한 접촉 수단을 확보할 수 있는 충분한 수의 조치를 갖추어 설치해야 한다. 예를 들면 덮개는 이동이 쉽게 하는 등이다. 또한 연기 제 거 장비를 갖추어야 한다. 자동 폐쇄 기능 및 내화 기능을 갖는 방화 밀폐 체가 적용되는 경우, 그러한 밀폐체는 화재 위험 시에 즉각 활성화되어야 한다. ¦ ¦ 독일 ¦ 522.4.1 ¦ ¦ ¦ 독일에서는 내부가 빈 벽 설치에서는 보호등급 이 IP30 이상인 박스 및 외함을 사용해야 한다. ¦ ¦ 독일 ¦ 522.8.9 ¦ ¦ ¦ 독일에서는 내부가 빈 벽 설치에서는 케이블을 수납하는 장치를 갖춘 박스 및 외함을 사용해야 한다. ¦ ¦ 독일 ¦ 523.3 ¦ ¦ ¦ 독일에서는 24 시간 부하도(24 h load diagram) 또 한 고려해야 한다. ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 67 | {}
4097beb2-bcd4-4361-b4c5-3088e84f2cd4 | KSCIEC60364-5-52_KR | KS CIEC 60364-5-52:2009 ¦ 국가 ¦ 절 ¦ 성격(IEC 지침에 따라 영구적 또는 영구성이 덜함) ¦ 근거 (요청 국가의 상세한 근거 설명) ¦ 내용 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 독일 ¦ 527 절 ¦ ¦ ¦ 독일에서는 일부 구역에 대한 특정 소방 보호 요건이 있다. ¦ ¦ 독일 ¦ 527.2.5 ¦ ¦ ¦ 독일에서는 케이블 환기구에 대한 밀폐체는 독 일건축공학협회(DIBT)의 승인을 받아야 한다. ¦ ¦ 네덜란드 ¦ 521.6 ¦ ¦ ¦ 네덜란드는 전선관, 케이블트렁킹, 케이블덕트의 기본 절연전선의 경우에 주회로와 결합된 보조 회로를 포함한 하나의 주회로 도체만이 다중 채 널 트렁킹의 단일 덕트 또는 단일 채널 트렁킹 또는 전선관 내에 설치될 수 있다. 밀폐 전기 작동 구역은 제외한다. 그러나 복수의 회로로 이루어진 재단하지 않은 도체는 공통의 스루런 박스를 통해 공급될 수 있다. ¦ ¦ 네덜란드 ¦ 521.7 ¦ ¦ ¦ 비고 네덜란드에서는 하나의 케이블에 복수의 회로를 두는 것을 허용하지 않는다. 다만, 다음은 예외로 한다. a) 측정 및 신호 기기 접속 b) 보조 회로 c) 주회로와 그 보조 회로의 접속을 끊은 이 후에는 주회로와 보조 회로에 동력이 공 급될 수 없는 경우의 주회로와 보조 회로 d) 프로세싱 설비나 대규모 교통 수송 설 비 등과 같은 매우 규모가 큰 설비. 이러한 경우, 실질적으로 이 요건에 적합할 수 없다. ¦ ¦ 아일랜드 ¦ 522.6.2 ¦ ¦ ¦ 아일랜드에서는 은폐 배선은 고정 장치나 드릴 이 침투하여 손상을 입지 않도록 도기 금속 외 함이나 일체형 스크린으로 보호해야 한다. 다만, 다음의 구역에서는 예외로 한다. : 구석에서 수 평으로 150 mm. 천장에서 수직으로 150 mm. 한 지점에 대해 수직 또는 수평으로 일직선 포 설. 부속물 또는 개폐장치. 이들 경우의 배선은 벽의 배면으로부터 50 mm 이상 떨어져야 한다. ¦ ¦ 덴마크 ¦ 521.8.1 ¦ ¦ ¦ 덴마크에서는 이 요건을 준수하지 않는다. ¦ ¦ 덴마크 ¦ 521.8.2 ¦ ¦ ¦ 덴마크에서는 이 요건을 준수하지 않는다. ¦ ¦ 덴마크 ¦ 522.8.10 ¦ ¦ ¦ 덴마크에서는 다음이 적용된다. : 이 요건은 정 격 전압이 교류 50V, 직류 120 V 이하인 케이 블에는 요구되지 않는다. 케이블을 지중 매설하 는 깊이는 0.35 m 이상이다. 지중 매설 깊이가 0.7m 미만인 케이블은 전선관, U 자형 또는 시 트로 보호해야 한다. 지중 매설 깊이가 0.7 m 를 넘는 케이블은 케이블 위 약 0.2m 에 표시 밴드 를 설치한 경우 기계적 보호 조치를 추가하지 않는다. ¦ 68 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
75dae559-6316-4b75-a461-1c2422c4d674 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 ¦ 국가 ¦ 절 ¦ 성격(IEC 지침에 따라 영구적 또는 영구성이 덜함) ¦ 근거 (요청 국가의 상세한 근거 설명) ¦ 내용 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 덴마크 (계속) ¦ 522.8.10 (계속) ¦ ¦ ¦ 외부 케이블 사이에 0.2m 미만인 케이블이 다수 있는 경우, 표시 밴드는 하나만 요구된다. 지중에 서 기중으로 나오는 케이블은 지상뿐 아니라 지 중도 기계적 보호조치가 되어 있어야 한다. 비고 보호용 물질로 작업 압력 0.6 MPa 에 대한 DS DS/EN 12201 : Parts 1~5 에 따르는 아연 도금한 철, 강철 또는 플라스틱 전 선관 또는 전선관을 사용할 수 있다. ¦ ¦ 덴마크 (계속) ¦ 527.1.3 ¦ ¦ ¦ 덴마크에서는 KS C IEC 60332-1-1 및 KS C IEC 60332-1-2 에 적합한 케이블뿐 아니라 DS 2393 에 적합한 케이블도 인정된다. ¦ ¦ 덴마크 (계속) ¦ 528.1 ¦ ¦ ¦ 덴마크에서는 다음 요건이 적용된다. : 저압 설 비에 접속되지 않고 숙련된 전문가가 설치, 감 독, 보수하지 않는 설비는 해당 저압 설비를 해 체하지 않고 작업이 가능할 수 있도록 저압 설 비로부터 독립적으로 설치해야 한다. ¦ ¦ 덴마크 (계속) ¦ 표 C.52.3 ¦ ¦ ¦ 덴마크에서는 다음이 적용된다. : 그룹 내 회로 의 전류가 주위온도에 대한 보정계수를 곱하고 표 C.52.3 에 따른 허용전류의 75% 이하인 경 우, 다음이 허용된다. · 회로의 허용전류는 그룹에 대한 저감 계수를 곱할 필요가 없다. 저감 계수를 결정하기 위해 회로 수를 셀 때 해당 회로는 다른 회로와 함께 세지 않는다. 그룹의 모든 회로의 전류가 표 C.52.3 에 따른 허 용전류의 75 %를 초과 할 경우 주위온도에 대한 보정계수를 곱하고 더 이상의 보정이 필요하지 않다. ¦ ¦ 미국 ¦ 523 절 ¦ ¦ ¦ 미국에서는 도체에 대한 허용전류 결정은 NFPA 70-National Electrical Code 에 따른다. ¦ ¦ 영국 ¦ 522.6.4 ¦ ¦ ¦ 영국에서는 다음 추가적인 요건이 적용된다. 1. 바닥 밑이나 천장 위에 설치되는 케이블은 바닥이나 천상 또는 그 고정 장치와 접촉하 여 손상을 입지 않는 위치로 포설되어야 한 다. 바닥이나 천장 구조물의 결합부를 통과 하거나 천장 지지 구조물을 통과 하는 케이블 (예를 들면 마룻장 아래)은 다음의 어느 하나 를 따라야 한다. (i) 널빤지나 결합부의 상단 또는 바닥으로부터 수직으로 50 mm 이상 떨어져야 한다. ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 69 | {}
96b3c71c-d852-4dd8-8c74-609de4870546 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 ¦ 국가 ¦ 절 ¦ 성격(IEC 지침에 따라 영구적 또는 영구성이 덜함) ¦ 근거 (요청 국가의 상세한 근거 설명) ¦ 내용 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 영국 ¦ 522.6.4 (계속) ¦ ¦ ¦ (ii) 제 5-54 부 관련 회로의 보호도체에 대한 요 건에 적합한 도기 금속 덮개를 써야 한다. 케이블은 BS 5467, BS 6346, BS 6724, BS 7846, BS EN 60702-1 또는 BS 8436 에 적합 해야 한다. (iii) BS EN 61386 에 적합하고 제 5-54 부 보호도체 요건을 충족하는 도기 전선관에 시설한다. (iv) BS EN 50085 에 적합하고 제 5-54 부 보호도 체 요건을 충족하는 도기 트렁킹 또는 덕트 에 시설한다. (V) 못, 나사 등이 케이블에 침투하지 않도록 충 분한 기계적인 보호조치가 되어 있어야 한다. 2. 벽이나 격벽 표면에서 매설 깊이 50 mm 미 만으로 매설된 케이블은 다음 중 어느 하나 를 따라야 한다. (i) 제 5-54 부 관련 회로의 보호도체 요건에 적합 한 도기 금속 덮개를 사용한다. 케이블은 BS 5467, BS 6346, BS 6724, BS 7846, BS EN 60702-1 또는 BS 8436 을 준수한다. (ii) BS EN 61386 및 제 5-54 부 보호도체 요건에 적합한 도기 전선관에 시설한다. (iii) BS EN 50085 에 적합하고 제 5-54 부 보호도체 요건을 충족하는 도기 트렁킹 또는 덕트에 시설한다. (iv) 못, 나사 등이 케이블에 침투하지 못하도록 기계적으로 충분한 보호 조치를 취한다. (V) 두 벽이나 격벽이 접하여 형성되는 각에서 150 mm 이내 또는 벽이나 격벽의 상단으로 부터 150 mm 이내에 설치한다. 케이블이 벽 이나 격벽의 일정 지점, 부속물 또는 개폐장 치에 접속되는 경우, 케이블을 해당 지점 부 속물 또는 개폐장치에 대해 수평 또는 수직 으로 설치할 수 있다. 부속물이나 지점, 개 폐장치의 위치를 배면으로부터 정할 수 있 는 경우, 두께 100 mm 이하 벽 또는 두께 100 mm 이하의 격벽의 한 면에 형성된 구 역이 배면까지 확장된다. ¦ 70 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
a2e5f173-53ec-4969-94ee-b89eaa50814b | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 ¦ 국가 ¦ 절 ¦ 성격(IEC 지침에 따라 영구적 또는 영구성이 덜함) ¦ 근거 (요청 국가의 상세한 근거 설명) ¦ 내용 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 영국 ¦ 522.6.4 (계속) ¦ ¦ ¦ 3. 상기 요건 2 가 적용되는 경우에, 숙련된 전문가 또는 제대로 교육받은 사람이 설치를 감독하게 되어 있지 않을 때는 상기 요건 2(v)에 따라 설 치되지만 상기 2 (i) (ii) (iii) (iv)에는 적합하지 않 은 케이블은 제 4-41 부의 415.1 에서 규정된 특 성을 갖는 RCD 수단에 의해 보호 조치를 추가 해야 한다. 벽이나 격벽 표면으로부터의 케이블 깊이와 상관없이 숙련된 전문가 또는 제대로 교육받 은 사람이 설치를 감독하지 않는 경우, 벽이 나 격벽에 매입되는 케이블의 내부 구조물에 못, 나사 등과 같은 고정 장치 이외의 금속 부분을 포함하는 케이블은 다음 어느 하나에 부합해야 한다. (i) 제 5-54 부 관련 회로의 보호도체 요건에 적 합한 도기 금속 덮개를 사용하며, 케이블은 BS 5467, BS 6346, BS 6724, BS 7846, BS EN 60702-1 또는 BS 8436 을 준수한다. (ii) BS EN 61386 및 제 5-54 부 보호도체 요건에 적합한 도기 전선관에 설치한다. (iii) BS EN 50085 및 제 5-54 부 보호도체 요건에 적합한 도기 트렁킹 또는 덕트에 설치한다. (iv) 케이블에 못이나 나사 등이 침투하지 못하 도록 충분한 기계적인 보호 조치를 한다. (V) 제 4-41 부의 415.1 에 규정된 특성을 갖는 RCD 의 수단에 의해 추가적인 보호 조치를 갖춘다. 비고 케이블을 벽이나 격벽 표면에서 50 mm 이하 깊이에 매설했다면 상기 요건 2 의 조건 또한 적용된다. ¦ ¦ 스위스 ¦ 525. ¦ ¦ ¦ 스위스에서는 국내법에 따라 건물의 접속점(주 차단기)과 최종 회로, 예를 들면 콘센트 간의 설 비에 대해 4% 이내의 전압강하가 허용된다. ¦ ¦ 스위스 ¦ 528.2 ¦ ¦ ¦ 스위스에서는 국내법(Verordnung uber elektrische Leitungen 734.31)에 따라 지중 통신선이나 지중 동력 케이블을 지나거나 이에 근접하는 경우 최 소 300 mm 이격을 유지하거나, a) 또는 b) 요건 을 충족해야 한다. ¦ ¦ 벨기에 ¦ 527. ¦ ¦ ¦ 벨기에에서는 일부 구역에 대해서는 특정 소방 요건이 존재한다. ¦ ¦ 이탈리아 ¦ 528.2 ¦ ¦ ¦ 이탈리아에서는 최소 30 m 이격을 유지해야 한다. ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 71 | {}
3064e5f7-d68b-4b54-ac4e-51bf7f82c15a | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 참고문헌 [1] IEC 60050-605:1983, International Electrotechnical Vocabulary Chapter 605: Generation, transmission and distribution of electricity Substations [2] IEC 60332-3(all Parts 3), Tests on electric and optical fibre cables under fire conditions Part 3: Test for vertical flame spread of vertically-mounted bunched wire or cables [3] KS C IEC 60332-3-24, 화재 조건에서의 전기 및 광섬유 케이블 시험- 제 3-24 부: 수직 배치된 케이블 또는 전선의 불꽃전파 시험 - 카테고리 C [4] KS C IEC 60364-4-43:2012, 저압 전기설비 - 제 4-43 부: 안전을 위한 보호 - 과전류에 대한 보호 [5] KS C IEC 60364-5-51:2005, 건축 전기설비 - 제 5-51 부: 전기기기의 선정 및 시공 - 공통 규칙 [6] KS C IEC 60364-7-715, 저압 전기설비 - 제 7-715 부: 특수 설비 또는 특수 장소에 관한 요구 사항 - 특별 저전압 조명 설비 [7] IEC 61000(all parts), Electromagnetic compatibility(EMC) [8] KS C IEC 61200-52, 전기설비 지침 - 제 52 부: 전기설비의 선정 및 설치 - 배선 [9] KS C IEC 61386-24, 전기설비용 전선관 시스템 - 제 24 부: 지하에 매설된 전선관 시스템에 대한 특정 요구사항 [10] IEC 61535, Installation couplers intended for permanent connection in fixed installations [11] KS C IEC 62305(모든 부), 피뢰시스템 [12] DS DS/EN 12201-1, Plastics piping systems for water supply Polyethylene(PE) Part 1 : General [13] DS DS/EN 12201-2, Plastics piping systems for water supply - Polyethylene(PE) - Part 2: Pipes [14] DS DS/EN 12201-3, Plastics piping systems for water supply Polyethylene(PE) - Part 3: Fittings [15] DS DS/EN 12201-4, Plastics piping systems for water supply Polyethylene(PE) - Part 4: Valves [16] DS DS/EN 12201-5, Plastics piping systems for water supply Polyethylene(PE) - Part 4: Fitness for purpose of the system [17] DS 2393-2:1996, Polyvinyl chloride insulated sheathed cables of rated voltages up to and including 450/750 V - Test methods [18] NFPA 70:2008, National Electrical Code [19] BS 5467:1997, Electric cables. Thermosetting insulated, armoured cables for voltages of 600/1 000 V and 1 900/3 300 V [20] BS 6346:1997, Electric cables. PVC insulated, armoured cables for voltages of 600/1 000 V and 1 900/3 300 V [21] BS 6724:1997, Electric cables. Thermosetting insulated, armoured cables for voltages of 600/1 000 V and 1 900/3 300 V, having low emission of smoke and corrosive gases when affected by fire [22] BS 7846:2000, Electric cables. 600/1 000 V armoured fire-resistant cables having thermosetting insulation and low emission of smoke and corrosive gases when affected by fire [23] BS EN 60702-1:2002, Mineral insulated cables and their terminations with a rated voltage not exceeding 750 V. Cables 72 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
2a869681-f73c-41b0-be12-a5322fb115c7 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 [24] BS 8436:2004, Electric cables. 300/500 V screened electric cables having low emission of smoke and corrosive gases when affected by fire, for use in walls, partitions and building voids. Multicore cables [25] BS EN 50085(all parts), Cable trunking and cable ducting systems for electrical installations 73 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
00b5291d-7100-4c3f-b373-8782d4b9729e | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 KS C IEC 60364-5-52:2009 해 설 이 해설은 이 표준과 관련된 사항을 설명하는 것으로 표준의 일부는 아니다. 1 개정취지 이 표준은 2009 년 제 3 판으로 발행된 IEC 60364-5-52, Low-voltage electrical installations - Part 5-52: Selection and erection of electrical equipment - Wiring systems 를 기초로, 기술적인 내용 및 대응국제 표준의 구성을 변경하지 않고 작성한 한국산업표준이다. 2 개정경위 2.1 이 표준은 1993 년 제 1 판으로 발행된 IEC 60364-5-52, Electrical installations of buildings Part 5: Selection and erection of electrical equipment - Chapter 52: Wiring systems 및 Amendment 1 을 번역하 여 기술적인 내용 및 대응국제표준의 구성을 변경하지 않고 작성한 한국산업표준이다. 2.2 이 표준은 2001 년 8 월 제 2 판으로 발행된 IEC 60346-5-52, Electrical Installations of Buildings Part 5-52: Selection and erection of electrical equipment - Wiring systems 를 번역하여 기술적인 내용 및 대응국제표준의 구성을 변경하지 않고 작성한 한국산업표준이다. 2.3 2009 년 제 3 판으로 발행된 IEC 60364-5-52, Low-voltage electrical installations - Part 5-52: Selection and erection of electrical equipment - Wiring systems 를 기초로, 기술적인 내용 및 대응국제 표준의 구성을 변경하지 않고 작성한 한국산업표준이다. 2.4 2024 년 민원 신청에 따라, 표 B.52.21 의 제목을 '기중 개방의 단심케이블의 참고허용전류로 적 용되는 복수의 다심케이블의 집합에 대한 저감계수'에서 '기중 개방의 하나의 단심케이블의 참고허용 전류에 적용되는 하나 이상의 단심케이블의 집합에 대한 저감 계수'로 수정하였다. 이는 IEC 원문에 충실하게 부합화하기 위함이다. 3 적용범위 이 표준은 배선설비의 선정과 설치를 다루고 있다. 4 개정내용 4.1 주요 개정내용 a) 521.4 버스바트렁킹 시스템 및 파워트랙 시스템은 관련표준에 적합하도록 정함. b) 523.6.3 에서 중성선이 선도체보다 커야 하는 고조파 함유량을 10% 이상에서 15% 이상으로 개 정함. c) 523.9 에 금속 피복된 단심케이블을 신설 d) 525 절 수용자설비의 전압강하 내용을 신설 74 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
74eb7096-dd6a-48f9-b366-128906fd2d6a | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 e) 526.2~526.9 개정 또는 신설 · 전선의 전기적 접속에 관해 땜납접속, 다중선 등의 추가요건 개정 및 신설 f) 528 절에 지중통신케이블과 지중전력케이블의 접근에 관한 요구사항 신설 g) 529 절은 청소를 포함하여 유지 보수와 관련하여 문구를 정비함. 5 국내 여건을 고려한 허용전류의 계산 5.1 주위온도 우리나라 기상청자료를 근거로 하여 다음과 같이 주위온도를 적용하는 것으로 한다. 다만, 설치 현장 의 기후조건에 따라 배선경로의 최악조건을 고려하여 이를 달리 적용할 수 있다. 기중: 여름 40 °C 지중: 여름 30 °C(매설 깊이 1.2m) 해설 표 1 - 우리나라 최근 6 년간 7, 8 월 중 월평균기온 최고 값(2005~2010) ¦ 구분 ¦ 2005 ¦ 2006 ¦ 2007 ¦ 2008 ¦ 2009 ¦ 2010 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 월평균 최고기온 ¦ 포항 30.4 ¦ 목포 32.5 ¦ 제주 31.2 ¦ 포항 30.8(7 월) ¦ 수원 30.3 ¦ 제주 32.1 ¦ ¦ 일최고기온 ¦ 영월 37.2 ¦ 진주 37.5 ¦ 임실 33.5 ¦ 영덕 37.7 ¦ 밀양 38.3 ¦ 강릉 31.5 ¦ ¦ 일최저기온 ¦ 금산 - 19.7 ¦ 문산 -17.6 ¦ 동두천 -10.7 ¦ 해남 -12.7 ¦ 상주 -13.8 ¦ 철원 -26.8 ¦ ¦ 지중온도 0.5 m ¦ 제주 29.1, 대전 27.4 ¦ 제주 30.0, 대전 28.8 ¦ 제주 30.5, 대전 27.8 ¦ 제주 29.2, 대전 27.5 ¦ 제주 27.5, 대전 27.3 ¦ 제주 30.2, 대전 28.5 ¦ ¦ 지중온도 1.0 m ¦ 제주 27.4, 대전 26.5 ¦ 제주 28.0, 대전 26.9 ¦ 제주 28.2, 대전 26.5 ¦ 제주 27.8, 대전 26.7 ¦ 제주 26.2, 대전 26.1 ¦ 제주 27.7, 대전 27.1 ¦ ¦ 지중온도 1.2 m (보간법) ¦ 26.72 26.14 ¦ 27.08 26.42 ¦ 27.32 26.30 ¦ 27.08 26.42 ¦ 25.60 25.78 ¦ 27.1 26.46 ¦ ¦ 지중온도 1.5 m ¦ 제주 25.7, 대전 25.6 ¦ 제주 25.7, 대전 25.2 ¦ 제주 26.0, 대전 25.1 ¦ 제주 26.0, 대전 25.5 ¦ 제주 24.7, 대전 24.8 ¦ 제주 26.2, 대전 25.5 ¦ ¦ 자료출처: 2010 기상연보, 기상청 ¦ 자료출처: 2010 기상연보, 기상청 ¦ 자료출처: 2010 기상연보, 기상청 ¦ 자료출처: 2010 기상연보, 기상청 ¦ 자료출처: 2010 기상연보, 기상청 ¦ 자료출처: 2010 기상연보, 기상청 ¦ 자료출처: 2010 기상연보, 기상청 ¦ 5.2 토양 열저항률 5.2.1 B.52.3 의 토양의 열저항률에서 금속외장이 없는 저압 지중케이블에 대해 실측자료가 없는 경 우, 토양 열저항률로서 2.5K · m/W 를 채택하여 IEC 60287 표준에 따라 계산한 허용전류 값을 제시하 고 실제의 토양 열저항률이 2.5K · m/W 와 다른 경우에 대한 보정계수를 표 B52.16 에 제시하고 있다. 이 값은 지리 및 토질을 모르는 상황에서 세계 어느 곳에서나 이 값을 사용하는 것은 부적절하므로 설치현장의 여건에 따라 적절한 값을 적용해야 할 필요가 있다. 이때의 허용전류는 토양의 열저항률 이 1.0 K · m/W 인 때와 비교하여 지중 덕트 매설 방법은 18 %, 지중 직접 매설 방법은 50 %의 여유 를 갖는 값이다. 5.2.2 토양의 열저항은 토양의 수분 함량에 매우 민감하고 시간이 지남에 따라 매우 다를 수 있으 며, 토양의 종류, 지형과 기상조건에 따라 달라진다. IEC 60287-3-1 에서는 기준 주위 온도와 토양의 75 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f81a3759-123f-4bf0-8882-d82ab267abe1 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 열저항에 대한 국가표준이 없는 경우 표 2 와 같은 조건에서 표 3 의 값을 채택할 것을 권장하고 있다. 이때 전류 정격은 주어진 최대온도에 대해 유효해야 하고, 낮은 값은 겨울철에 요구되며, 이 값은 겨 울과 여름, 건기와 우기철의 온도와 도 연관성이 있다. 포설 깊이에 관한 정보가 없을 경우 표준 깊이 는 1 m 로 한다. 해설 표 2 - 해수면에서의 주위온도 ¦ 기후 ¦ 기중주위온도[°C] ¦ 기중주위온도[°C] ¦ 깊이 1 m 에서의 지중 주위온도[C] ¦ 깊이 1 m 에서의 지중 주위온도[C] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기후 ¦ 최저 ¦ 최고 ¦ 최저 ¦ 최고 ¦ ¦ 열대 ¦ 25 ¦ 55 ¦ 25 ¦ 40 ¦ ¦ 아열대 ¦ 10 ¦ 40 ¦ 15 ¦ 30 ¦ ¦ 온대 ¦ 0 ¦ 25 ¦ 10 ¦ 20 ¦ 한국의 경우, 장기적 해수면 기준 대기온도는 평균 17.1 °C, 최고 30 °C, 최저 1 °C 이다. 해설 표 3 - 토양 열저항률 ¦ 열저항률 [K · m/W] ¦ 토양 조건 ¦ 기후 조건 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 0.7 ¦ 매우 젖음(Very moist) ¦ 습기 지속 ¦ ¦ 1.0 ¦ 젖음(Moist) ¦ 주기적 강우 ¦ ¦ 2.0 ¦ 건조(Dry) ¦ 드물게 비 ¦ ¦ 3.0 ¦ 매우 건조(Very dry) ¦ 조금 또는 비가오지 않음 ¦ 5.2.3 주요국가의 토양 열저항률에 관한 대표적인 조건은 표 4 와 같다. 영국에서는 모든 배전케이블 설치에서 토양이 젖거나 꽤 축축한 상태로 유지되는 것을 알 수 있는 경우에는 0.8K · m/W ~ 1.0K · m/W 의 채택이 합리적이며, 토양이 항상 젖어 있지 않는 일반적인 경우이지만 점토(clay)나 찰흙(loam)의 토양 열저항률의 대표 값은 1.2K · m/W 가 적정하다고 하고 있다. 해설 표 4 - 주요국가의 대표적인 조건 ¦ 국명 ¦ 기중주위온도 [C] ¦ 기중주위온도 [C] ¦ 지중주위온도 [C] ¦ 지중주위온도 [C] ¦ 토양 열저항률, [K · m/W] ¦ 매설 깊이 (1 kV 이하인 경우)[m] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 국명 ¦ 최고 ¦ 최저 ¦ 최고 ¦ 최저 ¦ 토양 열저항률, [K · m/W] ¦ 매설 깊이 (1 kV 이하인 경우)[m] ¦ ¦ 캐나다 ¦ 40 ¦ -40 ¦ 20 ¦ -5 ¦ 1.2 (평균 0.9) ¦ 0.9 ¦ ¦ 프랑스 ¦ 30 a ¦ 20b ¦ 20 a ¦ 10b ¦ 1.2a,0.85 b ¦ - ¦ ¦ 독일 ¦ 30 ¦ -20~ +20 평균 ¦ 20 ¦ 0 ¦ 1.0 ¦ 0.7 ¦ ¦ 일본 ¦ 40 a ¦ 30b ¦ 25a ¦ 15b ¦ 1.0 ¦ 1.2 ¦ ¦ 영국 ¦ 25(옥외), 30(건물 내) ¦ 25(옥외), 30(건물 내) ¦ 15 ¦ 15 ¦ 1.2 ¦ 0.5 ¦ ¦ 미국 ¦ 40 ¦ 40 ¦ 20 ¦ 20 ¦ 0.9 ¦ 0.9 ¦ ¦ a 여름 b ¦ a 여름 b ¦ a 여름 b ¦ a 여름 b ¦ a 여름 b ¦ a 여름 b ¦ a 여름 b ¦ 겨울 5.2.4 토양 열저항률의 권장 값 76 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
1b9d2bf2-4a49-4035-aa85-cbb6f40fd25e | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 설치현장의 토양특성을 측정하여 적용하는 것이 가장 바람직하며, 국내외 연구자료를 근거로 다음 값의 적용을 권장한다. 젖은 상태 토양의 경우, 0.6 K · m/W 일반적인 함수량일 때 1.0 K · m/W 건조 상태 토양의 경우, 1.5 K · m/W 5.2.5 향후 지중케이블의 전류용량을 적정하게 경제적으로 산정하기 위해서는 국내실정에 적합한 토양 열저항률 값에 관한 연구가 시급히 필요하다. 6 기타사항 이 표준은 KS A 0001:2023, 표준의 서식과 작성방법에 따라 작성하였다. 77 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
543a74d6-e218-46d8-a9a3-3daed41ab219 | KSCIEC60364-5-52_KR | KS C IEC 60364-5-52:2009 KSKSKS KSKSK KSKS KSK KS KSK KSKS KSKSK KSKSKS Low-voltage electrical installations Part 5-52: Selection and erection of electrical equipment - Wiring systems ICS 13.260; 91.140.50 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
bedbc4ca-8a12-4c0f-b887-a05925fc0b11 | 국내_기계설비_기술기준_매뉴얼_최종본 | 기계설비 기술기준 매뉴얼 최 종 본 2022. 05. 국토교통부 ![image](/image/placeholder) | {}
af365a0d-5460-498c-a981-97c7131edca8 | 국내_기계설비_기술기준_매뉴얼_최종본 | 알 아 두 기 ! · · · 「기계설비 기술기준」 을 포함하여 본 매뉴얼에서 인용한 국가건 설기준[KDS, KCS)과 각종 관련법에서 사용한 용어는 「설비 표준 용어집[2015 년)」 과 KS 표기법에 맞게 수정하였습니다. · · · · ¦ 기계설비 기술기준 및 관련법 사용 용어 ¦ 수정 용어 ¦ 수정 사유 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 호칭경 ¦ 호칭지름 또는 DN ¦ 국제 표준 부합 》 설비표준 용어집 용어 사용 ¦ ¦ 직경 ¦ 지름 ¦ 국제 표준 부합 》 설비표준 용어집 용어 사용 ¦ ¦ 내경 ¦ 안지름 ¦ 국제 표준 부합 》 설비표준 용어집 용어 사용 ¦ ¦ 외경 ¦ 바깥지름 ¦ 국제 표준 부합 》 설비표준 용어집 용어 사용 ¦ ¦ 넘침관 ¦ 오버플로관 ¦ 국제 표준 부합 》 설비표준 용어집 용어 사용 ¦ ¦ 마찰손실수두 손실수두 ¦ 마찰손실 ¦ 국제 표준 부합 》 설비표준 용어집 용어 사용 ¦ ¦ 수조 고가수조 지하저수조 저수조 축열조 빙축조 저류조 침사조 정화조 ¦ 탱크 고가탱크 지하저수탱크 저수탱크 축열탱크 빙축탱크 저류탱크 침사탱크 정화탱크 ¦ 한자로 쓸 경우 혼동 소지가 있는 용어 》 설비표준 용어집 용어 사용 ¦ ¦ 급수전 지수전 ¦ 급수수도꼭지 지수밸브 ¦ 한자로 쓸 경우 혼동 소지가 있는 용어 》 설비표준 용어집 용어 사용 ¦ ¦ 샤워기 ¦ 샤워 ¦ 》 설비표준 용어집 용어 사용 ¦ | {}
b1bd5e01-0ab0-4d0e-8b34-e19f0cb91782 | 국내_기계설비_기술기준_매뉴얼_최종본 | 목 차 1. 기계설비공사 업무의 절차와 방법 ・・・・・・・・ ·······················01 1. 기계설비 착공 전 확인과 사용 전 검사 업무처리 절차 - 02 2. 기계설비 착공 전 확인 신청서 등 .............................12 3. 기계설비 사용 전 검사 신청서 등 .....................21 2. 기계설비 기술기준 판단기준 ・・・・・・・・・ ··· ·····················32 1. 기계설비 착공 전 확인표 판단기준 ··················································· 2. 기계설비 사용 전 확인표 판단기준 ·················· 48 3. 기계설비 착공 전 확인 및 사용 전 검사 검토서 작성 예시 ····················· ---------------------- 84 4. 기계설비 안전확인서 판단기준 -----------------------95 3. 기계설비 기술기준 해설 ----------------------99 [별표 1] 열원 및 냉난방설비의 설계 및 시공 기준 ................................................... .........................100 [별표 2] 공기조화설비의 설계 및 시공 기준 ··················138 [별표 3] 환기설비의 설계 및 시공 기준 ··············156 [별표 4] 위생기구설비의 설계 및 시공 기준 ··························· ················177 [별표 5] 급수 · 급탕설비의 설계 및 시공 기준 ······ .................184 [별표 6] 오 · 배수 통기 및 우수배수설비의 설계 및 시공 기준 ······ ·················210 [별표 7] 오수정화 및 물재이용설비의 설계 및 시공 기준 ···············233 [별표 8] 배관설비의 설계 및 시공 기준 ·················252 [별표 9] 덕트설비의 설계 및 시공 기준 ················· ················278 [별표 10] 보온설비의 설계 및 시공 기준 ················298 [별표 11] 자동제어설비의 설계 및 시공 기준 ··············327 [별표 12] 방음 · 방진 · 내진 설비의 설계 및 시공 기준 ··············354 [별표 13] 플랜트설비의 설계 및 시공 기준 ···············381 [별표 14] 특수설비의 설계 및 시공 기준 ··················384 [별표 15] 기계설비 유지관리를 고려한 설계기준 ···························· .......................392 부록 ・・・・・・・・ ...................................11 1. 기계설비 기술기준 --------40 2. 기계설비 기술기준 그림 해설 ....................418 3. 관련기관 연락처 ·············· ..........................421 4. 별지 서식 등 ··················································· - 기계설비 기술기준 별지서식[제 1 호 ~ 제 6 호] - 기계설비법 시행규칙 별지서식[제 4 호 ~ 제 9 호] - 검토서 및 첨부서류 작성양식 | {}
ef45fcba-ed5c-49cc-ab14-f6c8737fc6b2 | 국내_기계설비_기술기준_매뉴얼_최종본 | I 기계설비공사 업무의 절차와 방법 1. 기계설비 착공 전 확인과 사용 전 검사 업무처리 절차 ·········· -02 2. 기계설비 착공 전 확인 신청서 등 12 3. 기계설비 사용 전 검사 신청서 등 ·····21 | {}
f9b64ad5-931d-4542-a60c-233e50c67ee3 | 국내_기계설비_기술기준_매뉴얼_최종본 | 1. 기계설비 착공 전 확인과 사용 전 검사 업무처리 절차 □ 목 적 「기계설비 기술기준」의 현장 적용과 기준 준수 여부의 확인, 착공 전 확인 및 사용 전 검사 등 기계설 비공사 행정업무를 효과 적으로 운영하기 위한 정보와 절차를 제공함 - 설계·시공·감리업무수행자 및 허가권자(시·군·구청장 등)에게 착공 전 확인 및 사용 전 검사 관련 서 식 작성 방법 등 행정절차 수행을 위한 정보 제공 - 「기계설비 기술기준」 적용 시 적합·부적합 판단을 위한 기준 및 정보 제공 - 「기계설비 기술기준」 내용 해석을 위한 정보 제공 □ 관련 법규 「기계설비법」 ('20.4.18.)시행 - 「기계설비법」 제 14 조, 제 15 조 - 「기계설비법 시행령」 제 11 조, 제 12 조, 제 13 조 - 「기계설비법 시행규칙」 제 5 조, 제 6 조 - 「기계설비 기술기준」 고시[제 2021-851 호](2021.6.7) □ 적용 시기 및 대상 (1) 2020 년 4 월 18 일 이후 설계계약을 체결하는 기계설비공사부터 적용함 (2) 「기계설비 기술기준」은 이 고시 시행 이후 설계계약을 체결하는 기계설비공사부터 적용함 (3) 「건축법」 등 관계법령에 따라 신축·증축·개축·재축·대수선·리모델링 등을 하기 위하여 허가를 받 거나 신고를 하는 건축물등에 대한 기계설비공사는 「기계설비법」의 착공 전 확인 대상임 (4) 기계설비공사의 착공 전 확인 적용대상 기계설비 및 제외대상 기계설비 - 적용 대상 : 「기계설비 기술기준」 제 8 조(기계설비의 설계 및 시공 기준) 제 1 호~제 12 호 제 9 조(유지관리를 고려한 설계 및 시공) 제 2 항 - 제외 대상 : 「기계설비 기술기준」 제 8 조(기계설비의 설계 및 시공 기준) 中 제 13 호(플랜트설비)~제 14 호(특수설비) (5) 사용 전 검사는 2020 년 4 월 18 일 이후 착공 전 확인을 받은 기계설비공사부터 적용함 □ 「기계설비 기술기준」 (법 제 14 조) 「기계설비법」 제 14 조(기계설비 기술기준) ① 국토교통부장관은 기계설비의 안전과 성능확보를 위하여 필요한 기술기준(이하 "기술기준"이라 한다)을 정하여 고시하여야 한다. 이를 변경하는 경우에도 또한 같다. 기계설비사업자는 기술기준을 준수하여야 한다. 2 기계설비 기술기준 매뉴얼 | {}
f53889be-420b-47b6-a6e0-d5379574632e | 국내_기계설비_기술기준_매뉴얼_최종본 | 1. 기계설비공사 업무의 절차와 방법 기계설비의 착공 전 확인과 사용 전 검사 대상 건축물(시행령 제 11 조, 별표 5) 「기계설비법 시행령」 제 11 조(기계설비의 착공 전 확인과 사용 전 검사 대상 공사) 법 제 15 조 제 1 항 본문에서 "대통령령으로 정하는 기 계설비공사"란 별표 5 에 해당하는 건축물(「건축법」 제 11 조에 따른 건축허가를 받으려거나 같은 법 제 14 조에 따른 건축신고를 하려는 건축물로 한정하며, 다른 법령에 따라 건축허가 또는 건축신고가 의제되는 행정처분 을 받으려는 건축물을 포함한다) 또는 시설물에 대한 기계설비공사를 말한다. 기계설비의 착공 전 확인과 사용 전 검사의 대상 건축물 또는 시설물(영 제 11 조 관련 별표 15) 1. 용도별 건축물 중 연면적 1 만제곱미터 이상인 건축물(「건축법」 제 2 조제 2 항제 18 호에 따른 창고시설은 제외한다) 2. 에너지를 대량으로 소비하는 다음 각 목의 어느 하나에 해당하는 건축물 가. 냉동 · 냉장, 항온 · 항습 또는 특수청정을 위한 특수설비가 설치된 건축물로서 해당 용도에 사용되는 바닥 면적의 합계가 500 제곱미터 이상인 건축물 나. 「건축법 시행령」 별표 1 제 2 호가목 및 나목에 따른 아파트 및 연립주택 다. 다음의 어느 하나에 해당하는 건축물로서 해당 용도에 사용되는 바닥면적 의 합계가 500 제곱미터 이상인 건축물 1) 「건축법 시행령」 별표 1 제 3 호다목에 따른 목욕장 2) 「건축법 시행령」 별표 1 제 13 호가목에 따른 놀이형시설(물놀이를 위하여 실내에 설치된 경우로 한정한다) 및 같은 호 다목에 따른 운동장(실내에 설치된 수영장과 이에 딸린 건축물로 한정한다) 라. 다음의 어느 하나에 해당하는 건축물로서 해당 용도에 사용되는 바닥면적의 합계가 2 천제곱미터 이상인 건 축물 1) 「건축법 시행령」 별표 1 제 2 호라목에 따른 기숙사 2) 「건축법 시행령」 별표 1 제 9 호에 따른 의료시설 3) 「건축법 시행령」 별표 1 제 12 호다목에 따른 유스호스텔 4) 「건축법 시행령」 별표 1 제 15 호에 따른 숙박시설 마. 다음의 어느 하나에 해당하는 건축물로서 해당 용도에 사용되는 바닥면적의 합계가 3 천제곱미터 이상인 건 축물 1) 「건축법 시행령」 별표 1 제 7 호에 따른 판매시설 2) 「건축법 시행령」 별표 1 제 10 호마목에 따른 연구소 3) 「건축법 시행령」 별표 1 제 14 호에 따른 업무시설 3. 지하역사 및 연면적 2 천제곱미터 이상인 지하도상가(연속되어 있는 둘 이상의 지하도상가의 연면적 합계가 2 천제곱미터 이상인 경우를 포함한다) □ 기계설비의 착공 전 확인과 사용 전 검사 업무 (법 제 15 조, 시행령 제 12 조, 제 13 조, 시행규칙 제 5 조, 제 6 조) (1) 기계설비공사 착공 전 확인 기계설비공사를 발주한 자는 해당 공사를 시작하기 전에 전체 설계도 서 중 기계설비에 해당하는 설계도서 특별자치시장·특별자치도지사·시장·군수 자치구 구청장(이 하 "시·군·구청장"이라 함)에게 제출하여 기술기준에 적합한지를 확인받아야 함 (2) 기계설비의 사용 전 검사 기계설비공사를 끝냈을 때에는 시·군·구청장의 사용 전 검사를 받고 기 계설비를 사용하여야 함 (3) 착공 전 확인 기계설비 설계도서가 기술기준에 적합한지를 확인받으려는 자는 기계설비공사 도급계약 후 기계 설비공사 착공 전 확인신청서를 해당 기계설비공사를 시작하기 전에 시장 、 군수 、 구청장에게 제 출해야 하며, 시장 、 군수 、 구청장은 해당 설계도서의 내용이 기술기준에 적합한지를 확인하고, 기계설비공사 업무의 절차와 방법 국토교통부 3 | {}
878c6689-ee35-44d4-a56a-7d8100a2404e | 국내_기계설비_기술기준_매뉴얼_최종본 | 기계설비공사 착공 전 확인 결과 통보서에 검토의 견 등을 적어 해당 신청인에게 통보해야 하며, 해 당 설계도서의 내용이 기술기준에 미달하는 등 시공에 부적합하다고 인정하는 경우에는 보완이 필 요한 사항을 함께 적어 통보하고, 그 내용을 기록하고 관리해야 함 (4) 사용 전 검사 사용 전 검사를 받으려는 자는 기계설비 사용 전 검사신청서를 건축 사용승인 절차에 따라 적합하 게 시장 、 군수 、 구청장에게 제출해야 하고, 시장 、 군수 、 구청장은 해당 기계설비가 기술기준에 적합한지를 검사하여 해당 기계설비가 기술기준에 적합하다고 인정하는 경우에는 기계설비 사용 전 검사 확인증을 해당 신청인에게 발급하며, 기술기준에 미달하는 등 사용에 부적합하다고 인정 하는 경우에는 그 사유와 보완기한을 명시하여 보완을 지시해야 함. 보완 지시를 받은 자가 보완기 한까지 보완을 완료한 경우에는 별도 신청 절차를 다시 거치지 않고 사용 전 검사를 다시 실시하여 기계설비 사용 전 검사 확인증을 발급할 수 있음 (5) 「기계설비법」의 기계설비공사 착공 전 확인 신고는 건축공사의 착공신고 시점이 아닌 기계설비공 사 착공 전에 신고하며, 기계설비 착공 전 신청서 작성 이전에 기계설비감리업무수행자와 계약하 여야 함 (6) 제출서류 ¦ 구 분 ¦ 세부내용 ¦ ¦ --- ¦ --- ¦ ¦ 착공 전 확인 ¦ 。 기계설비공사 착공 전 확인신청서(시행규칙 별지 제 4 호서식) - 날인자 : 기계설비설계자, 시공자, 기계설비감리업무수행자 ※ 기계설비시공자는 그 시공자 모두를 적으며, 하도급의 경우 하도급자를 포함 。 기계설비공사 설계도서 사본 。 기계설비설계자 등록증 사본 。 기계설비에 대한 감리업무를 수행한 자가 확인한 기계설비 착공적합 확인서 ¦ ¦ 사용 전 검사 ¦ 。 기계설비 사용 전 검사신청서(시행규칙 별지 제 7 호서식) - 날인자 : 기계설비시공자, 감리업무수행자 ※ 기계설비시공자는 그 시공자 모두를 적으며, 하도급의 경우 하도급자를 포함 。 기계설비공사 준공설계도서 사본 。 기계설비에 대한 감리업무를 수행한 자가 확인한 기계설비 사용적합 확인서 。 해당 기계설비가 다음 어느 하나에 해당하는 경우에는 그 검사 결과 를 함께 제출할 수 있음 - 「에너지이용 합리화법」 제 39 조제 2 항에 따른 검사대상기기 검사에 합격한 경우, - 「고압가스 안전관리법」 제 16 조제 3 항 본문에 따른 완성검사에 합격한 경우(같은 항 단서에 따라 감리적합판정을 받은 경우를 포함), 완성검사증명서 또는 시공감리증명서 제출 ¦ 「기계설비법」 제 15 조(기계설비의 착공 전 확인과 사용 전 검사) ① 대통령령으로 정하는 기계설비공사를 발주한 자는 해당 공 사를 시작하기 전에 전체 설계도서 중 기계설비에 해당하는 설계도서를 특별자치시장 · 특별자치도지사 · 시 장 · 군수 · 구청장(자치구의 구청장을 말한다. 이하 같다)에게 제출하여 기술기준에 적합한지를 확인받아야 하며, 그 공사를 끝냈을 때에는 특별자치시장 · 특별자치도지사 · 시장 · 군수 · 구청장의 사용 전 검사를 받고 기계설비를 사용하여야 한다. 다만, 「건축법」 제 21 조 및 제 22 조에 따른 착공신고 및 사용승인 과정에서 기술 기준에 적합한지 여부를 확인받은 경우에는 이 법에 따른 착공 전 확인 및 사용 전 검사를 받은 것으로 본다. ② 특별자치시장 · 특별자치도지사 · 시장 · 군수 · 구청장은 필요한 경우 기계설비공사를 발주한 자에게 제 1 항에 따른 착공 전 확인과 사용 전 검사에 관한 자료의 제출을 요구할 수 있다. 이 경우 기계설비공사를 발주한 자 는 특별한 사유가 없으면 자료를 제출하여야 한다. ③ 제 1 항에 따른 착공 전 확인과 사용 전 검사의 절차, 방법 등은 대통령령으로 정한다. 4 기계설비 기술기준 매뉴얼 | {}
be930b95-0890-495a-be94-ed158f193ed8 | 국내_기계설비_기술기준_매뉴얼_최종본 | 1. 기계설비공사 업무의 절차와 방법 「기계설비법 시행령」 제 12 조(기계설비의 착공 전 확인) ① 법 제 15 조 제 1 항 본문에 따라 기계설비에 해당하는 설계도서가 법 제 14 조 제 1 항에 따른 기술기준(이하 "기술기준"이라 한다)에 적합한지를 확인받으려는 자는 국토교통부령으로 정하 는 기계설비공사 착공 전 확인신청서를 해당 기계설비공사를 시작하기 전에 특별자치시장 · 특별자치도지사 · 시장 · 군수 · 구청장(구청장은 자치구의 구청장을 말하며, 이하 "시장 · 군수 · 구청장"이라 한다)에게 제출 해야 한다. ② 시장 · 군수 · 구청장은 제 1 항에 따른 기계설비공사 착공 전 확인신청서를 받은 경우에는 해당 설계도서의 내 용이 기술기준에 적합한지를 확인해야 한다. ③ 시장 · 군수 · 구청장은 제 2 항에 따른 확인을 마친 경우에는 국토교통부령으로 정하는 기계설비공사 착공 전 확인 결과 통보서에 검토의 견 등을 적어 해당 신청인에게 통보해야 하며, 해당 설계도서의 내용이 기술기준에 미달하는 등 시공에 부적합하다고 인정하는 경우에는 보완이 필요한 사항을 함께 적어 통보해야 한다. ④ 시장 · 군수 · 구청장은 제 3 항에 따라 기계설비공사 착공 전 확인 결과 를 통보한 경우에는 그 내용을 기록하 고 관리해야 한다. 제 13 조(기계설비의 사용 전 검사) ① 법 제 15 조 제 1 항 본문에 따라 사용 전 검사를 받으려는 자는 국토교통부령 으로 정하는 기계설비 사용 전 검사신청서를 시장 · 군수 · 구청장에게 제출해야 한다. 이 경우 해당 기계설비 가 다음 각 호의 어느 하나에 해당하는 경우에는 그 검사 결과 를 함께 제출할 수 있다. 1. 「에너지이용 합리화법」 제 39 조 제 2 항에 따른 검사대상기기 검사에 합격한 경우 2. 「고압가스 안전관리법」 제 16 조 제 3 항 본문에 따른 완성검사에 합격한 경우(같은 항 단서에 따라 감리적합판 정을 받은 경우를 포함한다) ② 시장 · 군수 · 구청장은 제 1 항 각 호 외의 부분 전단에 따른 기계설비 사용 전 검사신청서를 받은 경우에는 해 당 기계설비가 기술기준에 적합한지를 검사해야 한다. 이 경우 검사 대상 기계설비 중 제 1 항 각 호 외의 부분 후단에 따라 합격한 검사 결과 가 제출된 기계설비 부분에 대해서는 기술기준에 적합한 것으로 검사해야 한다. ③ 시장 · 군수 · 구청장은 제 2 항에 따른 검사 결과 해당 기계설비가 기술기준에 적합하다고 인정하는 경우에는 국토교통부령으로 정하는 기계설비 사용 전 검사 확인증을 해당 신청인에게 발급해야 한다. ④ 시장 · 군수 · 구청장은 제 2 항에 따른 검사 결과 해당 기계설비가 기술기준에 미달하는 등 사용에 부적합하다 고 인정하는 경우에는 그 사유와 보완기한을 명시하여 보완을 지시해야 한다. ⑤ 시장 · 군수 · 구청장은 제 4 항에 따른 보완 지시를 받은 자가 보완기한까지 보완을 완료한 경우에는 제 1 항에 따른 신청 절차를 다시 거치지 않고 제 2 항 및 제 3 항에 따라 사용 전 검사를 다시 실시하여 기계설비 사용 전 검사 확인증을 발급할 수 있다. 「기계설비법 시행규칙」 제 5 조(착공 전 확인 등) ① 영 제 12 조제 1 항에 따른 기계설비공사 착공 전 확인신청서는 별지 제 4 호서식에 따르 며, 신청인은 이를 제출할 때에는 다음 각 호의 서류를 첨부해야 한다. 1. 기계설비공사 설계도서 사본 2. 기계설비설계자 등록증 사본 3. 「건축법」 등 관계 법령에 따라 기계설비에 대한 감리업무를 수행하는 자가 확인한 기계설비 착공 적합 확인 서 ② 영 제 12 조제 3 항에 따른 기계설비공사 착공 전 확인 결과 통보서는 별지 제 5 호서식에 따른다. ③ 특별자치시장 · 특별자치도지사 · 시장 · 군수 · 구청장(구청장은 자치구의 구청장을 말하며, 이하 "시장 · 군수 · 구청장"이라 한다)은 영 제 12 조제 4 항에 따라 기계설비공사 착공 전 확인 결과 의 내용을 기록하고 관리하는 경우에는 별지 제 6 호서식의 기계설비공사 착공 전 확인업무 관리대장에 일련번호 순으로 기록해야 한다. 제 6 조(사용 전 검사 등) ① 영 제 13 조제 1 항 각 호 외의 부분 전단에 따른 기계설비 사용 전 검사신청서는 별지 제 7 호서식에 따르며, 신청인은 이를 제출할 때에는 다음 각 호의 서류를 첨부해야 한다. 1. 기계설비공사 준공설계도서 사본 2. 「건축법」 등 관계 법령에 따라 기계설비에 대한 감리업무를 수행한 자가 확인한 기계설비 사용 적합 확인서 3. 영 제 13 조제 1 항 각 호에 대한 검사 결과 서(해당하는 검사 결과 가 있는 경우로 한정한다) ② 영 제 13 조제 3 항에 따른 기계설비 사용 전 검사 확인증은 별지 제 8 호서식에 따른다. ③ 시장 · 군수 · 구청장은 영 제 13 조제 3 항에 따라 기계설비 사용 전 검사 확인증을 발급한 경우에는 별지 제 9 호 서식의 기계설비 사용 전 검사 확인증 발급대장에 일련번호 순으로 기록해야 한다. 기계설비공사 업무의 절차와 방법 국토교통부 5 | {}
d371f744-df17-4386-b57c-4dc6028e6f84 | 국내_기계설비_기술기준_매뉴얼_최종본 | 「에너지이용 합리화법」 제 39 조(검사대상기기의 검사) ① 특정열사용기자재 중 산업통상자원부령으로 정하는 검 사대상기기(이하 "검사대상기기"라 한다)의 제조업자는 그 검사대상기기의 제조에 관하여 시 · 도지사의 검사를 받아야 한다. ② 다음 각 호의 어느 하나에 해당하는 자(이하 "검사대상기기설치자"라 한다)는 산업통상자원부령으로 정하 는 바에 따라 시 · 도지사의 검사를 받아야 한다. 1. 검사대상기기를 설치하거나 개조하여 사용하려는 자 2. 검사대상기기의 설치장소를 변경하여 사용하려는 자 3. 검사대상기기를 사용중지한 후 재사용하려는 자 「에너지이용 합리화법 시행규칙」 제 31 조의 6(검사대상기기) 법 제 39 조제 1 항 및 법 제 39 조의 2 제 1 항에 따라 검 사를 받아야 하는 검사대상기기는 별표 3 의 3 과 같다. [별표 3 의 3] 검사대상기기(제 31 조의 6 관련) ¦ 구분 ¦ 검사대상기기 ¦ 적용범위 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 보일러 ¦ 강철제 보일러 주철제 보일러 ¦ 다음 각 호의 어느 하나에 해당하는 것은 제외한다. 1. 최고사용압력이 0.1 MPa 이하이고, 동체의 안지름이 300 mm 이하이 며, 길이가 600 mm 이하인 것 2. 최고사용압력이 0.1 MPa 이하이고, 전열면적이 5 m2 이하인 것 3. 2 종 관류보일러 4. 온수를 발생시키는 보일러로서 대기개방형인 것 ¦ ¦ 보일러 ¦ 소형 온수보일러 ¦ 가스를 사용하는 것으로서 가스사용량이 17 kg/h(도시가스는 232.6 kW)를 초과 하는 것 ¦ ¦ 압력용기 ¦ 1 종 압력용기 2 종 압력용기 ¦ 별표 1 에 따른 압력용기의 적용범위에 따른다. ¦ ¦ 요로 ¦ 철금속가열로 ¦ 정격용량이 0.58 MW 를 초과 하는 것 ¦ 「에너지이용 합리화법 시행규칙」 제 31 조의 7(검사의 종류 및 적용대상) 법 제 39 조제 1 항 · 제 2 항 · 제 4 항 및 법 제 39 조의 2 제 1 항에 따른 검사의 종류 및 적용대상은 별표 3 의 4 와 같다. [별표 3 의 4] 검사의 종류 및 적용대상(제 31 조의 7 관련) - 기계설비법 관련 내용 발췌 ¦ 검사의 종류 ¦ 적용대상 ¦ 근거 법조문 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 설치검사 ¦ 신설한 경우의 검사(사용연료의 변경에 의하여 검사대상이 아닌 보일러가 검사대상으로 되는 경우의 검사를 포함한다) ¦ 법 제 39 조제 2 항제 1 호 ¦ ¦ 개조검사 ¦ 다음 각 호의 어느 하나에 해당하는 경우의 검사 1. 증기보일러를 온수보일러로 개조하는 경우 2. 보일러 섹션의 증감에 의하여 용량을 변경하는 경우 3. 동체 · 돔 · 노통 · 연소실 · 경판 · 천정판 · 관판 · 관모음 또는 스테이의 변경으로서 산업통상자원부장관이 정하여 고시하는 대수리의 경우 4. 연료 또는 연소방법을 변경하는 경우 5. 철금속가열로로서 산업통상자원부장관이 정하여 고시하는 경 우의 수리 ¦ 법 제 39 조제 2 항제 1 호 ¦ ¦ 설치장소 변경검사 ¦ 설치장소를 변경한 경우의 검사. 다만, 이동식 검사대상기기를 제외한다. ¦ 법 제 39 조제 2 항제 2 호 ¦ ¦ 재사용검사 ¦ 사용중지 후 재사용하고자 하는 경우의 검사 ¦ 법 제 39 조제 2 항제 3 호 ¦ 6 기계설비 기술기준 매뉴얼 | {}
eb0ea9f5-4bac-4bb9-be1e-213633b9f959 | 국내_기계설비_기술기준_매뉴얼_최종본 | 1. 기계설비공사 업무의 절차와 방법 「고압가스 안전관리법」 제 16 조(검사대상기기의 검사) ② 고압가스제조자 중 대통령령으로 정하는 종류와 규모 이상의 고압가스제조자가 제 1 항에 따른 고압가스 제조시설의 설치공사나 변경공사를 할 때에 제조소 경계 밖의 지하에 고압가스배관의 설치공사나 변경공사를 하는 경우에는 허가관청이나 신고관청의 감리(��)를 받아야 한다 ③ 사업자등이 고압가스의 제조 · 저장 · 판매 · 수입의 시설이나 용기등의 제조시설의 설치공사 또는 변경공사 를 완공한 때에는 그 시설을 사용하기 전에 허가관청 · 신고관청 또는 등록관청의 완성검사를 받고 합격한 후 에 이를 사용하여야 한다. 다만, 제 2 항에 따라 감리를 받은 시설은 완성검사를 갈음하여 감리적합판정을 받아 야 한다. 「고압가스 안전관리법 시행령」 제 13 조의 2(감리대상) 법 제 16 조제 2 항에 따라 제조소의 경계 밖의 지하에 고압가 스배관의 설치 · 변경공사를 하는 경우 감리를 받아야 하는 고압가스제조자는 제 3 조제 1 호에 따른 고압가스 특정제조 또는 제 3 조제 2 호에 따른 고압가스 일반제조의 허가를 받은 자로 한다. 「고압가스 안전관리법 시행규칙」[별지 제 22 호 서식] 제 호 제 호 검사증명서 [ ]완성 「고압가스 안전관리법 시행규칙」 [별지 제 22 호의 2 서식] [ ]정기 1. 상호: 2. 사업의 종류: 3. 사무소 소재지: 4. 대표자 성명: 5, 사업소 소재지: 6, 검사원 성명: 7. 검사 연월일: 8, 차기 검사일: 「고압가스 안전관리법」 제 16 조제 3 항, 제 16 조의 2 제 1 항 및 같은 법 시행규칙 제 28 조 제 5 항, 제 30 조제 5 항에 따라 고압가스의 제조(저장소 · 판매 · 수입)시설, 용기(냉동기 · 특정설비)의 제조시설의 완성검사(정기검사)증명서를 발급합니다. 년 월 일 한국가스안전공사사장 직인 발급지사명(주소): 담당부서: 전화번호: ![image](/image/placeholder) 시공감리증명서 1. 상호: 2. 사업의 종류: 3. 사무소 소재지: 4. 대표자 성명: 5. 사업소 소재지: 6. 감리구역: 7. 감리원 성명: 8. 시공감리기간: 「고압가스 안전관리법」 제 16 조제 2 항 및 같은 법 시행규칙 제 28 조의 2 제 3 항에 따라 고압가스배관에 대한 시공감리증명서를 발급합니다. 년 월 일 한국가스안전공사사장 직인 발급지사명(주소): 담당부서: 전화번호: 210mmX297mm(백상지 120g/m2 210mmX297mm 박 살지 (20g/m) 기계설비공사 업무의 절차와 방법 국토교통부 7 | {}
cc7b73b4-f46e-4766-b2c6-2112cf5074f8 | 국내_기계설비_기술기준_매뉴얼_최종본 | □ 업무처리 기관 특별자치시 、 특별자치도 、 시 、 군· 구청의 해당 부서 - 이 매뉴얼 부록 관련기관 연락처 참고 □ 기계설비 착공 전 확인 및 사용 전 검사 업무 개요 현황 ¦ 구 분 ¦ 기계설비 설계자/시공자 ¦ 기계설비 감리업무수행자 ¦ 발주자(건축주) ¦ 시·군·구청 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 대 상 건축물 ¦ · 용도별 건축물 중 연면적 1 만 m2 이상인 건축물(창고 제외) · 에너지를 대량으로 소비하는 건축물 -바닥면적 500m2 이상 건축물 : 냉동·냉장, 항온·항습 또는 특수청정을 위한 특수설비, 목욕장, 놀 이형시설, 실배수영장 등 -아파트 및 연립주택 -바닥면적 2,000m2 이상 건축물 : 기술사, 의료시설, 숙박시설 등 -바닥면적 3,000m2 이상 건축물 : 판매시설, 연구시설, 업무시설 등 -지하역사 및 연면적 2,000m2 이상인 지하도상가 ¦ · 용도별 건축물 중 연면적 1 만 m2 이상인 건축물(창고 제외) · 에너지를 대량으로 소비하는 건축물 -바닥면적 500m2 이상 건축물 : 냉동·냉장, 항온·항습 또는 특수청정을 위한 특수설비, 목욕장, 놀 이형시설, 실배수영장 등 -아파트 및 연립주택 -바닥면적 2,000m2 이상 건축물 : 기술사, 의료시설, 숙박시설 등 -바닥면적 3,000m2 이상 건축물 : 판매시설, 연구시설, 업무시설 등 -지하역사 및 연면적 2,000m2 이상인 지하도상가 ¦ · 용도별 건축물 중 연면적 1 만 m2 이상인 건축물(창고 제외) · 에너지를 대량으로 소비하는 건축물 -바닥면적 500m2 이상 건축물 : 냉동·냉장, 항온·항습 또는 특수청정을 위한 특수설비, 목욕장, 놀 이형시설, 실배수영장 등 -아파트 및 연립주택 -바닥면적 2,000m2 이상 건축물 : 기술사, 의료시설, 숙박시설 등 -바닥면적 3,000m2 이상 건축물 : 판매시설, 연구시설, 업무시설 등 -지하역사 및 연면적 2,000m2 이상인 지하도상가 ¦ · 용도별 건축물 중 연면적 1 만 m2 이상인 건축물(창고 제외) · 에너지를 대량으로 소비하는 건축물 -바닥면적 500m2 이상 건축물 : 냉동·냉장, 항온·항습 또는 특수청정을 위한 특수설비, 목욕장, 놀 이형시설, 실배수영장 등 -아파트 및 연립주택 -바닥면적 2,000m2 이상 건축물 : 기술사, 의료시설, 숙박시설 등 -바닥면적 3,000m2 이상 건축물 : 판매시설, 연구시설, 업무시설 등 -지하역사 및 연면적 2,000m2 이상인 지하도상가 ¦ ¦ 기계설비 범 위 ¦ 열원 및 냉난방 설비, 공기조화설비, 환기설비, 위생기구설비, 급수·급탕설비, 오·배수·통기 및 우수 배수설비, 오수정화 및 물재이용설비, 배관설비, 덕트설비, 보온설비, 자동제어설비, 방음·방진·내진 설비(기술기준 별표 1~12) ¦ 열원 및 냉난방 설비, 공기조화설비, 환기설비, 위생기구설비, 급수·급탕설비, 오·배수·통기 및 우수 배수설비, 오수정화 및 물재이용설비, 배관설비, 덕트설비, 보온설비, 자동제어설비, 방음·방진·내진 설비(기술기준 별표 1~12) ¦ 열원 및 냉난방 설비, 공기조화설비, 환기설비, 위생기구설비, 급수·급탕설비, 오·배수·통기 및 우수 배수설비, 오수정화 및 물재이용설비, 배관설비, 덕트설비, 보온설비, 자동제어설비, 방음·방진·내진 설비(기술기준 별표 1~12) ¦ 열원 및 냉난방 설비, 공기조화설비, 환기설비, 위생기구설비, 급수·급탕설비, 오·배수·통기 및 우수 배수설비, 오수정화 및 물재이용설비, 배관설비, 덕트설비, 보온설비, 자동제어설비, 방음·방진·내진 설비(기술기준 별표 1~12) ¦ ¦ 수행업무 ¦ · 기계설비 착공 전 확 인 수행 · 기계설비 성능 및 안 전 평가 ¦ · 기계설비 설계기준 적합 설계 검토 · 기계설비 성능 및 안 전 평가 검토 ¦ · 기계설비 설계도서 기준적합 확인신청 · 기계설비 사용 전 검 사 신청 ¦ · 기계설비설계기준 및 시공기준 적합 여부 확인 · 기계설비 착공 전 확인 결과 통보 및 관리 · 기계설비 사용 전 검 사 확인증 발급 및 관리 ¦ ¦ 착공 전 작성 서류 ¦ · 기계설비 착공 전 확 인표(별지 1 호) ※ (시공자) 시공계획서 작성, 필요시 시공상 세도면 작성, 공정표 작성 ¦ · 기계설비 착공적합 확인서(별지 2 호) ※ 시공계획서·시공상세 도면·공정표 승인 ¦ · 기계설비공사 착공 전 확인신청서(규칙 별지 4 호) -기계설비공사 설계도 서 사본 -기계설비설계자 등록 증 사본 -기계설비 착공적합 확 인서 ¦ · 기계설비공사 착공 전 확인 결과 통보서 (규칙 별지 5 호) · 기계설비공사 착공 전 확인업무 관리대 장(규칙 별지 6 호) ¦ ¦ 사용 전 작성서류 ¦ · 기계설비 사용 전 확 인표(별지 3 호) · 기계설비 성능확인서 (별지 4 호) · 기계설비 안전확인서 (별지 5 호) ※ (시공자) 유지관리지 침서 작성 ¦ · 기계설비 사용적합 확인서(별지 6 호) ¦ · 기계설비 사용 전 검 사신청서(규칙 별지 7 호) -기계설비공사 준공 설 계도서 사본 -기계설비 사용적합 확 인서 -에너지이용합리화법 에 따른 검사증 - 고압가스안전관리법 에 따른 완성검사증 ¦ · 기계설비 사용 전 검 사 확인증(규칙 별지 8 호) · 기계설비 사용전 검 사 확인증 발급대장 (별지 9 호) ¦ ¦ 근거조항 ¦ · 기술기준 제 19 조 제 1 항, 제 4 항 ¦ · 기술기준 제 19 조 제 2~3 항, 제 5~6 항 ¦ · 법 제 15 조제 2 항 · 영 제 12~13 조 · 규칙 제 5~6 조 ¦ · 법 제 15 조제 1 항 · 영 제 12~13 조 · 규칙 제 5~6 조 ¦ 8 기계설비 기술기준 매뉴얼 | {}
45559ae3-71f4-4aac-bcca-a3888fb9afaf | 국내_기계설비_기술기준_매뉴얼_최종본 | 1. 기계설비공사 업무의 절차와 방법 □ 업무처리 절차 ![image](/image/placeholder) 기계설비 착공 전 확인 및 사용 전 검사 업무처리 절차 설 계 기계설비공사 설계 계약 시 공 (기준 부칙 제 6 조, 제 9 조) 기계설비 기계설비 기계설비 착공 전 확인 수행 성능 및 안전 평가 수행 설계자/시공자 (기준 제 19 조제 1 항) (기준 제 19 조제 4 항) · 기계설비 착공 전 확인표 · 기계설비 사용 전 확인표 (기준 별지 제 1 호서식) (기준 별지 제 3 호서식) · 기계설비 성능확인서 (기준 별지 제 4 호서식) · 기계설비 안전확인서 (기준 별지 제 5 호서식) 기계설비 기계설비 설계기준 적합 설계 검토 성능 및 안전 평가 검토 기계설비 (기준 제 19 조제 2 항, 제 3 항) (기준 제 19 조제 5 항, 제 6 항) 감리업무수행자 · 기계설비 착공적합 확인서 · 기계설비 사용적합 확인서 (기준 별지 제 2 호서식) (기준 별지 제 6 호서식) 기계설비 설계도서 기계설비 기준적합 확인 신청 사용 전 검사 신청 (법 제 15 조제 2 항, 영 제 12 조제 1 항, 규칙 제 5 조제 1 항) (법 제 15 조제 2 항, 영 제 13 조제 1 항, 규칙 제 6 조제 1 항) 발주자 · 기계설비공사 착공 전 확인신청서 · 기계설비 사용 전 검사신청서 (규칙 별지 제 7 호서식) (건축주) (규칙 별지 제 4 호서식) - 기계설비공사 준공설계도서 사본 - 기계설비공사 설계도서 사본 - 에너지이용합리화법에 따른 검사증 - 기계설비설계자 등록증 사본 - 고압가스안전관리법에 따른 완성검사증 · 기준 별지 제 1 호 및 제 2 호서식 · 기준 별지 제 3 호 ~ 제 6 호서식 기계설비 설계기준 기계설비 시공기준 적합 작성 여부 확인 적합 시공 여부 검사 (법 제 15 조제 1 항, 영 제 12 조제 2 항, 기준 제 18 조) (법 제 15 조제 1 항, 영 제 13 조제 2 항, 기준 제 20 조) 기계설비공사 착공 전 확인 기계설비 사용 전 검사 시 · 군 · 구청장 결과 통보서 발급 및 관리 확인증 발급 및 관리 (영 제 12 조제 3 항, 제 4 항, 규칙 제 5 조제 2 항, 제 3 항) (영 제 13 조제 3 항~제 5 항, 규칙 제 6 조제 2 항, 제 3 항) · 기계설비공사 착공 전 확인 결과 통보서 · 기계설비 사용 전 검사 확인증 (규칙 별지 제 5 호서식) (규칙 별지 제 8 호서식) · 기계설비공사 착공 전 확인업무 관리대장 · 기계설비 사용 전 검사 확인증 발급대장 (규칙 별지 제 6 호서식) (규칙 별지 제 9 호서식) 기계설비공사 업무의 절차와 방법 국토교통부 9 | {}
d2cbd146-65f5-4711-aa56-48978d54af56 | 국내_기계설비_기술기준_매뉴얼_최종본 | 착공 전 확인 업무처리 절차 ![image](/image/placeholder) 신 청 인 시 · 군 · 구청장 착공 전 확인신청서 제출 착공 전 확인 접수 기계설비공사 설계도서 제출 기계설비공사 설계도서 검토 (기술기준 적합여부 확인) 합 보완지시 부적합 적 보완제출 → ↓ ⑤ 대장 작성 및 정리 기계설비공사 착공 전 확인 ⑥ 결과 통보 결과 통보서 수령 사용 전 검사 업무처리 절차 ![image](/image/placeholder) 신 청 인 시 · 군 · 구청장 사용 전 검사신청서 제출 사용 전 검사 접수 현장 검사 (기술기준 적합여부 확인) 합 보완지시 부적합 적 보완제출 → ↓ 사용 전 검사 확인증 대장 작성 및 정리 기계설비 사용 전 검사 ⑤ 사용 전 검사 확인증 교부 확인증 수령 10 기계설비 기술기준 매뉴얼 | {}
3d4f8991-3c09-410a-b754-8941bac8309b | 국내_기계설비_기술기준_매뉴얼_최종본 | 1. 기계설비공사 업무의 절차와 방법 □ 벌칙기준 (1) 「기계설비법」 제 15 조제 1 항을 위반하여 착공 전 확인을 받지 아니하고 기계설비공사를 발주한 자 또는 사용 전 검사를 받지 아니하고 기계설비를 사용한 자는 1 년 이하의 징역 또는 1 천만원 이하의 벌금에 처함 「기계설비법」 제 15 조(기계설비의 착공 전 확인과 사용 전 검사) ① 대통령령으로 정하는 기계설비공사를 발주한 자는 해당 공 사를 시작하기 전에 전체 설계도서 중 기계설비에 해당하는 설계도서를 특별자치시장 · 특별자치도지사 · 시 장 · 군수 · 구청장(자치구의 구청장을 말한다. 이하 같다)에게 제출하여 기술기준에 적합한지를 확인받아야 하며, 그 공사를 끝냈을 때에는 특별자치시장 · 특별자치도지사 · 시장 · 군수 · 구청장의 사용 전 검사를 받고 기계설비를 사용하여야 한다. 다만, 「건축법」 제 21 조 및 제 22 조에 따른 착공신고 및 사용승인 과정에서 기술 기준에 적합한지 여부를 확인받은 경우에는 이 법에 따른 착공 전 확인 및 사용 전 검사를 받은 것으로 본다. (2) 「기계설비법」 제 15 조제 2 항을 위반하여 착공 전 확인과 사용 전 검사에 관한 자료를 특별자치시장 、 특별자치도지사 、 시장 、 군수 , 구청장에게 제출하지 아니한 자는 100 만원 이하의 과태료를 부 과함 「기계설비법」 제 15 조(기계설비의 착공 전 확인과 사용 전 검사) ② 특별자치시장 · 특별자치도지사 · 시장 · 군수 · 구청장은 필 요한 경우 기계설비공사를 발주한 자에게 제 1 항에 따른 착공 전 확인과 사용 전 검사에 관한 자료의 제출을 요구할 수 있다. 이 경우 기계설비공사를 발주한 자는 특별한 사유가 없으면 자료를 제출하여야 한다. 기계설비공사 업무의 절차와 방법 국토교통부 11 | {}
3f7de6f7-82e1-4b2a-854d-7a9990194951 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 착공 전 확인 신청서 등 「기계설비법 시행규칙」 [별지 제 4 호 서식] ■ 기계설비법 시행규칙 [별지 제 4 호서식] <개정 2022. 2. 25.> 기계설비공사 착공 전 확인신청서 ¦ ※ 색상이 어두운 칸은 신청인이 적지 않습니다. (앞 쪽) ¦ ※ 색상이 어두운 칸은 신청인이 적지 않습니다. (앞 쪽) ¦ ※ 색상이 어두운 칸은 신청인이 적지 않습니다. (앞 쪽) ¦ ※ 색상이 어두운 칸은 신청인이 적지 않습니다. (앞 쪽) ¦ ※ 색상이 어두운 칸은 신청인이 적지 않습니다. (앞 쪽) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 접수번호 ¦ 접수번호 ¦ 접수일 ¦ 처리일 ¦ 처리기간 14 일 ¦ ¦ 신청인 (건축주) ¦ 성명(기관 또는 법인 명칭) ¦ 성명(기관 또는 법인 명칭) ¦ 대표자 ¦ 대표자 ¦ ¦ 신청인 (건축주) ¦ 주소 (전화번 호: ) ¦ 주소 (전화번 호: ) ¦ 주소 (전화번 호: ) ¦ 주소 (전화번 호: ) ¦ ¦ 공사 현장 명칭 ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 공사 현장 주소 ¦ ¦ ¦ ¦ ① 공사의 종류 ¦ ¦ ¦ ¦ ②구조 및 용도 ¦ ¦ ¦ ¦ 건축면적 ¦ 제곱미터 ¦ 연면적/규모(층) 제곱미터/지하 층, 지상 층 ¦ ¦ ③건 축허가번호 ¦ ④ ¦ 건축허가일 ¦ ¦ ⑤착공 예정일 ¦ ⑥ ¦ 준공예정일 ¦ ¦ 기계설비 설계자 ¦ ⑧ 상호 기계설비 설계 관련 등록(신고)번호 ¦ ⑧ 상호 기계설비 설계 관련 등록(신고)번호 ¦ ¦ 기계설비 설계자 ¦ 대표자 (서명 또는 인) ¦ 전화번호 ¦ ¦ 기계설비 설계자 ¦ 영업소 소재지 ¦ 영업소 소재지 ¦ ¦ 기계설비 설계자 ¦ 도급 계약일 ⑨ ¦ 도급 계약일 ⑨ ¦ ¦ ⑩ 기계설비 시공자 ¦ 상호 ⑪ ¦ 공사업 등록 번호 ¦ ¦ ⑩ 기계설비 시공자 ¦ 대표자 (서명 또는 인) ¦ 전화번호 ¦ ¦ ⑩ 기계설비 시공자 ¦ 영업소 소재지 ⑫ ¦ 현장 배치 기계설비기술인 ¦ ¦ ⑩ 기계설비 시공자 ¦ 도급 계약일 13 ¦ 도급 계약일 13 ¦ ¦ ⑭ 기계설비 감리업무 수행자 ¦ 상호 ⑮ ¦ 기계설비 감리 관련 등록(신고)번호 ¦ ¦ ⑭ 기계설비 감리업무 수행자 ¦ 대표자 (서명 또는 인) ¦ 전화번호 ¦ ¦ ⑭ 기계설비 감리업무 수행자 ¦ 영업소 소재지 ⑯ ¦ 현장배 치기계설비감리인 ¦ ¦ ⑭ 기계설비 감리업무 수행자 ¦ 도급 계약일⑰ ¦ 도급 계약일⑰ ¦ 「기계설비법 コ 제 15 조제 1 항, 같은 법 시행령 제 12 조제 1 항 및 같은 법 시행규칙 제 5 조제 1 항에 따라 위와 같이 기계설비공사 착공 전 확인을 신청합니다. 년 월 일 신청인 (서명 또는 인) 특별자치시장 · 특별자치도지사 · 시장 · 군수 · 자치구구청장 귀하 ![image](/image/placeholder) ⑱ 1. 기계설비공사 설계도서 사본 첨부서류 ⑲ 2. 기계설비설계자 등록증 사본 ⑳ 3. 「건축법」 등 관계 법령에 따라 기계설비에 대한 감리업무를 수행하는 자가 확인한 기계설비 착공 적합 확인서 작 성 방 법 기계설비시공자는 그 시공자 모두를 적으며, 하도급의 경우 하도급자를 포 함하여 적습니다. 210mmX297mm[백상지(80g/m2) 또는 중질지(80g/m2) ] 12 기계설비 기술기준 매뉴얼 | {}
bb290476-843f-4534-834e-7cfd503ac6e3 | 국내_기계설비_기술기준_매뉴얼_최종본 | 1. 기계설비공사 업무의 절차와 방법 ① "공사의 종류"란 「기계설비법 시행령」 제 2 조 [별표 1] 기계설비의 범위를 말한다. ② "구조 및 용도"란 「기계설비 기술기준」 제 18 조제 2 항제 4 호에 따른 건축허가서에 기재된 해당 건 축물등의 구조 및 용도를 말한다. ③ "건축허가번호"란 「기계설비 기술기준」 제 18 조제 2 항제 6 호에 따른 건축허가서에 기재된 건축허 가번호를 말한다. ④ "건축허가일"란 「기계설비 기술기준」 제 18 조제 2 항제 6 호에 따른 건축허가서에 기재된 건축허가 일을 말한다. ⑤ "착공예정일"이란 「기계설비 기술기준」 제 18 조제 2 항제 7 호에 따른 기계설비공사 착공예정일을 말한다. ⑥ "준공예정일"이란 「기계설비 기술기준」 제 18 조제 2 항제 7 호에 따른 기계설비공사 준공예정일을 말한다. ⑦ "기계설비설계자"란 「기계설비 기술기준」 제 2 조제 3 호의 「건설기술 진흥법」제 26 조에 따른 건설 기술 용역사업자, 「엔지니어링산업 진흥법」제 21 조에 따른 엔지니어링사업자, 「기술사법」제 6 조 에 따른 기술사사무소 또는 「건축사법」제 23 조에 따른 건축사사무소 등에 소속되어 기계설비공 사의 설계업무를 수행하는 자를 말한다. 복수의 설계업체일 경우에는 대표 업체만 기입하거나 모 든 업체를 기입할 수 있다. ⑧ "기계설비 설계 관련 등록(신고)번호"란 「엔지니어링산업진흥법」 제 2 조 제 4 호에 따라 엔지니어링 사업자로 "설비" 분야에 등록한 번호 또는 「기술사법」 제 6 조 1 항에 따라 "건축기계설비" 또는 "공조냉동기계" 분야로 등록한 기술사사무소의 개설등록번호를 말한다. ⑨ "도급계약일"란 기계설비설계자가 본 공사현장에 대한 설계용역 계약 체결한 날을 말한다. ⑩ "기계설비시공자"란 「기계설비 기술기준」 제 2 조제 4 호의 「건설산업기본법」제 9 조에 따라 건설업 을 등록하고 기계설비공사를 하는 자를 말한다. 하나의 건축물 등에 복수의 회사가 기계설비 시 공 업무를 수행한 경우, 해당되는 모든 회사를 기입한다. ⑪ "공사업 등록번호"란 「건설산업기본법」에 따라 건설업을 등록하여 부여받은 등록번호를 말한다. ⑫ "현장배치기계설비기술인"이란 「기계설비 기술기준」 제 2 조제 6 호의 「건설산업기본법」 제 40 조 및 같은법 시행령 제 35 조에 따라 기계설비공사 현장에 배치된 건설기술인을 말한다. ⑬ "도급계약일"란 기계설비시공자가 본 공사현장에 대한 시공계약 체결한 날을 말한다. ⑭ "기계설비감리업무수행자"란 「기계설비 기술기준」 제 2 조제 5 호의 「건설산업기본법」 제 2 조제 8 호, 「건설기술 진흥법」제 2 조제 5 호, 「건축법」제 2 조제 15 호, 「주택법」제 43 조 및 기타 관계 법령에 따 라 기계설비공사와 관련된 건설사업관리및 감리업무 등을 수행하는 자를 말한다. 복수의 감리업 체일 경우에는 대표 업체만 기입하거나 모든 업체를 기입할 수 있다. ⑮ "기계설비 감리 관련 등록(신고)번호"란 「건설산업기본법」 제 2 조제 8 호, 「건설기술 진흥법」 제 2 조제 5 호, 「건축법」 제 2 조제 15 호, 「주택법」 제 43 조에 따라 등록(신고)하여 부여받은 등록(신고)번호를 기입한다. ⑯ "현장배치기계설비감리인"이란 「기계설비 기술기준」 제 2 조제 7 호의 「건설기술 진흥법 시행령」제 60 조에 따라 기계설비공사 현장에 배치되어 제 5 호에 따른 기계설비공사의 감리업무를 수행하는 건설기술인, 「건축법」제 25 조에 따른 공사감리자 또는 「주택법」 제 43 조에 따른 감리자를 말하며, 배치일을 같이 기입할 수 있다.(예 홍길동(22.01.01)) ⑰ "도급계약일"란 기계설비감리업무수행자가 본 공사현장에 대한 감리용역을 계약 체결한 날을 말한다. ⑱ "기계설비공사 설계도서"란 기계설비 설계도면, 시방서, 부하 및 장비선정 계산서를 말한다. ⑲ "기계설비설계자 등록증"이란 「건설기술 진흥법」제 26 조에 따른 건설기술 용역사업자, 「엔지니어 링산업 진흥법」제 21 조에 따른 엔지니어링사업자, 「기술사법」제 6 조에 따른 기술사사무소 또는 「건축사법」제 23 조에 따른 건축사사무소를 해당기관에 등록한 서류를 말한다. ⑳ "기계설비 착공적합 확인서"란 「기계설비 기술기준」 [별지 제 2 호 서식]을 말한다. [별지 제 2 호 서 식]의 작성방법에 따라 [별지 제 1 호 서식]도 작성하여 착공 전 확인 신청 시 같이 제출하여야 한다. 국토교통부 13 기계설비공사 업무의 절차와 방법 | {}
16425832-d576-48ce-9e88-75ed07e4b114 | 국내_기계설비_기술기준_매뉴얼_최종본 | 「기계설비 기술기준」 [별지 제 2 호 서식] 기계설비 착공적합 확인서 ¦ 기계설비 감리업무 수행지① ¦ 상 호 ¦ ②기계설비 감리 관련 등록번호 ¦ ②기계설비 감리 관련 등록번호 ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기계설비 감리업무 수행지① ¦ 대표자 ¦ (서명 또는 인) ¦ 전 화 번 호 ¦ ¦ ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 공사명 ¦ ¦ ¦ ¦ 건축허가번호 ③ ¦ 건축허가번호 ③ ¦ 건축허가번호 ③ ¦ ¦ 현장배치 ④ (서명 또는 인) 작 성 일 기계설비감리인 ¦ ¦ ¦ ¦ 확 인 내 용 ⑤ ¦ 해당여부 ¦ ⑥ 확인결과 ¦ ¦ 1. 기계설비 일반 ¦ ¦ ¦ ¦ 1) 기계설비 설계원칙 ¦ [ ] ¦ [ 1 적합 [ ] 부적합 ¦ ¦ 2) 기계설비 시공원칙 ¦ I 1 ¦ [ 1 적합 [] 부적합 ¦ ¦ 3) 유지관리 고려한 설계 및 시공 ¦ [ ] ¦ [ 1 적합 [ ] 부적합 ¦ ¦ 2. 기계설비 설계 및 시공기준 ¦ ¦ ¦ ¦ 1) 열원 및 냉난방설비 [별표 1] ¦ [ ] ¦ [ ] 적합 [ ] 부적합 ¦ ¦ 2) 공기조화설비 [별표 2] ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 3) 환기설비 [별표 3] ¦ I 1 ¦ I I 적합 [] 부적합 ¦ ¦ 4) 위생기구설비 [별표 4] ¦ I 1 ¦ I 1 적합 [] 부적합 ¦ ¦ 5) 급수·급탕설비 [별표 5] ¦ [ 1 ¦ [ ] 적합 [] 부적합 ¦ ¦ 6) 오·배수통기 및 우수배수설비 [별표 6] ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 7) 오수정화 및 물재이용설비 [별표 7] ¦ I 1 ¦ [ I 적합 [] 부적합 ¦ ¦ 8) 배관설비 [별표 8] ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 9) 덕트설비 [별표 9] ¦ I ] ¦ [ 1 적합 [] 부적합 ¦ ¦ 10) 보온설비 [별표 10] ¦ [ ] ¦ [ 1 적합 [] 부적합 ¦ ¦ 11) 자동제어설비 [별표 11] ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 12) 방음·방진·내진설비 [별표 12] ¦ [ ] ¦ [ 1 적합 [] 부적합 ¦ ¦ 첨부서류⑦ 기계설비 착공 전 확인표 ¦ 첨부서류⑦ 기계설비 착공 전 확인표 ¦ 첨부서류⑦ 기계설비 착공 전 확인표 ¦ 종합 검토의 견⑧ 작성방법 : 1. 기계설비 착공전 확인표를 확인하여 작성한다. 2. 해당하는 곳에 V 표시를 한다. 210mmX297mm[백상지 80g/m2] ① "기계설비감리업무수행자"란 「건설산업기본법」 제 2 조제 8 호, 「건설기술 진흥법」제 2 조제 5 호, 「건 축법」제 2 조제 15 호, 「주택법」제 43 조 및 기타 관계 법령에 따라 기계설비공사와 관련된 건설사업 관리및 감리업무 등을 수행하는 자를 말한다. 복수의 감리업체일 경우에는 대표 업체만 기입하거 나 모든 업체를 기입할 수 있다. ② "기계설비 감리 관련 등록(신고)번호"란 「건설산업기본법」 제 2 조제 8 호, 「건설기술 진흥법」 제 2 조 제 5 호, 「건축법」 제 2 조제 15 호, 「주택법」 제 43 조에 따라 등록(신고)하여 부여받은 등록(신고)번호 를 기준으로 한다. ③ "건축허가번호"란 「기계설비 기술기준」 제 18 조제 2 항제 6 호에 따라 건축허가서에 기재된 건축허 가번호를 말한다. ④ "현장배치기계설비감리인"이란 「건설기술 진흥법 시행령」제 60 조에 따라 기계설비공사 현장에 배 14 기계설비 기술기준 매뉴얼 | {}
5e25958b-2671-48ba-8801-147ce1286a09 | 국내_기계설비_기술기준_매뉴얼_최종본 | 1. 기계설비공사 업무의 절차와 방법 치되어 제 5 호에 따른 기계설비공사의 감리업무를 수행하는 건설기술인, 「건축법」제 25 조에 따른 공사감리자 또는 「주택법」제 43 조에 따른 감리자를 말한다. 복수의 감리업체일 경우 대표 감리인 만 기입하거나 각 회사의 현장배치기계설비감리인을 기입할 수 있다. ⑤⑥ 「기계설비 기술기준」 [별지 제 1 호 서식] 기계설비 착공 전 확인표의 결과 를 바탕으로 체크[V]한 다. ⑦ "기계설비 착공 전 확인표"란 「기계설비 기술기준」 [별지 제 1 호 서식]을 말한다. ⑧ "종합 검토의 견"에는 「기계설비 기술기준」 [별지 제 1 호 서식] 기계설비 착공 전 확인표에서 발생 한 부적합과 관련된 세부내용을 기재하거나, 적합하지만 추후 시공 시 고려 사항들을 기재한다. 기재 내용이 많을 경우, 이 서식에 줄을 추가하거나 뒷면을 이용할 수 있다. 기계설비공사 업무의 절차와 방법 국토교통부 15 | {}
4ab219b9-b747-4589-9ad1-3ad78bcd8362 | 국내_기계설비_기술기준_매뉴얼_최종본 | 「기계설비 기술기준」 [별지 제 1 호 서식] ¦ 기계설비 착공 전 확인표 ¦ 기계설비 착공 전 확인표 ¦ 기계설비 착공 전 확인표 ¦ 기계설비 착공 전 확인표 ¦ 기계설비 착공 전 확인표 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 구 분 ¦ 확 인 항 목 ¦ 해당여부 ¦ ¦ 2 확인결과 ¦ ¦ 일 반 ¦ 기계설비기술기준 제 6 조에 따른 기계설비설계원칙 적용 여부 확인 ¦ [ ¦ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 1] ¦ 지역난방 의무고시지역 적용 여부 확인 ¦ [ ] ¦ ¦ [] 적합 [] 부적합 ¦ ¦ [별표 1] ¦ 냉난방 설계기준 온도 적용 여부 확인 ¦ I I ¦ ¦ [] 적합 [] 부적합 ¦ ¦ [별표 1] ¦ 냉각탑 수처리 설비 적용 여부 확인 ¦ ¦ ¦ [] 적합 II 부적합 ¦ ¦ [별표 1] ¦ I I 냉방부하의 40% 이상 축열시설 적용 여부 확인 I ¦ ¦ ¦ [] 적합 [] 부적합 ¦ ¦ [별표 1] ¦ 열교환기 안전밸브 설치 적용 여부 확인 I ¦ ¦ ¦ I [] 적합 [] 부적합 ¦ ¦ [별표 1] ¦ 팽창탱크 배관의 역류방지밸브 적용 여부 확인 ¦ I I ¦ ¦ [] 적합 [] 부적합 ¦ ¦ [별표 1] ¦ 펌프 효율은 KS 규격 이상 적용 여부 확인 ¦ ¦ I I ¦ 적합 II 부적합 ¦ ¦ [별표 1] ¦ 항온항습기 비상전원 적용 여부 확인 ¦ ¦ I I ¦ 적합 [] 부적합 ¦ ¦ [별표 2] ¦ 건축물의 규모 및 형태에 따른 공기조화 조닝 적용 여부 확인 ¦ [ 1 ¦ ¦ [] 적합 [] 부적합 ¦ ¦ [별표 2] ¦ 팬코일의 열수요 변화 대응 적용 여부 확인 ¦ I I ¦ ¦ [] 적합 [] 부적합 ¦ ¦ [별표 3] ¦ 건축물 및 시설물의 필요 환기량 적용 여부 확인 ¦ I ¦ I ¦ II 적합 II 부적합 ¦ ¦ [별표 3] ¦ 시설 용도에 맞는 환기방식 적용 여부 확인 ¦ ¦ I ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 3] ¦ 환기설비의 열교환 효율 기입 적용 여부 확인 ¦ ¦ I I ¦ [] 적합 [] 부적합 ¦ ¦ [별표 4] ¦ 위생기구 종류에 따른 사용조건 적용 여부 확인 ¦ [ ¦ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 4] ¦ 설치장소와 이용자의 편의 성 적용 여부 확인 ¦ ¦ I I ¦ [] 적합 [] 부적합 ¦ ¦ [별표 4] ¦ 위생설비별 절수기능 적용 여부 확인 ¦ I ¦ ¦ [] 적합 [] 부적합 ¦ ¦ [별표 5] ¦ 음료용 급수의 음용수 전용 공급 여부 확인 ¦ ¦ I I ¦ 적합 [] 부적합 ¦ ¦ [별표 5] ¦ 저수탱크 최대급수량에 따른 오버플로관 적용 여부 확인 ¦ I ¦ I ¦ [] 적합 [] 부적합 ¦ ¦ [별표 5] ¦ 급탕탱크방식의 팽창탱크 적용 여부 확인 ¦ ¦ ¦ II 적합 II 부적합 ¦ ¦ [별표 6] ¦ 오배수 집수정크기 적정 여부 확인 ¦ I [ ¦ I 1 ¦ 적합 부적합 ¦ ¦ [별표 6] ¦ 오배수 배관 청소구 적용 여부 확인 ¦ I ¦ I ¦ II 적합 II 부적합 ¦ ¦ [별표 6] ¦ 집수정 펌프 배관과 토출관 배관 크기 확인 ¦ ¦ I I ¦ [] 적합 [] 부적합 ¦ ¦ [별표 7] ¦ 하수도법에 따른 개인하수처리시설의 설치기준 적용 여부 확인 ¦ [ ¦ I ¦ 적합 II 부적합 ¦ ¦ [별표 7] ¦ 오수발생량과 정화탱크 처리대상인원의 고시기준 적용 여부 확인 ¦ I I ¦ I ¦ 적합 II 부적합 ¦ ¦ [별표 7] ¦ 빗물 저류탱크 시설 적용 여부 확인 ¦ ¦ I ¦ [] 적합 [] 부적합 ¦ ¦ [별표 8] ¦ 냉온수배관의 신축이음 적용 여부 확인 ¦ [ ¦ 1 ¦ [] 적합 [] 부적합 ¦ ¦ [별표 8] ¦ 용도에 맞는 배관 선정 및 호칭지름 적용 여부 확인 ¦ I I I I ¦ ¦ [] 적합 [] 부적합 ¦ ¦ [별표 8] ¦ 고압증기배관의 압력배관 적용 여부 확인 ¦ ¦ ¦ [] 적합 II 부적합 ¦ ¦ [별표 9] ¦ 사용용도에 따른 덕트 적용 여부 확인 ¦ ¦ ¦ [] 적합 [] 부적합 ¦ ¦ [별표 9] ¦ 외기도입구와 배기구 적용 여부 확인 ¦ I I ¦ ¦ I II 적합 [] 부적합 ¦ ¦ [별표 10] ¦ 배관 및 덕트 등 보온설비 적용 여부 확인 ¦ [ 1 ¦ ¦ [] 적합 [] 부적합 ¦ ¦ [별표 10] ¦ 수도계량기보호함의 보온 적용 여부 확인 I ¦ ¦ ¦ [] 적합 [] 부적합 ¦ ¦ [별표 10] ¦ 동파방지 열선 적용 및 이상 여부 확인 I ¦ ¦ ¦ I [] 적합 [] 부적합 ¦ ¦ [별표 11] ¦ 경보 및 감시시스템 적용 여부 확인 [ ¦ ¦ 1 ¦ [] 적합 [] 부적합 ¦ ¦ [별표 11] ¦ 원격검침 시스템 적용 여부 확인 ¦ ¦ ¦ [] 적합 [] 부적합 ¦ ¦ [별표 12] ¦ 방음 ·방진· 내진 등 적용 여부 확인 ¦ 방음 ·방진· 내진 등 적용 여부 확인 ¦ [ 1 [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ [별표 15] ¦ 기계설비 유지관리를 고려한 설계 적용 여부 확인 ¦ 기계설비 유지관리를 고려한 설계 적용 여부 확인 ¦ I 1 ¦ I ] 적합 I 부적합 ¦ ¦ 구 분 ¦ 회사명/대표자 ¦ 현장배치기계설비기술인 ¦ 현장배치기계설비기술인 ¦ 확인일 ¦ ¦ 기계설비 설계자 ¦ ③ (인) ¦ ⑤ (인) ¦ ⑤ (인) ¦ - ⑥ ¦ ¦ 기계설비 시공자 ¦ ④ (인) ¦ (인) ¦ (인) ¦ ¦ ¦ 작성방법: 해당여부 및 확인결과 에 V 표시를 한다. 210mmX297mm[백상지 80g/m2] ¦ 작성방법: 해당여부 및 확인결과 에 V 표시를 한다. 210mmX297mm[백상지 80g/m2] ¦ 작성방법: 해당여부 및 확인결과 에 V 표시를 한다. 210mmX297mm[백상지 80g/m2] ¦ 작성방법: 해당여부 및 확인결과 에 V 표시를 한다. 210mmX297mm[백상지 80g/m2] ¦ 작성방법: 해당여부 및 확인결과 에 V 표시를 한다. 210mmX297mm[백상지 80g/m2] ¦ ① 착공 전 확인 대상 건축물등에 설치된 기계설비가 기계설비 착공 전 확인표의 일반과 [별표 1] ~ [별표 12], [별표 15]의 확인항목에 해당되는 경우 체크[V]한다. ② 확인항목별로 「기계설비 기술기준」 및 본 매뉴얼을 참고하여 적합/부적합을 판단한다. 적합/부적 합을 판단하기 위해 별표별로 검토표를 만들어 첨부할 수 있다. ③ "기계설비설계자"란 「기계설비 기술기준」 제 2 조제 3 호의 「건설기술 진흥법」제 26 조에 따른 건설 기술 용역사업자, 「엔지니어링산업 진흥법」제 21 조에 따른 엔지니어링사업자, 「기술사법」제 6 조 16 기계설비 기술기준 매뉴얼 | {}
99e61b4a-eb98-4b8f-a1e3-b19120ea07fb | 국내_기계설비_기술기준_매뉴얼_최종본 | 1. 기계설비공사 업무의 절차와 방법 에 따른 기술사사무소 또는 「건축사법」 제 23 조에 따른 건축사사무소 등에 소속되어 기계설비공 사의 설계업무를 수행하는 자를 말한다. 하나의 건축물등에 복수의 회사가 기계설비 설계 업무를 수행한 경우, 해당되는 모든 회사를 기입한다. 이 경우 이 서식에 줄을 추가하거나 뒷면을 이용할 수 있다. ④ "기계설비시공자"란 「기계설비 기술기준」 제 2 조제 4 호의 「건설산업기본법」 제 9 조에 따라 건설업 을 등록하고 기계설비공사를 하는 자를 말한다. 하나의 건축물등에 복수의 회사가 기계설비 시공 업무를 수행한 경우, 해당되는 모든 회사를 기입한다. 이 경우 이 서식에 줄을 추가하거나 뒷면을 이용할 수 있다. ⑤ "현장배치기계설비기술인"이란 「기계설비 기술기준」 제 2 조제 6 호의 「건설산업기본법」 제 40 조 및 같은법 시행령 제 35 조에 따라 기계설비공사 현장에 배치된 건설기술인을 말한다. 하나의 건축물 등에 복수의 회사가 기계설비 시공 업무를 수행한 경우, 해당되는 각 회사의 현장배치기계설비기 술인의 성명을 기입한다. ⑥ "확인일" 이란 배치된 현장배치기계설비기술인이 본 서식과 첨부서류들을 확인한 날을 말한다. 기계설비공사 업무의 절차와 방법 국토교통부 17 | {}
27d4fd6e-81f2-4d85-b02c-b6b0fd670254 | 국내_기계설비_기술기준_매뉴얼_최종본 | 「기계설비법 시행규칙」 [별지 제 5 호 서식] 기계설비법 시행규칙 [별지 제 5 호서식 ] ![image](/image/placeholder) 기계설비공사 착공 전 확인 결과 통보서 ⑨ 발급번호 : 신 청 인 ① 전화번호 (건축주) 주 소 ②기계설비 전화번호 설계자 주 소 ③건축허가 건축현장명 번호 (소재지) ⑤ 검토의 견 ⑥ 보완사항 ⑦기술기준 근거 등) 확인자 소속 성명 (서명 또는 인) 전화번호 「기계설비법」 제 15 조, 같은 법 시행령 제 12 조제 3 항 및 같은 법 시행규칙 제 5 조제 2 항에 따라 위와 같이 기계설 비공사 착공 전 확인 결과 를 통보합니다. ※ 「기계설비법」 제 15 조제 1 항에 따라 발주자는 설계도서가 기술기준에 적합한지를 반드시 확인받아야 하며, 기 계설비 사용 전 검사 결과 기술기준에 부적합한 사항이 있을 경우 이를 보완하지 않으면 재시공 등의 불이익 이 있으니 반드시 보완 후 착공해야 합니다. 년 월 일 특별자치시장 · 특별자치도지사 · 시장 · 군수 · 자치구구청장 직인 210mm x 297mm[백상지(80g/ m2) 또는 중질지(80g/m2)] ① "신청인"에는 제출된 「기계설비법 시행규칙」 [별지 제 4 호 서식] 기계설비공사 착공 전 확인신청 서에 작성된 신청인의 인적사항을 기재한다. ② "기계설비설계자"란 「기계설비 기술기준」 제 2 조제 3 호의 「건설기술 진흥법」 제 26 조에 따른 건설 기술 용역사업자, 「엔지니어링산업 진흥법」 제 21 조에 따른 엔지니어링사업자, 「기술사법」제 6 조 18 기계설비 기술기준 매뉴얼 | {}
83e81a76-2d96-4833-8c97-3808820272fa | 국내_기계설비_기술기준_매뉴얼_최종본 | 1. 기계설비공사 업무의 절차와 방법 에 따른 기술사사무소 또는 「건축사법」 제 23 조에 따른 건축사사무소 등에 소속되어 기계설비공 사의 설계업무를 수행하는 자를 말한다. 복수의 설계업체일 경우에는 대표 업체만 기입하거나 모 든 업체를 기입할 수 있다. ③ "건축허가번호"란 「기계설비 기술기준」 제 18 조제 2 항제 6 호에 따른 건축허가서에 기재된 건축허 가번호를 말한다. ④ "건축현장명(소재지)"이란 「기계설비법 시행규칙」 [별지 제 4 호 서식] 기계설비공사 착공 전 확인 신청서에 기재된 건축현장명과 소재지를 말한다. ⑤ "검토의 견"에는 「기계설비 기술기준」 [별지 제 1 호 서식] 기계설비 착공 전 확인표의 확인결과 를 참고하여 작성한다. (적합/부적합) ⑥ "보완사항"에는 「기계설비 기술기준」 [별지 제 1 호 서식] 기계설비 착공 전 확인표의 확인결과 를 참고하여 보완사항이 있을 경우, 해당사항을 작성한다. ⑦ "관련근거(기술기준 등)"에는 위 기재한 보완사항에 대한 관련 근거를 법령, 기술기준을 근거로 기재 한다. ⑧ "확인자"에는 담당 허가권자(사무분장등에 따라 분장받은 업무에 대하여 그업무를 당당하는자 또 는 위임받은자)의 소속, 이름 및 서명, 전화번호를 기재한다. ⑨ "발급번호"에는 관할부처에서 행정규칙에 따라 번호를 지정하여 관리해야 한다. 국토교통부 19 기계설비공사 업무의 절차와 방법 | {}
f9164c5f-e32e-4d6b-a7bf-05c6c048ac8f | 국내_기계설비_기술기준_매뉴얼_최종본 | 「기계설비법 시행규칙」 [별지 제 6 호 서식] 기계설비법 시행규칙 [별지 제 6 호서식 ] 기계설비공사 착공 전 확인업무 관리대장 Chart Type: bar 꼬 컨 컨 쉰청인 1 건축주 처럼 전 엄사 3 건축주 비용 전 검사 1 건축주 브 설계 2 건축주 도록번 ᄆ 1 건축주 프 프 션 1 건축주 현장 주소 1 건축주 공사 구조 1 건축주 공사 므로 1 건축주 축 적/규 1 건축주 던 뫼(층 일 자 1 건축주 번호 1 건축주 뽕 꼬 1 건축주 접 확인 확인 1 건축주 ※ 검토의 견 : 적합, 부적합(보완 필요) 작성 297mmX210mm[백상지(80g/m2)] ① 허가권자는 기계설비공사 착공 전 확인업무 관리대장 관리 시 일련번호를 작성하여 해당 공사를 관리해야 한다. ② 신청인, 기계설비설계자, 건축현장에 관한 내용은 「기계설비법 시행규칙」 별지 제 4 호 서식 기계 설비공사 착공 전 확인신청서 및 근거도서를 토대로 내용을 기재한다. ③ 처리_착공 전 확인 - 접수일 : 「기계설비법 시행규칙」 [별지 제 4 호 서식] 기계설비공사 착공 전 확인신청서를 접수한 일자 기재 - 검토자 : 「기계설비법 시행규칙」 [별지 제 4 호 서식] 기계설비공사 착공 전 확인신청서와 관련서 류를 접수받아 검토하는 담당 허가권자(사무분장등에 따라 분장받은 업무에 대하여 그업무를 당 당하는자 또는 위임받은자)의 이름 기재 - 검토의 견 : 「기계설비법 시행규칙」 [별지 제 5 호 서식] 기계설비공사 착공 전 확인 결과 통보서를 참고하여 적합/부적합(보완필요)으로 작성 - 통보서 발급번호 : 「기계설비법 시행규칙」 [별지 제 5 호 서식] 기계설비공사 착공 전 확인 결과 통 보서의 발급번호 기재 - 통보일 : 「기계설비법 시행규칙」 [별지 제 5 호 서식] 기계설비공사 착공 전 확인 결과 통보서의 통 보일자 기재 ④ 처리_사용 전 검사 - 접수일 : 「기계설비법 시행규칙」 [별지 제 7 호 서식] 기계설비 사용 전 검사신청서 접수일 기재 - 검사확인증 발급일 : 「기계설비법 시행규칙」 [별지 제 8 호 서식] 기계설비 사용 전 검사 확인증 발 급일 기재 - 검사확인증 번호 : 해당 허가권 지역의 행정절차에 따라 번호를 발급하여 기재 및 자체 관리 20 기계설비 기술기준 매뉴얼 | {}
4d69e648-425c-4db0-bcaf-11d59f220dcf | 국내_기계설비_기술기준_매뉴얼_최종본 | 1. 기계설비공사 업무의 절차와 방법 3. 기계설비 사용 전 검사 신청서 등 「기계설비법 시행규칙」 [별지 제 7 호 서식] 기계설비법 시행규칙 [별지 제 7 호서식] <개정 2021. 2. 2.> 기계설비 사용 전 검사신청서 ※ 색상이 어두운 칸은 신청인이 적지 않습니다. (앞쪽) ¦ 접수번호 ¦ 접수일 ¦ 발급일 처리기간 14 일 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 신청인 (건축주) ¦ 성명(기관 또는 법인 명칭) ¦ 대표자 ¦ ¦ 신청인 (건축주) ¦ 주소 (전화번 호: ) ¦ 주소 (전화번 호: ) ¦ ¦ 기계설비 시공자 ¦ 상호 2 ¦ 공사업 등록번호 ¦ ¦ 기계설비 시공자 ¦ 대표자 (서명 또는 인) ¦ 전화번 호 ¦ ¦ 기계설비 시공자 ¦ 영업소 소재지 3 ¦ 현장 배치 기계설비기술인 ¦ ¦ ④ 기계설비 감리업무 수행자 ¦ 상호 5 ¦ 기계설비 감리 관련 등록(신고)번호 ¦ ¦ ④ 기계설비 감리업무 수행자 ¦ 대표자 (서명 또는 인) ¦ 전화번 호 ¦ ¦ ④ 기계설비 감리업무 수행자 ¦ 영업소 소재지 6 ¦ 현장 배치 기계설비감리인 ¦ ¦ 건축허가 번호 ¦ ⑦ ¦ 검사 현장 명칭 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 건축허가 번호 ¦ ⑦ ¦ 검사 현장 주소 ¦ 공사의 종류 ⑧ 구조 및 용도 ⑨ ¦ 건축면적 ¦ 제곱미터 ¦ 연면적/규모(층수) ¦ 제곱미터/지하 층, 지상 층 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ⑩ 착공일 ¦ ¦ ⑪ 완공일 ¦ ¦ 검사 희망 연월일 「기계설비법」 제 15 조제 1 항, 같은 법 시행령 제 13 조제 1 항 및 같은 법 시행규칙 제 6 조제 1 항에 따라 기계설비 사용 전 검사를 신청합니다. 년 월 일 신 청 인 (서명 또는 인) 특별자치시장 · 특별자치도지사 · 시장 · 군수 · 자치구구청장 귀하 ⑫ 첨부서류㉖ ⑭ ¦ 1. 기계설비공사 준공설계도서 사본 2. 「건축법」 등 관계 법령에 따라 기계설비에 대한 감리업무를 수행한 자가 확 인한 기계설비 사용 적합 확인서 3. 「기계설비법 시행령」 제 13 조제 1 항 각 호에 대한 검사 결과 서(해당하는 검사 결과 가 있는 경우에만 제출합니다) ¦ 수 수 료 없 음 ¦ ¦ --- ¦ --- ¦ 작 성 방 법 1. 연면적은 건축허가서상의 연면적을 적습니다. 2. 기계설비시공자는 그 시공자 모두를 적으며, 하도급의 경우 하도급자를 포함하여 적습니다. 210mm x297mm[백상지(80g/m2) 또는 중질지(80g/m2) ] 국토교통부 21 기계설비공사 업무의 절차와 방법 | {}
f7f29de1-b3a4-4942-954f-3211b3e3c80b | 국내_기계설비_기술기준_매뉴얼_최종본 | ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ (뒤쪽) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ![image](/image/placeholder) 처 리 절 차 이 신청서는 아래와 같이 처리됩니다. 처리기관 신청인 특별자치시 · 특별자치도 · 시 · 군 · 구청 신 청 접 수 15 적합성 검사 기계설비 기계설비 사용 전 검사 확인증 발급 사용 전 검사 확인증 작성 기계설비 사용 전 검사 확인증 발급대장 작성 210mm X297mm[백상지(80g/ m2) 또는 중질지(80g/m2) ] 22 기계설비 기술기준 매뉴얼 | {}
ee47cba2-5d8d-4d7e-8328-d445e91ef890 | 국내_기계설비_기술기준_매뉴얼_최종본 | 1. 기계설비공사 업무의 절차와 방법 "기계설비시공자"란 「기계설비 기술기준」 제 2 조제 4 호의 「건설산업기본법」 제 9 조에 따라 건설업 을 등록하고 기계설비공사를 하는 자를 말한다. 하나의 건축물 등에 복수의 회사가 기계설비 시 공 업무를 수행한 경우, 해당되는 모든 회사를 기입한다. ② "공사업 등록번호"란 「건설산업기본법」에 따라 건설업을 등록하여 부여받은 등록번호를 말한다. ③ "현장배치기계설비기술인"이란 「건설산업기본법」제 40 조 및 같은법 시행령 제 35 조에 따라 기계 설비공사 현장에 배치된 건설기술인을 말한다. ④ "기계설비감리업무수행자"란 「기계설비 기술기준」 제 2 조제 5 호의 「건설산업기본법」 제 2 조제 8 호, 「건설기술 진흥법」제 2 조제 5 호, 「건축법」제 2 조제 15 호, 「주택법」제 43 조 및 기타 관계 법령에 따 라 기계설비공사와 관련된 건설사업관리및 감리업무 등을 수행하는 자를 말한다. 복수의 감리업 체일 경우에는 대표 업체만 기입하거나 모든 업체를 기입할 수 있다. ⑤ "기계설비 감리 관련 등록(신고)번호"란 「건설산업기본법」 제 2 조제 8 호, 「건설기술 진흥법」 제 2 조 제 5 호, 「건축법」 제 2 조제 15 호, 「주택법」 제 43 조에 따라 등록(신고)하여 부여받은 등록(신고)번호 를 기준으로 한다. ⑥ "현장배치기계설비감리인"이란 「기계설비 기술기준」 제 2 조제 7 호의 「건설기술 진흥법 시행령」제 60 조에 따라 기계설비공사 현장에 배치되어 제 5 호에 따른 기계설비공사의 감리업무를 수행하는 건설기술인, 「건축법」제 25 조에 따른 공사감리자 또는 「주택법」제 43 조에 따른 감리자를 말한다. ⑦ "건축허가번호"란 「기계설비 기술기준」 제 20 조제 2 항제 4 호에 따라 건축허가서에 기재된 건축허 가번호를 말한다. ⑧ "공사의 종류"란 「기계설비법 시행령」 제 2 조 [별표 1] 기계설비의 범위를 말한다. ⑨ "구조 및 용도"란 「기계설비 기술기준」 제 20 조제 2 항제 6 호에 따라 건축허가서에 기재된 해당 건 축물등의 구조 및 용도를 말한다. ⑩ "착공일"이란 「기계설비 기술기준」 제 20 조제 2 항제 8 호에 따라 기계설비공사 착공일을 말한다. ⑪ "완공일"이란 「기계설비 기술기준」 제 20 조제 2 항제 8 호에 따라 기계설비공사 완공일을 말한다. ⑫ "기계설비공사 준공설계도서"란 준공된 건물의 최종설계도서로 기계설비 설계도면, 시방서, 부하 및 장비선정 계산서를 말한다. ⑬ "기계설비 사용 적합 확인서"란 「기계설비 기술기준」 [별지 제 6 호 서식]을 말한다. [별지 제 6 호 서 식]의 첨부사항에 따라 [별지 제 3 호, 제 4 호, 제 5 호 서식]도 작성하여 사용 전 검사 신청 시 같이 제 출하여야 한다. ⑭ "「기계설비법 시행령」 제 13 조제 1 항 각 호에 대한 검사"란 제 1 호 「에너지이용 합리화법」 제 39 조 제 2 항에 따른 검사대상기기 검사와 제 2 호 「고압가스 안전관리법」 제 16 조제 3 항 본문에 따른 완 성검사(같은 항 단서에 따라 감리적합판정을 받은 경우를 포함한다)를 말한다. ⑮ "적합성 검사"란 기계설비 사용 적합여부를 「기계설비 기술기준」 [별지 제 3 호 서식], [별지 제 4 호 서식], [별지 제 5 호 서식]을 검사한다. 국토교통부 23 기계설비공사 업무의 절차와 방법 | {}
f6a07d7c-c473-4fe9-9984-de44b8c9a36c | 국내_기계설비_기술기준_매뉴얼_최종본 | 「기계설비 기술기준」 [별지 제 6 호 서식] ¦ 기계설비 사용적합 확인서 ¦ 기계설비 사용적합 확인서 ¦ 기계설비 사용적합 확인서 ¦ 기계설비 사용적합 확인서 ¦ 기계설비 사용적합 확인서 ¦ 기계설비 사용적합 확인서 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ① ¦ 기계설비 상 호 감리업무 ¦ ¦ 기계설비 감리 관련 ② 등록번호 ¦ 기계설비 감리 관련 ② 등록번호 ¦ ¦ ¦ ① ¦ 수행자 대 표 자 ¦ (서명 또는 인) ¦ 전 화 번 호 ¦ 전 화 번 호 ¦ ¦ ¦ 공사명 ¦ 공사명 ¦ ¦ ¦ ¦ ¦ ¦ 건축허가번호 ¦ 건축허가번호 ¦ ¦ ¦ ¦ ¦ ¦ 3 ¦ 현장배치 기계설비감리인 ¦ (서명 또는 인) ¦ 작 성 일 ¦ 작 성 일 ¦ ¦ ¦ 검 사 항 목 및 내 용 (해당항목만 V 기재) 4 ¦ 검 사 항 목 및 내 용 (해당항목만 V 기재) 4 ¦ 검 사 항 목 및 내 용 (해당항목만 V 기재) 4 ¦ 해당여부 ¦ ⑤ 검사결과 ¦ 비 고 ¦ ¦ 1. 기계설비 유지관리 공간 계획 ¦ 1. 기계설비 유지관리 공간 계획 ¦ 1. 기계설비 유지관리 공간 계획 ¦ ¦ ¦ ¦ ¦ 1) 기계실 ¦ 1) 기계실 ¦ 1) 기계실 ¦ [ ] ¦ [] 적합 [ ] 부적합 ¦ ¦ ¦ 2) 피트 ¦ 2) 피트 ¦ 2) 피트 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 3) 샤프트 ¦ 3) 샤프트 ¦ 3) 샤프트 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 4) 점검구 ¦ 4) 점검구 ¦ 4) 점검구 ¦ [ ] ¦ [] 적합 [ ] 부적합 ¦ ¦ ¦ 2. 기계설비 기술기준 ¦ 2. 기계설비 기술기준 ¦ 2. 기계설비 기술기준 ¦ ¦ ¦ ¦ ¦ 1) 열원 및 냉난방설비 ¦ 1) 열원 및 냉난방설비 ¦ 1) 열원 및 냉난방설비 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 2) 공기조화설비 ¦ 2) 공기조화설비 ¦ 2) 공기조화설비 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 3) 환기설비 ¦ 3) 환기설비 ¦ 3) 환기설비 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 4) 위생기구설비 ¦ 4) 위생기구설비 ¦ 4) 위생기구설비 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 5) 급수·급탕설비 ¦ 5) 급수·급탕설비 ¦ 5) 급수·급탕설비 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 6) 오·배수통기 및 우수배수설비 ¦ 6) 오·배수통기 및 우수배수설비 ¦ 6) 오·배수통기 및 우수배수설비 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 7) 오수정화 및 물재이용설비 ¦ 7) 오수정화 및 물재이용설비 ¦ 7) 오수정화 및 물재이용설비 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 8) 배관설비 ¦ 8) 배관설비 ¦ 8) 배관설비 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 9) 덕트설비 ¦ 9) 덕트설비 ¦ 9) 덕트설비 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 10) 보온설비 ¦ 10) 보온설비 ¦ 10) 보온설비 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 11) 자동제어설비 ¦ 11) 자동제어설비 ¦ 11) 자동제어설비 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 12) 방음·방진·내진설비 ¦ 12) 방음·방진·내진설비 ¦ 12) 방음·방진·내진설비 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 3. 기계설비 안전 및 성능 확인 ¦ 3. 기계설비 안전 및 성능 확인 ¦ 3. 기계설비 안전 및 성능 확인 ¦ ¦ ¦ ¦ ¦ 1) 기계설비 성능 확인 ¦ 1) 기계설비 성능 확인 ¦ 1) 기계설비 성능 확인 ¦ [ ] ¦ [] 적합 [ ] 부적합 ¦ ¦ ¦ 2) 기계설비 안전 확인 ¦ 2) 기계설비 안전 확인 ¦ 2) 기계설비 안전 확인 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 첨부사항 1. 기계설비 사용 전 확인표 2. 기계설비 성능확인서 3. 기계설비 안전확인서 ¦ 첨부사항 1. 기계설비 사용 전 확인표 2. 기계설비 성능확인서 3. 기계설비 안전확인서 ¦ 첨부사항 1. 기계설비 사용 전 확인표 2. 기계설비 성능확인서 3. 기계설비 안전확인서 ¦ 첨부사항 1. 기계설비 사용 전 확인표 2. 기계설비 성능확인서 3. 기계설비 안전확인서 ¦ 첨부사항 1. 기계설비 사용 전 확인표 2. 기계설비 성능확인서 3. 기계설비 안전확인서 ¦ 첨부사항 1. 기계설비 사용 전 확인표 2. 기계설비 성능확인서 3. 기계설비 안전확인서 ¦ ¦ 종합 검토의 견 ¦ 종합 검토의 견 ¦ 종합 검토의 견 ¦ 종합 검토의 견 ¦ 종합 검토의 견 ¦ 종합 검토의 견 ¦ 210mmX297mm[백상지 80g/m2] ① "기계설비감리업무수행자"란 「기계설비 기술기준」 제 2 조제 5 호의 「건설산업기본법」 제 2 조제 8 호, 「건설기술 진흥법」제 2 조제 5 호, 「건축법」제 2 조제 15 호, 「주택법」제 43 조 및 기타 관계 법령에 따 라 기계설비공사와 관련된 건설사업관리및 감리업무 등을 수행하는 자를 말한다. ② "기계설비 감리 관련 등록(신고)번호"란 「건설산업기본법」 제 2 조제 8 호, 「건설기술 진흥법」 제 2 조 제 5 호, 「건축법」 제 2 조제 15 호, 「주택법」 제 43 조에 따라 등록(신고)하여 부여받은 등록(신고)번호 를 기준으로 한다. ③ "현장배치기계설비감리인"이란 「기계설비 기술기준」 제 2 조제 7 호의 「건설기술 진흥법 시행령」제 60 조에 따라 기계설비공사 현장에 배치되어 제 5 호에 따른 기계설비공사의 감리업무를 수행하는 건설기술인, 「건축법」제 25 조에 따른 공사감리자 또는 「주택법」제 43 조에 따른 감리자를 말한다. ④⑤ 「기계설비 기술기준」 [별지 제 3 호 서식] 기계설비 사용 전 확인표의 결과 를 바탕으로 체크[V]한다. 「기계설비 기술기준」 [별지 제 3 호 서식], [별지 제 4 호 서식], [별지 제 5 호 서식]을 첨부한다. ⑥ 24 기계설비 기술기준 매뉴얼 | {}
eec7be7b-571f-4ce0-8854-2d920fdbe429 | 국내_기계설비_기술기준_매뉴얼_최종본 | 1. 기계설비공사 업무의 절차와 방법 「기계설비 기술기준」 [별지 제 3 호 서식] ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 2] ¦ [별표 2] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ 공기조화설비 ¦ 공기조화설비 ¦ ¦ 공 종 ¦ 공기조화설비 ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ① ¦ 검 사 항 목 (해당항목만 V 기재) ① ¦ 해당여부 ¦ ② 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [] ¦ [] 적합 [] 부적합 ¦ ¦ 자 재 ¦ 주요기자재 선정 및 사용은 적합한가 ¦ 주요기자재 선정 및 사용은 적합한가 ¦ [ ] ¦ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 공기조화기의 설치는 기술기준에 적합한가 ¦ 공기조화기의 설치는 기술기준에 적합한가 ¦ [ ] ¦ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 팬코일유닛의 설치는 기술기준에 적합한가 ¦ 팬코일유닛의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 방열기의 설치는 기술기준에 적합한가 ¦ 방열기의 설치는 기술기준에 적합한가 ¦ [ ] ¦ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 온수온돌난방의 설치는 기술기준에 적합한가 ¦ 온수온돌난방의 설치는 기술기준에 적합한가 ¦ [ 1 ¦ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 배관 및 덕트 등의 연결상태는 기술기준에 적합한가 ¦ 배관 및 덕트 등의 연결상태는 기술기준에 적합한가 ¦ [ ] ¦ I ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 밸브 및 계측기기류 설치는 기술기준에 적합한가 ¦ 밸브 및 계측기기류 설치는 기술기준에 적합한가 ¦ [ ] ¦ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 보온 및 마감상태는 기술기준에 적합한가 ¦ 보온 및 마감상태는 기술기준에 적합한가 ¦ [ 1 ¦ [ ] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 공기조화기의 작동은 적합한가 ¦ 공기조화기의 작동은 적합한가 ¦ [ ] ¦ ] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 온수온돌난방설비의 공기빼기작동은 적합한가 ¦ 온수온돌난방설비의 공기빼기작동은 적합한가 ¦ [ ] ¦ ] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ I ] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [] ¦ [ ] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 ¦ ¦ ¦ ¦ 회사명(상호) ¦ ¦ (인) ¦ 확인일 ¦ 확인일 ¦ ¦ 회사명(상호) ¦ ¦ (인) ¦ ¦ ¦ ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/m2] ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/m2] ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/m2] ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/m2] ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/m2] ¦ ① 사용 전 검사 대상 건축물 등에 설치된 기계설비(공기조화설비)가 각 검사항목에 해당되는 경우 체크[V]한다. ② 검사항목별로 이 매뉴얼의 '2. 기계설비 기술기준 판단기준'을 참고하여 적합/부적합을 판단한다. ③ "기계설비시공자"란 「기계설비 기술기준」 제 2 조제 4 호의 「건설산업기본법」제 9 조에 따라 건설업을 등록하고 기계설비공사를 하는 자를 말한다. 기계설비 시공을 담당하는 회사의 사업자등록증 상의 회사명과 대표자를 말하며, 하나의 건축물등에 복수의 회사가 기계설비 시공 업무를 수행한 경우, 해당되는 모든 회사를 기입한다. 이 경우 이 서식에 줄을 추가하거나 뒷면을 이용할 수 있다. ④ "현장배치기계설비기술인"이란 「건설산업기본법」제 40 조 및 같은법 시행령 제 35 조에 따라 기계 설비공사 현장에 배치된 건설기술인을 말한다. 기계설비 시공 시 현장에 배치되는 기계설비 기술 인을 말하며, 하나의 건축물등에 복수의 회사가 기계설비 시공 업무를 수행한 경우, 해당되는 각 회사의 현장배치기계설비기술인 성명을 기입한다. 국토교통부 25 기계설비공사 업무의 절차와 방법 | {}
f3234e40-46cf-4b0a-b492-2111676bf44c | 국내_기계설비_기술기준_매뉴얼_최종본 | 「기계설비 기술기준」 [별지 제 4 호 서식] ¦ 기계설비 성능확인서 ¦ 기계설비 성능확인서 ¦ 기계설비 성능확인서 ¦ 기계설비 성능확인서 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기계설비①상 호 시 공 자 ¦ (서명 또는 인) ¦ 시공면허등록번호 ② 전 화 번 호 ¦ ¦ ¦ 대 표 자 ¦ ¦ ¦ ¦ ¦ 공 사 명 ¦ ¦ ¦ ¦ ¦ 건축허가번호 ③ ¦ ¦ ¦ ¦ ¦ 현장배치 (서명 또는 인) ④ 기계설비기술인 검 사 항 목 및 내 용 (해당항목만 V 기재) ⑤ ¦ 작 성 일 ¦ ¦ 비 고 ¦ ¦ 1. 열원 및 냉난방설비 계통 ¦ 해당여부 ¦ ⑥ 검사결과 ¦ ¦ ¦ 1) 열원 장비 ¦ ¦ [] 적합 [ ] 부적합 ¦ ¦ ¦ 2) 냉난방 펌프 ¦ [ ] [ ] ¦ [] 적합 [ ] 부적합 ¦ ¦ ¦ 2. 공기조화/환기 계통 ¦ ¦ ¦ ¦ ¦ 1) 공기조화기 ¦ ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 2) 송풍기 ¦ [ ] [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 3) 단말기기(팬코일, 방열기 등) ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 4) 환기장치(환기유니트 등) ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 5) 덕트 계통 ¦ [ ] ¦ [ - 적합 [] 부적합 ¦ ¦ ¦ 6) 배관 계통 ¦ [ ] ¦ [] 적합 [ ] 부적합 ¦ ¦ ¦ 3. 위생기구/급수급탕/오배수통기 계통 ¦ ¦ ¦ ¦ ¦ 1) 위생 펌프 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 2) 배관 계통 ¦ [ ] ¦ [] 적합 [ ] 부적합 ¦ ¦ ¦ 4. 오수정화, 중수도, 빗물처리 계통 ¦ ¦ ¦ ¦ ¦ 1) 오수정화설비 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 2) 중수도설비 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 3) 빗물처리설비 ¦ [ ] ¦ [] 적합 [ ] 부적합 ¦ ¦ ¦ 5. 자동제어 계통 ¦ ¦ ¦ ¦ ¦ 1) 중앙제어설비 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 2) 현장제어설비 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 3) 건물에너지관리시스템(BEMS) ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 4) 원격검침설비 ¦ [ ] ¦ [] 적합 [ ] 부적합 ¦ ¦ ¦ 6. 방음방진내진 계통 ¦ ¦ ¦ ¦ ¦ 1) 장비 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 2) 덕트계통 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 3) 배관계통 ¦ ¦ [ ] ¦ ¦ ¦ 210mmX297mm[백상지 80g/m2] ¦ [ ] ¦ [ ] 적합 부적합 ¦ ¦ ① "기계설비시공자"란 「기계설비 기술기준」 제 2 조제 4 호의 「건설산업기본법」제 9 조에 따라 건설업을 등록하고 기계설비공사를 하는 자를 말한다. 기계설비 시공을 담당하는 회사의 사업자등록증 상의 회사명과 대표자를 말하며, 하나의 건축물등에 복수의 회사가 기계설비 시공 업무를 수행한 경우, 해당되는 모든 회사를 기입한다. 이 경우 이 서식에 줄을 추가하거나 뒷면을 이용할 수 있다. ② "시공면허등록번호"란 「건설산업기본법」에 따라 건설업을 등록하여 부여받은 등록번호를 말한다. ③ "건축허가번호"란 「기계설비 기술기준」 제 18 조제 2 항제 6 호에 따라 건축허가서에 기재된 건축허 가번호를 말한다. ④ "현장배치기계설비기술인"이란 「기계설비 기술기준」 제 2 조제 6 호의 「건설산업기본법」제 40 조 및 같은법 시행령 제 35 조에 따라 기계설비공사 현장에 배치된 건설기술인을 말한다. 기계설비 시공 26 기계설비 기술기준 매뉴얼 | {}
ee78735e-e2a6-4896-a063-95336e54fc64 | 국내_기계설비_기술기준_매뉴얼_최종본 | 1. 기계설비공사 업무의 절차와 방법 시 현장에 배치되는 기계설비 기술인을 말하며, 하나의 건축물등에 복수의 회사가 기계설비 시공 업무를 수행한 경우, 해당되는 모든 기술인의 성명을 기입한다. ⑤ 사용 전 확인 대상 건축물등에 설치된 기계설비가 각 검사항목에 해당되는 경우 체크[V]한다. 검 사항목은 「기계설비 기술기준」[별지 제 3 호 서식] 기계설비 사용 전 확인표의 성능부분을 참고하 여 선정한다. 「기계설비 기술기준」 [별지 제 3 호 서식] 기계설비 사용 전 확인표의 성능 부분과 이 매뉴얼의 성 능 확인 사항을 종합적으로 참고하여 적합/부적합을 판단한다. 기계설비공사 업무의 절차와 방법 국토교통부 27 | {}
c76b3e15-b6ec-4ed1-b0ae-d4b457c2da04 | 국내_기계설비_기술기준_매뉴얼_최종본 | 「기계설비 기술기준」 [별지 제 5 호 서식] 기계설비 안전확인서 ¦ 기계설비 ¦ 상 호 ¦ ② 시공면허등록번호 ¦ ② 시공면허등록번호 ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ①시공자 ¦ 대 표 자 ¦ (서명 또는 인) ¦ 전 화 번 호 ¦ ¦ 공 사 명 건축허가번호 ③ 현장배치 기계설비기술인 ④ (서명 또는 인) 작 성 일 ¦ 검 사 항 목 및 내 용 (해당항목만 V 기재) ⑤ ¦ 해당여부 ¦ ⑥ 검사결과 ¦ 비 고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 보일러실의 일산화탄소 감지기, 경보기는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 보일러의 안전장치는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 냉동기는 친환경냉매를 사용하기에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 냉동기의 안전장치는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 탱크류 안전밸브 설치는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 환기장치의 외기도입구 및 배기구는 안전에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 실외기는 안전에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 냉각탑의 냉각수에 레지오넬라균 번식방지 조치는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 저수탱크 청소 완료(필증)는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 저수탱크 물넘침에 대비하여 배수시설과 알람시설은 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 음용수는 수질기준에 적합한가(시험성적서) ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 급수, 급탕 등의 역류방지 장치는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 급탕가열장치의 온도 및 압력에 대한 안전장치는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 교차배관으로 인한 오염발생 방지조치는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 각 위생기구에 공급되는 급수압은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 물배관 및 계량기의 동파방지 조치는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 동파방지 발열선의 과열시 전원차단 및 경보시설은 적합한가 ¦ [ ] ¦ [ ] 적합 [ ] 부적합 ¦ ¦ ¦ 210mmX297mm[백상지 80g/m2] ¦ 210mmX297mm[백상지 80g/m2] ¦ 210mmX297mm[백상지 80g/m2] ¦ 210mmX297mm[백상지 80g/m2] ¦ ① "기계설비시공자"란 「기계설비 기술기준」 제 2 조제 4 호의 「건설산업기본법」제 9 조에 따라 건설업을 등록하고 기계설비공사를 하는 자를 말한다. 기계설비 시공을 담당하는 회사의 사업자등록증 상의 회사명과 대표자를 말하며, 하나의 건축물등에 복수의 회사가 기계설비 시공 업무를 수행한 경우, 해당되는 모든 회사를 기입한다. 이 경우 이 서식에 줄을 추가하거나 뒷면을 이용할 수 있다. ② "시공면허등록번호"란 「건설산업기본법」에 따라 건설업을 등록하여 부여받은 등록번호를 말한다. ③ "건축허가번호"란 「기계설비 기술기준」 제 18 조제 2 항제 6 호에 따라 건축허가서에 기재된 건축허 가번호를 말한다. ④ "현장배치기계설비기술인"이란 「기계설비 기술기준」 제 2 조제 6 호의 「건설산업기본법」제 40 조 및 같은법 시행령 제 35 조에 따라 기계설비공사 현장에 배치된 건설기술인을 말한다. 기계설비 시공 시 현장에 배치되는 기계설비 기술인을 말하며, 하나의 건축물등에 복수의 회사가 기계설비 시공 업무를 수행한 경우, 해당되는 모든 기술인의 성명을 기입한다. ⑤ 안전확인 대상 건축물등에 설치된 기계설비가 각 검사항목 에 해당되는 경우 체크[V]한다. ⑥ 검사항목별로 이 매뉴얼의 '2. 기계설비 기술기준 판단기준'을 참고하여 적합/부적합을 판단한다. 28 기계설비 기술기준 매뉴얼 | {}
0aaf4c2e-50a1-4196-88c5-42a1a97440c3 | 국내_기계설비_기술기준_매뉴얼_최종본 | 1. 기계설비공사 업무의 절차와 방법 「기계설비법 시행규칙」 [별지 제 8 호 서식] 기계설비법 시행규칙 [별지 제 8 호서식 ] 기계설비 사용 전 검사 확인증 ¦ ① 신청인 (건축주) ¦ 성명(기관 또는 법인 명칭) ¦ 대표자 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ ① 신청인 (건축주) ¦ ¦ 전화번호 ¦ ¦ ① 신청인 (건축주) ¦ 주소 ¦ 주소 ¦ ¦ ② 기계설비 시공자 ¦ 상호 ¦ 공사업 등록번호 ¦ ¦ ② 기계설비 시공자 ¦ 대표자 ¦ 전화번호 ¦ ¦ ② 기계설비 시공자 ¦ 영업소 소재지 ¦ 영업소 소재지 ¦ ¦ ③ 기계설비 감리업무 수행자 ¦ 상호 ¦ 기계설비 감리 관련 등록번호 ¦ ¦ ③ 기계설비 감리업무 수행자 ¦ 대표자 ¦ 전화번호 ¦ ¦ ③ 기계설비 감리업무 수행자 ¦ 영업소 소재지 ¦ 영업소 소재지 ¦ ¦ 4 검사 결과 ¦ 건축허가번호 ¦ 검사 현장 명칭 ¦ ¦ 4 검사 결과 ¦ 건축허가번호 ¦ 검사 현장 주소 ¦ ¦ 4 검사 결과 ¦ 검사 연월일 ¦ 검사 연월일 ¦ ¦ 4 검사 결과 ¦ 검사자 소속: ¦ 검사자 소속: ¦ ¦ 4 검사 결과 ¦ ¦ 성명: (서명 또는 인) ¦ ¦ 4 검사 결과 ¦ 판정 ¦ 판정 ¦ 「기계설비법」 제 15 조, 같은 법 시행령 제 13 조제 3 항 및 같은 법 시행규칙 제 6 조제 2 항에 따라 위와 같이 기계설비 사용 전 검사 확인증을 발급합니다. 년 월 일 특별자치시장 · 특별자치도지사 · 시장 · 군수 · 자치구구청장 직인 210mmX297mm[백상지(120g/ m2 ) ] ① "신청인(건축주)"의 신상정보(주소는 주민등록기준지를 기재)를 기재한다. ② "기계설비시공자"란 「기계설비 기술기준」 제 2 조제 4 호의 「건설산업기본법」 제 9 조에 따라 건설업을 등록하고 기계설비공사를 하는 자를 말한다. 기계설비 시공을 담당하는 회사의 사업자등록증 상의 회사명과 대표자를 말하며, 하나의 건축물등에 복수의 회사가 기계설비 시공 업무를 수행한 경우, 해당되는 모든 회사를 기입한다. 이 경우 이 서식에 줄을 추가하거나 뒷면을 이용할 수 있다. - 상호 : 기계설비시공자의 소속 업체의 상호명을 기재 국토교통부 29 기계설비공사 업무의 절차와 방법 | {}
8c614ac7-e874-4d94-9be4-3360977e806c | 국내_기계설비_기술기준_매뉴얼_최종본 | - 공사업 등록번호 : 「건설산업기본법」 에 따라 건설업을 등록하여 부여받은 등록번호 - 대표자 : 기계설비시공자 소속업체의 대표전화 번호 기재 - 전화번호 : 기계설비시공자 소속업체의 대표전화 번호 기재 - 영업소 소재지 : 기계설비시공자의 소속 업체의 주소(소재지)를 기재 ③ "기계설비감리업무수행자"란 「기계설비 기술기준」 제 2 조제 5 호의 「건설산업기본법」 제 2 조제 8 호, 「건설기술 진흥법」제 2 조제 5 호, 「건축법」제 2 조제 15 호, 「주택법」제 43 조 및 기타 관계 법령에 따 라 기계설비공사와 관련된 건설사업관리및 감리업무 등을 수행하는 자를 말한다. 복수의 감리업 체일 경우에는 대표 업체만 기입하거나 모든 업체를 기입할 수 있다. - 상호 : 기계설비감리업무수행자 소속 업체의 상호명 기재 - 기계설비 감리 관련 등록번호 : 기계설비감리 업무를 수행한 자의 관련 등록번호 - 대표자 : 기계설비감리업무수행자 소속 업체의 대표자명 기재 및 서명 - 전화번호 : 기계설비감리업무수행자 소속 업체의 대표 전화번호 기재 - 영업소 소재지 : 기계설비감리업무수행자 소속 업체의 주소(소재지) 기재 ④ "검사 결과"는 「기계설비법 시행규칙」 [별지 제 7 호 서식] 기계설비 사용 전 검사신청서와 관련서 류들을 검토한 결과 를 참고하여 기재한다. - 건축허가번호 : 「기계설비 기술기준」 제 18 조제 2 항제 6 호에 따른 건축허가서에 기재된 건축허가번호 - 공사 현장 명칭 : 「기계설비 기술기준」 제 18 조제 2 항제 6 호에 따른 건축허가서에 기재된 공사현장명칭 - 검사 연월일 : 기계설비 사용 전 검사 일자 기재 一 검사자 : 기계설비의 사용 전 검사를 수행한 담당 검사자(허가권자)의 소속과 성명 기재 및 서명 - 판정 : 적합/부적합 여부 기재 및 부적합 시 부적합 이유 기재 30 기계설비 기술기준 매뉴얼 | {}
01b26e4a-15fe-46b4-8851-4a528b6f23e2 | 국내_기계설비_기술기준_매뉴얼_최종본 | 1. 기계설비공사 업무의 절차와 방법 「기계설비법 시행규칙」 [별지 제 9 호 서식] 기계설비법 시행규칙 [별지 제 9 호서식 ] 기계설비 사용 전 검사 확인증 발급대장 ¦ ① 신청인(건축주) 일련 번호 ¦ ① 신청인(건축주) 일련 번호 ¦ 건축 현장 ¦ 건축 현장 ¦ 건축 현장 ¦ 건축 현장 ¦ 건축 현장 ¦ 건축 현장 ¦ ③ 처리 ¦ ③ 처리 ¦ ③ 처리 ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ① 신청인(건축주) 일련 번호 ¦ ① 신청인(건축주) 일련 번호 ¦ 성명 (기관 또는 법인 명칭) ¦ 대표 자 ¦ 현장 명 ¦ 현장 주소 ¦ 현장 주소 ¦ 공사 의 종류 ¦ 구조 및 용 도 ¦ 건축 면적 ¦ 연면 적/ 검사 규모 연월일 (층 수) ¦ 발급 연월일 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 297mmX210mm[백상지(80g/m2)] ① "일련번호"는 허가권자(사무분장등에 따라 분장받은 업무에 대하여 그업무를 당당하는자 또는 위 임받은자)가 기계설비공사 사용 전 검사 확인증 발급대장 기록 시 발급하는 번호를 말한다. ② "신청인(건축주)", "건축현장"은 신청인, 건축현장에 관한 내용은 「기계설비법 시행규칙」 [별지 제 7 호 서식] 기계설비공사 사용 전 검사신청서를 토대로 내용을 기재한다. ③ "처리"는 「기계설비법 시행규칙」 [별지 8 호 서식] 기계설비 사용 전 검사 확인증을 참고하여 관련 사항을 기재한다. - 검사 연월일 : 사용 전 검사를 위한 현장 검사일의 일자를 기재 - 발급 연월일 : 사용 전 검사 후 확인증 발급 일자를 기재 - 담당자 : 사용 전 검사 담당 허가권자의 소속 및 성명 기재 기계설비공사 업무의 절차와 방법 국토교통부 31 | {}
d5d5d6dd-a73b-40de-8780-2f33df8b4aa1 | 국내_기계설비_기술기준_매뉴얼_최종본 | 02 기계설비 기술기준 판단기준 1. 기계설비 착공 전 확인표 판단기준 33 2. 기계설비 사용 전 확인표 판단기준 48 3. 기계설비 착공 전 확인 및 사용 전 검사 검토서 작성 예시 ·84 4. 기계설비 안전확인서 판단기준 95 | {}
348baccc-ce57-4f85-910d-11136f601b6f | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 1. 기계설비 착공 전 확인표 판단기준 기계설비 착공 전 확인표_[별지 제 1 호 서식] ¦ 기계설비 착공 전 확인표 ¦ 기계설비 착공 전 확인표 ¦ 기계설비 착공 전 확인표 ¦ 기계설비 착공 전 확인표 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 구 분 ¦ 확 인 항 목 ¦ 해당여부 ¦ 확인결과 ¦ ¦ 일 반 ¦ 기계설비기술기준 제 6 조에 따른 기계설비설계원칙 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 1] ¦ 지역난방 의무고시지역 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 1] ¦ 냉난방 설계기준 온도 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 1] ¦ 냉각탑 수처리 설비 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 1] ¦ 축열시설 40%이상 부분냉방식 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 1] ¦ 열교환기 안전밸브 설치 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 1] ¦ 팽창탱크 배관의 역류방지밸브 적용 여부 확인 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ [별표 1] ¦ 펌프 효율은 KS 규격 이상 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 1] ¦ 항온항습기 비상전원 적용 여부 확인 ¦ I ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 2] ¦ 건축물의 규모 및 형태에 따른 공기조화 조닝 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 2] ¦ 팬코일의 열수요 변화 대응 적용 여부 확인 ¦ I ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 3] ¦ 건축물 및 시설물의 필요 환기량 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 3] ¦ 시설 용도에 맞는 환기방식 적용 여부 확인 ¦ I ¦ [ ] 적합 [] 부적합 ¦ ¦ [별표 3] ¦ 환기설비의 열교환 효율 기입 적용 여부 확인 ¦ I I ¦ [] 적합 [] 부적합 ¦ ¦ [별표 4] ¦ 위생기구 종류에 따른 사용조건 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 4] ¦ 설치장소와 이용자의 편의 성 적용 여부 확인 ¦ [ I ¦ [] 적합 [] 부적합 ¦ ¦ [별표 4] ¦ 위생설비별 절수기능 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 5] ¦ 음료용 급수의 음용수 전용 공급 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 5] ¦ 저수조 최대급수량에 따른 오버플로관 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 5] ¦ 급탕탱크방식의 팽창탱크 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 6] ¦ 오배수 집수정크기 적정 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 6] ¦ 오배수 배관 청소구 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 6] ¦ 집수정 펌프 배관과 토출관 배관 크기 확인 ¦ I ¦ [] 적합 [] 부적합 ¦ ¦ [별표 7] ¦ 하수도법에 따른 개인하수처리시설의 설치기준 적용 여부 확인 ¦ [ ] ¦ [1 적합 [] 부적합 ¦ ¦ [별표 7] ¦ 오수발생량과 정화조 처리대상인원의 고시기준 적용 여부 확인 빗물저류조 시설 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 8] ¦ 냉온수배관의 신축이음 적용 여부 확인 ¦ [ ] [ ] ¦ [] 적합 [] 부적합 [] 적합 [] 부적합 ¦ ¦ [별표 8] ¦ 용도에 맞는 배관 선정 및 호칭지름 적용 여부 확인 ¦ I I ¦ [] 적합 [] 부적합 ¦ ¦ [별표 8] ¦ 고압증기배관의 압력배관 적용 여부 확인 ¦ I I ¦ [] 적합 [] 부적합 ¦ ¦ [별표 9] ¦ 사용용도에 따른 덕트 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 9] ¦ 외기도입구와 배기구 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 10] ¦ 배관 및 덕트 등 보온설비 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 10] ¦ ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 수도계량기보호함의 보온 적용 여부 확인 동파방지 열선 적용 및 이상 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 경보 및 감시시스템 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ [별표 11] ¦ 원격검침 시스템 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 12] ¦ 방음 ·방진· 내진 등 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 12] ¦ 확인 ¦ ¦ ¦ ¦ [별표 15] 구 분 ¦ 기계설비 유지관리를 고려한 설계 적용 여부 회사명/대표자 ¦ [ ] 현장배치기계설비기술인 ¦ [] 적합 [ ] 부적합 확인일 ¦ ¦ 기계설비 설계자 ¦ (인) ¦ (인) ¦ ¦ 기계설비 시공자 (인) (인) 작성방법: 해당여부 및 확인결과 에 V 표시를 한다. 210mmx297mm[백상지 80g/m2] 국토교통부 33 기계설비 기술기준 판단기준 | {}
e383ce40-aeb3-447b-a9b4-1d3a36f67d24 | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 1] 열원 및 냉난방설비의 착공 전 확인 적합/부적합 판단기준 ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ 집단에너지 공급대상지역 관련 공문/질의 회신문서 첨부하고 확인하였 다면 적합으로 함 ¦ - ¦ 공문/질의 회신 문서 ¦ ¦ 2 ¦ 냉난방 설계기준의 온도 적용여부를 계산서에 명기한 경우 적합으로 함 [계산서] 계산서의 냉난방 설계기준(온도) 확인 ¦ [별표 1] 2.1 ¦ 계산서 ¦ ¦ 3 ¦ 냉각탑에 수처리 설비(냉각수 수질 오염 및 레지오넬라균 번식 방지)를 적용하고, 이를 장비일람표에 반영한 경우 적합으로 함 [도면] 장비일람표 냉각탑에서 수처리 설비 명기 확인 ¦ [별표 1] 2.3 (4) (5) ¦ 장비일람표 ¦ ¦ 4 ¦ 축열시설 40% 이상 부분축냉방식(세부항목 관련기준 참조)을 만족하는 열원장비를 설치 확인 [검토서/도면] 장비일람표를 참고하여 건축물의 모든 열원설비 용량을 명기하고, 그 중 축열시설 용량의 부분이 40% 이상임을 산정한 용량검 토서 확인 ¦ [별표 1] 2.1 (8) ¦ 검토서, 장비일람표 ¦ ¦ 5 ¦ 관 내부 압력의 이상 상승으로 상승한 압력이 압력용기의 최고사용압 력을 초과 할 우려가 있는 관형 열교환기의 경우에는 안전밸브 설치를 확인(「산업안전보건기준에 관한 규칙」 제 261 조(안전밸브 등의 설치) 제 1 항 제 1 호) [도면] 기계실 배관평면도/계통도 열교환기 배관에 안전밸브 명기 확인 ¦ [별표 1] 2.6 (5) ¦ 설계도면(평면도/ 계통도 등) ¦ ¦ 6 ¦ 팽창탱크 배관에 역류방지 밸브를 적용하고, 이를 설계도면에 반영한 경우 적합으로 함 [도면] 기계실 배관평면도/계통도 팽창탱크 연결배관에 역류방지밸브 명기 확인 ¦ [별표 1] 2.7 (4) ¦ 설계도면(평면도/ 계통도 등) ¦ ¦ 7 ¦ 펌프 효율을 KS 규격 이상으로 적용하고, 이를 장비일람표에 반영한 경 우 적합으로 함 [도면] 장비일람표 펌프에서 효율을 KS 규격이상 적용 명기 확인 ¦ [별표 1] 2.8 (1) ¦ 장비일람표 ¦ ¦ 8 ¦ 항온항습기의 비상전원을 적용하고, 이를 장비일람표에 반영한 경우 적합으로 함 [도면] 장비일람표 항온항습기에서 비상전원 명기 확인 ¦ [별표 1] 2.13 (3) ¦ 장비일람표 ¦ ※ 모든 항목은 기계설비감리업무수행자의 확인을 받아 관련항목이 적합하다고 인정받는 경우, 적합으로 함. 34 기계설비 기술기준 매뉴얼 | {}
c05e1fa0-6018-400a-ac20-f42c067c1f2d | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 [별표 2] 공기조화설비의 착공 전 확인 적합/부적합 판단기준 ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ 건축물의 규모와 형태를 고려하여 공기조화 조닝(저층·중층·고층 등 수직조닝, 일사 등 외기의 영향을 받는 외주부와 재실자 등 건축물 등의 내부 요소의 영향을 받는 내주부 조닝, 주 용도별 및 시간대별 조닝 등) 설계한 경우 적합으로 함 [도면] 공조조닝 설계의 도를 기술하고, 이를 증빙하는 설계도면(공조조 닝도, 평면도, 계통도) 확인 ¦ [별표 2] 2.1.2 ¦ 설계도면 (공조조닝도/평면 도/계통도 등 ¦ ¦ 2 ¦ 열수요 변화 대응을 고려한 팬코일(예 팬코일 유량/풍량 조절)을 적 용하고 이를 장비 일람표에 반영한 경우 적합으로 함 [도면] 장비일람표 팬코일에서 관련항목 명기 확인 ¦ [별표 2] 2.4 (2) ¦ 장비일람표 ¦ ※ 모든 항목은 기계설비감리업무수행자의 확인을 받아 관련항목이 적합하다고 인정받는 경우, 적합으로 함. 국토교통부 35 기계설비 기술기준 판단기준 | {}
608885d9-4b48-4bdc-a99d-3fc51a1bfd8f | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 3] 환기설비의 착공 전 확인 적합/부적합 판단기준 ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ 건축물 및 시설물에 따라 필요 환기량(최소외기도입량)을 적용하고 이를 계산서에 반영하여 설계한 경우 적합으로 함 2.1.2 용도별 환기설비 (1) 공동주택 ① 공동주택의 필요환기량을 「건축물의 설비기준 등에 관한 규 칙」제 11 조제 1 항에 따라 시간당 0.5 회 이상으로 한 경우 적합 으로 함 ⑥ 주방의 환기량은 각 배기후드의 유효 환기량의 합계와 후드 의 면풍속 0.3 m/s 이상 중 큰 값을 만족하도록 설계한 경우 적 합으로 함 (2) 일반건축물의 필요환기량은 25 m2/인 · h 이상으로 한 경우 적합으로 함 (3) 기계실, 전기실 등 ① 보일러실 등 연소기기를 사용하는 실의 환기량은 장비 및 연 도로부터의 방열량과 허용온도 및 장비의 연소 공기량을 고려 해서 결정한 경우 적합으로 함 ③ 발전기 운전 중 환기량은 장비의 방열량과 허용온도에 의해 계산된 값과 장비의 연소공기량을 고려해서 결정한 경우 적합 으로 함 ④ 전기실의 환기량을 장비의 발열량과 허용온도에 의해 구한 경 우 적합으로 함 ⑤ 엘리베이터 기계실의 환기량은 기계의 발열량을 포함한 취득 열량과 허용온도에 의해 구한 경우 적합으로 함 [계산서] 설계대상 건축물의 필요환기량 기준이 계산서에 명기되었 는지 확인하고, 이를 활용하여 환기량을 산정하였는지 계산서 확인 ¦ [별표 3] 2.1.2 (1)~(3) ¦ 계산서 ¦ ¦ 2 ¦ 2.1.2 (3) ~ (8) 용도별 환기설비 및 2.1.3 터널 환기설비, 2.1.4 공동구 에 맞는 환기방식을 적용한 경우 적합으로 함 2.1.2 용도별 환기설비 (1) 공동주택 ② 공기여과 장치는 입자형 · 가스형 오염물질을 차단할 수 있는 형식으로 한국산업표준(KS B 6141)에 따른 공기필터를 갖추어 야 하며, 여과 장치의 교체시기의 알림기능과 교체가 용이하도 록 설치한 경우 적합으로 함 ⑨ 욕실 배기덕트에는 세대별 역류방지댐퍼를 설치한 경우 적합 으로 함 (2) 일반건축물 ④ 필터가 부착된 기계환기설비의 환기장치는 미세먼지 측정값 을 확인할 수 있는 센서를 통해 감지된 데이터를 모니터링할 수 있도록 설계한 경우 적합으로 함 ⑤ 필터가 부착된 기계환기설비의 환기장치는 차압센서 등을 통 해 감지한 미세먼지 값에 의해 공기질을 제어할 수 있고, 필터 의 교환 시기를 나타낼 수 있게 설계한 경우 적합으로 함 (3) 기계실, 전기실 등 ② 냉동기 전용 기계실의 냉매 배기용 흡입구 하단은 바닥면에서 300 ~ 500 mm 높이에 설치한 경우 적합으로 함 ④ 급배기 송풍기는 실내 온도감지기로 자동 운전하도록 설계한 경우 적합으로 함 ¦ [별표 3] 2.1.2 (1)~(8) ¦ 장비일람표 설계도면, 시방서 ¦ 36 기계설비 기술기준 매뉴얼 | {}
f12ac5f4-53f9-4287-bfd2-d998cac59d4e | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ ⑤ 엘리베이터 기계실의 환기용 송풍기는 실내 온도 감지기에 의해 자동운전되도록 설계한 경우 적합으로 함 (4) 제연겸용 환기송풍기는 화재시를 대비하여 250°C 에서 60 분 이상 가동이 가능하도록 설치한 경우 적합으로 함 (5) 주방과 같이 화기를 사용하는 실 등은 기계환기를 적용하고, 연소기구의 상부에는 가스를 포집할 수 있는 후드를 설치하며, 배기후드의 목 또는 덕트에는 적절한 위치에 풍량조절 댐퍼를 설치한 경우 적합으로 함 (6) 수영장에서는 수질유지를 위하여 물에 약품처리를 하므로 배 기는 공기조화기의 회기(Return air, 공기조화기로 되돌아오는 공기)로 사용하지 않고 전배기한 경우 적합으로 함 (8) 정화탱크 관리실은 음압이 유지될 수 있도록 급배기 시설을 하며, 배기 시에는 탈취설비를 계획한 경우 적합으로 함 [도면/시방서] 설계대상의 용도별로 세부항목들이 준공도서(장비일 람표, 설계도면, 시방서 등)에 적합하게 반영되었는지 확인 ¦ ¦ ¦ ¦ 3 ¦ 폐열회수환기장치의 경우, 사용용도, 형식, 용량, 열교환 효율을 장비 일람표에 기입하였다면 적합으로 함 [도면] 장비일람표 폐열회수환기장치에서 사용용도, 형식, 용량, 열교 환 효율 명기 확인 ¦ [별표 3] 2.3 ¦ 장비일람표 ¦ ※ 모든 항목은 기계설비감리업무수행자의 확인을 받아 관련항목이 적합하다고 인정받는 경우, 적합으로 함. 국토교통부 37 기계설비 기술기준 판단기준 | {}
04e6c63c-5bf3-420d-8066-3e24d1e0d847 | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 4] 위생기구설비의 착공 전 확인 적합/부적합 판단기준 ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ 위생기구 종류에 따른 사용조건을 위생기구일람표에 반영한 경우 적 합으로 함(위생기구, 대소변기, 세면기, 싱크대, 청소싱크, 욕조) (2.2.1) 위생기구에서 급탕은 왼쪽, 급수는 오른쪽에 위치하는 경 우 적합으로 함 (2.2.2) 일반, 유아, 장애인 대변기를 구분한 경우 적합으로 함 (2.2.3) DN 32 이상의 세면기, 수세기, 세발기 배수구를 설계한 경 우 적합으로 함 (2.2.4) DN 40 이상의 싱크대 배수구를 설계한 경우 적합으로 함 (2.2.5) 300 mm 이상의 깊이와 DN 40 이상의 배수구를 갖춘 청 소싱크로 설계한 경우 적합으로 함 (2.2.6) DN 40 이상의 배수관 연결 가능하도록 욕조를 설계한 경 우 적합으로 함 [도면/시방서] 위생기구별 사용조건들이 기입되어 있는지 위생기구 일람표와 시방서 확인 ¦ [별표 4] 2.2.1 ~2.2.6 ¦ 위생기구일람표, 시방서 ¦ ¦ 2 ¦ 설치장소와 이용자의 편의 성 여부를 고려하여 위생기구를 적용한 경 우 적합으로 함(음수기, 비데, 위생설비 유닛, 식기세척기, 세탁기) (2.2.7) 음수기에 배수트랩을 설치한 경우 적합으로 함 (2.2.8) (2.2.9) 확인 사항 없음 (2.2.10) (2.2.11) 식기세척기와 세탁기의 배수가 간접배수로 설계 된 경우 적합으로 하며, 제품에 역류방지 기능이 있는 경우에 는 예외로 할 수 있음 [도면] 음수기, 식기세척기, 세탁기이 설치된 경우 검토서를 작성하며, 위생기구일람표 또는 설계도면에 위생기구별 사용조건 기입 확인 ¦ [별표 4] 2.2.7 ~2.2.11 ¦ 위생기구일람표, 설계도면 ¦ ¦ 3 ¦ 위생설비별 절수기능을 적용한 경우 적합으로 함 [도면] 위생설비별 절수기능 및 절수제품이 적용되어 있는지 위생기 구 일람표 확인 ¦ [별표 4] 2.1.1 (2) ¦ 검토서(위생기구 일람표) ¦ ※ 모든 항목은 기계설비감리업무수행자의 확인을 받아 관련항목이 적합하다고 인정받는 경우, 적합으로 함. 38 기계설비 기술기준 매뉴얼 | {}
93610a2a-a0a3-4d8a-b35f-0cebf11b3024 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 [별표 5] 급수 · 급탕설비의 착공 전 확인 적합/부적합 판단기준 ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ 음료나 목욕, 조리, 음식가공 공정, 의료 또는 제약 공정용으로 급수 하는 위생기구에는 음용수만을 공급하도록 설계한 경우 적합으로 함 [도면] 음료나 목욕, 조리, 음식가공 공정, 의료 또는 제약 공정용에 연결된 급수배관이 타용도의 급수배관과 연결되지 않았음을 확인 ¦ [별표 5] 2.1.1 (1) ¦ 설계도면(평면도/ 계통도 등) ¦ ¦ 2 ¦ 최대 급수량에 맞는 오버플로 호칭지름을 설계하고, 오버플로 관의 토수구 공간을 150 mm 이상으로 하며. 토수구에는 내식성 방충용 철망을 덮도록 설계한 경우 적합으로 함 [도면] ①최대 급수량에 따른 오버플로 호칭지름 설계, ② 오버플로관 의 토수구 공간 150 mm, ③ 토수구에 내식성 방충용 철망 적용 사항 들을 설계도면에 적합하게 설계하였는지 확인 ¦ [별표 5] 2.1.4 (1) ¦ 설계도면(평면도/ 상세도 등) ¦ ¦ 3 ¦ 급탕탱크방식의 급탕배관에 온도상승에 의한 압력을 도피시킬 수 있 는 팽창탱크를 설계한 경우 적합으로 함 [도면] 장비일람표에 급탕용 팽창탱크를 설계한 경우 적합으로 함 ¦ [별표 5] 2.2.1 (8) ¦ 장비일람표 ¦ ※ 모든 항목은 기계설비감리업무수행자의 확인을 받아 관련항목이 적합하다고 인정받는 경우, 적합으로 함 국토교통부 39 기계설비 기술기준 판단기준 | {}
a91d267e-9ddb-4b9d-a56d-59442874f59c | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 6] 오 · 배수 통기 및 우수배수설비의 착공 전 확인 적합/부적합 판단기준 ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ 집수정은 직경 450 mm 이상, 깊이 600 mm 이상으로 설계한 경우 적 합으로 함 [도면] 설계도면에서 설계된 집수정 크기(직경, 깊이)를 확인 ¦ [별표 6] 2.1.3 (4) ¦ 설계도면(평면도) ¦ ¦ 2 ¦ 2.1.4 에 따라 오배수 배관에 청소구를 적용하고 점검구를 설계한 경 우 적합으로 함 (1) 아래의 장소에 청소구를 설계한 경우 적합으로 함 ① 건물 내의 모든 배수 수평관에는 DN 100 이하인 경우는 15 m 이내, DN 100 을 넘는 경우는 매 30 m 마다 ② 배수 수직관의 최하부 또는 그 부근 ③ 건물배수 수평주관과 부지배수관의 연결점 부근 ④ 배수 수평지관 및 배수 수평주관의 기점 ⑤ 배수관이 45°를 넘는 각도로 방향을 변경한 개소 ⑥ 상기 이외에 필요하다고 판단되는 개소 (2) 은폐 배관이나 바닥 밑 배관 또는 높이나 공간이 600 mm 이 하의 좁은 공간에 설계하는 청소구는 마감 벽이나 바닥 또는 지면까지 연장하여 올리거나 건물 외부까지 연장하여 설계한 경우 적합으로 함 (3) 모든 청소구에는 점검구를 설계한 경우 적합으로 함 [도면/시방서] 오배수배관평면도/상세도 등에서 설계기준 2.1.4 에 따 라 청소구 및 점검구 설계되었는지 확인하거나 시방서에 관련내용 명기 확인 ¦ [별표 6] 2.1.4 ¦ 설계도면, 시방서 ¦ ¦ 3 ¦ 집수정 배출관은 차단밸브와 역류방지밸브를 설계하고, 집수정 펌프 배관과 이음쇠의 크기는 펌프 토출관 이상으로 설계한 경우 적합으 로 함 [도면] 오배수배관평면도/상세도 등에서 집수정 배출관에 차단밸브 와 역류방지밸브 적용을 확인하고, 집수정 펌프배관과 이음쇠 크기 를 펌프 토출관 이상으로 설계하였는지 확인 ¦ [별표 6] 2.2.4 (3) ¦ 설계도면 ¦ ※ 모든 항목은 기계설비감리업무수행자의 확인을 받아 관련항목이 적합하다고 인정받는 경우, 적합으로 함. 40 기계설비 기술기준 매뉴얼 | {}
b826ebf3-e8eb-4956-a5a0-d2a205ab8441 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 [별표 7] 오수정화 및 물재이용설비의 착공 전 확인 적합/부적합 판단기준 ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ 개인하수처리시설 대상건물일 경우, 2.2 의 조건에 따라 설계해야만 적합으로 함 2.2 「하수도법」에 따른 「개인하수처리시설의 설치기준」 에 따라 단독 또는 공동으로 개인하수처리시설을 설치하는 경우 적합 으로 함 2.2.1 없음 2.2.2 개인하수처리시설 제품의 구조와 규격, 재질, 성능기준은 「하수도법」에 따랐다면 적합으로 함 2.2.3 방류수 수질기준을 「하수도법」 에 따랐다면 적합으로 함 2.2.4 세부 설치기준을 「하수도법」에 따랐다면 적함으로 함 2.2.5 배수펌프의 유량은 시간최대 처리 수량을 30 분 이내에 배 출할 수 있는 용량 이상으로 하고, 예비펌프와 탈착장치를 구 비하였다면 적합으로 함 2.2.6 오수정화탱크에서 취기 발생의 우려가 있는 경우에는 탈취 장치를 설치하였다면 적합으로 함 [공문/질의 회신] 관련된 관공서에서 오배수 처리방식에 대한 공문/질 의회신 확인 [도면/계산서/시방서] 개인하수처리시설 대상일 경우, 2.2 의 세부조 항들을 적합하게 적용하였는지, 계산서, 시방서, 장비일람표, 설계도 면 등을 확인 ¦ [별표 7] 2.2 ¦ 공문/질의 회신문 서 계산서, 시방서, 장비일람표, 설계도면 등 ¦ ¦ 2 ¦ 건축물의 용도별 오수발생량과 정화조 처리대상인원이 환경부 관련 최근 고시 기준을 만족한다면 적합으로 함 (하수도법 시행령 제 24 조(개인하수처리시설의 설치)에 따른 환경부 고시 「건축물의 용도별 오수발생량 및 정화탱크 처리대상인원 산정 방법」) [고시안/계산서] 최신 환경부 고시안대로 계산서에 적용하였는 지 확인 ¦ [별표 7] 2.2.1 ¦ 환경부고시안, 계산서 ¦ ¦ 3 ¦ 빗물저류조 시설을 설치한 건축물의 경우, 2.3 의 조건에 따라 설치한 다면 적합으로 함 2.3.1 없음 2.3.2 처음 내린 빗물을 배제할 수 있는 장치나 빗물에 섞여 있는 이물질을 제거할 수 있는 여과 장치를 구비하였다면 적합으로 함 2.3.3 내부 청소가 쉬운 구조의 빗물저류탱크를 설치한 경우 적 합으로 함 [도면] 우수관련 평면도(옥상, 옥외 등)에서 여과 장치와 장비일람표 및 기계실 평면도/상세도에서 빗물저류탱크 적용 확인 ¦ [별표 7] 2.3 ¦ 장비일람표 설계도면 ¦ ※ 모든 항목은 기계설비감리업무수행자의 확인을 받아 관련항목이 적합하다고 인정받는 경우, 적합으로 함. 국토교통부 41 기계설비 기술기준 판단기준 | {}
9604aa23-c73d-43ca-888d-d473b7017a76 | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 8] 배관설비의 착공 전 확인 적합/부적합 판단기준 ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ 배관의 신축량, 배관 호칭지름, 배관 공간, 사용압력 등에 따라 적합 한 형식을 선정한 경우 적합으로 함 [도면/계산서] 냉온수배관 평면도 및 계통도에서 신축이음 적용 여부 와 신축이음 관련 계산서 확인 ¦ [별표 8] 2.10 (2) ¦ 설계도면, 계산서 ¦ ¦ 2 ¦ 2.1~2.9 의 조건에 따라 용도에 맞는 배관 선정 및 배관재료에 따른 호칭지름을 적용한 경우 적합으로 함 2.1~2.3 냉온수, 냉각수, 증기배관의 호칭지름은 단위마찰손실과 유속을 기준으로 결정한 경우 적합으로 함 2.3 증기압력이 100 kPa 미만일 경우 저압증기배관, 100 kPa 이 상의 경우 고압증기배관을 적용한 경우 적합으로 함 2.4 급수관 호칭지름은 순간최대유량, 허용마찰손실 및 유속을 산정하고 배관 유량 선도 등을 활용하여 선정한 경우 적합으 로 함 2.5 급탕관의 호칭지름은 급탕부하단위(FU) 값에 의한 순간최대 유량으로 선정하고, 환탕관의 유량을 급탕배관의 열손실을 구 하여 계산하여 선정한 경우 적합으로 함 2.6 오 · 배수배관 호칭지름 산정은 최대 기구배수부하단위수 (DFU)를 사용하여 선정한 경우 적합으로 함 2.7 통기관의 최소 호칭지름은 배관길이와 연결되는 총 기구배수 부하단위로 결정한 경우 적합으로 함 2.8 옥내 우수 수직관과 수평 지관의 호칭지름은 그 지역의 기상 자료에 의한 시간최대강우량을 기준으로 하고, 최대 수평투영 지붕면적을 고려하여 선정한 경우 적합으로 함 2.9 냉매배관의 호칭지름 및 분기방법은 실내기의 합계용량과 같 거나 크게 한 경우 적합으로 함 [도면/시방서/계산서] 2.1~2.9 의 세부항목별 검토사항을 계산서, 시 방서, 설계도면 등에서 확인 ¦ [별표 8] 2.1~2.9 ¦ 계산서 시방서, 설계도면 등 ¦ ¦ 3 ¦ 사용압력 1 Mpa 이상의 관에는 압력배관용 탄소강관 또는 고압배관 용 탄소강관을 적용한 경우 적합으로 함 [도면/시방서] 시방서 또는 설계도면에서 사용압력 1 Mpa 이상의 관 에 압력배관용 탄소강관 또는 고압배관용 탄소강관을 적용 확인 ¦ [별표 8] 2.3.2 (1) ¦ 설계도면, 시방서 ¦ ※ 모든 항목은 기계설비감리업무수행자의 확인을 받아 관련항목이 적합하다고 인정받는 경우, 적합으로 함. 42 기계설비 기술기준 매뉴얼 | {}
82fe6bd9-5562-41ad-af7b-d25f8cbdabc9 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 [별표 9] 덕트설비의 착공 전 확인 적합/부적합 판단기준 ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ 부식성 공기에 접하는 덕트는 부식을 방지하기 위해 PVC 나 스테인 리스강 등 내식성 덕트로 한 경우 적합으로 함 [도면/시방서] 시방서 또는 설계도면에서 부식성 공기에 접하는 덕트 가 부식을 방지하기 위해 PVC 나 스테인리스강 등 내식성 덕트로 하 였는지 확인 ¦ [별표 9] 3.1. (3) ¦ 설계도면(평면도, 시방서 등), 시방서 ¦ ¦ 2 ¦ 외기도입구와 배기구의 설계를 2.3.4 와 2.3.5 의 조건을 만족하게 설계 한 경우, 적합으로 함 2.3.4 외기도입구 (1) 강제 및 자연식 외기 도입구는 배기구, 도로, 골목, 주차장 및 하역장과 같이 유해 오염물질 발생지점에서 수평방향으로 최 소 3 m 이상 이격하고, 도로, 골목, 주차장 및 하역장과 같은 오염원으로부터 7 m 상부에 외기도입구를 설치하면 수평이격 거리는 3 m 이하로 유지하도록 설계한 경우 적합으로 함 (2) 외기도입구가 유해물질 배출원의 3 m 내에 위치한 경우 외기 도입구는 유해물질 배출원에서 최소 1 m 이상 수직 이격한 경 우 적합으로 함 (4) 외부에 면하는 외기 도입구와 배기구는 교차오염을 방지하기 위하여, 1.5 m 이상의 이격거리를 확보하거나 이격거리가 짧 은 경우, 외기도입구와 배기구의 방향이 90° 이상 변경된 위치 에 설치한 경우 적합으로 함 2.3.5 배기구는 아래 조건을 만족하는 경우 적합으로 함 (1) 폭발성 또는 인화성의 증기, 악취가스 및 분진의 배기구 ① 건물경계선에서 9 m 이격 ② 인입 개구부에서 3 m 이격 ③ 외부벽체, 지붕에서 1.8 m 이격 ④ 배기방향에 직면한 가연성 벽체 및 외기도입구에서 9 m 이 격 ⑤ 인접 지면 상부에서 3 m 이격 (2) 일반 건물 배기구 ① 건물 경계선에서 0.9 m ② 건물 출입문에서 0.9 m ③ 기계식 강제 외기도입구에서 3 m 「건축물의 설비기준 등에 관한 규칙」_제 11 조제 3 항 별표 1 의 4 및 별표 1 의 5 (개정안) 공동주택의 보일러 배기통의 돌출길이는 돌출면으로부터 수직거 리로부터 0.5m 이상이어야 하며 자연 기계환기설비의 흡기구의 이격거리는 1.2m 이상확보해야 한다. 또한 교차오염을 방지하기 위하여 0.6m 이상 이격거리를 확보해야 하며, 흡입구와 배기구의 방향이 서로 90 도 이상의 각도가 되는 위치에 설치해야 한다. [도면] 2.3.4 외기도입구와 2.3.5 배기구 기준에 따라 설계도면(배치도, 옥외평면도, 입면도, 단면도, 상세도 등)에서 세부항목별로 적합하게 적 용되었는지 확인 ¦ [별표 9] 2.3.4 2.3.5 「건축물의 설비기준 등에 관한 규칙」 제 11 조제 3 항 별표 1 의 4 및 별표 1 의 5 ¦ 설계도면(배치도/ 평면도/입면도/상 세도 등) ¦ ※ 모든 항목은 기계설비감리업무수행자의 확인을 받아 관련항목이 적합하다고 인정받는 경우, 적합으로 함. 국토교통부 43 기계설비 기술기준 판단기준 | {}
5f066585-d7db-440b-8597-b5a4f4b2cab2 | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 10] 보온설비의 착공 전 확인 적합/부적합 판단기준 ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ 2.2 2.3 2.4 의 조건에 만족하도록 배관, 덕트, 장비에 보온설비를 적용 한 경우 적합으로 함 2.2.1 보랭용 기기 보온두께는 표 1 을 만족하는 경우 적합으로 함 2.2.2 보온용 기기 보온두께는 표 2 을 만족하는 경우 적합으로 함 2.2.3 급수탱크류의 보온두께는 표 3 을 만족하는 경우 적합으로 함 2.3.1 냉수관 및 냉온수관의 보온두께는 표 4, 표 5 를 만족하는 경우 적합으로 함 2.3.2 냉매배관의 보온두께는 표 6 을 만족하는 경우 적합으로 함 2.3.3 급수관 및 배수관의 보온두께는 표 7 을 만족하는 경우 적합 으로 함 2.3.4 급탕관, 온수관, 증기관의 보온두께는 표 8 을 만족하는 경우 적합으로 함 2.4.1 장방형 및 원형덕트의 보온두께는 표 9 를 만족하는 경우 적 합으로 함 2.4.2 제연덕트의 보온두께는 표 10 을 만족하는 경우 적합으로 함 [시방서] 시방서에 기술기준 2.2, 2.3, 2.4 의 보온두께 기준이 명기되 어 있는지 확인 ¦ [별표 10] 2.2 2.3 2.4 ¦ 시방서 ¦ ¦ 2 ¦ 수도계량기 보호함의 보온설비 설치기준은 「건축물의 설비기준 등 에 관한 규칙」제 18 조제 3 호 및 별표 3 의 2 에 따랐을 경우 적합으로 함 「건축물의 설비기준 등에 관한 규칙」 [별표 3 의 2] 급수관 및 수도 계량기보호함의 설치기준(제 18 조제 3 호관련) 1. 급수관의 단열재 두께(단위 : mm) 20 50 70 DN 이상 이상 이상 20 100 설치장소 ~ ~ ~ 미만 이상 50 70 100 설계용 외기온도(°C) ·외기에 미만 미만 미만 노출된 배관 200 50 25 25 25 -10 미만 옥상 등 (50) (25) (25) (25) (25) 그밖에 100 40 25 25 25 동파가 -5 미만 ~ -10 (50) (25) (25) (25) (25) 우려되는 40 25 25 25 25 건축물의 0 미만 ~ -5 (25) (25) (25) (25) (25) 부위 0 이상 유지 20 1) ( )은 기온강하에 따라 자동으로 작동하는 전기 발열선이 설치하는 경우 단열재의 두께를 완화할 수 있는 기준 2) 단열재의 열전도율은 0.04 kcal/m2·h·°C 이하인 것으로 한국산업표준제품을 사용할 것 3) 설계용 외기온도:법 제 59 조제 2 항의 규정에 의한 에너지 절약설계기준에 따를 것 ¦ [별표 10] 2.3.5 ¦ 시방서 ¦ 44 기계설비 기술기준 매뉴얼 | {}
80e57946-4b7c-4af2-9597-ca8a04672c02 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ 2. 수도계량기보호함(난방공간내에 설치하는 것을 제외한다) 가. 수도계량기와 지수밸브 및 역지밸브를 지중 혹은 공동주택 의 벽면 내부에 설치하는 경우에는 콘크리트 또는 합성수 지제 등의 보호함에 넣어 보호할 것 나. 보호함 내 옆면 및 뒷면과 전면판에 각각 단열재를 부착할 것(단열재는 밀도가 높고 열전도율이 낮은 것으로 한국산업 표준제품을 사용할 것) 다. 보호함의 배관입출구는 단열재 등으로 밀폐하여 냉기의 침 입이 없도록 할 것 라. 보온용 단열재와 계량기 사이 공간을 유리섬유 등 보온재로 채울 것 마. 보호통과 벽체사이틈을 밀봉재 등으로 채워 냉기의 침투를 방지할 것 [시방서] 수도계량기 보호함이 있을 경우, 시방서에 관련기준이 명기 되어 있는지 확인 ¦ ¦ ¦ ¦ 3 ¦ 동파방지 발열선 설치 시 2.5 의 조건에 만족하는 경우 적합으로 함 2.5.2 발열선의 구조 (1) 발열선은 연속병렬 저항체로서 온도변화에 따라 자동으로 발열 량이 조절되는 기능을 갖는 자율온도 제어형 정온전선일 경우 적합으로 함 (3) 발열선은 KC, UL, FM, EX 표시 시스템인증제품 또는 동등 이상 의 시스템인증제품일 경우 적합으로 함 2.5.3 배관의 동파방지와 에너지절감을 위하여 발열선의 주위 온도 감지기능, 작동온도 조절기능 및 작동상태 표시기능 등을 갖추었을 경우 적합으로 함 [도면/시방서] 동파방지 발열선 설치 시 시방서 또는 설계도면(동파 방지 열선 상세도)에서 2.5 의 세부항목을 명기하였는지 확인 ¦ [별표 10] 2.5.2 2.5.3 ¦ 시방서, 설계도면 ¦ ※ 모든 항목은 기계설비감리업무수행자의 확인을 받아 관련항목이 적합하다고 인정받는 경우, 적합으로 함. 국토교통부 45 기계설비 기술기준 판단기준 | {}
fb96dc61-ebcc-4d6e-b9af-749f6c0016b7 | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 11] 자동제어설비의 착공 전 확인 적합/부적합 판단기준 ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ 기계설비의 운전상태를 확인할 수 있는 현장제어반을 설치하고 중앙 제어반으로 데이터 전송이 가능하도록 설계한 경우 적합으로 함 [도면] 자동제어 계통도 및 평면도에서 기계설비의 운전상태를 확인할 수 있는 현장제어반을 설치하고 중앙제어반으로 데이터 전송이 가능 하도록 설계하였는지 확인 ¦ [별표 11] 2.2.1 ¦ 설계도면 ¦ ¦ 2 ¦ 원격검침을 설치할 경우, 전력 사용량, 수도 사용량, 가스 사용량, 열사 용량 등을 검침할 수 있도록 설계한 경우 적합으로 함 [도면] 원격검침 설치 시 원격검침 관련 평면도 및 상세도에서 전력 사 용량, 수도 사용량, 가스 사용량, 열사용량 등 중 한 가지 이상을 검침 할 수 있는지 확인 ¦ [별표 11] 2.5.1 ¦ 설계도면 ¦ ※ 모든 항목은 기계설비감리업무수행자의 확인을 받아 관련항목이 적합하다고 인정받는 경우, 적합으로 함. 46 기계설비 기술기준 매뉴얼 | {}
9ad327c0-eaaa-4b42-9ba3-055e734ec238 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 [별표 12] 방음 · 방진 · 내진설비의 착공 전 확인 적합/부적합 판단기준 ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ 방음·방진·내진설비 적용 시 2.1~ 2.3 의 조건에 만족하는 경우 적합으 로 함 2.1 방음설비 (2) KCS 31 50 10 05(1.1) 표 1.1-1 에 따른 표 1 의 NC 실내허용 소음기준에 따른 중심주파수별 값 이하가 유지될 수 있도록 방음설비(흡음형소음기, 소음챔버, 능동형소음기, 흡음덕트 등) 를 선정한 경우 적합으로 함 2.3 방진설비 (1) 장비의 강제진동수 및 장비발생진동레벨은 제조사의 강제진동 수 및 장비발생진동레벨을 기준으로 설계한 경우 적합으로 함 2.4 내진설비 (3) 내진설비 설계의 적정성은「건축법」시행령 제 91 조의 3 제 2 항 제 2 호에 따른 관계전문기술자와 협의 해야 하며, 내진설계 책 임구조기술사가 승인하였을 경우 적합으로 함 [승인서/계산서] 방음방진설비 적용 시 기술기준 2.1~2.3 의 세부항목 을 시방서, 설계도면, 계산서 등에서 적합하게 설계하였는지 확인 > 2.1(2) 실내허용소음기준을 만족하는 소음측정보고서 > 2.3(1) 방진 계산서에서 관련내용 확인 > 2.4(3) 내진설계 책임구조기술사 승인 확인 ¦ [별표 12] 2.1 2.2 2.3 ¦ 소음측정보고서, 계산서, 승인서 등 ¦ ※ 모든 항목은 기계설비감리업무수행자의 확인을 받아 관련항목이 적합하다고 인정받는 경우, 적합으로 함. 국토교통부 47 기계설비 기술기준 판단기준 | {}
dcc0d865-5889-455b-9481-5e74a6be063e | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 사용 전 확인표 판단기준 [별표 1] 열원 및 냉난방설비의 사용 전 확인표_[별지 제 3 호 서식] ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 1] ¦ [별표 1] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ 열원 및 냉난방설비 ¦ 열원 및 냉난방설비 ¦ ¦ 공 종 ¦ 열원 및 냉난방설비(1/2) ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 자 재 ¦ 주요기자재 선정 및 사용은 적합한가 ¦ 주요기자재 선정 및 사용은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 냉동기, 냉온수기 설치는 기술기준에 적합한가 ¦ 냉동기, 냉온수기 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 보일러 설치는 기술기준에 적합한가 ¦ 보일러 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 항온항습기, 열펌프 설치는 기술기준에 적합한가 ¦ 항온항습기, 열펌프 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 패키지 에어컨 설치는 기술기준에 적합한가 ¦ 패키지 에어컨 설치는 기술기준에 적합한가 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 냉각탑 설치는 기술기준에 적합한가 ¦ 냉각탑 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 펌프 설치는 기술기준에 적합한가 ¦ 펌프 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 열교환기 설치는 기술기준에 적합한가 ¦ 열교환기 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 탱크류 설치는 기술기준에 적합한가 ¦ 탱크류 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 장비별 배관 접속은 기술기준에 적합한가 ¦ 장비별 배관 접속은 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 열원기기의 명판 및 마감상태는 적합한가 ¦ 열원기기의 명판 및 마감상태는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 열원기기류의 작동과 성능은 적합한가 ¦ 열원기기류의 작동과 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 ¦ 확인일 ¦ 확인일 ¦ ¦ 회사명(상호) ¦ ¦ (인) ¦ ¦ ¦ ¦ 회사명(상호) ¦ ¦ ¦ ¦ ¦ ¦ (인) 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 ¦ (인) 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 ¦ (인) 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 ¦ (인) 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 ¦ (인) 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 ¦ 210mmX297mm[백상지 80g/m2 ] 48 기계설비 기술기준 매뉴얼 | {}
b3d27ceb-5dc0-4d10-aacb-e0f183b9d4d9 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 [별표 1] 열원 및 냉난방설비의 사용 전 검사 적합/부적합 판단기준 ¦ ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도서 ¦ 도서 ¦ 열원 및 냉난방설비 관련 준공도서를 모두 확인하였다면 적합으로 함 [준공도서] 준공도서(준공도면, 시방서, 부하 및 장비선정 계산서 등) 가 모두 구비되어 있는 지 확인 ¦ - ¦ 준공도서 ¦ ¦ 자재 ¦ 자재 ¦ 장비일람표, 시방서 등의 설계사항을 반영한 주요 장비 및 기자재 구 매, 반입 및 관련 도서를 확인하고, 설치된 장비의 사양과 규격 일치 여부를 확인하였다면 적합으로 함 [검토서] 설계대로 발주된 주요 장비 및 기자재 자재승인서와 자재검 수요청서 확인하여 일치여부를 기계설비감리업무수행자가 확인한 경우 적합으로 함 ¦ ¦ 검토서(자재승인서, 자재검수요청서 등) ¦ ¦ 시공 ¦ 1-1 ¦ 한국가스안전공사 완성검사 확인서를 확인한 경우 적합으로 함 ¦ [별표 1] 3.2.1 (1) ¦ 한국가스안전공사 완성검사 확인서 ¦ ¦ 시공 ¦ 1-2 ¦ 냉동기에 접속하는 냉각수, 냉수배관에 플렉시블이음을 확인하였다 면 적합으로 함 [도면/사진] 준공도면의 기계실 평면도에서 플렉시블 이음을 확인하 고, 설치된 사진을 기계설비감리업무수행자가 확인한 경우 적합으로 함 ¦ [별표 1] 3.2.1 (3) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 2-1 ¦ 이 기준 개별 보일러를 설치한 경우, 일산화탄소 경보기를 정상적으 로 설치한 경우 적합으로 함 [도면/사진] 준공도면의 보일러실 평면도/상세도에서 일산화탄소 경 보기 설치를 확인하고, 설치된 사진 첨부 확인 ¦ [별표 1] 3.5 (4) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 2-2 ¦ 연도의 이음에 내열성 있는 재질을 적용한 경우 적합으로 함 [검토서] 준공도면의 연도 평면도/상세도 및 시방서에서 이음의 재질 관련 부분 확인하고, 설치된 사진을 기계설비감리업무수행자가 확인 한 경우 적합으로 함 ¦ [별표 1] 3.5.1 ¦ 검토서(준공도면, 시방서, 현장사진 등) ¦ ¦ 시공 ¦ 3-1 ¦ 실외기 설치 상태가 「환경정책기본법」 시행령 [별표 1]의 소음기준 을 만족하는 경우 적합으로 함 [보고서] 「환경정책기본법」 시행령 [별표 1]에서 지역구분/적용대상 지역에 따라서 낮과 밤의 소음 측정자료 확인 ¦ [별표 1] 3.12 (1) ① ¦ 소음측정보고서 ¦ ¦ 시공 ¦ 3-2 ¦ 실외기 설치금지 조건에 따라 실외기를 적정한 장소에 설치한 경우 를 적합으로 함 [검토서] 3.12 (1) ⑥ 가~라 조건을 설계도면의 실외기 평면도/상세도, 현장 사진 등을 통해 기계설비감리업무수행자가 확인한 경우 적합으로 함 ¦ [별표 1] 3.12 (1) ⑥ ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 3-3 ¦ 실외기 과열 시 자동으로 전원이 차단되도록 실외기 전용의 차단개 폐기를 설치한 경우 적합으로 함 [검토서] 준공도면의 실외기 평면도/상세도에서 차단개폐기를 확인하 고, 설치된 사진 첨부 확인 ¦ [별표 1] 3.12 (1) ⑦ ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 4-1 ¦ 실외기 설치 상태가 「환경정책기본법」 시행령 [별표 1]의 소음기준 을 만족하는 경우 적합으로 함 [보고서] 「환경정책기본법」 시행령 [별표 1]에서 지역구분/적용대상 지역에 따라서 낮과 밤의 소음 측정자료 확인 ¦ [별표 1] 3.12 (1) ① ¦ 소음측정보고서 ¦ ¦ 시공 ¦ 4-2 ¦ 실외기 설치금지 조건에 따라 실외기를 적정한 장소에 설치한 경우 를 적합으로 함 [검토서] 3.12 (1) ⑥ 가~라 조건을 설계도면의 실외기 평면도/상세도, 현장 사진 등을 통해 기계설비감리업무수행자가 확인한 경우 적합으로 함 ¦ [별표 1] 3.12 (1) ⑥ ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 4-3 ¦ 실외기 과열 시 자동으로 전원이 차단되도록 실외기 전용의 차단개 폐기를 설치한 경우 적합으로 함 [검토서] 실외기 평면도/상세도에서 차단개폐기를 확인하고, 설치된 사진 첨부 확인 ¦ [별표 1] 3.12 (1) ⑦ ¦ 검토서(준공도면, 현장사진 등) ¦ 국토교통부 49 기계설비 기술기준 판단기준 | {}
a0d91d6a-0e2d-4b4b-bb46-a0943f064613 | 국내_기계설비_기술기준_매뉴얼_최종본 | ¦ ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ 5 ¦ 표면을 모르타르로 마감한 콘크리트기초 또는 형강제 받침대 위에 자중, 적설, 풍압, 지진 기타의 진동에 대하여 안전하게 냉각탑을 시 공한 경우 적합으로 함 [도면/사진] 준공도면의 냉각탑 설치상세도에서 관련사항을 확인하 고 설치된 사진 첨부 확인 ¦ [별표 1] 3.3 (1) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 6 ¦ 펌프 기초를 윗면 주위의 배수 홈에 배수구를 설치하고 DN 32 이상 의 배관으로 배수관에 간접배수되도록 시공한 경우 적합으로 함 [검토서] 준공도면의 공조실 배관평면도에서 관련사항을 확인하고 설치된 사진 첨부 확인 ¦ [별표 1] 3.8 (1) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ ¦ 7 ¦ 「안전검사 고시」 및 「열사용기자재의 검사 및 검사면제에 관한 기 준」을 검사하여 통과 한 경우 적합으로 함 ¦ [별표 1] 3.6 (1) ¦ 열사용기자재 검사 확인서 ¦ ¦ ¦ 8 ¦ 콘크리트제 또는 철제베드 위에 안전하고 견고하게 설치한 경우 적 합으로 함 [검토서] 준공도면의 기계실 및 저수조실 평면도/상세도에서 관련사 항을 확인하고 설치된 사진 첨부 확인 ¦ [별표 1] 3.7 (2) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ ¦ 9 ¦ [별표 8] 배관설비의 사용 전 확인표를 만족할 경우, 적합으로 함 ¦ [별표 8] ¦ ¦ ¦ ¦ 10 ¦ 「기계설비 유지관리기준」 [별지 제 1 호서식] 기계설비 유지관리 및 성능점검 대상 현황표에 기록해야 하는 내용이 명판에 반영되어 있 으며, 마감상태가 식별이 용이한 것을 확인한 경우 적합으로 함 [검토서] 열원장비 명판과 장비일람표의 세부사양을 확인하고, 설치 된 사진 첨부 확인 ¦ ¦ 검토서(장비일람 표, 현장사진 등) ¦ ¦ ¦ 성능 ¦ 1 ¦ 시운전을 실시하고 작동 상태와 성능 기준이 만족한 경우 적합으로 함. 다만, 냉방 또는 난방설비로 계절상(부하가 없어) 성능확인이 불가할 경우에는 제조사의 성능시험성적서 확인으로 갈음하고, 「기계설비 유지관리기준」 제 6 조에 따른 유지관리지침서에 관련 정보를 반영하 여 해당 설비의 성능점검 시 해당 설비의 점검이 우선 실시될 수 있 도록 함 [시운전보고서] 시운전 시 기계설비감리업무수행자가 적합여부 확인 한 경우, 적합으로 함 ¦ ¦ 시운전보고서 ¦ ¦ 성능 ¦ 2 ¦ 성능시험 성적서 발행기관의 적정성, 성적서의 유효기간 등이 만족 한 경우 적합으로 함 [시험성적서] 제출된 시험성적서의 적정성, 유효기간 등을 확인 ¦ - ¦ 시험성적서 ¦ ¦ 유지 관리 ¦ 1 ¦ 「기계설비 유지관리기준」 제 6 조제 2 항 기계설비 시스템 운용 매뉴얼 (기계설비 제조사의 검사사 또는 성적서 포함, 열원 및 냉난방설비)을 갖춘 경우 적합으로 함 [매뉴얼] 기계설비 시스템 운용 매뉴얼에서 열원설비 목차 및 내용 확인 ¦ ¦ 기계설비 시스템 운용 매뉴얼 ¦ ¦ 유지 관리 ¦ 2 ¦ [별표 15] 2.기계설비 유지관리 공간의 조건을 만족할 경우 적합으로 함 [검토서] 준공도면의 기계실/공조실 평면도, 샤프트 상세도 등에서 장비 및 기기별 이격거리 및 공간 확보 등의 조건과 설치된 사진을 기계설비감리업무수행자가 확인한 경우 적합으로 함 ¦ [별표 15] 2. ¦ 검토서(준공도면, 현장사진 등) ¦ ※ 모든 항목은 기계설비감리업무수행자의 확인을 받아 관련항목이 적합하다고 인정받는 경우, 적합으로 함 ※ 판단기준 조건을 만족하는 서류(ex 감리관련서류, 관련 용역보고서 등)가 있을 경우, 필요서류를 대체할 수 있음 50 기계설비 기술기준 매뉴얼 | {}
c88b6dd0-63a8-4806-9138-0066fc729359 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 [별표 1-2] 신재생에너지설비의 사용 전 확인표_[별지 제 3 호 서식] ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 1] ¦ [별표 1] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ 신재생에너지설비 ¦ 신재생에너지설비 ¦ ¦ 공 종 ¦ 열원 및 냉난방설비(2/2) ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 자 재 ¦ 주요기자재 선정 및 사용은 적합한가 ¦ 주요기자재 선정 및 사용은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 지열 설비의 설치는 기술기준에 적합한가 ¦ 지열 설비의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 태양열 설비의 설치는 기술기준에 적합한가 ¦ 태양열 설비의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 연료전지 설비의 설치는 기술기준에 적합한가 ¦ 연료전지 설비의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 배관 계통과 장비의 연결 상태는 기술기준에 적합한가 ¦ 배관 계통과 장비의 연결 상태는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 탱크류(급수, 급탕, 팽창탱크 등)의 설치는 기술기준에 적합한가 ¦ 탱크류(급수, 급탕, 팽창탱크 등)의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 밸브류, 기기류 설치는 기술기준에 적합한가 ¦ 밸브류, 기기류 설치는 기술기준에 적합한가 ¦ [ ] ¦ - ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 연료전지실의 환기설비 설치는 기술기준에 적합한가 ¦ 연료전지실의 환기설비 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 동파방지, 과열방지 등의 조치는 기술기준에 적합한가 ¦ 동파방지, 과열방지 등의 조치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 장비명판, 계통도 표지 등 마감상태는 기술기준에 적합한가 ¦ 장비명판, 계통도 표지 등 마감상태는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 신재생(지열, 태양열, 연료전지) 설비의 작동과 성능은 적합한가 ¦ 신재생(지열, 태양열, 연료전지) 설비의 작동과 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 ¦ 확인일 ¦ 확인일 ¦ ¦ 회사명(상호) ¦ (인) ¦ ¦ ¦ ¦ ¦ 회사명(상호) (인) ¦ ¦ ¦ ¦ ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/ m2 ] 국토교통부 51 기계설비 기술기준 판단기준 | {}
e0d4c311-2c0d-470e-8ddc-072af2a9fb92 | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 1-2] 신재생에너지설비의 사용 전 검사 적합/부적합 판단기준 ¦ ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도서 ¦ 도서 ¦ 신재생설비 관련 준공도서를 모두 확인하였다면 적합으로 함 [준공도서] 준공도서(준공도면, 시방서, 부하 및 장비선정 계산서 등) 가 모두 구비되어 있는 지 확인 ¦ - ¦ 준공도서 ¦ ¦ 자재 ¦ 자재 ¦ 장비일람표, 시방서 등의 설계사항을 반영한 주요 장비 및 기자재 구 매, 반입 및 관련 도서를 확인하고, 설치된 장비의 사양과 규격 일치 여부를 확인하였다면 적합으로 함 [검토서] 설계대로 발주된 주요 장비 및 기자재 자재승인서와 자재검 수요청서 확인하여 일치여부를 기계설비감리업무수행자가 확인한 경우 적합으로 함 ¦ ¦ 검토서(자재승인서, 자재검수요청서 등) ¦ ¦ 시공 ¦ 1-1 ¦ 지열원 열펌프 중 「고압가스안전관리법」의 적용을 받는 장비는 해당 법률에 따라 한국가스안전공사의 시험을 합격한 경우 적합으로 함 ¦ [별표 1] 3.9 (1) ② ¦ 한국가스안전공사 시험합격 확인서 ¦ ¦ 시공 ¦ 1-2 ¦ 천공완료 후 케이싱을 제거하지 않을 경우, 지표수가 유입되지 않도 록 조치한 경우 적합으로 함 [검토서] 지열천공부분에 지표수가 유입되지 않도록 잘 마감하였는 지 사진 등을 통해 기계설비감리업무수행자가 확인한 경우 적합으로 함 ¦ [별표 1] 3.9 (2) ③ ¦ 검토서 (현장사진 등) ¦ ¦ 시공 ¦ 2-1 ¦ 유지보수를 위한 공간을 두거나 안전을 고려한 발판과 안전난간을 설치한 경우 적합으로 함 [검토서] 준공도서의 태양열 설비 평면도/상세도에서 유지관리공간 및 안전발판/안전난간(필요 시)을 확인하고, 설치된 사진 첨부 확인 ¦ [별표 1] 3.10 (1) ③ ¦ 검토서 (준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 2-2 ¦ 집열기 설치가대는 집열기 하단부가 설치면으로부터 150 mm 이상 높이로 설치한 경우 적합으로 함 [검토서] 준공도서의 태양열 설비 상세도에서 설치면 높이를 확인하 고, 설치된 사진 첨부 확인 ¦ [별표 1] 3.10 (4) ② ¦ 검토서 (준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 3 ¦ 연료전지 주위로 급수유량을 배수할 수 있는 배수구를 설치한 경우 적합으로 함 [검토서] 준공도서의 연료전지 관련 평면도에서 배수구를 설치를 확 인하고, 설치된 사진 첨부 확인 ¦ [별표 1] 3.11 (3) ¦ 검토서 (준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 4 ¦ [별표 8] 배관설비의 사용 전 확인표를 만족할 경우, 적합으로 함 ¦ [별표 8] ¦ ¦ ¦ 시공 ¦ 5 ¦ 태양열 시스템의 경우, 모든 펌프를 고효율 인증제품으로 사용하고 인증제품이 없는 경우 KS 표준 규격 및 동등이상의 제품을 사용한 경 우 적합으로 함 [검토서] 준공도서의 태양열 설비 모든 펌프의 고효율 인증제품 확인 서 확인 또는 장비일람표 혹은 자재승인서에서 KS 표준 규격 동등 이 상 제품을 기계설비감리업무수행자가 확인한 경우 적합으로 함 ¦ [별표 1] 3.10 (3) ③ ¦ 검토서 (장비일람표, 자재승인서) ¦ ¦ 시공 ¦ 6 ¦ [별표 8] 배관설비의 사용 전 확인표를 만족할 경우, 적합으로 함 ¦ [별표 8] ¦ - ¦ ¦ 시공 ¦ 7 ¦ 건축물 내부로 배기가스 유입방지 조치를 하고, 연료전지실 내부의 환기설비를 설치한 경우 적합으로 함 [검토서] 준공도서의 연료전지실 평면도/상세도에서 관련내용을 확 인하고 설치된 사진을 기계설비감리업무수행자가 확인한 경우 적합 으로 함 ¦ [별표 1] 3.11 (1) ¦ 검토서 (준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 8 ¦ 태양열 시스템의 경우, 과열방지 및 동파방지 대책을 마련한 경우, 적 합으로 함 [검토서] 준공도서의 태양열 설비의 평면도/상세도에서 관련내용을 확인하고 설치된 사진을 기계설비감리업무수행자가 확인한 경우 적 합으로 함 ¦ [별표 1] 3.10.(5) ① ¦ 검토서 (준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 9 ¦ 「기계설비 유지관리기준」 [별지 제 1 호서식] 기계설비 유지관리 및 성능점검 대상 현황표에 기록해야 하는 내용이 명판에 반영되어 있 ¦ - ¦ 검토서 (준공도서, ¦ 52 기계설비 기술기준 매뉴얼 | {}
36ce7e06-c08a-4792-89d0-5f8a376f72aa | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 ¦ ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ ¦ 으며, 마감상태가 식별이 용이한 것을 확인한 경우 적합으로 함 [검토서] 열원장비 명판과 장비일람표의 세부사양을 확인하고, 사진 첨부 확인 ¦ ¦ 현장사진 등) ¦ ¦ 성능 ¦ 1 ¦ 시운전을 실시하고 작동 상태와 성능 기준이 만족한 경우 적합으로 함. 다만, 냉방 또는 난방설비로 계절상(부하가 없어) 성능확인이 불 가할 경우에는 제조사의 성능시험성적서 확인으로 갈음하고, 「기계 설비 유지관리기준」 제 6 조에 따른 유지관리지침서에 관련 정보를 반 영하여 해당 설비의 성능점검 시 해당 설비의 점검이 우선 실시될 수 있도록 함 [시운전보고서] 시운전 시 기계설비감리업무수행자가 적합여부 확인 한 경우, 적합으로 함 ¦ ¦ 시운전보고서 ¦ ¦ 성능 ¦ 2 ¦ 성능시험 성적서 발행기관의 적정성, 성적서의 유효기간 등이 만족 한 경우 적합으로 함 [시험성적서] 제출된 시험성적서의 적정성, 유효기간 등을 확인 ¦ ¦ 시험성적서 ¦ ¦ 유지 관리 ¦ 1 ¦ 「기계설비 유지관리기준」 제 6 조제 2 항 기계설비 시스템 운용 매뉴얼 (기계설비 제조사의 검사결과 또는 성적서 포함, 신재생에너지 설비) 을 갖춘 경우 적합으로 함 [매뉴얼] 기계설비 시스템 운용 매뉴얼에서 신재생설비 목차 및 내용 확인 ¦ ¦ 기계설비 시스템 운용 매뉴얼 ¦ ¦ 유지 관리 ¦ 2 ¦ [별표 15] 2.기계설비 유지관리 공간의 조건을 만족할 경우 적합으로 함 [검토서] 준공도면의 기계실/공조실 평면도, 샤프트 상세도 등에서 장비 및 기기별 이격거리 및 공간 확보 등의 조건과 설치된 사진을 기계설비감리업무수행자가 확인한 경우 적합으로 함 ¦ [별표 15] 2. ¦ 검토서(준공도면, 현장사진 등) ¦ ※ 모든 항목은 기계설비감리업무수행자의 확인을 받아 관련항목이 적합하다고 인정받는 경우, 적합으로 함 ※ 판단기준 조건을 만족하는 서류(ex 감리관련서류, 관련 용역보고서 등)가 있을 경우, 필요서류를 대체할 수 있음 기계설비 기술기준 판단기준 국토교통부 53 | {}
b8959fab-c8a3-420c-9819-6856932fd3a1 | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 2] 공기조화설비의 사용 전 확인표_[별지 제 3 호 서식] ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 2] ¦ [별표 2] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ 공기조화설비 ¦ 공기조화설비 ¦ ¦ 공 종 ¦ 공기조화설비 ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ ] ¦ [] 적합 [ ] 부적합 ¦ ¦ 자 재 ¦ 주요기자재 선정 및 사용은 적합한가 ¦ 주요기자재 선정 및 사용은 적합한가 ¦ [ I ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 공기조화기의 설치는 기술기준에 적합한가 ¦ 공기조화기의 설치는 기술기준에 적합한가 ¦ [ ] ¦ - ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 팬코일유닛의 설치는 기술기준에 적합한가 ¦ 팬코일유닛의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 방열기의 설치는 기술기준에 적합한가 ¦ 방열기의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 온수온돌난방의 설치는 기술기준에 적합한가 ¦ 온수온돌난방의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 배관 및 덕트 등의 연결상태는 기술기준에 적합한가 ¦ 배관 및 덕트 등의 연결상태는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 밸브 및 계측기기류 설치는 기술기준에 적합한가 ¦ 밸브 및 계측기기류 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 보온 및 마감상태는 기술기준에 적합한가 ¦ 보온 및 마감상태는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 공기조화기의 작동은 적합한가 ¦ 공기조화기의 작동은 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 온수온돌난방설비의 공기빼기작동은 적합한가 ¦ 온수온돌난방설비의 공기빼기작동은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 ¦ 확인일 ¦ 확인일 ¦ ¦ 회사명(상호) ¦ ¦ ¦ (인) ¦ (인) ¦ ¦ 회사명(상호) (인) ¦ ¦ ¦ ¦ ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/m2 ] 54 기계설비 기술기준 매뉴얼 | {}
676d0573-3f64-4086-b0c2-937a63f4b706 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 [별표 2] 공기조화설비의 사용 전 검사 적합/부적합 판단기준 ¦ ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도서 ¦ 도서 ¦ 공기조화설비 관련 준공도서를 모두 확인하였다면 적합으로 함 [준공도서] 준공도서(준공도면, 시방서, 부하 및 장비선정 계산서 등) 가 모두 구비되어 있는 지 확인 ¦ ¦ 준공도서 ¦ ¦ 자재 ¦ 자재 ¦ 장비일람표, 시방서 등의 설계사항을 반영한 주요 장비 및 기자재 구 매, 반입 및 관련 도서를 확인하고, 설치된 장비의 사양과 규격 일치 여부를 확인하였다면 적합으로 함 [검토서] 설계대로 발주된 주요 장비 및 기자재 자재승인서와 자재검 수요청서 확인하여 일치여부를 기계설비감리업무수행자가 확인한 경우 적합으로 함 ¦ ¦ 검토서(자재승인서, 자재검수요청서 등) ¦ ¦ 시공 ¦ 1 ¦ 공기조화기 배수판의 물은 간접배수로 하였다면 적합으로 함 [검토서] 준공도서의 공기조화기 기계실 평면도에서 간접배수를 확 인하고 설치된 사진 첨부 확인 ¦ [별표 2] 3.1 (1) ¦ 검토서(현장도면, 현장사진 등) ¦ ¦ 시공 ¦ 2 ¦ 팬코일유니트가 벽 또는 바닥에 견고하게 설치하였다면 적합으로 함 [검토서] 준공도서의 공조배관 평면도/상세도 등에서 팬코일 유니트 를 확인하고 설치된 사진을 통해 견고하게 설치됨을 확인 ¦ [별표 2] 3.2 ¦ 검토서(현장도면, 현장사진 등) ¦ ¦ 시공 ¦ 3 ¦ 바닥설치형 방열기는 벽면으로부터 60 mm 이상 간격을 두고 설치하였 다면 적합으로 함 [검토서] 준공도서의 공조배관 평면도/상세도 등에서 방열기가 벽면으 로부터 60 mm 이상 간격을 두었는지 확인하고, 설치된 사진 첨부 확인 ¦ [별표 2] 3.4 (1) ¦ 검토서(현장도면, 현장사진 등) ¦ ¦ 시공 ¦ 4 ¦ 공기체류가 예상되는 부분에는 공기빼기밸브를 설치하였다면 적합 으로 함 [검토서] 준공도서의 공조배관 평면도/계통도 등에서 공기체류가 예 상되는 부분의 공기빼기밸브 설계도와 설치된 사진을 기계설비감리 업무수행자가 확인하는 경우 적합으로 함 ¦ [별표 2] 3.5 (3) ¦ 검토서(현장도면, 현장사진 등) ¦ ¦ 시공 ¦ 5 ¦ [별표 8] 배관설비의 사용 전 확인표를 만족할 경우, 적합으로 함 [별표 9] 덕트설비의 사용 전 확인표를 만족할 경우, 적합으로 함 ¦ [별표 8] [별표 9] ¦ - ¦ ¦ 시공 ¦ 6 ¦ [별표 8] 배관설비의 사용 전 확인표를 만족할 경우, 적합으로 함 ¦ [별표 8] ¦ - ¦ ¦ 시공 ¦ 7 ¦ [별표 10] 보온설비의 사용 전 확인표를 만족할 경우, 적합으로 함 ¦ [별표 10] ¦ - ¦ ¦ 성능 ¦ 1 ¦ 시운전을 실시하고 작동 상태와 성능 기준이 만족한 경우 적합으로 함. 다만, 냉방 또는 난방설비로 계절상(부하가 없어) 성능확인이 불가할 경우에는 제조사의 성능시험성적서 확인으로 갈음하고, 「기계설비 유 지관리기준」 제 6 조에 따른 유지관리지침서에 관련 정보를 반영하여 해 당 설비의 성능점검 시 해당 설비의 점검이 우선 실시될 수 있도록 함 [시운전보고서] 시운전 시 기계설비감리업무수행자가 적합여부 확인한 경우, 적합으로 함 ¦ ¦ 시운전보고서 ¦ ¦ 성능 ¦ 2 ¦ 온수온돌난방설비의 공기빼기밸브가 정상작동하는 경우, 적합으로 함 [검토서] 온수온돌난방설비에 공기빼기밸브가 설계된 경우, 정상작동 여부를 기계설비감리업무수행자가 확인한 경우 적합으로 함 ¦ - ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 성능 ¦ 3 ¦ 성능시험 성적서 발행기관의 적정성, 성적서의 유효기간 등이 만족 한 경우 적합으로 함 [시험성적서] 제출된 시험성적서의 적정성, 유효기간 등을 확인 ¦ ¦ 시험성적서 ¦ ¦ 유지 관리 ¦ 1 ¦ 「기계설비 유지관리기준」 제 6 조제 2 항 기계설비 시스템 운용 매뉴얼 (기계설비 제조사의 검사결과 또는 성적서 포함, 공기조화설비)을 갖 춘 경우 적합으로 함 [매뉴얼] 기계설비 시스템 운용 매뉴얼에서 공기조화설비 목차 및 내용 확인 ¦ ¦ 기계설비 시스템 운용 매뉴얼 ¦ ¦ 유지 관리 ¦ 2 ¦ [별표 15] 2.기계설비 유지관리 공간의 조건을 만족할 경우 적합으로 함 [검토서] 준공도면의 기계실/공조실 평면도, 샤프트 상세도 등에서 장비 및 기기별 이격거리 및 공간 확보 등의 조건과 설치된 사진을 기계설비감리업무수행자가 확인한 경우 적합으로 함 ¦ [별표 15] 2. ¦ 검토서(준공도면, 현장사진 등) ¦ ※ 모든 항목은 기계설비감리업무수행자의 확인을 받아 관련항목이 적합하다고 인정받는 경우, 적합으로 함 ※ 판단기준 조건을 만족하는 서류(ex 감리관련서류, 관련 용역보고서 등)가 있을 경우, 필요서류를 대체할 수 있음 국토교통부 55 기계설비 기술기준 판단기준 | {}
a13d55fc-13da-441b-8cb7-d03134de18ed | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 3] 환기설비의 사용 전 확인표_[별지 제 3 호 서식] ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 3] 환기설비 ¦ [별표 3] 환기설비 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 공 종 ¦ 환기설비 ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ ] ¦ [] 적합 [ ] 부적합 ¦ ¦ 자 재 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 송풍기의 설치는 기술기준에 적합한가 ¦ 송풍기의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 열회수형 환기장치의 설치는 기술기준에 적합한가 ¦ 열회수형 환기장치의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 주차장 배기송풍기는 기술기준에 적합한가 ¦ 주차장 배기송풍기는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 송풍기의 방진장치 설치는 기술기준에 적합한가 ¦ 송풍기의 방진장치 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 환기장치의 공기흡입구와 배기구 설치는 기술기준에 적합한가 ¦ 환기장치의 공기흡입구와 배기구 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 송풍기와 덕트 등의 연결상태는 기술기준에 적합한가 ¦ 송풍기와 덕트 등의 연결상태는 기술기준에 적합한가 ¦ [ 1 ¦ [ ] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 송풍기의 작동과 성능은 적합한가 ¦ 송풍기의 작동과 성능은 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 ¦ 확인일 ¦ 확인일 ¦ ¦ 회사명(상호) ¦ ¦ (인) ¦ ¦ ¦ ¦ 회사명(상호) ¦ ¦ (인) ¦ ¦ ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/m2] 56 기계설비 기술기준 매뉴얼 | {}
466c06b0-3f76-4819-a0a7-a0bc06dfd92b | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 [별표 3] 환기설비의 사용 전 검사 적합/부적합 판단기준 ¦ ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도서 ¦ 도서 ¦ 환기설비 관련 준공도서를 모두 확인하였다면 적합으로 함 [준공도서] 준공도서(준공도면, 시방서, 부하 및 장비선정 계산서 등) 가 모두 구비되어 있는 지 확인 ¦ - ¦ 준공도서 ¦ ¦ 자재 ¦ 자재 ¦ 장비일람표, 시방서 등의 설계사항을 반영한 주요 장비 및 기자재 구 매, 반입 및 관련 도서를 확인하고, 설치된 장비의 사양과 규격 일치 여부를 확인하였다면 적합으로 함 [검토서] 설계대로 발주된 주요 장비 및 기자재 자재승인서와 자재검 수요청서 확인하여 일치여부를 기계설비감리업무수행자가 확인한 경우 적합으로 함 ¦ ¦ 검토서(자재승인서, 자재검수요청서 등) ¦ ¦ 시공 ¦ 1-1 ¦ 바닥설치형의 경우 콘크리트 기초 또는 형강제 베드 위에 직접 고정하 거나, 방진재를 사용한 방진구조 위에 설치한 경우 적합으로 함 [검토서] 준공도서의 공조실 평면도/상세도에서 기초를 확인하고, 설 치된 사진 첨부 확인 ¦ [별표 3] 3.1 (1) ¦ 검토서 (준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 1-2 ¦ 환기 및 제연 겸용으로 사용하는 송풍기(지하주차장 등)는 필요에 따라 자동조절하거나 대수제어 가능한 환기시스템을 구성한 경우 적합으로 함 [검토서] 준공도서의 장비일람표에서 환기 및 제연겸용 송풍기가 인 버터 제어나 대수제어 가능하게도록 구성하였는지 확인하고, 설치된 사진 첨부 확인 ¦ [별표 3] 3.1 (4) ¦ 검토서 (장비일람표, 현장사진 등) ¦ ¦ 시공 ¦ 2-1 ¦ 덕트형 환기장치의 유지관리를 위해 점검구를 설치한 경우, 적합으로 함 [검토서] 준공도서의 공조덕트평면도/상세도 등에서 덕트형 환기장치에 유지관리를 위한 점검구를 설치하였는지 확인하고 설치된 사진 첨부 확인 ¦ [별표 3] 3.2 (2) (3) ¦ 검토서 (준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 2-2 ¦ 환기장치 가동으로 [별표 12] 표 1 실내허용소음기준을 초과 하지 않도 록 설치하여야 적합으로 함 [보고서] 실내허용소음기준에 적합한 소음측정결과 확인 ¦ [별표 3] 3.2 (4) ¦ 소음측정보고서 ¦ ¦ 시공 ¦ 3 ¦ 제연겸용 환기송풍기는 화재시를 대비하여 250°C 에서 60 분 이상 가 동이 가능하도록 설치하면 적합으로 함 [검토서] 준공도서의 장비일람표에서 제연겸용 환기송풍기가 250°C 에 서 60 분 이상 가동이 가능한 제품인지 확인하고, 설치된 사진 첨부 확인 ¦ [별표 3] 2.1.2 (4) ③ ¦ 검토서 (장비일람표, 현장사진, 자재승인서 등) ¦ ¦ 시공 ¦ 4 ¦ [별표 12] 방음·방진·내전설비의 사용 전 확인표를 만족할 경우, 적합 으로 함 ¦ [별표 12] ¦ - ¦ ¦ 시공 ¦ 5 ¦ [별표 9] 덕트설비의 사용 전 확인표를 만족할 경우, 적합으로 함 ¦ [별표 9] ¦ - ¦ ¦ 시공 ¦ 6 ¦ 덕트와 접속하는 송풍기의 흡입측과 토출측에 플렉시블 이음을 설치 하였다면 적합으로 함 [검토서] 준공도면의 공조실 평면도/상세도에서 플렉시블 이음을 확 인하고, 설치된 사진 첨부 확인 ¦ [별표 3] 3.1 (3) ¦ 검토서 (준공도면, 현장사진 등) ¦ ¦ 성능 ¦ 1 ¦ 시운전을 실시하고 작동 상태와 성능 기준이 만족한 경우 적합으로 함 [시운전보고서] 시운전 시 기계설비감리업무수행자가 적합여부 확인 한 경우, 적합으로 함 ¦ - ¦ 시운전보고서 ¦ ¦ 성능 ¦ 2 ¦ 성능시험 성적서 발행기관의 적정성, 성적서의 유효기간 등이 만족 한 경우 적합으로 함 [시험성적서] 제출된 시험성적서의 적정성, 유효기간 등을 확인 ¦ ¦ 시험성적서 ¦ ¦ 유지 관리 ¦ 1 ¦ 「기계설비 유지관리기준」 제 6 조제 2 항 기계설비 시스템 운용 매뉴얼 (기계설비 제조사의 검사결과 또는 성적서 포함, 환기설비)을 갖춘 경 우 적합으로 함 [매뉴얼] 기계설비 시스템 운용 매뉴얼에서 환기설비 목차 및 내용 확인 ¦ ¦ 기계설비 시스템 운용 매뉴얼 ¦ ¦ 유지 관리 ¦ 2 ¦ [별표 15] 2.기계설비 유지관리 공간의 조건을 만족할 경우 적합으로 함 [검토서] 준공도면의 기계실/공조실 평면도, 샤프트 상세도 등에서 장비 및 기기별 이격거리 및 공간 확보 등의 조건과 설치된 사진을 기계설비감리업무수행자가 확인한 경우 적합으로 함 ¦ [별표 15] 2. ¦ 검토서 (준공도면, 현장사진 등) ¦ ※ 모든 항목은 기계설비감리업무수행자의 확인을 받아 관련항목이 적합하다고 인정받는 경우, 적합으로 함 ※ 판단기준 조건을 만족하는 서류(ex 감리관련서류, 관련 용역보고서 등)가 있을 경우, 필요서류를 대체할 수 있음 국토교통부 57 기계설비 기술기준 판단기준 | {}
41d30f8d-c238-4ea0-8daa-6450f95661f2 | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 4] 위생기구설비의 사용 전 확인표_[별지 제 3 호 서식] ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 4] ¦ [별표 4] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ ¦ ¦ 위생기구설비 ¦ 위생기구설비 ¦ ¦ 공 종 ¦ 위생기구설비 ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 자 재 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 대변기의 설치는 기술기준에 적합한가 ¦ 대변기의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 세면기의 설치는 기술기준에 적합한가 ¦ 세면기의 설치는 기술기준에 적합한가 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 소변기의 설치는 기술기준에 적합한가 ¦ 소변기의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 욕조의 설치는 기술기준에 적합한가 ¦ 욕조의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 악세사리(수건걸이, 거울, 선반, 청소도구함, 잡지꽂이 등) 설치는 기술기준에 적합한가 ¦ 악세사리(수건걸이, 거울, 선반, 청소도구함, 잡지꽂이 등) 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 급수전 및 배수기구의 설치는 기술기준에 적합한가 ¦ 급수전 및 배수기구의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 급수구, 배수구 주변처리 등 설치는 기술기준에 적합한가 ¦ 급수구, 배수구 주변처리 등 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 위생기구의 접속상태는 기술기준에 적합한가 ¦ 위생기구의 접속상태는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 고정상태, 외부손상상태 등 마감상태는 기술기준에 적합한가 ¦ 고정상태, 외부손상상태 등 마감상태는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 위생기구의 급수 및 배수 성능은 적합한가 ¦ 위생기구의 급수 및 배수 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 위생기구의 작동과 성능은 적합한가 ¦ 위생기구의 작동과 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 (인) ¦ ¦ 확인일 ¦ ¦ 회사명(상호) ¦ ¦ ¦ ¦ ¦ ¦ 회사명(상호) (인) ¦ ¦ ¦ ¦ ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/m2 ] 58 기계설비 기술기준 매뉴얼 | {}
3c7d1d5a-7c05-479f-9760-df70880db65f | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 [별표 4] 위생기구설비의 사용 전 검사 적합/부적합 판단기준 ¦ ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도서 ¦ 도서 ¦ 위생기구설비 관련 준공도서를 모두 확인하였다면 적합으로 함 [준공도서] 준공도서(준공도면, 시방서, 부하 및 장비선정 계산서 등) 가 모두 구비되어 있는 지 확인 ¦ ¦ 준공도서 ¦ ¦ 자재 ¦ 자재 ¦ 장비일람표, 시방서 등의 설계사항을 반영한 주요 장비 및 기자재 구 매, 반입 및 관련 도서를 확인하고, 설치된 장비의 사양과 규격 일치 여부를 확인하였다면 적합으로 함 [검토서] 설계대로 발주된 주요 장비 및 기자재 자재승인서와 자재검 수요청서 확인하여 일치여부를 기계설비감리업무수행자가 확인한 경우 적합으로 함 ¦ ¦ 검토서(자재승인서, 자재검수요청서 등) ¦ ¦ 시공 ¦ 1 ¦ 플랜지의 테이퍼 면과 일치되게 배수관을 확관하여 밀착시키고, 플 랜지 볼트를 통해 견고하게 고정한 경우, 적합으로 함 [검토서] 준공도서의 위생배관 평면도/상세도에서 관련내용과 설치 된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 4] 3.2.1 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 2 ¦ 세면기를 벽면에 밀착시킨 후 브래킷, 백 행거, 카운터 방식 등으로 견 고하게 고정하고, 브래킷 고정은 앵커볼트를 사용한 경우, 적합으로 함 [검토서] 준공도서의 위생배관 평면도/상세도에서 관련내용과 설치 된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 4] 3.2.3 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 3 ¦ 배수관과 의 접속은 소변기용 바닥 또는 벽 플랜지를 사용하여 조임 볼트로 완전하게 접속한 경우, 적합으로 함 [검토서] 준공도서의 위생배관 평면도/상세도에서 관련내용과 설치 된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 4] 3.2.2 ¦ 검토서 (준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 4 ¦ 욕조는 바닥에 움직이지 않도록 견고하게 설치하고, 욕조 내 물을 배 수 시 남지 않도록 구배를 맞추어 배수구에 설치한 경우 적합으로 함 [검토서] 준공도서의 위생배관 평면도/상세도에서 관련내용과 설치 된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 4] 3.2.6 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 5 ¦ 수건걸이, 비누갑, 컵걸이, 칫솔걸이, 휴지걸이, 옷걸이 등 각각의 목 적에 적합하고 가장 편리한 위치와 높이에 견고하게 설치하였을 경 우 적합으로 함 [검토서] 준공도서의 위생배관 평면도/상세도에서 관련내용과 설치 된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 4] 3.2.12 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 6 ¦ 수도꼭지 및 배수구가 설계도면 대로 설치된 경우 적합으로 함 [검토서] 준공도서의 위생배관 평면도/상세도에서 관련내용과 설치 된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 7 ¦ 위생기구 주변 시공이 청결하게 마감된 경우, 적합으로 함 [검토서] 현장사진을 통해 위생기구 주변이 청결하게 마감 확인 ¦ - ¦ 검토서 (현장사진 등) ¦ ¦ 시공 ¦ 8 ¦ 위생기구와 급수구 연결부에 누수 발생을 육안 확인 후 이상이 없는 경우 적합으로 함(세대 수압테스트 검측자료 첨부) [검토서] 위생기구와 급수구 연결부에 누수가 발생하는 지 측정 및 세대별 수압테스트 검측결과 보고서 등을 참고하여 기계설비감리업 무수행자가 확인한 경우 적합으로 함 ¦ ¦ 검토서(현장사진, 수압테스트 검측자료 등) ¦ ¦ 시공 ¦ 9 ¦ 시공완료 후 위생기구의 고정 및 마감상태를 확인하여 손상된 부분 이 없는 것을 확인한 후 적합으로 함 [검토서] 현장사진을 통해 위생기구 손상 여부를 확인하여 이상없는 지 확인 ¦ ¦ 검토서 (현장사진 등) ¦ ¦ 성능 ¦ 1 ¦ 급수수도꼭지 작동 시 수격발생 여부를 확인하고 오배수배관 통수검 사를 하여 이상이 없을 경우, 적합으로 함 ¦ - ¦ 검토서(수격검사 보고서, 통수 ¦ 국토교통부 59 기계설비 기술기준 판단기준 | {}
3f417caa-b3c3-41dd-b6a6-bd65eafde9ce | 국내_기계설비_기술기준_매뉴얼_최종본 | ¦ ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ ¦ [검토서] 오배수배관 통수검사 등을 기계설비감리업무수행자가 확인 한 경우 적합으로 함 ¦ ¦ 검측요청서, 오배수 내시경자료) ¦ ¦ 2 ¦ 위생기구 밸브 작동상태 및 세면대 배수 상태를 검사하여 이상 없을 경우 적합으로 함 [검토서] 현장사진을 통해 위생기구 밸브 작동상태 및 세면대 배수트 랩 상태 등을 기계설비감리업무수행자가 확인한 경우 적합으로 함 ¦ ¦ 검토서 (현장사진 등) ¦ ¦ ¦ 유지 관리 ¦ 1 ¦ 「기계설비 유지관리기준」 제 6 조제 2 항 기계설비 시스템 운용 매뉴얼 (기계설비 제조사의 검사결과 또는 성적서 포함, 위생기구설비)을 갖 춘 경우 적합으로 함 [매뉴얼] 기계설비 시스템 운용 매뉴얼에서 위생기구설비 목차 및 내용 확인 ¦ ¦ 기계설비 시스템 운용 매뉴얼 ¦ ¦ 유지 관리 ¦ 2 ¦ [별표 5] 급수급탕설비의 사용 전 확인표를 만족할 경우, 적합으로 함 ¦ [별표 5] ¦ ¦ ※ 모든 항목은 기계설비감리업무수행자의 확인을 받아 관련항목이 적합하다고 인정받는 경우, 적합으로 함 ※ 판단기준 조건을 만족하는 서류(ex 감리관련서류, 관련 용역보고서 등)가 있을 경우, 필요서류를 대체할 수 있음 60 기계설비 기술기준 매뉴얼 | {}
df9c5a3e-e9b8-45db-b58c-f3e060ed7172 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 [별표 5] 급수 · 급탕설비의 사용 전 확인표_[별지 제 3 호 서식] ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 5] ¦ [별표 5] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ 급수·급탕설비 ¦ 급수·급탕설비 ¦ ¦ 공 종 ¦ 급수·급탕설비 ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ ] ¦ [] 적합 [ - 부적합 ¦ ¦ 자 재 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 급수펌프의 설치는 기술기준에 적합한가 ¦ 급수펌프의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 급탕펌프의 설치는 기술기준에 적합한가 ¦ 급탕펌프의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 저수조(고가, 지하 등)의 설치는 기술기준에 적합한가 ¦ 저수조(고가, 지하 등)의 설치는 기술기준에 적합한가 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 장비류의 배관 접속상태는 기술기준에 적합한가 ¦ 장비류의 배관 접속상태는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 역류방지밸브 등 세대 인입급수관 기기류의 설치는 기술기준에 적합한가 ¦ 역류방지밸브 등 세대 인입급수관 기기류의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 음용수 배관, 음수기 등의 설치는 기술기준에 적합한가 ¦ 음용수 배관, 음수기 등의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 개별급탕기기(순간온수기) 급탕가열장치 등 설치는 기술기준에 적합한가 ¦ 개별급탕기기(순간온수기) 급탕가열장치 등 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 수격방지기의 설치는 기술기준에 적합한가 ¦ 수격방지기의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 급탕배관의 신축이음은 기술기준에 적합한가 ¦ 급탕배관의 신축이음은 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 급수·급탕설비의 마감상태는 기술기준에 적합한가 ¦ 급수·급탕설비의 마감상태는 기술기준에 적합한가 ¦ I ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 급수의 유량 및 수압 성능은 적합한가 ¦ 급수의 유량 및 수압 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 급탕의 온도 및 수압 성능은 적합한가 ¦ 급탕의 온도 및 수압 성능은 적합한가 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 (인) ¦ 확인일 ¦ 확인일 ¦ ¦ 회사명(상호) ¦ ¦ ¦ ¦ ¦ ¦ 회사명(상호) ¦ ¦ ¦ (인) ¦ (인) ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/m2 ] 국토교통부 61 기계설비 기술기준 판단기준 | {}
93dca021-f3da-4c62-bbd9-e74e88b758c3 | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 5] 급수 · 급탕설비의 사용 전 검사 적합/부적합 판단기준 ¦ ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도서 ¦ 도서 ¦ 급수·급탕설비 관련 준공도서를 모두 확인하였다면 적합으로 함 [준공도서] 준공도서(준공도면, 시방서, 부하 및 장비선정 계산서 등) 가 모두 구비되어 있는 지 확인 ¦ ¦ 준공도서 ¦ ¦ 자재 ¦ 자재 ¦ 장비일람표, 시방서 등의 설계사항을 반영한 주요 장비 및 기자재 구 매, 반입 및 관련 도서를 확인하고, 설치된 장비의 사양과 규격 일치 여부를 확인하였다면 적합으로 함 [검토서] 설계대로 발주된 주요 장비 및 기자재 자재승인서와 자재검 수요청서 확인하여 일치여부를 기계설비감리업무수행자가 확인한 경우 적합으로 함 ¦ ¦ 검토서(자재승인서, 자재검수요청서 등) ¦ ¦ 시공 ¦ 1 ¦ 급수펌프에 밸브 및 관을 부착할 때는 그 운전중량이 직접 펌프에 걸 리지 않도록 지지하였다면 적합으로 함 [검토서] 준공도서의 위생배관 평면도/상세도에서 관련내용과 설치 된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 5] 3.2.2 (4) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 2 ¦ 급탕펌프에 밸브 및 관을 부착할 때는 그 운전중량이 직접 펌프에 걸 리지 않도록 지지하였다면 적합으로 함 [검토서] 준공도서의 위생배관 평면도/상세도에서 관련내용과 설치 된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 5] 3.2.2 (4) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 3-1 ¦ 저수조를 옥외에 설치하는 경우에는 저수조 점검용 뚜껑을 이중으로 설치하고 잠금장치를 하였다면 적합으로 함 [검토서] 준공도서의 장비일람표에서 저수조 점검용 뚜껑 이중 명기 를 확인하고, 설치된 사진을 첨부 확인 ¦ [별표 5] 3.2.3 (1) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 3-2 ¦ 급수 저수조의 내부 및 상부로는 급수관 이외의 배관이 통과 되지 않 도록 하였다면 적합으로 함 [검토서] 준공도서의 기계실 평면도/상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 5] 3.2.3 (3) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 3-3 ¦ 저수조의 드레인 및 물넘침은 간접배수로 하고 오버플로관은 방충망 을 부착한 경우, 적합으로 함 [검토서] 준공도서의 기계실 평면도/상세도에서 간접배수 및 오버플 로관 방충망 설치 설계안과 설치된 사진을 기계설비감리업무수행자 가 확인한 경우, 적합으로 함 ¦ [별표 5] 3.2.3 (4) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 4 ¦ [별표 8] 배관설비의 사용 전 확인표를 만족할 경우, 적합으로 함 ¦ [별표 8] ¦ - ¦ ¦ 시공 ¦ 5 ¦ 수돗물의 오염을 방지하기 위한 메인 계량기 후단, 저수탱크 흡입관 과 가압펌프 사이, 온수탱크의 보급수관에 역류방지밸브 설치가 된 경우 적합으로 함 [검토서] 준공도서의 위생배관 평면도/상세도에서 관련내용과 설치 된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 5] 3.1 (5) 3.3.1 (3) ⑥ ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 6 ¦ 음용수배관과 비음용수 배관을 크로스 커넥션 하지 않고, 음용수배 관을 타배관계통과 식별할 수 있도록 설치하였다면 적합으로 함 [검토서] 준공도서의 위생배관 평면도/상세도에서 관련내용과 설치 된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 5] 2.1.8 3.2.1 (1) ③ ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 7 ¦ 난방겸용 급탕가열장치는 60°C 이하로 제한할 수 있는 온도조절밸브 를 설치한 경우 적합으로 함 [검토서] 준공도서의 장비알람표, 위생배관 평면도/상세도, 자동제어 설계도면에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 5] 3.3.2 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 8 ¦ 펌프 토출측(부스터 펌프를 포함한 급수펌프 토출관) 및 양수관의 구 간에 설치된 역류방지밸브 근처 배관과 급수 배관계통의 전자밸브, 모터밸브 등 급폐쇄형 밸브 근처 배관에 수격방지기가 설치된 경우 ¦ [별표 5] 3.2.4 (2) ¦ 검토서(준공도면, 현장사진 등) ¦ 62 기계설비 기술기준 매뉴얼 | {}
860d6545-508c-4b84-a73f-fd4907074227 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 ¦ ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ ¦ 적합으로 함 [검토서] 준공도서의 기계실 평면도, 위생배관 평면도/상세도에서 관 련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합 으로 함 ¦ ¦ ¦ ¦ 9 ¦ 배관에 관의 신축이 가능하도록 신축이음을 설치하고, 설치되는 배 관에는 일정구간에 고정점을 두고 신축 시 소음과 진동이 발생하지 않도록 설치한 경우 적합으로 함 [검토서] 준공도서의 위생배관 평면도/상세도에서 관련내용과 설치 된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 5] 3.3.1 (2) ② ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ ¦ 10 ¦ 시공완료 후 급수 및 급탕설비 의 고정 및 마감상태를 확인하여 손상 된 부분이 없는 것을 확인한 후 적합으로 함 [검토서] 현장사진을 통해 급수급탕설비의 마감상태 및 손상여부 확인 ¦ ¦ 검토서 (현장사진 등) ¦ ¦ ¦ 성능 ¦ 1 ¦ 시운전을 실시하여 워터해머가 발생하지 않고, 적정 수압으로 공급 될 경우, 적합으로 함 [시운전보고서] 시운전 시 기계설비감리업무수행자가 워터해머 발생 방지 및 적정수압 적합여부를 확인한 경우, 적합으로 함 ¦ ¦ 시운전보고서 ¦ ¦ 성능 ¦ 2 ¦ 중앙공급방식의 급탕은 50°C 이상을 유지하는 수단을 갖춘 경우 적 합으로 함 [검토서] 준공도서의 장비일람표에 중앙공급식 급탕의 경우 50°C 이 상으로 설계안과 말단에서 화상 방지를 위한 조치를 기계설비감리업 무수행자가 확인한 경우 적합으로 함 ¦ ¦ 검토서 (현장사진 등) ¦ ¦ 유지 관리 ¦ 1 ¦ 「기계설비 유지관리기준」 제 6 조제 2 항 기계설비 시스템 운용 매뉴얼 (기계설비 제조사의 검사결과 또는 성적서 포함, 급수급탕설비)을 갖 춘 경우 적합으로 함 [매뉴얼] 기계설비 시스템 운용 매뉴얼에서 급수·급탕설비 목차 및 내용 확인 ¦ ¦ 기계설비 시스템 운용 매뉴얼 ¦ ¦ 유지 관리 ¦ 2 ¦ [별표 15] 2.기계설비 유지관리 공간의 조건을 만족할 경우 적합으로 함 [검토서] 준공도면의 기계실/공조실 평면도, 샤프트 상세도 등에서 장비 및 기기별 이격거리 및 공간 확보 등의 조건과 설치된 사진을 기계설비감리업무수행자가 확인한 경우 적합으로 함 ¦ [별표 15] 2. ¦ 검토서(준공도면, 현장사진 등) ¦ ※ 모든 항목은 기계설비감리업무수행자의 확인을 받아 관련항목이 적합하다고 인정받는 경우, 적합으로 함 ※ 판단기준 조건을 만족하는 서류(ex 감리관련서류, 관련 용역보고서 등)가 있을 경우, 필요서류를 대체할 수 있음 국토교통부 63 기계설비 기술기준 판단기준 | {}
02e387e6-1ace-43ed-99eb-ac4e7f21dbc2 | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 6] 오 · 배수 통기 및 우수배수설비의 사용 전 확인표_[별지 제 3 호 서식] ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 6] ¦ [별표 6] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ 오·배수 통기/우수배수설비 ¦ 오·배수 통기/우수배수설비 ¦ ¦ 공 종 ¦ 오·배수 통기 및 우수배수설비 ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 자 재 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 오·배수배관의 설치는 기술기준에 적합한가 ¦ 오·배수배관의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 통기배관의 설치는 기술기준에 적합한가 ¦ 통기배관의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 우수배수관의 설치는 기술기준에 적합한가 ¦ 우수배수관의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 위생기구, 배수구 등과 의 접속상태는 기술기준에 적합한가 ¦ 위생기구, 배수구 등과 의 접속상태는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 동파우려 개소에 대한 방동조치는 기술기준에 적합한가 ¦ 동파우려 개소에 대한 방동조치는 기술기준에 적합한가 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 통기관 외부 마감기구의 설치는 기술기준에 적합한가 ¦ 통기관 외부 마감기구의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 오·배수관과 우수배수관의 분리 시공 상태는 기술기준에 적합한가 ¦ 오·배수관과 우수배수관의 분리 시공 상태는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 배관 내외부의 청소 등 마감상태는 기술기준에 적합한가 ¦ 배관 내외부의 청소 등 마감상태는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 오·배수관 및 우수배수관의 수밀성과 배수성능은 적합한가 ¦ 오·배수관 및 우수배수관의 수밀성과 배수성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 우수관의 통기 성능은 적합한가 ¦ 우수관의 통기 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 침수 등 비상시를 대비한 설비는 기술기준에 적합한가 ¦ 침수 등 비상시를 대비한 설비는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 ¦ 확인일 ¦ 확인일 ¦ ¦ 회사명(상호) ¦ ¦ ¦ (인) ¦ (인) ¦ ¦ 회사명(상호) ¦ ¦ ¦ (인) ¦ (인) ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/m2] 64 기계설비 기술기준 매뉴얼 | {}
d3d4c7d6-85d3-4699-8154-fd920dee79e0 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 [별표 6] 오 · 배수 통기 및 우수배수설비의 사용 전 검사 적합/부적합 판단기준 ¦ ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도서 ¦ 도서 ¦ 오·배수 통기 및 우수배수설비 관련 준공도서를 모두 확인하였다면 적합으로 함 [준공도서] 준공도서(준공도면, 시방서, 부하 및 장비선정 계산서 등) 가 모두 구비되어 있는 지 확인 ¦ ¦ 준공도서 ¦ ¦ 자재 ¦ 자재 ¦ 장비일람표, 시방서 등의 설계사항을 반영한 주요 장비 및 기자재 구 매, 반입 및 관련 도서를 확인하고, 설치된 장비의 사양과 규격 일치 여부를 확인하였다면 적합으로 함 [검토서] 설계대로 발주된 주요 장비 및 기자재 자재승인서와 자재검수요 청서 확인하여 일치여부를 기계설비감리업무수행자가 확인한 경우 적합 으로 함 ¦ ¦ 검토서(자재승인서, 자재검수요청서 등) ¦ ¦ 시공 ¦ 1 ¦ 오배수배관은 3.2.1(1) ①~⑫ 준수여부를 확인하였을 경우 적합으로 함 [검토서] 준공도서의 오배수배관 평면도/상세도에서 관련내용과 설 치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 6] 3.2.1 (1) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 2 ¦ 통기배관은 3.2.1(2) ①~⑤ 준수여부를 확인하였을 경우 적합으로 함 [검토서] 준공도서의 통기배관 평면도/상세도에서 관련내용과 설치 된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 6] 3.2.1 (2) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 3 ¦ 우수배수관은 3.3(1)~(4) 준수여부 확인를 확인하였을 경우 적합으로 함 [검토서] 준공도서의 우수배수배관 평면도/상세도에서 관련내용과 설 치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 6] 3.3 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 4 ¦ [별표 4] 위생기구설비의 사용 전 확인표를 만족할 경우, 적합으로 함 [별표 8] 배관설비의 사용 전 확인표를 만족할 경우, 적합으로 함 ¦ [별표 4] [별표 8] ¦ - ¦ ¦ 시공 ¦ 5 ¦ [별표 10] 보온설비의 사용 전 확인표를 만족할 경우, 적합으로 함 ¦ [별표 10] ¦ - ¦ ¦ 시공 ¦ 6 ¦ 통기관의 외부마감기구는 성능을 잘 발휘할 수 있도록 설치된 경우 적합으로 함 [검토표] 현장사진을 통해 통기관의 외부마감기구 설치를 기계설비 감리업무수행자가 확인한 경우 적합으로 함 ¦ ¦ 검토서 (현장사진 등) ¦ ¦ 시공 ¦ 7 ¦ 우수수직관을 배수수직관 또는 통기관과 겸용하는 방식으로 시공하 지 않은 경우와 위생배수관과 우수관을 완전히 분리하여 시공한 경 우 적합으로 함 [검토서] 준공도서의 오배수 통기 및 우수배수배관 평면도/상세도에서 관 련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으 로 함 ¦ [별표 6] 2.2.3 (1)(2) 3.3 (2) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 8 ¦ 시공완료 후 배관 내외부 청소 및 마감상태를 확인하여 손상된 부분 이 없는 것을 확인한 후 적합으로 함 [검토서] 현장사진을 통해 배관 내외부 청소 및 마감상태, 손상여부를 기계설비감리업무수행자가 확인한 경우 적합으로 함 ¦ ¦ 검토서 (현장사진 등) ¦ ¦ 성능 ¦ 1 ¦ 만수검사를 하여 이상이 없을 경우, 적합으로 함 [보고서] 만수검사 결과 를 기계설비감리업무수행자가 확인한 경우 적합 으로 함 ¦ ¦ 만수검사 보고서 ¦ ¦ 성능 ¦ 2 ¦ 우수수직관은 통기관으로 사용하지 않은 경우 적합으로 함 [검토서] 준공도서의 통기 및 우수배수배관 평면도/상세도에서 관련 내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합 으로 함 ¦ [별표 6] 2.2.3 (1) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 유지 관리 ¦ 1 ¦ 「기계설비 유지관리기준」 제 6 조제 2 항 기계설비 시스템 운용 매뉴얼 (기계설비 제조사의 검사결과 또는 성적서 포함, 오배수 통기 및 우 수배수설비)을 갖춘 경우 적합으로 함 [매뉴얼] 기계설비 시스템 운용 매뉴얼에서 오·배수 통기 및 우수배 수설비 목차 및 내용 확인 ¦ ¦ 기계설비 시스템 운용 매뉴얼 ¦ 국토교통부 65 기계설비 기술기준 판단기준 | {}
6225408b-a612-4e25-b378-3b11534461d8 | 국내_기계설비_기술기준_매뉴얼_최종본 | ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 2 ¦ 유입수를 30 분 이상 저장할 수 있는 집수정이 설치되고, 배수펌프는 수중모터펌프 형식으로 하고 전체 펌프의 유량은 시간최대 유입수량 의 200% 이상으로 설치된 경우 적합으로 함 [검토서] 준공도서의 장비일람표, 오배수 배관 평면도/상세도에서 관련내용 과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 6] 2.2.5 (1) (2) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 3 ¦ [별표 15] 2.기계설비 유지관리 공간의 조건을 만족할 경우 적합으로 함 [검토서] 준공도면의 기계실/공조실 평면도, 샤프트 상세도 등에서 장비 및 기기별 이격거리 및 공간 확보 등의 조건과 설치된 사진을 기계설비감리업무수행자가 확인한 경우 적합으로 함 ¦ [별표 15] 2. ¦ 검토서(준공도면, 현장사진 등) ¦ ※ 모든 항목은 기계설비감리업무수행자의 확인을 받아 관련항목이 적합하다고 인정받는 경우, 적합으로 함 ※ 판단기준 조건을 만족하는 서류(ex 감리관련서류, 관련 용역보고서 등)가 있을 경우, 필요서류를 대체할 수 있음 66 기계설비 기술기준 매뉴얼 | {}
7297276d-a0d9-4979-bc9a-5c2ec5732a66 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 [별표 7] 오수정화 및 물재이용설비의 사용 전 확인표_[별지 제 3 호 서식] ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 7] ¦ [별표 7] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ 오수정화 및 물재이용설비 ¦ 오수정화 및 물재이용설비 ¦ ¦ 공 종 ¦ 오수정화 및 물재이용설비 ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 자 재 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 오수정화설비의 설치는 기술기준에 적합한가 ¦ 오수정화설비의 설치는 기술기준에 적합한가 ¦ I ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 빗물이용설비의 설치는 기술기준에 적합한가 ¦ 빗물이용설비의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 중수처리설비의 설치는 기술기준에 적합한가 ¦ 중수처리설비의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 펌프류의 설치는 기술기준에 적합한가 ¦ 펌프류의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 송풍기의 설치는 기술기준에 적합한가 ¦ 송풍기의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 밸브류, 기기류 등의 설치는 기술기준에 적합한가 ¦ 밸브류, 기기류 등의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 장비계통도, 명판부착 등 외부 마감상태는 기술기준에 적합한가 ¦ 장비계통도, 명판부착 등 외부 마감상태는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 오수정화설비의 수처리 성능은 적합한가 ¦ 오수정화설비의 수처리 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 물재이용설비의 수처리 성능은 적합한가 ¦ 물재이용설비의 수처리 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 중수처리설비의 수처리 성능은 적합한가 ¦ 중수처리설비의 수처리 성능은 적합한가 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 ¦ 확인일 ¦ 확인일 ¦ ¦ 회사명(상호) ¦ (인) ¦ ¦ ¦ ¦ ¦ 회사명(상호) ¦ ¦ (인) ¦ ¦ ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/m2 ] 국토교통부 67 기계설비 기술기준 판단기준 | {}
4672a07b-5256-4956-9f49-5b7e4da6fe9b | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 7] 오수정화 및 물재이용설비의 사용 전 검사 적합/부적합 판단기준 ¦ ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도서 ¦ 도서 ¦ 오수정화 및 물재이용설비 관련 준공도서를 모두 확인하였다면 적합 으로 함 [준공도서] 준공도서(준공도면, 시방서, 부하 및 장비선정 계산서 등) 가 모두 구비되어 있는 지 확인 ¦ ¦ 준공도서 ¦ ¦ 자재 ¦ 자재 ¦ 장비일람표, 시방서 등의 설계사항을 반영한 주요 장비 및 기자재 구 매, 반입 및 관련 도서를 확인하고, 설치된 장비의 사양과 규격 일치 여부를 확인하였다면 적합으로 함 [검토서] 설계대로 발주된 주요 장비 및 기자재 자재승인서와 자재검 수요청서 확인하여 일치여부를 기계설비감리업무수행자가 확인한 경우 적합으로 함 ¦ ¦ 검토서(자재승인서, 자재검수요청서 등) ¦ ¦ 시공 ¦ 1 ¦ 개인하수처리시설의 경우, 3.2 준수여부를 확인하였을 경우 적합으로 함 [검토서] 준공도서의 개인하수처리시설 평면도/상세도에서 관련내용 과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 7] 3.2 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 2 ¦ 빗물이용설비는 2.3 준수여부를 확인하였을 경우 적합으로 함 [검토서] 준공도서의 빗물이용설비 평면도/상세도에서 관련내용과 설 치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 7] 2.3 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 3 ¦ 중수처리설비는 2.4 준수여부를 확인하였을 경우 적합으로 함 [검토서] 준공도서의 중수처리설비 평면도/상세도에서 관련내용과 설 치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 7] 2.4 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 4 ¦ [별표 5] 급수급탕설비의 사용 전 확인표를 만족할 경우, 적합으로 함 [별표 6] 오배수 통기 및 우수배수 설비의 사용 전 확인표를 만족할 경우, 적합으로 함 ¦ [별표 5] [별표 6] ¦ ¦ ¦ 시공 ¦ 5 ¦ [별표 3] 환기설비의 사용 전 확인표를 만족할 경우, 적합으로 함 ¦ [별표 3] ¦ - ¦ ¦ 시공 ¦ 6 ¦ [별표 8] 배관설비의 사용 전 확인표를 만족할 경우, 적합으로 함 ¦ [별표 8] ¦ - ¦ ¦ 시공 ¦ 7 ¦ 「기계설비 유지관리기준」 [별지 제 1 호서식] 기계설비 유지관리 및 성능점검 대상 현황표에 기록해야 하는 내용이 명판에 반영되어 있 으며, 마감상태가 식별이 용이한 것을 확인한 경우 적합으로 함 [검토서] 오수정화 및 물재이용설비 장비 명판과 장비일람표의 세부 사양을 확인하고, 설치된 사진 첨부 확인 ¦ ¦ 검토서 (장비일람표, 현장사진 등) ¦ ¦ 성능 ¦ 1 ¦ 오수정화설비 시운전을 실시하고 작동 상태와 성능 기준이 만족한 경우 적합으로 함 [시운전보고서] 시운전 시 기계설비감리업무수행자가 적합여부 확인 한 경우, 적합으로 함 ¦ ¦ 시운전보고서 ¦ ¦ 성능 ¦ 2 ¦ 물재이용설비 시운전을 실시하고 작동 상태와 성능 기준이 만족한 경우 적합으로 함 [시운전보고서] 시운전 시 기계설비감리업무수행자가 적합여부 확인 한 경우, 적합으로 함 ¦ ¦ 시운전보고서 ¦ ¦ 성능 ¦ 3 ¦ 중수처리설비 시운전을 실시하고 작동 상태와 성능 기준이 만족한 경우 적합으로 함 [시운전보고서] 시운전 시 기계설비감리업무수행자가 적합여부 확인 한 경우, 적합으로 함 ¦ ¦ 시운전보고서 ¦ ¦ 성능 ¦ 4 ¦ 성능시험 성적서 발행기관의 적정성, 성적서의 유효기간 등이 만족 한 경우 적합으로 함 [시험성적서] 제출된 시험성적서의 적정성, 유효기간 등을 확인 ¦ ¦ 기기별 시험성적서 ¦ ¦ 유지 관리 ¦ 1 ¦ 「기계설비 유지관리기준」 제 6 조제 2 항 기계설비 시스템 운용 매뉴얼 (기계설비 제조사의 검사결과 또는 성적서 포함, 오수정화 및 물재이 용설비)을 갖춘 경우 적합으로 함 ¦ - ¦ 기계설비 시스템 운용 매뉴얼 ¦ 68 기계설비 기술기준 매뉴얼 | {}
bb898bc1-7eca-47a9-870a-cced59f2be67 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ [매뉴얼] 기계설비 시스템 운용 매뉴얼에서 오수정화 및 물재이용설 비 목차 및 내용 확인 ¦ ¦ ¦ ¦ [별표 15] 2.기계설비 유지관리 공간의 조건을 만족할 경우 적합으로 함 [검토서] 준공도면의 기계실/공조실 평면도, 샤프트 상세도 등에서 2 장비 및 기기별 이격거리 및 공간 확보 등의 조건과 설치된 사진을 기계설비감리업무수행자가 확인한 경우 적합으로 함 ¦ [별표 15] 2. ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ ※ 모든 항목은 기계설비감리업무수행자의 확인을 받아 관련항목이 적합하다고 인정받는 경우, 적합으로 함 ※ 판단기준 조건을 만족하는 서류(ex 감리관련서류, 관련 용역보고서 등)가 있을 경우, 필요서류를 대체할 수 있음 기계설비 기술기준 판단기준 국토교통부 69 | {}
fadecece-0459-4412-83e6-bb5835877262 | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 8] 배관설비의 사용 전 확인표_[별지 제 3 호 서식] ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 8] 배관설비 ¦ [별표 8] 배관설비 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ ¦ ¦ ¦ 공 종 ¦ 배관설비 ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 자 재 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 냉난방배관, 증기배관의 설치는 기술기준에 적합한가 ¦ 냉난방배관, 증기배관의 설치는 기술기준에 적합한가 ¦ [ I ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 냉각수, 냉·온수 배관의 설치는 기술기준에 적합한가 ¦ 냉각수, 냉·온수 배관의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 각종 장비류(펌프, 냉동기 등) 접속부분의 설치는 기술기준에 적합한가 ¦ 각종 장비류(펌프, 냉동기 등) 접속부분의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 난방급탕 및 증기배관 신축이음의 설치는 기술기준에 적합한가 ¦ 난방급탕 및 증기배관 신축이음의 설치는 기술기준에 적합한가 ¦ [ 1 ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 밸브류, 기기류 등의 설치는 기술기준에 적합한가 ¦ 밸브류, 기기류 등의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 배관의 경로, 고정 상태는 기술기준에 적합한가 ¦ 배관의 경로, 고정 상태는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 배관의 구배 등이 적절하며, 유체의 흐름은 적합한가 ¦ 배관의 구배 등이 적절하며, 유체의 흐름은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 배관의 유량분배는 적합한가 ¦ 배관의 유량분배는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 ¦ ¦ 확인일 ¦ ¦ 회사명(상호) ¦ ¦ ¦ ¦ ¦ ¦ 회사명(상호) ¦ ¦ ¦ (인) (인) ¦ (인) (인) ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/m2] 70 기계설비 기술기준 매뉴얼 | {}
f4eb0523-9d5a-4cf4-a0d5-2a9cb280e29c | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 [별표 8] 배관설비의 사용 전 검사 적합/부적합 판단기준 ¦ ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도서 ¦ 도서 ¦ 배관설비 관련 준공도서를 모두 확인하였다면 적합으로 함 [준공도서] 준공도서(준공도면, 시방서, 부하 및 장비선정 계산서 등) 가 모두 구비되어 있는 지 확인 ¦ ¦ 준공도서 ¦ ¦ 자재 ¦ 자재 ¦ 장비일람표, 시방서 등의 설계사항을 반영한 주요 장비 및 기자재 구 매, 반입 및 관련 도서를 확인하고, 설치된 배관의 사양과 규격 일치 여부를 확인하였다면 적합으로 함 [검토서] 설계대로 발주된 주요 장비 및 기자재 자재승인서와 자재검 수요청서 확인하여 일치여부를 기계설비감리업무수행자가 확인한 경우 적합으로 함 ¦ ¦ 검토서(자재승인서, 자재검수요청서 등) ¦ ¦ 시공 ¦ 1-1 ¦ 증기주관의 말단, 입상관 하부 등 응축수가 체류할 우려가 있는 곳은 증기트랩을 설치한 경우 적합으로 함 [검토서] 준공도서의 증기배관 평면도/상세도에서 관련내용과 설치 된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 8] 3.3.1 (6) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 1-2 ¦ 증기배관의 이음은 나사이음, 플랜지이음 또는 용접이음으로 시공한 경우 적합으로 함 [검토서] 준공도서의 시방서, 증기배관 평면도/상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 8] 3.3.2. (1) ¦ 검토서(준공도면, 시방서, 현장사진 등) ¦ ¦ 시공 ¦ 1-3 ¦ 증기 공급관의 경우 순기울기(하향기울기)일 때에는 1/250 이상, 역기 울기(상향기울기)일 때에는 1/80 이상으로 하며 환수관의 경우는 순기 울기 1/200~1/300 로 하였을 경우 적합으로 함 [검토서] 준공도서의 시방서, 증기배관 평면도/상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 8] 3.3.3 ¦ 검토서(준공도면, 시방서, 현장사진 등) ¦ ¦ 시공 ¦ 1-3 ¦ 증기배관의 지지간격은 표 1 에 따라 설치한 경우 적합으로 함 [검토서] 준공도서의 증기배관 평면도/상세도에서 관련내용과 설치 된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 8] 3.3.4 (1) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 2-1 ¦ 냉온수/냉각수 배관계에서 공기가 체류할 유려가 있는 곳에는 공기빼기 밸브를 설치하였을 경우 적합으로 함 [검토서] 준공도서의 냉온수/냉각수 배관 평면도/상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 8] 3.1.1 (3) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 2-2 ¦ 냉온수/냉각수 주배관의 적절한 위치에 물채움 밸브와 물채움 높이를 확인할 수 있는 압력계를 설치하였을 경우 적합으로 함 [검토서] 준공도서의 냉온수/냉각수 배관 평면도/상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 8] 3.1.1 (5) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 2-3 ¦ 냉온수/냉각수 배관의 공급관은 역기울기, 환수관은 순기울기로 하고, 기울기는 1/250 이상으로 하였을 경우 적합으로 함 [검토서] 준공도서의 냉온수/냉각수 배관 평면도/상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 8] 3.1.3 ¦ 검토서(준공도면, 시방서, 현장사진 등) ¦ ¦ 시공 ¦ 2-4 ¦ 급탕배관의 지지간격은 [별표 8] 표 1 에 따라 설치한 경우 적합으로 함 [검토서] 준공도서의 급탕배관 평면도/상세도에서 관련내용과 설치 된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 8] 3.4.2. (3) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 3-1 ¦ 장비류 등과 연결되는 모든 배관은 그 운전중량이 장비에 직접 미치 지 않도록 지지하였을 경우 적합으로 함 [검토서] 준공도서의 모든 배관 평면도/상세도에서 관련내용과 설치 된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 8] 3.6.1 (1) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 3-2 ¦ 배관의 시공 시 부식이 예상되는 부분에는 이종관의 절연부속, 방식 테이프 등을 사용하여 부식을 방지한 경우 적합으로 함 [검토서] 준공도서의 모든 배관 평면도/상세도에서 관련내용과 설치 된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 8] 3.6.1 (2) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 3-3 ¦ 배관 용접은 용접기능사 자격증 소지자 또는 현장 용접 시험을 통과 한 자 로 시공한 경우 적합으로 함 ¦ [별표 8] 3.6.2 ¦ 용접기능사 자격증 현장용접시험확인 ¦ 국토교통부 71 기계설비 기술기준 판단기준 | {}
ea913129-94b9-4369-8691-74cab3ff971e | 국내_기계설비_기술기준_매뉴얼_최종본 | ¦ ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ ¦ [검토서] 용접기능사 자격증 소지자 또는 현장 용접 시험을 통과 한 자가 배관용접 하도록 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ ¦ 서 ¦ ¦ 4 ¦ 배관에 관의 신축이 가능하도록 신축이음을 설치하고, 설치되는 배 관에는 일정구간에 고정점을 두고 신축 시 소음과 진동이 발생하지 않도록 설치한 경우 적합으로 함 [검토서] 준공도서의 모든 배관 평면도/상세도에서 관련내용과 설치 된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 8] 2.10 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ ¦ 5-1 ¦ 기기와 의 모든 연결부에는 차단밸브를 설치하고, 기기와 배관의 연 결은 플랜지, 유니언, 그루브 조인트, 기타 기계식 이음을 사용하여 배관의 손상 없이 기기의 탈착이 가능하도록 한 경우 적합으로 함 [검토서] 준공도서의 모든 배관 평면도/상세도에서 관련내용과 설치 된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 8] 2.1.3 (1) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ ¦ 5-2 ¦ 냉동기 주변배관에는 방진이음을 설치한 경우 적합으로 함 (흡수식 냉동기 및 흡수식 냉온수기 제외) [검토서] 준공도서의 방음방진 평면도/상세도에서 냉동기 주변배관 에 방진이음을 설치된 사진을 기계설비감리업무수행자가 확인한 경 우, 적합으로 함 ¦ [별표 8] 2.1.3 (2) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ ¦ 5-3 ¦ 온수보일러, 열교환기 등의 안전장치를 안전밸브와 팽창관으로 병용한 경우 적합으로 함 [검토서] 준공도서의 온수(난방)배관 평면도/상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 8] 2.1.3 (3) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ ¦ 5-4 ¦ 방진기가 설치된 모든 펌프의 토출구와 흡입구에는 방진이음을 설치 한 경우 적합으로 함 [검토서] 준공도서의 방음방진 평면도/상세도에서 관련내용과 설치 된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 8] 2.1.3 (5) ① ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ ¦ 5-5 ¦ 펌프의 입구와 출구에는 압력계를 설치한 경우 적합으로 함 [검토서] 준공도서의 기계실 평면도/상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 8] 2.1.3 (5) ② ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ ¦ 5-6 ¦ 열원기기의 냉수, 온수, 냉각수 공급 및 환수관의 직관부에는 온도계 및 압력계를 부착한 경우 적합으로 함 [검토서] 준공도서의 기계실 평면도/상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 8] 2.1.4 (1) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ ¦ 6 ¦ 배관의 지지간격은 표 1 에 따라 설치한 경우 적합으로 함 [검토서] 준공도서의 모든배관 평면도/상세도에서 관련내용과 설치 된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 8] 3.1.4 (1) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ ¦ 성능 ¦ 1 ¦ 시공 1-3, 2-3, 확인한 경우 적합으로 함 ¦ - ¦ - ¦ ¦ 성능 ¦ 2 ¦ 냉동기, 온수보일러, 흡수식 냉온수기, 빙축열유닛 및 열교환기를 통과 하는 유량은 장비 허용범위를 벗어나지 않도록 한 경우 적합으로 함 [검토서] 준공도서의 계산서, 기계실 배관 평면도/상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 8] 2.1.1 (2) ¦ 검토서(준공도면, 계산서 등) ¦ ¦ 유지 관리 ¦ 1 ¦ 「기계설비 유지관리기준」 제 6 조제 2 항 기계설비 시스템 운용 매뉴얼 (기계설비 제조사의 검사결과 또는 성적서 포함, 배관설비)을 갖춘 경 우 적합으로 함 [매뉴얼] 기계설비 시스템 운용 매뉴얼에서 배관설비 목차 및 내용 확인 ¦ ¦ 기계설비 시스템 운용 매뉴얼 ¦ ¦ 유지 관리 ¦ 2 ¦ [별표 15] 2.기계설비 유지관리 공간의 조건을 만족할 경우 적합으로 함 [검토서] 준공도면의 기계실/공조실 평면도, 샤프트 상세도 등에서 장비 및 기기별 이격거리 및 공간 확보 등의 조건과 설치된 사진을 기계설비감리업무수행자가 확인한 경우 적합으로 함 ¦ [별표 15] 2. ¦ 검토서(준공도면, 현장사진 등) ¦ ※ 모든 항목은 기계설비감리업무수행자의 확인을 받아 관련항목이 적합하다고 인정받는 경우, 적합으로 함 ※ 판단기준 조건을 만족하는 서류(ex 감리관련서류, 관련 용역보고서 등)가 있을 경우, 필요서류를 대체할 수 있음 72 기계설비 기술기준 매뉴얼 | {}
e0d255b6-dbbf-4b36-8abd-e294a84188d0 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 [별표 9] 덕트설비의 사용 전 확인표_[별지 제 3 호 서식] ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 9] 덕트설비 ¦ [별표 9] 덕트설비 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ ¦ ¦ ¦ 공 종 ¦ 덕트설비 ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 자 재 ¦ 주요기자재 선정 및 사용은 적합한가 ¦ 주요기자재 선정 및 사용은 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 덕트 고정상태는 기술기준에 적합한가 ¦ 덕트 고정상태는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 덕트기구(디퓨저, 그릴, 외기구, 배기구 등) 설치는 기술기준에 적합한가 ¦ 덕트기구(디퓨저, 그릴, 외기구, 배기구 등) 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 방화구획 관통부의 F.D 설치는 기술기준에 적합한가 ¦ 방화구획 관통부의 F.D 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 덕트와 장비의 접속부분(플렉시블 조인트 등) 설치는 기술기준에 적합한가 ¦ 덕트와 장비의 접속부분(플렉시블 조인트 등) 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 덕트 외면 손상여부 등 마감상태는 기술기준에 적합한가 ¦ 덕트 외면 손상여부 등 마감상태는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 덕트의 풍량은 설계기준 풍량에 적합한가 ¦ 덕트의 풍량은 설계기준 풍량에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 덕트와 장비 연결부분의 소음 및 진동 방지 상태는 적합한가 ¦ 덕트와 장비 연결부분의 소음 및 진동 방지 상태는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 (인) ¦ 확인일 ¦ ¦ ¦ 회사명(상호) ¦ ¦ ¦ ¦ ¦ ¦ 회사명(상호) ¦ ¦ ¦ ¦ ¦ ¦ (인) 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 ¦ (인) 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 ¦ (인) 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 ¦ (인) 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 ¦ (인) 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 ¦ 210mmX297mm[백상지 80g/m2 ] 국토교통부 73 기계설비 기술기준 판단기준 | {}
1db377b5-bfbc-4557-988e-806ed2ef3762 | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 9] 덕트설비의 사용 전 검사 적합/부적합 판단기준 ¦ ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도서 ¦ 도서 ¦ 덕트설비 관련 준공도서를 모두 확인하였다면 적합으로 함 [준공도서] 준공도서(준공도면, 시방서, 부하 및 장비선정 계산서 등) 가 모두 구비되어 있는 지 확인 ¦ ¦ 준공도서 ¦ ¦ 자재 ¦ 자재 ¦ 장비일람표, 시방서 등의 설계사항을 반영한 주요 장비 및 기자재 구 매, 반입 및 관련 도서를 확인하고, 설치된 배관의 사양과 규격 일치 여부를 확인하였다면 적합으로 함 [검토서] 설계대로 발주된 주요 장비 및 기자재 자재승인서와 자재검수요 청서 확인하여 일치여부를 기계설비감리업무수행자가 확인한 경우 적합 으로 함 ¦ ¦ 검토서(자재승인서, 자재검수요청서 등) ¦ ¦ 시공 ¦ 1 ¦ 플렉시블 덕트의 길이는 1.5 m 이하를 기본으로 하며 벽이나 바닥 또는 천장을 통과 하지 않도록 하고, 처짐이나 굴곡이 발생하지 않도록 플렉시 블 덕트에 폭 50 mm 의 받침대가 있는 행거를 설치한 경우 적합으로 함 [검토서] 준공도서의 공조 및 환기덕트 평면도/상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 9] 3.1 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 2 ¦ 2.3.4 외기도입구 2.3.5 배기구 의 조건을 만족할 경우, 적합으로 함 [검토서] 준공도서의 공조 및 환기덕트 평면도/상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 9] 2.3.4 2.3.5 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 3 ¦ KS F 2815(배연설비의 검사표준)에 따라 방화댐퍼를 설치한 경우 적합으 로 함 [검토서] 준공도서의 제연 및 공조 겸용덕트 평면도/상세도에서 관련내용 과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 9] 3.3.2 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 4 ¦ 송풍기 흡입구에 연결하는 덕트는 송풍기 날개 지름의 4 배 이상 직선 덕트 로 연결하거나, 날개 지름 이상을 직선 덕트로 하고 엘보에 터닝 베인을 설 치하여 정상류로 유입되게 시공한 경우, 송풍기 출구 연결 덕트는 송풍기 출구 장변의 1.5 배 이상을 직선으로 유지시켜 송풍기 시스템 영향을 최소 화되도록 시공한 경우, 대기로 토출하는 원심송풍기의 출구에는 송풍기 출 구 장변의 1.5 배 이상의 직관 덕트를 설치한 경우 적합으로 함 [검토서] 준공도서의 공조 및 환기덕트 평면도/상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 9] 3.4 (2) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 5 ¦ 시공 완료 후 덕트 외면 등의 마감상태를 확인하여 손상된 부분이 없는 것을 확인한 경우 적합으로 함 [검토서] 현장사진을 통해 공조 및 환기덕트 평면도/상세도의 마감상태 및 손상여부를 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ ¦ 검토서 (현장사진 등) ¦ ¦ 성능 ¦ 1 ¦ 공조 및 환기설비 시운전을 실시하여 풍량을 측정하여 만족하는 경 우, 적합으로 함 [시운전보고서] 시운전 시 기계설비감리업무수행자가 적합여부 확인 한 경우, 적합으로 함 ¦ ¦ 시운전보고서 ¦ ¦ 성능 ¦ 2 ¦ 시운전을 실시하여 [별표 12] 2.1 표 1 의 실내허용소음기준을 만족하 는 경우 적합으로 함 [보고서] 시운전 시 실내허용소음기준을 만족하는 소음측정결과 를 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 12] 2.1 ¦ 소음측정보고서 ¦ ¦ 유지 관리 ¦ 1 ¦ 「기계설비 유지관리기준」 제 6 조제 2 항 기계설비 시스템 운용 매뉴얼 (기계설비 제조사의 검사결과 또는 성적서 포함, 덕트설비)을 갖춘 경 우 적합으로 함 [매뉴얼] 기계설비 시스템 운용 매뉴얼에서 덕트설비 목차 및 내용 확인 ¦ ¦ 기계설비 시스템 운용 매뉴얼 ¦ ¦ 유지 관리 ¦ 2 ¦ [별표 15] 2.기계설비 유지관리 공간의 조건을 만족할 경우 적합으로 함 [검토서] 준공도면의 기계실/공조실 평면도, 샤프트 상세도 등에서 장비 및 기기별 이격거리 및 공간 확보 등의 조건과 설치된 사진을 기계설비감리업무수행자가 확인한 경우 적합으로 함 ¦ [별표 15] 2. ¦ 검토서(준공도면, 현장사진 등) ¦ ※ 모든 항목은 기계설비감리업무수행자의 확인을 받아 관련항목이 적합하다고 인정받는 경우, 적합으로 함 ※ 판단기준 조건을 만족하는 서류(ex 감리관련서류, 관련 용역보고서 등)가 있을 경우, 필요서류를 대체할 수 있음 74 기계설비 기술기준 매뉴얼 | {}
a7a97d30-c806-41d3-9d3a-dfe6ad134d35 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 [별표 10] 보온설비의 사용 전 확인표_[별지 제 3 호 서식] ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 10] ¦ [별표 10] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ 보온설비 ¦ 보온설비 ¦ ¦ 공 종 ¦ 보온설비 ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ ] ¦ [ ] 적합 [ ] 부적합 ¦ ¦ 자 재 ¦ 주요기자재 선정 및 사용은 적합한가 ¦ 주요기자재 선정 및 사용은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 배관 보온재의 설치는 기술기준에 적합한가 ¦ 배관 보온재의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 장비 보온재의 설치는 기술기준에 적합한가 ¦ 장비 보온재의 설치는 기술기준에 적합한가 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 밸브, 기기류, 탱크류 등의 보온재의 설치는 기술기준에 적합한가 ¦ 밸브, 기기류, 탱크류 등의 보온재의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 보온 및 비보온 개소의 구별은 기술기준에 적합한가 ¦ 보온 및 비보온 개소의 구별은 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 방화구획 등 관통부 주변 시공은 기술기준에 적합한가 ¦ 방화구획 등 관통부 주변 시공은 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 발열선의 설치는 기술기준에 적합한가 ¦ 발열선의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 발열선의 과열방지에 대한 조치는 기술기준에 적합한가 ¦ 발열선의 과열방지에 대한 조치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 보온관의 유로표지부착, 장비명판 식별여부 등 마감상태는 기술기준에 적합한가 ¦ 보온관의 유로표지부착, 장비명판 식별여부 등 마감상태는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 계량기함등의 동파방지는 기술기준에 적합한가 ¦ 계량기함등의 동파방지는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 배관류의 방동, 방로, 보온 성능은 적합한가 ¦ 배관류의 방동, 방로, 보온 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 장비류의 방동, 방로, 보온 성능은 적합한가 ¦ 장비류의 방동, 방로, 보온 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 열선 화재안전 등의 과열방지 조치는 적합한가 ¦ 열선 화재안전 등의 과열방지 조치는 적합한가 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 ¦ 확인일 ¦ 확인일 ¦ ¦ 회사명(상호) ¦ ¦ ¦ (인) ¦ (인) ¦ ¦ 회사명(상호) ¦ ¦ ¦ (인) ¦ (인) ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/m2 ] 국토교통부 75 기계설비 기술기준 판단기준 | {}
ce11d918-5346-472b-8aa9-a95a914b7cd3 | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 10] 보온설비의 사용 전 검사 적합/부적합 판단기준 ¦ ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도서 ¦ 도서 ¦ 보온설비 관련 준공도서를 모두 확인하였다면 적합으로 함 [준공도서] 준공도서(준공도면, 시방서, 부하 및 장비선정 계산서 등) 가 모두 구비되어 있는 지 확인 ¦ ¦ 준공도서 ¦ ¦ 자재 ¦ 자재 ¦ 장비일람표, 시방서 등의 설계사항을 반영한 주요 장비 및 기자재 구 매, 반입 및 관련 도서를 확인하고, 설치된 배관의 사양과 규격 일치 여부를 확인하였다면 적합으로 함 [검토서] 설계대로 발주된 주요 장비 및 기자재 자재승인서와 자재검수요 청서 확인하여 일치여부를 기계설비감리업무수행자가 확인한 경우 적합 으로 함 ¦ ¦ 검토서(자재승인서, 자재검수요청서 등) ¦ ¦ 시공 ¦ 1 ¦ 단열재가 적용된 배관(냉방, 난방, 급수, 급탕, 환탕) 및 덕트(공조, 환 기) 등 각 계통별로 최소 3 곳 이상 탐침하여 조건에 맞는 단열 두께 시 공 여부가 확인된 경우 적합으로 함 [검토서] 준공도서의 시방서, 배관 보온재 상세도 등에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 10] 2.1 2.3 2.4 ¦ 검토서(준공도면, 현장사진, 탐침측정 등) ¦ ¦ 시공 ¦ 2 ¦ 단열재가 적용된 장비들에 대해 최소 3 곳 이상 탐침하여 조건에 맞 는 단열 두께 시공 여부가 확인된 경우 적합으로 함 [검토서] 준공도서의 시방서, 장비 보온재 상세도에서 관련내용과 설 치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 10] 2.2 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 3 ¦ 단열재가 적용된 밸브, 탱크, 기기류 등에 대해 종류별로 최소 3 곳 이상 탐 침하여 조건에 맞는 단열 두께 시공 여부가 확인된 경우 적합으로 함 [검토서] 준공도서의 시방서, 배관 및 기기류 보온상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 4 ¦ 보온을 하지 않는 개소와 이 기준 1.2 의 보온을 하지않는 경우에 해당 되는 개소를 비교·확인할 수 있는 자료를 제출하는 경우 적합으로 함 [검토서] 준공도서의 시방서, 보온설비 평면도/상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 5 ¦ 관통부 주변을 내화성능 인정을 받은 불연재료로 충전된 것이 확인된 경 우 적합으로 함 [검토서] 준공도서의 시방서, 관통부 보온설비 평면도/상세도에서 관련내용 과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 6 ¦ 발열선의 설치는 3.5 의 조건을 만족한 경우 적합으로 함 [검토서] 준공도서의 시방서, 동파방지 발열선 평면도/상세도에서 관 련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합 으로 함 ¦ [별표 10] 3.5 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 7 ¦ 발열선 제조사의 시험 성적서 등이 확인된 경우 적합으로 함 [시험성적서] 제출된 시험성적서의 적정성, 유효기간 등을 확인 ¦ - ¦ 시험성적서 ¦ ¦ 시공 ¦ 8 ¦ 보온관 유로표지 등이 준공도면과 일치하는 것이 확인된 경우 적합 으로 함 [검토서] 준공도서의 보온관 평면도/상세도에서 관련내용과 설치된 사 진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 9 ¦ 2.3.5 급수관 및 수도계량기보호함의 설치기준을 준수한 경우 적합으 로 함 [검토서] 준공도서의 시방서, 급수관 및 수도계량기 보호함 상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합 으로 함 ¦ [별표 10] 2.3.5 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 성능 ¦ 1 ¦ 시공 1 이 확인된 경우 적합으로 함 ¦ - ¦ - ¦ ¦ 성능 ¦ 2 ¦ 시공 2 이 확인된 경우 적합으로 함 ¦ - ¦ - ¦ 76 기계설비 기술기준 매뉴얼 | {}
3ec5490d-cd05-4878-95f3-c6d8fb5f483c | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 ¦ ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 유지 관리 ¦ 3 ¦ 성 ¦ - ¦ ¦ ¦ 유지 관리 ¦ 1 ¦ 「기계설비 유지관리기준」 제 6 조제 2 항 기계설비 시스템 운용 매뉴얼 (기계설비 제조사의 검사결과 또는 성적서 포함, 보온설비)을 갖춘 경 우 적합으로 함 [매뉴얼] 기계설비 시스템 운용 매뉴얼에서 보온설비 목차 및 내용 확인 ¦ ¦ 기계설비 시스템 운용 매뉴얼 ¦ ¦ 유지 관리 ¦ 2 ¦ [별표 8] 배관설비의 사용 전 확인표를 만족할 경우, 적합으로 함 [별표 9] 덕트설비의 사용 전 확인표를 만족할 경우, 적합으로 함 ¦ [별표 8] [별표 9] ¦ ¦ ※ 모든 항목은 기계설비감리 업무수행자의 확인을 받아 관련항목이 적합하다고 인정받는 경우, 적합으로 함 ※ 판단기준 조건을 만족하는 서류(ex 감리관련서류, 관련 용역보고서 등)가 있을 경우, 필요서류를 대체할 수 있음 기계설비 기술기준 판단기준 국토교통부 77 | {}
7de74fc3-d845-4457-bc46-568590c3e8d2 | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 11] 자동제어설비의 사용 전 확인표_[별지 제 3 호 서식] ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 11] ¦ [별표 11] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ 자동제어설비 ¦ 자동제어설비 ¦ ¦ 공 종 ¦ 자동제어설비 ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ ] ¦ [ ] 적합 [ ] 부적합 ¦ ¦ 자 재 ¦ 주요기자재는 승인된 제품이며, 선정은 적합한가 ¦ 주요기자재는 승인된 제품이며, 선정은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 중앙관제설비의 설치는 기술기준에 적합한가 ¦ 중앙관제설비의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 건물에너지 관리시스템 설치는 기술기준에 적합한가 ¦ 건물에너지 관리시스템 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 현장제어설비 설치는 기술기준에 적합한가 ¦ 현장제어설비 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 원격검침설비 설치는 기술기준에 적합한가 ¦ 원격검침설비 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 공동주택 자동제어설비 설치는 기술기준에 적합한가 ¦ 공동주택 자동제어설비 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 자동제어 배관, 배선의 설치는 기술기준에 적합한가 ¦ 자동제어 배관, 배선의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 장비별 연동 및 인터록은 기술기준에 적합한가 ¦ 장비별 연동 및 인터록은 기술기준에 적합한가 ¦ I ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 중앙관제설비의 작동과 성능은 적합한가 ¦ 중앙관제설비의 작동과 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 건물에너지 관리시스템의 작동과 성능은 적합한가 ¦ 건물에너지 관리시스템의 작동과 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 현장제어설비의 작동과 성능은 적합한가 ¦ 현장제어설비의 작동과 성능은 적합한가 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 원격검침설비의 누수감지시스템의 작동과 성능은 적합한가 ¦ 원격검침설비의 누수감지시스템의 작동과 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 공동주택 자동제어설비의 작동과 성능은 적합한가 ¦ 공동주택 자동제어설비의 작동과 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 각 장비별 개별제어 및 통합제어 성능은 적합한가 (stand-alone and integrated) ¦ 각 장비별 개별제어 및 통합제어 성능은 적합한가 (stand-alone and integrated) ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 (인) ¦ 확인일 ¦ 확인일 ¦ ¦ 회사명(상호) ¦ ¦ ¦ ¦ ¦ ¦ 회사명(상호) ¦ ¦ ¦ (인) ¦ (인) ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/m2 ] 78 기계설비 기술기준 매뉴얼 | {}
7b398532-1040-4cd6-ae0b-ebdb78351dbb | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 [별표 11] 자동제어설비의 사용 전 검사 적합/부적합 판단기준 ¦ ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도서 ¦ 도서 ¦ 자동제어설비 관련 준공도서를 모두 확인하였다면 적합으로 함 [준공도서] 준공도서(준공도면, 시방서, 부하 및 장비선정 계산서 등) 가 모두 구비되어 있는 지 확인 ¦ ¦ 준공도서 ¦ ¦ 자재 ¦ 자재 ¦ 장비일람표, 시방서 등의 설계사항을 반영한 주요 장비 및 기자재 구 매, 반입 및 관련 도서를 확인하고, 설치된 배관의 사양과 규격 일치 여부를 확인하였다면 적합으로 함 [검토서] 설계대로 발주된 주요 장비 및 기자재 자재승인서와 자재검수요 청서 확인하여 일치여부를 기계설비감리업무수행자가 확인한 경우 적합 으로 함 ¦ ¦ 검토서(자재승인서, 자재검수요청서 등) ¦ ¦ 시공 ¦ 1 ¦ 중앙관제설비 설비는 3.1 의 조건을 만족할 경우 적합으로 함 [검토서] 준공도서의 자동제어 계통도/평면도/상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 11] 3.1 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 2 ¦ 건물에너지관리시스템은 3.2 의 조건을 만족할 경우 적합으로 함 [검토서] 준공도서의 자동제어 계통도/평면도/상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 11] 3.2 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 3 ¦ 현장제어설비는 3.3.1, 3.3.2 의 조건을 만족할 경우 적합으로 함 [검토서] 준공도서의 자동제어 계통도/평면도/상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 11] 3.3.1 3.3.2 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 4 ¦ 원격검침설비는 3.4 의 조건을 만족할 경우 적합으로 함 [검토서] 준공도서의 자동제어 계통도/평면도/상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 11] 3.4 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 5 ¦ 공동주택 자동제어설비는 3.5 의 조건을 만족할 경우 적합으로 함 [검토서] 준공도서의 자동제어 계통도/평면도/상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 11] 3.5 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 6 ¦ 배관 및 배선 시공 완료 후 외면 등의 마감상태를 확인하여 손상된 부분이 없는 것을 확인한 경우 적합으로 함 [검토서] 현장사진을 통해 배관 및 배선의 마감상태 및 손상여부를 기 계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 11] 3.3.3 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 7 ¦ 성능 1~6 이 확인된 경우 적합으로 함 ¦ 、 ¦ ¦ ¦ 성능 ¦ 1 ¦ 중앙관제설비 시운전을 실시하여 정상운전 상태를 확인한 경우 적합 으로 함 [시운전보고서] 시운전 시 기계설비감리업무수행자가 적합여부 확인 한 경우, 적합으로 함 ¦ ¦ 시운전보고서 ¦ ¦ 성능 ¦ 2 ¦ 건물에너지 관리 시스템 시운전을 실시하여 정상운전 상태를 확인한 경우 적합으로 함 [시운전보고서] 시운전 시 기계설비감리업무수행자가 적합여부 확인 한 경우, 적합으로 함 ¦ ¦ 시운전보고서 ¦ ¦ 성능 ¦ 3 ¦ 현장제어설비 시운전을 실시하여 정상운전 상태를 확인한 경우 적합 으로 함 [시운전보고서] 시운전 시 기계설비감리업무수행자가 적합여부 확인 한 경우, 적합으로 함 ¦ ¦ 시운전보고서 ¦ ¦ 성능 ¦ 4 ¦ 원격검침설비 시운전을 실시하여 정상운전 상태를 확인한 경우 적합 으로 함 [시운전보고서] 시운전 시 기계설비감리업무수행자가 적합여부 확인 한 경우, 적합으로 함 ¦ ¦ 시운전보고서 ¦ ¦ 성능 ¦ 5 ¦ 공동주택 자동제어설비 시운전을 실시하여 정상운전 상태를 확인한 경우 적합으로 함 [시운전보고서] 시운전 시 기계설비감리업무수행자가 적합여부 확인 ¦ - ¦ 시운전보고서 ¦ 국토교통부 79 기계설비 기술기준 판단기준 | {}
cf9e0ab9-4e4c-4c29-9d37-3d866aa61ed2 | 국내_기계설비_기술기준_매뉴얼_최종본 | ¦ ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ ¦ 한 경우, 적합으로 함 ¦ ¦ ¦ ¦ 6 ¦ 각 장비별 개별제어 및 통합제어 시운전을 실시하여 정상운전 상태 를 확인한 경우 적합으로 함 [시운전보고서] 시운전 시 기계설비감리업무수행자가 적합여부 확인 한 경우, 적합으로 함 ¦ ¦ 시운전보고서 ¦ ¦ ¦ 7 ¦ 성능시험 성적서 발행기관의 적정성, 성적서의 유효기간 등을 확인 한 경우 적합으로 함 [시험성적서] 제출된 시험성적서의 적정성, 유효기간 등을 확인 ¦ - ¦ 시험성적서 ¦ ¦ ¦ 유지 관리 ¦ 1 ¦ 「기계설비 유지관리기준」 제 6 조제 2 항 기계설비 시스템 운용 매뉴얼 (기계설비 제조사의 검사결과 또는 성적서 포함, 자동제어설비)을 갖 춘 경우 적합으로 함 [매뉴얼] 기계설비 시스템 운용 매뉴얼에서 자동제어설비 목차 및 내 용 확인 ¦ ¦ 기계설비 시스템 운용 매뉴얼 ¦ ¦ 유지 관리 ¦ 2 ¦ [별표 1] 열원 및 냉난방설비/신재생설비의 사용 전 확인표를 만족할 경우, 적합으로 함 [별표 2] 공기조화설비의 사용 전 확인표를 만족할 경우, 적합으로 함 [별표 3] 환기설비의 사용 전 확인표를 만족할 경우, 적합으로 함 [별표 8] 배관설비의 사용 전 확인표를 만족할 경우, 적합으로 함 [별표 9] 덕트설비의 사용 전 확인표를 만족할 경우, 적합으로 함 ¦ [별표 1] [별표 2] [별표 3] [별표 8] [별표 9] ¦ ¦ ※ 모든 항목은 기계설비감리업무수행자의 확인을 받아 관련항목이 적합하다고 인정받는 경우, 적합으로 함 ※ 판단기준 조건을 만족하는 서류(ex 감리관련서류, 관련 용역보고서 등)가 있을 경우, 필요서류를 대체할 수 있음 80 기계설비 기술기준 매뉴얼 | {}
27a70438-c825-41bb-a7d3-983cc674e05c | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 [별표 12] 방음 · 방진 · 내진설비의 사용 전 확인표_[별지 제 3 호 서식] ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 12] ¦ [별표 12] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ 방음·방진·내진설비 ¦ 방음·방진·내진설비 ¦ ¦ 공 종 ¦ 방음·방진·내진설비 ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ ] ¦ [] 적합 [ ] 부적합 ¦ ¦ 자 재 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 각종 장비의 방음·방진설비 설치는 기술기준에 적합한가 ¦ 각종 장비의 방음·방진설비 설치는 기술기준에 적합한가 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 각종 장비의 내진설비 설치는 기술기준에 적합한가 ¦ 각종 장비의 내진설비 설치는 기술기준에 적합한가 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 배관의 방음·방진·내진 설비는 기술기준에 적합한가 ¦ 배관의 방음·방진·내진 설비는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 방음·방진 기초설비 및 보강재의 설치는 기술기준에 적합한가 ¦ 방음·방진 기초설비 및 보강재의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 내진기초설비 및 보강재의 설치는 기술기준에 적합한가 ¦ 내진기초설비 및 보강재의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 방음·방진·내진설비의 공간배치는 기술기준에 적합한가 ¦ 방음·방진·내진설비의 공간배치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 이중바닥(잭업) 시스템의 설치는 기술기준에 적합한가 ¦ 이중바닥(잭업) 시스템의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 방음·방진·내진설비의 마감상태는 기술기준에 적합한가 ¦ 방음·방진·내진설비의 마감상태는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 각종 장비의 방음설비 성능은 적합한가 ¦ 각종 장비의 방음설비 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 각종 장비의 방진설비 성능은 적합한가 ¦ 각종 장비의 방진설비 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 각종 장비의 내진설비 성능은 적합한가 ¦ 각종 장비의 내진설비 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 (인) ¦ 확인일 ¦ 확인일 ¦ ¦ 회사명(상호) ¦ ¦ ¦ ¦ ¦ ¦ 회사명(상호) ¦ ¦ ¦ (인) ¦ (인) ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/m2 ] 국토교통부 81 기계설비 기술기준 판단기준 | {}
b2e6f271-c327-4820-a641-d88028d750f2 | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 12] 방음 · 방진 · 내진설비의 사용 전 검사 적합/부적합 판단기준 ¦ ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도서 ¦ 도서 ¦ 방음·방진·내진설비 관련 준공도서를 모두 확인하였다면 적합으로 함 [준공도서] 준공도서(준공도면, 시방서, 부하 및 장비선정 계산서 등) 가 모두 구비되어 있는 지 확인 ¦ ¦ 준공도서 ¦ ¦ 자재 ¦ 자재 ¦ 장비일람표, 시방서 등의 설계사항을 반영한 주요 장비 및 기자재 구 매, 반입 및 관련 도서를 확인하고, 설치된 배관의 사양과 규격 일치 여부를 확인하였다면 적합으로 함 [검토서] 설계대로 발주된 주요 장비 및 기자재 자재승인서와 자재검수요 청서 확인하여 일치여부를 기계설비감리업무수행자가 확인한 경우 적합 으로 함 ¦ ¦ 검토서(자재승인서, 자재검수요청서 등) ¦ ¦ 시공 ¦ 1 ¦ 각종 장비의 방음·방진설비 설치는 3.2.1~3.2.3 의 조건을 만족할 경우 적합으로 함 [검토서] 준공도서의 방음·방진설비 평면도/상세도에서 관련내용과 설 치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 12] 3.2.1 ~3.2.3 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 2 ¦ 각종 장비의 내전설비 설치는 3.3.1 (1) (2) (6)의 조건을 만족할 경우 적합으로 함 [검토서] 준공도서의 내진설비 평면도/상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 12] 3.3.1 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 3 ¦ 배관의 방음·방진·내진설비는 3.2.4, 3.3.2 의 조건을 만족할 경우 적합으 로 함 [검토서] 준공도서의 방음·방진·내진설비 평면도/상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 12] 3.2.4 3.3.2 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 4 ¦ 방음·방진 기초설비 및 보강재의 설치는 3.2.2 (3), 3.2.3 (5) 3.2.6 (1)의 조건을 만족할 경우 적합으로 함 [검토서] 준공도서의 방음·방진·내진설비 평면도/상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 12] 3.2.2 (3) 3.2.3 (5) 3.2.6 (1) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 5 ¦ 내진기초설비 및 보강재의 설치는 3.3.1 (3) (4) (5)의 조건을 만족할 경 우 적합으로 함 [검토서] 준공도서의 방음·방진·내진설비 평면도/상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 12] 3.3.1 (3) (4) (5) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 6 ¦ 유지관리 2 를 만족할 경우, 적합으로 함 ¦ - ¦ ¦ ¦ 시공 ¦ 7 ¦ 이중바닥(잭업) 시스템의 설치는 3.2.7 의 조건을 만족할 경우 적합으로 함 [검토서] 준공도서의 방음·방진·내진설비 평면도/상세도에서 관련내용과 설치된 사진을 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ [별표 12] 3.2.7 ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 시공 ¦ 8 ¦ 방음·방진·내진설비 시공 완료 후 마감상태를 확인하여 손상된 부분 이 없는 것을 확인한 경우 적합으로 함 [검토서] 현장사진을 통해 방음·방진·내진설비의 마감상태 및 손상여 부를 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ ¦ 검토서 (현장사진 등) ¦ ¦ 성능 ¦ 1 ¦ 시운전하여 2.1 표 1 의 실내허용소음기준을 만족하는 경우 적합으로 함 [보고서] 각종 장비를 시운전하여 실내허용소음기준에 만족하는 소음 측정결과 를 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ ¦ 소음측정보고서 ¦ ¦ 성능 ¦ 2 ¦ 시운전하여 장비, 배관, 덕트의 진동 및 소음 상태를 확인하는 경우 적합으로 함 [보고서] 각종 장비를 시운전하여 장비, 배관, 덕트의 진동 및 소음 상태 를 기계설비감리업무수행자가 확인한 경우, 적합으로 함 ¦ ¦ 시운전보고서 ¦ ¦ 성능 ¦ 3 ¦ 설치된 내진제품의 공인기관 내진시험 성적서를 확인한 경우 적합으 로 함 [시험성적서] 제출된 시험성적서의 적정성, 유효기간 등을 확인한 경 ¦ - ¦ 시험성적서 ¦ 82 기계설비 기술기준 매뉴얼 | {}
d7756a6b-eec5-467a-bfc2-487bcffa12b9 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 ¦ ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ ¦ 우 적합으로 함 ¦ ¦ ¦ ¦ 4 ¦ 성능시험 성적서 발행기관의 적정성, 성적서의 유효기간 등을 확인 한 경우 적합으로 함 [시험성적서] 제출된 시험성적서의 적정성, 유효기간 등을 확인 ¦ ¦ 시험성적서 ¦ ¦ ¦ 유지 관리 ¦ 1 ¦ 「기계설비 유지관리기준」 제 6 조제 2 항 기계설비 시스템 운용 매뉴얼 (기계설비 제조사의 검사결과 또는 성적서 포함, 방음·방진·내진설비) 을 갖춘 경우 적합으로 함 [매뉴얼] 기계설비 시스템 운용 매뉴얼에서 방음·방진·내진설비 목차 및 내용 확인 ¦ ¦ 기계설비 시스템 운용 매뉴얼 ¦ ¦ 유지 관리 ¦ 2 ¦ [별표 1] 열원 및 냉난방설비/신재생설비의 사용 전 확인표를 만족할 경우, 적합으로 함 [별표 2] 공기조화설비의 사용 전 확인표를 만족할 경우, 적합으로 함 [별표 3] 환기설비의 사용 전 확인표를 만족할 경우, 적합으로 함 [별표 8] 배관설비의 사용 전 확인표를 만족할 경우, 적합으로 함 [별표 9] 덕트설비의 사용 전 확인표를 만족할 경우, 적합으로 함 ¦ [별표 1] [별표 2] [별표 3] [별표 8] [별표 9] ¦ ¦ ※ 모든 항목은 기계설비감리업무수행자의 확인을 받아 관련항목이 적합하다고 인정받는 경우, 적합으로 함 ※ 판단기준 조건을 만족하는 서류(ex 감리관련서류, 관련 용역보고서 등)가 있을 경우, 필요서류를 대체할 수 있음 기계설비 기술기준 판단기준 국토교통부 83 | {}
1d56bd49-b6b5-4405-afdd-6f4f38b92952 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 착공 전 확인 및 사용 전 검사 검토서 작성 예시 (1) 기계설비 착공 전 확인 검토서 ① 기계설비 착공 전 확인 적합/부적합 판단을 위한 업무 수행 시 이 검토서를 이용하여 필요한 서류를 작성할 수 있다. ② 착공 전 확인 검토서 작성 예시 기계설비 착공 전 확인 검토서 ¦ 구분 ¦ 검 사 항 목 ¦ 해당 여부 ¦ 해 당 근 거 ¦ 첨부 서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 별표 1 ¦ 집단에너지 공급대상지역 적용 여부 확인 ¦ [V] ¦ -질의 회신(첨부 1) 집단에너지 공급대상지역 확인 ¦ 첨부 1 ¦ ¦ 별표 1 ¦ 냉난방 설계기준 온도 적용 여부 확인 ¦ [V] ¦ -계산서(첨부 2)에 설계기준 온도 적용 > 실내 온·습도 조건은 : 사무소 > 외기 온·습도 조건 : 부산 ¦ 첨부 2 ¦ ¦ 별표 1 ¦ 냉각탑 수처리 설비 적용 여부 확인 ¦ [V] ¦ -장비일람표(첨부 3) 냉각수 수처리설비 적용 ¦ 첨부 3 ¦ ¦ 별표 1 ¦ 축열시설 40%이상 부분냉방식 적용 여부 확인 ¦ [V] ¦ -검토서(첨부 4)에 축열시설(빙축열, 수축열) 42% 적용 확인 ¦ 첨부 4 ¦ ¦ 별표 1 ¦ 열교환기 안전밸브 설치 적용 여부 확인 ¦ [V] ¦ -설계도면(첨부 5)에 열교환기 안전밸브 적용 확인 ¦ 첨부 5 ¦ ¦ 별표 1 ¦ 팽창탱크 배관의 역류방지밸브 적용 여부 확인 ¦ [V] ¦ -설계도면(첨부 6) 팽창탱크에 각각 역류방지밸브 적 용(난방, 급탕 2 대 적용) ¦ 첨부 6 ¦ ¦ 별표 1 ¦ 펌프 효율은 KS 규격 이상 적용 여부 확인 ¦ [V] ¦ -장비일람표(첨부 3)에 KS 규격이상 제품 명기 ¦ 첨부 3 ¦ ¦ 별표 1 ¦ 항온항습기 비상전원 적용 여부 확인 ¦ [] ¦ -항온항습기 없음 ¦ - ¦ ¦ 별표 2 ¦ 건축물의 규모 및 형태에 따른 공기조화 조닝 적용 여부 확인 ¦ [V] ¦ -검토서(첨부 8) 용도별 공조조닝 분리(오피스텔/근린 생활시설) 확인 ¦ 첨부 7 ¦ ¦ 별표 2 ¦ 팬코일의 열수요 변화 대응 적용 여부 확인 ¦ [V] ¦ -장비일람표(첨부 9) 팬코일 유니트의 4 단 풍량조절 기 능 적용 ¦ 첨부 8 ¦ ¦ 별표 3 ¦ 건축물 및 시설물의 필요 환기량 적용 여부 확인 ¦ [V] ¦ -검토서(첨부 10) 계산서에 기술기준에 적합한 필요환 기량 적용여부 확인 ¦ 첨부 9 ¦ ¦ 별표 3 ¦ 시설 용도에 맞는 환기방식 적용 여부 확인 ¦ [V] ¦ -검토서(첨부 11) 용도별로 적합한 필요환기 방식 여부 확인 ①기계실 ②발전기실 ③발전기실 ④전기실 ⑤EV 기계실 ⑥ 지하주차장 ⑦주방 ⑧수영장 ⑨정화조 ¦ 첨부 10 ¦ ¦ 별표 3 ¦ 환기설비의 열교환 효율 기입 적용 여부 확인 ¦ [V] ¦ -장비일람표(첨부 3)에 사용용도, 형식, 용량, 냉·난방 열교환 효율 명기 확인 ¦ 첨부 3 ¦ ¦ 별표 4 ¦ 위생기구 종류에 따른 사용조건 적용 여부 확인 ¦ [V] ¦ -검토서(첨부 11)의 시방서와 위생기구일람표의 위생 기구 종류별 세부항목 설계 확인 ¦ 첨부 11 ¦ ¦ 별표 4 ¦ 설치장소와 이용자의 편의 성 적용 여부 확인 ¦ [V] ¦ -검토서(첨부 12)의 시방서와 위생기구일람표의 위생 기구 종류별 세부항목 설계 확인 ¦ 첨부 12 ¦ ¦ 별표 4 ¦ 위생설비별 절수기능 적용 여부 확인 ¦ [V] ¦ -위생기구일람표(첨부 13)에 "절수형제품 적용" 확인 ¦ 첨부 13 ¦ ¦ 별표 5 ¦ 음료용 급수의 음용수 전용 공급 여부 확인 ¦ [V] ¦ -검토서(첨부 14) 음용수 전용 급수배관 설계안 확인 ¦ 첨부 14 ¦ ¦ 별표 5 ¦ 저수조 최대급수량에 따른 오버플로관 적용 여부 확인 ¦ [V] ¦ -검토서(첨부 15) 오버플로관 관련사항 확인 ¦ 첨부 15 ¦ ¦ 별표 5 ¦ 급탕탱크방식의 팽창탱크 적용 여부 확인 ¦ [] ¦ -지역열원에 의한 순간가열식 급탕시스템으로 해당사 항 없음 ¦ - ¦ 84 기계설비 기술기준 매뉴얼 | {}
1e24eefe-d0c5-44b0-991c-25ca4fede42f | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 기계설비 착공 전 확인 검토서 ¦ 구분 ¦ 검 사 항 목 ¦ 해당 여부 ¦ 해 당 근 거 ¦ 첨부 서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 별표 6 ¦ 오배수 집수정크기 적정 여부 확인 ¦ [V] ¦ -설계도면(첨부 16)에서 기술기준을 준수하는 개방형 집수정 크기 적용 확인 ¦ 첨부 16 ¦ ¦ 별표 6 ¦ 오배수 배관 청소구 적용 여부 확인 ¦ [V] ¦ -검토서(첨부 17)의 도면과 시방서에서 관련사항 확인 ¦ 첨부 17 ¦ ¦ 별표 6 ¦ 집수정 펌프 배관과 토출관 배관 크기 확인 ¦ [V] ¦ -검토서(첨부 18)의 도면에서 관련사항 확인 ¦ 첨부 18 ¦ ¦ 별표 7 ¦ 하수도법에 따른 개인하수처리시설의 설치기준 적용 여부 확인 ¦ [] ¦ -공문(첨부 19)에서 ○○시 하수도과 공문 결과 개인하 수처리시설 적용 -검토서(첨부 20)에서 오수발생량 기준에 따른 정화조 설계 확인 ¦ 첨부 19 첨부 20 ¦ ¦ 별표 7 ¦ 오수발생량과 정화조 처리대상인원의 고시기준 적용 여부 확인 ¦ [] ¦ -검토서(첨부 21)의 2022 년 고시안(22-00112001) 그대 로 계산서 명기 ¦ 첨부 21 ¦ ¦ 별표 7 ¦ 빗물저류조 시설 적용 여부 확인 ¦ [V] ¦ -검토서(첨부 22)의 빗물저류조(200ton)의 관련사항 확인 ¦ 첨부 22 ¦ ¦ 별표 8 ¦ 냉온수배관의 신축이음 적용 여부 확인 ¦ [V] ¦ -검토서(첨부 23) 도면과 계산서에서 신축이음 관련 사 항 확인 ¦ 첨부 23 ¦ ¦ 별표 8 ¦ 용도에 맞는 배관 선정 및 호칭지름 적용 여부 확인 ¦ [V] ¦ -검토서(첨부 24)시방서, 도면, 계산서에서 배관 관련 사항 확인 ¦ 첨부 24 ¦ ¦ 별표 8 ¦ 고압증기배관의 압력배관 적용 여부 확인 ¦ [] ¦ 고압증기배관 없음 ¦ ¦ ¦ 별표 9 ¦ 사용용도에 따른 덕트 적용 여부 확인 ¦ [V] ¦ -검토서(첨부 25) 시방서에 관련사항을 명기하고, 근린생 활시설 주방배기 덕트 스테인리스강 덕트 적용 확인 ¦ 첨부 25 ¦ ¦ 별표 9 ¦ 외기도입구와 배기구 적용 여부 확인 ¦ [V] ¦ -검토서(첨부 26) 설계도면에서 외기도입구/배기구 관 련사항 확인 ¦ 첨부 26 ¦ ¦ 별표 10 ¦ 배관 및 덕트 등 보온설비 적용 여부 확인 ¦ [V] ¦ -검토서(첨부 27) 시방서에서 배관 및 덕트 보온설비 관련사항 확인 ¦ 첨부 27 ¦ ¦ 별표 10 ¦ 수도계량기보호함의 보온 적용 여부 확인 ¦ [V] ¦ -검토서(첨부 28) 시방서에서 수도계량기보호함 보온 설비 관련사항 확인 ¦ 첨부 28 ¦ ¦ 별표 10 ¦ 동파방지 열선 적용 및 이상 여부 확인 ¦ [V] ¦ -검토서(첨부 29) 시방서 및 도면에서 지하 1 층 주차장 동파방지열선 관련사항 확인 ¦ 첨부 29 ¦ ¦ 별표 11 ¦ 경보 및 감시시스템 적용 여부 확인 ¦ [V] ¦ -검토서(첨부 30) 도면에서 자동제어 관련사항 확인 (BEMS, CCMS) ¦ 첨부 30 ¦ ¦ 별표 11 ¦ 원격검침 시스템 적용 여부 확인 ¦ [V] ¦ -검토서(첨부 31) 원격검침 관련사항 확인 ¦ 첨부 31 ¦ ¦ 별표 12 ¦ 방음 ·방진· 내진 등 적용 여부 확인 ¦ [V] ¦ -검토서(첨부 32) 방음방진설비의 관련사항 확인 ¦ 첨부 32 ¦ 기계설비 기술기준 판단기준 국토교통부 85 | {}
aa400548-74ad-49a9-8245-8db5dde8b2f7 | 국내_기계설비_기술기준_매뉴얼_최종본 | ¦ (2) 기계설비 사용 전 검사 검토서 ¦ ¦ --- ¦ ¦ ① 기계설비 사용 전 검사 적합/부적합 판단을 위한 업무 수행 시 이 검토서를 이용하여 필요한 서류를 작성할 수 있다. ¦ ¦ ② 사용 전 검사 검토서 작성 예시 ¦ 기계설비 사용 전 검사 검토서[별표 1 열원 및 냉난방] ¦ 구분 ¦ 검 사 항 목 ¦ 해당 여부 ¦ 해 당 근 거 ¦ 첨부 서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도서 ¦ 준공도서는 기술기준에 적합한가(준공 도면, 시방서) ¦ [V] ¦ -준공도서(첨부 1)(준공도면,시방서, 계산서) 확인 ¦ 첨부 1 ¦ ¦ 자재 ¦ 주요기자재 선정 및 사용은 적합한가 ¦ [V] ¦ -검토서(첨부 2)의 주요기자재 납품확인서(냉온수기, 보일러, 펌프 등), 자재승인서, 자재검수요청서를 기 계설비감리업무수행자 적합 확인 ¦ 첨부 2 ¦ ¦ 시공 ¦ 1. 냉동기, 냉온수기 설치는 기술기준에 적합한가 ¦ [V] ¦ -한국가스안전공사 완성검사 확인서(첨부 3) 확 1-1 인(흡수식 냉온수기 2 대) ¦ 첨부 3 ¦ ¦ 시공 ¦ 1. 냉동기, 냉온수기 설치는 기술기준에 적합한가 ¦ [V] ¦ -검토서(첨부 4)의 냉온수기 접속하는 냉각수, 냉 1-2 수배관에 플렉시블이음 도면 및 사진을 기계설 비감리업무수행자 적합 확인 ¦ 첨부 4 ¦ ¦ 시공 ¦ 2. 보일러 설치는 기술기준에 적합한가 ¦ [V] ¦ -검토서(첨부 5)의 세대별로 개별보일러실에 일 2-1 산화탄소 경보기 시공 및 사진 확인 ¦ 첨부 5 ¦ ¦ 시공 ¦ 2. 보일러 설치는 기술기준에 적합한가 ¦ [V] ¦ -검토서(첨부 6)의 냉온수기/보일러 연도의 이음 2-2 에 내열성이 있는 자재 시공도면, 시공사진 및 기계설비감리업무수행자 적합 확인 ¦ 첨부 6 ¦ ¦ 시공 ¦ 3. 항온항습기, 열펌프 설치는 기술기준 에 적합한가 ¦ [] ¦ 3-1 -항온항습기 없음 ¦ - ¦ ¦ 시공 ¦ 3. 항온항습기, 열펌프 설치는 기술기준 에 적합한가 ¦ [] ¦ 3-2 -항온항습기 없음 ¦ - ¦ ¦ 시공 ¦ 3. 항온항습기, 열펌프 설치는 기술기준 에 적합한가 ¦ [] ¦ 3-3 -항온항습기 없음 ¦ 、 ¦ ¦ 시공 ¦ 4. 패키지 에어컨 설치는 기술기준에 합한가 ¦ 적 [V] ¦ -소음측정보고서(첨부 7)의 환경정책기본법 시행 4-1 령 [별표 1] 소음기준 만족 확인 ¦ 첨부 7 ¦ ¦ 시공 ¦ 4. 패키지 에어컨 설치는 기술기준에 합한가 ¦ 적 [V] ¦ -검토서(첨부 8)의 실외기 설치금지항목을 기계 4-2 설비감리업무수행자 적합 확인 ¦ 첨부 8 ¦ ¦ 시공 ¦ 4. 패키지 에어컨 설치는 기술기준에 합한가 ¦ 적 [V] ¦ -검토서(첨부 9)의 실외기 전용의 차단개폐기 도면 4-3 및 사진을 기계설비감리업무수행자 적합 확인 ¦ 첨부 9 ¦ ¦ 시공 ¦ 5. 냉각탑 설치는 기술기준에 적합한가 ¦ [V] ¦ -검토서(첨부 10)의 냉각탑 콘크리트 기초 시공 및 사 진 확인 ¦ 첨부 10 ¦ ¦ 시공 ¦ 6. 펌프 설치는 기술기준에 적합한가 ¦ [V] ¦ -검토서(첨부 11)의 펌프 주위 기초 배수홈 배수구 설 치 및 32A 이상 배관 간접배수 확인 ¦ 첨부 11 ¦ ¦ 시공 ¦ 7. 열교환기 설치는 기술기준에 적합한가 ¦ [V] ¦ -열사용기가재 안전검사 확인서(첨부 12) ¦ 첨부 12 ¦ ¦ 시공 ¦ 8. 탱크류 설치는 기술기준에 적합한가 ¦ [V] ¦ -검토서(첨부 13)의 저수조, 팽창탱크 콘크리트 기초 시공 및 사진 확인 ¦ 첨부 13 ¦ ¦ 시공 ¦ 9. 장비별 배관 접속은 기술기준에 적합한가 ¦ [V] ¦ [별표 8] 사용전검사 검토표 확인 ¦ - ¦ ¦ 성능 ¦ 10. 열원기기의 명판 및 마감상태는 적 합한가 열원기기류의 작동과 성능은 적합한가 ¦ [V] [V] ¦ -검토서(첨부 14)의 열원기기별 명판 및 마감상태 사 진 확인 -시운전보고서(첨부 15)의 냉온수기, 보일러 등 시운 전하여 작동상태 및 성능기준을 기계설비감리업무 수행자 적합 확인 ¦ 첨부 14 ¦ ¦ 성능 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ [V] ¦ -시험성적서(첨부 16) 적정성 확인 ¦ 첨부 15 첨부 16 ¦ ¦ 유지 관리 ¦ 유지관리(운전관리 등) 지침서는 적합한 가 ¦ [V] ¦ -기계설비 시스템 운용 매뉴얼(첨부 17) 열원설비 목 차 및 내용 확인 ¦ 첨부 17 ¦ ¦ 유지 관리 ¦ 유지관리공간은 적합한가 ¦ [V] ¦ -검토서(첨부 18)의 기계실, 샤프트, 장비반출입 공간 등 [별표 15] 2. 기준 만족을 기계설비감리업무수행 자 적합 확인 ¦ 첨부 18 ¦ 86 기계설비 기술기준 매뉴얼 | {}
687c255f-a89d-4a0c-96a1-cbe28e2b87b8 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 ③ 사용 전 검사 검토서 작성 예시_첨부서류 첨부 10 기계설비 사용 전 검사 검토서 ¦ 1.현 장 명 ¦ 서울시 강남구 00 로 01 00 빌딩 신축공사 ¦ 서울시 강남구 00 로 01 00 빌딩 신축공사 ¦ 서울시 강남구 00 로 01 00 빌딩 신축공사 ¦ 서울시 강남구 00 로 01 00 빌딩 신축공사 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 2.작 성 자 ¦ 회사이름 ¦ 회사이름 ¦ 00 건설 작성인 ¦ 이몽룡 ¦ ¦ 3.작성항목 ¦ 사용 전 확인표 ¦ 별표 ¦ [별표 1] 열원 및 냉난방 ¦ [별표 1] 열원 및 냉난방 ¦ ¦ 3.작성항목 ¦ 사용 전 확인표 ¦ 구분 ¦ 시공 5. 냉각탑 설치는 기술기준에 적합한가 ¦ 시공 5. 냉각탑 설치는 기술기준에 적합한가 ¦ ¦ 3.작성항목 ¦ 기계설비 기술기준 매뉴얼 ¦ 기계설비 기술기준 ¦ [별표 1] 3.3 냉각탑 (1) ¦ [별표 1] 3.3 냉각탑 (1) ¦ ¦ 3.작성항목 ¦ 기계설비 기술기준 매뉴얼 ¦ 5 사용 전 검사 판단기준 ¦ 표면을 모르타르로 마감한 콘크리트기초 또는 형강제 받침대 위에 자중, 적설, 풍압, 지진 기타의 진동에 대하여 안전하게 냉각탑을 시공한 경우 적합으로 함 [도면/사진] 준공도면의 냉각탑 설치상세도에서 관련사항을 확인하고 설치된 사진 첨부 확인 ¦ 표면을 모르타르로 마감한 콘크리트기초 또는 형강제 받침대 위에 자중, 적설, 풍압, 지진 기타의 진동에 대하여 안전하게 냉각탑을 시공한 경우 적합으로 함 [도면/사진] 준공도면의 냉각탑 설치상세도에서 관련사항을 확인하고 설치된 사진 첨부 확인 ¦ ¦ 4.작성내용 ¦ ① 냉각탑 설치 대수 : 냉방용 2 대 확인(CT-1, CT-2) ② 냉각탑 설치 장소 : 옥상층 ③ 냉각탑 기초 : 콘크리트 기초(현장사진 참조), 방진 시공 ¦ ① 냉각탑 설치 대수 : 냉방용 2 대 확인(CT-1, CT-2) ② 냉각탑 설치 장소 : 옥상층 ③ 냉각탑 기초 : 콘크리트 기초(현장사진 참조), 방진 시공 ¦ ① 냉각탑 설치 대수 : 냉방용 2 대 확인(CT-1, CT-2) ② 냉각탑 설치 장소 : 옥상층 ③ 냉각탑 기초 : 콘크리트 기초(현장사진 참조), 방진 시공 ¦ ① 냉각탑 설치 대수 : 냉방용 2 대 확인(CT-1, CT-2) ② 냉각탑 설치 장소 : 옥상층 ③ 냉각탑 기초 : 콘크리트 기초(현장사진 참조), 방진 시공 ¦ ¦ 5.첨부파일 ¦ ① 준공도면 - 공조배관 옥상층 평면도/냉각탑 상세도 ② 현장사진 - 냉각탑 기초 사진 ¦ ① 준공도면 - 공조배관 옥상층 평면도/냉각탑 상세도 ② 현장사진 - 냉각탑 기초 사진 ¦ ① 준공도면 - 공조배관 옥상층 평면도/냉각탑 상세도 ② 현장사진 - 냉각탑 기초 사진 ¦ ① 준공도면 - 공조배관 옥상층 평면도/냉각탑 상세도 ② 현장사진 - 냉각탑 기초 사진 ¦ ¦ 6.검 토 자 ¦ 8 기계설비 감리업무수행자 ¦ 00 감리 ¦ 현장배치 기계설비 감리인 ¦ 홍길동 ¦ ¦ 6.검 토 자 ¦ 10 검토일 ¦ 2022.04.01 ¦ 11 검토의 견 ¦ 적합 ¦ ¦ 6.검 토 자 ¦ 본 기계설비 사용 전 검사 검토서가 「기계설비 기술기준」 관련사항에 따라 적합하게 작성되었음을 확인함 현장배치기계설비감리인 : 홍 길 동 (인/싸인) 210mmX297mm[백상지 80g/m2] ¦ 본 기계설비 사용 전 검사 검토서가 「기계설비 기술기준」 관련사항에 따라 적합하게 작성되었음을 확인함 현장배치기계설비감리인 : 홍 길 동 (인/싸인) 210mmX297mm[백상지 80g/m2] ¦ 본 기계설비 사용 전 검사 검토서가 「기계설비 기술기준」 관련사항에 따라 적합하게 작성되었음을 확인함 현장배치기계설비감리인 : 홍 길 동 (인/싸인) 210mmX297mm[백상지 80g/m2] ¦ 본 기계설비 사용 전 검사 검토서가 「기계설비 기술기준」 관련사항에 따라 적합하게 작성되었음을 확인함 현장배치기계설비감리인 : 홍 길 동 (인/싸인) 210mmX297mm[백상지 80g/m2] ¦ 국토교통부 87 기계설비 기술기준 판단기준 | {}
d3fb1454-36ac-40cb-9c0f-b84e4fe81adc | 국내_기계설비_기술기준_매뉴얼_최종본 | ① "현장명"이란 「기계설비 시행규칙」 [별지 4 호 서식] 기계설비공사 착공 전 확인신청서의 공사 현 장 명칭을 말한다. ② "작성자"란 기계설비 착공 전 확인 검토서를 작성하는 자를 말한다. ③ "사용전확인표"란 「기계설비 기술기준」 [별지 3 호 서식] 기계설비 사용 전 확인표을 말하며, 검토 가 필요한 별표와 내용을 명기한다. ④ "기계설비 기술기준"이란 "기계설비 기술기준 매뉴얼"의 기계설비 사용 전 검사 적합/부적합 판단 기준에서 본 검토사항에 대한 기계설비 기술기준 상의 근거부분을 그대로 명기한다. ⑤ "사용전검사 판단기준" 이란 "기계설비 기술기준 매뉴얼"의 기계설비 사용 전 검사 적합/부적합 판단기준에서 본 검토사항에 대한 부분을 그대로 명기한다. ⑥ "작성내용"이란 본 검토사항에 대해 핵심적인 내용으로 간단명료하게 작성한다. ⑦ "첨부파일"이란 ⑥작성내용을 증빙하기 위해 첨부된 자료를 말한다. ⑧ "기계설비감리업무수행자"란 「기계설비 기술기준」 제 2 조제 5 호의 「건설산업기본법」 제 2 조제 8 호, 「건설기술 진흥법」제 2 조제 5 호, 「건축법」제 2 조제 15 호, 「주택법」제 43 조 및 기타 관계 법령에 따 라 기계설비공사와 관련된 건설사업관리 및 감리업무 등을 수행하는 자를 말한다. ⑨ "현장배치기계설비감리인"이란 「기계설비 기술기준」 제 2 조제 7 호의 「건설기술 진흥법 시행령」제 60 조에 따라 기계설비공사 현장에 배치되어 제 5 호에 따른 기계설비공사의 감리업무를 수행하는 건설기술인, 「건축법」제 25 조에 따른 공사감리자 또는 「주택법」제 43 조에 따른 감리자를 말하며, 본 검토사항을 직접 검토해야 한다. ⑩ "검토일"이란 현장배치기계설비감리인이 본 검토사항에 대해 검토한 날을 말한다. ⑪ "검토의 견"에는 본 검토사항에 대한 검토의 견을 명기하며 적합/부적합으로 명기한다. 88 기계설비 기술기준 매뉴얼 | {}
a4753798-589a-4b6d-9b42-7642ef09671d | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 ④ 착공 전 확인 및 사용 전 검사 첨부서류 작성 예시 ![image](/image/placeholder) [ 첨부#1 ] 부산도시가스 I SK E&S 예시 48313 부산광역시 수영구 황령대로 513(남천동) (명지집단에너지팀 Tel: 051-607-1417 Fax:051-202-7366) 문서번호 : 제 2021-C04212 호 2021-11-10 수 신 : (주)웅도엔지니어링 황 조 : 제 목 : 지역열원 공급에 관한 질의 회신(명지동 3589-1 번지) 1. 귀사의 무궁한 발전을 기원합니다. 2. 문서번호 용도 2021-098 호(2021.11.02 오피스텔 신축공사와 관련하여 다음과 같이 회 신 하오니, 지역난방 설계 업무 추진에 반영하여 주시기 바랍니다. 가. 질의 1 열원 공급 가능여부 및 냉,난방 의무고시지역 여부 답변 지식경제부공고 제 2009-47 호(2009.2.12)에 의거하여 질의 하신 명지동 3589-1 번지는 집단에너지 공급대상지역에 해당됩니다. 또한 집단에너지사업법 시행령 제 8 조에 의거 냉난방 설계되어야 합니다. 나. 질의 2 예상시설 분담금 답변 공사비부담금 산정 및 부과 기준은 열공급규정 제 35 조(공사비부담금의 부과 기준 등) 참조, 제공하신 자료를 근거로 예상 공사비부담금을 산정하기 어렵습니다. 예상 공사비부담금 산정을 위해서는 난방열교환기 열량 및 급탕연결열부하를 산정하여 제출하여 주기기 바랍니다. 다. 질의 3 지역난방 1 차측 배관 공급 예상인입 위치 및 공급열원 온도조건 답변 첨부 위치도 참조 및 열공급규정 제 18 조(공급조건)을 참조하여 주시기 바랍니다. 구분 온도 합 력 공급온도 75°C~115°C 난방용 회수온도 35°C~55°C 온수 최대 16kg/cm2 공급온도 95°C±3°C 냉방용 회수온도 최고 80°C * 지하 기계실 위치는 인입위치와 근접하여 설치하여주시길 요청드리며, 열공급계약 후 협의 라. 질의 4 기타 권장사항 답변 : 건축 용도별 1 차 배관 및 계량장치를 각각 분리하여 주시기 바랍니다. * 열공급규정 및 열사용시설기준은 부산도시가스 홈페이지→안내→자료실에서 확인하실수 있습니다. 첨부 인입위치도 "끝" 주식회사 부산도시가스 免 样 되지 대 표 이 사 弯 국토교통부 89 기계설비 기술기준 판단기준 | {}
547e63fd-7611-46ab-8c50-d8abc7867fbc | 국내_기계설비_기술기준_매뉴얼_최종본 | ![image](/image/placeholder) 장비일람표-4 예시 wa's a'0 수 김수철 초음기준이상기품지음 때 M-007 - - NONE · 16 : 김철수 SCNI SAFE NONE A UP A 2022.01 全 · 여부관한 Whin 삶의 제조님은 제 46 으로 같이 일력보험 응급 철수현 기타표준투숙용 김치포함 [물표 1]냉작방 바른 필수기능 기타로운투숙을 별표 2 에 기타표준투숙용 및 일체포함 확률 제 1 조의 2 사용조건 밀체포함 일체포함 환경공지인증착용 일찍포함 포함, 기타표분투숙물 위생설비 적용, [수호법시행규칙] 기타표준부속품 손잡이 기타표종투숙품 환경표지인증제품 기타표준부속품 비고 [별표 4] 장애인용 일제조합 적용, 工智 비エ 적용, 손잡히 환경표자인증제품 타립형, ; 전자바임형, 기타표훈투숙물 적용, 개대주 환경표지인중개봉 혼합수전, 장애인동 전자 환경표자신용제품 일처포함 실적포함 실제조합 일러포항 일체포함 일차포함 일체포함 [수포법] 전기실), 상품비비식 기타표준투숙용 기타표준부숙품 투숙한 기타표준부속중 기타표준투숙용 부효용 기타표준투숙품 · 제공손주렁시닝 ThappinuE 감동식(전기식), RV 질수동, 활동식 기타표준 980W 기타표준 소비전혀 실수함. 철수형, 전자 전자 100 보수 100 100 008'+·089·08L (mm) 료 40 7 7 · · - · · 4 결 WIMIL.MM 규격 교수 60 60 16 , + , , / / 4 · - · · 접속관련 급된 16 16 · · · F 7 4 , , , . · . 사용압력 20 비만 ligium 교수 26 16 9 16 16 1 회 26 Z · · · · · 、 144 17 78 표 7 , 7 · · 7 4 4 · - SMB - 구 경 8 합계 출구 술 ww 음 접 입구 - 음 : F · 6 1 . . ▼ 8 · · , · · 4 16F Ch-V-Hz 1-220-03 18 8 , · ↓ 초 · · . / · 2 - 1 V 전환 사양 - 148 6 9 3 / · , , F 7 2 1 - - · 장비일람표 전기 소비용적 0.3 127 w 8 & · , · 8 · T , 2 · · ■ 8 125 8 ↓ 8 · , · 4 , , - · · · 1 wm 200,200,90 19 8 1 3 1 V , · , # ■ - · · 규정 WXHXL 컨트롤러 、 · V · · 10P 6 8 , · 1 · = # - 4 、 3 of , · , , , · - 7 · · - 수량 비고 1 , k 、 3 일처포함 , . 1 , . 실회포항 , · · · · · 설치수량 - ▶ 8 3 , , 뿐 · , 1 - · · - - 880-400-930 mm 기타표본부속품 기타표본부역품 Dispenser V 8 ▶ 3 , 규과 · · · 7 . , . , · · 하여 0 、 8 ↓ , · , . 7 7 . · · 4 4 8 A , 8 · , - · · , 7 · - ■ 수량 : 49 재질 BT8 RTD OF 、 ▶ 3 , T · · · + · . 1 - 100-186-219 " 2F 、 A 3 , · , , · , 1 · · . 22,000x7,000x1,700 12,000x6,000x2,000 규격 WXHAL & mm 8 그 1 , , · · · , , · · · 1 정량펌프 규격 WrHirL Bif 5 . , , 8 · · 1 · , , , 4 · Ilmin 위원 0.08 B2P 5 : , · · , · , · · · · · · BSP ¦ , · 7 · / · , / · . - · 수량 . . 통행 유효 210 100 一 B47 , · 1 , · / . · · , · . · · 설치위치 기계실 동풍이상, 설치위치 동봉이상 원본이상 동풍이상 동풍이상 KBU-812 동풍이상 동풍이상 기계실 기계실 모밀번호 고혜약품용해식 KBVD-R100 K8V0-8100 KBVO-9100 KBVL-10608 · . · - K88-6700 · · KOU-DID 식 형식 각형 각형 형 장치 대소구분동,F.VI F.V) 소전기(장애인용) 원프파폴리스원잭 철수형, 물비보디스원격 균 수처리용 냉각왕 1CT-01 냉각수 혼합수전 원드드라이어 용도 용도 취소수전 혼자결이 소변기 세평가 용도 비누대 살 표 비에 000000 시수자주조 준수 차수조 리 TEALIZAB celloical 대변기(장애인용) 사회 일 람 처 냉각수수 위생기구 [첨부 03] � z 而 + 参 : 、 . 수 W0-08 BH8-01 CT8-01 WO-01 wo-02 UR-02 LAY-01 UR-01 장비 번호 장비 번호 장비 번호 J0-01 T-01 T-02 , = 4 4 저 90 기계설비 기술기준 매뉴얼 | {}
10134205-2d33-401c-b544-7e296ceaac17 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 첨부 3 [장비일람표] 냉각탑 수처리 설비 확인 ![image](/image/placeholder) 1.현 장 명 서울시 강남구 00 로 01 00 빌딩 신축공사 2.작 성 자 회사이름 00 건설 작성인 이몽룡 착공전확인표 [별표 1] 냉각탑 수처리 설비 적용 여부 확인 3.작성항목 기계설비 냉각탑에 수처리 설비(냉각수 수질 오염 및 레지오넬라균 번식 착공전확인 기술기준 방지)를 적용하고, 이를 장비 일람표에 반영한 경우 적합으로 함 판단기준 매뉴얼 [도면] 장비 일람표 냉각탑에서 수처리 설비 명기 확인 요 제 ENON :: 10 :EV 800-W 군풍송 2022 NONE 장비일림표-1 페이지아 TICRABITALON 예시 : 보 最 세(190% 이어야 NISROGACIS 81-080 MIRTECTS - 별표 '아이비 · · m 블록움도 소 ◁ ◁ ◁ ◁ ◁ ◁ ◁ - : · 4 하나 kike http://www..ar.kr.vir T R 19 분야기 비용자가 (음) (☏ T N lacke 래 (방송금공)육 lc 로종 (g 송픔성)육 lcg 을 T · OH/MMI OB/DRE/E 05/022/2 OS/OBE/E 05/022/ T m %52 %5C.8÷8 피부속집물이 배급 피부 MOE NOVE 150 분을 눈을 등장표 796 국 급 三 ���� 吸引 70.6 과 010 長 kthe http 물자는 경영 AZ130 1,0 파트 news : 병 업 병 yw 과 ���� (8x) DES'S: (M) · 음부공공을 울농심공료(비 응용되는 (6x) 018°C 마다 제 ITHWNYIE 09/0ZZ/L 09/00/L F 전산 (WW) BREAP 유한 호 금융훈 자체 교수&h 과태 월 통 ⑩ 주 2 = 비 る be T 등 장 ④ 0199 0.22% 개 befa � 8 81020 하드 W 종목 Tanva COSLKMODEXHODE 0051KMOOZXHODE 술 이 DOE'r 0021 금 . 061 ~ 나는 4 바탕이 항공료는 화곡문자 + bi 류 SAWARMI OS/DRE/S 05/0RE/E 11 A1 - 05 분'9 009°C ⑩ 10%UNO3 キ 내 울융주수금 유금주독은 황금주수공 응급공동은 lecks 효과 ③ ③ NU Regiv48 09/DRE/E OS/2PE/E ▼ Fale ama 10,010 16,210 hereha-Beak 물누슈로프 - ※ (wws ==== 총 양 will)들은유 CLAILLIBE QUISZLXBE 월 M 100 라자도 PAPE ※ inte⌀h 90ndd COMEMIH LD*dd 뉴포스스 및 가 和 = 등 器 HOSEX.10PP HZZZX70LL 병원 병 도입 50 52 법 현금초 · · 병 ta 00000 높은 · (PIRS) Z···DGE Y·ELE 종별 종 그 kn 또는 월 SLE 보내 9LE BLE BLE 번 류 금종 농동송 요금 화학송 차 r E E SLS SIS E - ��� (ww. ※ 괄 ト& NY:09 NER 신 7 명칭 행 병원 예비 영업 결 8ph aph 급 1 끝 표 소불법 to 수 죽 사 람 소식을 7 2 의 호 ����� 이야 2 1282000 원 hattle 0011CX10M 0025LX125L baks Oftoa/Ge = 본 : 본 2 a : 우 교 일 알고 따라 929°C 소문동메뉴 (인) 2.0 의 (Wilk - 화 을 12 8 록 발 3 续 비 P 9 ⑩ F 梁 모 10 NEW 19 滋 손花로保 +3 2 발 음 elak WILLES WdT592 눈눈을 컬러 * R) 장 23 w 발생 eas'l LZZ EZZ 192 류 료 15: 코 산동로 to 系 발 IMM 라는유 ⑫ 운 p (Ejaythg) : 별 : 본 2 凸量不必 May 田 K 뽀 지 20001 8 MR to 발 발 공공 일 30 5 和 유 가 산업진 용 음료일 . 손의 위 번호 景 별 R * 2 3 ㉜ 월 종 토 ~ PER 육 hamights ose 목 자 or Bet (MW) 용 용 V 월 L P 2 19 : 병 6 F ���� 101 EFE 001 ね T 금을 0 流 종 lift Auth 2 9 옆집 료 류 肉 수 류 12 ~ ~ 항 근류'표 0 �� to 혈 혈 2 일 유 여 Bir 또는 월 . # 0008 JH205Z 차근종료 h 09:22 따 09°E 012 9L'2 ht 료 중 발생 세계 MOL'L 5 an 마 50 공급등을 h 주 유는 みな 별표 월 629'2 skicenair skicemalx 해 세대 GLM'L 도정보 589C 0'04 0% 진행권 V 돌 ⑨ 은 反应处于 경풍파은 2 ha 홍보 kaka Ack-Brialy Akiceeivix 동 용 육 * 000'DLP'L 001992 085792 000°CL 000'BE : 타 40 여 = 위해 094'920', 049'ZEE 谢 노유관리또는 아니라 노동관리비스·이 7 물음표 유로 bj 은 유럽뉴유은 출 위 마 to to 南 ⑨ ~ - + 의존 Ⓡ 家 상적 제 걸 과 ~ - 제작하는 용대동 용품을 to + · F 그 而 음료 M + 과 beks 하시이올아리노 하나,용어가고 점 13% 동 김희옥 。 수용농구 수동일부·수증등록 + 따라 Ack sklo Inflobesx 보충전 년 ·�용�� 유유유 내 위(용유율주는 용노용 R SHARGE 비 윤곤류 콩전류 kkka 용어오는 erish 00 the (을큰 41 대 응을 음료보호주 shappe (����x⌀1020 * 수상번출구보호 의료재료를 晶片) 구 제 8 통찰해유퇴근 8806 일 교수해 + ��를 자동따라 김동 - is A&P * 내 ATLE 5 항 6 시놀이 w 옮김 및 진 조수는 146 동 착 Ivo 등 140 분 걸 58b 소용히 hat 목표물 7 음성부(�) 응하대로 7 885 BAIL · 広徳世帯 7 음파를 sake 상 P - 비용호 20 효과 의 10-0V ⑪+개 병 효과 목 U·D a·b 환불 효율법을 GO·LM ZO·LM 피눈물 효과 서울 10-BHO 리·카이 구호원, '무료 경우 14 동 10·1 20*1 + 재 점 띤 합 종류농급 &�흐른 골드 각 첨부#4 음 국토교통부 91 기계설비 기술기준 판단기준 | {}
cc1fe02b-2da8-4a22-9347-218c256aeafd | 국내_기계설비_기술기준_매뉴얼_최종본 | [계산서] 냉난방 설계기준 온도 적용 여부 확인 ¦ 첨부 2 장 명 ¦ ¦ ¦ 서울시 강남구 00 로 01 00 빌딩 신축공사 ¦ 서울시 강남구 00 로 01 00 빌딩 신축공사 ¦ 서울시 강남구 00 로 01 00 빌딩 신축공사 ¦ 서울시 강남구 00 로 01 00 빌딩 신축공사 ¦ 서울시 강남구 00 로 01 00 빌딩 신축공사 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1.현 2.작 성 자 ¦ 회사이름 ¦ 회사이름 ¦ 00 건설 작성인 이몽룡 ¦ 00 건설 작성인 이몽룡 ¦ 00 건설 작성인 이몽룡 ¦ 00 건설 작성인 이몽룡 ¦ 00 건설 작성인 이몽룡 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 3.작성항목 ¦ 착공전확인표 ¦ 착공전확인표 ¦ [별표 1] 냉난방 설계기준 온도 적용 여부 확인 ¦ [별표 1] 냉난방 설계기준 온도 적용 여부 확인 ¦ [별표 1] 냉난방 설계기준 온도 적용 여부 확인 ¦ [별표 1] 냉난방 설계기준 온도 적용 여부 확인 ¦ [별표 1] 냉난방 설계기준 온도 적용 여부 확인 ¦ ¦ 3.작성항목 ¦ 기계설비 기술기준 매뉴얼 ¦ 착공전확인 판단기준 ¦ 냉난방 설계기준의 온도 적용여부를 계산서에 명기한 경우 적합으로 함 [계산서] 계산서의 냉난방 설계기준(온도) 확인 ¦ 냉난방 설계기준의 온도 적용여부를 계산서에 명기한 경우 적합으로 함 [계산서] 계산서의 냉난방 설계기준(온도) 확인 ¦ 냉난방 설계기준의 온도 적용여부를 계산서에 명기한 경우 적합으로 함 [계산서] 계산서의 냉난방 설계기준(온도) 확인 ¦ 냉난방 설계기준의 온도 적용여부를 계산서에 명기한 경우 적합으로 함 [계산서] 계산서의 냉난방 설계기준(온도) 확인 ¦ 냉난방 설계기준의 온도 적용여부를 계산서에 명기한 경우 적합으로 함 [계산서] 계산서의 냉난방 설계기준(온도) 확인 ¦ ¦ 예시 ¦ ¦ ¦ 설 신축공사 01. 설계개요 및 기준 기계계산서 ¦ 설 신축공사 01. 설계개요 및 기준 기계계산서 ¦ 설 신축공사 01. 설계개요 및 기준 기계계산서 ¦ 설 신축공사 01. 설계개요 및 기준 기계계산서 ¦ 설 신축공사 01. 설계개요 및 기준 기계계산서 ¦ ¦ ¦ 1.3.1 설계용 외기 온 · 습도 조건 ¦ 1.3.1 설계용 외기 온 · 습도 조건 ¦ 1.3.1 설계용 외기 온 · 습도 조건 ¦ 1.3.1 설계용 외기 온 · 습도 조건 ¦ 1.3.1 설계용 외기 온 · 습도 조건 ¦ 1.3.1 설계용 외기 온 · 습도 조건 ¦ 1.3.1 설계용 외기 온 · 습도 조건 ¦ ¦ 구분 ¦ 하 절 기 ¦ 하 절 기 ¦ 하 절 기 ¦ 동 절 기 건구온도(°C) ¦ 동 절 기 건구온도(°C) ¦ 동 절 기 건구온도(°C) ¦ 기준지역 ¦ ¦ 일 반 ¦ ¦ 건구온도(°C) ¦ 상대습도(%) TAC(%) ¦ ¦ 상대습도(%) ¦ TAC(%) ¦ ¦ ¦ ¦ + 국토교통부 고시 제 2017-881 호, 건축물의 에너지절약설계기준(시행 2018. 요 � (별표 7) 용량계산을 위한 설계 외기 온습도 ¦ 31.2 ¦ 63.6 25 % ¦ ¦ -11.3 63.0 ¦ 97.5 % ¦ 서울 기준 ¦ ¦ 참조 * 항온항습조건의 의 경우 설비공학편람, :ASHRAE 방식의 ¦ 냉.난방설비의 기준 한국 주요도시 기상조건' 참조 ¦ 냉.난방설비의 기준 한국 주요도시 기상조건' 참조 ¦ 냉.난방설비의 기준 한국 주요도시 기상조건' 참조 ¦ 냉.난방설비의 기준 한국 주요도시 기상조건' 참조 ¦ 냉.난방설비의 기준 한국 주요도시 기상조건' 참조 ¦ 냉.난방설비의 기준 한국 주요도시 기상조건' 참조 ¦ 냉.난방설비의 기준 한국 주요도시 기상조건' 참조 ¦ ¦ 1.3.2 실내 온습도 조건 ¦ 1.3.2 실내 온습도 조건 ¦ 1.3.2 실내 온습도 조건 ¦ 1.3.2 실내 온습도 조건 ¦ 1.3.2 실내 온습도 조건 ¦ 1.3.2 실내 온습도 조건 ¦ 1.3.2 실내 온습도 조건 ¦ 1.3.2 실내 온습도 조건 ¦ ¦ 구 분 ¦ 냉 방 ¦ 냉 방 ¦ 냉 방 ¦ 난 방 시 ¦ 난 방 시 ¦ 난 방 시 ¦ 비 고 ¦ ¦ ¦ 건구온도('CDB) ¦ ¦ 시 상대습도(%) ¦ 건구온도(°CDB) ¦ ¦ 상대습도(%) ¦ ¦ ¦ 업무시설 근린생활시설 ¦ ¦ 26 26 ¦ 50 ¦ 20 ¦ ¦ 40 ¦ ¦ ¦ ¦ 미팅룸 ¦ 26 ¦ 50 ¦ 20 ¦ ¦ 40 ¦ ¦ ¦ 홀 로비 ¦ ¦ 26 ¦ 50 ¦ 20 20 ¦ ¦ 40 ¦ ¦ ¦ 휴게실 ¦ ¦ 26 ¦ 50 ¦ 20 ¦ ¦ 40 ¦ ¦ ¦ 주방 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 28 ¦ 55 ¦ ¦ 18 ¦ ¦ ¦ ¦ 참조 국토교통부 ¦ 고시 제 2017-881 호, 건축물의 에너지절약설계기준(시행 2018. 모 � 별표히 냉.난방설비의 용량계산을 위한 실내 온.습도 기준 ¦ 고시 제 2017-881 호, 건축물의 에너지절약설계기준(시행 2018. 모 � 별표히 냉.난방설비의 용량계산을 위한 실내 온.습도 기준 ¦ 고시 제 2017-881 호, 건축물의 에너지절약설계기준(시행 2018. 모 � 별표히 냉.난방설비의 용량계산을 위한 실내 온.습도 기준 ¦ 고시 제 2017-881 호, 건축물의 에너지절약설계기준(시행 2018. 모 � 별표히 냉.난방설비의 용량계산을 위한 실내 온.습도 기준 ¦ 고시 제 2017-881 호, 건축물의 에너지절약설계기준(시행 2018. 모 � 별표히 냉.난방설비의 용량계산을 위한 실내 온.습도 기준 ¦ 고시 제 2017-881 호, 건축물의 에너지절약설계기준(시행 2018. 모 � 별표히 냉.난방설비의 용량계산을 위한 실내 온.습도 기준 ¦ 고시 제 2017-881 호, 건축물의 에너지절약설계기준(시행 2018. 모 � 별표히 냉.난방설비의 용량계산을 위한 실내 온.습도 기준 ¦ ¦ 1.3.3 실내부하 조건 ¦ 1.3.3 실내부하 조건 ¦ 1.3.3 실내부하 조건 ¦ 1.3.3 실내부하 조건 ¦ 1.3.3 실내부하 조건 ¦ 1.3.3 실내부하 조건 ¦ 1.3.3 실내부하 조건 ¦ 1.3.3 실내부하 조건 ¦ ¦ 구 ¦ 조명부하 ¦ 기기부하 ¦ 인원수 ¦ ¦ 인체발열량(W/인) ¦ 도입외기량 ¦ ¦ ¦ 분 ¦ W/m2 ¦ W/m2 ¦ 인/m2 ¦ 현열 ¦ 잠열 기준온도(°C) ¦ m2/h- 인 ¦ 비 고 ¦ ¦ 사무실 ¦ 15 ¦ 15 ¦ 0.2 ¦ 61 ¦ 54 ¦ 26 29 ¦ ¦ ¦ 근린생활시설 ¦ 15 ¦ 10 ¦ 0.3 ¦ 61 ¦ 54 ¦ 26 29 ¦ ¦ ¦ 미팅룸 ¦ 15 ¦ 5 ¦ 좌석수 ¦ 61 ¦ 54 26 ¦ 29 ¦ ¦ ¦ 홀/로비 ¦ 15 ¦ · ¦ 0.1 ¦ 61 ¦ 54 26 ¦ 29 ¦ ¦ ¦ 휴게실 ¦ 15 ¦ · ¦ 0.3 ¦ 61 ¦ 54 26 ¦ 29 ¦ ¦ ¦ ¦ + 인체발열량 설계 기준 : 2009 ASHRAE HANDBOOK, Fundamentals, p18.4 * 도입외기량 기준 : 국토교통부령 제 54 호, 건축물의 설비기준 등에 관한 규칙, [별표 1 의 61 각 시설의 필요 환기량 참조 바닥면적당 인원, 조명 및 기기부하는 설계자의 의도로 추후 변경될 여지가 있으며, 변경될 경우에는 반드시 설계자와 의 협의 를 기본으로 함 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 참조 (주)기계설비 ¦ 7 ¦ 7 ¦ 7 ¦ 7 ¦ 7 ¦ 7 ¦ 7 ¦ 92 기계설비 기술기준 매뉴얼 | {}
7dcfc85a-bac3-4467-8bf7-26917a92409e | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 ![image](/image/placeholder) 첨부 13 [설계도면] 위생설비별 절수기능 적용 여부 확인 1. 현 장 명 서울시 강남구 00 로 01 00 빌딩 신축공사 2.작 성 자 회사이름 00 건설 작성인 이몽룡 착공전 확인표 [별표 4] 위생설비별 절수시능 적용 여부 확인 3.작성항목 기계설비 위생설비별 절수기능을 적용한 경우 적합으로 함 착공전확인 기술기준 [도면] 위생설비별 절수기능 및 절수제품이 적용되어 있는지 판단기준 매뉴얼 위생기구 일람표 확인 ·The M-OOT 예시 PURSTERS 小限位 · ��� ' �������� NONE #ip MIGL'D 위대 � 10,2220 ENON - ok8hina in 제조노조필수수증빙용으로 동포살코 ##수제 68(##동) 대한 포스트 물류 loD 포츠 봉농심공원(의료 ########### 세포부를 또는 통신금산한번호 세종서류 별표 세포실행 조선포내 레코칠헥 "응능 lo 입구 [p 있음] [농촌롤마매크수] 띠 불농심공료정보 음농심공포(비뇨 "올등 az 공부소공공업소 동 18楼版 통작용지노벨용당 동부공공표(alc 세포부터 HI lo-창구 and 세트에서로 "유수출물 홈누리공표(ale'MORE 초포카노 물 풍토용포도포항목 東日10版 사업 '용도 로메파트 [매표소] 음식용가노述전달 품목소공방(비교 ����� 제공손주정과 당 Thankinup Thigg(뉴유래 Thizkin 용은 hibpo ★★★정보生危険 레마살롱 레프워즈 제표물류 최초시트 몸통을 STRESTATES 물누수공보다고 물농습골표이로 풍수소금보다고 비용해야 레포노트메뉴스글로이나 - 항목 18 종류 제공휴 공페이나 숨어 10 을 8 당 모 · . · · · . . , · kt www. 008':·085·08L (WW)한군부를 20 : · · · , , 당 무 2 . · . · F · 1 + · · + · 반 · . · . · , . 그 len 용 ly 시미터 (alwoo � 器 器 者 별 명 반 번 · , 표 , F , . 법 포 , . : ' 2 t- 스 1 · . F ' 1 번호판 / 8 끝손누 ! I 8 료 별 / 8 4 + - · · - ' ▼ · - , · , · , · 료료 PH-1-40 09-020- 환 - · · ~ , + , · 、 · · · . . I Strick , - F · 따 · + , F · · ' ' ' · 장비일람표 비용해수 병 : 원 - E . - ' ▼ ' F · 표 , · , · 원 - F , - , ▼ , - · 표 , · ' · ww 08-002-002 본 - F . - ' · , - · 표 · · F · ���� 또는 THE 整 " F . - / → · F . · · · · . � · F . - , ▼ . - · · . , ' · , - == 레포노트 SING � - i . - ' · . ▶ 1 i · · ' i ���� 명 - F · - . · ' F · · ' · . ' -- 065°COP1085 동농심공원(보고 공무소금합니다 S - F . - ' . , + , 표 , . ' · Jesuedsio 또는 'Hie 5 - F . - + ▼ · + · 표 ' · , · 명 " : " F · - , ▼ · F · · , · ' · 差距 드 료 5 - · · - , ▼ , + , · · · , · 일유 8131861100 ww 002"1X000'LX060'23 000'0x000'9x000'21 出 으 . . - ' · ' ▶ , · · ' ' ' 告 - · . - , + ' · ' 표 ' · . · 또는 그대로 효율용을 let THAM 또 e · . 의 ' · ' - . . ' · , · 칸 1.1.1 등 点 " F . · ' " , · , · ' · , · ゃ " 남도읍 - · . · , - , E , · · , · · 효광 h 음 8 유용 � - , . · ' - ▶ · · · ' . . · kike Meic ···· Bikie Micic Rlo乘客 유 io 응용 Alo 들을 Alo 등을 tio-nex 018-78H BORDI-TACH C0L8-38X · . · , ' . �lc 음을 Ria 움을 Rig 음을 商品质이 0016-0^8H 0018-0ARH 0018-0^8* 식 하늘동물는않은 등을 종 : 森 치 롯해복수수는음 미 (A's."最小限 www.요금주는 노유구 (동포동로)신공부 비용과 교수증을 유수부를 withal- kik lowluk 상승우는흥선물을 Meloirss lel* 장 급 (☏16 월 12 유럽 곡을 살 Ⓡ 버 표 리 10-10(R/2 위 포아노 oly 보수도 수용 일 TEANZAB 'skelleR lity ㉫ 람 처 + [約][3] 文在民 1m& 여길 10-810 ��� Im& 4 에 10-1 20-L 버스가구 la 문 여길 10-0M 20-0M 80-0M 10-an 30-an 10-197 0-8H8 10-0° ■ , , . + a - ~ + 市 . · 꿈 국토교통부 93 II 기계설비 기술기준 판단기준 | {}
cb5e9de5-ed12-4fff-96cc-0ab3acd96cf7 | 국내_기계설비_기술기준_매뉴얼_최종본 | 첨부 14 [현장사진] 열원기기의 명판 및 마감상태 확인 ¦ 1.현 장 명 ¦ 서울시 강남구 00 로 01 00 빌딩 신축공사 ¦ 서울시 강남구 00 로 01 00 빌딩 신축공사 ¦ 서울시 강남구 00 로 01 00 빌딩 신축공사 ¦ 서울시 강남구 00 로 01 00 빌딩 신축공사 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 2.작 성 자 ¦ 회사이름 ¦ 회사이름 ¦ 00 건설 ¦ 작성인 이몽룡 ¦ ¦ 3.작성 항목 ¦ 사용전검사표 ¦ 사용전검사표 ¦ [별표 1] 시공 10 열원기기의 명판 및 마감상태 확인 ¦ [별표 1] 시공 10 열원기기의 명판 및 마감상태 확인 ¦ ¦ 3.작성 항목 ¦ 기계설비 기술기준 매뉴얼 ¦ 사용전검사 판단기준 ¦ 「기계설비 유지관리기준」 [별지 제 1 호서식] 기계설비 유지 관리 및 성능점검 대상 현황표에 기록해야 하는 내용이 명 판에 반영되어 있으며, 마감상태가 식별이 용이한 것을 확 인한 경우 적합으로 함 [검토서] 열원장비 명판과 장비일람표의 세부사양을 확인하 고, 설치된 사진 첨부 확인 ¦ 「기계설비 유지관리기준」 [별지 제 1 호서식] 기계설비 유지 관리 및 성능점검 대상 현황표에 기록해야 하는 내용이 명 판에 반영되어 있으며, 마감상태가 식별이 용이한 것을 확 인한 경우 적합으로 함 [검토서] 열원장비 명판과 장비일람표의 세부사양을 확인하 고, 설치된 사진 첨부 확인 ¦ ![image](/image/placeholder) 2014/10/02 10:48 예시 2014/10/12 18: 스 펌 2014.510/02 94 기계설비 기술기준 매뉴얼 | {}
51f6ce7e-58e9-460d-9c6e-8166790da658 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 4. 기계설비 안전확인서 판단기준 기계설비 안전확인서 ¦ 기계설비 시공자 ¦ 상 호 ¦ ¦ 시공면허등록번호 ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기계설비 시공자 ¦ 대 표 자 ¦ (서명 또는 인) ¦ 전 화 번 호 ¦ ¦ ¦ 공 사 명 ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 건축허가번호 ¦ ¦ ¦ ¦ ¦ 현장배치 기계설비기술인 ¦ (서명 또는 인) ¦ 작 성 일 ¦ ¦ ¦ 검 사 항 목 ¦ 및 ¦ 내 용 (해당항목만 ¦ V 기재) ¦ 해당여부 ¦ ¦ 검사결과 비 고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 보일러실의 일산화탄소 감지기, 경보기는 적합한가 ¦ [ ] ¦ [ ] 적합 [ ] 부적합 ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 보일러의 안전장치는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 냉동기는 친환경냉매를 사용하기에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 냉동기의 안전장치는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 탱크류 안전밸브 설치는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 환기장치의 외기도입구 및 배기구는 안전에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 실외기는 안전에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 냉각탑의 냉각수에 레지오넬라균 번식방지 조치는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 저수조 청소 완료(필증)는 적합한가 ¦ [ ] ¦ [ ] 적합 [ ] 부적합 ¦ ¦ ¦ 저수조 물넘침에 대비하여 배수시설과 알람시설은 적합한가 ¦ [ ] ¦ [ ] 적합 [ ] 부적합 ¦ ¦ ¦ 음용수는 수질기준에 적합한가( 시험성적서) ¦ [ ] ¦ [ ] 적합 [ ] 부적합 ¦ ¦ ¦ 급수, 급탕 등의 역류방지 장치는 적합한가 ¦ I ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 급탕가열장치의 온도 및 압력에 대한 안전장치는 적합한가 ¦ I ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 교차배관으로 인한 오염발생 방지조치는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 각 위생기구에 공급되는 급수압은 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 물배관 및 계량기의 동파방지 조치는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 동파방지 발열선의 과열시 전원차단 및 경보시설은 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 210mmX297mm[백상지 80g/m2 ] 기계설비 기술기준 판단기준 국토교통부 95 | {}
4f072dd6-d114-4592-9c38-552a874b3aa4 | 국내_기계설비_기술기준_매뉴얼_최종본 | 기계설비 안전확인서의 적합/부적합 판단기준_[별지 제 5 호 서식] ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ 보일러의 일산화탄소 감기지 경보기는 적합한가 [별표 1] 3.5 (4)에 대한 시공 상태를 확인 경우 적합으로 함 3.5 보일러 (4) 개별 보일러를 설치하는 건축물의 경우에는 소방청장이 정하 여 고시하는 기준에 따라 일산화탄소 경보기를 설치해야 한다. ¦ [별표 1] 3.5 (4) ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 2 ¦ 보일러의 안전장치는 적합한가 안전밸브, 압력 제한장치(압력차단 스위치), 과열방지 스위치, 저수위 차단장치, 연소 안전장치(프로텍트 릴레이 기능), 연료공급 안전장치 (가스버너 적용), 가스누설 안전장치. 미연소 가스 배출 안전장치 등 이 있으며 보일러 제조사의 제작승인 도서에 표시된 안전장치가 설 치된 경우 적합으로 함 ¦ ¦ 검토서(준공도면, 현장사진 등) ¦ ¦ 3 ¦ 냉동기는 친환경냉매를 사용하기에 적합한가 [별표 1] 2.1 (4)에 대한 시공 상태를 확인 경우 적합으로 함 2.1 일반사항 (4) 냉매는 KS B ISO 817(냉매-명칭과 안전 분류) 최신판의 명칭 과 분류에 따른다. ¦ [별표 1] 2.1 (4) ¦ 장비일람표 ¦ ¦ 4 ¦ 냉동기의 안전장치는 적합한가 제작승인도서에 표시된 안전장치가 설치된 경우 적합으로 함 1) 압력에 의한 안전장치 고압스위치, 저압스위치, 듀얼 프레셔(dual pressure) 스위치(고 압과 저압스위치를 하나의 박스에 결합한 제품), 유압보호 스 위치, 수압 스위치 등 2) 온도에 의한 안전장치 토출온도조절기, 오일온도조절기, 모터온도조절기, 가용전, 동 결방지 온도조절기 등 3) 전기적 안전장치 누전차단기, 과부하계전기, 결상방지기, 전류불평형, 역상방지 기 등 4) 기타 플로우 스위치, 유면 광센서, 안전밸브, 가용전(응축기나 수액 기에 장착하는 안전장치로, 냉동 설비의 화재 발생시 저융합금 이 용융되어 냉매를 대기 중에 유출시켜 냉동기의 파손을 방지 하는 것) 등 ¦ ¦ 제작승인도 ¦ ¦ 5 ¦ 탱크류 안전밸브 설치는 적합한가 산업안전보건기준에 관한 규칙 제 261 조 제 3 항에 준하여 국가교정기 관에서 교정을 받은 압력계를 이용하여 설정압력에서 안전밸브가 적 정하게 작동하는지를 검사를 한 경우 적합으로 함 제 261 조(안전밸브 등의 설치) ① ②생략 ③ 제 1 항에 따라 설치된 안전밸브에 대해서는 다음 각 호의 구분 에 따른 검사주기마다 국가교정기관에서 교정을 받은 압력계 를 이용하여 설정압력에서 안전밸브가 적정하게 작동하는지를 검사한 후 납으로 봉인하여 사용하여야 한다. 이하 생략 ¦ 「산업안전 보건기준 에 관한 규칙」 제 261 조 제 3 항 ¦ 검토서(현장도면, 현장사진 등) ¦ ¦ 6 ¦ 환기장치의 외기도입구 및 배기구는 안전에 적합한가 이 매뉴얼 '[별표 9] 덕트설비의 착공 전 확인 적합/부적합 판단기준' 의 '2'의 서류를 확인하고 시공상태를 검사함 ¦ [별표 9] 2.3.4, 2.3.5 ¦ 검토서(현장도면, 현장사진 등) ¦ ¦ 7 ¦ 실외기는 안전에 적합한가 [별표 1] 3.12 에 대한 설계 및 시공 상태를 확인하여 만족한 경우 적 합으로 함 ¦ [별표 1] 3.12 ¦ 이 매뉴얼 '[별표 1] 열원 및 냉난방 설비의 사용 전 검 ¦ 96 기계설비 기술기준 매뉴얼 | {}
20715a5e-1cd9-4546-ac75-c64d34e1f240 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 기계설비 기술기준 판단기준 ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ ¦ ¦ 사 적합/부적합 판 단기준'의 '시공 3-1 ~ 3-3, 4-1 ~ 4-3'의 서류로 갈 음함 ¦ ¦ 8 ¦ 냉각탑의 냉각수에 레지오넬라균 번식방지 조치는 적합한가 이 매뉴얼 '[별표 1] 열원 및 냉난방설비의 착공 전 확인 적합/부적합 판단기준'의 '3'의 서류 및 시험성적서를 확인함 저수탱크 ¦ [별표 1] 2.3 ¦ 시험성적서 ¦ ¦ 9 ¦ 청소완료(필증)는 적합한가 저수탱크 청소완료(필증)를 확인 경우 적합으로 함 ¦ 「수도법 시행규칙」 제 22 조의 3 ¦ 저수탱크 청소완료(필증) ¦ ¦ 10 ¦ 저수탱크 물넘침에 대비하여 배수시설과 알림시설은 적합한가 이 매뉴얼 '[별표 5] 급수·급탕설비의 착공 전 확인 적합/부적합 판단 기준'의 '2'의 서류를 확인하고 시공상태를 검사함 ¦ [별표 5] 2.1.4 ¦ 검토서(현장도면, 현장사진 등) ¦ ¦ 11 ¦ 음용수는 수질기준에 적합한가(시험성적서) 이 매뉴얼 '[별표 5] 급수·급탕설비의 착공 전 확인 적합/부적합 판단 기준'의 '1'의 서류 및 시험성적서를 확인함 급수, 급탕 등의 역류방지 장치는 적합한가 ¦ [별표 5] 2.1.1 ¦ 시험성적서 ¦ ¦ 12 ¦ [별표 5] 2.1.8(2)(3)(4)(8), 2.2.5(1), 3.1(5), 3.3.1(3)⑥에 대한 설계 및 시공 상태를 확인하여 만족한 경우 적합으로 함 2.1.8 급수의 오염방지 (2) 위생기구의 급수배관은 역류되지 않도록 설계한다. (3) 위생기구나 물 사용기기가 상수도관에 직접 연결된 경우에는 역류방지 조치를 한다. (4) 급수관을 냉 · 온수배관 계통과 같은 비 음용배관 계통의 보급 수용으로 연결할 때는 역류방지 조치를 한다. (8) 모든 음용수 개방구와 토출구는 토수구공간이나 역류방지기 또는 진공브레이커로 역류되지 않게 한다. 2.2.5 급탕계통의 부속장치 (1) 역류방지밸브 급탕탱크의 급수관에는 급탕이 급수관으로 역류하지 않도록 역 류방지밸브를 설계한다. 3.1 일반사항 (5) 수돗물의 오염을 방지하기 위한 계량기 후단의 역류방지밸브 를 설치해야 한다. 3.3.1 급탕배관 및 기기 (3) 기기 주위의 배관 ⑥ 온수탱크의 보급수관에는 역류방지밸브를 설치한다. ¦ [별표 5] 2.1.8 (2)(3)(4)(8) 2.2.5(1) 3.1(5) 3.3.1(3)⑥ ¦ 검토서(현장도면, 현장사진 등) ¦ ¦ 13 ¦ 급탕가열장치의 온도 및 압력에 대한 안전장치는 적합한가 [별표 5] 3.3.2 에 대한 설계 및 시공 상태를 확인하여 만족한 경우 적 합으로 함 ¦ [별표 5] 3.3.2 ¦ 이 매뉴얼 '[별표 5] 급수·급탕설비 의 사용 전 검사 적합/부적합 판단 기준'의 '시공 7'의 서류로 갈음함 ¦ ¦ 14 ¦ 교차배관으로 인한 오염발생 방지조치는 적합한가 [별표 5] 2.1.8 에 대한 설계 및 시공 상태를 확인하여 만족한 경우 적 합으로 함 2.1.8 급수의 오염방지 (1) 음용수 배관과 비음용수 배관을 크로스커넥션 시켜서는 안 된 다. ¦ [별표 5] 2.1.8 ¦ 검토서(현장도면, 현장사진 등) ¦ 국토교통부 97 기계설비 기술기준 판단기준 | {}
d62760fb-baae-47ad-96d4-b703b1be9f83 | 국내_기계설비_기술기준_매뉴얼_최종본 | ¦ ¦ 판단기준 ¦ 판단근거 ¦ 필요서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 15 ¦ 각 위생배관에 공급되는 급수압은 적합한가 [별표 5] 2.1.7 에 대한 설계 및 시공 상태를 확인하여 만족한 경우 적 합으로 함 2.1.7 위생기구의 최대급수압력 제한 위생기구에 수압이 550 kPa 이상 걸릴 경우에는 감압밸브를 설계 하거나, 급수 조닝을 하여 최대압력을 550 kPa 이하로 제한한다. ¦ [별표 5] 2.1.7 ¦ 검토서(시운전보 고서 등) ¦ ¦ 16 ¦ 물배관 및 계량기의 동파방지조치는 적합한가 이 매뉴얼 '[별표 10] 보온설비의 착공 전 확인 적합/부적합 판단기 준'의 '2'의 서류를 확인하고 시공상태를 검사함 ¦ [별표 10] 2.3.5 ¦ 검토서(현장도면, 현장사진 등) ¦ ¦ 17 ¦ 동파방지 발열선의 과열시 전원차단 및 경보시설은 적합한가 이 매뉴얼 '[별표 10] 보온설비의 착공 전 확인 적합/부적합 판단기 준'의 '3'의 서류를 확인하고 시공상태를 검사함 ¦ [별표 10] 2.5 ¦ 검토서(현장도면, 현장사진 등) ¦ 98 기계설비 기술기준 매뉴얼 | {}
edab3616-e5c5-4bf1-838a-d944de58138e | 국내_기계설비_기술기준_매뉴얼_최종본 | I + 기계설비 기술기준 해설 [별표 1] 열원 및 냉난방설비의 설계 및 시공 기준 .........................100 [별표 2] 공기조화설비의 설계 및 시공 기준 ·········138 [별표 3] 환기설비의 설계 및 시공 기준 ··················156 [별표 4] 위생기구설비의 설계 및 시공 기준 ·······177 [별표 5] 급수 · 급탕설비의 설계 및 시공 기준 ······ ··········184 [별표 6] 오 · 배수 통기 및 우수배수설비의 설계 및 시공 기준 ····210 [별표 7] 오수정화 및 물재이용설비의 설계 및 시공 기준 ·······233 [별표 8] 배관설비의 설계 및 시공 기준 ···252 [별표 9] 덕트설비의 설계 및 시공 기준 ········278 [별표 10] 보온설비의 설계 및 시공 기준 ·········298 [별표 11] 자동제어설비의 설계 및 시공 기준 ········327 [별표 12] 방음 · 방진 · 내진 설비의 설계 및 시공 기준 354 [별표 13] 플랜트설비의 설계 및 시공 기준 ------ 381 [별표 14] 특수설비의 설계 및 시공 기준 ------ 384 [별표 15] 기계설비 유지관리를 고려한 설계기준 ············392 | {}
ee198f1b-1aae-443b-ab25-2de8a5ac12ff | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 1] 열원 및 냉난방설비의 설계 및 시공 기준 1. 열원 및 냉난방설비 일반사항 1.1 목적 이 기준은 건축물, 시설물 등에 설치하는 열원 및 냉난방설비의 안정성 확보와 합리적 사용을 위하여 필요한 설계 및 시공 방법 등 세부 기술기준을 정함을 목적으로 한다. 해 설 이 기준의 목적은 「기계설비법」 제 14 조(기계설비 기술기준)과 같은 법 영 제 2 조 및 [별표 1]에 근 거하여, 건축물이나 시설물에 필요한 열원 및 냉난방설비의 설계 및 시공 시 기계설비의 안전과 성능을 확보하기 위하여 필요한 기술적 요건을 규정하기 위함 「기계설비법」 제 14 조(기계설비 기술기준) ① 국토교통부장관은 기계설비의 안전과 성능확보를 위하여 필요 한 기술기준(이하 "기술기준이라 한다)를 정하여 고시하여야 한다. 이를 변경하는 경우에도 또한 같다. 1.2 적용범위 (1) 이 기준은 건축물, 시설물 등에 열원 및 냉난방설비를 설치하는 경우에 대하여 적용한다. (2) 지역난방 의무고시지역에 설치하는 열원설비는 해당지역 열사용 시설기준을 우선 적용한다. 해 설 이 기준의 적용범위는 「기계설비법」 제 2 조제 1 호에 따른 건축물등에 같은 법 영 제 2 조에 따라 대 통령령으로 정한 열원 및 냉난방설비를 설치하는 경우와 그와 관련된 부속설비들을 포함함 「기계설비법」 제 2 조(정의) 1. "기계설비"란 건축물, 시설물 등(이하 "건축물등"이라 한다)에 설치된 기계 · 기 구 · 배관 및 그 밖에 건축물등의 성능을 유지하기 위한 설비로서 대통령령으로 정하는 설비를 말한다. 「기계설비법 시행령」 제 2 조(기계설비의 범위) 「기계설비법」(이하 "법"이라 한다) 제 2 조제 1 호에서 "대통령령 으로 정하는 설비"란 별표 1 의 설비를 말한다. 「기계설비법 시행령」 [별표 1] 기계설비의 범위 1. 열원설비 : 건축물등에서 에너지를 이용하여 열매체를 가열, 냉각하기 위하여 설치된 기계 · 기구 · 배관 및 그 밖에 성능을 유지하기 위한 설비 2. 냉난방설비 : 건축물등에서 일정한 실내온도 유지를 위하여 설치된 기계 · 기구 · 배관 및 그 밖에 성능을 유지하기 위한 설비 100 기계설비 기술기준 매뉴얼 | {}
8414e212-bbb1-4277-a6a3-8cc133bab9dd | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 1.3 타 규정과 의 관계 다음의 규정과 이 기준에서 정하는 내용이 상이한 경우에는 해당 규정을 따른다. (1) 「건축물의 설비기준 등에 관한 규칙」 (2) 「, 산업안전보건기준에 관한 규칙」 (3) 「건축물의 에너지절약설계기준」 (4) 「건축물의 냉방설비에 대한 설치 및 설계기준」 (5) 「에너지관리기준」 (6) KDS 31 25 10 열원기기 설계기준 (7) KDS 31 25 15 공기조화기기 설계기준 (8) KDS 31 50 16 지열원열펌프설비 설계기준 (9) KCS 31 25 15 공기조화기기설비공사 표준시방서 (10) KCS 31 40 00 냉동냉장설비공사 표준시방서 (11) KCS 31 50 15 05 지열원열펌프설비공사 표준시방서 (12) KCS 31 50 15 10 태양열설비공사 표준시방서 해 설 이 기준과 타 규정 및 기준과 다른 경우에는 상기 규정에 명시된 내용을 따름 기계설비 기술기준 해설 (별표 01 국토교통부 101 | {}
3df682b7-617b-4ebc-8c3f-9ee951c41eaf | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 열원 및 냉난방설비 설계 2.1 일반사항 (1) 열원설비는 부분부하 및 전부하 운전효율이 좋은 것을 선정한다. (2) 냉난방기기, 냉동기, 송풍기, 펌프 등은 부하조건에 따라 최고의 성능을 유지할 수 있도록 대수분 할 또는 비례제어운전이 가능하도록 설계할 수 있다. (3) 냉난방기기는 에너지소비효율 등급이 높은 제품을 선정한다. (4) 냉매는 KS B ISO 817(냉매-명칭과 안전 분류) 최신판의 명칭과 분류에 따른다. 지구 환경을 위해 서 오존파괴지수(ODP)는 0.05 이하이면서 가능한 지구온난화지수(GWP)가 낮은 냉매 사용을 권 장한다. (5) 순환 펌프는 열원기기마다 각 1 대씩 설치하는 것을 기본으로 한다.(예비용 펌프 별도) (6) 냉난방설비의 용량계산을 위한 설계기준 실내온도는 난방의 경우 20°C, 냉방의 경우 28°C 를 기 준으로 하되(목욕장 및 수영장은 제외) 각 건축물 용도 및 개별 실의 특성에 따라 표 1 에서 제시된 범위를 참고하여 설비 용량이 과다해지지 않도록 한다. 표 1 냉·난방설비의 용량계산을 위한 실내 온·습도 기준 ¦ 구 분 ¦ 난 방 ¦ 냉 방 ¦ 냉 방 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 용 도 ¦ 건구온도(°C) ¦ 건구온도(°C) ¦ 상대습도(%) ¦ ¦ 공동주택 ¦ 20~22 ¦ 26~28 ¦ 50~60 ¦ ¦ 학교(교실) ¦ 20~22 ¦ 26~28 ¦ 50~60 ¦ ¦ 병원(병실) ¦ 21~23 ¦ 26~28 ¦ 50~60 ¦ ¦ 관람집회시설(객석) ¦ 20~22 ¦ 26~28 ¦ 50~60 ¦ ¦ 숙박시설(객실) ¦ 20~24 ¦ 26~28 ¦ 50~60 ¦ ¦ 판매시설 ¦ 18~21 ¦ 26~28 ¦ 50~60 ¦ ¦ 사무소 ¦ 20~23 ¦ 26~28 ¦ 50~60 ¦ ¦ 목욕장 ¦ 26~29 ¦ 26~29 ¦ 50~75 ¦ ¦ 수영장 ¦ 27~30 ¦ 27~30 ¦ 50~70 ¦ (7) 냉난방설비의 용량계산을 위한 외기조건은 각 지역별로 위험률 2.5%(냉방기 및 난방기를 분리 한 온도출현분포를 사용할 경우) 또는 1%(연간 총시간에 대한 온도출현 분포를 사용할 경우)로 하거나 표 2 에서 정한 외기온 * 습도를 사용한다. 표 2 이외의 지역인 경우에는 상기 위험률을 기 준으로 하여 가장 유사한 기후조건을 갖는 지역의 값을 사용한다. 102 기계설비 기술기준 매뉴얼 | {}
dc79c5d4-a5bd-43ae-a83b-bfbb41861fa2 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 표 2 냉·난방설비의 용량계산을 위한 설계 외기온·습도 기준 ¦ 구 분 ¦ 냉 방 ¦ 냉 방 ¦ 난 방 ¦ 난 방 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도시명 ¦ 건구온도(°C) ¦ 습구온도(°C) ¦ 건구온도(°C) ¦ 상대습도(%) ¦ ¦ 서 울 ¦ 31.2 ¦ 25.5 ¦ -11.3 ¦ 63 ¦ ¦ 인 천 ¦ 30.1 ¦ 25.0 ¦ -10.4 ¦ 58 ¦ ¦ 수 원 ¦ 31.2 ¦ 25.5 ¦ -12.4 ¦ 70 ¦ ¦ 춘 천 ¦ 31.6 ¦ 25.2 ¦ -14.7 ¦ 77 ¦ ¦ 강 릉 ¦ 31.6 ¦ 25.1 ¦ -7.9 ¦ 42 ¦ ¦ 대 전 ¦ 32.3 ¦ 25.5 ¦ -10.3 ¦ 71 ¦ ¦ 청 주 ¦ 32.5 ¦ 25.8 ¦ -12.1 ¦ 76 ¦ ¦ 전 주 ¦ 32.4 ¦ 25.8 ¦ - 8.7 ¦ 72 ¦ ¦ 서 산주 ¦ 31.1 ¦ 25.8 ¦ - 9.6 ¦ 78 ¦ ¦ 광 ¦ 31.8 ¦ 26.0 ¦ - 6.6 ¦ 70 ¦ ¦ 대 구 ¦ 33.3 ¦ 25.8 ¦ - 7.6 ¦ 61 ¦ ¦ 부 산 ¦ 30.7 ¦ 26.2 ¦ - 5.3 ¦ 46 ¦ ¦ 진 주 ¦ 31.6 ¦ 26.3 ¦ - 8.4 ¦ 76 ¦ ¦ 울 산 ¦ 32.2 ¦ 26.8 ¦ - 7.0 ¦ 70 ¦ ¦ 포 항 ¦ 32.5 ¦ 26.0 ¦ - 6.4 ¦ 41 ¦ ¦ 목 포 ¦ 31.1 ¦ 26.3 ¦ - 4.7 ¦ 75 ¦ ¦ 제 주 ¦ 30.9 ¦ 26.3 ¦ 0.1 ¦ 70 ¦ (8) 다음에 해당하는 건축물 중 중앙집중냉방설비를 설치하는 경우에는 「건축물의 냉방설비에 대한 설치 및 설계기준」 제 4 조에 따른 축냉식 또는 가스를 이용한 중앙집중냉방방식으로 해야 한다. ① 영 별표 5 제 2 호 다목부터 마목까지의 건축물 ② 1 만제곱미터 이상인 건축물 중 「건축법 시행령」 [별표 1] 제 5 호 가목부터 라목까지에 해당하는 문화 및 집회시설, 제 6 호에 따른 종교시설, 제 10 호에 따른 교육연구시설(연구소는 제외한다), 제 28 호에 따른 장례식장 (9) 냉방기기는 전력피크 부하를 줄일 수 있도록 해야 하며, 상황에 따라 심야전기를 이용한 축열 、 축냉시스템, 가스 및 유류를 이용한 냉방설비, 집단에너지를 이용한 지역냉방방식, 소형열병합발 전을 이용한 냉방방식, 신 · 재생에너지를 이용한 냉방방식을 채택할 수 있다. (10) 장비일람에 사용용도, 형식, 용량, 효율 등을 기입한다. (11) 장비의 운전중량을 건축구조에 반영한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 열원설비 제조사의 시험 데이터 등을 검토하여 최대부하와 부분부하 운전 시에도 효율이 좋은 제품을 선정해야 함 냉열원 기기인 터보냉동기와 흡수식냉동기의 부분부하 특성은 부분부하가 40% 미만일 때 효율 저하가 크게 발생하며 특히, 터보냉동기는 흡수식냉동기에 비해 부분운전에 따른 효율 저하가 큰 것으로 보고되고 있다. 온열원기기인 증기보일러와 고온수 보일러는 부분부하 특성이 유사하며 부분부하율이 30% 미만일 때 효율 저하가 발생하는 것으로 나타났다. 출처 : 부분부하 특성을 고려한 열원기기의 운전성능 평가, 대한설비공학회, KJACR, 이왕제 외 4 인 V (2 항) 냉난방기기, 냉동기, 송풍기, 펌프 등은 열원 또는 공조방식에 따라 비례제어운전이 가능한 기계설비 기술기준 해설 (별표 어) 국토교통부 103 | {}
6f8a0f7a-32e0-4d60-b05c-498c48b6c31d | 국내_기계설비_기술기준_매뉴얼_최종본 | 인버터를 채택한 제품을 선정하거나, 부하 단계별로 기계설비의 대수 분할 운전하여 최상의 성능 을 유지할 수 있도록 설계할 수 있음 V (3 항) 냉난방기기는 한국에너지공단의 효율관리제도(https://eecenergy.com/maimaimalinalago.kr 따른 등급 및 인증제도를 확인하고, 효율이 높은 제품 사용을 권장해야 하며, 설계 온도차를 유지 할 수 있어야 함 V (4 항) 열원기기에 사용된 냉매의 오존층파괴지수와 지구온난화지수를 확인해야 함 ¦ 항목 ¦ HCFC 계열 ¦ HFC 계열 ¦ HFC 계열 ¦ HFC 계열 ¦ 자연냉매 ¦ 자연냉매 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 항목 ¦ R-22 ¦ R-134a ¦ R-407C ¦ R-410A ¦ CO2 ¦ 프로판 ¦ ¦ 오존층파괴지수(ODP) ¦ 0.034 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ ¦ 지구온난화지수(GWP) ¦ 1 700 ¦ 1 300 ¦ 1 700 ¦ 2 000 ¦ 1 ¦ 3 ¦ 출처 : 친환경 규제에 따른 철도차량 에어컨 냉매선정 및 특성에 대한 고찰, 한국철도학회, 2007 년도 춘계학술대회 논문집, 조용성 외 2 인 V (5 항) 열원기기는 독립적인 순환 펌프를 사용해야 하며, 예비용 펌프를 고려할 수 있음 V (6 항) 열원설비 용량이 과다해지지 않도록 건축물 용도별 및 개별 실의 특성을 파악하여 부하계 산을 실시해야 함 V (7 항) 6 항과 함께 사용하는 부하계산에서 사용하는 외기온도는 위험률 또는 제시한 표의 온도 값 등으로 계산해야 함 V (8 항 1 호) 영 별표 5 제 2 호 다목부터 마목까지의 건축물 「기계설비법 시행령」 [별표 5] 기계설비의 착공 전 확인과 사용 전 검사의 대상 건축물 또는 시설물 2. 에너지를 대량으로 소비하는 다음 각 목의 어느 하나에 해당하는 건축물 다. 다음의 어느 하나에 해당하는 건축물로서 해당 용도에 사용되는 바닥면적 의 합계가 500 m2 이상인 건 축물 1) 「건축법 시행령」 별표 1 제 3 호다목에 따른 목욕장 2) 「건축법 시행령」 별표 1 제 13 호가목에 따른 놀이형시설(물놀이를 위하여 실내에 설치된 경우로 한정 한다) 및 같은 호 다목에 따른 운동장(실내에 설치된 수영장과 이에 딸린 건축물로 한정한다) 라. 다음의 어느 하나에 해당하는 건축물로서 해당 용도에 사용되는 바닥면적의 합계가 2 000 m2 이상인 건 축물 1) 「건축법 시행령」 별표 1 제 2 호라목에 따른 기숙사 2) 「건축법 시행령」 별표 1 제 9 호에 따른 의료시설 3) 「건축법 시행령」 별표 1 제 12 호다목에 따른 유스호스텔 4) 「건축법 시행령」 별표 1 제 15 호에 따른 숙박시설 마. 다음의 어느 하나에 해당하는 건축물로서 해당 용도에 사용되는 바닥면적의 합계가 3 000 m2 이상인 건 축물 1) 「건축법 시행령」 별표 1 제 7 호에 따른 판매시설 2) 「건축법 시행령」 별표 1 제 10 호마목에 따른 연구소 3) 「건축법 시행령」 별표 1 제 14 호에 따른 업무시설 (8 항 2 호) 10 000 m2 이상인 건축물 중 「건축법 시행령」 [별표 1] 제 5 호 가목부터 라목까지에 해 당하는 문화 및 집회시설, 제 6 호에 따른 종교시설, 제 10 호에 따른 교육연구시설(연구소는 제외한 다), 제 28 호에 따른 장례식장 104 기계설비 기술기준 매뉴얼 | {}
cd833f37-cb95-4265-a12f-84f8f8e9d907 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 「건축법 시행령」 [별표 1] 용도별 건축물의 종류 5. 문화 및 집회시설 가. 공연장으로서 제 2 종 근린생활시설에 해당하지 아니하는 것 나. 집회장[예식장, 공회당, 회의 장, 마권(��) 장외 발매소, 마권 전화투표소, 그 밖에 이와 비슷한 것을 말 한다]으로서 제 2 종 근린생활시설에 해당하지 아니하는 것 다. 관람장(경마장, 경륜장, 경정장, 자동차 경기장, 그 밖에 이와 비슷한 것과 체육관 및 운동장으로서 관람 석의 바닥면적의 합계가 1 000 m2 이상인 것을 말한다) 라. 전시장(박물관, 미술관, 과학관, 문화관, 체험관, 기념관, 산업전시장, 박람회장, 그 밖에 이와 비슷한 것 을 말한다) 6. 종교시설 가. 종교집회장으로서 제 2 종 근린생활시설에 해당하지 아니하는 것 나. 종교집회장(제 2 종 근린생활시설에 해당하지 아니하는 것을 말한다)에 설치하는 봉안당(���) 10. 교육연구시설(제 2 종 근린생활시설에 해당하는 것은 제외한다) 가. 학교(유치원, 초등학교, 중학교, 고등학교, 전문대학, 대학, 대학교, 그 밖에 이에 준하는 각종 학교를 말 한다) 나. 교육원(연수원, 그 밖에 이와 비슷한 것을 포함한다) 다. 직업훈련소(운전 및 정비 관련 직업훈련소는 제외한다) 라. 학원(자동차학원·무도학원 및 정보통신기술을 활용하여 원격으로 교습하는 것은 제외한다), 교습소(자동 차교습 · 무도교습 및 정보통신기술을 활용하여 원격으로 교습하는 것은 제외한다) 바. 도서관 28. 장례시설 가. 장례식장[의료시설의 부수시설(「의료법」 제 36 조제 1 호에 따른 의료기관의 종류에 따른 시설을 말한다) 에 해당하는 것은 제외한다] 나. 동물 전용의 장례식장 V (9 항) 이 기준에 나열된 것 이외에도 설계 시 국가 에너지정책을 반영하여 열원방식을 채택해야 함 V (10 항) 기계설비공사를 완료한 후, 기계설비시공자가 장비일람표에 사용용도, 형식, 용량, 효율 등 의 정보를 이 기준 제 15 조 및 「기계설비 유지관리기준」 제 6 조 유지관리지침서에 반영할 수 있도 록 해당 정보를 정확히 기록해야 함 V (11 항) 열원장비의 중량과 운전 시 가해지는 힘을 고려하여 건축구조를 설계해야 하며, 장비의 운 전중량을 건축구조에 반영한다. 2. 용어 기계설비 기술기준 해설 (별표 01 국토교통부 105 | {}
34628e0f-e164-4623-84ab-6381ce57a31e | 국내_기계설비_기술기준_매뉴얼_최종본 | ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 대수분할운전 ¦ 기기를 여러 대 설치하여 부하상태에 따라 최적 운전상태를 유지할 수 있도록 기기 를 조합하여 운전하는 방식 출처 : 건축물의 에너지 절약설계 기준 ¦ ¦ 비례제어운전 ¦ 기기의 출력값과 목표값의 편차에 비례하여 입력량을 조절하여 최적운전상태를 유 지할 수 있도록 운전하는 방식 출처 : 건축물의 에너지 절약설계 기준 조절 값과 설정 값의 편차의 크기에 비례하여 조작부가 최소에서 최대까지 변화하는 제어방식 출처 : 건축물의 에너지 절약설계 기준 해설서 ¦ ¦ 에너지소비효율등급 표시제도 ¦ 소비자들이 효율이 높은 에너지절약형 제품을 쉽게 구입할 수 있도록 하고 제조(수 입)업자들이 생산(수입)단계에서부터 원천적으로 에너지절약형 제품을 생산하고 판 매하도록 하기위한 의무적인 신고제도 이 제도에서는 에너지소비효율 또는 에너지사용량에 따라 효율등급을 1~5 등급으로 나누어 표시하도록 하며, 대상품목은 전기냉장고 등 33 개 품목임 출처 : 한국에너지공단 효율관리제도 ¦ ¦ 위험률 ¦ 냉(난)방기간동안 또는 연간 총시간에 대한 온도출현분포 중에서 가장 높은(낮은) 온 도쪽으로부터 총시간의 일정 비율에 해당하는 온도를 제외시키는 비율 출처 : 건축물의 에너지 절약설계 기준 ¦ ¦ 위험률 ¦ 연중 가장 더운 시간 또는 추운 시간의 외기온도를 부하계산에 적용하면 설비용량이 과대해 질 우려가 있음에 따라 부하계산에서는 최고 또는 최저 온도의 피크 값을 일 정 비율 제거한 외기온도를 사용하게 되는데 피크 값을 제외시키는 비율을 위험률이 라고 함 출처 : 건축물의 에너지 절약설계 기준 해설서 ¦ ○ ---- 2.2 냉동기 2.2.1 일반냉동기 (1) 흡수식, 압축식 냉동기 반영 시 열원과 사용범위에 따라 성적계수(COP), 에너지효율비(EER), 통 합성능계수(IPLV) 등을 고려하여 선정한다. (2) 냉수 조건에는 냉수 입 、 출구온도, 순환유량, 마찰손실 및 최고사용압력을 명기하고, 냉동기 입 、 출구온도와 2 차 측 장비의 출 、 입구온도가 일치하도록 하며, 증발기 마찰손실은 순환펌프 양 정에 반영한다. (3) 냉각수 조건에는 냉각수 입 、 출구온도, 순환유량, 마찰손실 및 최고사용압력을 명기하고, 냉동 기 입 、 출구온도와 냉각탑의 출 、 입구온도가 일치하도록 하며, 응축기 마찰손실은 순환펌프 양 정에 반영한다. (4) 압축식 냉동기는 사용동력, 기동방식, 전원을 기입하고, 흡수식 냉동기는 사용열원에 대한 조건 을 기입하고, 용액펌프와 냉매펌프는 비상전원을 연결한다. (5) 물 이외의 열매를 사용할 경우에는 열매의 밀도와 비열을 기준하여 냉동기의 유량과 온도차를 정 한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 흡수식 가스냉방기기 장려금 지급 기준이 기존 성적계수(COP)기준에서 2018 년 1 월 1 일부 터 IPLV(통합성능계수)로 변경됨에 따라 에너지 성능 표기를 보다 정확하게 표현해야 함 106 기계설비 기술기준 매뉴얼 | {}
c6c52fc6-3c7f-46fc-ba8e-5473288fda93 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 (2 항, 3 항) 일반냉동기 공사를 완료한 후, 기계설비시공자가 냉수 및 냉각수 관련한 설계값 등의 정보를 이 기준 제 15 조 및 「기계설비 유지관리기준」 제 6 조 유지관리지침서에 반영할 수 있도록 해당 정보를 정확히 기록해야 함 냉수 및 냉각수 배관의 모든 마찰손실과 배관에 부착된 기기 및 장비의 저항, 증발기 및 응축수 마찰손실을 순환펌프 양정에 반영해야 함 V (4 항) 일반냉동기 공사를 완료한 후, 기계설비시공자가 압축식 냉동기는 사용동력, 기동방식, 전원 방식, 흡수식 냉동기는 사용열원에 대한 조건 등을 이 기준 제 15 조 및 「기계설비 유지관리기준」 제 6 조 유지관리지침서에 반영할 수 있도록 해당 정보를 정확히 기록해야 함 정전시 용액펌프와 냉매펌프는 정지에 따른 이상 상황(결정, Crystallization) 발생 방지를 위해 비 상전원을 연결해야 함 V (5 항) 추가 설명 없음 2. 용어 ¦ 용 어 ¦ 해 설 ¦ 해 설 ¦ 해 설 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 성적계수(COP) ¦ 성적계수 또는 성능계수는 공급된 에너지 대비 냉방 혹은 난방에 유효하게 사용된 에너지의 비율로 정의 함. 냉동기나 열펌프는 효율대신 성능계수를 이용하여 기기의 성능을 판별함 냉방 COP = 냉동능력(kW) / 입력에너지(kW) 난방 COP = 난방능력(kW) / 입력에너지(kW) 출처 : 에너지관리기준 [산업통상자원부고시 제 2018-135 호, 2018. 7. 3., 일부개정] ¦ 성적계수 또는 성능계수는 공급된 에너지 대비 냉방 혹은 난방에 유효하게 사용된 에너지의 비율로 정의 함. 냉동기나 열펌프는 효율대신 성능계수를 이용하여 기기의 성능을 판별함 냉방 COP = 냉동능력(kW) / 입력에너지(kW) 난방 COP = 난방능력(kW) / 입력에너지(kW) 출처 : 에너지관리기준 [산업통상자원부고시 제 2018-135 호, 2018. 7. 3., 일부개정] ¦ 성적계수 또는 성능계수는 공급된 에너지 대비 냉방 혹은 난방에 유효하게 사용된 에너지의 비율로 정의 함. 냉동기나 열펌프는 효율대신 성능계수를 이용하여 기기의 성능을 판별함 냉방 COP = 냉동능력(kW) / 입력에너지(kW) 난방 COP = 난방능력(kW) / 입력에너지(kW) 출처 : 에너지관리기준 [산업통상자원부고시 제 2018-135 호, 2018. 7. 3., 일부개정] ¦ 성적계수 또는 성능계수는 공급된 에너지 대비 냉방 혹은 난방에 유효하게 사용된 에너지의 비율로 정의 함. 냉동기나 열펌프는 효율대신 성능계수를 이용하여 기기의 성능을 판별함 냉방 COP = 냉동능력(kW) / 입력에너지(kW) 난방 COP = 난방능력(kW) / 입력에너지(kW) 출처 : 에너지관리기준 [산업통상자원부고시 제 2018-135 호, 2018. 7. 3., 일부개정] ¦ ¦ 에너지효율비(EER) ¦ 열출력/기기로의 에너지입력, EER = COP X 3.41 출처 : 국가청정생산지원센터 용어사전 일반적으로 전기열펌프시스템을 냉방조건으로 운전하였을 때의 성적계수로, 냉방용 량을 유효소비전력값으로 나눈 값을 말함(해설서 주) ¦ 열출력/기기로의 에너지입력, EER = COP X 3.41 출처 : 국가청정생산지원센터 용어사전 일반적으로 전기열펌프시스템을 냉방조건으로 운전하였을 때의 성적계수로, 냉방용 량을 유효소비전력값으로 나눈 값을 말함(해설서 주) ¦ 열출력/기기로의 에너지입력, EER = COP X 3.41 출처 : 국가청정생산지원센터 용어사전 일반적으로 전기열펌프시스템을 냉방조건으로 운전하였을 때의 성적계수로, 냉방용 량을 유효소비전력값으로 나눈 값을 말함(해설서 주) ¦ 열출력/기기로의 에너지입력, EER = COP X 3.41 출처 : 국가청정생산지원센터 용어사전 일반적으로 전기열펌프시스템을 냉방조건으로 운전하였을 때의 성적계수로, 냉방용 량을 유효소비전력값으로 나눈 값을 말함(해설서 주) ¦ ¦ 통합성능계수(IPLV) ¦ 각 부분부하 운전조건에서 산출된 성능계수에 부분부하 운전시간을 곱하여 적산한 값의 평균값으로 다음과 같이 계산한다. - 산출기준은 100% 부하운전시간(1%), 75% 부하운전시간(42%), 50% 부하운전시간 (45%), 25% 부하운전시간(12%)으로 규정한다. - IPLV 산출기준 : IPLV = 0.01A + 0.42B + 0.45C + 0.12D ¦ 각 부분부하 운전조건에서 산출된 성능계수에 부분부하 운전시간을 곱하여 적산한 값의 평균값으로 다음과 같이 계산한다. - 산출기준은 100% 부하운전시간(1%), 75% 부하운전시간(42%), 50% 부하운전시간 (45%), 25% 부하운전시간(12%)으로 규정한다. - IPLV 산출기준 : IPLV = 0.01A + 0.42B + 0.45C + 0.12D ¦ 각 부분부하 운전조건에서 산출된 성능계수에 부분부하 운전시간을 곱하여 적산한 값의 평균값으로 다음과 같이 계산한다. - 산출기준은 100% 부하운전시간(1%), 75% 부하운전시간(42%), 50% 부하운전시간 (45%), 25% 부하운전시간(12%)으로 규정한다. - IPLV 산출기준 : IPLV = 0.01A + 0.42B + 0.45C + 0.12D ¦ 각 부분부하 운전조건에서 산출된 성능계수에 부분부하 운전시간을 곱하여 적산한 값의 평균값으로 다음과 같이 계산한다. - 산출기준은 100% 부하운전시간(1%), 75% 부하운전시간(42%), 50% 부하운전시간 (45%), 25% 부하운전시간(12%)으로 규정한다. - IPLV 산출기준 : IPLV = 0.01A + 0.42B + 0.45C + 0.12D ¦ ¦ 통합성능계수(IPLV) ¦ 성능계수 ¦ A B ¦ C ¦ D ¦ ¦ 통합성능계수(IPLV) ¦ 운전부하(%) ¦ 100 75 ¦ 50 ¦ 25 ¦ ¦ 통합성능계수(IPLV) ¦ 출처 : 지역냉방 흡수식냉동기 기술규격서 냉동기 운전 시 부분부하 운전이 일반적이기 때문에 COP 가 실질적인 운전조건을 반 영하지 못한다는 지적에 따라 흡수식냉동기에 대하여 부분부하 특성을 반영한 계수 임(해설서 주) ¦ 출처 : 지역냉방 흡수식냉동기 기술규격서 냉동기 운전 시 부분부하 운전이 일반적이기 때문에 COP 가 실질적인 운전조건을 반 영하지 못한다는 지적에 따라 흡수식냉동기에 대하여 부분부하 특성을 반영한 계수 임(해설서 주) ¦ 출처 : 지역냉방 흡수식냉동기 기술규격서 냉동기 운전 시 부분부하 운전이 일반적이기 때문에 COP 가 실질적인 운전조건을 반 영하지 못한다는 지적에 따라 흡수식냉동기에 대하여 부분부하 특성을 반영한 계수 임(해설서 주) ¦ 출처 : 지역냉방 흡수식냉동기 기술규격서 냉동기 운전 시 부분부하 운전이 일반적이기 때문에 COP 가 실질적인 운전조건을 반 영하지 못한다는 지적에 따라 흡수식냉동기에 대하여 부분부하 특성을 반영한 계수 임(해설서 주) ¦ 기계설비 기술기준 해설 (별표 01 국토교통부 107 | {}
385a3f3d-5e36-4611-aa4d-582f34697fc8 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2.2 냉동기(계속) 2.2.2 흡수식 냉온수기 (1) 냉 、 온수 조건에는 냉 、 온수 입 , 출구온도, 순환유량, 마찰손실 및 최고사용압력을 명기하고, 냉온수기 입 , 출구온도와 2 차 측 장비의 출 , 입구 온도가 일치하도록 하고 열교환기 마찰손실은 순환펌프 양정에 반영한다. (2) 냉방 운전 시 냉수 순환량과 난방 운전 시 온수 순환량은 같게 한다. (3) 냉각수 조건에는 냉각수 입 , 출구온도, 순환유량, 마찰손실 및 최고사용압력을 명기하고, 냉온 수기 입 , 출구온도와 냉각탑의 출 、 입구 온도가 일치해야하며 응축기 마찰손실은 순환펌프 양정 에 반영한다. (4) 버너에는 형식, 사용연료, 사용압력, 표준발열량을 기입하고, 도시가스 공급 시 지역의 공급압력 을 확인해야 하며, 연료는 공급형식, 대기오염, 경제성, 취급자격 등을 고려하여 결정한다. (5) 냉매펌프 및 용액펌프는 부하조절과 흡수기에서 냉각수에 의한 열손실을 최소화하기 위하여 유 량을 조절할 수 있도록 회전수제어장치 설치를 검토해야 한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 흡수식 냉온수기 공사를 완료한 후, 기계설비시공자가 냉온수기 관련한 설계값 등의 정보를 이 기준 제 15 조 및 「기계설비 유지관리기준」 제 6 조 유지관리지침서에 반영할 수 있도록 해당 정보를 정확히 기록해야 함 냉온수기 배관의 모든 마찰손실과 배관에 부착된 기기 및 장비의 저항, 펌프의 전양정에 반영해야 함 V (2 항) 1 대의 순환펌프로 냉방과 난방에 사용하므로 동일 순환량으로 함 V (3 항) 흡수식 냉온수기 공사를 완료한 후, 기계설비시공자가 냉각수 관련한 설계값 등의 정보를 이 기준 제 15 조 및 「기계설비 유지관리기준」 제 6 조 유지관리지침서에 반영할 수 있도록 해당 정 보를 정확히 기록해야 함 냉각수 배관의 모든 마찰손실과 배관에 부착된 기기 및 장비의 저항 그리고 장비 또는 장치의 마 찰손실도 펌프의 전양정에 포함되어야 하므로 응축수 마찰손실을 순환펌프 양정에 반영해야 함 V (4 항) 흡수식 냉온수기 공사를 완료한 후, 기계설비시공자가 버너의 형식, 사용연료, 사용압력, 가 스발열량 등의 정보를 이 기준 제 15 조 및 「기계설비 유지관리기준」 제 6 조 유지관리지침서에 반 영할 수 있도록 해당 정보를 정확히 기록해야 함 도시가스 공급 시 지역의 공급압력 확인, 타 연료의 경우에는 공급형식, 대기오염, 경제성, 취급자 격 등을 검토하여 결정해야 함 108 기계설비 기술기준 매뉴얼 | {}
df6e0fe9-f3c5-4168-8605-e93272b216ad | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 에너지법 시행규칙 [별표] 에너지열량 환산기준(제 5 조제 1 항 관련) ¦ 구분 ¦ 에너지원 ¦ 단위 ¦ 총발열량 ¦ 총발열량 ¦ 총발열량 ¦ 순발열량 ¦ 순발열량 ¦ 순발열량 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 구분 ¦ 에너지원 ¦ 단위 ¦ MJ ¦ kcal ¦ 석유환산톤 (10-3 toe) ¦ MJ ¦ kcal ¦ 석유환산톤 (10-3 toe) ¦ ¦ 석유 ¦ 원유 ¦ kg ¦ 45.0 ¦ 10750 ¦ 1.075 ¦ 42.2 ¦ 10 080 ¦ 1.008 ¦ ¦ 석유 ¦ 휘발유 ¦ L ¦ 32.7 ¦ 7810 ¦ 0.781 ¦ 30.4 ¦ 7 260 ¦ 0.726 ¦ ¦ 석유 ¦ 등유 ¦ L ¦ 36.7 ¦ 8 770 ¦ 0.877 ¦ 34.2 ¦ 8170 ¦ 0.817 ¦ ¦ 석유 ¦ 경유 ¦ L ¦ 37.8 ¦ 9030 ¦ 0.903 ¦ 35.2 ¦ 8410 ¦ 0.841 ¦ ¦ 석유 ¦ B-A 유 ¦ L ¦ 39.0 ¦ 9310 ¦ 0.931 ¦ 36.4 ¦ 8690 ¦ 0.869 ¦ ¦ 석유 ¦ B-B 유 ¦ L ¦ 40.5 ¦ 9670 ¦ 0.967 ¦ 38.0 ¦ 9080 ¦ 0.908 ¦ ¦ 석유 ¦ B-C 유 ¦ L ¦ 41.7 ¦ 9 960 ¦ 0.996 ¦ 39.2 ¦ 9 360 ¦ 0.936 ¦ ¦ 석유 ¦ 프로판(LPG1 호) ¦ kg ¦ 50.4 ¦ 12 040 ¦ 1.204 ¦ 46.3 ¦ 11 060 ¦ 1.106 ¦ ¦ 석유 ¦ 부탄(LPG3 호) ¦ kg ¦ 49.5 ¦ 11 820 ¦ 1.182 ¦ 45.7 ¦ 10 920 ¦ 1.092 ¦ ¦ 석유 ¦ 나프타 ¦ L ¦ 32.3 ¦ 7710 ¦ 0.771 ¦ 29.9 ¦ 7140 ¦ 0.714 ¦ ¦ 석유 ¦ 용제 ¦ L ¦ 32.8 ¦ 7 830 ¦ 0.783 ¦ 30.3 ¦ 7240 ¦ 0.724 ¦ ¦ 석유 ¦ 항공유 ¦ L ¦ 36.5 ¦ 8720 ¦ 0.872 ¦ 33.9 ¦ 8100 ¦ 0.810 ¦ ¦ 석유 ¦ 아스팔트 ¦ kg ¦ 41.4 ¦ 9 890 ¦ 0.989 ¦ 39.2 ¦ 9360 ¦ 0.936 ¦ ¦ 석유 ¦ 윤활유 ¦ L ¦ 40.0 ¦ 9550 ¦ 0.955 ¦ 37.3 ¦ 8910 ¦ 0.891 ¦ ¦ 석유 ¦ 석유코크스 ¦ kg ¦ 35.0 ¦ 8 360 ¦ 0.836 ¦ 34.2 ¦ 8170 ¦ 0.817 ¦ ¦ 석유 ¦ 부생연료유 1 호 ¦ L ¦ 37.1 ¦ 8860 ¦ 0.886 ¦ 34.6 ¦ 8260 ¦ 0.826 ¦ ¦ 석유 ¦ 부생연료유 2 호 ¦ L ¦ 39.9 ¦ 9530 ¦ 0.953 ¦ 37.7 ¦ 9000 ¦ 0.900 ¦ ¦ 가스 ¦ 천연가스(LNG) ¦ kg ¦ 54.7 ¦ 13060 ¦ 1.306 ¦ 49.4 ¦ 1,800 ¦ 1,180 ¦ ¦ 가스 ¦ 도시가스(LNG) ¦ Nm3 ¦ 43.1 ¦ 10290 ¦ 1.029 ¦ 38.9 ¦ 9290 ¦ 0.929 ¦ ¦ 가스 ¦ 도시가스(LPG) ¦ Nm3 ¦ 63.6 ¦ 15190 ¦ 1.519 ¦ 58.4 ¦ 13 950 ¦ 1.395 ¦ ¦ 석탄 전기 등 ¦ 국내무연탄 ¦ kg ¦ 19.8 ¦ 4730 ¦ 0.473 ¦ 19.4 ¦ 4630 ¦ 0.463 ¦ ¦ 석탄 전기 등 ¦ 연료용 수입무연탄 ¦ kg ¦ 21.2 ¦ 5060 ¦ 0.506 ¦ 20.5 ¦ 4 900 ¦ 0.490 ¦ ¦ 석탄 전기 등 ¦ 원료용 수입무연탄 ¦ kg ¦ 25.2 ¦ 6020 ¦ 0.602 ¦ 24.7 ¦ 5900 ¦ 0.590 ¦ ¦ 석탄 전기 등 ¦ 연료용 유연탄(역청탄) ¦ kg ¦ 24.8 ¦ 5920 ¦ 0.592 ¦ 23.7 ¦ 5660 ¦ 0.566 ¦ ¦ 석탄 전기 등 ¦ 원료용 유연탄(역청탄) ¦ kg ¦ 29.2 ¦ 6970 ¦ 0.697 ¦ 28.0 ¦ 6690 ¦ 0.669 ¦ ¦ 석탄 전기 등 ¦ 아역청탄 ¦ kg ¦ 21.4 ¦ 5110 ¦ 0.511 ¦ 19.9 ¦ 4750 ¦ 0.475 ¦ ¦ 석탄 전기 등 ¦ 코크스 ¦ kg ¦ 29.0 ¦ 6930 ¦ 0.693 ¦ 28.9 ¦ 6900 ¦ 0.690 ¦ ¦ 석탄 전기 등 ¦ 전기(발전기준) ¦ kWh ¦ 8.9 ¦ 2130 ¦ 0.213 ¦ 8.9 ¦ 2130 ¦ 0.213 ¦ ¦ 석탄 전기 등 ¦ 전기(소비기준) ¦ kWh ¦ 9.6 ¦ 2290 ¦ 0.229 ¦ 9.6 ¦ 2290 ¦ 0.229 ¦ ¦ 석탄 전기 등 ¦ 신탄 ¦ kg ¦ 18.8 ¦ 4 500 ¦ 0.450 ¦ - ¦ - ¦ - ¦ 비고 1. "총발열량"이란 연료의 연소과 정에서 발생하는 수증기의 잠열을 포함한 발열량을 말한다. 2. "순발열량"이란 연료의 연소과 정에서 발생하는 수증기의 잠열을 제외한 발열량을 말한다. 3. "석유환산톤"(toe: ton of oil equivalent)이란 원유 1 톤(t)이 갖는 열량으로 107 kcal 를 말한다. 4. 석탄의 발열량은 인수식(引受式)을 기준으로 한다. 다만, 코크스는 건식(��)을 기준으로 한다. 5. 최종 에너지사용자가 사용하는 전력량 값을 열량 값으로 환산할 경우에는 1 kWh = 860 kcal 를 적용한다. 6. 1 cal = 4,1868 J 이며, 도시가스 단위인 Nm2 은 0°C 1 기압(atm) 상태의 부피 단위(m2)를 말한다. 7. 에너지원별 발열량(MJ)은 소수점 아래 둘째 자리에서 반올림한 값이며, 발열량(kcal)은 발열량(MJ)으로부터 환산 한 후 1 의 자리에서 반올림한 값이다. 두 단위 간 상충될 경우 발열량(MJ)이 우선한다. V (5 항) 냉매 및 용액펌프의 회전수 제어를 통해 유량 조절이 가능하도록 하여 기기의 효율을 높일 수 있도록 고려할 수 있음 2. 용어 V 내용 없음 기계설비 기술기준 해설 (별표 01 국토교통부 109 | {}
09b1311e-d327-4094-967a-640c7106251d | 국내_기계설비_기술기준_매뉴얼_최종본 | 2.2 냉동기(계속) 2.2.3 열펌프 (1) 공랭식 실외기는 냉방전용과 냉난방 겸용, 냉난방 동시형, 실내기와 의 조합비율, 배관길이, 고저 차, 실내외 온도조건 및 난방 시 제상운전에 따른 능력변화 등을 고려하여 선정한다. (2) 냉각 , 가열 능력은 실내 냉난방부하에 도입외기부하를 가산한다. (3) 압축기는 냉난방 능력, 소비전력, 전원을 기입한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 공랭식 실외기는 표준조건 대비 설치 조건(실내기와 실외기간 배관 길이, 고저차 등) 또는 운전조건(난방시 실외 저온 외기온도 조건, 제상운전 등)에 따라 성능 변동이 발생하므로 제조사 의 기술 및 설치기준을 충분히 고려해야 함 제상운전 공랭식 증발기에서 대기 중의 수증기가 응축 동결되어 서리상태로 냉각관 표면에 부착하는 현상을 적상이 라 하는데, 적상이 되면 증발기의 전열이 방해를 받아 냉장 실내 온도 상승 및 압축기에서의 액 압축 발생 등의 여러 가지 악영향을 끼침. 이를 제거하는 운전을 제상(defrosting) 운전이라 함 출처 : 공조냉동건축설비 용어사전 V (2 항) 외기부하 변동에 따른 냉각 · 가열 능력이 증감하므로 이를 고려해야 함 V (3 항) 열펌프 공사를 완료한 후, 기계설비시공자가 압축기의 냉난방 능력, 소비전력, 전원 등의 정 보를 이 기준 제 15 조 및 「기계설비 유지관리기준」 제 6 조 유지관리지침서에 반영할 수 있도록 해 당 정보를 정확히 기록해야 함 2. 용어 V 내용 없음 - 2.3 냉각탑 냉각탑은 송풍방식, 공기흐름방향, 충전재 종류, 형상 등을 고려하여 선정한다. (1) 냉각수 조건에는 냉각수 입 、 출구온도, 순환유량, 외기 습구온도를 명기하고, 냉각탑 입 , 출구 온도와 냉동기의 출 , 입구 온도가 일치해야 하며, 냉각탑 살수압, 냉각탑 높이에 따른 실양정을 순환펌프 양정에 반영한다. (2) 냉각탑의 증발량과 비산량을 냉각탑 보충수로 산정하여 시수 사용량에 반영하고, 시간당 냉각탑 보급수량은 급수가압펌프 용량에 반영한다. (3) 냉각탑의 용량산정에는 외기 습구온도를 고려하여 냉각탑 용량을 산정한다. (4) 냉각탑 냉각수가 용해 고형물질로 인한 농축이나 주변의 오염공기로 인해 냉각수 수질 오염 발생 이 예상되는 경우 냉각탑 수처리설비를 계획하여 냉동기 성능저하를 방지해야 한다. (5) 레지오넬라균의 번식을 방지하기 위한 조치를 한다. 110 기계설비 기술기준 매뉴얼 | {}
68fea9e3-d340-4075-bf44-1d2b76219589 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 해 설 1. 본문 해설 및 관련 법규 V 냉각탑 운전 시 소음 발생 등 주변 환경에 영향을 미치므로 「환경정책기본법」 환경기준을 추가 로 검토할 수 있음 V (1 항) 냉각탑 공사를 완료한 후, 기계설비시공자가 냉각수 입 · 출구온도, 순환유량, 외기 습구온도 등의 정보를 이 기준 제 15 조 및 「기계설비 유지관리기준」 제 6 조 유지관리지침서에 반영할 수 있 도록 해당 정보를 정확히 기록해야 함 냉각탑 살수압과 냉각탑 높이도 펌프의 전양정에 포함되므로 순환펌프 양정에 반영해야 함 V (2 항) 냉각탑 운전에 필요한 보충수를 시수 사용량 및 급수가압펌프 용량에 반영해야 함 V (3 항) 어프로치(approach ; 냉각탑 출구수온과 냉각탑 입구 공기의 습구온도 차, 냉각탑 출구온도 가 32°C, 냉각탑 입구의 습구온도가 27°C 인 경우 △5°C 를 표준 어프로치라함)를 통한 냉각탑 용 량을 산정하기 위해 외기 습구온도를 사용해야 함 V (4 항) 냉각탑이 설치된 위치와 사용하는 냉각수의 상태 등을 고려하여 금속 부식, 칼슘 등 수중의 미네랄 성분의 농축에 의한 스케일 형성, 그리고 이끼, 슬라임 등의 미생물에 의한 수질오염에 대 비한 수질방지대책(예 : 이물질 제거를 위한 자동 수처리 설비 적용 등)을 마련하여 성능저하를 방지해야 함 V (5 항) 레지오넬라균은 따뜻하고 습기 찬 환경(온도 25 ~ 45°C, pH 7.2 ~ 8.3)에서 잘 번식하며, 대 형건물의 냉각탑수, 목욕탕 등 샤워(냉·온수), 수도꼭지(냉·온수)등의 오염된 물 속에서 균이 서식 하다가 호흡기를 통해 감염됨에 따라, 이 기준 제 15 조 및 「기계설비 유지관리기준」 제 6 조 유지관 리지침서에 관련한 유지관리방법을 마련하고 이를 유지관리자에게 전달되도록 해야 함 기계설비 기술기준 해설 (별표 01 국토교통부 111 | {}
78f24992-ccff-4721-88a7-986e5dd308a9 | 국내_기계설비_기술기준_매뉴얼_최종본 | 「환경정책기본법 시행령」 [별표 1] 환경기준 2. 소음 (단위: Leq dB(A)) ¦ 지역 구분 ¦ 적용 대상지역 ¦ 기준 ¦ 기준 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 지역 구분 ¦ 적용 대상지역 ¦ 낮 (06 : 00 ~ 22 : 00) ¦ 밤 (22 : 00 ~ 06 : 00) ¦ ¦ 일반 지역 ¦ "가"지역 ¦ 50 ¦ 40 ¦ ¦ 일반 지역 ¦ "나"지역 ¦ 55 ¦ 45 ¦ ¦ 일반 지역 ¦ "다"지역 ¦ 65 ¦ 55 ¦ ¦ 일반 지역 ¦ "라"지역 ¦ 70 ¦ 65 ¦ ¦ 도로변 지역 ¦ "가" 및 "나"지역 ¦ 65 ¦ 55 ¦ ¦ 도로변 지역 ¦ "다"지역 ¦ 70 ¦ 60 ¦ ¦ 도로변 지역 ¦ "라"지역 ¦ 75 ¦ 70 ¦ 비 고 1. 지역구분별 적용 대상지역의 구분은 다음과 같다. 가. "가"지역 1) 「국토의 계획 및 이용에 관한 법률」 제 36 조제 1 항제 1 호라목에 따른 녹지지역 2) 「국토의 계획 및 이용에 관한 법률」 제 36 조제 1 항제 2 호가목에 따른 보전관리지역 3) 「국토의 계획 및 이용에 관한 법률」 제 36 조제 1 항제 3 호 및 제 4 호에 따른 농림지역 및 자연환경보전지역 4) 「국토의 계획 및 이용에 관한 법률 시행령」 제 30 조제 1 호가목에 따른 전용주거지역 5) 「의료법」 제 3 조제 2 항제 3 호마목에 따른 종합병원의 부지경계로부터 50 m 이내의 지역 6) 「초·중등교육법」 제 2 조 및 「고등교육법」 제 2 조에 따른 학교의 부지경계로부터 50 m 이내의 지역 7) 「도서관법」 제 2 조제 4 호에 따른 공공도서관의 부지경계로부터 50 m 이내의 지역 나. "나"지역 1) 「국토의 계획 및 이용에 관한 법률」 제 36 조제 1 항제 2 호나목에 따른 생산관리지역 2) 「국토의 계획 및 이용에 관한 법률 시행령」 제 30 조제 1 호나목 및 다목에 따른 일반주거지역 및 준주거지역 다. "다"지역 1) 「국토의 계획 및 이용에 관한 법률」 제 36 조제 1 항제 1 호나목에 따른 상업지역 및 같은 항 제 2 호다목에 따른 계획관리지역 2) 「국토의 계획 및 이용에 관한 법률 시행령」 제 30 조제 3 호다목에 따른 준공업지역 라. "라"지역 「국토의 계획 및 이용에 관한 법률 시행령」 제 30 조제 3 호가목 및 나목에 따른 전용공업지역 및 일반공업지역 2. "도로"란 자동차(2 륜자동차는 제외한다)가 한 줄로 안전하고 원활하게 주행하는 데에 필요한 일정 폭의 차선이 2 개 이상 있는 도로를 말한다. 3. 이 소음환경기준은 항공기소음, 철도소음 및 건설작업 소음에는 적용하지 않는다. 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 양정 ¦ 펌프가 실제로 양수하는 수면 간의 높이의 차를 실양정(���)이라 하며, 배관계통 의 마찰손실을 감안해서 실양정에 가산한 것을 전양정(���)이라고 한다. 출처 : 두산백과 ¦ ¦ 레지오넬라균 ¦ 레지오넬라균은 길이 2 ~ 20 �m, 폭 0.3 ~ 0.9 �m 의 막대기 모양을 한 박테리아의 일종이다. 레지오넬라균은 흙에 서식하는 세균 중 하나인데 따뜻한 물에서도 잘 번 식하며, 자연 및 인공적인 급수시설에서 흔히 발견된다. 사람의 몸에 호흡기를 통해 흡입되어 심하면 폐렴을 일으키고, 약 25% 정도의 치사율을 보이고있다. 몸속에 들 어온 레지오넬라균은 2 ~ 12 일 가량 잠복기를 거치고, 감기와 같은 고열, 설사, 두통, 구토 증세를 보이게 한다. 출처 : 물백과 사전 ¦ 112 기계설비 기술기준 매뉴얼 | {}
effab1a5-53d3-4325-b103-920691d6a7d6 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.4 축열(빙축열, 수축열) (1) 2.1(8)의 기준에 따라 축냉식 전기냉방으로 설치할 경우에는 전체 축냉방식 또는 축열률 40% 이 상인 부분축냉방식으로 설치해야 한다. (2) 축열 시스템의 브라인은 입 、 출구온도, 순환유량, 마찰손실 및 최고사용압력, 부동액 종류 및 농 도를 명기하고, 냉동기 입 、 출구온도와 2 차 측 장비의 출 , 입구 온도가 일치하도록 하고 증발기 마찰손실은 순환펌프 양정에 반영한다. (3) 축열 냉동기의 주간 운전 시 주간 브라인 입 * 출구온도, 순환유량, 마찰손실 및 최고사용압력을 명기한다. (4) 축열탱크에는 축열량, 축열률, 축열탱크 크기, 장비 운전중량 등을 명기한다. (5) 열원용량과 축열탱크 용량의 산정은 열부하와 열원용량의 열취득과 운전시간을 고려하여 결정 한다. (6) 열원기기의 운전시간 및 정지시간은 열부하특성을 고려하여 결정한다. (7) 열펌프식 빙축열 유닛은 다음 사항을 고려한다. ① 빙축열 유닛을 통과 하는 수량은 변화시키지 않는다. ② 빙축열 유닛을 복수로 설치하는 경우는 각 축열탱크의 수위를 일정하도록 하기 위하여 연통관을 설치한다. ③ 야간 운전을 고려하여 소음대책을 검토한다. ④ 축열탱크에는 배수용 배관을 설치한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 2.1(8)의 기준에 따라 축냉식 전기냉방으로 설치할 경우에는 건축물의 냉방부하에 대해서 전체 축냉방 또는 축열률 40% 이상인 부분 축냉방식으로 설치하여 냉난방기기 사용에 따른 전력 사용량이 분산되도록 하여야 함 (8) 다음에 해당하는 건축물 중 중앙집중냉방설비를 설치하는 경우에는 「건축물의 냉방설비에 대한 설치 및 설계기준」 제 4 조에 따른 축냉식 또는 가스를 이용한 중앙집중냉방방식으로 해야 한다. ① 영 별표 5 제 2 호 다목부터 마목까지의 건축물 ② 10 000 m2 이상인 건축물 중 「건축법 시행령」 [별표 1] 제 5 호 가목부터 라목까지에 해당하는 문화 및 집 회시설, 제 6 호에 따른 종교시설, 제 10 호에 따른 교육연구시설(연구소는 제외한다), 제 28 호에 따른 장례식 장 (2 항) 축열 시스템 공사를 완료한 후, 기계설비시공자가 브라인 입 · 출구온도, 순환유량, 마찰손실 및 최고사용압력, 부동액 종류 및 농도 등의 정보를 이 기준 제 15 조 및 「기계설비 유지관리기준」 제 6 조 유지관리지침서에 반영할 수 있도록 해당 정보를 정확히 기록해야 하며, 증발기 마찰손실 은 펌프의 전양정에 포함되므로 순환펌프 양정에 반영해야 함 V (3 항, 4 항) 기계설비시공자가 축열 냉동기의 주간 운전 시 주간 브라인 입 · 출구온도, 순환유량, 마찰손실 및 최고사용압력과 축열탱크의 축열량, 축열률, 축열탱크 크기, 장비 운전중량 등의 정 보를 이 기준 제 15 조 및 「기계설비 유지관리기준」 제 6 조 유지관리지침서에 반영할 수 있도록 해 당 정보를 정확히 기록해야 함 V (5 항, 6 항) 건축물 용도별로 부하 특성(일반 건축물의 주 사용 시간은 주간, 공동주택, 호텔 등의 주 사용 시간은 야간 등)이 다르므로, 이를 고려하여 용량과 운전 방법을 결정해야 함 국토교통부 113 기계설비 기술기준 해설 (별표 01 | {}
16d449bf-820e-4323-8f80-bf14717ff2a0 | 국내_기계설비_기술기준_매뉴얼_최종본 | V (7 항 1 호) 추가 설명 없음 V (7 항 2 호) 연통관은 축열탱크 내 물의 혼합과 흐름에 영향을 주는 요소로, 각 축열탱크마다 상하, 좌우로 나누고 하부 연통관은 가능한 바닥에 가깝게, 상부 연통관은 수면에 가까이 배치해야 함 V (7 항 3 호) 「환경정책기본법」 환경기준을 검토해야 함 V (7 항 4 호) 축열탱크 청소 등에 필요한 조치임 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 축열률 ¦ 통계적으로 연중 최대냉방부하를 갖는 날을 기준으로 그 밖의 시간에 필요한 냉방 열량 중에서 이용이 가능한 냉열량이 차지하는 비율을 말하며 백분율(%)로 표시한 다. 축열률 = (이용가능한 축열용량 ÷ 일일 최대부하량) x 100 [%] 출처 : 건축물의 냉방설비에 대한 설치 및 설계기준 제 3 조(정의) ¦ - 2.5 보일러 (1) 버너에는 형식, 사용연료 종류, 연료 사용량, 사용압력, 표준발열량을 기입하고, 도시가스 공급 시 지역의 공급압력을 확인하며, 연료는 공급형식, 대기오염, 경제성, 취급자격 등을 고려하여 결 정한다. (2) 온열원기기를 복수로 설치하는 경우는 사용 시간대, 조닝부하의 조건, 온열원기기의 효율, 보수 점검 등을 종합 검토하여 결정한다. (3) 온수보일러는 보일러 형식과 연료 종류 및 압력, 출력, 운전압력, 유량, 유체 종류, 입 、 출구 온도, 효율, 부속품 등의 자료가 명기되어야 한다. (4) 증기보일러는 보일러 형식과 효율, 출력, 운전압력, 증기유량, 부속품 등을 장비일람표에 명기한 다. (5) 증기보일러 계통에는 거품방지 약품과 스케일 방지 약품을 보일러 보급수에 주입하거나 부식억 제제를 증기관에 주입할 수 있다. 보일러 보급수는 스케일 방지를 위하여 연수를 사용해야 한다. (6) 증기보일러의 응축수 등의 폐열을 회수하기 위한 열회수설비를 설치한다. (7) 응축수 탱크의 저수위는 보급수 펌프의 캐비테이션이 발생하지 않는 높이로 한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 보일러 공사를 완료한 후, 기계설비시공자가 버너의 형식, 사용연료 종류, 연료 사용량, 사용 압력, 발열량 등의 정보를 이 기준 제 15 조 및 「기계설비 유지관리기준」 제 6 조 유지관리지침서에 반영할 수 있도록 해당 정보를 정확히 기록해야 하며, 도시가스 공급 시 지역의 공급압력 확인, 타 연료의 경우에는 공급형식, 대기오염, 경제성, 취급자격 등을 검토하여 결정해야 함 V (2 항, 5 항) 추가 설명 없음 V (3 항, 4 항) 기계설비시공자가 이 기준 제 15 조 및 「기계설비 유지관리기준」 제 6 조 유지관리지침서 에 반영할 수 있도록 해당 정보(온수보일러 : 보일러 형식, 연료 종류 및 압력, 출력, 운전압력, 유 114 기계설비 기술기준 매뉴얼 | {}
759ebb0d-f414-4e50-bfc2-e222c874d2d2 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 량, 유체 종류, 입 · 출구 온도, 효율, 부속품 등, 증기보일러 : 보일러 형식과 효율, 출력, 운전압력, 증기유량, 부속품 등)를 정확히 기록해야 함 V (6 항) 응축수 등의 폐열 회수를 통한 기계설비 에너지 절약을 위함 V (7 항) 저수위시 보급수 펌프로의 증기 또는 공기 흡입에 따른 캐비테이션에 의한 응축수 공급 불 량을 방지하기 위함 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 연수(��) ¦ 물의 경도를 초래하는 다가 양이온(polyvalent cation), 특히 칼슘이온이나 마그네슘 이온의 함유량이 적은 물로 단수라고도 하며, 센물에 대응하는 말 출처 : K-water 와 함께하는 물정보포털 물백과 사전 ¦ ¦ 캐비테이션 (cavitation) ¦ 캐비테이션(cavitation): 조절밸브의 1, 2 차측 간의 압력차가 클 때, 즉 빠른 속도로 액 체가 운동할 때 유체의 압력이 그 온도에서의 증기압 보다 낮아져 유체가 기화하여 기포(��)가 발생하는 현상이다. 2 개의 과정으로 발생하는데, 1 차는 내부 유체 압력 이 임계점까지 떨어지는 단계, 2 차는 증기의 공동(空洞) 즉 기포가 형성되는 단계이 다. 기포는 유체와 함께 운반되어 밸브 내 고압영역에 도달하여 갑자기 터지거나 쭈 그러져 붕괴된다. 이로 인해 밸브 내표면 부식은 물론 인접된 배관부분을 손상시킨 다. 소음과 진동을 일으켜 마치 배관계통에 자갈이 흐르는 것과 유사한 것으로 설명 된다. 출처: 설비공학편람, 제 4 권. p5.33-7 ¦ 2.5 보일러(계속) 2.5.1 연도 및 배기통 (1) 연도는 원형을 원칙으로 하고 수평 길이는 가능한 짧게 하며, 곡관 부분을 최소화 한다. 수평연도 의 길이가 긴 경우에는 수평 길이를 고려하여 입상 연도 단면적을 결정한다. (2) 매연 발생시설의 연도에는 분진 측정구를 부착한다. (3) 보일러 연도 설계 시 다음을 고려한다. ① 연도의 표면온도는 50°C 이하로 해야 한다. ② 보일러의 수직형 연도 하단부에는 물빼기 밸브를 설치하고, 배수 배관을 배수구까지 연결한다. ③ 연도 크기는 보일러 정격용량과 굴뚝 연결 및 높이에 적합하게 한다. ④ 기타 필요한 사항은 KGS GC208(주거용 가스보일러의 설치 、 검사 기준), GC209(상업 、 산업용 가스보일러의 설치 、 검사 기준)에 따른다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 연도는 가능한 단순한 형태로 설치하여 내부에 응축수 고임이 발생하지 않도록 해야함 V (2 항) 「대기환경보전법」, 「대기오 염공정시험기준」 참고 InpwwwwwaNaN62-343AGENPMWRINEWERWAENCENCENCE0 NEWEIGETBORMENEVENSMENEISIENSTENSIGNENGNGNGNEN V (3 항 1 호) 최대한 연기 중 잠열을 회수하고, 연도 표면온도에 의한 화상방지를 위함 기계설비 기술기준 해설 (별표 언 국토교통부 115 | {}
07e7f594-1989-419a-8eb9-dee7080a6ee4 | 국내_기계설비_기술기준_매뉴얼_최종본 | V (3 항 2 호) 연소가스 중 포함된 수분을 제거하기 위함 V (3 항 3 호, 4 호) 추가 설명 없음 2. 용어 V 내용 없음 -- --- 2.6 열교환기 열교환기는 판형, 원통다관형, 스파이럴형, 원통 판형(Shell & Plate) 등으로 아래 사항을 고려한다. (1) 고온유체와 저온유체 사이에 에너지 전달이 균형을 이루도록 해야 한다. (2) 운전압력은 연결 계통의 운전조건과 열교환기의 조건을 확인하여 결정한다. (3) 열교환기의 마찰손실은 유체 분배계통 내의 다른 장치의 마찰손실을 고려해야 한다. (4) 판형 열교환기의 마찰손실은 70 kPa 이하로 하고, 가능한 고온과 저온관의 운전압력이 비슷하도 록 한다. (5) 안전/릴리프밸브의 설정 압력은 배관계통과 열교환기의 최고사용압력 이하로 한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항 ~ 4 항) 추가 설명 없음 V (5 항) 배관 계통과 열교환기의 파손을 방지하기 위함 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 안전 밸브 (Safety Valve) ¦ 증기 또는 가스의 발생장치에 안전확보를 위하여 사용하고, 유체의 압력이 기준치를 넘었을 때 순간적으로 자동 작동하는 기능을 가진 밸브 출처 : 한국조선협회 단체표준 KMS 300 : 2012 선박용 안전 릴리프 밸브 ¦ ¦ 릴리프 밸브 (Relief Valve) ¦ 주로 액체에 사용하고, 액체의 압력이 기준치에 도달하면 그 압력의 상승에 따라서 자동적으로 열리는 기능을 가진 밸브 출처 : 한국조선협회 단체표준 KMS 300 : 2012 선박용 안전 릴리프 밸브 ¦ ¦ 안전 릴리프 밸브 (Safety relief valve) ¦ 주로 배관계통에 설치하며, 용도에 따라 기체 또는 액체에서도 사용 할 수 있는 밸브 출처 : 한국조선협회 단체표준 KMS 300 : 2012 선박용 안전 릴리프 밸브 ¦ 116 기계설비 기술기준 매뉴얼 | {}
fd1644ab-8488-463b-9484-033801c486ca | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.7 팽창탱크 (1) 밀폐 배관계통에는 팽창탱크의 용량 및 형식 등을 고려하여 설치위치를 정한다. (2) 개방형 팽창탱크의 팽창관, 압력 도피관에는 밸브를 사용해서는 안 된다. (3) 밀폐형 팽창탱크에는 보급수 압력이 배관 계통의 정수두보다 50 kPa 이상 높은 경우에는 압력계 와 함께 감압밸브와 역류방지밸브를 설치하며, 최고 압력 제어를 위한 릴리프밸브를 구비한다. (4) 공조 배관의 물이 음용수 계통으로 역류하지 않도록 역류방지 밸브 등을 구비한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항, 2 항, 3 항) 추가 설명 없음 V (4 항) 역류밸브 구비에 앞서 공조배관과 음용수배관 간에 크로스커넥션 여부를 검토하고, 불가피 한 경우에는 역류방지밸브를 설치함 2. 용어 V 내용 없음 - 2.8 펌프 펌프의 형식은 일반용 펌프, 보일러급수펌프, 순환펌프 및 오일펌프 등으로 구분하며 다음 사항을 고 려한다. (1) 펌프효율은 KS 규격 효율 이상을 적용하며, 장비일람표에 명기한다. (2) 고장 및 유지보수를 고려하여 순환펌프는 예비펌프를 두어야 한다. (3) 펌프 전동기는 사용동력 및 전원을 기입하고 비상전원 필요 여부를 확인한다. (4) 펌프의 제어방식(대수제어, 교차순번제어 등)을 결정하여 장비일람에 명시한다. (5) 단, 대수제어방식을 채택한 경우에는 예비펌프 설치하지 않을 수 있다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) KS B 6318(양쪽 흡입 벌류트 펌프), KS B 7501(소형 흡입 벌류트 펌프), KS B 7505(소형 다 단 원심펌프)를 규정하고 있으므로, 기계설비시공업자가 이 기준 제 15 조 및 「기계설비 유지관리 기준」 제 6 조 유지관리지침서에 반영할 수 있도록 해당 정보를 정확히 기록해야 함 V (2 항) 추가 설명 없음 V (3 항, 4 항) 기계설비시공업자가 이 기준 제 15 조 및 「기계설비 유지관리기준」 제 6 조 유지관리지침 서에 반영할 수 있도록 해당 정보(펌프 전동기의 사용동력 및 전원과 비상전원 필요 여부, 그리고 펌프의 제어방식(대수제어, 교차순번제어 등))를 정확히 기록해야 함 V (5 항) 펌프 구성 및 제어방식에 따라서 고장 및 유지관리 시에도 정상적으로 펌프 운전이 가능하 국토교통부 117 기계설비 기술기준 해설 (별표 01 | {}
788cd00a-efad-4623-b13e-86ef16664fae | 국내_기계설비_기술기준_매뉴얼_최종본 | 다면, 예비펌프를 설치하지 않아도 됨(예시, 펌프 2 대(용량 50%)에 인버터 제어를 적용한 경우) 2. 용어 V 내용 없음 --- 2.9 지열 열펌프 시스템 (1) 부하계산 전문프로그램을 이용하여 건축물의 용도, 건축재, 마감재 등을 반영하여 부하를 계산한 다. (2) 지중열교환기 및 시스템 일반형식 결정은 다음에 따른다. ① 부하계산 결과 의 부하패턴, 부하용량, 천공부지의 상황을 고려하여 유지보수가 용이한 지중 열 원 방식을 선정한다. ② 냉 、 난방부하 처리, 급탕부하 처리 등의 지열원 열펌프 사용 용도와 건물 높이, 부하측 시스템을 고려하여 물 , 물, 물 , 공기 또는 물 、 냉매 방식을 결정한다. ③ 전력피크 및 사용자의 운전비 절감을 위하여 수축열 지열시스템, 냉각탑, 보일러 등과 연동된 하 이브리드 지열시스템 등의 적용을 검토한다. (3) 지중 열전도 시험은 다음에 따른다. 다음과 같은 지중 열전도 시험을 통하여 지열 시스템의 사양 을 결정한다. ① 시험 홀에 열매체(물)를 주입하고 열교환기 내부를 순환시켜 열매체의 온도 변화와 지중 온도 변 화 추이를 측정하여 지반의 열특성과 열교환능력을 예측한다. ② 시뮬레이션 프로그램은 국제적으로 통용되고, 인정되는 전문 설계 프로그램(GLD, GLHEPro, GchpCalc, EED, FEFLOW 등)을 이용한다. ③ 시뮬레이션은 20 년 이상의 입구수온(EWT; entering water temperature) 변화를 검토하여 설 계 시 적용한 냉방 입구수온과 난방 입구수온이 확보되는지 확인한다. (4) 지중 열교환기 사양 확정 및 설계는 다음에 따른다. ① 지중 열교환기 설계프로그램을 사용하여 시험시추 암반의 성상 및 열전도 시험 결과 를 입력하여 계산한다. ② 설계 시에는 건물의 연간부하, 현장의 열전도 시험 결과, 현장의 암반구성 자료, 열펌프 사양, 지 중 평균온도, 순환수 사양, 지중 열교환기 배치 등의 자료를 활용한다. ③ 지중 열교환기의 총길이는 냉난방시 지중 열교환기 필요길이의 최댓값으로 한다. ④ 천공(bore hole) 개수는 지중 열교환기 필요길이를 지중열교환기 1 개당 길이를 나누어 산출한 다. ⑤ 지중 열교환기에 사용하는 열매체는 물을 원칙으로 한다. 다만, 한랭지 등의 동결방지 대책으로 서 부동액의 사용을 검토하는 경우는 기기에 대한 영향, 안정성, 환경성 등을 고려하여 결정한 다. 부동액을 주입할 경우에는 동결점이 -6°C 이하가 되도록 한다. ⑥ 그라우트의 혼합비율을 명시해야 한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 대상 건축물의 정확한 지중열교환기 수량과 열펌프 용량을 산출하기 위해서는 건축물의 월 118 기계설비 기술기준 매뉴얼 | {}
1a70ac89-c4cc-43de-99a2-17b6db2caab7 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 별 냉·난방 부하 집계가 가능한 동적 열부하 계산 프로그램 사용을 권장함 V (2 항 1 호) 지중열교환기는 시공 대상 부지의 건폐율, 지하층수, 천공간격 및 그에 따른 토목 공사 등과 의 간섭을 최소화할 수 있는 공법을 선택해야 함 V (2 항 2 호) 추가 설명 없음 V (2 항 3 호) 대상 건축물의 냉난방 부하 비율을 확인하여 지중열교환기로 들어가는 연중 냉난방 부 하의 불균형으로 인해 지중 온도가 계속 올라가거나 내려가지 않도록 해야 함 V (3 항 1 호, 2 호) 지중열교환기 형식에 따라 지중 열전도 시험 방법 및 시뮬레이션 프로그램을 선택 해야 함 V (3 항 3 호) 시뮬레이션을 통해 확인이 가능한 사항으로, 이때 지중에 입력되는 부하는 대상 건축물 의 월별 냉난방 부하를 입력해야 함 V (4 항 1 호 ~ 3 호) 추가 설명 없음 V (4 항 4 호) 개방형 지중열교환기는 전체 천공 깊이 중 지하수가 순환하는 깊이가 실제 열교환되는 길이이므로 이를 고려하여 수량을 산출해야 함 V (4 항 5 호) 밀폐형은 부동액 사용을 고려할 수 있으며, 개방형은 지하수를 그대로 사용하므로 부동 액을 사용할 수 없음 V (4 항 6 호) 그라우트는 지중과 열교환 배관을 열적으로 연결하는 역할을 하므로 시공 완료 후 밀폐 할 수 있는 혼합비를 사용해야 하며, 동시에 열전도율이 높은 것을 사용해야함. 이때 열전도를 높 이기 위해 모래를 혼합하여 사용하는 경우는 모래의 무게로 인해 배관이 압착 변형될 수 있으므 로 주의 해야 함 2. 용어 V 내용 없음 - ○--- --- 2.10 태양열 시스템 (1) 온수 조건에는 온수 입 , 출구온도, 순환유량, 마찰손실 및 최고사용압력을 명기하고, 집열기 입 , 출구온도와 2 차 측 장비의 출 、 입구온도가 일치하도록 하며, 집열기 마찰손실은 순환펌프 양 정에 반영한다. (2) 태양열 의존율 및 집열기 매수 선정은 다음에 따른다. ① 연간 급탕부하 형태와 태양열 집열량 형태를 비교하여 최적의 시스템 용량을 선정한다. ② 태양열 집열량은 부하보다 커지지 않고 보조열원 사용량을 최소화하도록 선정한다. ③ 계절별 부하특성을 고려하여 집열기의 경사각을 결정한다. (3) 축열탱크 용량 선정은 다음에 따른다. ① 축열탱크에서의 열손실, 초기 예열부하 등을 고려하되 과다 선정되지 않도록 한다. (4) 시스템 구성은 다음에 따른다. ① 경제적이고 보수 점검이 용이하도록 집열기, 축열탱크, 팽창탱크, 열교환기, 순환펌프, 컨트롤러 를 조합하여 배치한다. ② 건축물의 규모와 계절별 부하특성, 부하용량 등을 고려하여 태양열과 보조열원과 의 연동이 원활 하게 이루어지도록 제어장치를 설치한다. 기계설비 기술기준 해설 (별표 01 국토교통부 119 | {}
e40082d2-a73f-40b7-ac4b-87624fdb1d3a | 국내_기계설비_기술기준_매뉴얼_최종본 | 해 설 1. 본문 해설 및 관련 법규 V (1 항) 기계설비시공업자가 이 기준 제 15 조 및 「기계설비 유지관리기준」 제 6 조 유지관리지침서에 반영할 수 있도록 해당 정보(온수 입 · 출구온도, 순환유량, 마찰손실 및 최고사용압력 등의 온수 조건)를 정확히 기록해야 하며, 집열기 마찰손실은 펌프의 전양정에 포함되므로 순환펌프 양정에 반영해야 함 V (2 항 ~ 4 항) 추가 설명 없음 2. 용어 V 내용 없음 -- --- 2.11 연료전지 (1) 장비일람에 연료전지의 사용연료의 종류, 연료 사용량, 사용압력을 기입하고, 도시가스 공급 시 지역의 공급압력을 확인한다. (2) 연료전지의 급탕이용 시 주열원 또는 보조열원으로 사용하고 장비일람에 급탕열량, 급탕유량 및 입 、 출구온도조건, 최고사용압력을 명시한다. (3) 통풍이 잘 되는 장소에 배치해야 하며, 실내에 배치할 경우는 환기설비를 갖추어야 한다. (4) 가스, 급수, 배수 등의 설비를 갖추어야 한다. (5) 그 밖의 필요한 사항은 KGS FU551(도시가스 사용시설의 시설 , 기술 、 검사 기준)에 따른다. 해 설 1. 본문 해설 및 관련 법규 V (1 항, 2 항) 기계설비시공자가 연료전지 관련 정보(연료전지 형식 SOFC, PEMFC), 연료 사용량, 사 용압력, 도시가스 공급 시 지역의 공급압력 등) 및 연료전지 급탕이용 시의 정보(주열원 또는 보 조열원 여부, 급탕열량, 급탕유량 및 입 · 출구온도조건, 최고사용압력 등)를 이 기준 제 15 조 및 「기계설비 유지관리기준」 제 6 조 유지관리지침서에 반영할 수 있도록 해당 정보를 정확히 기록해 야 함 V (3 항) 보통 도시가스(CH4)에서 수소를 추출하고 공기에서 산소를 추출하여 반응시켜 전기와 열을 생산하므로 설치된 공간에 충분한 급배기가 되도록 자연 및 기계식 환기설비를 갖추어야 함 V (4 항, 5 항) 추가 설명 없음 2. 용어 V 내용 없음 120 기계설비 기술기준 매뉴얼 | {}
afc12664-0d4a-4734-83e1-d5cdec05bd4d | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.12 패키지 에어컨 (1) 장비일람표에 유닛의 형식과 풍량, 기외정압(덕트 연결형), 외기량, 냉각 、 가열능력, 동력, 전압, 상, 주파수, 입 、 출구 공기 、 물 조건, 공기필터 성능 등을 명기한다. (2) 실외기는 냉방전용과 냉난방 겸용, 냉난방 동시형, 실내기와 의 조합비율, 배관길이, 고저차, 실내 외 온도조건 및 난방 시 제상운전에 따른 능력변화 등을 고려하여 선정한다. (3) 냉각 , 가열 능력은 실내 냉난방부하에 도입외기부하를 가산한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 기계설비시공자가 패키지 에어컨 형식과 풍량, 기외정압(덕트 연결형), 외기량, 냉각 · 가열 능력(냉방 · 난방능력), 동력, 전압, 상, 주파수, 입 · 출구 공기 · 물 조건, 공기필터 성능 등의 정보 를 이 기준 제 15 조 및 「기계설비 유지관리기준」 제 6 조 유지관리지침서에 반영할 수 있도록 해당 정보를 정확히 기록해야 함 V (2 항) 제조사의 기술 및 설치기준을 충분히 고려해야 함 V (3 항) 외기부하 변동에 따른 냉각 · 가열능력(냉방 · 난방능력)이 증감하므로 이를 고려해야 함 2. 용어 V 내용 없음 2.13 항온항습기 (1) 항온항습기는 열이나 수증기 발생 등이 없는 곳에 설치한다. (2) 전원이 가깝고 장비 배수가 용이한 장소에 설치한다. (3) 비상전원 필요 여부를 확인하여 반영한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 외부의 영향을 가능한 최소화해야 함 V (2 항) 수시로 발생하는 응축수를 즉시 배출할 수 있어야 함 V (3 항) 항온항습기의 요구조건을 파악하여 정전 대비 여부를 판단해야 함 2. 용어 V 내용 없음 국토교통부 121 기계설비 기술기준 해설 (별표 01 | {}
b1c35359-d4ba-45d8-9531-5ae8bd8b01df | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 열원 및 냉난방설비 시공 3.1 일반사항 (1) 각종 열원기기의 설치에는 기기의 성능을 충분히 발휘할 수 있도록 하고, 기기설치 관련 법규 등 을 준수하여 시공한다. (2) 기초는 기기의 운전중량과 외력에 견딜 수 있고, 지지면을 가지는 철근콘크리트 및 콘크리트조로 서 지지력이 있는 바닥 또는 지반 위에 설치한다. 표면은 모르타르를 바르고 설치면은 수평으로 마무리한다. (3) 기기는 지진 등에 변형을 일으키지 않도록 기초 볼트로 고정한다. (4) 본체에는 배관 등의 운전중량이 직접 걸리지 않도록 시공한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 「고압가스 안전관리법」, 「환경정책기본법」, 「안전검사 고시」, 「열사용기자재의 검사 및 검 사면제에 관한 기준」 등의 관련 법규를 준수해야 함 V (2 항, 3 항, 4 항) 이 기준 [별표 12]의 관련 내용을 참조하여 시공함 2. 용어 내용 없음 ---- ○----- --- -- 3.2 냉동기 3.2.1 일반냉동기 (1) 냉동기의 설치는 「고압가스 안전관리법」및 그 외의 관련 법규에 준하여 운전, 유지관리, 안전상 에 지장이 없도록 시공한다. (2) 콘크리트 기초 또는 강제기초 위에 기초판을 수평으로 설치한다. 방진장치를 하는 경우에도 같 다. (3) 냉동기에 접속하는 냉각수, 냉수배관에는 플렉시블이음을 설치한다. (4) 냉동기용 보호계전기함 등 진동에 의하여 작동이 저해될 염려가 있는 것은 방진을 고려해서 설치 한다. 3.2.2 흡수식 냉온수기 흡수식 냉온수기 시공은 3.2.1 에 따른다. 3.2.3 열펌프 열펌프 시공은 3.12 에 따른다. 해 설 1. 본문 해설 및 관련 법규 122 기계설비 기술기준 매뉴얼 | {}
d5d9904a-8df6-4dd0-9c25-5fa89f5eeb32 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 (1 항) 「고압가스 안전관리법」 에 적용을 받는 냉동기를 사용하려는 자는 냉동기기를 설치하기 전 에 행정관청에 허가 또는 신고하여야 하고, 사용하기 전에 한국가스안전공사의 완성검사를 받아 야 하며, 정기적으로 정기검사 및 자율검사를 받아야 함 ![image](/image/placeholder) 기술검토등 한국가스안전공사 검토신청 · 시설 및 기술기준 적합 여부 기술검토서 또는 안전성 향 (기술검토) 상계획서(종합적안전관리대 · 공정안정자료, 안전성 평가, 안 상자)제출 결과 회신 전운전계획, 비상조치계획 등 법 제 13 조의 2 영 제 3 조, 의 적정성(안전성향상계획) 사 사업허가_법 제 4 조 허가관청 허가신청 업 · 국민의 생명 및 재산보호 · 사업계획서 · 안전성 확보 여부 개 · 정관 및 등기부 등본 설치금지지역 여부 시 · 공사의 기술검토서 허가 · 이 법령 및 타 법령 저촉 여부 · 결격사유(저장, 냉동 제외) 전 검사신청 완성검사_법 제 16 조 한국가스안전공사 · 중간검사 · 시설기준에 적합 여부검사 · 시설 완공 시 완성검사 결과 통보 · 안전관리규정제출 허가관청 · 안전관리자 선임 · 법령 위반 시 행정처분 ■ 위해 유발 시 행정처분 허가(신고)관청 · 위해 방지를 위한 조치 명령 · 법령 위반 시 벌칙, 과태료 부과 한국가스안전공사 ■시설에 대한 정기, 수시검사 정기검사 : 공인검사기관(냉난방용) 사 · 안전관리규정 심사 평가 한국가스안전공사 후 · 안전관리자 교육 관 리 보험가입 시설을 기준에 적합하도록 유지 안전관리규정 준수 사업 자 시설에 대한 자율검사 실시 수리, 청소 등 안전기준 준수 · 시설 변경 시 변경허가, 완성검사 ※ 신규허가 절차와 동일 출처 : 냉동설비와 고압가스 안전관리법 해설(집중기획), 대한설비공학회 설비저널, 2013. 07 V (2 항, 3 항) 이 기준 [별표 12]의 관련 내용을 참조하여 시공함 V (4 항) 추가 설명 없음 V (3.2.2, 3.2.3) 추가 설명 없음 2. 용어 내용 없음 국토교통부 123 기계설비 기술기준 해설 (별표 01 | {}
c4225cb3-26c4-4a04-9cb6-623dd6396817 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3.3 냉각탑 (1) 냉각탑은 표면을 모르타르로 마감한 콘크리트기초 또는 형강제 받침대 위에 자중, 적설, 풍압, 지 진, 기타의 하중 및 진동에 대하여 안전하게 설치한다. (2) 냉각탑의 설치 위치는 풍향 및 장해물을 고려하여 선정하고, 냉각탑에서의 배기 및 소음이 해당 지역의 「환경정책기본법」에 따른 환경기준을 준수할 수 있도록 한다. 해 설 1. 본문 해설 및 관련 법규 (1 항) 이 기준 [별표 12]의 관련 내용을 참조하여 시공함 V (2 항) 「환경정책기본법」 시행령 [별표 1] 환경기준은 다음과 같음 「환경정책기본법 시행령」 [별표 1] 환경기준 1. 대기 ¦ 항목 ¦ 기준 ¦ ¦ --- ¦ --- ¦ ¦ 아황산가스(SO2) ¦ 연간 평균치 0.02 ppm 이하 24 시간 평균치 0.05 ppm 이하 1 시간 평균치 0.15 ppm 이하 ¦ ¦ 일산화탄소(CO) ¦ 8 시간 평균치 9 ppm 이하 1 시간 평균치 25 ppm 이하 ¦ ¦ 이산화질소(NO2) ¦ 연간 평균치 0.03 ppm 이하 24 시간 평균치 0.06 ppm 이하 1 시간 평균치 0.10 ppm 이하 ¦ ¦ 미세먼지(PM-10) ¦ 연간 평균치 50 �g/m3 이하 24 시간 평균치 100 �g/m3 이하 ¦ ¦ 초미세먼지(PM-2.5) ¦ 연간 평균치 15 �g/m2 이하 24 시간 평균치 35 �g/m3 이하 ¦ ¦ 오존(O3) ¦ 8 시간 평균치 0.06 ppm 이하 1 시간 평균치 0.1 ppm 이하 ¦ ¦ 납(Pb) ¦ 연간 평균치 0.5 �g/m3 이하 ¦ ¦ 벤젠 ¦ 연간 평균치 5 �g/m3 이하 ¦ 비 고 1. 1 시간 평균치는 999 천분위수(千分��)의 값이 그 기준을 초과 해서는 안 되고, 8 시간 및 24 시간 평균치는 99 백분위수의 값이 그 기준을 초과 해서는 안 된다. 2. 미세먼지(PM-10)는 입자의 크기가 10 �m 이하인 먼지를 말한다. 3. 초미세먼지(PM-2.5)는 입자의 크기가 2.5 �m 이하인 먼지를 말한다. 124 기계설비 기술기준 매뉴얼 | {}
3af68911-cfc2-415c-9c2f-625aafcec552 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 「환경정책기본법 시행령」 [별표 1] 환경기준(계속) 2. 소음 (단위: Leq dB(A)) ¦ 지역 구분 ¦ 적용 대상지역 ¦ 기준 ¦ 기준 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 지역 구분 ¦ 적용 대상지역 ¦ 낮 (06 : 00 ~ 22 : 00) ¦ 밤 (22 : 00 ~ 06 : 00) ¦ ¦ 일반 지역 ¦ "가"지역 ¦ 50 ¦ 40 ¦ ¦ 일반 지역 ¦ "나"지역 ¦ 55 ¦ 45 ¦ ¦ 일반 지역 ¦ "다"지역 ¦ 65 ¦ 55 ¦ ¦ 일반 지역 ¦ "라"지역 ¦ 70 ¦ 65 ¦ ¦ 도로변 지역 ¦ "가" 및 "나"지역 ¦ 65 ¦ 55 ¦ ¦ 도로변 지역 ¦ "다"지역 ¦ 70 ¦ 60 ¦ ¦ 도로변 지역 ¦ "라"지역 ¦ 75 ¦ 70 ¦ 비 고 1. 지역구분별 적용 대상지역의 구분은 다음과 같다. 가. "가"지역 1) 「국토의 계획 및 이용에 관한 법률」 제 36 조제 1 항제 1 호라목에 따른 녹지지역 2) 「국토의 계획 및 이용에 관한 법률」 제 36 조제 1 항제 2 호가목에 따른 보전관리지역 3) 「국토의 계획 및 이용에 관한 법률」 제 36 조제 1 항제 3 호 및 제 4 호에 따른 농림지역 및 자연환경보전지역 4) 「국토의 계획 및 이용에 관한 법률 시행령」 제 30 조제 1 호가목에 따른 전용주거지역 5) 「의료법」 제 3 조제 2 항제 3 호마목에 따른 종합병원의 부지경계로부터 50 m 이내의 지역 6) 「초·중등교육법」 제 2 조 및 「고등교육법」 제 2 조에 따른 학교의 부지경계로부터 50 m 이내의 지역 7) 「도서관법」 제 2 조제 4 호에 따른 공공도서관의 부지경계로부터 50 m 이내의 지역 나. "나"지역 1) 「국토의 계획 및 이용에 관한 법률」 제 36 조제 1 항제 2 호나목에 따른 생산관리지역 2) 「국토의 계획 및 이용에 관한 법률 시행령」 제 30 조제 1 호나목 및 다목에 따른 일반주거지역 및 준주거지역 다. "다"지역 1) 「국토의 계획 및 이용에 관한 법률」 제 36 조제 1 항제 1 호나목에 따른 상업지역 및 같은 항 제 2 호다목에 따른 계획관리지역 2) 「국토의 계획 및 이용에 관한 법률 시행령」 제 30 조제 3 호다목에 따른 준공업지역 "라"지역 라. 「국토의 계획 및 이용에 관한 법률 시행령」 제 30 조제 3 호가목 및 나목에 따른 전용공업지역 및 일반공업지역 2. "도로"란 자동차(2 륜자동차는 제외한다)가 한 줄로 안전하고 원활하게 주행하는 데에 필요한 일정 폭의 차선이 2 개 이상 있는 도로를 말한다. 3. 이 소음환경기준은 항공기소음, 철도소음 및 건설작업 소음에는 적용하지 않는다. 2. 용어 V 내용 없음 3.4 축열(빙축열, 수축열) 빙축열 시스템의 설치는 KCS 31 25 10 의 2.13 에 따른다. 해 설 1. 본문 해설 및 관련 법규 V KCS 31 25 10 의 2.12(수축열), 2.13(빙축열)은 다음과 같음 ![image](/image/placeholder) 2.12 수축열 시스템 국토교통부 125 기계설비 기술기준 해설 (별표 01 | {}
033571d2-4ae5-4dfb-9b50-8bdfe25e5f9e | 국내_기계설비_기술기준_매뉴얼_최종본 | 2.12.1 일반사항 (1) 건물의 냉난방을 공급할 목적으로 냉동기 및 보일러 또는 열펌프 등 열원기기와 축열탱크를 갖추고 축열 매체로는 물을 사용하는 시스템에 적용한다. 기기의 구성은 특기에 따른다. (2) 열교환기를 사용하여 축열탱크 배관회로와 공조배관 회로를 분리하거나, 또는 축열탱크 배관회로와 공조 배관 회로를 직접 연결하는 경우도 있으며, 열반송 매체로는 물을 사용한다. (3) 고압가스 안전관리법의 적용을 받는 것은 동법 및 고압가스 안전관리법 시행규칙에 나열된 관계 기준에 정하는 바에 따른다. (4) 보일러는 열사용기자재의 검사 및 검사면제에 관한 기준에 따른다. 2.12.2 건축구조물을 이용한 개방형 콘크리트제 축열탱크 축열탱크를 건물의 최하부 기초 슬라브 내에 설치하는 경우에는 지하수위를 확인하여 지하수위가 축열탱 (1) 크보다 높을 경우에는 지하수 침입방지를 위한 적절한 대책을 실시한다. (2) 축열탱크 상부바닥은 방수를 확실히 하고, 외부로부터 물이 스며들지 않도록 한다. (3) 온수축열을 겸하는 축열탱크는 내열성을 가지는 재료로 시공한다. (4) 축열탱크의 최소 단열두께는 KCS 31 20 05(2.3.3(2))의 기준에 따른다. 이 기준 별표 10 보온설비, 2.2.1 보냉용, 표 1 공기조화기 기준에 따름 (5) 축열탱크는 내부단열을 원칙으로 하며, 수압에 충분히 견딜 수 있는 강도의 단열재를 사용한다. (6) 축열탱크는 단열시공 이후에 방수작업을 하고, 72 시간 이상 담수시험을 실시하여 누수가 없어야 한다. (7) 축열탱크를 통과 하거나, 축열탱크 내에 설치되는 모든 배관은 반드시 콘크리트와 절연하여 지지한다. (8) 온도성층화를 위하여 축열탱크 수온보다 높은 온도의 물은 상부로 공급되고 축열탱크 수온보다 낮은 물 은 하부로 공급되어야 한다. 이를 위해서 필요한 경우에는 배관회로의 방향을 바꿀 수 있는 자동밸브와 제어장치를 갖추어야 한다. (9) 축열탱크의 용량은 이용효율을 고려한 용량으로 설치한다. (10) 펌프는 캐비테이션이 생기지 않도록 축열탱크로부터 물을 인출하는 펌프의 흡입측에는 자동제어밸브를 설치하지 않는다. 또한 너무 정밀한 스트레이너도 설치하지 않도록 한다. (11) 축열탱크의 수위보다 배관의 최고높이가 10 m 이상 높을 때에는 펌프가 정지 시 배관의 물이 축열탱크 로 유입되지 않도록 낙수 방지용 자동 차단밸브를 설치한다. (12) 축열탱크는 유지보수를 고려하여 적절한 용량으로 구획하고 각 탱크마다 점검 및 청소를 위한 지름 600 mm 이상으로서 단열성능을 갖춘 맨홀, 내식성 재료로 하고, 수심이 깊은 경우에는 등받이를 부착한 사다 리, 배수피트 등을 설치하고 배수관, 오버플로관, 통기관, 보급수관 등을 갖추어야 한다. 2.12.3 독립구조로 설치되는 개방형 축열탱크 (1) 탱크 본체의 재료는 플라스틱제 (FRP, PE 등) 또는 강판제로 하며, 내부 및 외부의 응력에 충분히 견고한 구조로 제작한다. (2) 축열탱크의 제작, 시공에 있어서 앞의 2.12.2(3) 내지 (11)의 사항은 동일하게 적용한다. (3) 외부에서 단열을 하는 경우에는 탱크본체와 바닥사이에 열이 전달되지 않도록 강도가 높은 단열재를 사 용하여 열손실을 차단한다. (4) 축열탱크는 유지보수를 고려하여 적절한 용량으로 구획하고, 각 탱크마다 점검을 위한 지름 600 mm 이상 으로서 단열성능을 갖춘 맨홀을 갖추어야 한다. (5) 축열탱크가 공장제작품인 경우, 현장설치 후의 담수 확인시험은 2 시간 이상으로 한다. 2.12.4 압력용기 구조의 밀폐형 강판제 축열탱크 (1) 축열탱크의 설계 · 제작기준은 KS B 6321 압력용기의 구조에 따른다. (2) 용접부의 부식방지를 위해 탱크내부 전체를 방청라이닝 시공한다. (3) 축열탱크를 공장에서 제작한 후 분할하여 반입하며, 현장에서 용접하여 최종 조립하는 경우에는 라이닝 시공은 현장에서 모든 용접작업이 끝난 후에 한다. 또 현장 조립 후에는 반드시 설계압력의 1.5 배 이상의 압력으로 30 분 이상 수압시험을 실시한다. 축열탱크의 제작, 시공에 있어서 앞의 (11)과 ~ (5)의 사항은 동일하게 적용한다. (4) 2.12.2(3) ~ 2.12.3(3) 2.13 빙축열 시스템 2.13.1 일반사항 (1) 건물의 냉방용 열원을 공급할 목적으로 냉동기, 축열탱크, 판형 열교환기, 브라인펌프, 자동제어밸브, 무인 운전용 제어시스템 등을 갖추고 축열매체는 얼음, 또는 PCM(잠열축열재) 등을, 열반송 매체로는 냉수, 브 126 기계설비 기술기준 매뉴얼 | {}
a3a3a7de-1dc7-4f60-88d6-dea407dc4fbc | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 라인, 슬러리(물과 얼음의 혼합물) 등을 사용하는 시스템에 적용한다. (2) 빙축열 냉방시스템의 설계 및 시공에 관한 사항은 SPS-KARSE B 0027-0189 빙축열시스템에 따른다. 해당 자료는 다음의 사이트에서 구할 수 있음 https://www.kare.onkr/hew_htm/subbage_05_05_05jpppt 2.13.2 냉동기 (1) 저온냉동기는 심야시간 제빙운전 시 축열탱크의 제빙 종료온도 이하에서 1 시간 이상 연속운전이 가능해 야 하며, 주간에는 높은 온도로 상온냉방운전이 가능하도록 2 중 증발온도 설정 기능을 갖추어야 한다 (2) 냉동기는 심야 10 시간 동안에 축열탱크를 충분히 제빙할 수 있는 용량으로 선정하며, 조기방열 등 특수한 경우에는 해당시간 안에 축열탱크의 제빙을 완료할 수 있어야 한다. (3) 냉동기의 제어패널은 마이크로프로세서에 의한 제어를 기본원칙으로 하며, 냉동기에 본체에 부착된 패널 에서 모든 조작이 가능해야 한다. (4) 고압가스 안전관리법의 적용을 받는 것은 동법 및 고압가스 안전관리법 시행규칙에 나열된 관계 기준에 정하는 바에 따른다. 2.13.3 축열탱크 (1) 축열탱크는 해빙이 진행되어도 일정수준 이하의 브라인 출구온도를 유지하도록 반드시 해빙효율을 고려 한 용량으로 설치한다. (2) 축열탱크는 축열량을 확인할 수 있는 축열량 센서 또는 수위 센서를 부착하며, 유량과 온도를 계측하여 축 열량 및 방열량을 연산하는 경우에는 적절한 위치에 유량측정 센서를 설치하여 이로부터 연속적으로 신호 를 받아 계산한다. 표 2.13-1 축열탱크 센서 ¦ 구분 ¦ 정밀도 ¦ 형식 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 냉온수 온도센서 ¦ +/- 0.1°C ¦ 열전대, 측온저항체 ¦ ¦ 브라인 온도센서 ¦ +/- 0.1 °C ¦ 열전대, 측온저항체 ¦ ¦ 유량센서 ¦ +/- 2% ¦ 임펠러식, 마그네텍, 초음파식 ¦ ¦ 수위센서 ¦ +/- 1% ¦ 정전용량식, 압력식, 전극식 ¦ (3) 축열탱크의 최소 단열두께는 다음 표 2.13-2 에 따른다. 표 2.13-2 축열탱크 단열두께 ¦ 단열재의 종류 ¦ 0 °C 부근의 물과 접촉 ¦ 0 °C 보다 낮은 온도의 브라인과 접촉 ¦ 비 고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 유리솜 보온판 40K ¦ 75 ¦ 100 ¦ ¦ ¦ 발포 폴리스틸렌 보온판 ¦ 75 ¦ 100 ¦ ¦ ¦ 경질 우레탄 폼 보온판 ¦ 60 ¦ 75 ¦ ¦ (4) 축열탱크는 개방형 콘크리트제, 개방형 플라스틱제 (FRP 또는 PE) 탱크, 개방형 강판제 탱크, 압력용기 구 조의 밀폐형 강판제 탱크 등을 사용하며 그 구조 및 제작, 설치에 있어서는 2.13 수축열 시스템의 2.12.2 ~ 2.12.4 의 기준에 따른다. (5) 개방형 콘크리트제의 캡슐형 축열탱크는 건물의 구조체를 직접 이용하지 않는다. 1 차 방수층이 파괴되어 도 저온의 브라인이 건물구조체와 직접 접촉되지 않는 구조로 한다. (6) 캡슐형 축열탱크의 유량분배 디퓨저는 유동압력에 대한 강도를 가지면서 부식을 방지하도록 스테인리스 관 또는 동등이상의 내식성 금속제로 한다. 또한 캡슐에 의해 유출입구가 막히지 않도록 디퓨저 주위에는 적합한 유동공간을 확보한다. (7) 압력용기 구조의 밀폐형 강판제 탱크를 이용하는 캡슐형 축열탱크는 제빙시 팽창하는 브라인을 받아줄 수 있는 용량의 인벤토리 탱크를 기계실 내의 축열탱크 가까이에 설치하며, 인벤토리 탱크에서 자연압에 의해 팽창수가 유동되지 않을 경우에는 팽창수의 유동을 위한 펌프와 자동밸브 등을 적절히 구비한다. (8) 빙박리형, 슬러리형의 축열탱크는 쌓인 얼음이 수면 밖으로 나오지 않도록 제빙기의 대수, 배치, 축열탱크 기계설비 기술기준 해설 (별표 언 국토교통부 127 | {}
da73601a-c7ec-43a5-aa5e-646090885b07 | 국내_기계설비_기술기준_매뉴얼_최종본 | 의 형상 등을 적절히 분산 배치한다. (9) PCM 을 캡슐에 내장한 축열탱크는 캡슐형 축열탱크와 동일한 기준을 적용한다. 2.13.4 펌프 (1) 제빙 및 해빙 운전 시 브라인 펌프의 설계유량이 다른 경우에는 제빙용 펌프와 해빙용 펌프를 별도로 설 치하거나, 주야간 겸용 펌프에 인버터에 의한 회전수 제어를 적용한다. (2) 브라인을 헤더방식으로 공급하면서 부하에 따라 운전대수를 조절하는 경우에는 냉동기, 열교환기, 축열탱 크 등에 적정한 유량배분이 이루어지도록 자동 밸브등을 설치하여 적절한 밸런싱이 유지되도록 한다. 2.13.5 열교환기 (1) 열교환기를 사용하여 축열탱크 배관회로와 공조배관회로를 분리하는 것이 일반적이며, 열교환기는 주로 판형을 사용하고 2.10.3 에 따른다. 2.10.3 판형 열교환기 (1) 재료 및 구조 개스킷식 판형 열교환기는 STS 304 또는 STS 316 등의 재료를 파형으로 프레스 성형한 전열판(판의 주 위를 둘러싸고 있는 내열성 합성고무 개스킷을 포함한다.)을 여러 장을 조립한 전열판 조립체와 이를 압축하여 밀봉하고 지지하는 프레임 본체로 구성된다. 용접식 판형열교환기는 개스킷이 없는 구조로 전열판 조립체를 스테인리스 재질의 프레임과 일체화시켜 용접 또는 브레이징하여 제작한 것으로 제 조회사의 규격에 따른다. (2) 증기 대 물 열교환기에는 증기관, 응축수관, 온수공급관, 온수환수관 등의 접속구를 설치한다. 이외 사 항은 특기에 따른다. (3) 물 대 물 열교환기에는 고온수 측 및 저온수 측 공급 및 환수관의 접속구를 설치한다. 이외 사항은 특 기에 따른다. (2) 열교환기를 두지 않고 축열탱크로부터 냉수 또는 슬러리, 브라인 등을 부하측 공조배관 회로에 직접 연결 하는 경우에 대해서는 설계시방 및 특기에 따른다. 2.13.6 자동제어밸브 (1) 축열탱크용 온도제어밸브는 정밀한 유량제어를 위해 글로브밸브를 사용하며 3 방밸브 또는 2 방밸브를 2 조 연동하여 사용하고 수동조작기능이 있는 것으로 한다. (2) 야간에 축열운전 시 열교환기측으로 브라인이 흘러 동파되는 것을 방지하기 위한 열교환기 바이패스용 3 방밸브를 사용하는 경우에는 열교환기 입구에 추가로 차단 밸브를 설치한다. 2.13.7 제어시스템 무인운전 제어패널에는 각종 운전상황표시 및 계기가 부착되어 운전 시 이상 유무 및 냉동기의 운전상태를 판독확인이 가능하며, 제어값을 설정할 수 있고 원격제어(정지, 기동, 온도제어 등)가 되는 빌딩제어시스템과 연결한다. 2.13.8 배관 및 보온 (1) 브라인배관은 아연도금강관(백관)을 사용하지 않는다. (2) 브라인 배관의 보온기준은 다음과 같다. (관내온도 -10°C, 주위온도 30°C, 상대습도 90% 기준 ) 표 2.13-3 브라인 배관 보온 두께, mm ¦ 최소 보온두께 ¦ DN 15~80 ¦ DN 100 이상 ¦ 비고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 유리솜 보온통 ¦ 75 ¦ 100 ¦ 비중 30 K 이상 ¦ ¦ 발포 폴리에틸렌 보온통 ¦ 50 ¦ 75 ¦ ¦ ¦ 고무 발포 보온재 ¦ 38 ¦ 50 ¦ ¦ (3) 판형 열교환기는 하부를 제외하고는 프레임 및 플레이트 전체를 고무발포보온재 또는 발포폴리에틸렌 25 mm 로 감싸고 밀봉한다. 외부는 우레탄 폼 충진 샌드위치 패널 50 mm 이상으로 케이싱을 제작 · 시공하고 공기가 들어가지 않도록 모든 틈새는 실리콘으로 코킹 처리한다. 2. 용어 128 기계설비 기술기준 매뉴얼 | {}
b07601d4-aa00-4057-99ef-edf945373e30 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 내용 없음 3.5 보일러 (1) 보일러는 도면에 따라 정해진 위치 및 네 귀에 규격틀을 설치하고, 수평, 수직, 적정기울기 등은 수준기, 물수평보기, 수평실줄띠우기 등의 기구를 사용하여 위치와 중심내기 등을 한다. (2) 새들 및 잭 등으로 받침대에 보일러 본체를 가설치하고, 정확한 설치 치수를 측정한 후에 마감설 치를 한다. (3) 기타 필요한 사항은 KGS GC208(주거용 가스보일러의 설치 , 검사 기준), GC209(상업 * 산업용 가스보일러의 설치 * 검사 기준)에 따른다. (4) 개별 보일러를 설치하는 건축물의 경우에는 소방청장이 정하여 고시하는 기준에 따라 일산화탄 소 경보기를 설치해야 한다. 3.5.1 연도 및 배기통 연도의 이음에는 내열성이 있는 재질을 사용하여 기밀을 유지한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항, 2 항) 추가 설명 없음 V (3 항) 다음의 최신 기준을 사용해야 함 : KGS GC208(주거용 가스보일러의 설치 · 검사 기준) ; 2020. 9. 14 심의·의결 : GC209(상업 · 산업용 가스보일러의 설치 · 검사 기준) ; 2018. 7. 20 심의·의결 V (4 항) 가스누설경보기의 화재안전기준(NFSC 206) 제 5 조에 따라 설치함 V (3.5.1) 연도 및 배기통을 통한 배기가스 누출 가능성을 제거해야 함 2. 용어 V 내용 없음 3.6 열교환기 (1) 압력용기에 해당하는 열교환기는 「안전검사 고시」 및 「열사용기자재의 검사 및 검사면제에 관한 기준」에 따른다. (2) 운전중량을 지지할 수 있는 기초로 하고, 지진 등의 충격에 견딜 수 있도록 받침대를 수평으로 설 치하며, 열교환기와 강제 받침대는 볼트 등으로 고정한다. 해 설 기계설비 기술기준 해설 (별표 01 국토교통부 129 | {}
52e76d1f-a799-4a56-9788-963321890364 | 국내_기계설비_기술기준_매뉴얼_최종본 | 1. 본문 해설 및 관련 법규 V (1 항) 「열사용기자재의 검사 및 검사면제에 관한 기준」은 산업통상자원부 고시 제 2021-133 호를 참조함 안전검사 고시 [별표 4] 압력용기의 검사기준(제 10 조 관련) ¦ 번호 ¦ 구 분 ¦ 내 용 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ 외관상태 및 두께 ¦ 가. 용기본체, 노즐, 맨홀, 부속물, 지지대 및 기초볼트 등은 손상, 변형 또는 깨짐이 없 을 것 나. 용접이음부, 노즐부 및 맨홀에는 누설의 흔적이 없을 것 다. 동체 및 경판 등 압력을 받는 부분의 측정두께는 필요두께(부식여유 제외) 이상일 것 ¦ ¦ 2 ¦ 내면 ¦ 용기의 내면은 심한 손상, 변형 또는 깨짐이 없고 부식상태가 양호하여야 하며, 필요 시 용기를 개방하여 이를 확인할 수 있음 ¦ ¦ 3 ¦ 용접이음부 ¦ 가. 용접이음부는 육안검사 시 균열 또는 이상이 없어야 하며, 육안검사로 판정이 곤 란한 경우에는 액체 침투탐상검사 또는 자분탐상 검사를 실시할 것 나. 가목에 따라 검사결과 이상발견 부위는 방사선투과 검사 또는 초음파 탐상검사를 실시할 것 ¦ ¦ 4 ¦ 덮개판 및 플랜지 ¦ 가. 덮개판 및 플랜지에 체결되어 있는 가스켓은 손상 또는 탈락이 없을 것 나. 볼트 및 너트는 풀림이나 나사의 파손이 없고 체결상태가 적정할 것 ¦ ¦ 5 ¦ 지지대 및 기초볼트 ¦ 가. 지지대는 외력에 의한 손상 및 좌굴현상이 없을 것 나. 기초부분에는 부등침하가 없어야 하며, 기초볼트는 풀림이 없을 것 ¦ ¦ 6 ¦ 압력 방출장치 ¦ 가. 압력방출장치는 법 제 34 조에 따른 안전인증품으로 현저한 손상, 부식, 마모가 없 고, 유체의 누출이 없을 것 나. 설정압력은 설계압력 또는 최대허용 사용압력을 초과 해서는 아니 되며, 작동압력 은 설정압력치의 ±5% 이내이고, 봉인상태가 양호할 것 다. 표시판에 설정압력 등의 식별이 가능해야 하며 부착이 견고할 것 ¦ ¦ 7 ¦ 압력계 ¦ 압력계는 현저한 손상, 마모 및 누설이 없어야 하며, 정확도는 ±5 퍼센트 이내일 것 ¦ ¦ 8 ¦ 온도계 ¦ 온도계의 면 유리는 손상이 없어야 하며, 지시바늘은 휘거나 떨림이 없을 것 ¦ ¦ 9 ¦ 응축수 ¦ 공기저장탱크는 내부에 응축수가 고이지 않도록 드레인 밸브를 조작하여 응축수를 방출해야 할 것 ¦ ¦ 10 ¦ 접지편 ¦ 가. 접지편은 압력용기의 받침대 하단에 최소한 1 개 이상 견고히 접속되어있을 것(을 종용기는 제외한다) 나. 접지편은 부식이 되지 않고 전기가 잘 통하도록 관리할 것 ¦ ¦ 11 ¦ 이름판 ¦ 압력용기에는 제조자, 설계압력 또는 최대허용사용압력, 설계온도, 제조연도, 비파괴 시험, 적용규격 등이 표시된 이름판이 붙어 있을 것 ¦ V (2 항) 이 기준 [별표 12]의 관련 내용을 참조하여 시공함 2. 용어 V 내용 없음 ---○--- --- 3.7 팽창탱크 (1) 압력용기에 해당하는 것은 취급, 검사 및 청소에 지장이 없는 위치에 설치한다. (2) 기초는 운전중량에 대하여 변형되지 않아야 하며, 충격에 견딜 수 있는 견고한 콘크리트제 또는 철제베드 위에 안전하고 견고하게 설치한다. 130 기계설비 기술기준 매뉴얼 | {}
a8bb6174-fb21-475a-bf11-2969bb552a0b | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 해 설 1. 본문 해설 및 관련 법규 (1 항) 이 기준 [별표 15] 2.1 (1)에 따라 탱크 주변 유지관리공간을 확보해야 하며, 아래와 같이 검 사 대상에 해당하는 경우 관련 검사 기준을 고려하여 설치해야 함 밀폐형 팽창탱크가 산업용(생산공정 등에 설치·사용되는 것)으로 사용되는 경우 사용자가 안전검사를 받아 야 하지만, 빌딩 등 건물의 난방 및 급수용으로 설치되어 비산업용으로 사용하는 경우에는 안전검사 대상이 아님 출처 : 안전보건공단 KOSHA 전자민원센터 답변 발췌 (2 항) 이 기준 [별표 12]의 관련 내용을 참조하여 시공함 2. 용어 V 내용 없음 3.8 펌프 (1) 기초는 윗면 주위의 배수 홈에 배수구를 설치하고 DN 32 이상의 배관으로 배수관에 간접 배수한 다. (2) 펌프는 기초 위에 수평으로 설치하고, 축심을 정확하게 조정한 다음 기초 볼트 구멍에는 모르타 르를 채워 충분히 굳은 다음에 균등하게 조여 고정시킨다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 추가 설명 없음 V (2 항) 이 기준 [별표 12]의 관련 내용을 참조하여 시공하며, 라인형 펌프는 기초를 설치하지 않을 수 있음 2. 용어 V 내용 없음 기계설비 기술기준 해설 (별표 01 국토교통부 131 | {}
806c05ff-0712-47e9-a79b-687c3e4d39f2 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3.9 지열원 열펌프 시스템 (1) 지열원 열펌프 ① 지열원 열펌프는 운전 시 소음, 진동이 적고, 소정의 성능을 가지는 것으로 한다. ② 지열원 열펌프 중 「고압가스안전관리법」의 적용을 받는 것은 해당 관련 법률이 정하는 바에 따 르며 한국가스안전공사의 각종 시험에 합격한 것으로 한다. ③ 지열원 열펌프 공사는 KCS 31 50 15 05 에 따른다. (2) 보어홀 ① 그라우트가 혼합물인 경우 설계 시 혼합비율을 준수 시공해야 한다. ② 보어홀 상단부의 붕괴를 방지하기 위해 지면에서 지하 암반층 출현 지점까지 케이싱을 삽입한 다. ③ 천공완료 후 케이싱을 제거하지 않을 경우, 지표수가 유입되지 않도록 조치해야 한다. (3) 지중열교환기 ① 지중 매설용 배관은 산, 알카리, 염분 등에 부식되지 않고 세균류가 번식되지 않아야 한다. ② 지중 매설용 배관은 내벽이 매끈하여 유체의 마찰손실이 최소화되는 것을 사용한다. (4) 자동제어 ① 지열원 열펌프 시스템의 자동제어는 자동 및 수동운전이 가능해야 하며 열펌프가 무인 운전이 될 수 있도록 자기진단기능과 이상 징후 시 알람기능 등을 포함하고 있어야 한다. ② 중앙제어장치는 건물관리가 쉬운 방재실 또는 중앙 관리실에 설치한다. (5) 기타 ① 배관 내부에 남아있을 수 있는 이물질 등을 제거하기 위하여 깨끗한 물을 고속으로 순환시켜 배 관 내부를 세척한다. ② 시운전을 완료한 후 반드시 스트레이너, 필터 등 배관계통에 대한 청소를 실시한다. ③ 그 외 사항은 「신 , 재생에너지 설비의 지원 등에 관한 규정」에 따른다. 해 설 1. 본문 해설 및 관련 법규 V (1 항 1 호) 추가 설명 없음 V (1 항 2 호) 액화석유가스 또는 도시가스를 연료로 하는 가스엔진으로 증기압축식 냉동사이클의 압 축기를 구동하는 고압가스용 가스히트펌프식 냉난방기로 「고압가스용 가스히트펌프 제조의 시 설·기술·검사기준」에 따라 제조되고 검사를 받은 제품을 말함 V (1 항 3 호) 국가건설기준센터(https://www.krs.re.or/Home/ince) -> [설비코드] -> [표준시방서] KCS 31 50 15 05(지열원열펌프설비공사) 내용에 따름 V (2 항 1 호) 열전도를 높이기 위해 모래를 혼합하여 사용하는 경우는 모래의 무게로 인해 배관이 압 착 변형될 수 있으므로 주의 해야 함 바닷가 근처 매립지 또는 공항 등 염분을 포함한 지반에는 해수용 그라우트를 사용할 수 있음 V (2 항 2 호) 개방형의 경우 케이싱을 암반층 출현 지점까지 삽입하지 않을 경우 토사의 유입으로 심 정펌프, 열교환기 등에 손상을 주므로 주의 해야 함 V (2 항 3 호) 개방형은 케이싱을 제거해서는 안됨 V (3 항 1 호, 2 호) 추가 설명 없음 132 기계설비 기술기준 매뉴얼 | {}
d5125d8e-a61b-4578-8d2f-04c5b1bbfc79 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 V (4 항 1 호, 2 호) 추가 설명 없음 V (5 항 1 호) 이물질 50 �m 이상을 처리할 수 있는 이물질 분리기(스트레이너, Strainer) 설치를 권장 함 V (5 항 2 호 ~ 3 호) 추가 설명 없음 2. 용어 V 내용 없음 ---○---- 3.10 태양열 시스템 (1) 집열기 설치 ① 바람, 적설하중, 구조하중, 건축물의 방수 등에 문제가 없도록 설치한다. ② 집열기 지지대 제작 시 형강류, 기초지지대에 포함된 철판부위, 체결용 볼트, 너트, 와셔(볼트캡 포함)는 용융아연도금 처리 또는 동등 이상의 녹방지 처리를 하며 용접부위는 방식처리한다. ③ 유지보수를 위한 공간을 두거나 안전을 고려한 발판과 안전난간을 설치한다. (2) 축열탱크 설치 ① 축열탱크의 내부 상태를 확인할 수 있는 온도계, 압력계 및 안전밸브를 설치한다. ② 축열탱크 최하단에는 배수와 청소가 가능하도록 적정규격의 배수밸브 DN 25 이상을 설치한다. ③ 축열탱크를 옥외에 설치하는 경우에는 콘크리트 기초 위에 조립식 패널 등을 설치하여 빗물 침 투 등을 방지할 수 있도록 하고, 공급수 배관에는 동파방지를 위하여 보온조치를 한다. ④ 축열탱크의 보온은 글라스울 100 mm 또는 우레탄폼 100 mm 이상의 조건에 해당하는 소재 및 규격으로 하며 외부케이싱은 흡습 및 부식 방지 소재로 한다. (3) 팽창탱크 및 펌프 설치 ① 팽창탱크는 구분된 배관계통마다 펌프 흡입구 측에 적정용량을 설치한다. ② 팽창배관에 밸브를 설치할 경우, 밸브의 '열림 또는 '닫힘'을 표시하고, 운전 시에는 '열림 '으로 고정되어야 한다. ③ 모든 펌프는 고효율인증제품을 우선 사용하며, 해당 용량에 인증제품이 없는 경우에는 KS 및 동 등 이상의 제품을 사용한다. (4) 집열기 가대 설치 ① 집열기 설치가대는 풍압이나 설치하중에 견딜 수 있어야 하며 뒤틀림이나 흔들림이 없도록 지면 에 고정한다. ② 집열기 설치가대는 집열기 하단부가 설치면으로부터 최소 150 mm 이상 높이를 유지할 수 있도 록 하며 낙수나 눈에 잠기지 않는 구조체로 한다. ③ 설치가대 구조물은 형강을 사용하여 용접 또는 볼트로 조립하며 부식에 대한 침식이 없도록 페 인팅 또는 아연도금 한다. ④ 집열기 설치 받침대에는 집열기의 점검, 보수가 쉽도록 사람이 다닐 수 있는 통로를 상단부에 설 치한다. ⑤ 집열기 및 축열탱크의 기초는 각각의 운전중량을 견딜 수 있는 강도로 설치한다. (5) 기타 ① 시스템 내에 과열방지 및 동파방지 대책을 마련한다. ② 정전 및 고장 시에도 열매체가 누출되지 않도록 한다. 기계설비 기술기준 해설 (별표 언 국토교통부 133 | {}
a2491c21-4636-4fc6-aaa1-1a941447b74d | 국내_기계설비_기술기준_매뉴얼_최종본 | 해 설 1. 본문 해설 및 관련 법규 V (1 항 ~ 2 항) 추가 설명 없음 V (3 항 1 호 ~ 2 호) 추가 설명 없음 V (3 항 3 호) 이 기준 [별표 1] 3.8 참조 V (4 항) 추가 설명 없음 V (5 항 1 호) 과열방지에는 과열방지밸브(SPV; scald protection valve), 동파방지에는 동결방지밸브 (FPV; freeze protection valve)를 사용한다. 다만. 동파방지 대책 시 열선으로 할 경우, 이 기준 [별 표 10] 2.5 참조함 V (5 항 2 호) 추가 설명 없음 2. 용어 V 내용 없음 3.11 연료전지 (1) 건축물 내부로 배기가스 유입 방지 조치를 한다. (2) 급수, 온수 배관은 기밀성이 손상되지 않는 구조이어야 하며, 씰 부위는 열화를 충분히 견딜 수 있 는 구조로 한다. (3) 연료전지 주위에 급수 유량에 해당하는 배수능력을 갖춘 배수구가 있는지 확인하며, 배수배관은 고온의 물이 흐를 수 있으므로 내열성 재료를 사용하고 물이 원활히 배수되도록 한다. (4) 기타 필요한 사항은 KGS FU551(도시가스 사용시설의 시설 、 기술 . 검사 기준)에 따른다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 연료전지 운전 시 배기가스 중 대기 오염물질인 미연탄화수소(UHC), CO, 질소산화물(NOx) 등을 발생시킬 가능성이 있으므로 배기가스가 건축물 내부로 유입이 되지 않도록 해야 함 V (2 항, 4 항) 추가 설명 없음 V (3 항) 연료전지의 반응 후 생성되는 물의 열을 회수하지 않고 배수(고온)하는 경우를 고려해야 함 2. 용어 V 내용 없음 134 기계설비 기술기준 매뉴얼 | {}
2f217cdf-8afe-48a9-9439-44598a66388c | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 3.12 패키지 에어컨 (1) 실외기 ① 실외기는 KS C 9306 에 따른 제품을 사용하고, 설치장소 주변 인접실 또는 인접건물에 미치는 소음, 진동의 영향은「환경정책기본법」 시행령」 별표 1 제 2 호에 따른 환경기준을 준수할 수 있도 록 한다. ② 실외기의 열과 전자파가 다른 전기제품이나 통신선, 전원선 등의 주변기기에 영향을 미치지 않 도록 이격하여 설치한다. ③ 전자파 발생 장비나 고온의 배기열 또는 부식성이 강한 배기가스가 발생하는 배기구 등과 이격 하여 설치한다. ④ 제조사에서 규정하는 배관길이 및 허용 높이 내에서 설치한다. ⑤ 실외기를 집단으로 설치할 경우, 상호 간섭에 의한 영향이 없도록 제작업체의 지침에 따라 적정 거리를 유지하여 설치한다. ⑥ 아래의 장소에 실외기를 설치하면 안 된다. 가. 가연성 가스가 발생하는 장소 나. 기름(기계류 포함)이 많은 장소 다. 산성용액이나 유황가스가 많은 장소 라. 설치환경이 특수하여 부적합한 장소 ⑦ 실외기 과열 시 자동으로 전원이 차단되도록 실외기 전용의 차단 개폐기를 설치한다. ⑧ 실외기를 옥외에 설치할 경우에는 보행자의 안전에 유의 한다. 해 설 1. 본문 해설 및 관련 법규 V (1 호) KS C 9306, 「환경정책기본법 시행령」 별표 1 제 2 호에 따른 환경기준은 다음과 같음 국토교통부 135 기계설비 기술기준 해설 (별표 01 | {}
296c43ac-db74-4394-939c-5dffe21337af | 국내_기계설비_기술기준_매뉴얼_최종본 | KS C 9306 에어컨디셔너 - 이 표준은 실내의 쾌적한 공기 조화를 목적으로 하여 냉방(난방 · 제습을 겸하는 구조의 것을 포함한다.) 및 공기의 순환과 정화를 하는 에어컨디셔너(이하 에어컨이라 한다.) 중, 일체형인 것(압축기, 송풍기 열교환기 등을 하나의 캐비닛에 내장한 것.) 또는 분리형인 것(압축기, 송풍기, 열교환기 등을 두 개의 캐비닛에 내장 한 것.)으로, 정격 냉방 소비 전력이 13 000 W 이하이고, 또한 정격 냉방 능력이 35 000 W 이하인 제품에 대 하여 규정한다. 「환경정책기본법 시행령」 [별표 1] 환경기준 2. 소음 (단위: Leq dB(A)) ¦ 지역 구분 ¦ 적용 대상지역 ¦ 기준 ¦ 기준 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 지역 구분 ¦ 적용 대상지역 ¦ 낮 (06 : 00 ~ 22 : 00) ¦ 밤 (22 : 00 ~ 06 : 00) ¦ ¦ 일반 지역 ¦ "가"지역 ¦ 50 ¦ 40 ¦ ¦ 일반 지역 ¦ "나"지역 ¦ 55 ¦ 45 ¦ ¦ 일반 지역 ¦ "다"지역 ¦ 65 ¦ 55 ¦ ¦ 일반 지역 ¦ "라"지역 ¦ 70 ¦ 65 ¦ ¦ 도로변 지역 ¦ "가" 및 "나"지역 ¦ 65 ¦ 55 ¦ ¦ 도로변 지역 ¦ "다"지역 ¦ 70 ¦ 60 ¦ ¦ 도로변 지역 ¦ "라"지역 ¦ 75 ¦ 70 ¦ 비 고 1. 지역구분별 적용 대상지역의 구분은 다음과 같다. 가. "가"지역 1) 「국토의 계획 및 이용에 관한 법률」 제 36 조제 1 항제 1 호라목에 따른 녹지지역 2) 「국토의 계획 및 이용에 관한 법률」 제 36 조제 1 항제 2 호가목에 따른 보전관리지역 3) 「국토의 계획 및 이용에 관한 법률」 제 36 조제 1 항제 3 호 및 제 4 호에 따른 농림지역 및 자연환경보전지역 4) 「국토의 계획 및 이용에 관한 법률 시행령」 제 30 조제 1 호가목에 따른 전용주거지역 5) 「의료법」 제 3 조제 2 항제 3 호마목에 따른 종합병원의 부지경계로부터 50m 이내의 지역 6) 「초·중등교육법」 제 2 조 및 「고등교육법」 제 2 조에 따른 학교의 부지경계로부터 50 m 이내의 지역 7) 「도서관법」 제 2 조제 4 호에 따른 공공도서관의 부지경계로부터 50 m 이내의 지역 나. "나"지역 1) 「국토의 계획 및 이용에 관한 법률」 제 36 조제 1 항제 2 호나목에 따른 생산관리지역 2) 「국토의 계획 및 이용에 관한 법률 시행령」 제 30 조제 1 호나목 및 다목에 따른 일반주거지역 및 준주거지역 다. "다"지역 1) 「국토의 계획 및 이용에 관한 법률」 제 36 조제 1 항제 1 호나목에 따른 상업지역 및 같은 항 제 2 호다목에 따른 계획관리지역 2) 「국토의 계획 및 이용에 관한 법률 시행령」 제 30 조제 3 호다목에 따른 준공업지역 라. "라"지역 「국토의 계획 및 이용에 관한 법률 시행령」 제 30 조제 3 호가목 및 나목에 따른 전용공업지역 및 일반공업지역 2. "도로"란 자동차(2 륜자동차는 제외한다)가 한 줄로 안전하고 원활하게 주행하는 데에 필요한 일정 폭의 차선이 2 개 이상 있는 도로를 말한다. 3. 이 소음환경기준은 항공기소음, 철도소음 및 건설작업 소음에는 적용하지 않는다. V (2 호, 3 호) 추가 설명 없음 V (4 호, 5 호) 배관길이 및 허용 높이와 집단으로 실외기를 설치할 경우의 상호 간섭에 의한 영향 등 은 제조사의 설치 기준에 따르도록 함 V (6 호) 가에서 라까지의 장소 외에 화재의 위험이 있는 장소의 설치는 피해야 함 V (7 호) 실외기 과열에 의한 화재 방지를 위해 실외기 전용의 차단 개폐기를 설치해야 함(단, 주거용 에 설치되는 실외기는 제외) V (8 호) 실외기 배기 기류가 보행자를 향하지 않도록 하기위해 설치하는 구조물 등이 보행자의 안 전을 방해하지 않도록 함 2. 용어 136 기계설비 기술기준 매뉴얼 | {}
4fc702e0-6ed0-4f2d-84d1-7adfe06108e2 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 패키지 에어컨 ¦ 이 기준에서 패키지 에어컨은 실외기와 실내기가 1 : N 으로 연결하어 건축물등에 설치하는 냉·난방 장치로 시스템 에어컨과 같은 의미로 사용함(해설서 주) ¦ 3.12 패키지 에어컨(계속) (2) 실내기 ① 흡입구, 토출구 부근에 공기의 흐름을 방해하는 장애물이 없고, 냉풍 또는 온풍이 실내 전체를 고 르게 퍼져나갈 수 있는 곳에 설치한다. ② 실내기가 설치되는 구조물이 실내기 무게를 충분히 지탱할 수 있는지 여부를 확인하고, 구조물 의 하중강도에 문제가 있을 경우에는 반드시 실내기 설치 전에 보강한다. ③ 실내기는 수평이 되도록 설치한다. ④ 덕트형 실내기의 설치에 따른 덕트공사는 [별표 9]에 따른다. ⑤ 실내기가 설치되는 위치 또는 공간은 필터 교체 및 점검 등 유지보수를 위한 공간을 반드시 확보 한다. 해 설 1. 본문 해설 및 관련 법규 V (1 호, 2 호, 4 호) 추가 설명 없음 V (3 호) 실내기 팬 가동시 소음 방지 등을 위해 실내기는 수평이 되도록 설치해야 함 V (5 호) 천장 설치형의 경우 이 기준 [별표 15] 2.4 (3)에 따라 필요한 점검구를 설치해야 함 2. 용어 내용 없음 --- 3.13 항온항습기 항온항습기 시공은 3.12 에 따른다. 해 설 1. 본문 해설 및 관련 법규 추가 설명 없음 2. 용어 내용 없음 기계설비 기술기준 해설 (별표 어) 국토교통부 137 | {}
68966197-7270-447f-b5c6-4247bc124be2 | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 2] 공기조화설비의 설계 및 시공 기준 1. 공기조화설비 일반사항 1.1 목적 이 기준은 건축물, 시설물 등에 필요한 온도, 습도, 청정도, 기류 등을 조절하여 쾌적한 환경 조건을 제공하기 위한 공기조화설비 설계 및 시공 방법 등 세부 기술기준을 정함을 목적으로 한다. 해 설 이 기준의 목적은 「기계설비법」 제 14 조(기계설비 기술기준)과 같은 법 영 제 2 조 및 [별표 1]에 근 거하여, 건축물이나 시설물에 필요한 공기조화설비의 설계 및 시공 시 기계설비의 안전과 성능을 확보하기 위하여 필요한 기술적 요건을 규정하기 위함 「기계설비법」 제 14 조(기계설비 기술기준) ① 국토교통부장관은 기계설비의 안전과 성능확보를 위하여 필요 한 기술기준(이하 "기술기준이라 한다)를 정하여 고시하여야 한다. 이를 변경하는 경우에도 또한 같다. 1.2 적용범위 이 기준은 건축물, 시설물 등에 공기조화설비를 설치하는 경우에 대하여 적용한다. 해 설 이 기준의 적용범위는 「기계설비법」 제 2 조제 1 호에 따른 건축물등에 같은 법 영 제 2 조에 따라 대 통령령으로 정한 공기조화설비를 설치하는 경우 및 그와 관련된 부속설비들을 포함함 「기계설비법」 제 2 조(정의) 1. "기계설비"란 건축물, 시설물 등(이하 "건축물등"이라 한다)에 설치된 기계 · 기 구 · 배관 및 그 밖에 건축물등의 성능을 유지하기 위한 설비로서 대통령령으로 정하는 설비를 말한다. 「기계설비법 시행령」 제 2 조(기계설비의 범위) 「기계설비법」(이하 "법"이라 한다) 제 2 조제 1 호에서 "대통령령 으로 정하는 설비"란 별표 1 의 설비를 말한다. 「기계설비법 시행령」 [별표 1] 기계설비의 범위 3. 공기조화 · 공기청정 · 환기설비 : 건축물등에서 온도, 습도, 청정도, 기류 등을 조절하기 위하여 설치된 기 계 · 기구 · 배관 및 그 밖에 성능을 유지하기 위한 설비 138 기계설비 기술기준 매뉴얼 | {}
26955c69-6bbb-44b3-b22b-ead6a3b9697f | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 1.3 타 규정과 의 관계 다음의 규정과 이 기준에서 정하는 내용이 상이한 경우에는 해당 규정을 따른다. (1) 「 주택건설기준 등에 관한 규정」 (2) 「건축물의 에너지절약설계기준」 (3) 「에너지관리기준」 (4) KDS 31 25 15 공기조화기기 설계기준 (5) KCS 31 20 15 배관설비공사 표준시방서 해 설 이 기준과 타 규정 및 기준과 다른 경우에는 상기 규정에 명시된 내용을 따름 국토교통부 139 기계설비 기술기준 해설 (별표 02 | {}
a56444dc-0bae-458d-af8c-b0f52de01511 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 공기조화설비 설계 2.1 일반사항 2.1.1 부하계산 (1) 부하계산은 건축물, 시설물 등에 설치되는 냉난방 열원장비와 공기조화장비를 선정하고 공기조 화 배관과 덕트를 설계하기 위하여 수행한다. (2) 공기조화설비는 시간 최대 냉난방부하를 고려하여 선정한다. (3) 냉난방부하는 실내 환경조건에 따라 변하며, 외기 온 、 습도와 일사, 공간에 거주하는 재실자 수, 환기 등에 의해 결정된다. (4) 열원장치부하는 공기조화장비 부하와 배관 및 덕트의 열손실이나 취득 열을 고려하여 안전율을 반영한다. (5) 부하계산 조건 ① 실내 온 、 습도조건 부하계산에 사용되는 실내 온 , 습도조건은 [별표 1] 표 1 에 따른다. ② 외기 온 、 습도 조건 부하계산에 사용되는 외기 온 、 습도조건은 [별표 1] 표 2 에 따른다. ③ 건축물의 부위별 열관류율 부하계산에 사용되는 건축물의 부위별 열관류율은 「건축물의 에너지절약 설계기준 」제 2 조제 1 항 제 1 호에 따른다. ④ 최소외기도입량 부하계산에 사용되는 최소외기도입량은 [별표 3] 표 1 에 따른다. ⑤ 실내부하 기준 가. 일반사항 냉방부하계산에 사용하는 실내부하 요소에는 인체, 조명 및 기기부하가 포함되며 계산서에 실 내부하 기준을 명기한다. 나. 재실인원, 조명 및 부하기기 실내부하를 명확하게 알 수 없는 경우에는 바닥면적(m2) 당 예상 재실인원, 조명 및 기기부하로 냉방부하를 계산한다. 다. 인체 발열부하 인체에서 발생하는 현열(SH)과 잠열(LH)은 실내 온도 및 작업상태를 고려하여 부하에 반영한 다. (6) 외기냉방시스템과 가변속제어방식 등 에너지절약적 제어방식을 적용할 수 있다. 해 설 1. 본문 해설 및 관련 법규 V (1 항, 2 항) 건축물등에 설치하는 냉난방 열원장비와 공기조화설비 그리고 그에 부속되는 배관 및 덕트 등의 용량 및 크기의 결정은 해당 건축물등의 시간당 최대 냉난방부하 계산을 바탕으로 설계 해야함 V (3 항) 시간당 최대 냉난방 부하계산은 건축물등이 위치하는 △지역의 외기 온·습도 및 일사량 △ 용도 등에 따른 재실자 수 △환기 등의 요소들을 고려해야하며, 동 건축물등의 △노후도 △용도 의 변경 △기계설비의 효율저하정도 △기상변화 등을 고려하여 적정한 안전율을 반영해야함 140 기계설비 기술기준 매뉴얼 | {}
40b35014-0ecf-4678-af11-5adc1f908553 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 V (4 항) 부하계산에 사용되는 최소외기량은 「건축물의 설비기준 등에 관한 규칙」 별표 1 의 6 에 따름 「건축물의 설비등에 관한 규칙」 [별표 1 의 6] 다중이용시설 면적별 필요환기량 기준 ¦ 적용시설 ¦ 적용시설 ¦ 기준면적 (연면적 또는 바닥면적, m2) ¦ 필요 환기량(m2/인·h) ¦ 비고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 가. 지하시설 ¦ 지하역사 ¦ 모든 지하역사 ¦ 25 이상 ¦ 출입통로/대합실/승 장장/환승통로 및 이에 딸린 시설 포함 ¦ ¦ 가. 지하시설 ¦ 지하도상가 ¦ 2 000 이상 ¦ 36 이상 ¦ 매장(상점) 기준 ¦ ¦ 나. 문화 및 집회시설 ¦ 실내전시장 ¦ 2000 이상 ¦ 29 이상 ¦ ¦ ¦ 나. 문화 및 집회시설 ¦ 혼인예식장 ¦ 2000 이상 ¦ 29 이상 ¦ ¦ ¦ 나. 문화 및 집회시설 ¦ 실내공연장 ¦ 1 000 이상 ¦ 29 이상 ¦ ¦ ¦ 나. 문화 및 집회시설 ¦ 체육시설 ¦ 1000 이상 ¦ 29 이상 ¦ ¦ ¦ 나. 문화 및 집회시설 ¦ 영화상영관 ¦ ¦ 29 이상 ¦ ¦ ¦ 다. 판매시설 ¦ 대규모점포 ¦ - 、 ¦ 29 이상 ¦ ¦ ¦ 다. 판매시설 ¦ 인터넷컴퓨터게임시 설제공업 ¦ 300 이상 ¦ 29 이상 ¦ ¦ ¦ 라. 운수시설 ¦ 항만 대합실 ¦ 5 000 이상 ¦ 29 이상 ¦ ¦ ¦ 라. 운수시설 ¦ 자동차 여객터미널 ¦ 5 000 이상 ¦ 29 이상 ¦ ¦ ¦ 라. 운수시설 ¦ 철도대합실 ¦ 2 000 이상 ¦ 29 이상 ¦ ¦ ¦ 라. 운수시설 ¦ 공항 여객터미널 ¦ 2000 이상 ¦ 29 이상 ¦ ¦ ¦ 마. 의료시설 ¦ 의료기관 ¦ 1 500 이상/ 병상수 100 개 ¦ 36 이상 ¦ ¦ ¦ 바. 교육연구시설 ¦ 도서관 ¦ 2 000 이상 ¦ 36 이상 ¦ ¦ ¦ 바. 교육연구시설 ¦ 학원 ¦ 3 000 이상 ¦ 36 이상 ¦ ¦ ¦ 사. 노유자시설 ¦ 어린이집 ¦ 430 이상 ¦ 36 이상 ¦ ¦ ¦ 사. 노유자시설 ¦ 노인요양시설 ¦ - 000 이상 ¦ 36 이상 ¦ ¦ ¦ 아. 업무시설 ¦ 업무시설 ¦ 1 000 이상 ¦ 29 이상 ¦ ¦ ¦ 자. 자동차 관련 시설 ¦ 실내주차장 ¦ 3 000 이상 ¦ 27 이상 ¦ ¦ ¦ 차. 장례식장 ¦ 장례식장 ¦ 2000 이상 ¦ 36 이상 ¦ ¦ ¦ 카. 그 밖의 시설 ¦ 목욕장 ¦ 1000 이상 ¦ 25 이상 ¦ ¦ ¦ 카. 그 밖의 시설 ¦ 산후조리원 ¦ 1 000 이상 ¦ 25 이상 ¦ ¦ ¦ 카. 그 밖의 시설 ¦ 실내 어린이놀이시설 ¦ 500 이상 ¦ 25 이상 ¦ ¦ (5 항 1 호) 실내 온습도 조건은 [별표 1]의 표 1 과 같이 「건축물의 에너지절약 설계기준」제 9 조 1 항 [별표 8] 내용을 따름 [별표 8] 냉.난방설비의 용량계산을 위한 실내 온.습도 기준 ¦ 구 분 ¦ 난 방 ¦ 냉 방 ¦ 냉 방 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 용 도 ¦ 건구온도(°C) ¦ 건구온도(°C) ¦ 상대습도(%) ¦ ¦ 공동주택 ¦ 20~22 ¦ 26~28 ¦ 50~60 ¦ ¦ 학교(교실) ¦ 20~22 ¦ 26~28 ¦ 50~60 ¦ ¦ 병원(병실) ¦ 21~23 ¦ 26~28 ¦ 50~60 ¦ ¦ 관람집회시설(객석) ¦ 20~22 ¦ 26~28 ¦ 50~60 ¦ ¦ 숙박시설(객실) ¦ 20~24 ¦ 26~28 ¦ 50~60 ¦ ¦ 판매시설 ¦ 18~21 ¦ 26~28 ¦ 50~60 ¦ ¦ 사무소 ¦ 20~23 ¦ 26~28 ¦ 50~60 ¦ ¦ 목욕장 ¦ 26~29 ¦ 26~29 ¦ 50~75 ¦ ¦ 수영장 ¦ 27~30 ¦ 27~30 ¦ 50~70 ¦ V (5 항 2 호) 외기 온습도 조건은 [별표 1]의 표 2 와 같이 「건축물의 에너지절약 설계기준」 제 8 조 1 항 국토교통부 141 기계설비 기술기준 해설 (별표 02 | {}
60265fe2-8606-45d1-b60d-5efb9a6d01c7 | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 7] 내용을 따름 [별표 7] 냉.난방설비의 용량계산을 위한 설계 외기온.습도 기준 ¦ 구 분 ¦ 냉 방 ¦ 냉 방 ¦ 난 방 ¦ 난 방 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도시명 ¦ 건구온도(°C) ¦ 습구온도(°C) ¦ 건구온도(°C) ¦ 상대습도(%) ¦ ¦ 서 울 ¦ 31.2 ¦ 25.5 ¦ -11.3 ¦ 63 ¦ ¦ 인 천 ¦ 30.1 ¦ 25.0 ¦ -10.4 ¦ 58 ¦ ¦ 수 원 ¦ 31.2 ¦ 25.5 ¦ -12.4 ¦ 70 ¦ ¦ 춘 천 ¦ 31.6 ¦ 25.2 ¦ -14.7 ¦ 77 ¦ ¦ 강 릉 ¦ 31.6 ¦ 25.1 ¦ -7.9 ¦ 42 ¦ ¦ 대 전 ¦ 32.3 ¦ 25.5 ¦ -10.3 ¦ 71 ¦ ¦ 청 주 ¦ 32.5 ¦ 25.8 ¦ -12.1 ¦ 76 ¦ ¦ 전 주 ¦ 32.4 ¦ 25.8 ¦ - 8.7 ¦ 72 ¦ ¦ 서 산 ¦ 31.1 ¦ 25.8 ¦ - 9.6 ¦ 78 ¦ ¦ 광 주구 ¦ 31.8 ¦ 26.0 ¦ - 6.6 ¦ 70 ¦ ¦ 대 ¦ 33.3 ¦ 25.8 ¦ - 7.6 ¦ 61 ¦ ¦ 부 산주 ¦ 30.7 ¦ 26.2 ¦ - 5.3 ¦ 46 ¦ ¦ 진 ¦ 31.6 ¦ 26.3 ¦ - 8.4 ¦ 76 ¦ ¦ 울 산 ¦ 32.2 ¦ 26.8 ¦ - 7.0 ¦ 70 ¦ ¦ 포 항 ¦ 32.5 ¦ 26.0 ¦ - 6.4 ¦ 41 ¦ ¦ 목 포 ¦ 31.1 ¦ 26.3 ¦ - 4.7 ¦ 75 ¦ ¦ 제 주 ¦ 30.9 ¦ 26.3 ¦ 0.1 ¦ 70 ¦ V (5 항 3 호) 건축물의 부위별 열관류율은 「건축물의 에너지절약 설계기준」 제 2 조제 1 항제 1 호 내용을 따름 ① 건축물을 건축하거나 대수선, 용도변경 및 건축물대장의 기재내용을 변경하는 경우에는 다음 각 호의 기 준에 의한 열손실방지 등의 에너지이용합리화를 위한 조치를 하여야 한다. 1. 거실의 외벽, 최상층에 있는 거실의 반자 또는 지붕, 최하층에 있는 거실의 바닥, 바닥난방을 하는 층간 바 닥, 거실의 창 및 문 등은 별표 1 의 열관류율 기준 또는 별표 3 의 단열재 두께 기준을 준수하여야 하고, 단 열조치 일반사항 등은 제 6 조의 건축부문 의무사항을 따른다. 142 기계설비 기술기준 매뉴얼 | {}
5ead1877-c10d-46f8-9b4d-fab0ca2dc104 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 「건축물의 에너지절약 설계기준」 [별표 1] 지역별 건축물 부위의 열관류율표 (단위 : W/m2 · K) ¦ 지역 건축물의 부위 ¦ 지역 건축물의 부위 ¦ 지역 건축물의 부위 ¦ 중부 1 지역 1) ¦ 중부 2 지역 2) ¦ 남부지역 3) ¦ 제주도 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 거실의 외벽 ¦ 외기에 직접 면하는 경우 ¦ 공동주택 ¦ 0.150 이하 ¦ 0.170 이하 ¦ 0.220 이하 ¦ 0.290 이하 ¦ ¦ 거실의 외벽 ¦ 외기에 직접 면하는 경우 ¦ 공동주택 외 ¦ 0.170 이하 ¦ 0.240 이하 ¦ 0.320 이하 ¦ 0.410 이하 ¦ ¦ 거실의 외벽 ¦ 외기에 간접 면하는 경우 ¦ 공동주택 ¦ 0.210 이하 ¦ 0.240 이하 ¦ 0.310 이하 ¦ 0.410 이하 ¦ ¦ 거실의 외벽 ¦ 외기에 간접 면하는 경우 ¦ 공동주택 외 ¦ 0.240 이하 ¦ 0.340 이하 ¦ 0.450 이하 ¦ 0.560 이하 ¦ ¦ 최상층에 있는 거실의 반자 또는 지붕 ¦ 외기에 직접 면하는 경우 ¦ 외기에 직접 면하는 경우 ¦ 0.150 이하 ¦ 0.150 이하 ¦ 0.180 이하 ¦ 0.250 이하 ¦ ¦ 최상층에 있는 거실의 반자 또는 지붕 ¦ 외기에 간접 면하는 경우 ¦ 외기에 간접 면하는 경우 ¦ 0.210 이하 ¦ 0.210 이하 ¦ 0.260 이하 ¦ 0.350 이하 ¦ ¦ 최하층에 있는 거실의 바닥 ¦ 외기에 직접 면하는 경우 ¦ 바닥난방인 경우 ¦ 0.150 이하 ¦ 0.170 이하 ¦ 0.220 이하 ¦ 0.290 이하 ¦ ¦ 최하층에 있는 거실의 바닥 ¦ 외기에 직접 면하는 경우 ¦ 바닥난방이 아닌 경우 ¦ 0.170 이하 ¦ 0.200 이하 ¦ 0.250 이하 ¦ 0.330 이하 ¦ ¦ 최하층에 있는 거실의 바닥 ¦ 외기에 간접 면하는 경우 ¦ 바닥난방인 경우 ¦ 0.210 이하 ¦ 0.240 이하 ¦ 0.310 이하 ¦ 0.410 이하 ¦ ¦ 최하층에 있는 거실의 바닥 ¦ 외기에 간접 면하는 경우 ¦ 바닥난방이 아닌 경우 ¦ 0.240 이하 ¦ 0.290 이하 ¦ 0.350 이하 ¦ 0.470 이하 ¦ ¦ 바닥난방인 층간바닥 ¦ 바닥난방인 층간바닥 ¦ 바닥난방인 층간바닥 ¦ 0.810 이하 ¦ 0.810 이하 ¦ 0.810 이하 ¦ 0.810 이하 ¦ ¦ 창 및 문 ¦ 외기에 직접 면하는 경우 ¦ 공동주택 ¦ 0.900 이하 ¦ 1.000 이하 ¦ 1.200 이하 ¦ 1.600 이하 ¦ ¦ 창 및 문 ¦ 외기에 직접 면하는 경우 ¦ 공동주택 창 외 ¦ 1.300 이하 1,500 이하 ¦ 1.500 이하 ¦ 1.800 이하 ¦ 2.200 이하 ¦ ¦ 창 및 문 ¦ 외기에 직접 면하는 경우 ¦ 문 ¦ ¦ 1.500 이하 ¦ 1.800 이하 ¦ 2.200 이하 ¦ ¦ 창 및 문 ¦ 외기에 간접 면하는 경우 ¦ 공동주택 ¦ 1.300 이하 ¦ 1.500 이하 ¦ 1,700 이하 ¦ 2.000 이하 ¦ ¦ 창 및 문 ¦ 외기에 간접 면하는 경우 ¦ 공동주택 외 문 ¦ 창 1.600 이하 1,900 이하 ¦ 1,900 이하 ¦ 2.200 이하 ¦ 2.800 이하 ¦ ¦ 공동주택 세대현관문 및 방화문 ¦ 외기에 직접 면하는 경우 및 거실 내 방화문 ¦ 외기에 직접 면하는 경우 및 거실 내 방화문 ¦ 1.400 이하 ¦ 1.400 이하 ¦ 1.400 이하 ¦ 1.400 이하 ¦ ¦ 공동주택 세대현관문 및 방화문 ¦ 외기에 간접 면하는 경우 ¦ 외기에 간접 면하는 경우 ¦ 1.800 이하 ¦ 1.800 이하 ¦ 1.800 이하 ¦ 1.800 이하 ¦ 비 고 1) 중부 1 지역 : 강원도(고성, 속초, 양양, 강릉, 동해, 삼척 제외), 경기도(연천, 포천, 가평, 남양주, 의정부, 양 주, 동두천, 파주), 충청북도(제천), 경상북도(봉화, 청송) 2) 중부 2 지역 : 서울특별시, 대전광역시, 세종특별자치시, 인천광역시, 강원도(고성, 속초, 양양, 강릉, 동해, 삼 척), 경기도(연천, 포천, 가평, 남양주, 의정부, 양주, 동두천, 파주 제외), 충청북도(제천 제외), 충청남도, 경 상북도(봉화, 청송, 울진, 영덕, 포항, 경주, 청도, 경산 제외), 전라북도, 경상남도(거창, 함양) 3) 남부지역 : 부산광역시, 대구광역시, 울산광역시, 광주광역시, 전라남도, 경상북도(울진, 영덕, 포항, 경주, 청도, 경산), 경상남도(거창, 함양 제외) 국토교통부 143 기계설비 기술기준 해설 (별표 02 | {}
74e8cf49-fd4e-4831-93bd-6ec05d1f0390 | 국내_기계설비_기술기준_매뉴얼_최종본 | 「건축물의 에너지절약 설계기준」 [별표 3] 단열재의 두께 (단위: mm) ¦ [중부 1 지역] ¦ 단열재의 등급 ¦ 단열재의 등급 ¦ 단열재의 등급 ¦ 단열재 등급별 허용 두께 ¦ 단열재 등급별 허용 두께 ¦ 단열재 등급별 허용 두께 ¦ 단열재 등급별 허용 두께 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ [중부 1 지역] ¦ 건축물의 부위 ¦ 건축물의 부위 ¦ 건축물의 부위 ¦ 가 ¦ 나 ¦ 다 ¦ 라 ¦ ¦ 거실의 외벽 ¦ 외기에 직접 면하는 경우 ¦ 외기에 직접 면하는 경우 ¦ 공동주택 ¦ 220 ¦ 255 ¦ 295 ¦ 325 ¦ ¦ 거실의 외벽 ¦ 외기에 직접 면하는 경우 ¦ 외기에 직접 면하는 경우 ¦ 공동주택 외 ¦ 190 ¦ 225 ¦ 260 ¦ 285 ¦ ¦ 거실의 외벽 ¦ 외기에 직접 면하는 경우 ¦ 외기에 직접 면하는 경우 ¦ 공동주택 ¦ 150 ¦ 180 ¦ 205 ¦ 225 ¦ ¦ 거실의 외벽 ¦ 외기에 간접 면하는 경우 ¦ 외기에 간접 면하는 경우 ¦ 공동주택 외 ¦ 130 ¦ 155 ¦ 175 ¦ 195 ¦ ¦ 최상층에 있는 거실의 반자 또는 지붕 ¦ 외기에 직접 면하는 경우 ¦ 외기에 직접 면하는 경우 ¦ 외기에 직접 면하는 경우 ¦ 220 ¦ 260 ¦ 295 ¦ 330 ¦ ¦ 최상층에 있는 거실의 반자 또는 지붕 ¦ 외기에 간접 면하는 경우 ¦ 외기에 간접 면하는 경우 ¦ 외기에 간접 면하는 경우 ¦ 155 ¦ 180 ¦ 205 ¦ 230 ¦ ¦ 최하층에 있는 거실의 바닥 ¦ 외기에 직접 ¦ 외기에 직접 ¦ 바닥난방인 경우 ¦ 215 ¦ 250 ¦ 290 ¦ 320 ¦ ¦ 최하층에 있는 거실의 바닥 ¦ 면하는 경우 ¦ 면하는 경우 ¦ 바닥난방이 아닌 경우 ¦ 195 ¦ 230 ¦ 265 ¦ 290 ¦ ¦ 최하층에 있는 거실의 바닥 ¦ 외기에 간접 ¦ 외기에 간접 ¦ 바닥난방인 경우 ¦ 145 ¦ 170 ¦ 195 ¦ 220 ¦ ¦ 최하층에 있는 거실의 바닥 ¦ 면하는 경우 ¦ 면하는 경우 ¦ 바닥난방이 아닌 경우 ¦ 135 ¦ 155 ¦ 180 ¦ 200 ¦ ¦ 바닥난방인 층간바닥 ¦ 바닥난방인 층간바닥 ¦ 바닥난방인 층간바닥 ¦ 바닥난방인 층간바닥 ¦ 30 ¦ 35 ¦ 45 ¦ 50 ¦ ¦ [중부 2 지역] ¦ 단열재의 등급 ¦ 단열재의 등급 ¦ 단열재 등급별 허용 두께 ¦ 단열재 등급별 허용 두께 ¦ 단열재 등급별 허용 두께 ¦ 단열재 등급별 허용 두께 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ [중부 2 지역] ¦ 건축물의 부위 ¦ 건축물의 부위 ¦ 가 ¦ 나 ¦ 다 ¦ 라 ¦ ¦ 거실의 외벽 ¦ 외기에 직접 면하는 경우 ¦ 공동주택 ¦ 190 ¦ 225 ¦ 260 ¦ 285 ¦ ¦ 거실의 외벽 ¦ 외기에 직접 면하는 경우 ¦ 공동주택 외 ¦ 135 ¦ 155 ¦ 180 ¦ 200 ¦ ¦ 거실의 외벽 ¦ 외기에 직접 면하는 경우 ¦ 공동주택 외기에 간접 면하는 경우 ¦ 130 ¦ 155 ¦ 175 ¦ 195 ¦ ¦ 거실의 외벽 ¦ 외기에 직접 면하는 경우 ¦ 공동주택 외 ¦ 90 ¦ 105 ¦ 120 ¦ 135 ¦ ¦ 최상층에 있는 거실의 반자 또는 지붕 ¦ 외기에 직접 면하는 경우 ¦ 외기에 직접 면하는 경우 ¦ 220 ¦ 260 ¦ 295 ¦ 330 ¦ ¦ 최상층에 있는 거실의 반자 또는 지붕 ¦ 외기에 간접 면하는 경우 ¦ 외기에 간접 면하는 경우 ¦ 155 ¦ 180 ¦ 205 ¦ 230 ¦ ¦ 최하층에 있는 거실의 바닥 ¦ 외기에 직접 면하는 경우 ¦ 바닥난방인 경우 ¦ 190 ¦ 220 ¦ 255 ¦ 280 ¦ ¦ 최하층에 있는 거실의 바닥 ¦ 외기에 직접 면하는 경우 ¦ 바닥난방이 아닌 경우 ¦ 165 ¦ 195 ¦ 220 ¦ 245 ¦ ¦ 최하층에 있는 거실의 바닥 ¦ 외기에 간접 경우 ¦ 바닥난방인 경우 ¦ 125 ¦ 150 ¦ 170 ¦ 185 ¦ ¦ 최하층에 있는 거실의 바닥 ¦ 외기에 간접 경우 ¦ 면하는 바닥난방이 아닌 경우 ¦ 110 ¦ 125 ¦ 145 ¦ 160 ¦ ¦ 바닥난방인 층간바닥 ¦ 바닥난방인 층간바닥 ¦ 바닥난방인 층간바닥 ¦ 30 ¦ 35 ¦ 45 ¦ 50 ¦ ¦ [남부지역] ¦ 단열재의 등급 ¦ 단열재의 등급 ¦ 단열재의 등급 ¦ 단열재 등급별 허용 두께 ¦ 단열재 등급별 허용 두께 ¦ 단열재 등급별 허용 두께 ¦ 단열재 등급별 허용 두께 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ [남부지역] ¦ 건축물의 부위 ¦ 건축물의 부위 ¦ 건축물의 부위 ¦ 가 ¦ 나 ¦ 다 ¦ 라 ¦ ¦ 거실의 외벽 ¦ 외기에 직접 면하는 경우 ¦ 외기에 직접 면하는 경우 ¦ 공동주택 ¦ 145 ¦ 170 ¦ 200 ¦ 220 ¦ ¦ 거실의 외벽 ¦ 외기에 직접 면하는 경우 ¦ 외기에 직접 면하는 경우 ¦ 공동주택 외 ¦ 100 ¦ 115 ¦ 130 ¦ 145 ¦ ¦ 거실의 외벽 ¦ 외기에 직접 면하는 경우 ¦ 외기에 직접 면하는 경우 ¦ 공동주택 ¦ 100 ¦ 115 ¦ 135 ¦ 150 ¦ ¦ 거실의 외벽 ¦ 외기에 간접 면하는 경우 ¦ 외기에 간접 면하는 경우 ¦ 공동주택 외 ¦ 65 ¦ 75 ¦ 90 ¦ 95 ¦ ¦ 최상층에 있는 거실의 반자 또는 지붕 ¦ 외기에 직접 면하는 경우 ¦ 외기에 직접 면하는 경우 ¦ 외기에 직접 면하는 경우 ¦ 180 ¦ 215 ¦ 245 ¦ 270 ¦ ¦ 최상층에 있는 거실의 반자 또는 지붕 ¦ 외기에 간접 면하는 경우 ¦ 외기에 간접 면하는 경우 ¦ 외기에 간접 면하는 경우 ¦ 120 ¦ 145 ¦ 165 ¦ 180 ¦ ¦ 최하층에 있는 거실의 바닥 ¦ 외기에 직접 ¦ 바닥난방인 경우 ¦ 바닥난방인 경우 ¦ 140 ¦ 165 ¦ 190 ¦ 210 ¦ ¦ 최하층에 있는 거실의 바닥 ¦ 면하는 경우 ¦ 바닥난방이 아닌 경우 ¦ 바닥난방이 아닌 경우 ¦ 130 ¦ 155 ¦ 175 ¦ 195 ¦ ¦ 최하층에 있는 거실의 바닥 ¦ 외기에 간접 ¦ 바닥난방인 경우 ¦ 바닥난방인 경우 ¦ 95 ¦ 110 ¦ 125 ¦ 140 ¦ ¦ 최하층에 있는 거실의 바닥 ¦ 면하는 경우 ¦ 바닥난방이 아닌 경우 ¦ 바닥난방이 아닌 경우 ¦ 90 ¦ 105 ¦ 120 ¦ 130 ¦ ¦ 바닥난방인 층간바닥 ¦ 바닥난방인 층간바닥 ¦ 바닥난방인 층간바닥 ¦ 바닥난방인 층간바닥 ¦ 30 ¦ 35 ¦ 45 ¦ 50 ¦ ¦ [제주도] ¦ 단열재의 등급 ¦ 단열재의 등급 ¦ 단열재의 등급 ¦ 단열재 등급별 허용 두께 ¦ 단열재 등급별 허용 두께 ¦ 단열재 등급별 허용 두께 ¦ 단열재 등급별 허용 두께 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ [제주도] ¦ 건축물의 부위 ¦ 건축물의 부위 ¦ 건축물의 부위 ¦ 가 ¦ 나 ¦ 다 ¦ 라 ¦ ¦ 거실의 외벽 ¦ 외기에 직접 면하는 경우 ¦ 외기에 직접 면하는 경우 ¦ 공동주택 ¦ 110 ¦ 130 ¦ 145 ¦ 165 ¦ ¦ 거실의 외벽 ¦ 외기에 직접 면하는 경우 ¦ 외기에 직접 면하는 경우 ¦ 공동주택 외 ¦ 75 ¦ 90 ¦ 100 ¦ 110 ¦ ¦ 거실의 외벽 ¦ 외기에 직접 면하는 경우 ¦ 외기에 직접 면하는 경우 ¦ 공동주택 ¦ 75 ¦ 85 ¦ 100 ¦ 110 ¦ ¦ 거실의 외벽 ¦ 외기에 간접 면하는 경우 ¦ 외기에 간접 면하는 경우 ¦ 공동주택 외 ¦ 50 ¦ 60 ¦ 70 ¦ 75 ¦ ¦ 최상층에 있는 거실의 반자 또는 지붕 ¦ 외기에 직접 면하는 경우 ¦ 외기에 직접 면하는 경우 ¦ 외기에 직접 면하는 경우 ¦ 130 ¦ 150 ¦ 175 ¦ 190 ¦ ¦ 최상층에 있는 거실의 반자 또는 지붕 ¦ 외기에 간접 면하는 경우 ¦ 외기에 간접 면하는 경우 ¦ 외기에 간접 면하는 경우 ¦ 90 ¦ 105 ¦ 120 ¦ 130 ¦ ¦ 최하층에 있는 거실의 바닥 ¦ 외기에 직접 ¦ 바닥난방인 경우 ¦ 바닥난방인 경우 ¦ 105 ¦ 125 ¦ 140 ¦ 155 ¦ ¦ 최하층에 있는 거실의 바닥 ¦ 면하는 경우 ¦ 바닥난방이 아닌 경우 ¦ 바닥난방이 아닌 경우 ¦ 100 ¦ 115 ¦ 130 ¦ 145 ¦ ¦ 최하층에 있는 거실의 바닥 ¦ 외기에 간접 ¦ 바닥난방인 경우 ¦ 바닥난방인 경우 ¦ 65 ¦ 80 ¦ 90 ¦ 100 ¦ ¦ 최하층에 있는 거실의 바닥 ¦ 면하는 경우 ¦ 바닥난방이 아닌 경우 ¦ 바닥난방이 아닌 경우 ¦ 65 ¦ 75 ¦ 85 ¦ 95 ¦ ¦ 바닥난방인 층간바닥 ¦ 바닥난방인 층간바닥 ¦ 바닥난방인 층간바닥 ¦ 바닥난방인 층간바닥 ¦ 30 ¦ 35 ¦ 45 ¦ 50 ¦ 비 고 1) 중부 1 지역 : 강원도(고성, 속초, 양양, 강릉, 동해, 삼척 제외), 경기도(연천, 포천, 가평, 남양주, 의정부, 양주, 동두천, 파주), 충청북도(제천), 경상북도(봉화, 청송) 2) 중부 2 지역 : 서울특별시, 대전광역시, 세종특별자치시, 인천광역시, 강원도(고성, 속초, 양양, 강릉, 동해, 삼척), 경기도(연천, 포천, 가평, 남양주, 의정부, 양주, 동두천, 파주 제외), 충청북도(제천 제외), 충청남도, 경상북도(봉화, 청송, 울진, 영덕, 포항, 경주, 청도, 경산 제외), 전라북도, 경상남도(거창, 함양) 3) 남부지역 : 부산광역시, 대구광역시, 울산광역시, 광주광역시, 전라남도, 경상북도(울진, 영덕, 포항, 경주, 청도, 경산), 경상남도(거창, 함양 제외) 144 기계설비 기술기준 매뉴얼 | {}
5c83a428-e33d-4e41-a576-0d8dd3dae22a | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 「건축물의 에너지절약 설계기준」 제 1 절 건축부문 설계기준 제 6 조(건축부문의 의무사항) 제 2 조에 따른 열손실방지 조치 대상 건축물의 건축주와 설계자 등은 다음 각 호에서 정하는 건축부문의 설계기준을 따라야 한다. 1. 단열조치 일반사항 가. 외기에 직접 또는 간접 면하는 거실의 각 부위에는 제 2 조에 따라 건축물의 열손실방지 조치를 하여야 한다. 다만, 다음 부위에 대해서는 그러하지 아니할 수 있다. 1) 지표면 아래 2 m 를 초과 하여 위치한 지하 부위(공동주택의 거실 부위는 제외)로서 이중벽의 설치 등 하계 표면결로 방지 조치를 한 경우 2) 지면 및 토양에 접한 바닥 부위로서 난방공간의 외벽 내표면까지의 모든 수평거리가 10 m 를 초과 하는 바닥부위 3) 외기에 간접 면하는 부위로서 당해 부위가 면한 비난방공간의 외피를 별표 1 에 준하여 단열조치하는 경우 4) 공동주택의 층간바닥(최하층 제외) 중 바닥난방을 하지 않는 현관 및 욕실의 바닥부위 5) 제 5 조제 10 호아목에 따른 방풍구조(외벽제외) 또는 바닥면적 150 m2 이하의 개별 점포의 출입문 나. 단열조치를 하여야 하는 부위의 열관류율이 위치 또는 구조상의 특성에 의하여 일정하지 않는 경우에 는 해당 부위의 평균 열관류율 값을 면적가중 계산에 의하여 구한다. 2. 3. 다. 단열조치를 하여야 하는 부위에 대하여는 다음 각 호에서 정하는 방법에 따라 단열기준에 적합한지를 판단할 수 있다. 1) 이 기준 별표 3 의 지역별·부위별·단열재 등급별 허용 두께 이상으로 설치하는 경우(단열재의 등급 분류 는 별표 2 에 따름) 적합한 것으로 본다. 2) 해당 벽·바닥·지붕 등의 부위별 전체 구성재료와 동일한 시료에 대하여 KS F2277(건축용 구성재의 단 열성 측정방법)에 의한 열저항 또는 열관류율 측정값(국가공인시험기관의 KOLAS 인정마크가 표시된 시험성적서의 값)이 별표 1 의 부위별 열관류율에 만족하는 경우에는 적합한 것으로 보며, 시료의 공기 층(단열재 내부의 공기층 포함) 두께와 동일하면서 기타 구성재료의 두께가 시료보다 증가한 경우와 공기층을 제외한 시료에 대한 측정값이 기준에 만족하고 시료 내부에 공기층을 추가하는 경우에도 적 합한 것으로 본다. 단, 공기층이 포함된 경우에는 시공 시에 공기층 두께를 동일하게 유지하여야 한다. 3) 구성재료의 열전도율 값으로 열관류율을 계산한 결과 가 별표 1 의 부위별 열관류율 기준을 만족하는 경 우 적합한 것으로 본다.(단, 각 재료의 열전도율 값은 한국산업규격 또는 국가공인시험기관의 KOLAS 인정마크가 표시된 시험성적서의 값을 사용하고, 표면열전달저항 및 중공층의 열저항은 이 기준 별표 5 및 별표 6 에서 제시하는 값을 사용) 4) 창 및 문의 경우 KS F 2278(창호의 단열성 시험 방법)에 의한 국가공인시험기관의 KOLAS 인정마크가 표시된 시험성적서 또는 별표 4 에 의한 열관류율 값 또는 산업통상자원부고시 「효율관리기자재 운용 규정」에 따른 창 세트의 열관류율 표시값이 별표 1 의 열관류율 기준을 만족하는 경우 적합한 것으로 본다. 5) 열관류율 또는 열관류저항의 계산결과 는 소수점 3 자리로 맺음을 하여 적합 여부를 판정한다.(소수점 4 째 자리에서 반올림) 라. 별표 1 건축물부위의 열관류율 산정을 위한 단열재의 열전도율 값은 한국산업규격 KS L 9016 보온재의 열전도율 측정방법에 따른 국가공인시험기관의 KOLAS 인정마크가 표시된 시험성적서에 의한 값을 사 용하되 열전도율 시험을 위한 시료의 평균온도는 20±5°C 로 한다. 마. 수평면과 이루는 각이 70 도를 초과 하는 경사지붕은 별표 1 에 따른 외벽의 열관류율을 적용할 수 있다. 바. 바닥난방을 하는 공간의 하부가 바닥난방을 하지 않는 공간일 경우에는 당해 바닥난방을 하는 바닥부 위는 별표 1 의 최하층에 있는 거실의 바닥으로 보며 외기에 간접 면하는 경우의 열관류율 기준을 만족 하여야 한다. 에너지절약계획서 및 설계 검토서 제출대상 건축물은 별지 제 1 호 서식 에너지절약계획 설계 검토서 중 에너지성능지표(이하 "에너지성능지표"라 한다) 건축부문 1 번 항목 배점을 0.6 점 이상 획득하여야 한다. 바닥난방에서 단열재의 설치 가. 바닥난방 부위에 설치되는 단열재는 바닥난방의 열이 슬래브 하부 및 측벽으로 손실되는 것을 막을 수 있도록 온수배관(전기난방인 경우는 발열선) 하부와 슬래브 사이에 설치하고, 온수배관(전기난방인 경 우는 발열선) 하부와 슬래브 사이에 설치되는 구성 재료의 열저항의 합계는 층간 바닥인 경우에는 해당 바닥에 요구되는 총열관류저항(별표 1 에서 제시되는 열관류율의 역수)의 60% 이상, 최하층 바닥인 경 우에는 70%(단, 중부 1 지역은 60%, 중부 2 지역은 65%) 이상이 되어야 한다. 다만, 바닥난방을 하는 욕실 및 현관부위와 슬래브의 축열을 직접 이용하는 심야전기이용 온돌 등(한국전력의 심야전력이용기기 승 인을 받은 것에 한한다)의 경우에는 단열재의 위치가 그러하지 않을 수 있다. 국토교통부 145 기계설비 기술기준 해설 (별표 02 | {}
059fd3dc-9c27-4433-bd0f-a1b43e366fe6 | 국내_기계설비_기술기준_매뉴얼_최종본 | 「건축물의 에너지절약 설계기준」 제 1 절 건축부문 설계기준(계속) 4. 기밀 및 결로방지 등을 위한 조치 가. 벽체 내표면 및 내부에서의 결로를 방지하고 단열재의 성능 저하를 방지하기 위하여 제 2 조에 의하여 단열조치를 하여야 하는 부위(창 및 문과 난방공간 사이의 층간 바닥 제외)에는 제 5 조제 10 호카목에 따 른 방습층을 단열재의 실내측에 설치하여야 한다. 나. 방습층 및 단열재가 이어지는 부위 및 단부는 이음 및 단부를 통한 투습을 방지할 수 있도록 다음과 같 이 조치하여야 한다. 1) 단열재의 이음부는 최대한 밀착하여 시공하거나, 2 장을 엇갈리게 시공하여 이음부를 통한 단열성능 저하가 최소화될 수 있도록 조치할 것 2) 방습층으로 알루미늄박 또는 플라스틱계 필름 등을 사용할 경우의 이음부는 100 mm 이상 중첩하고 내 습성 테이프, 접착제 등으로 기밀하게 마감할 것 3) 단열부위가 만나는 모서리 부위는 방습층 및 단열재가 이어짐이 없이 시공하거나 이어질 경우 이음부 를 통한 단열성능 저하가 최소화되도록 하며, 알루미늄박 또는 플라스틱계 필름 등을 사용할 경우의 모서리 이음부는 150 mm 이상 중첩되게 시공하고 내습성 테이프, 접착제 등으로 기밀하게 마감할 것 4) 방습층의 단부는 단부를 통한 투습이 발생하지 않도록 내습성 테이프, 접착제 등으로 기밀하게 마감할 것 다. 건축물 외피 단열부위의 접합부, 틈 등은 밀폐될 수 있도록 코킹과 가스켓 등을 사용하여 기밀하게 처 리하여야 한다. 라. 외기에 직접 면하고 1 층 또는 지상으로 연결된 출입문은 제 5 조제 10 호아목에 따른 방풍구조로 하여야 한다. 다만, 다음 각 호에 해당하는 경우에는 그러하지 않을 수 있다. 1) 바닥면적 300 m2 이하의 개별 점포의 출입문 2) 주택의 출입문(단, 기숙사는 제외) 3) 사람의 통행을 주목적으로 하지 않는 출입문 4) 너비 1.2 m 이하의 출입문 마. 방풍구조를 설치하여야 하는 출입문에서 회전문과 일반문이 같이 설치되어진 경우, 일반문 부위는 방 풍실 구조의 이중문을 설치하여야 한다. 바. 건축물의 거실의 창이 외기에 직접 면하는 부위인 경우에는 제 5 조제 10 호자목에 따른 기밀성 창을 설치 하여야 한다. 5. 영 제 10 조의 2 에 해당하는 공공건축물을 건축 또는 리모델링하는 경우 법 제 14 조의 2 제 1 항에 따라 에너지 성능지표 건축부문 8 번 항목 배점을 0.6 점 이상 획득하여야 한다. 다만, 건축물 에너지효율 1++등급 이상 을 취득한 경우 또는 제 21 조제 2 항에 따라 건축물 에너지소요량 평가서의 단위면적당 1 차 에너지소요량 의 합계가 적합할 경우에는 그러하지 아니할 수 있다. (5 항 4 호) 최소외기도입량은 「건축물의 설비기준 등에 관한 규칙」 제 11 조제 5 항 관련 [별표 1 의 6] 내용을 따름 146 기계설비 기술기준 매뉴얼 | {}
48cb51ab-c592-4807-bd8f-804788249ec0 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 [별표 1 의 6] 기계환기설비를 설치해야 하는 다중이용시설 및 각 시설의 필요 환기량 1. 기계환기설비를 설치하여야 하는 다중이용시설 가. 지하시설 1) 모든 지하역사(출입통로·대기실·승강장 및 환승통로와 이에 딸린 시설을 포함한다) 2) 연면적 2 000 m2 이상인 지하도상가(지상건물에 딸린 지하층의 시설 및 연속되어 있는 둘 이상의 지하 도상가의 연면적 합계가 2 000 m2 이상인 경우를 포함한다) 나. 문화 및 집회시설 1) 연면적 2 000 m2 이상인 「건축법 시행령」 별표 1 제 5 호라목에 따른 전시장(실내 전시장으로 한정한다) 2) 연면적 2 000 m2 이상인 「건전가정의 례의 정착 및 지원에 관한 법률」에 따른 혼인예식장 3) 연면적 1 000 m2 이상인 「공연법」 제 2 조제 4 호에 따른 공연장(실내 공연장으로 한정한다) 4) 관람석 용도로 쓰이는 바닥면적이 1 000 m2 이상인 「체육시설의 설치·이용에 관한 법률」 제 2 조제 1 호 에 따른 체육시설 5) 「영화 및 비디오물의 진흥에 관한 법률」 제 2 조제 10 호에 따른 영화상영관 다. 판매시설 1) 「유통산업발전법」 제 2 조제 3 호에 따른 대규모점포 2) 연면적 300 m2 이상인 「게임산업 진흥에 관한 법률」 제 2 조제 7 호에 따른 인터넷컴퓨터게임시설제공업 의 영업시설 라. 운수시설 1) 「항만법」 제 2 조제 5 호에 따른 항만시설 중 연면적 5 000 m2 이상인 대기실 2) 「여객자동차 운수사업법」 제 2 조제 5 호에 따른 여객자동차터미널 중 연면적 2 000 m2 이상인 대기실 3) 「철도산업발전기본법」 제 3 조제 2 호에 따른 철도시설 중 연면적 2 000 m2 이상인 대기실 4) 「공항시설법」 제 2 조제 7 호에 따른 공항시설 중 연면적 1 500 m2 이상인 여객터미널 마. 의료시설: 연면적이 2 000 m2 이상이거나 병상 수가 100 개 이상인 「의료법」 제 3 조에 따른 의료기관 바. 교육연구시설 1) 연면적 3 000 m2 이상인 「도서관법」 제 2 조제 1 호에 따른 도서관 2) 연면적 1 000 m2 이상인 「학원의 설립·운영 및 과외교습에 관한 법률」 제 2 조제 1 호에 따른 학원 사. 노유자시설 1) 연면적 430 m2 이상인 「영유아보육법」 제 2 조제 3 호에 따른 어린이집 2) 연면적 1 000 m2 이상인 「노인복지법」 제 34 조제 1 항제 1 호에 따른 노인요양시설 아. 업무시설: 연면적 3 000 m2 이상인 「건축법 시행령」 별표 1 제 14 호에 따른 업무시설 자. 자동차 관련 시설: 연면적 2 000 m2 이상인 「주차장법」 제 2 조제 1 호에 따른 주차장(실내주차장으로 한 정하며, 같은 법 제 2 조제 3 호에 따른 기계식주차장은 제외한다) 차. 장례식장: 연면적 1 000 m2 이상인 「장사 등에 관한 법률」 제 28 조의 2 제 1 항 및 제 29 조에 따른 장례식장 (지하에 설치되는 경우로 한정한다) 카. 그 밖의 시설 1) 연면적 1 000 m2 이상인 「공중위생관리법」 제 2 조제 1 항제 3 호에 따른 목욕장업의 영업시설 2) 연면적 500 m2 이상인 「모자보건법」 제 2 조제 10 호에 따른 산후조리원 3) 연면적 430 m2 이상인 「어린이놀이시설 안전관리법」 제 2 조제 2 호에 따른 어린이놀이시설 중 실내 어 린이놀이시설 기계설비 기술기준 해설 (별표 02 국토교통부 147 | {}
efc54888-9cb1-435a-9073-bf0d44c98830 | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 1 의 6] 기계환기설비를 설치해야 하는 다중이용시설 및 각 시설의 필요 환기량(계속) 2. 각 시설의 필요 환기량 ¦ 구분 ¦ 구분 ¦ 필요 환기량(m2/인-h) ¦ 비고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 가. 지하시설 ¦ 1) 지하역사 ¦ 25 이상 ¦ ¦ ¦ 가. 지하시설 ¦ 2) 지하도상가 ¦ 36 이상 ¦ 매장(상점) 기준 ¦ ¦ 나. 문화 및 집회시설 ¦ 나. 문화 및 집회시설 ¦ 29 이상 ¦ ¦ ¦ 다. 판매시설 ¦ 다. 판매시설 ¦ 29 이상 ¦ ¦ ¦ 라. 운수시설 ¦ 라. 운수시설 ¦ 29 이상 ¦ ¦ ¦ 마. 의료시설 ¦ 마. 의료시설 ¦ 36 이상 ¦ ¦ ¦ 바. 교육연구시설 ¦ 바. 교육연구시설 ¦ 36 이상 ¦ ¦ ¦ 사. 노유자시설 ¦ 사. 노유자시설 ¦ 36 이상 ¦ ¦ ¦ 아. 업무시설 ¦ 아. 업무시설 ¦ 29 이상 ¦ ¦ ¦ 자. 자동차 관련 시설 ¦ 자. 자동차 관련 시설 ¦ 27 이상 ¦ ¦ ¦ 차. 장례식장 ¦ 차. 장례식장 ¦ 36 이상 ¦ ¦ ¦ 카. 그 밖의 시설 ¦ 카. 그 밖의 시설 ¦ 25 이상 ¦ ¦ 비고 가. 제 1 호에서 연면적 또는 바닥면적을 산정할 때에는 실내공간에 설치된 시설이 차지하는 연면적 또는 바닥면적을 기준으로 산정한다. 나. 필요 환기량은 예상 이용인원이 가장 높은 시간대를 기준으로 산정한다. 다. 의료시설 중 수술실 등 특수 용도로 사용되는 실(�)의 경우에는 소관 중앙행정기관의 장이 달리 정할 수 있다. 라. 제 1 호자목의 자동차 관련 시설의 필요 환기량은 단위면적당 환기량(m2/m2h)으로 산정한다. V (5 항 5 호) 기계설비계산서에 재실인원, 조명부하, 기기부하 등이 포함된 실내부하기준을 명시해야 함 (5 항 6 호) 외기냉방시스템과 가변속제어방식 외 공기조화설비에 적용 가능한 에너지절약적 제어 방식을 채택할 수 있음 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 외기냉방시스템 ¦ 외기를 직접 실내로 끌어들여 냉방하는 방식으로 외기온도가 실내온도보다 낮을 때 외기를 도입하여 냉동기를 운전하지 않아도 외기만으로 냉방 운전이 가능하다. 출처 : 공조냉동건축설비 용어사전 ¦ ¦ 가변속 제어방식 = 변풍량제어방식 ¦ 공조 공간의 열부하 증감에 따라서 급기량을 자동적으로 조절해서 온습도를 유지하 는 방식. VAV 로 칭한다. 출처 : 설비공학편람 제 4 권 - 공기조화방식과 장비 ¦ ○ 2.1 일반사항(계속) 2.1.2 공기조화조닝 계획 (1) 건물의 규모 및 형태에 따라 열부하특성을 고려하여 조닝한다. (2) 운영시간 및 운영특성이 상이한 곳에는 별도 조닝하여 계획한다. (3) 별도의 청정기준이 요구되는 클린룸, 실험실, 무균실, 수술실 등은 별도조닝을 계획한다. 해 설 148 기계설비 기술기준 매뉴얼 | {}
394a531d-cf87-4a5d-9635-91e027fc3fb0 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 1. 본문 해설 및 관련 법규 V (1 항) 건축물은 저층·중층·고층 등 수직적인 구분과 일사 등 외기의 영향을 받는 외주부 및 재실자 등 건축물 내부 요소의 영향을 받는 내주부 등으로 구분 가능함 V (2 항) 하나의 건축물에 다양한 용도(오피스, 오피스텔, 다중이용시설, 체육관 등)또는 운영시간(간 헐사용, 8 시간, 24 시간 등)이 다른 시설이 있는 경우에는 각각 별도의 조닝을 계획함 V (3 항) 별도의 공기질 기준이 적용되는 클린룸, 실험실, 무균실, 수술실 등과 실내 부압이 형성되는 유해물질 발생실 등은 각각 별도 조닝으로 계획함 2. 용어 V 내용 없음 2.2 공기조화기 (1) 장비일람에는 공기조화기의 주요용도 및 공기조화기 형식 등을 명기한다. (2) 공기조화기는 케이싱과 송풍기, 냉각 , 가열 코일, 필터, 가습기, 댐퍼 등으로 구성되며, 구성품의 사양은 장비일람에 명기한다. 또한, 실내 온 、 습도 및 공기청정도 조건에 맞게 제어할 수 있어야 한다. (3) 공기조화기 부속의 유지관리를 위하여 공기조화기 폭 만큼의 여유 공간을 확보한다. (4) 동결의 우려가 있는 공기조화설비는 동파방지대책을 고려한다. (5) 외기댐퍼와 배기댐퍼는 기밀댐퍼로 하고, 면풍속은 1.5~7.5 m/s 로 한다. (6) 필터의 통과 풍속은 2.5 m/s 이하로 한다. (7) 필터 전후의 차압을 측정할 수 있는 차압계를 계획한다. (8) 감염병 대비 전외기 방식 등을 고려해야 한다. 단, 기존 건축물의 공기조화기에는 인버터, 살균장 치 등의 설치를 할 수 있다. (9) 건축물 이용특성 및 타당성을 검토하여 변풍량제어(VAV: Variable Air Volume)방식 및 송풍기 의 인버터제어 등 에너지절약형 공조방식을 적용할 수 있다. (10) 변풍량제어방식을 도입할 경우에는 온도센서 및 급 、 환기덕트에 각각 풍량측정장치 또는 급 환기팬 입력제어장치를 설치하여 과열 및 과랭을 방지한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항, 2 항) 공기조화기 설치 시 장비일람표에 공기조화기의 형식, 용도, 송풍기 사양, 냉난방 코일 용량, 필터, 가습기, 댐퍼 등 공기조화기와 관련된 중요사항들을 명기해야 함 기계설비 기술기준 해설 (별표 02 국토교통부 149 | {}
5182eae5-47ed-471b-a62a-e0b008074f31 | 국내_기계설비_기술기준_매뉴얼_최종본 | 장비일람 적용 예_공기조화기 ¦ 장비번호 구분 ¦ 장비번호 구분 ¦ AHU-01 ¦ AHU-02 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 수 량 ¦ 수 량 ¦ 1 ¦ 1 ¦ ¦ 용 도 ¦ 용 도 ¦ 1F 대강당(무대부) ¦ 1F 대강당(객석부) ¦ ¦ 형 식 ¦ 형 식 ¦ 수평형 ¦ 수평형 ¦ ¦ 설치위치 ¦ 설치위치 ¦ 지하 1 층 기계실 ¦ 지하 1 층 기계실 ¦ ¦ 급기송풍기 ¦ 형식 ¦ AIRFOIL ¦ AIRFOIL ¦ ¦ 급기송풍기 ¦ 풍량(CMH) ¦ 8 000 ¦ 17 000 ¦ ¦ 급기송풍기 ¦ 정압(Pa) ¦ 1 050 ¦ 1 060 ¦ ¦ 급기송풍기 ¦ 변수*대수 ¦ DS#3 ¦ DS#4 ¦ ¦ 급기송풍기 ¦ 전동기(kW) ¦ 5.5 ¦ 11 ¦ ¦ 급기송풍기 ¦ 효율(%) ¦ 55.1 ¦ 73.0 ¦ ¦ 냉수코일 ¦ 냉각능력(kW) ¦ 62.2 ¦ 143.5 ¦ ¦ 냉수코일 ¦ 입구공기온도(°C) ¦ 27.9 ¦ 28.1 ¦ ¦ 냉수코일 ¦ 출구공기온도(°C) ¦ 15.7 ¦ 15.3 ¦ ¦ 온수코일 ¦ 가열능력(kW) ¦ 42.1 ¦ 88 ¦ ¦ 온수코일 ¦ 온수량(l/min) ¦ 60 ¦ 126 ¦ ¦ 온수코일 ¦ 온수온도(°C) ¦ 60/70 ¦ 60/70 ¦ ¦ 온수코일 ¦ 입구공기온도(°C) ¦ 10.8 ¦ 9.8 ¦ ¦ 온수코일 ¦ 출구공기온도(°C) ¦ 24.0 ¦ 22.8 ¦ ¦ 필터 ¦ 프리필터 ¦ MERV12 ¦ MERV12 ¦ ¦ 필터 ¦ 중성능필터 ¦ MERV15 ¦ MERV15 ¦ ¦ 가습기 ¦ 형식 ¦ - ¦ - ¦ ¦ 가습기 ¦ 가습량(LPM) ¦ - ¦ - ¦ V (3 항) 이 기준 [별표 15]의 기준에 맞게 공기조화기의 폭만큼 벽 또는 다른 장비와 의 여유공간을 확보해야 하며, 이때 여유공간 확보는 부속의 교체 등을 위해 필요한 방향으로 할 수 있음 V (4 항) 겨울철 공기조화기 배관 내 유체의 동결로 인한 파손이 우려되는 경우, 동파방지댐퍼코일 등의 동결방지대책을 수립해야 함 V (5 항) 에너지 손실 및 소음 방지를 위해 외기댐퍼와 배기댐퍼는 기밀댐퍼(Air tight damper)를 채 택하며, 적정 풍속을 유지하여야 함 V (6 항) 필터 통과 에 따른 정압손실 최소화를 위해 풍속은 2.5 m/s 이하로 함 V (7 항) 필터 전후 차압을 통해 필터 표면 오염도 파악 등 유지관리 여부를 판단함 V (8 항) 추가 설명 없음 V (9 항) 봄, 가을 등 냉난방 부하가 적은 중간기에는 풍량을 줄여 에너지 손실을 방지할 수 있도록 함 V (10 항) 변풍량제어 방식 채택 시에는 기준에 있는 방법을 포함하여 과열 및 과냉 방지를 위한 조 치를 갖추어야 함 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 인버터제어 ¦ 정지형 전력변환기로서 전동기의 가변속운전을 위하여 설치하는 설비로서 고효율인 증제품 또는 동등 이상의 성능을 가진 것을 말한다. 출처 : 건축물의 에너지절약설계기준 ¦ 150 기계설비 기술기준 매뉴얼 | {}
d6469db2-06e3-46e3-9d64-b4bf3d94980d | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.3 터미널 유닛 장비일람에 유닛의 형식과 최대 풍량, 최소 풍량, 입구 크기, 냉방전용, 재열 유무, 마찰손실 등을 명 기한다. 해 설 1. 본문 해설 및 관련 법규 장비일람표에 터미널 유닛의 형식, 최대 풍량, 최소 풍량, 입구 크기, 냉방전용, 재열 유무, 마찰손 실 등 터미널 유닛과 관련된 중요사항들을 명기해야 함 2. 용어 V 내용 없음 2.4 팬코일 유닛 (1) 장비일람에 유닛 형식과 풍량, 전기사항(동력, 전압, 전류, 주파수, 상), 냉각 , 가열 능력, 입 、 출 구 공기 조건, 입 , 출구 냉 , 온수 조건, 최고사용압력 등을 명기한다. (2) 열 수요 변화에 대응할 수 있도록 구역에 따라 유량 및 풍량 조절이 가능하도록 설치한다. 해 설 1. 본문 해설 및 관련 법규 (1 항) 장비일람표에 팬코일 유닛의 형식, 풍량, 전기사항(동력, 전압, 전류, 주파수, 상), 냉방 · 난방 능력, 입 · 출구 공기 조건, 입 · 출구 냉 · 온수 조건, 최고사용압력 등 팬코일 유닛과 관련된 중요 사항들을 명기해야 함 V (2 항) 건축물등의 내부 구획의 변경, 재실자 수 증감 등에 대처할 수 있도록 유량 및 풍량 조절이 가능하도록 설치해야 함 2. 용어 내용 없음 2.5 방열기 장비일람에 방열기 형식, 열량, 열매종류, 입 , 출구 온도조건 및 유량 등을 명기한다. 국토교통부 151 기계설비 기술기준 해설 (별표 02 | {}
6e3874bf-442c-448a-a5df-49b6f35960d2 | 국내_기계설비_기술기준_매뉴얼_최종본 | 해 설 1. 본문 해설 및 관련 법규 장비일람표에 방열기의 형식, 열량, 열매종류, 입 · 출구 온도조건 및 유량 등 방열기와 관련된 중 요사항들을 명기해야 함 방열기 표기방법 열 수 형 식 입구 X 출구 관경 2. 용어 V 내용 없음 2.6 온수온돌 난방 (1) 각 방은 한 개 또는 그 이상의 난방코일로 구획한다. (2) 「」 주택건설기준 등에 관한 규정」 제 37 조에 따라 침실에 포함되는 옷방 또는 붙박이 가구 설치 공 간에도 난방설비를 설치해야 한다. 해 설 1. 본문 해설 및 관련 법규 (1 항) 해당 방이 전용 부속실(욕실, 드레스룸, 펜트리 등)을 포함하는 경우에는 하나의 방으로 간 주할 수 있음 (2 항) 추가 설명 없음 2, 용어 V 내용 없음 152 기계설비 기술기준 매뉴얼 | {}
87629f09-8509-4b65-a39f-c42d049f6475 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 3. 공기조화설비 시공 3.1 공기조화기 (1) 배수판의 물은 간접배수를 하며 연결 배수트랩은 봉수 유지와 응축수의 배출이 용이하도록 한다. (2) 진동 및 소음이 적고 풍량, 정압, 냉각, 가열 등 소정의 능력을 충분히 발휘하는 것으로 설치한다. (3) 조립 설치 시 연결부분의 기밀과 단열성능이 유지되도록 해야 한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 추가 설명 없음 V (2 항) 공기조화기 장비일람 상에 표시된 능력을 발휘할 수 있는 제품으로 선정하고, 장비의 안전 및 재실자 쾌적을 위해 진동 및 소음 방지 장치를 선정하여 시공해야 함 V (3 항) 덕트와 공기조화기의 연결부위를 기밀하게 하여 에너지 손실이 없도록 하며, 공기조화기 자 체의 단열 성능이 유지되도록 기밀 및 단열 조치를 해야 함 2. 용어 V 내용 없음 - --- 3.2 터미널 유닛 (1) 바닥 설치형은 벽 또는 바닥에 견고하게 설치한다. (2) 천장걸이형은 걸이철물 등으로 수평으로 견고하게 설치한다. 은폐 설치할 때에는 보수 및 점검이 쉽도록 설치한다. 3.3 팬코일 유닛 팬코일 유닛설치는 3.2 에 따른다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 바닥에 설치하는 터미널 유닛은 기류 이송에 따른 소음 및 고장 발생을 최소화하고, 타 시설 물 및 재실자에 의한 훼손을 방지할 수 있도록 바닥에 단단히 고정해야 함 V (2 항) 천장에 설치하는 터미널 유닛은 수평으로 설치하고, 「기계설비 유지관리기준」 [별지 제 2 호 서식] 팬코일 유닛 유지관리 점검표 및 [별지 제 3 호서식] 팬코일 유닛 성능점검표 상의 유지관리 가 가능하도록 설치해야 함 2. 용어 V 내용 없음 국토교통부 153 기계설비 기술기준 해설 (별표 02 | {}
99f23d62-ab58-4e22-8986-54f6a0d9f906 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3.4 방열기 (1) 바닥설치형 방열기는 벽면으로부터 60 mm 이상의 간격을 두고 설치한다. (2) 벽걸이 방열기 ① 벽걸이 방열기에 사용하는 걸이철물의 개수는 KCS 31 25 15(3.8.1) 표 3.8-1 에 따른 표 1 을 적 용한다. ② 벽걸이철물 설치 위치는 양쪽 끝으로 두 번째와 세 번째 쪽 사이로 한다. 중간용이 필요한 경우에 는 그 사이를 등분한 위치로 한다. 표 1 벽걸이 방열기의 걸이철물 수(KCS 31 25 15(3.8.1) 표 3.8-1) ¦ 종별 ¦ 벽걸이철물의 개수 ¦ 벽걸이철물의 개수 ¦ 벽걸이철물의 개수 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 종별 ¦ 2 ¦ 3 ¦ 4 ¦ ¦ 수직형 ¦ 2~4 쪽 ¦ 5~8 쪽 ¦ 9~12 쪽 ¦ ¦ 수평형 ¦ 2~3 쪽 ¦ 4~6 쪽 ¦ 7~9 쪽 ¦ 해 설 1. 본문 해설 및 관련 법규 V (1 항) 대류 확산 촉진 및 유지관리를 위해 60 mm 이상 간격을 두고 설치해야 함 V (2 항 1 호, 2 호) 벽걸이 방열기를 설치하는 경우 사용하는 최소 철물 수는 KCS 31 25 15(3.8.1) 표 3.8-1 에 따르며, 기준에 따라 가능한 균등하게 시공해야 함 2. 용어 내용 없음 3.5 온수온돌 난방 (1) 설계에서 요구하는 배관간격이 유지되도록 하고, 온도변화에 따른 관의 신축을 고려하여 시공해 야 한다. (2) 관의 굽힌 부분은 관의 변형 및 단면적 축소가 없도록 한다. (3) 공기체류가 예상되는 부분에는 공기빼기밸브를 설치한다. (4) 축열재 충진 등의 작업 시 방열관이 변형되거나 밀리지 않도록 해야 하며, 방열관 및 단열층이 충 격 등에 의하여 변형 또는 손상되지 않도록 한다. (5) 온수분배기 주위 등 코일배관 조밀지역에는 과열방지 조치를 한다. 154 기계설비 기술기준 매뉴얼 | {}
e8c383c7-4ed9-4d43-8620-c36403432e70 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 해 설 1. 본문 해설 및 관련 법규 V (1 항, 2 항) 배관 사이의 간격은 해당 설계도서에 따르되 사용하는 배관의 곡률 반경 이하로 설치 하지 않으며, 온수온돌 온도 변화에 따른 바닥면 크랙 발생 등에 유의 하여 시공하여야 함 V (3 항) 배관은 최대한 수평으로 설치하여 공기가 체류하지 못하도록 시공하는 것이 우선이며, 그럼 에도 불구하고 공기체류가 예상되는 부분에는 공기빼기밸브를 설치해야 함 V (4 항) 배관 시공 간격 등 설치된 배관의 상태가 다른 공정에 의해 훼손되지 않도록 관리해야 함 V (5 항) 온수 분배기 등에서 배관 간격이 조밀하게 시공되는 공급측에는 개별 배관의 단열 조치 등 을 통해 과열되지 않도록 함 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 공기빼기밸브 ¦ 관내 공기 체류로 인한 순환장애로 효율저하, 소음 발생, 순환 불량 등으로 공기 정체 가 우려되는 곳에서 공기를 배제하는 밸브 ¦ 국토교통부 155 기계설비 기술기준 해설 (별표 02 | {}
0fdef23c-1b49-4192-8d8d-b44c71d6f541 | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 3] 환기설비의 설계 및 시공 기준 1. 환기설비 일반사항 1.1 목적 이 기준은 건축물, 시설물 내 공간을 대상으로 신선한 외기 공급과 공기 중 미세먼지 및 오염물질 제 거, 열과 연소가스의 제거, 실내 공기전파 감염병의 확산 방지를 통하여 대상 공간의 공기질을 사용 목적에 적합하도록 유지하는데 필요한 설계 및 시공 방법 등 세부 기술기준을 정함을 목적으로 한다. 해 설 이 기준의 목적은 「기계설비법」 제 14 조(기계설비 기술기준)과 같은 법 영 제 2 조 및 [별표 1]에 근 거하여, 건축물이나 시설물에 필요한 환기설비의 설계 및 시공 시 기계설비의 안전과 성능을 확 보하기 위하여 필요한 기술적 요건을 규정하기 위함 「기계설비법」 제 14 조(기계설비 기술기준) ① 국토교통부장관은 기계설비의 안전과 성능확보를 위하여 필요 한 기술기준(이하 "기술기준이라 한다)를 정하여 고시하여야 한다. 이를 변경하는 경우에도 또한 같다. 1.2 적용범위 이 기준은 건축물, 시설물 등에 환기설비를 설치하는 경우에 대하여 적용한다. 해 설 이 기준의 적용범위는 「기계설비법」 제 2 조제 1 호에 따른 건축물등에 같은 법 영 제 2 조에 따라 대 통령령으로 정한 환기설비를 설치하는 경우 및 그와 관련된 부속설비들을 포함함 「기계설비법」 제 2 조(정의) 1. "기계설비"란 건축물, 시설물 등(이하 "건축물등"이라 한다)에 설치된 기계 · 기 구 · 배관 및 그 밖에 건축물등의 성능을 유지하기 위한 설비로서 대통령령으로 정하는 설비를 말한다. 「기계설비법 시행령」 제 2 조(기계설비의 범위) 「기계설비법」(이하 "법"이라 한다) 제 2 조제 1 호에서 "대통령령 으로 정하는 설비"란 별표 1 의 설비를 말한다. 「기계설비법 시행령」 [별표 1] 기계설비의 범위 3. 공기조화 · 공기청정 · 환기설비 : 건축물등에서 온도, 습도, 청정도, 기류 등을 조절하기 위하여 설치된 기 계 · 기구 · 배관 및 그 밖에 성능을 유지하기 위한 설비 156 기계설비 기술기준 매뉴얼 | {}
940bb23e-cd6f-447b-b851-97c59d2af1cf | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 1.3 타 규정과 의 관계 다음의 규정과 이 기준에서 정하는 내용이 상이한 경우에는 해당 규정을 따른다. (1) 「 주택건설기준 등에 관한 규정」 (2) 「건축물의 설비기준 등에 관한 규칙」 (3) KDS 27 60 00 터널환기, 조명, 방재설비 설계기준 (4) KDS 31 25 15 공기조화기기 설계기준 (5) KDS 31 25 20 환기설비 설계기준 (6) KCS 31 25 15 공기조화기기 설비공사 표준시방서 해 설 V 이 기준과 타 규정 및 기준과 다른 경우에는 상기 규정에 명시된 내용을 따름 국토교통부 157 기계설비 기술기준 해설 (별표 03 | {}
420ed8b5-1da4-40ca-b69b-9e28c866232f | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 환기설비 설계 2.1 설계기준 2.1.1 오염원 기준 (1) 실내공기 오염물질 실내공기 오염물질의 적용대상 및 허용농도는「실내공기질 관리법」시행규칙 제 3 조(실내공기질 유 지기준), 제 4 조(실내공기질 권고기준)에 따른다. (2) 대기 오염물질 실내에 도입되는 대기 오염물질의 허용농도는 실내공기질 유지기준 이하로 유지한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 다음의 기준을 준수해야 함 실내공기질 유지기준(제 3 조 관련) ¦ 오염물질 항목 다중이용시설 ¦ 미세먼지 (PM-10) (�g/m2) ¦ 미세먼지 (PM-2.5) (�g/m2) ¦ 이산화 탄소 (ppm) ¦ 폼알데하 이드 (�g/m2) ¦ 총 부유세균 (CFU/m2) ¦ 일산화 탄소 (ppm) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 가. 지하역사, 지하도상가, 철도역사의 대합실, 여객자동차터미널의 대합실, 항만시설 중 대합실, 공항시설 중 여객터미널, 도서관 · 박물관 및 미술관, 대규모 점포, 장례식장, 영화상영관, 학원, 전시시설, 인터넷컴퓨터게임시설제공업의 영업시설, 목욕장업의 영업시설 ¦ 100 이하 ¦ 50 이하 ¦ 1,000 이하 ¦ 100 이하 ¦ ¦ 10 이하 ¦ ¦ 나. 의료기관, 산후조리원, 노인요양시설, 어린이집, 실내 어린이놀이시설 ¦ 75 이하 ¦ 35 이하 ¦ 1,000 이하 ¦ 80 이하 ¦ 800 이하 ¦ 10 이하 ¦ ¦ 다. 실내주차장 ¦ 200 이하 ¦ - ¦ 1,000 이하 ¦ 100 이하 ¦ - ¦ 25 이하 ¦ ¦ 라. 실내 체육시설, 실내 공연장, 업무시설, 둘 이상의 용도에 사용되는 건축물 ¦ 200 이하 ¦ ¦ ¦ - ¦ - ¦ ¦ 비고 1. 도서관, 영화상영관, 학원, 인터넷컴퓨터게임시설제공업 영업시설 중 자연환기가 불가능하여 자연환기설비 또는 기계환기설비를 이용하는 경우에는 이산화탄소의 기준을 1 500 ppm 이하로 한다. 2. 실내 체육시설, 실내 공연장, 업무시설 또는 둘 이상의 용도에 사용되는 건축물로서 실내 미세먼지(PM-10)의 농도가 200 �g/m2 에 근접하여 기준을 초과 할 우려가 있는 경우에는 실내공기질의 유지를 위하여 다음 각 목의 실내공기정화시설(덕트) 및 설비를 교체 또는 청소하여야 한다. 가. 공기정화기와 이에 연결된 급·배기관(급·배기구를 포함한다) 나. 중앙집중식 냉·난방시설의 급·배기구 다. 실내공기의 단순배기관 라. 화장실용 배기관 마. 조리용 배기관 158 기계설비 기술기준 매뉴얼 | {}
c836af35-e4d0-40ce-a16c-7533abb7a463 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 실내공기질 권고기준(제 4 조 관련) ¦ 오염물질 항목 다중이용시설 ¦ 이산화질소 (ppm) ¦ 라돈 (Bq/m2) ¦ 총휘발성 유기화합물 (�g/m2) ¦ 곰팡이 (CFU/m2) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 가. 지하역사, 지하도상가, 철도역사의 대합실, 여객자동차터미널의 대합실, 항만시설 중 대합실, 공항시설 중 여객터미널, 도서관·박물관 및 미술관, 대규모점포, 장례식장, 영화상영관, 학원, 전시시설, 인터넷컴퓨터게임시설제공업의 영업시설, 목욕장업의 영업시설 ¦ 0.1 이하 ¦ 148 이하 ¦ 500 이하 ¦ ¦ ¦ 나. 의료기관, 산후조리원, 노인요양시설, 어린이집, 실내 어린이놀이시설 ¦ 0.05 이하 ¦ 148 이하 ¦ 400 이하 ¦ 500 이하 ¦ ¦ 다. 실내주차장 ¦ 0.30 이하 ¦ 148 이하 ¦ 1 000 이하 ¦ ¦ (2 항) 도입되는 외기 중의 분진을 필터 등을 통해 제거해야 함 2. 용어 내용 없음 - -- 2.1 설계기준(계속) 2.1.2 용도별 환기설비 (1) 공동주택(영 별표 5 제 2 호나목에 따른 아파트 및 연립주택을 말한다) ① 영 별표 5 제 2 호나목에 따른 아파트, 연립주택의 필요환기량은「건축물의 설비기준 등에 관한 규 칙」제 11 조제 1 항에 따라 시간당 0.5 회 이상으로 한다. ② 공기여과 장치는 입자형 , 가스형 오염물질을 차단할 수 있는 형식으로 한국산업표준(KS B 6141)에 따른 공기필터를 갖추어야 하며, 여과 장치의 교체시기의 알림기능과 교체가 용이하도 록 한다. ③ 세대 내 기계환기설비에서 발생하는 소음의 측정은 국가표준규격 KSB6361 에 따른다. ④ 「주택건설기준 등에 관한 규정」 제 44 조에 따라 각 세대의 침실에 밀폐된 옷방 또는 붙박이 가구 를 설치하는 경우에는 배기설비 또는 통풍구를 설치해야 한다. 다만, 외벽 및 욕실에서 이격하여 설치하는 옷방 또는 붙박이 가구에는 배기설비 또는 통풍구를 설치하지 아니할 수 있다. ⑤ 실내공기질 관리를 위하여 온도, 습도, 이산화탄소, 미세먼지의 상태를 모니터링할 수 있는 설비 를 세대별 1 개소 이상 두어야 한다. ⑥ 주방의 환기량은 각 배기후드의 유효 환기량의 합계와 후드의 면풍속 0.3 m/s 이상 중 큰 값을 만족하도록 한다. ⑦ 주방 후드 등을 가동하여 실내오염물질을 배기하는 경우 부족한 외기량을 확보할 수 있도록 한 다. ⑧ 욕실의 전용배기는 다른 계통의 배기와 혼합하여 배출되지 않도록 한다. 입상 건식 덕트의 상부 캡은 풍압대의 영향을 받지 않도록 배치한다. 부득이한 경우에는 역압이 발생하여도 오염물질이 효과 적으로 배출될 수 있도록 강제배기 장치를 설치한다. ⑨ 욕실 배기덕트에는 세대별 역류방지댐퍼를 설치한다. 국토교통부 159 기계설비 기술기준 해설 (별표 03 | {}
2d32819b-8f89-4225-b44a-689ab55bad24 | 국내_기계설비_기술기준_매뉴얼_최종본 | 해 설 1. 본문 해설 및 관련 법규 V (1 항 1 호) 시간당 0.5 회 필요환기량 적용 대상은 다음과 같음 영 별표 5 제 2 호나목에 따른 아파트, 연립주택 나. 「건축법 시행령」 별표 1 제 2 호가목 및 나목에 따른 아파트 및 연립주택 「건축법 시행령」 별표 1 제 2 호가목 및 나목 2. 공동주택[공동주택의 형태를 갖춘 가정어린이집·공동생활가정·지역아동센터 · 공동육아나눔터 · 작은 도서관·노인복지시설(노인복지주택은 제외한다) 및 「주택법 시행령」 제 10 조제 1 항제 1 호에 따른 원룸 형 주택을 포함한다]. 다만, 가목이나 나목에서 층수를 산정할 때 1 층 전부를 필로티 구조로 하여 주 차장으로 사용하는 경우에는 필로티 부분을 층수에서 제외하고, 다목에서 층수를 산정할 때 1 층의 전 부 또는 일부를 필로티 구조로 하여 주차장으로 사용하고 나머지 부분을 주택 외의 용도로 쓰는 경우 에는 해당 층을 주택의 층수에서 제외하며, 가목부터 라목까지의 규정에서 층수를 산정할 때 지하층 을 주택의 층수에서 제외한다. 가. 아파트: 주택으로 쓰는 층수가 5 개 층 이상인 주택 나. 연립주택: 주택으로 쓰는 1 개 동의 바닥면적(2 개 이상의 동을 지하주차장으로 연결하는 경우에는 각각의 동으로 본다) 합계가 660 m2 를 초과 하고, 층수가 4 개 층 이하인 주택 「건축물의 설비기준 등에 관한 규칙」 제 11 조(공동주택 및 다중이용시설의 환기설비기준 등) ①영 제 87 조 제 2 항의 규정에 따라 신축 또는 리모델 링하는 다음 각 호의 어느 하나에 해당하는 주택 또는 건축물(이하 "신축공동주택등"이라 한다)은 시간당 0.5 회 이상의 환기가 이루어질 수 있도록 자연환기설비 또는 기계환기설비를 설치해야 한다. 1. 30 세대 이상의 공동주택 2. 주택을 주택 외의 시설과 동일건축물로 건축하는 경우로서 주택이 30 세대 이상인 건축물 V (1 항 2 호) 공기여과 장치 적용 표준은 다음과 같음 KS B 6141_환기용 공기 필터 유닛 이 표준은 빌딩, 공장, 사무실 등에서 공기 중에 부유하는 먼지를 제거하기 위하여 사용하는 공기 필터 중, 여과 재를 사용하여 먼지를 제거하는 환기용 공기 필터 유닛(이하, "필터 유닛"이라 한다.)에 대하여 규정한 다. V (1 항 3 호) 「건축물의 설비기준 등에 관한 규칙」 제 11 조제 3 항 및 별표 1 의 5 제 13 호의 기준과 이 기준의 55dB 이하 중 별표 1 의 5 제 13 호를 적용함 160 기계설비 기술기준 매뉴얼 | {}
8eeb0f78-46e1-42d7-8381-e0a682dc4517 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 「건축물의 설비기준 등에 관한 규칙」 제 11 조(공동주택 및 다중이용시설의 환기설비기준 등) ① 생략 ③신축공동주택등에 자연환기설비 또는 기계환기설비를 설치하는 경우에는 별표 1 의 4 또는 별표 1 의 5 의 기 준에 적합하여야 한다. [별표 1 의 5] 신축공동주택등의 기계환기설비의 설치기준(제 11 조제 3 항 관련) 13. 기계환기설비에서 발생하는 소음의 측정은 한국산업규격(KS B 6361)에 따르는 것을 원칙으로 한다. 측 정위치는 대표길이 1 m(수직 또는 수평 하단)에서 측정하여 소음이 40 dB 이하가 되어야 하며, 암소음(측 정대상인 소음 외에 주변에 존재하는 소음을 말한다)은 보정하여야 한다. 다만, 환기설비 본체(소음원)가 거주공간 외부에 설치될 경우에는 대표길이 1 m(수직 또는 수평 하단)에서 측정하여 50 dB 이하가 되거 나, 거주공간 내부의 중앙부 바닥으로부터 1.0 ~ 1.2 m 높이에서 측정하여 40 dB 이하가 되어야 한다. V (1 항 4 호) 「주택건설기준 등에 관한 규정」 제 44 조는 다음과 같으며 취기 배출, 습기 배출을 통한 결로 방지와 곰팡이 발생을 방지하기 위함 「주택건설기준 등에 관한 규정」 제 44 조(배기설비 등) ①주택의 부엌 · 욕실 및 화장실에는 바깥의 공기에 면하는 창을 설치하거나 국토교통 부령이 정하는 바에 따라 배기설비를 하여야 한다. ② 공동주택 각 세대의 침실에 밀폐된 옷방 또는 붙박이 가구를 설치하는 경우에는 그 옷방 또는 붙박이 가 구에 제 1 항에 따른 배기설비 또는 통풍구를 설치해야 한다. 다만, 외벽 및 욕실에서 떨어뜨려 설치하는 옷 방 또는 붙박이 가구에는 배기설비 또는 통풍구를 설치하지 않을 수 있다. ③법 제 40 조에 따라 공동주택의 각 세대에 설치하는 환기시설의 설치기준 등은 건축법령이 정하는 바에 의 한다. V (1 항 5 호) 미세먼지 등 실내공기질에 대한 관심과 중요성이 증가함에 따라 세대 입주민이 스스로 실내공기질 관리를 할 수 있도록 하는 최소한의 조치임 V (1 항 6 호) 추가 설명 없음 V (1 항 7 호) 에너지 절감, 연돌현상 방지 등의 이유로 건축물 기밀 성능이 크게 향상됨에 따라 주방 후드 가동 시 실내가 음압이 되고, 이를 보충하기 위한 외부공기가 충분하게 공급되지 못하여 배 기성능이 저하될 수 있음에 따라 초고층 건축물(층수가 50 층 이상 이거나 높이가 200m 이상)인 경우에는 기계적 수단을 이용하여 부족한 공기를 보충해야 함 V (1 항 8 호) 화장실의 공기배출 송풍기를 덕트를 이용하여 세탁실 또는 옷방 등 인접실에 연결할 경 우 화장실에서 발생하는 다량의 습기와 악취가 해당실에 전달하여 곰팡이 발생 등의 원인을 제공 할 수 있으며, 이때 외부 풍속에 의한 압력 변화에도 배출 성능이 저하되지 않아야 함 V (1 항 9 호) 욕실 배기는 인접실에 습기와 악취가 침입하지 못하도록 3 종 환기방식으로 하고, 공통 덕트방식일 경우에는 세대별로 역류방지댐퍼를 설치하여야 하며, 직배기방식일 경우에는 역류방 지캡을 설치하여야 함 욕실팬에 MD 가 부착된 경우에는 역류방지댐퍼가 설치된 것으로 간주함 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 유효 환기량 ¦ 급기량(m2/h)에서 누설량(m2/h)의 차이 풍량(m2/h) 출처 : KS B 6879:2020 열회수형 환기장치 해설 ¦ 국토교통부 161 기계설비 기술기준 해설 (별표 03 | {}
f27f92b8-ba2b-4d17-a6db-300a176cae7f | 국내_기계설비_기술기준_매뉴얼_최종본 | 2.1 설계기준(계속) 2.1.2 용도별 환기설비(계속) (2) 일반 건축물 ① 영 별표 5 에 따른 건축물 또는 시설물 중 공동주택 이외의 건축물 또는 시설물에는 기계환기설비 를 설치한다. ② 제 1 항에 따른 필요환기량은 25(m2/인 、 h)이상으로 한다. ③ 미세먼지 등 실내공기질에 관련된 사항은 「실내공기질관리법」, 「학교보건법」 등 관련 법령에서 규정한 적용대상과 실내공기질 기준에 따른다. ④ 필터가 부착된 기계환기설비의 환기장치는 미세먼지 측정값을 확인할 수 있는 센서를 통해 감지 된 데이터를 모니터링할 수 있도록 해야 한다. ⑤ 필터가 부착된 기계환기설비의 환기장치는 차압센서 등을 통해 감지한 미세먼지 값에 의해 공기 질을 제어할 수 있고, 필터의 교환 시기를 나타낼 수 있어야 한다. 해 설 1. 본문 해설 및 관련 법규 V (2 항 1 호) 「기계설비법 시행령」 제 11 조 관련 [별표 5]의 기계설비의 착공 전 확인과 사용 전 검사 의 대상 건축물 또는 시설물 중에서 시간당 0.5 회 기준을 적용받는 2 호 나목을 제외한 대상에는 환 기설비를 설치해야 함 V (2 항 2 호) 「건축물의 설비기준 등에 관한 규칙」 [별표 1 의 6] 기계환기설비를 설치해야 하는 다중이 용시설 및 각 시설의 필요환기량에서 정해지지 않은 건축물의 환기량은 25 m2/인 · h 이상으로 함 V (2 항 3 호) 「실내공기질관리법」의 적용대상 및 「학교보건법」 기준은 다음과 같음 「학교보건법 시행규칙」 [별표 2] 환기·채광·조명·온습도의 조절기준과 환기설비의 구조 및 설치기준 1. 환기 가. 환기의 조절기준 환기용 창 등을 수시로 개방하거나 기계식 환기설비를 수시로 가동하여 1 인당 환기량이 시간당 21.6 m2 이상이 되도록 할 것 나. 환기설비의 구조 및 설치기준(환기설비의 구조 및 설치기준을 두는 경우에 한한다) 1) 환기설비는 교사 안에서의 공기의 질의 유지기준을 충족할 수 있도록 충분한 외부공기를 유입하고 내 부공기를 배출할 수 있는 용량으로 설치할 것 2) 교사의 환기설비에 대한 용량의 기준은 환기의 조절기준에 적합한 용량으로 할 것 3) 교사 안으로 들어오는 공기의 분포를 균등하게 하여 실내공기의 순환이 골고루 이루어지도록 할 것 4) 중앙관리방식의 환기설비를 계획할 경우 환기덕트는 공기를 오염시키지 아니하는 재료로 만들 것 (2 항 4 호, 5 호) 「실내공기질관리법」의 적용대상으로 중앙환기 방식을 적용 시 미세먼지의 상태 및 이를 제거하는 필터의 유지관리 상태 등을 확인하고 관리하기 위함 2. 용어 V 내용 없음 162 기계설비 기술기준 매뉴얼 | {}
a7512b2e-dd48-4b3a-abc1-b585e7eee25b | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.1 설계기준(계속) 2.1.2 용도별 환기설비(계속) (3) 기계실, 전기실 등 ① 보일러실 · 냉온수기실의 환기 가. 보일러실 등 연소기기를 사용하는 실의 환기량은 장비 및 연도로부터의 방열량과 허용온도 및 장비의 연소 공기량을 고려해서 결정한다. 나. 하계에 연소기기를 사용하는 실 등은 외기 온도 조건을 고려해서 환기량을 결정한다. 다. 연소공기가 필요한 공간의 외기구 및 배기구는 다음에 따른다. (가) 연소공기의 외기구는 연소공기를 유효하게 얻을 수 있는 위치에 설치한다. (나) 배기구는 천장 근처에 설치한다. ② 냉동기실의 환기 가. 공기보다 무거운 냉매를 사용하는 냉동기실의 환기는 기계환기로 하고, 배기구는 누설된 냉 매가 유효하게 배출되도록 덕트방식으로 한다. 나. 냉매 배기용 흡입구 하단은 바닥면에서 300 ~ 500 mm 높이에 설치한다. ③ 발전기실의 환기 가. 발전기 운전 중 환기량은 장비의 방열량과 허용온도에 의해 계산된 값과 장비의 연소공기량을 고려해서 결정한다. 나. 환기처리에는 다음 사항을 고려한다. (가) 엔진 배기의 대기 방출구는 급기 취입구로부터 배기가스가 재순환 되지 않는 위치를 선정 하고, 빗물이 침입하지 않도록 한다. 또한 망을 부착하여 이물질 침입을 방지한다. (나) 엔진 주변은 상시 강제환기를 하고, 만일 연료가 새더라도 연료가 체류하지 않고 안전하 게 배출할 수 있도록 한다. (다) 배기구는 엔진이 위치한 장소의 상부에 설치하고, 급기구는 발전기가 위치한 장소의 하부 에 설치한다. (라) 발전기가 운전하고 있지 않을 때에도 최소 환기량을 확보한다. ④ 전기실의 환기 가. 전기실의 환기량은 장비의 발열량과 허용온도에 의해 구한다. 나. 급배기 송풍기는 실내 온도감지기로 자동 운전하도록 한다. 또한, 급기 쪽에는 필터 부착을 권 장한다. ⑤ 엘리베이터 기계실의 환기 가. 엘리베이터 기계실의 환기량은 기계의 발열량을 포함한 취득 열량과 허용온도에 의해 구한 다. 나. 환기량 산정에 사용하는 외기온도는 [별표 1] 표 2 에 따른다. 다. 엘리베이터 기계실의 환기용 송풍기는 실내 온도 감지기에 의해 자동운전되는 것으로 설치하 며, 급기 쪽에는 필터 부착을 권장한다. 라. 엘리베이터 기계실에 기계환기 설비를 설치할 경우에는 제어반의 상부 등 발열이 많은 부위에 서는 배기를 한다. 해 설 국토교통부 163 기계설비 기술기준 해설 (별표 03 | {}
b1f6a4c9-29bd-4b7d-96fb-9b7a69e60045 | 국내_기계설비_기술기준_매뉴얼_최종본 | 1. 본문 해설 및 관련 법규 V (3 항 1 호 가) 보일러실 등 연소기기를 사용하는 실은 보일러 등의 연소로 인해 실내 산소가 부족하 지 않도록 충분한 외기 도입이 가능하도록 해야 함 V (3 항 1 호 나) 하계 외기 온도가 높으므로 (3 항 5 호 가) 엘리베이터 기계실의 환기량 산정에 사용하 는 외기온도 [별표 1] 표 2 에 따라 보일러의 발열량을 포함한 취득 열량과 허용온도(40°C)에 의해 구함 V (3 항 1 호 다 (가)) 연소공기가 필요한 공간의 외기구는 외기 도입이 쉬운 위치에 배치하거나 덕트 를 설치하는 경우에는 외기 도입에 방해를 받지 않도록 경로를 단순하게 설치해야 함 V (3 항 1 호 다 (나)) 연소공기가 필요한 공간의 배기구는 연소 가스 등이 실내에 머무르지 못하도록 거주영역보다 높게 설치해야 함 V (3 항 2 호 가, 나) 냉동기 냉매의 비중에 따라, 공기보다 무거운 냉매의 냉동기실 배기용 흡입구는 바닥면에서 300~500 mm 높이에 설치하며, 공기보다 가벼운 냉매의 경우는 연소기기 기준에 준 하여 배기구를 설치함 V (3 항 3 호 가) 추가 설명 없음 V (3 항 3 호 나 (가)(나)) 추가 설명 없음 V (3 항 3 호 나 (다)) 발전기실 공기의 부력에 의한 원활한 자연환기가 되도록 배기구는 상부, 급기구 는 하부에 설치하지만, 배기구까지 배기관 또는 배기덕트를 설치할 경우 급·배기구 위치제한 기 준 제외 가능함. 다만 배기덕트를 설치할 경우 급·배기구 위치를 다르게 할 수 있음 V (3 항 3 호 나 (라)) 발전기실은 연소로 인해 실내 산소가 부족하지 않도록 충분한 외기 도입이 가능 하도록 해야 함 V (3 항 4 호 가, 나) 전기실의 환기량은 해당실의 장비 발생열로 인하여 관련한 전기 부품이 과열되 어 오작동이 발생하지 않도록, 허용된 온도 조건을 고려하기 위해 온도감지기를 이용한 자동운전 을 실시하며, 급기되는 공기 중 먼지 등으로 인한 합선 등을 방지하기 위해 필터 부착을 권장함 V (3 항 5 호 가, 다) 엘리베이터 기계실의 환기량은 해당실 기계의 발생열로 인하여 기계장치의 오작 동이 발생하지 않도록, 허용된 온도 조건(5~40°C)을 고려하기 위해 온도감지기를 이용한 자동운 전을 실시하며, 급기되는 공기 중 먼지 등으로 인한 오작동 등을 방지하기 위해 필터 부착을 권장 함. 환기가 불가능한 엘리베이터 기계실의 경우에는 에어컨을 이용하여 온도를 제어할 수 있음 V (3 항 5 호 나) 환기량 산정에 사용하는 외기온도 164 기계설비 기술기준 매뉴얼 | {}
d7a22e17-f65c-48dc-b238-a63ebb98bd0b | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 [별표 1] 표 2 냉·난방설비의 용량계산을 위한 설계 외기온.습도 기준 ¦ 구 분 ¦ 냉 방 ¦ 냉 방 ¦ 난 방 ¦ 난 방 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도시명 ¦ 건구온도(°C) ¦ 습구온도(°C) ¦ 건구온도(°C) ¦ 상대습도(%) ¦ ¦ 서 울 ¦ 31.2 ¦ 25.5 ¦ -11.3 ¦ 63 ¦ ¦ 인 천 ¦ 30.1 ¦ 25.0 ¦ -10.4 ¦ 58 ¦ ¦ 수 원천 ¦ 31.2 ¦ 25.5 ¦ -12.4 ¦ 70 ¦ ¦ 춘 ¦ 31.6 ¦ 25.2 ¦ -14.7 ¦ 77 ¦ ¦ 강 릉 ¦ 31.6 ¦ 25.1 ¦ -7.9 ¦ 42 ¦ ¦ 대 전주 ¦ 32.3 ¦ 25.5 ¦ -10.3 ¦ 71 ¦ ¦ 청 ¦ 32.5 ¦ 25.8 ¦ -12.1 ¦ 76 ¦ ¦ 전 주 ¦ 32.4 ¦ 25.8 ¦ - 8.7 ¦ 72 ¦ ¦ 서 산 ¦ 31.1 ¦ 25.8 ¦ - 9.6 ¦ 78 ¦ ¦ 광 주 ¦ 31.8 ¦ 26.0 ¦ - 6.6 ¦ 70 ¦ ¦ 대 구 ¦ 33.3 ¦ 25.8 ¦ - 7.6 ¦ 61 ¦ ¦ 부 산주 ¦ 30.7 ¦ 26.2 ¦ - 5.3 ¦ 46 ¦ ¦ 진 ¦ 31.6 ¦ 26.3 ¦ - 8.4 ¦ 76 ¦ ¦ 울 산 ¦ 32.2 ¦ 26.8 ¦ - 7.0 ¦ 70 ¦ ¦ 포 항 ¦ 32.5 ¦ 26.0 ¦ - 6.4 ¦ 41 ¦ ¦ 목 포 ¦ 31.1 ¦ 26.3 ¦ - 4.7 ¦ 75 ¦ ¦ 제 주 ¦ 30.9 ¦ 26.3 ¦ 0.1 ¦ 70 ¦ (3 항 5 호 라) 추가 설명 없음 2. 용어 내용 없음 2.1 설계기준(계속) 2.1.2 용도별 환기설비(계속) (4) 지하주차장 ① 주차장의 환기방식은 덕트방식 또는 유인유도 환기방식 등을 적용할 수 있다. ② 주차장의 환기는 배기가스가 허용농도 이상으로 체류하지 않도록 급 , 배기구를 설치한다. 주차 장 공기가 건물로 유입되지 않도록 한다. ③ 제연겸용 환기송풍기는 화재시를 대비하여 250°C 에서 60 분 이상 가동이 가능하도록 설치한다. ④ 급배기 송풍기는 주차장 내 CO 감지기에 의한 자동운전이 가능하도록 하고 미세먼지 감지기에 의한 자동운전을 권장한다. ⑤ 주차장이 외기에 면하는 경우 자연환기를 우선적으로 고려하여 환기설비를 계획한다. 해 설 1. 본문 해설 및 관련 법규 V (4 항 1 호) 이 기준에 명시된 방식 이외 이 기준 제 23 조에 따른 신기술 신공법으로 인정한 방식인 국토교통부 165 기계설비 기술기준 해설 (별표 03 | {}
ecfb6c24-1421-47a5-9768-87fd36d59c48 | 국내_기계설비_기술기준_매뉴얼_최종본 | 경우 적용이 가능함 (4 항 2 호) 「주차장법」 상 배기가스 허용농도는 다음과 같으나, 지방자치단체별로 일산화탄소 기 준이 다르므로 조례를 확인하여 적용하여야 함(예: 서울시, 경기도는 20 ppm) 「주차장법 시행규칙」 제 6 조제 1 항제 8 호 노외주차장 내부 공간의 일산화탄소 농도는 주차장을 이용하는 차량이 가장 빈번한 시각의 앞뒤 8 시간의 평 균치가 50 ppm 이하 「다중이용시설 등의 실내공기질관리법」 제 3 조 제 1 항 제 9 호에 따른 실내주차장은 25ppm 이하)로 유지되어야 한다. 「실내공기질 관리법 시행규칙」 ¦ 오염물질 항목 다중이용시설 ¦ 실내공기질 유지기준(제 3 조 관련) ¦ 실내공기질 유지기준(제 3 조 관련) ¦ 실내공기질 유지기준(제 3 조 관련) ¦ 실내공기질 권고기준(제 4 조 관련) ¦ 실내공기질 권고기준(제 4 조 관련) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 오염물질 항목 다중이용시설 ¦ 미세먼지 (PM-10) (�g/m2) ¦ 폼알데하이드 (�g/ m2) ¦ 일산화탄소 (ppm) ¦ 이산화질소 (ppm) ¦ 총휘발성 유기화합물 (�g/m2) ¦ ¦ 다. 실내주차장 ¦ 200 이하 ¦ 100 이하 ¦ 25 이하 ¦ 0.30 이하 ¦ 1 000 이하 ¦ V (4 항 3 호) 제연겸용 환기송풍기 적용 시 화재안전기준(NFSC501)에 적합하게 설치되어야 함 V (4 항 4 호, 5 호) 추가 설명 없음 2. 용어 내용 없음 2.1 설계기준(계속) 2.1.2 용도별 환기설비(계속) (5) 주방 ① 주방의 조리용 기구 등과 같이 개방식으로 연소기구가 설치되는 공간은 독립하여 배출하는 국소 배기덕트를 설치하고, 그 배기는 직접 옥외에 배출시켜야 한다. ② 주방과 같이 화기를 사용하는 실 등은 기계환기를 적용하고, 연소기구의 상부에는 가스를 포집 할 수 있는 후드를 설치하며, 배기후드의 목 또는 덕트에는 적절한 위치에 풍량조절 댐퍼를 설치 한다. ③ 환기구는 연소를 방해하지 않는 위치에 설치한다. 환기구의 크기는 환기송풍기의 배기능력을 유 지할 수 있는 개구면적 이상으로 한다. ④ 오염물질이나 취기가 인접실로 유출되지 않도록 한다. 해 설 1. 본문 해설 및 관련 법규 (5 항 1 호) 주방 배기는 인접 건축물에 피해를 주지 않도록 건축물 상부 또는 탈취 후 옥외공간 에 배출해야 함 166 기계설비 기술기준 매뉴얼 | {}
cbd8b392-63aa-4295-87d8-bd5897dd60e5 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 V (5 항 2 호) 풍량조절 댐퍼는 배기팬 1 대로 여러 개소의 주방을 배기하는 경우에도 적용 가능함 V (5 항 3 호, 4 호) 환기구에 의한 불완전 연소로 추가적인 실내공기 오염물질이 발생하지 않도록 해 야 하며, 오염물질이나 취기가 인접실로 유출되지 않도록 충분히 음압을 유지할 수 있는 크기여 야 함 2. 용어 내용 없음 2.1 설계기준(계속) 2.1.2 용도별 환기설비(계속) (6) 탕비실 탕비실에 가스레인지를 설치하는 경우의 환기는 다음과 같이 한다. ① 연소기구에서 배기가스를 포집할 수 있는 후드를 설치하고 기계환기를 적용한다. 탕비실이 밀폐된 공간에 위치하는 경우, 급기구는 환기가 되는 공간에 접하도록 설치한다. 해 설 1. 본문 해설 및 관련 법규 V (6 항 1 호, 2 호) 추가 설명 없음 2. 용어 V 내용 없음 2.1 설계기준(계속) 2.1.2 용도별 환기설비(계속) (7) 수영장 ① 수영장에서는 수질유지를 위하여 물에 약품처리를 하므로 배기는 공기조화기의 회기(Return air, 공기조화기로 되돌아오는 공기)로 사용하지 않고 전배기해야 한다. ② 열교환기를 설치하는 경우 습기 재유입을 방지하기 위하여 현열교환기만 사용한다. ③ 배기덕트의 성능은 내습성, 내부식성을 고려하여 계획한다. 해 설 1. 본문 해설 및 관련 법규 국토교통부 167 기계설비 기술기준 해설 (별표 03 | {}
17c25d0d-64ee-4ddf-a063-63bde46562cf | 국내_기계설비_기술기준_매뉴얼_최종본 | (7 항 1 호) 수영장은 다량의 수증기뿐만 아니라 수처리를 위해 사용하는 염소가 수영장 내의 오염 물질과 반응하여 클로라민(Chloramine) 화합물이 생성되기 때문에 수영장 내부는 음압이 형성되 도록 하며, 재순환 및 인접실의 보충공기로의 사용을 금지해야 함 V (7 항 2 호, 3 호) 열교환기, 배기덕트를 포함하여 수영장의 각종 기계설비 부품은 수증기 및 각종 화 합물로 인한 곰팡이, 부식, 결로 등을 고려하여 선정해야 함 2. 용어 V 내용 없음 2.1 설계기준(계속) 2.1.2 용도별 환기설비(계속) (8) 정화탱크 ① 정화탱크 관리실은 음압이 유지될 수 있도록 급배기 시설을 하며, 배기 시에는 탈취설비를 계획 한다. ② 환기 미사용 시 역류방지를 위하여 역류방지댐퍼를 설치한다. ③ 정화탱크의 취기가 인접건물에 확산되지 않도록 환기를 계획한다. ④ 배기덕트와 송풍기의 성능은 내습성, 내부식성을 고려하여 계획한다. 해 설 1. 본문 해설 및 관련 법규 (8 항 1 호) 배기는 인접 건축물에 피해를 주지 않도록 건축물 상부 또는 탈취 후 옥외공간에 배출 해야 함 V (8 항 2 호 ~ 4 호) 추가 설명 없음 2. 용어 V 내용 없음 168 기계설비 기술기준 매뉴얼 | {}
ef5a69e3-b9a8-4127-86d8-5fd0d11f4a6e | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.1 설계기준(계속) 2.1.3 터널 환기설비 (1) 도로터널 ① 도로터널에서의 설계소요 환기량은 매연, 일산화탄소, 질소산화물 등의 오염물질을 대상으로 산 출하며, 오염물질별 허용농도기준을 만족해야 한다. ② 환기방식은 교통조건, 주변 환경조건, 화재 시 안전성, 지반조건, 유지관리, 경제성, 단계건설 등 을 종합 검토하여 선정한다. ③ 환기설비의 용량은 전 주행속도에서 소요 환기량을 만족할 수 있도록 계획하는 것을 원칙으로 한다. 가. 기계환기방식에서 환기설비 승압력을 최대로 요구하는 주행속도는 환기설비설계속도로 한 다. 나. 지체 시 환기설비용량이 과도하게 증가하는 경우에는 가스상물질(CO, NOx)만을 환기대상물 질로 고려할 수 있다. 다. 터널 내를 흐르는 차도 내 풍속은 일방향 터널인 경우는 10 m/s 이하로 하고, 양방향 터널인 경우는 8 m/s 이하로 한다. 라. 추정교통량이 현저하게 작은 경우나 지방부 터널의 경우 주행속도가 높고, 지정체 발생확률 이 낮은 경우에는 환기검토 제외속도를 적용하여 환기시스템을 설계할 수 있다. 마. 터널 내 소요환기량의 급격한 증가에 대처하기 위하여 시간당 최소 3 회 이상의 공기치환 횟수 를 고려하며, 1 km 이상의 종류식(종방향으로 유인하는 방식) 터널 내 최소 환기속도를 1.5 m/s 이상 확보할 수 있도록 환기풍량을 고려한다. ④ 환기설비는 화재 발생 시에는 제연이나 배연설비로 운영되므로 환기방식의 선정 단계부터 비상 시 안전성에 대하여 고려해야 하며, 제연을 위한 환기설비용량이 평상시 환기용량을 초과 하는 경우에는 제연용량으로 환기설비용량을 결정한다. 해 설 1. 본문 해설 및 관련 법규 V 도로터널은 이 기준에 명시된 것 외에 다음의 내용을 참조할 수 있음 국토교통부 169 기계설비 기술기준 해설 (별표 03 | {}
e3d2f02e-1c3b-4355-a059-7647a79faed0 | 국내_기계설비_기술기준_매뉴얼_최종본 | 「도로의 구조 · 시설 기준에 관한 규칙」 제 42 조(터널의 환기시설 등) ① 터널에는 안전하고 원활한 교통 소통을 위하여 필요하다고 인정되는 경우에 는 도로의 설계속도, 교통 조건, 환경 여건, 터널의 제원 등을 고려하여 환기시설 및 조명시설을 설치하여 야 한다. ② 화재나 그 밖의 사고로 인하여 교통에 위험한 상황이 발생될 우려가 있는 터널에는 소화설비, 경보설비, 피난설비, 소화활동설비, 비상전원설비 등의 방재시설을 설치하여야 한다. ③ 터널 안의 일산화탄소 및 질소산화물의 농도는 다음 표의 농도 이하가 되도록 하여야 하며, 환기 시의 터 널 안 풍속이 초속 10 m 를 초과 하지 아니하도록 환기시설을 설치하여야 한다. ¦ 구분 ¦ 농도 ¦ ¦ --- ¦ --- ¦ ¦ 일산화탄소 ¦ 100 ppm ¦ ¦ 질소화합물 ¦ 25 ppm ¦ 도로설계편람 터널편 617 환기시설, 2011 http://blow.blo.ck.cloppainted/BisteRh/BAntoutd. InJiangetilky elndex=1&sType=RefTypeAll 「도로터널 방재시설 설치 및 관리지침」 https://www.col.com/BeailAnkGuice.cp/hsfrne-295 2. 용어 V 내용 없음 2.1 설계기준(계속) 2.1.3 터널 환기설비(계속) (2) 철도터널 ① 오염물질 배출차량이 운행되는 경우에는 호흡과 관련된 일산화탄소, 질소산화물, 분진농도를 환 기대상 오염물질로 한다. ② 터널의 환기계획은 교통, 기상, 환경, 지형, 지물 및 관련 법규를 바탕으로 소요 환기량을 산정하 여 자연환기와 기계환기 중 적합한 방법을 선정한다. ③ 환기설비가 설치될 경우에는 비상시 승객이 안전하게 대피할 수 있도록 대피방향으로 신선외기 를 공급하고 발생 매연을 신속하게 배출하여 터널 내 환경을 회복할 수 있도록 환기용량을 계획 한다. ④ 상시 환기요소 인자를 검토, 분석하고 열차의 교통환기력에 의한 자연환기량을 산출한 결과 와 비교하여 경제적이고 신뢰성이 높은 환기방식 및 기기용량, 규모 등을 결정한다. 해 설 1. 본문 해설 및 관련 법규 170 기계설비 기술기준 매뉴얼 | {}
129881cc-7973-45ea-b88c-882e202ba0fc | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 철도터널은 이 기준에 명시된 것 외에 다음의 내용을 참조할 수 있음 「철도시설의 기술기준」 제 2 장 고속일반광역철도 제 2 절 선로시설 제 4 관 터널 제 29 조(일반기준) ① 터널은 열차가 안전하게 운행할 수 있도록 안전성 및 내구성을 갖추어야 한다. ② 터널에서 차량운행조건 및 기반시설 등에 대한 종합적인 안전성 분석을 하여 방재대책을 수립하여야 한 다. ③ 터널의 기울기는 원활한 배수가 가능하도록 하여야 하고, 출입구, 환기구 및 비상탈출구 등으로 빗물이 유입되지 않아야 한다. 제 42 조(제연·배연설비) ① 본선 터널에 대한 안전성 분석결과 에 따라 제연·배연설비가 필요한 경우에는 다음 각 호에 따라 설치하여야 한다. 1. 제연설비는 화재가 발생한 경우에 유독가스가 진입지역으로 급격히 확산되지 않도록 제어될 것 2. 배연설비는 화재가 발생한 경우에 유독가스의 배출방향·속도 등을 제어하여 유독가스가 밖으로 배출시킬 수 있을 것 3. 본선 터널 바닥면과 연결되어 있는 환기구를 대피통로로 사용하는 경우 배연설비는 비상시 승객 및 승무 원이 신속히 대피할 수 있는 구조로 설치할 것 4. 배연설비의 전원은 서로 다른 두 개의 회로에서 공급되어야 하고, 역회전이 가능한 송풍기를 2 대 이상 분 할하여 설치할 것 5. 환기 및 제연·배연 기능이 겸용인 설비는 비상시 충분한 기능을 발휘할 수 있도록 할 것 6. 제연·배연설비는 열차가 정상 운행할 경우 열차풍압에 의한 구조적 안전성 및 성능을 확보할 것 7. 제연·배연설비 중에서 전동기, 배풍기, 배출풍도 및 배풍막(배풍기와 배출풍도를 연결하는 막을 말한다)과 관련 부품, 동력전달기구 등은 250 °C 에서 1 시간 이상 정상적으로 기능을 유지할 것. 다만, 배풍기와 분리 설치되어 배출가스의 영향을 받지 않는 전동기는 그러하지 아니하다. ② 본선 터널 바닥과 연결되어 있는 환기구를 대피통로로 사용하는 경우에는 내화구조물로 구획되어야 하 며, 배연설비는 비상시 승객 및 승무원 등이 신속히 대피할 수 있는 구조로 설치하여야 한다. 「철도시설의 기술기준」 제 3 장 도시철도 제 1 절 선로시설 제 2 관 터널 제 123 조(일반기준) ① 터널은 충분한 내구성을 갖추어야 한다. ② 지하터널에는 역 출입구, 환기구 및 비상탈출구 등을 통하여 노면수가 유입되지 않아야 한다. 2. 용어 V 내용 없음 기계설비 기술기준 해설 (별표 03 국토교통부 171 | {}
abf57601-29e0-4775-89ce-9351c091445c | 국내_기계설비_기술기준_매뉴얼_최종본 | 2.1 설계기준(계속) 2.1.4 공동구 (1) 공동구 내 설치되는 배관 배선 시설물의 기능을 양호하게 유지하고 유지관리가 용이하도록 적정 온도 유지, 결로 방지, 유해가스 및 악취제거 등의 목적으로 환기설비를 설치한다. (2) 전력이송용 공동구나 통신용 공동구인 경우도 각 케이블에서 발생되는 열을 냉각하기 위하여 환 기되어야 하며, 여름철에도 공동구 내의 온도는 40°C 이상 상승되지 않도록 한다. (3) 제연겸용 환기송풍기는 화재시를 대비하여 250°C 에서 60 분 이상 가동이 가능한 기능을 보유해 야 된다. 또한 비상시를 위하여 공동구 내 환기는 정 , 역방향으로 공기흐름을 조정 할 수 있어야 한다. (4) 환기설비의 용량은 가동 후 시간당 2 회 이상 환기가 완료될 수 있는 용량이어야 하며, 현장 여건 에 따라 적정 용량을 산정한다. 발열이 있는 전력구의 경우 전력구 내 환기풍속은 2 m/s 이하, 환 기구 그레이팅 상부에서의 풍속은 5 m/s 이하로 한다. (5) 환기방식은 원칙적으로 종류식을 적용해야 하며, 현장 여건상 부득이한 경우 덕트방식으로 시공 한다. (6) 환풍기는 환기구 그레이팅 상부 0.5(또는 1 m)에서의 소음을 75 dB(A) 이하로 하며, 주변 지역에 대해 「환경정책기본법」 시행령」 [별표 1]의 환경기준을 준수할 수 있도록 필요시 소음저감장치를 설치한다. (7) 공동구의 지상 환기구는 250 m 이내의 간격으로 설치하되 환기시뮬레이션을 수행하여 설치 간 격을 결정할 수 있으며, 지상 환기구를 이용하여 공동구 내로 장비반입 및 관리자가 입출 가능하 도록 계획한다. 해 설 1. 본문 해설 및 관련 법규 V 해당 기준은 공동구 전용 공사 등에 적용하며, 공동주택 공동구에는 해당하지 않음 V (1 항, 2 항, 4 항, 5 항, 7 항) 추가 설명 없음 V (3 항) 제연겸용 환기송풍기는 「화재안전기준」(NFSC 501)에 적합해야 함 V (6 항) 「환경정책기본법」 시행령」[별표 1] 환경기준 172 기계설비 기술기준 매뉴얼 | {}
72ff990e-507f-4e66-9ad0-4e119c039435 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 「환경정책기본법 시행령」 [별표 1] 환경기준 2. 소음 (단위: Leq dB(A)) ¦ 지역 구분 ¦ 적용 대상지역 ¦ 기준 ¦ 기준 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 지역 구분 ¦ 적용 대상지역 ¦ 낮 (06 : 00 ~ 22 : 00) ¦ 밤 (22 : 00 ~ 06 : 00) ¦ ¦ 일반 지역 ¦ "가"지역 ¦ 50 ¦ 40 ¦ ¦ 일반 지역 ¦ "나"지역 ¦ 55 ¦ 45 ¦ ¦ 일반 지역 ¦ "다"지역 ¦ 65 ¦ 55 ¦ ¦ 일반 지역 ¦ "라"지역 ¦ 70 ¦ 65 ¦ ¦ 도로변 지역 ¦ "가" 및 "나"지역 ¦ 65 ¦ 55 ¦ ¦ 도로변 지역 ¦ "다"지역 ¦ 70 ¦ 60 ¦ ¦ 도로변 지역 ¦ "라"지역 ¦ 75 ¦ 70 ¦ 비고 1. 지역구분별 적용 대상지역의 구분은 다음과 같다. 가. "가"지역 1) 「국토의 계획 및 이용에 관한 법률」 제 36 조제 1 항제 1 호라목에 따른 녹지지역 2) 「국토의 계획 및 이용에 관한 법률」 제 36 조제 1 항제 2 호가목에 따른 보전관리지역 3) 「국토의 계획 및 이용에 관한 법률」 제 36 조제 1 항제 3 호 및 제 4 호에 따른 농림지역 및 자연환경보전지역 4) 「국토의 계획 및 이용에 관한 법률 시행령」 제 30 조제 1 호가목에 따른 전용주거지역 5) 「의료법」 제 3 조제 2 항제 3 호마목에 따른 종합병원의 부지경계로부터 50 m 이내의 지역 6) 「초·중등교육법」 제 2 조 및 「고등교육법」 제 2 조에 따른 학교의 부지경계로부터 50 m 이내의 지역 7) 「도서관법」 제 2 조제 4 호에 따른 공공도서관의 부지경계로부터 50 m 이내의 지역 나. "나"지역 1) 「국토의 계획 및 이용에 관한 법률」 제 36 조제 1 항제 2 호나목에 따른 생산관리지역 2) 「국토의 계획 및 이용에 관한 법률 시행령」 제 30 조제 1 호나목 및 다목에 따른 일반주거지역 및 준주거지역 다. "다"지역 1) 「국토의 계획 및 이용에 관한 법률」 제 36 조제 1 항제 1 호나목에 따른 상업지역 및 같은 항 제 2 호다목에 따른 계획관리지역 2) 「국토의 계획 및 이용에 관한 법률 시행령」 제 30 조제 3 호다목에 따른 준공업지역 라. "라"지역 「국토의 계획 및 이용에 관한 법률 시행령」 제 30 조제 3 호가목 및 나목에 따른 전용공업지역 및 일반공업지역 2. "도로"란 자동차(2 륜자동차는 제외한다)가 한 줄로 안전하고 원활하게 주행하는 데에 필요한 일정 폭의 차선이 2 개 이상 있는 도로를 말한다. 3. 이 소음환경기준은 항공기소음, 철도소음 및 건설작업 소음에는 적용하지 않는다. 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 종류식 환기방식 ¦ 터널입구 또는 연직갱, 경사갱 등으로부터 신선공기를 유입하여 종방향 기류를 형성 하여 터널출구 또는 연직갱, 경사갱 등으로 오염된 공기 또는 화재연기를 배출하는 방식을 말한다. 출처 : 서울시 도로터널 환기기준 개정(안), 터널 환기 및 방재 기술위원회, 2017 ¦ 2.2 송풍기 (1) 장비일람에 송풍기의 형식과 규격, 풍량, 정압(Pa), 회전수, 동력, 전원(전압, 상, 주파수), 재질 등 을 명기한다. (2) 송풍기의 형식은 정압과 풍량을 기준으로 효율이 높은 것으로 선정한다. 기계설비 기술기준 해설 (별표 03 국토교통부 173 | {}
cf4d652d-21e6-4a15-a0b8-19277b014383 | 국내_기계설비_기술기준_매뉴얼_최종본 | 해 설 1. 본문 해설 및 관련 법규 V (1 항) 송풍기 공사를 완료한 후, 기계설비시공자가 송풍기의 형식과 규격, 풍량, 정압(Pa), 회전수, 동력, 전원(전압, 상, 주파수), 재질 등의 정보를 이 기준 제 15 조 및 「기계설비 유지관리기준」 제 6 조 유지관리지침서에 반영할 수 있도록 해당 정보를 정확히 기록해야 함 V (2 항) 추가 설명 없음 2. 용어 V 내용 없음 2.3 환기장치 장비일람에 사용용도, 형식, 용량, 냉 , 난방 열교환 효율(폐열회수환기장치인 경우에 해당한다)을 기입해야 하며, 환기장치 설치에 따른 환기부하를 공기조화설비 장비용량에 반영해야 한다. 해 설 1. 본문 해설 및 관련 법규 V 환기 장치 공사를 완료한 후, 기계설비시공자가 사용용도, 형식, 용량, 냉 · 난방 열교환 효율 등의 정보를 이 기준 제 15 조 및 「기계설비 유지관리기준」 제 6 조 유지관리지침서에 반영할 수 있도록 해당 정보를 정확히 기록해야 함 환기설비와 공기조화설비가 함께 설치되어 운영할 경우에는 환기로 인한 실내 열손실 또는 취득 이 발생할 수 있으므로 이를 공기조화설비 장비용량에 반영해야 함 2. 용어 V 내용 없음 174 기계설비 기술기준 매뉴얼 | {}
5b6625ff-8f80-4a5d-8d32-35e7be2d235a | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 3. 환기설비 시공 3.1 송풍기 (1) 바닥설치형일 때에는 콘크리트기초 또는 형강제 베드 위에 직접 고정하거나 방진재를 사용하여 방진구조 위에 설치한다. (2) 천장걸이형일 때에는 송풍기의 운전중량에 충분히 견딜 수 있는 구조와 강도를 가진 형강제 철물 을 이용하여 건물 구조물에 견고히 고정시키고, 필요시 방진재를 사용하여 진동의 전달을 방지한 다. (3) 덕트와 접속하는 송풍기의 흡입측과 토출 측에는 플렉시블 이음을 한다. (4) 환기 및 제연겸용으로 사용하는 송풍기(지하주차장 등)는 필요에 따라 풍량을 자동조절하거나, 대수제어가 가능하도록 환기시스템을 구성한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항, 2 항) 바닥설치형 및 천장걸이형 모두 이 기준 [별표 12]의 관련 내용을 참조하여 시공함 V (3 항) 송풍기의 진동이 실내에 전파되는 것을 방지해야 함 V (4 항) 화재시 발생하는 대량의 연기를 신속히 외부로 배출할 수 있는 용량을 설치해야 하며, 평상 시에는 환기용으로 사용할 수 있어야 함 2. 용어 내용 없음 ---- --- 3.2 환기장치 (1) 창문형 열회수형 환기장치는 창문틀 또는 벽에 설치하며, 보수와 점검 등이 쉽도록 설치한다. (2) 덕트형 열회수형 환기장치는 공기여과 재 및 송풍기모터의 교체가 쉽도록 점검구를 설치한다. (3) 덕트형 열회수형 환기장치에 분배기를 설치하는 경우는 그 하부에 점검구를 설치한다. (4) 덕트형 열회수형 환기장치 가동에 의한 [별표 12] 표 1 실내허용소음기준을 초과 하지 않도록 한 다. (5) 덕트형 및 창문형 열회수형 환기장치가 정지할 때에는 자동으로 공기 유입 및 배출을 차단하는 댐퍼를 설치한다. (6) 열회수형 환기장치 급배기 디퓨저는 주방 및 화장실 배기시스템에서 배출되는 오염물질이 원활 하게 배출될 수 있도록 간섭이 없게 설치한다. 해 설 1. 본문 해설 및 관련 법규 기계설비 기술기준 해설 (별표 03 국토교통부 175 | {}
30ebd416-88dd-4141-bfcf-9f498763363b | 국내_기계설비_기술기준_매뉴얼_최종본 | (1 항) 환기장치를 창문틀 또는 벽에 설치하는 경우 설치된 틈 사이로 누기가 발생하지 않도록 해 야 함 V (2 항, 3 항) 이 기준 [별표 15] 기계설비 유지관리를 고려한 설계기준 2.4 점검구 등의 기준을 함께 검토해야 하며, 단, 분배기 부분의 점검구는 주거공간에 설치하는 경우에는 고려하지 않을 수 있 음 V (4 항) [별표 12] 표 1 실내허용소음기준은 다음과 같음 - 표 1 실내허용소음기준(KCS 31 50 10 05(1.1) 표 1.1-1) ¦ dB(A) ¦ 20 ¦ 25 ¦ 30 ¦ 35 ¦ 40 ¦ 45 ¦ 50 ¦ 55 ¦ 60 ¦ 70 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ NC ¦ 10-15 ¦ 15-20 ¦ 20-25 ¦ 25-30 ¦ 30-35 ¦ 35-40 ¦ 40-45 ¦ 45-50 ¦ 50-55 ¦ 60-65 ¦ ¦ 스튜 디오 ¦ 무향실 ¦ 아나운서 스튜디오 ¦ 라디오 스튜디오 ¦ TV 스튜디오 ¦ 주 조정실 ¦ 일반 사무실 ¦ ¦ ¦ ¦ ¦ ¦ 집회홀 ¦ ¦ 음악당 ¦ 극장 ¦ 무대극장 ¦ 영화관, 과학관 ¦ 영화관, 과학관 ¦ 로비 ¦ ¦ ¦ ¦ ¦ 병원 ¦ ¦ 청력 시험실 ¦ 특별 병실 ¦ 수술실 병원 ¦ 진찰실 ¦ 검사실 ¦ 대합실 ¦ ¦ ¦ ¦ ¦ 호텔 주택 ¦ ¦ ¦ ¦ 서재 ¦ 침실 객실 ¦ 연회장로비 ¦ 연회장로비 ¦ ¦ ¦ ¦ ¦ 일반 사무실 ¦ ¦ ¦ ¦ 중역실 대회의 실 ¦ 응접실 ¦ 소 회의 실 ¦ 일반사무실 ¦ 일반사무실 ¦ 전산실 ¦ ¦ ¦ 공공 건물 ¦ ¦ ¦ ¦ 공회당 ¦ 미술관 박물관 ¦ 도서 열람실 ¦ 체육관 ¦ 옥내스포츠시설 ¦ 옥내스포츠시설 ¦ ¦ ¦ 학교 교회 ¦ ¦ ¦ ¦ 음악 교실 ¦ 강당 예배당 ¦ 연구실, 보통교실 ¦ 연구실, 보통교실 ¦ 복도 ¦ 복도 ¦ ¦ ¦ 상업용 건물 ¦ ¦ ¦ ¦ ¦ 음악당, 서점 미술품점 ¦ 음악당, 서점 미술품점 ¦ 은행 레스토랑 ¦ 상점 식당 ¦ 공장 내 제어실 ¦ 공장 ¦ V (5 항) 환기장치 자체의 외부 공기 침입에 의한 에너지 낭비를 방지해야 함 V (6 항) 추가 설명 없음 2. 용어 V 내용 없음 176 기계설비 기술기준 매뉴얼 | {}
7228e96b-e35d-459c-bb7d-348507872502 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 [별표 4] 위생기구설비의 설계 및 시공 기준 1. 위생기구설비 일반사항 1.1 목적 이 기준은 건축물, 시설물 등에 거주하는 재실자의 위생을 위하여 필요한 각종 기구의 설계 및 시공 방법 등 세부 기술기준을 정함을 목적으로 한다. 해 설 이 기준의 목적은 「기계설비법」 제 14 조(기계설비 기술기준)과 같은 법 영 제 2 조 및 [별표 1]에 근 거하여, 건축물이나 시설물에 필요한 위생기구설비의 설계 및 시공 시 기계설비의 안전과 성능을 확보하기 위하여 필요한 기술적 요건을 규정하기 위함 「기계설비법」 제 14 조(기계설비 기술기준) ① 국토교통부장관은 기계설비의 안전과 성능확보를 위하여 필요 한 기술기준(이하 "기술기준이라 한다)를 정하여 고시하여야 한다. 이를 변경하는 경우에도 또한 같다. 1.2 적용범위 이 기준은 건축물, 시설물 등에 다음의 위생기구설비를 설치하는 경우에 대하여 적용한다. (1) 대소변기 (2) 세면기, 수세기, 세발기 (3) 싱크 (4) 욕조 및 샤워 (5) 음수기 (6) 비데 (7) 설비유닛 (8) 기타 위생기구 해 설 이 기준의 적용범위는 「기계설비법」 제 2 조제 1 호에 따른 건축물등에 같은 법 영 제 2 조에 따라 대 통령령으로 정한 위생기구설비를 설치하는 경우 및 그와 관련된 부속설비들을 포함함 「기계설비법」 제 2 조(정의) 1. "기계설비"란 건축물, 시설물 등(이하 "건축물등"이라 한다)에 설치된 기계 · 기 구 · 배관 및 그 밖에 건축물등의 성능을 유지하기 위한 설비로서 대통령령으로 정하는 설비를 말한다. 「기계설비법 시행령」 제 2 조(기계설비의 범위) 「기계설비법」(이하 "법"이라 한다) 제 2 조제 1 호에서 "대통령령 으로 정하는 설비"란 별표 1 의 설비를 말한다. 「기계설비법 시행령」 [별표 1] 기계설비의 범위 4. 위생기구 · 급수 · 급탕 · 오배수 · 통기설비 : 건축물등에서 위생과 냉수 · 온수 공급, 오배수(���), 통기 (通�) 등을 위하여 설치된 기계 · 기구 · 배관 및 그 밖에 성능을 유지하기 위한 설비 국토교통부 177 기계설비 기술기준 해설 (별표 04 | {}
94f28eda-41e9-4e73-8eb8-9e0dd078460d | 국내_기계설비_기술기준_매뉴얼_최종본 | 1.3 타 규정과 의 관계 다음의 규정과 이 기준에서 정하는 내용이 상이한 경우에는 해당 규정을 따른다. (1) KDS 31 30 10 위생기구 설비공사 해 설 V 이 기준과 타 규정 및 기준과 다른 경우에는 상기 규정에 명시된 내용을 따름 178 기계설비 기술기준 매뉴얼 | {}
1c0ccbb1-1404-435b-b671-6cfdeab1042f | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2. 위생기구설비 설계 2.1 일반사항 위생기구는 용도에 적합한 재료와 치수 및 구조로 하며, 성능기준을 만족하고 절수효과 와 설치장소 및 이용자의 편리성 등을 고려하여 결정한다. 해 설 1. 본문 해설 및 관련 법규 V 건축물의 용도에 따른 이용자 집단의 특성을 고려하여, 이용자의 편리성을 해치지 않으면서도 최 대의 성능과 절수효과 를 높일 수 있도록 위생기구설비를 선정하여 설계 및 시공해야 함 2. 용어 내용 없음 - 2.2 위생기구설비 2.2.1 위생기구 급수와 급탕을 동시에 공급하는 기구는 마주보아 왼쪽에 급탕이 공급되어야 한다. 2.2.2 대소변기 형식과 크기는 사용조건을 고려하여 정한다. 2.2.3 세면기 (1) 세면기 배수구는 DN 32 이상으로 하며, 배수금구는 십자형 스트레이너를 갖춘 마개부착식이나 폴업식으로 한다. (2) 수세기, 세발기는 세면기에 준한다. 2.2.4 싱크대 싱크대 배수구는 DN 40 이상으로 한다. 배수구가 완전 개방되지 않도록 스트레이너나 거름대를 설 계한다. 싱크대 배수금구는 스트레이너를 갖춘 마개 부착형으로 한다. 2.2.5 청소싱크 싱크는 300 mm 이상의 깊이로 하고, 배수트랩을 구비해야하며 배수구는 DN 40 이상으로 한다. 배 수금구는 마개를 부착해야 한다. 2.2.6 욕조 배수구는 DN 40 이상의 배수관에 연결한다. 배수구에는 수밀 마개를 구비한다. 2.2.7 음수기 음수기와 냉수기는 음용수배관에 사용하는 기기와 재질로 수질을 오염시키지 않는 구조와 재질로 한다. 2.2.8 비데 (1) 비데의 급수는 토수구공간이나 역류방지기로 역류를 방지하고, 비데에 공급되는 급수는 시수를 사용해야 하며, 중수는 사용해서는 안 된다. (2) 비데의 물 방출 최대온도는 43°C 이하로 제한한다. 2.2.9 위생설비 유닛 유비알(UBR; unit bath room), 유닛 토일렛(UT; unit toilet)등 위생설비 유닛은 공기의 단축, 공정 의 단순화, 시공 정밀도의 향상, 설비의 경량화 등을 고려하여 적용한다. 2.2.10 식기세척기 식기세척기의 배수는 간접배수로 한다. 2.2.11 세탁기 세탁기의 배수는 간접배수로 한다. 국토교통부 179 기계설비 기술기준 해설 (별표 04 | {}
88d0d803-6c86-4ca8-a78b-c67f9cc4a6dd | 국내_기계설비_기술기준_매뉴얼_최종본 | 해 설 1. 본문 해설 및 관련 법규 V (2.2.1) 위생기구 급수와 급탕을 동시에 공급하는 기구에서 급탕의 위치를 일관되게 설계하여 화 상 등의 안전사고를 예방해야 함 V (2.2.2) 대소변기는 건축물에 공급되는 급수의 수압, 건축물 용도 및 사용자 특성(고정 사용 또는 불특정 다수 사용 등) 등을 고려해야 함 V (2.2.3 1 항, 2 항) 세면기, 수세기, 세발기 등의 배수구를 통해 사용자가 착용한 소형 물품 등이 유 실되지 않도록 거름장치 등의 설치를 통해 미연에 방지해야 함 V (2.2.4) 싱크대는 일시에 많은 양의 물을 배수하므로 배수구는 DN 40 이상으로 하며, 세면기 등과 같이 사용자의 소형 물품 등이 유실되지 않도록 스트레이너 등의 설치를 통해 미연에 방지해야 함 V (2.2.5, 6) 청소싱크와 욕조 배수구는 일시에 많은 양의 물을 배수하므로 DN 40 이상의 배수관에 연결해야 함 V (2.2.7) 음수기와 냉수기에는 아연도강관 등과 같이 녹 등의 오염물질이 발생할 수 있는 재료의 사 용을 금지해야 함 V (2.2.8 1 항, 2 항) 비데의 물은 인체에 직접 닿기 때문에 시수와 같이 깨끗한 물을 공급해야 하고, 다른 계통의 배관과 혼합되지 않아야 하며, 화상에 의한 안전사고 방지를 위해 물 온도는 43°C 이 하로 제한해야 함 V (2.2.9) 추가 설명 없음 V (2.2.10, 11) 역류 발생 시 식기세척기 및 세탁기 내부 오염방지를 위함이며, 제품에 역류방지 기 능이 있는 경우에는 예외로 할 수 있음 2. 용어 V 내용 없음 -- --- 180 기계설비 기술기준 매뉴얼 | {}
0801f493-78bb-4fa2-aa8b-0f9cc1eb41f6 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 3. 위생기구설비 시공 3.1 일반사항 (1) 위생기구의 설치 위치와 높이에 따라서 토수구 공간을 확보한다. (2) 음수기의 배수는 간접배수로 하고 배수구 공간을 확보한다. (3) 도기의 일부를 콘크리트에 묻는 경우에는 신축에 의한 도기의 파손을 막기 위하여 콘크리트 또는 모르타르와 도기와 의 접촉면에 두께 3 mm 이상의 아스팔트나 그 밖의 방수 및 내식성 물질로 피 복을 한다. 단, 스톨형 소변기 등의 도기 밑부분 접촉면에는 모래 또는 동등 이상의 효과 를 가진 충진재를 채운다. (4) 기구에 접속한 실내에 노출되는 급수관, 급탕관, 세척관, 배수관이 벽이나 바닥을 관통하는 개소 에는 관좌금을 설치한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 위생기구의 최소 토수구 공간(A) ¦ 위생기구 ¦ 최소 토수구 공간 ¦ 최소 토수구 공간 ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 위생기구 ¦ 인접 벽의 영향이 없는 경우 1) ¦ 인접 벽의 영향이 있는 경우㉑ ¦ 측벽 C ¦ ¦ DN 15 이하의 세면기 ¦ 25 mm ¦ 38 mm ¦ 측벽 C ¦ ¦ DN 20 이하의 싱크, 세탁기 및 욕조 수도꼭지 ¦ 38 mm ¦ 57 mm ¦ 측벽 C ¦ ¦ DN 20 이하의 욕조 상부 붙이 욕조 혼합 수도꼭지 ¦ 50 mm ¦ 76 mm ¦ 측벽 C ¦ ¦ DN 25 이상의 유효 개구부 ¦ 유효개구부 지름 x 2 ¦ 유효개구부 지름 x 3 ¦ 측벽 C ¦ 주 1) 벽으로부터의 거리(그림의 C)가 인접 벽이 1 면인 경우는 토수구 내부의 가장자리에서 유효 개구부 지름의 3 배 이상 거리 또는 인접 벽이 2 면인 경우는 유효 개구부 지름의 4 배 이상 거리가 떨어져 있으면 측벽이나 이와 유사한 구조물은 토수구 공간에 영향을 주지 않으며 인접 벽의 영향이 없는 경우로 한다. 2) 수면에서부터 토수구 수평면이나 그 위까지 연장한 수직 벽이나 이와 유사한 구조물이 있는 경우 토수구의 내부 가장자리에서의 거리(그림의 C)가 주 (1)에서 정의 한 것보다 더 가까우면 토수구 공간은 인접 벽의 영향이 없는 경우보다 크게 한 인접 벽의 영향이 있는 경우로 한다. 3 면 이상의 수직 벽의 경우 토수구 공간은 벽 개구부 지름은 토수구 안지름, 수도꼭지 내부의 패킹 안지름 및 급수꼭지 접속관의 안지름 중 최소 3) 상북로부터 측정한다. 안지름을 말한다. 4) 토수구면이 오버플로우 면에 대해 평행하지 않은 경우는 토수구의 최하단과 위생기구나 물받이 용기의 물 넘침선과 의 공간을 토수구 공간으로 한다. 출처 : 토수구 공간의 설치 표준, 대한설비공학회, 2017, 07, 이용화 교수, 유한대학교 V (2 항) 배수 역류로 인한 음수기 오염 방지를 위함 V (3 항, 4 항) 추가 설명 없음 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 관좌금 ¦ 볼트나 너트로 물건을 죌 때, 너트 밑에 끼우는 둥글고 얇은 쇠붙이 또는 플라스틱 (해설서 주) ¦ 기계설비 기술기준 해설 (별표 04 국토교통부 181 | {}
d4710d77-6fe4-405f-91b5-6d6a384a4a4e | 국내_기계설비_기술기준_매뉴얼_최종본 | 3.2 위생기구설비 3.2.1 대변기 (1) 동양식 대변기의 설치 대변기에 스퍼드를 부착하여 고무패킹이 탄력성을 잃지 않을 정도로 조임너트를 조인다. 급수관이 매립되는 경우에는 배관 부속의 콘크리트 및 마감재 접촉부위에 탄력성이 있는 방수성 물질(아스팔 트 등)을 도장한다. (2) 서양식 대변기의 설치 ① 플랜지의 테이퍼 면과 일치되게 배수관을 확관하여 밀착시킨다. ② 플랜지에 볼트를 끼워 대변기를 가설하여 대변기 부착나사 위치를 정한다. 3.2.2 소변기 소정의 위치에 수평 또는 정확한 높이에 설치한다. 배수관과 의 접속은 소변기용 바닥 또는 벽 플랜지 를 사용하여 조임 볼트로 완전하게 접속한다. 3.2.3 세면기 세면기를 벽면에 밀착시킨 후 브래킷, 백 행거, 카운터 방식 등으로 견고하게 고정한다. 브래킷 고정 은 앵커볼트를 사용한다. 3.2.4 싱크대 싱크배수는 봉수기능이 있어야 하며, 배수호스와 주방 횡주배수지관과 의 연결부위는 기밀성이 확보 되어야 한다. 3.2.5 청소싱크 설치 위치 및 높이에 정확하게 백행거를 설치하고, 싱크의 윗면이 수평이 되도록 설치한다. 3.2.6 욕조 욕조는 바닥에 움직이지 않도록 견고하게 설치하고, 욕조 내 물을 배수 시 남지 않도록 구배를 맞추 어 배수구에 설치한다. 3.2.7 음수기 입형 또는 벽걸이형 설치 시 견고하게 설치하고 배수트랩을 설치한다. 3.2.8 비데 비데에 연결되는 급수관은 변기에 설치 시 움직이지 않도록 설치한다. 3.2.9 위생설비 유닛 유닛을 벽 및 바닥의 정확한 위치에 수평으로 설치하고, 유닛 등과 의 배관접속은 내압, 내구성, 내진 성 등을 고려하여 접속한다. 3.2.10 식기세척기 급수관에서 분기하여 식기세척기에 연결하고, 배수는 역류하지 않도록 설치한다. 3.2.11 세탁기 세탁기 설치 위치에 급수 、 급탕과 배수구를 설치하고, 배수배관은 역구배가 되지 않도록 설치한다. 3.2.12 욕실 및 화장실 비품 수건걸이, 비누갑, 컵걸이, 칫솔걸이, 휴지걸이, 옷걸이 등 각각의 목적에 적합하고 가장 편리한 위치 와 높이에 견고하게 설치한다. 3.2.13 장애인 시설 등 「장애인 、 노인 、 임산부 등의 편의 증진 보장에 관한 법률」에 따른다. 182 기계설비 기술기준 매뉴얼 | {}
2ad16baa-068a-43b4-b5fc-963602d60a94 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 해 설 1. 본문 해설 및 관련 법규 (3.2.1) 플렌지 연결부분의 누수발생여부 및 플렌지 볼트와 대변기의 고정여부를 확인함. 매립배 관에 탄력성 방수성물질 도장은 제외함 V (3.2.1 ~ 3.2.12) 추가 설명 없음 V (3.2.13) 「장애인 · 노인 · 임산부 등의 편의 증진 보장에 관한 법률」에 따름 「장애인 · 노인 · 임산부 등의 편의 증진 보장에 관한 법률 시행령 」 [별표 2] 대상시설별 편의 시설의 종류 및 설치기준(제 4 조관련) 2. 공원 ¦ 편의 시설의 종류 ¦ 설치기준 ¦ ¦ --- ¦ --- ¦ ¦ 다. 장애인 등의 이용이 가능한 화장실 ¦ 장애인 등이 편리하게 이용할 수 있도록 구조, 바닥의 재질 및 마감과 부 착물 등을 고려하여 설치하되, 장애인용 대변기는 남자용 및 여자용 각 1 개 이상을 설치하여야 하며, 영유아용 거치대 등 임산부 및 영유아가 안전하고 편리하게 이용할 수 있는 시설을 구비하여 설치하여야 한다. ¦ 3. 공공건물 및 공중이용시설 가. 일반사항 ¦ 편의 시설의 종류 ¦ 설치기준 ¦ ¦ --- ¦ --- ¦ ¦ (7) 장애인 등의 이용이 가능한 화장실 ¦ 장애인 등이 편리하게 이용할 수 있도록 구조, 바닥의 재질 및 마감과 부 착물 등을 고려하여 설치하되, 장애인용 대변기는 남자용 및 여자용 각 1 개 이상을 설치하여야 하며, 영유아용 거치대 등 임산부 및 영유아가 안전하고 편리하게 이용할 수 있는 시설을 구비하여 설치하여야 한다. ¦ ¦ (8) 장애인등의 이용이 가능한 욕실 ¦ 욕실은 1 개실 이상을 장애인등이 편리하게 이용할 수 있도록 구조, 바닥 의 재질 및 마감과 부착물등을 고려하여 설치하여야 한다. ¦ ¦ (9) 장애인등의 이용이 가능한 샤워실 및 탈의 실 ¦ 샤워실 및 탈의 실은 1 개이상을 장애인등이 편리하게 이용할 수 있도록 구조, 바닥의 재질 및 마감과 부착물 등을 고려하여 설치하여야 한다. ¦ 4. 공동주택 가. 일반 사항 ¦ 편의 시설의 종류 ¦ 설치기준 ¦ ¦ --- ¦ --- ¦ ¦ (7) 장애인 등의 이용이 가능한 화장실 및 욕실 ¦ 장애인전용주택의 화장실 및 욕실은 장애인등이 편리하게 이용할 수 있 도록 구조, 바닥의 재질 및 마감과 부착물 등을 고려하여 설치할 수 있다. ¦ 2. 용어 내용 없음 ¦ 용 어 ¦ 해 설 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 스퍼드 ¦ 대변기와 세정관을 접속하는데 사용되는 금구로 동양식 변기용과 서양식 변기용 2 종 있다. 출처 : 설비공학편람 제 5 권 1.8-5 ¦ ¦ ○ -○ 국토교통부 183 기계설비 기술기준 해설 (별표 04 | {}
b4d52c67-fc40-45b6-81e8-aca67d34e415 | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 5] 급수 · 급탕설비의 설계 및 시공 기준 1. 급수 · 급탕설비 일반사항 1.1 목적 이 기준은 건축물, 시설물 등에서 사람이 거주하거나 근무하는 공간에 위생적인 물 공급과 목욕, 세 면, 세탁, 조리, 음료 등에 급탕을 공급하기 위하여 필요한 설계 및 시공 방법 등 세부 기술기준을 정 함을 목적으로 한다. 해 설 이 기준의 목적은 「기계설비법」 제 14 조(기계설비 기술기준)과 같은 법 영 제 2 조 및 [별표 1]에 근 거하여, 건축물이나 시설물에 필요한 급수·급탕설비의 설계 및 시공 시 기계설비의 안전과 성능을 확보하기 위하여 필요한 기술적 요건을 규정하기 위함 「기계설비법」 제 14 조(기계설비 기술기준) ① 국토교통부장관은 기계설비의 안전과 성능확보를 위하여 필요 한 기술기준(이하 "기술기준이라 한다)를 정하여 고시하여야 한다. 이를 변경하는 경우에도 또한 같다. 1.2 적용범위 이 기준은 건축물, 시설물 등에 다음의 급수 、 급탕설비를 설치하는 경우에 대하여 적용한다. (1) 급수 , 급탕 배관 (2) 급수 , 급탕 펌프 (3) 저수탱크 및 급탕탱크 (4) 수도계량기 및 기타 부속장치 해 설 이 기준의 적용범위는 「기계설비법」 제 2 조제 1 호에 따른 건축물등에 같은 법 영 제 2 조에 따라 대 통령령으로 정한 급수·급탕설비를 설치하는 경우 및 그와 관련된 부속설비들을 포함함 「기계설비법」 제 2 조(정의) 1. "기계설비"란 건축물, 시설물 등(이하 "건축물등"이라 한다)에 설치된 기계 · 기 구 · 배관 및 그 밖에 건축물등의 성능을 유지하기 위한 설비로서 대통령령으로 정하는 설비를 말한다. 「기계설비법 시행령」 제 2 조(기계설비의 범위) 「기계설비법」(이하 "법"이라 한다) 제 2 조제 1 호에서 "대통령령 으로 정하는 설비"란 별표 1 의 설비를 말한다. 「기계설비법 시행령」 [별표 기계설비의 범위 1] 4. 위생기구 · 급수 · 급탕 · 오배수 · 통기설비 : 건축물등에서 위생과 냉수 · 온수 공급, 오배수(���), 오배 수관 통기(��) 등을 위하여 설치된 기계 · 기구 · 배관 및 그 밖에 성능을 유지하기 위한 설비 184 기계설비 기술기준 매뉴얼 | {}
8b80f1ee-9906-4fea-b1ef-fad9268116d1 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 1.3 타 규정과 의 관계 다음의 규정과 이 기준에서 정하는 내용이 상이한 경우에는 해당 규정을 따른다. (1) 「 주택건설기준 등에 관한 규정」 (2) 「건축물의 설비기준 등에 관한 규칙」 (3) KDS 31 30 15 급수설비 설계기준 (4) KDS 31 30 20 급탕설비 설계기준 (5) KCS 31 30 15 급수설비공사 표준시방서 (6) KCS 31 30 20 급탕설비공사 표준시방서 해 설 이 기준과 타 규정 및 기준과 다른 경우에는 상기 규정에 명시된 내용을 따름 국토교통부 185 기계설비 기술기준 해설 (별표 05 | {}
cbc78671-376e-499e-93c0-7c43ff6beade | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 급수 · 급탕설비 설계 2.1 급수설비 2.1.1 일반사항 (1) 음료나 목욕, 조리, 음식가공 공정, 의료 또는 제약 공정용으로 급수하는 위생기구에는 음용수만 을 공급한다. (2) 급수설비는 절수를 고려하여 설계한다. (3) 「주택건설기준 등에 관한 규정 」제 43 조에 따라 급수설비에는 감압밸브 등 수압을 조절하는 장치 를 설치하여 수압이 일정하게 유지되도록 한다. (4) 먹는물의 수질기준은 「먹는물 수질기준 및 검사 등에 관한 규칙 」제 2 조에 따른다. 해 설 1. 본문 해설 및 관련 법규 V (1 항, 2 항) 추가 설명 없음 V (3 항) 「주택건설기준 등에 관한 규정」 제 43 조 「주택건설기준 등에 관한 규정」 제 43 조(급 · 배수시설) ① 생략 ② 주택의 화장실에 설치하는 급수 · 배수용 배관은 다음 각 호의 기준에 적합해야 한다. 1. 급수용 배관에는 감압밸브 등 수압을 조절하는 장치를 설치하여 각 세대별 수압이 일정하게 유지되도록 할 것 V (4 항) 「먹는물 수질기준 및 검사 등에 관한 규칙」 제 2 조 186 기계설비 기술기준 매뉴얼 | {}
13436b81-04eb-4ecf-a7fd-048db3356fa4 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 「먹는물 수질기준 및 검사 등에 관한 규칙」 [별표 1] 먹는물의 수질기준(제 2 조 관련) 1. 미생물에 관한 기준 가. 일반세균은 1 mL 중 100 CFU(Colony Forming Unit)를 넘지 아니할 것. 다만, 샘물 및 염지하수의 경우 에는 저온일반세균은 20 CFU/mL, 중온일반세균은 5 CFU/mL 를 넘지 아니하여야 하며, 먹는샘물, 먹는 염지하수 및 먹는해양심층수의 경우에는 병에 넣은 후 4°C 를 유지한 상태에서 12 시간 이내에 검사하 여 저온일반세균은 100 CFU/mL, 중온일반세균은 20 CFU/mL 를 넘지 아니할 것 나. 총 대장균군은 100 mL(샘물·먹는샘물, 염지하수·먹는염지하수 및 먹는해양심층수의 경우에는 250 mL) 에서 검출되지 아니할 것. 다만, 제 4 조제 1 항제 1 호나목 및 다목에 따라 매월 또는 매 분기 실시하는 총 대장균군의 수질검사 시료(��) 수가 20 개 이상인 정수시설의 경우에는 검출된 시료 수가 5 퍼센트를 초과 하지 아니하여야 한다. 다. 대장균·분원성 대장균군은 100 mL 에서 검출되지 아니할 것. 다만, 샘물·먹는샘물, 염지하수·먹는염지하 수 및 먹는해양심층수의 경우에는 적용하지 아니한다. 라. 분원성 연쇄상구균·녹농균·살모넬라 및 쉬겔라는 250 mL 에서 검출되지 아니할 것(샘물·먹는샘물, 염지 하수·먹는염지하수 및 먹는해양심층수의 경우에만 적용한다) 마. 아황산환원혐기성포자형성균은 50 mL 에서 검출되지 아니할 것(샘물·먹는샘물, 염지하수·먹는 염지하수 및 먹는해양심층수의 경우에만 적용한다) 바. 여시니아균은 2 L 에서 검출되지 아니할 것(먹는물공동시설의 물의 경우에만 적용한다) 2. 건강상 유해영향 무기물질에 관한 기준 가. 납은 0.01 mg/L 를 넘지 아니할 것 나. 불소는 1.5 mg/L(샘물·먹는샘물 및 염지하수·먹는염지하수의 경우에는 2.0 mg/L)를 넘지 아니할 것 다. 비소는 0.01 mg/L(샘물·염지하수의 경우에는 0.05 mg/L)를 넘지 아니할 것 라. 셀레늄은 0.01 mg/L(염지하수의 경우에는 0.05 mg/L)를 넘지 아니할 것 마. 수은은 0.001 mg/L 를 넘지 아니할 것 바. 시안은 0.01 mg/L 를 넘지 아니할 것 사. 크롬은 0.05 mg/L 를 넘지 아니할 것 아. 암모니아성 질소는 0.5 mg/L 를 넘지 아니할 것 자. 질산성 질소는 10 mg/L 를 넘지 아니할 것 차. 카드뮴은 0.005 mg/L 를 넘지 아니할 것 카. 붕소는 1.0 mg/L 를 넘지 아니할 것(염지하수의 경우에는 적용하지 아니한다) 타. 브롬산염은 0.01 mg/L 를 넘지 아니할 것(수돗물, 먹는샘물, 염지하수·먹는염지하수, 먹는해양심층수 오존으로 살균·소독 또는 세척 등을 하여 먹는물로 이용하는 지하수만 적용한다) 및 파. 스트론튬은 4 mg/L 를 넘지 아니할 것(먹는염지하수 및 먹는해양심층수의 경우에만 적용한다) 하. 우라늄은 30 �g/L 를 넘지 않을 것[수돗물(지하수를 원수로 사용하는 수돗물을 말한다), 샘물, 먹는샘물, 먹는염지하수 및 먹는물공동시설의 물의 경우에만 적용한다)] 기계설비 기술기준 해설 (별표 05 국토교통부 187 | {}
f048fa8a-78b0-46f6-b775-c5959c0f12ba | 국내_기계설비_기술기준_매뉴얼_최종본 | 「먹는물 수질기준 및 검사 등에 관한 규칙」 [별표 1] 먹는물의 수질기준(제 2 조 관련)(계속) 3. 건강상 유해영향 유기물질에 관한 기준 가. 페놀은 0.005 mg/L 를 넘지 아니할 것 나. 다이아지논은 0.02 mg/L 를 넘지 아니할 것 다. 파라티온은 0.06 mg/L 를 넘지 아니할 것 라. 페니트로티온은 0.04 mg/L 를 넘지 아니할 것 마. 카바릴은 0.07 mg/L 를 넘지 아니할 것 바. 1,1,1-트리클로로에탄은 0.1 mg/L 를 넘지 아니할 것 사. 테트라클로로에틸렌은 0.01 mg/L 를 넘지 아니할 것 아. 트리클로로에틸렌은 0.03 mg/L 를 넘지 아니할 것 자. 디클로로메탄은 0.02 mg/L 를 넘지 아니할 것 차. 벤젠은 0.01 mg/L 를 넘지 아니할 것 카. 톨루엔은 0.7 mg/L 를 넘지 아니할 것 타. 에틸벤젠은 0.3 mg/L 를 넘지 아니할 것 파. 크실렌은 0.5 mg/L 를 넘지 아니할 것 하. 1,1-디클로로에틸렌은 0.03 mg/L 를 넘지 아니할 것 거. 사염화탄소는 0.002 mg/L 를 넘지 아니할 것 너. 1,2-디브로모-3-클로로프로판은 0.003 mg/L 를 넘지 아니할 것 더. 1,4-다이옥산은 0.05 mg/L 를 넘지 아니할 것 4. 소독제 및 소독부산물질에 관한 기준(생물 먹는샘물 영지하수 먹는영지하수 먹는허양심층수 및 먹는물공 동시설의 물의 경우에는 적용하지 아니한다) 가. 잔류염소(유리잔류염소를 말한다)는 4.0 mg/L 를 넘지 아니할 것 나. 총트리할로메탄은 0.1 mg/L 를 넘지 아니할 것 다. 클로로포름은 0.08 mg/L 를 넘지 아니할 것 라. 브로모디클로로메탄은 0.03 mg/L 를 넘지 아니할 것 마. 디브로모클로로메탄은 0.1 mg/L 를 넘지 아니할 것 바. 클로랄하이드레이트는 0.03 mg/L 를 넘지 아니할 것 사. 디브로모아세토니트릴은 0.1 mg/L 를 넘지 아니할 것 아. 디클로로아세토니트릴은 0.09 mg/L 를 넘지 아니할 것 자. 트리클로로아세토니트릴은 0.004 mg/L 를 넘지 아니할 것 차. 할로아세틱에시드(디클로르아세틱에시드, 트리클로로아세틱에시드 및 디브로모아세틱에시드의 합으 로 한다)는 0.1 mg/L 를 넘지 아니할 것 카. 포름알데히드는 0.5 mg/L 를 넘지 아니할 것 188 기계설비 기술기준 매뉴얼 | {}
34c1ba92-d7e3-483f-88e9-9c6d4092982a | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 「먹는물 수질기준 및 검사 등에 관한 규칙」 [별표 1] 먹는물의 수질기준(제 2 조 관련)(계속) 5. 심미적(���) 영향물질에 관한 기준 가. 경도(硬度)는 1 000 mg/L(수돗물의 경우 300 mg/L, 먹는염지하수 및 먹는해양심층수의 경우 1200 mg/L) 를 넘지 아니할 것. 다만, 샘물 및 염지하수의 경우에는 적용하지 아니한다. 나. 과망간산칼륨 소비량은 10 mg/L 를 넘지 아니할 것 다. 냄새와 맛은 소독으로 인한 냄새와 맛 이외의 냄새와 맛이 있어서는 아니될 것. 다만, 맛의 경우는 샘 물, 염지하수, 먹는샘물 및 먹는물공동시설의 물에는 적용하지 아니한다. 라. 동은 1 mg/L 를 넘지 아니할 것 마. 색도는 5 도를 넘지 아니할 것 바. 세제(음이온 계면활성제)는 0.5 mg/L 를 넘지 아니할 것. 다만, 샘물·먹는샘물, 염지하수·먹는염지하수 및 먹는해양심층수의 경우에는 검출되지 아니하여야 한다. 사. 수소이온 농도는 pH 5.8 이상 pH 8.5 이하이어야 할 것. 다만, 샘물, 먹는샘물 및 먹는물공동시설의 물 의 경우에는 pH 4.5 이상 pH 9.5 이하이어야 한다. 아. 아연은 3 mg/L 를 넘지 아니할 것 자. 염소이온은 250 mg/L 를 넘지 아니할 것(염지하수의 경우에는 적용하지 아니한다) 차. 증발잔류물은 수돗물의 경우에는 500 mg/L, 먹는염지하수 및 먹는해양심층수의 경우에는 미네랄 등 무 해성분을 제외한 증발잔류물이 500 mg/L 를 넘지 아니할 것 카. 철은 0.3 mg/L 를 넘지 아니할 것. 다만, 샘물 및 염지하수의 경우에는 적용하지 아니한다. 타. 망간은 0.3 mg/L(수돗물의 경우 0.05 mg/L)를 넘지 아니할 것. 다만, 샘물 및 염지하수의 경우에는 적용 하지 아니한다. 파. 탁도는 1NTU(Nephelometric Turbidity Unit)를 넘지 아니할 것. 다만, 지하수를 원수로 사용하는 마을 상수도, 소규모급수시설 및 전용상수도를 제외한 수돗물의 경우에는 0.5 NTU 를 넘지 아니하여야 한다. 하. 황산이온은 200 mg/L 를 넘지 아니할 것. 다만, 샘물, 먹는샘물 및 먹는물공동시설의 물은 250 mg/L 를 넘 지 아니하여야 하며, 염지하수의 경우에는 적용하지 아니한다. 거. 알루미늄은 0.2 mg/L 를 넘지 아니할 것 6. 방사능에 관한 기준(염지하수의 경우에만 적용한다) 가. 세슘(Cs-137)은 4.0 mBq/L 를 넘지 아니할 것 나. 스트론튬(Sr-90)은 3.0 mBq/L 를 넘지 아니할 것 다. 삼중수소는 6.0 Bq/L 를 넘지 아니할 것 2. 용어 V 내용 없음 2.1.2 급수관 호칭지름 산정기준 급수관 호칭지름은 [별표 8] 2.4 에 따른다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) [별표 8] 2.4 와 설비공학회 표준 급수관지름 산정방법(SAREK 표준 401-2020) 참조하여 유량 국토교통부 189 기계설비 기술기준 해설 (별표 05 | {}
1bee77c0-6a1f-49b0-a586-993363c59e02 | 국내_기계설비_기술기준_매뉴얼_최종본 | 을 구함 2.4 급수배관 급수관 호칭지름은 순간최대유량, 허용마찰손실 및 유속을 산정하고 배관 유량 선도 등을 활용하여 호칭지름을 결정한다. 2. 용어 V 내용 없음 2.1.3 급수펌프 (1) 고가탱크용 양수펌프 ① 양수펌프의 유량은 시간최대 예상급수량으로 한다. ② 예비펌프를 설계하여 교대 운전할 수 있도록 한다. (2) 자동부스터 급수펌프 유닛 ① 펌프 유닛의 전체 유량은 순간최대예상급수량으로 한다. ② 펌프는 2 대 이상으로 한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항 1 호) 시간최대예상급수량은 시간평균 예상급수량(1 일 급수량/사용시간)의 1.5~2 배로 산정하 나 공동주택은 기구급수부하단위방식으로도 산출 가능함 V (1 항 2 호) 추가 설명 없음 V (2 항 1 호) 순간최대예상급수량은 시간평균예상 급수량(1 일 급수량/사용시간)의 3~4 배로 산정하 나 공동주택은 기구급수부하단위방식으로도 산출 가능함 V (2 항 2 호) 추가 설명 없음 2. 용어 내용 없음 ----- ----- 190 기계설비 기술기준 매뉴얼 | {}
bf5f25c9-af1e-46f8-bc4c-2058a195dbc4 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.1.4 저수탱크 (1) 저수탱크의 오버플로관은 KDS 31 30 15(4.12) 표 4.12-1 에 따른 표 1 의 호칭지름 이상으로 설계 한다. 오버플로 관의 토수구 공간은 150 mm 이상으로 한다. 토수구에는 내식성 방충용 철망을 설계한다. 표 1 저수탱크 오버플로관의 호칭지름(KDS 31 30 15(4.12) 표 4.12-1) ¦ 최대 급수량(L/s) ¦ 오버플로관, DN ¦ ¦ --- ¦ --- ¦ ¦ 0~3 ¦ 50 ¦ ¦ 3~9 ¦ 65 ¦ ¦ 9~12 ¦ 80 ¦ ¦ 12~25 ¦ 100 ¦ ¦ 25~41 ¦ 125 ¦ ¦ 41~63 ¦ 150 ¦ ¦ 63 이상 ¦ 200 ¦ (2) 「주택건설기준 등에 관한 규정」 제 43 조에 따라 저수탱크의 재료는 수질을 오염시키지 아니하는 재료나 위생에 지장이 없는 내구성이 있는 도금 、 녹막이 처리 또는 피막처리를 한 재료를 사용한 다. (3) 저수탱크의 구조는 청소 등 관리가 쉬워야 하고, 음용수 외의 다른 물질이 들어갈 수 없도록 해야 한다. (4) 저수탱크의 물이 일정 수준 이상 넘거나 일정 수준 이하로 줄어들 때 울리는 경보장치를 설치하 고, 그 수신기는 관리실에 설치해야 한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 추가 설명 없음 V (2 항) 「주택건설기준 등에 관한 규정」 제 43 조 제 6 항 「주택건설기준 등에 관한 규정」 제 43 조(급 · 배수시설) ① ~ ⑤ 생략 ⑥주택에 설치하는 먹는물의 급수탱크 및 저수탱크는 다음 각 호의 기준에 적합해야 한다. 1. 급수탱크 및 저수탱크의 재료는 수질을 오염시키지 아니하는 재료나 위생에 지장이 없는 것으로서 내구 성이 있는 도금 · 녹막이 처리 또는 피막처리를 한 재료를 사용할 것 2. 급수탱크 및 저수탱크의 구조는 청소 등 관리가 쉬워야 하고, 먹는물 외의 다른 물질이 들어갈 수 없도록 할 것 이하 생략 V (3 항, 4 항) 추가 설명 없음 2. 용어 V 내용 없음 국토교통부 191 기계설비 기술기준 해설 (별표 05 | {}
c9dcd970-022f-4dfe-91bd-2503f08db4a3 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2.1.5 수격방지기 수격이 발생하지 않도록 급수설비의 유속을 제어한다. 급폐쇄밸브가 설계된 곳에는 수격방지기를 설계한다. 해 설 1. 본문 해설 및 관련 법규 V (2.1.5) 입상 상부 및 전자밸브, 역류방지밸브, 컨트롤밸브 등 수격 현상이 발생할 수 있는 급폐쇄 밸브 근처에는 워터해머흡수기를 설치함 압력파의 전파속도를 물 속에서의 음속(1 450 m/s, 실제는 이보다 더 빠름)과 같다고 보면, 강관의 경우 유속 의 약 14 배에 해당하는 워터해머 압력이 발생한다. 그러므로 유체배관, 특히 개폐가 빈번한 급수 급탕배관 계통은 반드시 워터해머 대책이 강구되어야 함 출처 : 설비공학편람, 제 5 권 p1.5~23 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 워터해머 (water hammer) = 수격작용 ¦ 일정한 압력과 유속으로 배관계통을 흐르던 유체의 흐름이 갑자기 차단될 때 발생하 는 높은 충격압력, 소음 및 이에 수반 되는 진동을 말한다. 일반적으로 워터해머가 발생하면 소음발생이 연상되지만, 들을 수 있는 소음의 동반 이 없는 워터해머도 있다. 즉, 급폐쇄의 경우 항상 어느 정도의 충격압력은 발생 되지 만 소음은 발생할 수도 있고, 발생하지 않을 수도 있다. 그러므로 소음이 없다고 해서 배관계통에 워터해머가 발생하지 않는다고 판단할 수는 없다. 워터해머로 인한 발생 압력은 Joukovsky 방정식으로 계산할 수 있다. = pav PT 식에서, Pr: 워터해머에 의한 압력 상승, kg/m2, p: 유체의 밀도, kg-s2/m4, a: 압력파 전파속도, m/s, v: 유체의 속도, m/s 이다. 출처: 설비공학편람, 제 5 권 pp 1.5-22~1.5-23 ¦ 192 기계설비 기술기준 매뉴얼 | {}
a3da86fe-d1fa-4a19-a717-5f11773956eb | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.1.6 위생기구의 최저 필요 급수압력과 유량 최대부하에서 위생기구의 급수 토출량이 KDS 31 30 15(4.3) 표 4.3-1 에 따른 표 2 의 값 이상이 되도 록 급수배관설비를 설계하고, 배관의 호칭지름을 결정한다. 표 2 에 없는 위생기구의 최소 유량과 압 력은 유사기구를 준용한다. 표 2 위생기구의 필요 급수압력과 유량(KDS 31 30 15(4.3) 표 4.3-1) ¦ 급수용 위생기구 ¦ 유량(L/s) ¦ 최저필요수압(kPa) ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 욕조 ¦ 0.25 ¦ 55 ¦ ¦ 연합기구 ¦ 0.25 ¦ 55 ¦ ¦ 식기세척기, 가정용 ¦ 0.17 ¦ 55 ¦ ¦ 음수기 ¦ 0.05 ¦ 55 ¦ ¦ 세탁트레이, 세탁기 ¦ 0.25 ¦ 55 ¦ ¦ 세면기 ¦ 0.1 ¦ 55 ¦ ¦ 샤워 ¦ 0.18 ¦ 100 ¦ ¦ 샤워(압력식, 온도감지 혹은 압력식/온도감지 혼합밸브) ¦ 0.18 ¦ 130 ¦ ¦ 호스연결용 수도꼭지 ¦ 0.3 ¦ 55 ¦ ¦ 싱크, 가정용 ¦ 0.15 ¦ 55 ¦ ¦ 싱크, 청소용 ¦ 0.18 ¦ 55 ¦ ¦ 소변기, 밸브 ¦ 0.75 ¦ 100 ¦ ¦ 대변기, 세정밸브 ¦ 1.6 ¦ 100 ¦ ¦ 대변기, 세정탱크, 밀결형 ¦ 0.18 ¦ 55 ¦ 해 설 1. 본문 해설 및 관련 법규 V 설비공학편람 참조 물사용 기구 중에서 특히 샤워는 몸을 씻는 단순한 용도만이 아니다. 의학적인 측면에서는 병원에서나 사용 되는 수치료기 (水治療器)의 역할을 겸하는 것이다. 수압 100 kPa 은 맨몸으로 샤워를 할 때 몸의 근육을 자 극시켜서 혈액순환을 좋게 하고, 혈액 속의 산소 함량이 늘어나 몸에 활력을 가지게 하는 조건이 된다. 출처: 설비공학편람, 제 5 권 p1.5-8 2. 용어 V 내용 없음 2.1.7 위생기구의 최대급수압력 제한 위생기구에 수압이 550 kPa 이상 걸릴 경우에는 감압밸브를 설계하거나, 급수 조닝을 하여 최대압 력을 550 kPa 이하로 제한한다. 국토교통부 193 기계설비 기술기준 해설 (별표 05 | {}
9f2f9c85-e04a-428d-905d-e500b33d3ccc | 국내_기계설비_기술기준_매뉴얼_최종본 | 해 설 1. 본문 해설 및 관련 법규 V (1 항) 추가 설명 없음 2. 용어 V 내용 없음 -- --- 2.1.8 급수의 오염방지 (1) 음용수 배관과 비음용수 배관을 크로스커넥션 시켜서는 안 된다. (2) 위생기구의 급수배관은 역류되지 않도록 설계한다. (3) 위생기구나 물 사용기기가 상수도관에 직접 연결된 경우에는 역류방지 조치를 한다. (4) 급수관을 냉 , 온수배관 계통과 같은 비 음용배관 계통의 보급수용으로 연결할 때는 역류방지 조 치를 한다. (5) 음용수용 탱크의 내부 표면을 음용수의 맛이나 냄새, 색깔 또는 음용수질을 변화시킬 수 있는 물 질로 도장하거나 수리해서는 안 된다. (6) 음용수를 다루는 펌프와 필터, 연수기, 탱크 및 기타 기구는 위해성물질로부터 보호한다. (7) 음용수용 저수탱크 상부에는 저수탱크에 관계없는 장치나 배관 등을 설계해서는 안 된다. (8) 모든 음용수 개방구와 토출구는 토수구공간이나 역류방지밸브 또는 진공브레이커로 역류되지 않게 한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 보급수 공급관과 같이 크로스커넥션이 불가피한 경우에는 역류방지밸브 설치로 역류를 차 단하여 음용수 오염을 방지해야 함 V (2 항) 싱크, 욕조, 세탁기와 같이 물받이 용기의 급수 배관에 토수구 공간을 둘 수 없을 경우에는, 오염된 물이 역사이펀 작용으로 역류하지 않도록 진공브레이커 설치로 역사이펀 역류를 차단하 여 음용수 오염을 방지해야 함 V (3 항 ~ 4 항) 역류방지밸브를 설치하여 역류를 차단해야 함 V (5 항 ~ 6 항) 추가 설명 없음 V (7 항) 음용수 저수탱크 상부에는 수질에 직접적으로 영향을 줄 수 있는 장치나 배관, 덕트 등을 설 계해서는 안 됨. 단 저수탱크실용 환기덕트 및 급수배관은 제외함 V (8 항) 역류방지밸브와 진공브레이커를 포함하는 경우 역류방지기(Backflow Preventer)로 칭함 2. 용어 194 기계설비 기술기준 매뉴얼 | {}
609361eb-7467-4753-9bb0-a4cf6277817d | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 크로스커넥션 ¦ 상수, 급수, 급탕 등 음용수 계통과 음용수 이외의 계통이 직접 연결된 상태를 말한 다. 그러므로 이 지점을 통하여 음용수 이외의 물이 역류하여 음용수를 오염시킬 수 있다. 이는 각종 보급수, 소화배관에 연결된 급수관처럼 시스템 구성상 있을 수밖에 없으므로, 그런 부위에는 반드시 역류방지밸브 설치로 역류를 차단하여 음용수 오염 을 방지하여야 한다. 출처: 설비공학편람, 제 5 권, p1.5-24 ¦ --- ○--- 2.1.9 비상급수시설 (1) 공동주택을 건설하는「주택법」제 2 조제 12 호의 주택단지에는 「주택건설기준 등에 관한 규정」 제 35 조에 따라 「먹는물관리법」 제 5 조의 규정에 의한 먹는물의 수질기준에 적합한 비상용수를 공급 할 수 있는 지하양수시설 또는 지하저수탱크시설을 설치해야 한다. (2) (1)에 따른 지하양수시설 및 지하저수탱크는 다음에 따른 설치기준을 갖추어야 한다. 다만, 철도 부지 활용 공공주택을 건설하는 주택단지의 경우에는 시 , 군지역의 기준을 적용한다. ① 지하양수시설 가. 1 일에 당해 주택단지의 매 세대당 0.2 톤(시 、 군지역은 0.1 톤)이상의 수량을 양수할 수 있을 것 나. 양수에 필요한 비상전원과 이에 의하여 가동될 수 있는 펌프를 설치할 것 다. 당해 양수시설에는 매 세대당 0.3 톤 이상을 저수할 수 있는 지하저수탱크(「 주택건설기준 등 에 관한 규정」제 43 조제 6 항의 규정에 의한 기준에 적합해야 한다)를 함께 설치할 것 ② 지하저수탱크 가. 고가탱크저수량(매 세대당 0.25 톤까지 산입한다)을 포함하여 매 세대당 0.5 톤(독신자용 주택 은 0.25 톤) 이상의 수량을 저수할 수 있을 것. 다만, 지역별 상수도 시설용량 및 세대당 수돗물 사용량 등을 고려하여 설치기준의 2 분의 1 의 범위에서 특별시 、 광역시 、 특별자치시 , 특별 자치도 , 시 또는 군의 조례로 완화 또는 강화하여 정할 수 있다. 나. 50 세대(독신자용 주택은 100 세대)당 1 대 이상의 수동식펌프를 설치하거나 양수에 필요한 비 상전원과 이에 의하여 가동될 수 있는 펌프를 설치할 것 다. 제 43 조제 6 항의 규정에 의한 기준에 적합하게 설치할 것 라. 먹는물을 당해 저수탱크를 거쳐 각 세대에 공급할 수 있도록 설치할 것 해 설 1. 본문 해설 및 관련 법규 V (1 항) 이 기준 (2)와 「주택건설기준 등에 관한 규정」 제 35 조의 내용은 동일함 기계설비 기술기준 해설 (별표 05 국토교통부 195 | {}
4d60d757-058b-4e6b-bead-73d89b6e9b00 | 국내_기계설비_기술기준_매뉴얼_최종본 | 「주택법」 제 2 조(정의) 목 12. "주택단지"란 제 15 조에 따른 주택건설사업계획 또는 대지조성사업계획의 승인을 받아 주택과 그 부대시 설 및 복리시설을 건설하거나 대지를 조성하는 데 사용되는 일단(��)의 토지를 말한다. 다만, 다음 각 의 시설로 분리된 토지는 각각 별개의 주택단지로 본다. 가. 철도 · 고속도로 · 자동차전용도로 나. 폭 20 m 이상인 일반도로 다. 폭 8 m 이상인 도시계획예정도로 라. 가목부터 다목까지의 시설에 준하는 것으로서 대통령령으로 정하는 시설 「주택건설기준 등에 관한 규정」 제 35 조(비상급수시설) ①공동주택을 건설하는 주택단지에는 「먹는물관리법」 제 5 조의 규정에 의한 먹는물 의 수질기준에 적합한 비상용수를 공급할 수 있는 지하양수시설 또는 지하저수탱크시설을 설치하여야 한 다. ② 제 1 항에 따른 지하양수시설 및 지하저수탱크는 다음 각 호에 따른 설치기준을 갖추어야 한다. 다만, 철도 부지 활용 공공주택을 건설하는 주택단지의 경우에는 시 · 군지역의 기준을 적용한다. 1. 지하양수시설 가. 1 일에 당해 주택단지의 매 세대당 0.2 톤(시 · 군지역은 0.1 톤)이상의 수량을 양수할 수 있을 것 나. 양수에 필요한 비상전원과 이에 의하여 가동될 수 있는 펌프를 설치할 것 다. 당해 양수시설에는 매 세대당 0.3 톤 이상을 저수할 수 있는 지하저수탱크(제 43 조제 6 항의 규정에 의한 기준에 적합하여야 한다)를 함께 설치할 것 2. 지하저수탱크 가. 고가탱크저수량(매 세대당 0.25 톤까지 산입한다)을 포함하여 매 세대당 0.5 톤(독신자용 주택은 0.25 톤) 이상의 수량을 저수할 수 있을 것. 다만, 지역별 상수도 시설용량 및 세대당 수돗물 사용량 등을 고 려하여 설치기준의 2 분의 1 의 범위에서 특별시 · 광역시 · 특별자치시 · 특별자치도 · 시 또는 군의 조 례로 완화 또는 강화하여 정할 수 있다. 나. 50 세대(독신자용 주택은 100 세대)당 1 대 이상의 수동식펌프를 설치하거나 양수에 필요한 비상전원과 이에 의하여 가동될 수 있는 펌프를 설치할 것 다. 제 43 조 제 6 항의 규정에 의한 기준에 적합하게 설치할 것 라. 먹는물을 당해 저수탱크를 거쳐 각 세대에 공급할 수 있도록 설치할 것 「주택건설기준 등에 관한 규정」 제 43 조(급·배수시설) ⑥주택에 설치하는 먹는물의 급수탱크 및 저수탱크는 다음 각 호의 기준에 적합해야 한다. 1. 급수탱크 및 저수탱크의 재료는 수질을 오염시키지 아니하는 재료나 위생에 지장이 없는 것으로서 내구성이 있는 도금 · 녹막이 처리 또는 피막처리를 한 재료를 사용할 것 2. 급수탱크 및 저수탱크의 구조는 청소 등 관리가 쉬워야 하고, 먹는물 외의 다른 물질이 들어갈 수 없 도록 할 것 2. 용어 V 내용 없음 --- ---- -- 196 기계설비 기술기준 매뉴얼 | {}
3fabf60b-48a5-4a45-96d6-2e8099ac878d | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.2 급탕설비 2.2.1 일반사항 (1) 급탕설비는 급탕이 오염되지 않게 한다. (2) 배관은 최대 급탕부하 시에 위생기구에 필요 급탕량을 공급할 수 있는 크기로 한다. (3) 냉수와 온수를 혼합하여 사용할 때 압력차에 의한 온도변화가 작아야 한다. (4) 배관은 내식성과 내열성이 있는 재료로 한다. (5) 급탕배관의 신축으로 배관이나 다른 기기가 손상될 수 있는 경우에는 신축이음을 사용하여 이를 방지한다. (6) 중앙급탕방식에는 배관의 열손실을 보상하여 일정한 급탕온도를 유지할 수 있는 환탕배관과 급 탕순환펌프를 설계한다. (7) 급탕장치는 보수점검 등 유지관리가 쉬워야 한다. (8) 급탕탱크방식의 급탕배관에는 온도상승에 의한 압력을 도피시킬 수 있는 팽창탱크를 설계한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항 ~ 8 항) 추가 설명 없음 2. 용어 내용 없음 2.2.2 급탕배관 및 기기 (1) 급탕관 호칭지름 급탕관 호칭지름은 [별표 8] 2.5(1)에 따른다. (2) 환탕관 호칭지름 급수관 호칭지름은 [별표 8] 2.5(2)에 따른다. (3) 급탕배관 길이 급탕열원에서 급탕 위생기구까지의 배관길이는 15 m 이하로 한다. 환탕배관과 가열관은 급탕열원 으로 간주한다. (4) 환탕유량의 균등 분배 환탕유량은 균등하게 분배될 수 있도록 설계한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항, 2 항) [별표 8] 2.5(1) (2) 참조 기계설비 기술기준 해설 (별표 05 국토교통부 197 | {}
462e218a-6b82-4739-8870-3ae23fc2e596 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2.5 급탕배관 (1) 급탕배관 호칭지름 급탕관의 호칭지름은 급탕부하단위(FU) 값에 의한 순간최대유량으로 선정한다. (2) 환탕배관 호칭지름 환탕관의 유량은 급탕배관의 열손실을 구하여 계산하여 선정한다. (3 항) 공동주택 단위세대 내 급탕분배기(오픈수전함, 수전박스 등)는 급탕열원으로 간주할 수 있음 V (4 항) 환탕유량이 균등하게 분배될 수 있게 역순환배관방식으로 하거나 수동밸런싱밸브 설치 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 가열관 ¦ 급탕 사용 시 배관 내 남아 있는 냉수의 낭비를 최소화할 수 있도록 '급탕이 머무르 거나 지나가는 배관' 내외부에 가온전선 등으로 배관의 급탕온도를 유지시킬 수 있 는 관 등을 설치하여 온수 온도 유지를 가능하게 하는 모든 수단을 포함함 출처 : 국민신문고 질의 답변 ¦ ---- 2.2.3 급탕가열장치 (1) 난방겸용 급탕가열장치 60°C 이상으로 공급되는 난방겸용 급탕가열장치는 온도조절밸브를 설치하여 급탕배관의 급탕온도 를 60°C 이하로 제한한다. (2) 위치 급탕가열장치와 급탕탱크는 유지관리, 정비 및 교체가 편리하고 상태확인과 점검이 용이한 위치에 설계한다. (3) 배출관 설계 압력릴리프 밸브와 온도릴리프 밸브의 배출관은 다음과 같이 설계한다. ① 배수관에 직접 연결해서는 안 된다. ② 급탕가열장치와 동일한 실의 배수구 공간으로 배출한다. ③ 배출밸브의 출구 호칭지름 이상으로 한다. ④ 릴리프 장치는 단독으로 사용하고, 다른 종류의 안전장치나 장비의 배관에 연결하지 않아야 한 다. ⑤ 인체나 구조물에 손상이 없도록 배관한다. ⑥ 건물 거주자가 확인할 수 있는 말단 지점으로 배출한다. ⑦ 트랩을 형성하지 말아야 한다. ⑧ 중력으로 배출한다. ⑨ 배출구는 바닥이나 배수용 물받이 용기 위 150 mm 이하로 설계한다. ⑩ 밸브나 티 이음쇠를 사용해서는 안 된다. 해 설 1. 본문 해설 및 관련 법규 198 기계설비 기술기준 매뉴얼 | {}
937e98f4-f975-4edc-8bd8-aacba78a12f3 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 V (1 항) 레지오넬라균의 번식을 방지하기 위해 50°C 이상을 유지해야 함 V (2 항) 추가 설명 없음 V (3 항 1 호 ~ 8 호) 추가 설명 없음 2. 용어 V 내용 없음 2.2.4 급탕탱크류 (1) 급탕탱크와 급탕열교환기의 재질은 내열성과 내식성이 있고 수질에 악영향을 주지 않아야 한다. (2) 스테인리스강을 사용한 경우에는 마그네시아나 유리면 등의 수용성 염화물을 포함하지 않은 단 열재를 사용하거나, 단열재의 내부에 물이 침입하지 않도록 금속판 등의 보온 덮개로 덮어야 한 다. (3) 급탕탱크는 STS 316L 이상으로 한다. (4) 압력탱크 및 급탕설비에는 폭발 등의 위험을 막을 수 있는 시설을 설치해야 한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항 ~ 2 항) 추가 설명 없음 V (3 항) STS 316L(탄소 0.03% 이하, 니켈 12~16%)은 STS 316(탄소 0.08% 이하, 니켈 10~14%)보다 탄소(C) 함유량을 현저히 저하시키고, 니켈(Ni)의 함량을 증가시켜 용접성과 내부식성 그리고 강 도가 우수함 STS 304 는 60~70°C 에서 균열(고온 크랙)이 발생하기 쉬움 V 급탕탱크에는 온도 상승에 따른 압력 상승 방지를 위해 릴리프 밸브 등의 설치를 해야 함 (4 항) 2. 용어 V 내용 없음 국토교통부 199 기계설비 기술기준 해설 (별표 05 | {}
e3132c34-e22e-4133-b08e-688801573147 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2.2.5 급탕계통의 부속장치 (1) 역류방지밸브 급탕탱크의 급수관에는 급탕이 급수관으로 역류하지 않도록 역류방지밸브를 설계한다. (2) 배수밸브 급탕탱크 하단에는 배수밸브를 설계한다. (3) 순간 급탕가열장치의 급탕온도제어 탱크 없는 순간 급탕가열장치의 급탕온도는 60°C 이하로 설정할 수 있어야 한다. (4) 급탕탱크의 압력표시 급탕탱크와 급탕가열장치에는 최대 허용압력을 반영하여 설계한다. (5) 온도제어장치 급탕탱크나 급탕가열장치의 급탕온도를 최저에서 최고허용온도까지 원하는 설정온도로 조정 가능 한 자동온도제어장치를 설계한다. (6) 차단밸브 급탕탱크나 급탕가열장치 급수관에는 차단밸브를 설계한다. (7) 진공 릴리프밸브 급탕탱크에는 급탕 온도 하강에 따른 진공에 의한 탱크 손상 방지를 위하여 진공 릴리프밸브를 설 계한다. (8) 압력 릴리프밸브 급탕탱크나 탱크 상부 급탕배관에 압력 릴리프밸브를 설계한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항 ~ 6 항, 8 항) 추가 설명 없음 V (7 항) 급탕탱크가 부압 발생 가능성이 있을 경우에는 진공 릴리프밸브 설치를 고려해야 함 2. 용어 200 기계설비 기술기준 매뉴얼 | {}
462889d5-5425-45c6-8817-3680cef51006 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 역류방지밸브 (backflow preventer, BFP) ¦ 배관계통에서 유체가 역류하는 현상을 차단하는 밸브이다. 역류는 역압(back pressure)과 역사이펀(back-siphonage) 작용에 의하여 발생되며, 설비배관 계통에서 의 역류는 음용수를 오염시키기 때문에 이를 방지하기 위하여 사용된다. 오염 정도 에 따라 위해성 오염과 불쾌성오염으로 나누어짐으로, 역류방지 밸브도 불쾌성오염 방지용의 복식첵밸브형 (double check valve backflow prevention assembly, DCV)과 위해성오염 방지용의 감압형 (reduced pressure principle backflow prevention assembly, RP 또는 RPZ) 두 가지 형태가 기본이다. 역류방지밸브는 2 개의 정지밸브 와 4 개의 테스트콕을 포함하는 것이 완전체로서의 표준품이다. 출처:설비공학편람,제 4 권. pp5.33-29~.33-30 ¦ ¦ 진공 릴리프밸브 (vacuum relief valve, VRV) ¦ 배관 내부가 설정된 진공도에 도달하면 자동으로 밸브가 열려 공기를 유입시켜서 진 공을 깨트림과 동시에 압력이 높아지므로 다시 원위치 되는 동작을 반복한다. 밀폐 식 압력용기나 수직배관에서의 진공파괴를 방지하는 기구. 출처: 설비공학편람,제 4 권 pp5.33-38~5.33-39 ¦ ¦ 압력 릴리프밸브 (pressure relief valve) ¦ 압력의 증감에 따라 밸브의 개도가 비례 조절되므로, 설정압력 초과 시에도 방출은 서서히 이루어진다. 설정점 이상의 압력만을 감소시킨다. 비압축성 액체용으로 사용된다. 출처: 설비공학편람, 제 4 권, pp5.33-36~5.33-37 ¦ 2.2.6 급탕순환펌프 (1) 순환펌프 유량은 2.2.2(2)의 환탕배관의 환탕유량으로 하고, 순환펌프의 양정은 마찰손실이 가장 큰 순환관로의 마찰손실로 한다. (2) 급탕순환펌프나 급탕 가열장치는 급탕하지 않을 때 자동이나 수동으로 정지시킬 수 있어야 한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항, 2 항) 추가 설명 없음 2. 용어 V 내용 없음 2.2.7 급탕온도 제어 (1) 온도 제한수단 위생기구에서의 최대허용 급탕온도를 제한하기 위한 수단으로 급탕가열장치의 온도조절기를 사용 해서는 안 된다. (2) 급탕사용온도 제어 온도제한장치나 혼합장치를 사용하여 위생기구의 급탕온도를 43°C 이하로 제한할 수 있어야 한다. 국토교통부 201 기계설비 기술기준 해설 (별표 05 | {}
3895fce4-9767-4e17-9870-570422b3129b | 국내_기계설비_기술기준_매뉴얼_최종본 | 해 설 1. 본문 해설 및 관련 법규 V (1 항) 추가 설명 없음 V (2 항) 샤워나 욕조의 위생기구에서는 사용자의 화상 방지를 위한 43°C 이하로 급탕온도를 제한할 수 있어야 함 2. 용어 V 내용 없음 202 기계설비 기술기준 매뉴얼 | {}
238ebdf8-d691-4783-aa80-9c32093d4f36 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 3. 급수 · 급탕설비 시공 3.1 일반사항 (1) 급수 、 급탕 배관은 엘리베이터 승강기 통로, 각종 탱크, 전기실 내에는 설치하지 않아야 하고, 설 치되는 기기에 필요한 배관은 예외로 하여 설치한다. (2) 주관으로부터 분기하는 지관의 분기부, 기기의 접속부에서 기기에 근접한 부분 등에 유지관리를 할 수 있는 밸브를 설치한다. (3) 수평배관에는 공기가 정체하지 않도록 해야 하며, 공기 정체가 예상되는 곳에는 공기빼기밸브를 설치한다. (4) 「주택건설기준 등에 관한 규정」 제 43 조에 따라 급수급탕 배관은 콘크리트 구조체안에 매설하여 서는 안 된다. 다만, 다음의 어느 하나에 해당하는 경우에는 그러하지 아니하다. ① 배관이 바닥면 또는 벽면 등을 직각으로 관통하는 경우 ② 구조안전에 지장이 없는 범위에서 덧관 등을 사용하여 미리 매설하여 배관하는 경우 ③ 배관의 매설이 부득이하다고 감리업무수행자에게 사전 승인한 경우로서 배관의 부식을 방지하 고 그 수선 및 교체가 쉽도록 하여 배관을 설치하는 경우 (5) 수돗물의 오염을 방지하기 위한 계량기 후단의 역류방지밸브를 설치해야 한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항 ~ 5 항) 추가 설명 없음 2. 용어 V 내용 없음 기계설비 기술기준 해설 (별표 05 국토교통부 203 | {}
49a76eee-a9c6-4e8c-8607-4810395f2b50 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3.2 급수설비 3.2.1 급수관 (1) 일반사항 ¦ ① 급수 배관에는 급수 이외의 물 배관이 연결되지 않도록 한다. 수 없 ¦ ¦ --- ¦ ¦ ② 토수구와 저수용기의 물넘침 면 사이에는 토수구 공간을 확보한다. 토수구 공간을 확보할 는 경우는 저수용기의 물넘침 선으로부터 150 mm 이상 위쪽 배관에 진공브레이커를 설치한다. ③ 음료수용 배관은 타 배관계통과 식별할 수 있도록 한다. ¦ ¦ 천장, 벽 등의 구조체를 통과 하는 ¦ ¦ ④ 배관이 부분에는 방화구획 상 지장이 없는 방법으로 관의 진동 이 구조체에 전달되지 않도록 고정한다. ¦ ¦ ⑤ 배관완료 후에는 관의 내부를 깨끗이 청소한다. ¦ ¦ (2) 급수배관 ¦ ¦ ① 수평관 배관한다. ¦ ¦ 가. 공기 및 물이 전부 빠질 수 있게 균일한 기울기로 공기빼기밸브, 물이 고일 수 있는 부분에는 배수밸브를 설치한 ¦ ¦ 나. 공기가 모일 수 있는 부분에는 다. ¦ ¦ ② 기기의 조작이나 점검과 보수가 주변에 압력계, 온도계 등의 필요한 계기를 설치한다. ¦ ¦ 쉽도록 배관하고, 그 ¦ ¦ ③ 급수관과 배수관이 평행으로 매설될 경우 양 배관의 수평간격은 500 mm 이상으로 하고 급수관 은 배수관 위에 매설한다. ¦ ¦ ¦ ¦ 수직배관에는 수격으로 인한 소음과 진동을 방지하고 역류에 의한 충격이 분산되도록 한다. ¦ ¦ ④ ⑤ 건물의 흔들림, 배관의 진동 등에 의한 변위를 흡수할 수 있는 이음을 설치한다. ¦ ¦ ¦ ¦ ¦ ¦ (3) 펌프 및 펌프유닛 주위의 배관 ¦ ¦ 상향 기울기로 배관한다. ¦ ¦ ① 양수관의 수평배관은 옥상물탱크를 향하여 ¦ ¦ ¦ ¦ ② 흡입 수평관은 될 수 있는 한 짧게 펌프를 향하여 상향 기울기로 배관하며 필요에 따라서 브를 설치한다. ¦ ¦ 차단밸 ¦ ¦ ③ 양수관의 운전중량 및 배관의 비틀림 하중이 직접 펌프에 걸리지 않도록 필요에 따라 방진이음, 플렉시블 ¦ ¦ 이음 등을 설치한다. ¦ ¦ ④ 펌프 베드와 콘크리트 기초 사이에 방진구를 넣는 경우에는 펌프 측과 모터 측에 합당한 것을 사 용한다. ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 해 설 1. 본문 해설 및 관련 법규 V (1 항, 3 항) 추가 설명 없음 V (2 항 1 호 ~ 3 호, 5 호) 추가 설명 없음 V (2 항 4 호) 저수탱크로부터 고가탱크까지는 급수 가압 펌프의 토출측 배관이 됨에 따라 고가탱크 가 고수위에 도달하여 펌프가 정지될 때, 입상관에서의 물기둥이 중력에 의해 하강함. 역류방지밸 브 토출 측에 워터해머흡수기를 설치하는 것은 역류방지밸브에 가해지는 에너지를 흡수하여 역 류방지밸브를 보호하기 위함 2. 용어 204 기계설비 기술기준 매뉴얼 | {}
c16378d0-7745-4d88-8db3-5c6fc0e78df2 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 내용 없음 3.2.2 급수펌프 (1) 수평형 및 수직형 원심펌프는 패드의 휩 또는 처짐이 발생하지 않도록 주의 하여 기초 위에 수평 또는 수직으로 고정하고, 기초 볼트의 조임은 균일하게 한다. (2) 펌프와 모터와 의 직결 주축은 정확하게 직선이 되도록 조정한다. (3) 필요에 따라서 방진기초를 한다. (4) 펌프에 밸브 및 관을 부착할 때는 그 운전중량이 직접 펌프에 걸리지 않도록 지지한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항 ~ 4 항) 이 기준 [별표 12]와 [별표 15]의 관련 내용을 참조하여 시공함 2. 용어 V 내용 없음 ----- -- 3.2.3 저수탱크 (1) 저수탱크를 옥외에 설치하는 경우에는 저수탱크 점검용 뚜껑을 이중으로 한다. (2) 점검 뚜껑에는 잠금장치를 부착한다. (3) 급수 저수탱크의 내부 및 상부로는 급수관 이외의 배관이 통과 되지 않도록 한다. (4) 저수탱크의 드레인 및 물넘침은 간접배수로 하며 오버플로관은 방충망을 부착한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항 ~ 4 항) 추가 설명 없음 2. 용어 V 내용 없음 국토교통부 205 기계설비 기술기준 해설 (별표 05 | {}
2da20bbe-a2b8-4037-bde7-9a8c2ea97cbb | 국내_기계설비_기술기준_매뉴얼_최종본 | 3.2.4 기타 부속장치 (1) 감압밸브 보수 관리에 필요한 공간을 고려하여 견고하게 설치한다. (2) 수격방지기 다음의 부위에는 수격방지기를 설치한다. ① 펌프 토출측 및 양수관의 구간에 설치된 역류방지밸브 근처 배관 ② 급수 배관계통의 전자밸브, 모터밸브 등 급 폐쇄형 밸브 근처 배관 해 설 1. 본문 해설 및 관련 법규 V (1 항) 추가 설명 없음 V (2 항 1 호) 모든 가압펌프 및 부스터 펌프 토출측 배관을 포함 2. 용어 V 내용 없음 ---- 206 기계설비 기술기준 매뉴얼 | {}
49ed5599-8f8e-4ed0-ada7-6a7f112c3f6b | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 3.3 급탕설비 3.3.1 급탕배관 및 기기 (1) 일반사항 ① 장비를 설치할 때는 본체 중심선이 기초의 중심선과 일치하게 한다. ② 장비 자체의 프레임과 기초 콘크리트 사이에는 철판제 라이너를 사용하여 수평을 조정한다. ③ 보일러, 펌프류, 급탕조 등의 앵커볼트는 매립용으로서 해당 장비의 규격에 맞는 것을 사용한다. ④ 기기류와 배관 사이에는 평행 간격을 유지한다. ⑤ 기기류는 사후 유지보수관리가 쉽도록 필요한 공간을 두고 설치한다. ⑥ 급수방식이 부스터펌프방식이나 압력탱크방식인 경우 밀폐식 팽창탱크를 설치한다. ⑦ 급탕설비의 도피관을 옥상물탱크에 개방하는 것은 수질오염의 위험이 있으므로 피한다. (2) 급탕배관 ① 배관이 천장, 벽 등의 구조체를 통과 하는 부분에는 방화구획 상 지장이 없는 방법으로 관의 진동 이 구조체로 전파되지 않도록 고정한다. ② 배관에는 관의 신축이 가능하도록 신축이음을 설치한다. 신축이음이 설치되는 배관에는 일정구 간에 고정점을 두고 신축 시 소음과 진동이 발생하지 않도록 한다. ③ 배관에는 균등한 기울기를 유지해야 하고, 역기울기 또는 공기고임 등으로 인하여 순환을 저해 할 우려가 있는 경우에는 보완장치를 한다. ④ 급탕계통에서는 온수의 원활한 순환을 저해하는 접속방법이나 시공 방법을 사용해서는 안 된다. (3) 기기 주위의 배관 ① 관에는 플랜지 및 밸브를 부착하여 기기류의 탈부착을 쉽게 한다. ② 배관의 운전중량이 직접 기기에 걸리지 않도록 지지 및 고정한다. ③ 보일러 및 온수저장탱크의 배수는 간접배수로 한다. ④ 팽창관은 단독배관으로 하고 밸브를 설치하지 않는다. ⑤ 안전밸브의 배수는 간접배수로 한다. ⑥ 온수탱크의 보급수관에는 역류방지밸브를 설치한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항 ~ 3 항) 추가 설명 없음 2. 용어 내용 없음 - 국토교통부 207 기계설비 기술기준 해설 (별표 05 | {}
0d495693-c9d5-4969-a604-37f0db1a0b0b | 국내_기계설비_기술기준_매뉴얼_최종본 | 3.3.2 급탕가열장치 (1) 난방겸용 급탕가열장치는 60°C 이하로 제한할 수 있는 온도조절밸브를 설치한다. (2) 유지관리, 정비, 교체가 편리하고 상태확인과 점검이 용이하도록 공간을 확보한다. (3) 압력릴리프 밸브와 온도릴리프 밸브의 배출관은 다음과 같이 설치한다. ① 배출밸브 출구 호칭지름 이상으로 설치하여 간접배수로 방류한다. ② 독립 배관을 하여 배출한다. ③ 트랩을 형성하지 말고 중력으로 배출될 수 있도록 설치한다. ④ 배출관에는 밸브를 설치하지 않는다. 해 설 1. 본문 해설 및 관련 법규 V (1 항 ~ 3 항) 추가 설명 없음 2. 용어 내용 없음 3.3.3 급탕탱크류 온수저장탱크, 팽창탱크 설치시 건축 기초위에 견고하게 설치하고, 유지관리 및 점검을 위한 공간을 확보한다. 해 설 1. 본문 해설 및 관련 법규 V 이 기준 [별표 12] 및 [별표 15]의 관련 내용을 참조하여 시공함 2. 용어 내용 없음 ------ ------ --- 3.3.4 온수공급 계량기 계량기와 의 접속에 연관 및 경질염화비닐관을 사용하지 않는다. 해 설 208 기계설비 기술기준 매뉴얼 | {}
37021950-9a0f-4c73-b23b-08b0e4a3ef0e | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 1. 본문 해설 및 관련 법규 V 추가 설명 없음 2. 용어 V 내용 없음 국토교통부 209 기계설비 기술기준 해설 (별표 05 | {}
290ce9e1-9a82-4ae4-b24f-8f47b0169e75 | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 6] 오 · 배수 통기 및 우수배수설비의 설계 및 시공 기준 1. 오 · 배수 통기 및 우수배수설비 일반사항 1.1 목적 이 기준은 건축물, 시설물 등에서 발생하는 오수나 잡배수 및 우수를 배수관 내 가스의 실내 누설 없 이 원활하게 건물 밖으로 배수하기 위하여 필요한 설계 및 시공 방법 등 세부 기술기준을 정함을 목 적으로 한다. 해 설 이 기준의 목적은 「기계설비법」 제 14 조(기계설비 기술기준)과 같은 법 영 제 2 조 및 [별표 1]에 근 거하여, 건축물이나 시설물에 필요한 오·배수 통기 및 우수배수설비의 설계 및 시공 시 기계설비 의 안전과 성능을 확보하기 위하여 필요한 기술적 요건을 규정하기 위함 「기계설비법」 제 14 조(기계설비 기술기준) ① 국토교통부장관은 기계설비의 안전과 성능확보를 위하여 필요 한 기술기준(이하 "기술기준이라 한다)를 정하여 고시하여야 한다. 이를 변경하는 경우에도 또한 같다. 1.2 적용범위 이 기준은 건축물, 시설물 등에 다음의 오 , 배수통기설비와 우수배수설비를 설치하는 경우에 대하 여 적용한다. (1) 오수배관 설비 (2) 배수배관 설비 (3) 통기배관 설비 (4) 우수배수 설비 (5) 오 、 배수용 펌프설비 (6) 기타 오 , 배수 배관 기기류 해 설 이 기준의 적용범위는 「기계설비법」 제 2 조제 1 호에 따른 건축물등에 같은 법 영 제 2 조에 따라 대 통령령으로 정한 오·배수 통기 및 우수배수설비를 설치하는 경우 및 그와 관련된 부속설비들을 포 함함 210 기계설비 기술기준 매뉴얼 | {}
6b2aa393-be48-4d52-b8a9-44f40c53c362 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 「기계설비법」 제 2 조(정의) 1. "기계설비"란 건축물, 시설물 등(이하 "건축물등"이라 한다)에 설치된 기계 · 기 구 · 배관 및 그 밖에 건축물등의 성능을 유지하기 위한 설비로서 대통령령으로 정하는 설비를 말한다. 「기계설비법 시행령」 제 2 조(기계설비의 범위) 「기계설비법」(이하 "법"이라 한다) 제 2 조제 1 호에서 "대통령령 으로 정하는 설비"란 별표 1 의 설비를 말한다. 「기계설비법 시행령」 [별표 1] 기계설비의 범위 4. 위생기구 · 급수 · 급탕 · 오배수 · 통기설비 : 건축물등에서 위생과 냉수 · 온수 공급, 오배수(���), 오배 수관 통기(��) 등을 위하여 설치된 기계 · 기구 · 배관 및 그 밖에 성능을 유지하기 위한 설비 6. 우수배수설비 : 건축물등에서 빗물을 외부로 배출하기 위하여 설치된 기계 · 기구 · 배관 및 그 밖에 성능 을 유지하기 위한 설비 1.3 타 규정과 의 관계 다음의 규정과 이 기준에서 정하는 내용이 상이한 경우에는 해당 규정을 따른다. (1) 「건축물의 설비기준 등에 관한 규칙」 (2) KDS 31 30 25 배수통기설비 설계기준 (3) KDS 31 30 35 우수설비 설계기준 (4) KCS 31 30 25 배수통기설비공사 표준시방서 해 설 V 이 기준과 타 규정 및 기준과 다른 경우에는 상기 규정에 명시된 내용을 따름 국토교통부 211 기계설비 기술기준 해설 (별표 06 | {}
5ca6d71c-79cc-46d0-a60a-d43039dfb421 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 오 · 배수 통기 및 우수배수설비 설계 2.1 오 · 배수 통기설비 2.1.1 일반사항 (1) 콘크리트구조체에 배관을 매설하거나 배관이 콘크리트구조체를 관통할 경우에는 「건축물의 설 비기준 등에 관한 규칙」제 17 조제 2 항제 6 호에 따라 구조체에 덧관을 미리 매설하는 등 배관의 부 식을 방지하고 수선 및 교체가 용이하도록 한다. (2) 급식시설에서는 오수관이나 배수관을 노출하지 않아야 한다. (3) 모든 트랩의 봉수보호를 위하여 기압차가 생기지 않도록 배수관에 통기관을 설계한다. (4) 화학배수관의 통기관은 오 、 배수배관의 통기관과 분리하고 대기로 인출한다. (5) 오 、 배수배관의 통기관은 이외의 다른 목적으로 사용하지 않아야 한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 배수 배관의 개선, 개량, 보수, 수선, 대수선 등의 필요한 조치 시 건축물 구조체의 훼손을 최 소화하기 위한 조치임 「건축물의 설비기준 등에 관한 규칙」 제 17 조(배관설비) ②제 1 항의 규정에 의한 배관설비로서 배수용으로 쓰이는 배관설비는 제 1 항 각호의 기준외 에 다음 각호의 기준에 적합하여야 한다. 6. 콘크리트구조체에 배관을 매설하거나 배관이 콘크리트구조체를 관통할 경우에는 구조체에 덧관을 미리 매 설하는 등 배관의 부식을 방지하고 그 수선 및 교체가 용이하도록 할 것 V (2 항) 급식시설이란 집단급식을 위한 조리, 배식 등의 작업을 위생적으로 하기 위한 실을 말하며, 식품 보관실을 포함함 V (3 항 ~ 5 항) 추가 설명 없음 2. 용어 V 내용 없음 ---- 212 기계설비 기술기준 매뉴얼 | {}
663f6241-e4d0-4745-8a3e-10c074f99783 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.1.2 오 · 배수배관 (1) 오 、 배수배관 호칭지름 산정은 [별표 8] 2.6 에 따른다. (2) 수평 오 、 배수배관은 일정한 기울기로 균일하게 정렬하여 설치한다. 수평 오 、 배수배관의 기울 기는 KDS 31 30 25(4.1.2) 표 4.1-1 에 따른 표 1 의 값 이상으로 한다. 표 1 수평 오배수배관의 기울기(KDS 31 30 25(4.1.2) 표 4.1-1) ¦ DN ¦ 최소 기울기 ¦ ¦ --- ¦ --- ¦ ¦ 65 이하 ¦ 1/50 ¦ ¦ 80~150 ¦ 1/100 ¦ ¦ 200 이상 ¦ 1/200 ¦ (3) 흐름 방향으로 오 、 배수관의 호칭지름은 축소하지 않아야 한다. (4) 수평지관을 수평주관에 연결할 때는 수직관에서 하류로 수직관 호칭지름의 10 배 이상 떨어진 수 평주관에 연결한다. (5) 세제를 사용하는 배수관은 하부에서 상부로 호칭지름의 40 배 이상 높이까지, 그리고 수평관은 굴 곡부에서 하류로 지름의 10 배 이상 떨어진 거리에서 연결하고, 도피통기관을 계획한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) [별표 8] 2.6 오 · 배수배관 2.6 오 · 배수배관 오 · 배수배관 호칭지름 산정은 최대 기구배수부하단위수를 사용하여 산정한다. V (2 항, 3 항) 추가 설명 없음 V (4 항) 수평주관의 배수 흐름에 의해 수평지관 또는 수직관으로 역류를 방지하기 위함 V (5 항) KDS 31 30 25 참고 KDS 31 30 25 세제를 사용하는 배수 수직관은 하부에서 상 부로 호칭지름의 40 배 이상 높이까지, 그리고 수평관은 굴곡부에서 하류로 관 지름의 10 배 까지 비누거품이 형성되므로 이 부분에는 배 수관을 연결하지 않으며 분리 배관한다. 거품 장애를 방지하기 위해서는 굴곡 부분을 줄이 고 도피통기관을 설치한다. ![image](/image/placeholder) U ▼ 통기수직관 오수 또는 잡배수 수직관 U : 40d U U D : 10d d: 관 내경 0 90° 수평 오프셋 국토교통부 213 기계설비 기술기준 해설 (별표 06 | {}
a0b72609-6d6c-44aa-acbe-114c230d6d15 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 용어 V 내용 없음 -- --- 2.1.3 오 , 배수펌프 ¦ (1) 일반사항 ¦ ¦ --- ¦ ¦ ① 중력으로 하수관에 배수할 수 없는 건물의 지하 오 , 배수는 뚜껑이 덮인 통기되는 집수정으로 모은 후 펌프로 양수하여 배출한다. ¦ ¦ ② 밸브 설치 시 펌프와 펌프배관 사이에는 배수역류방지밸브와 차단밸브를 설계한다. 밸브는 점검 이 가능하도록 한다. ¦ ¦ (2) 오수펌프 ¦ ¦ ① 오수펌프는 집수정의 내용물을 배수관에 자동으로 배출한다. ¦ ¦ ② 오수펌프의 유량과 압력은 예상사용 요구량에 적합하도록 한다. ¦ ¦ ③ 대변기용 배수펌프는 지름 50 mm 이하의 구형 고형물을 처리할 수 있어야 한다. ¦ ¦ ④ 대변기용 이외의 펌프는 지름 25 mm 이하의 구형 고형물을 처리할 수 있어야 한다. ¦ ¦ (3) 배수 역류방지밸브 ¦ ¦ 배수가 기구로 역류할 가능성이 있는 배수관에는 역류방지밸브를 설치한다. 역류방지밸브는 점검 이 가능한 곳에 설계한다. ¦ ¦ (4) 집수정 설계 ¦ ¦ 집수정 펌프와 피트 및 토출배관은 다음의 요구사항에 따라야 한다. ¦ ¦ ¦ ¦ ① 배수펌프의 유량과 압력은 예상 사용 요구량에 적합하도록 한다. ¦ ¦ 집수정은 ¦ ¦ ② 지름 450 mm 이상과 깊이 600 mm 이상으로 한다. 밀폐형인 경우는 2.1.5 에 따라 통 기를 한다. ③ 배수펌프는 배수가 상시 유입되는 곳은 최소한 2 대 이상을 설치하되 1 대는 예비를 두어야 한다. ¦ 해 설 1. 본문 해설 및 관련 법규 V (1 항 ~ 3 항) 추가 설명 없음 V (4 항 1 호, 2 호) 추가 설명 없음 V (4 항 3 호) 배수펌프의 고장을 대비하여 배수펌프는 1 대를 예비로 설치하여야 하며, 예비펌프의 용 량은 배수펌프 용량과 동일한 용량이어야 하며, 배수펌프의 운전을 예비펌프를 포함하여 교번운 전하도록 설계함을 권장함(엘리베이터용 배수펌프는 제외) 예) 2 대 설치 시 100%+100%, 3 대 설치 시 50%+50%+50% V (4 항 3 호) 다만, 상시 유입이 우려되지 않은 공동주택 동 지하 및 근린생활시설 등의 PIT 층에 설 치하는 배수펌프의 경우 1 대만 설치 가능함 2. 용어 214 기계설비 기술기준 매뉴얼 | {}
1670ece6-456e-4f6c-80b3-555bf2720d89 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 내용 없음 2.1.4 청소구 (1) 청소구 적용 장소 ① 건물 내의 모든 배수 수평관에는 배수관이 DN 100 이하인 경우는 15 m 이내, DN 100 을 넘는 경 우는 매 30 m 마다 ② 배수 수직관의 최하부 또는 그 부근 ③ 건물배수 수평주관과 부지배수관의 연결점 부근 ④ 배수 수평지관 및 배수 수평주관의 기점 ⑤ 배수관이 45°를 넘는 각도로 방향을 변경한 개소 ⑥ 상기 이외에 필요하다고 판단되는 개소 (2) 은폐 배관이나 바닥 밑 배관 또는 높이나 공간이 600 mm 이하의 좁은 공간에 설계하는 청소구는 마감 벽이나 바닥 또는 지면까지 연장하여 올리거나 건물 외부까지 연장한다. (3) 모든 청소구에는 점검구를 설계한다. 해 설 1. 본문 해설 및 관련 법규 (1 항 1 호, 2 항) 청소구 적용 장소 예시 Chart Type: line 바지 배우관 배우수평주관 배수수평지관 0.04 0.3 배수수직관 0.04 0.2 바 위 청소구 0.03 0.0 국토교통부 215 기계설비 기술기준 해설 (별표 06 | {}
8706ebc3-89eb-44dd-8d48-3eeaefdba124 | 국내_기계설비_기술기준_매뉴얼_최종본 | ![image](/image/placeholder) 바닥 위 청소구 15 m 이내 15 m 이내 (관 지름 100 mm 이하) 바닥 밑 청소구 30 m 이내 점검구 (관 지름 100 mm 이상) (b) 천정 내 배관 (c) 길이가 긴 수평배관 (3 항) 이 기준 [별표 15] 기계설비 유지관리를 고려한 설계기준 2.4 점검구 등의 기준을 함께 검토 해야 함 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 청소구 (CO = Clean Out) ¦ 오배수 배관이 막힐 경우 막힌 부분을 뚫기 위한 전용기구를 배관 내부로 쉽게 집어 넣을 수 있도록 T, Y-T, Y 또는 장반경 엘보 등를 설치하고 한쪽 구경을 캡이나 플럭 으로 막아 놓은 배관 부품. 출처: 배관공학 pp 420~425 ¦ ![image](/image/placeholder) 2.1.5 통기 오배수배관의 통기는 아래사항을 고려하여 결합통기, 신정통기, 각개통기, 루프통기 등 중에서 적합 한 방식을 선정하여 적용한다. (1) 통기관과 통기수직관이나 신정통기관은 통기관이 담당하는 가장 높은 기구의 물 넘침선 위 150 mm 이상에서 연결한다. 통기지관이나 도피통기관 또는 회로통기관의 수평 통기관 높이는 가장 높은 기구의 물 넘침선 위로 150 mm 이상 되어야 한다. (2) 통기관의 최소 호칭지름은 [별표 8] 2.7 에 따른다. (3) 크라운(정부) 통기는 트랩위어(weir)에서 호칭지름의 2 배 이내의 거리에는 통기관을 설계하지 않 아야 한다. (4) 2 개의 트랩이나 트랩이 달린 기구를 공용통기 할 수 있다. 공용 통기하는 트랩이나 트랩 달린 기 구는 같은 층에 있어야 한다. (5) 루프통기관 설치 시 배수 수평지관의 최대 8 개까지의 기구를 루프통기로 할 수 있다. 각 기구의 배수관은 루프통기 되는 수평지관에 수평으로 연결한다. (6) 추가 통기가 필요한 경우 기구들은 각개통기나 공용통기, 습통기, 회로통기 또는 배수통기 겸용 으로 통기한다. 해 설 1. 본문 해설 및 관련 법규 216 기계설비 기술기준 매뉴얼 | {}
3d420394-21f4-4823-b04e-7dae16a06c5b | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 V (1 항) 통기관 예시 Chart Type: line 통신수직관 통신수수정치관 통신 150mm 이상 140mm 이상 통신수수정치관 60mm 이상 210mm 이상 되는 최고위 기구의 넘침선 140mm 이상 5mm 이상 ![image](/image/placeholder) 신정통기관 공용통기관 신정통기관 입구 각개통기관 통기수직관 루프통기관 통기수평지관 도피통기관 모 습식 통기관 대변기 ▼ . 세면기 : 배수관 0 소변기 □ : 청소싱크 : 통기관 V (2 항) [별표 8] 2.7 통기배관 2.7 통기배관 통기관의 최소 호칭지름은 배관길이와 연결되는 총 기구배수부하단위로 결정한다. (3 항) 통기관을 정부에서 취출하게 되면 트랩의 봉수 증발을 가속시키고, 배수 시 배수가 통기관 내를 상승해서 통기의 역할을 방해하며, 물때가 부착되어 통기면적을 감소시키므로 금지함 (4) 공용 통기 적용 예 국토교통부 217 기계설비 기술기준 해설 (별표 06 | {}
c5d20feb-c047-4f1a-8e41-66b8b93f2698 | 국내_기계설비_기술기준_매뉴얼_최종본 | ![image](/image/placeholder) 공용통기관 공용통기관 세면기 청소싱크 세면기 xTd 상부 기구배수관경보다 1 구경 크게하고, 하부 기구배수관경보다 작게해서는 안됨 (a) 동일한 높이로 접속된 경우 (b) 높이가 다르게 접속된 경우 V (5) 루프통기 적용 예 ![image](/image/placeholder) 루프통기관 도피통기관 청소구 배수수평지관 배수수직관 통기수직관 V (6) 추가 설명 없음 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 결합통기, 결합통기관 ¦ 위생배수 입상관 으로부터 인출하여 통기입상관에 연결되는 도피통기관으로 위생배 수 입상관 내의 압력변화를 줄이거나 방지하기 위하여 설치한다. 결합통기관은 수직 배관에만 설치하는 것이다. 출처: 위생설비공학, p41 ¦ ¦ 신정통기관 ¦ 배수입상관의 끝을 지붕 위까지 연장시켜 통기관으로 겸용되는 배수관. 배수관과 통 기관의 연결은 최고층 전정 밑에서 이루어져야 한다. 출처: 위생설비공학, p46 ¦ ¦ 각개통기, 각개통기관 ¦ 1 개의 트랩을 위해 해당트랩 하류에서 통기관을 인출하여, 그 기구 보다 윗부분에서 통기계통에 접속하거나 또는 대기 중에 개구되는 통기관. 출처: 위생설비공학, p40 ¦ ¦ 루프통기 = 회로통기 ¦ 2 개 이상의 트랩을 보호하기 위해 최상류의 기구배수관이 배수횡지관에 접속하는 지점의 바로 하류에서 인출하여, 신정통기 관에 접속하는 통기관. 루프통기는 배수관(신정통기관)에 연결됨에 반하여, 회로 통기는 통기입 상관에 연결 되는 것이 다르다. 출처: 위생설비공학, p42 ¦ ¦ 크라운(정부) 통기 ¦ 트랩의 꼭대기나 배출구에서부터 지름의 2 배 이내인 위치에 접속되는 통기관 출처 : 공조냉동건축설비 용어사전 ¦ ¦ 트랩위어(trap weir) ¦ 관 트랩 등의 봉수부에서 배출시키는 정점이며, 둑에 해당하는 부분이다. 출처 : 공조냉동건축설비 용어사전 ¦ ---○ 218 기계설비 기술기준 매뉴얼 | {}
857084bb-f033-4a12-86cd-2cef736db2ba | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.1.6 간접배수와 특수 배수 (1) 간접배수 ① 식품 장비와 맑은 물 배수관, 모든 의료용 위생기구와 장치는 간접배수한다. ② 간접 배수관은 배수구와 의 공간을 두어 물받이 용기에 간접배수를 하고, 물받이 용기는 트랩 및 통기관을 설치하여 건물배수관에 연결한다. (2) 특수 배수 배수관에 해롭거나 유독가스를 발생하거나 배수처리과 정을 방해하는 부식성 액체나 폐산 또는 기 타 유해화학물질은 승인된 처리장치로 완전하게 처리한 후 위생배수관에 배출시켜야 한다. 해 설 1. 본문 해설 및 관련 법규 (1 항) 간접배수 적용 예 ![image](/image/placeholder) 냉장고, 주방기기 등 대기에 개구 신정통기관 배수구공간 수음기, 공기조화기 등 (a) 수수용기를 근접하여 설치하는 예 간접배수관 (단독으로 함) 식품세정용 싱크, 카운터 싱크 등 (주택의 조리용 싱크는 제외) 거리가 긴 경우는 트랩 설치 배수구공간 (500 mm 이상) 일반 배수계통으로 배수구공간 (b) 단독 배관하여 근처의 수수용기에 배관하는 예 (c) 동일한 기구의 종류를 모아서 배관하는 예 ![image](/image/placeholder) 간접배수관 배수구공간 바닥면 호퍼 (a) 바닥배수트랩 (b) 봉수 보급이 확실한 경우 간접배수관 간접배수관 배수구공간 지붕면 배수구공간 (c) 기구(청소용 싱크) (d) 지붕 등 V (2) 추가 설명 없음 국토교통부 219 기계설비 기술기준 해설 (별표 06 | {}
c0180f1f-ec3d-482d-8da6-96911abfd894 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 용어 내용 없음 2.1.7 배수트랩 배수트랩은 바닥배수트랩, U 트랩, 드럼트랩 등으로 아래의 사항을 고려한다. (1) 봉수깊이는 50~100 mm 로 한다. (2) 가동부분이 조립체 또는 칸막이에 의하여 봉수를 형성하는 구조가 아닌 것으로 한다. (3) 구조가 간단하고, 배수 시 자기세정이 가능한 구조로 한다. (4) 뚜껑 있는 트랩은 뚜껑을 열었을 때 배수관의 하류 측으로부터 하수가스가 실내에 침입하지 않는 구조로 한다. 해 설 1. 본문 해설 및 관련 법규 (1 항) 봉수 깊이 예 ![image](/image/placeholder) 크라운 기구로부터의 위어 P 트랩의 경우 배수 기구배수관 봉수심 벽면 50 ~ 100 mm 경우 S 트랩의 Deep 바닥면 봉수밀면 (1 항) 배수 트랩의 종류 ![image](/image/placeholder) P 트랩 ![image](/image/placeholder) S 트랩 U 트랩 (a) 사이펀트 랩(관트랩) ![image](/image/placeholder) 벨트랩 ![image](/image/placeholder) 역벨트랩 보틀트랩 드럼트랩 (b) 비사이펀트랩(격벽트랩) 220 기계설비 기술기준 매뉴얼 | {}
18ca7b51-e672-44ed-9d56-a0af5a0a4ab5 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2. 용어 내용 없음 2.2 우수배수설비 2.2.1 우수배수설비 일반사항 (1) 모든 지붕과 포장지역 그리고 옥외 마당의 우수는 분리된 우수관이나 하수관 또는 배출이 허용된 장소로 배수한다. (2) 우수는 하수전용 배수관에 배수하지 않는다. (3) 흐름 방향으로 배수관의 크기를 축소하지 않는다. (4) 이음쇠가 우수 흐름을 방해하거나 느리게 하지 않아야 한다. (5) 청소구가 필요한 경우 우수배관에는 청소구를 설계해야 하며, 청소구에 대해서는 2.1.4 에 따른 다. (6) 옥내 우수 수직관의 트랩 크기는 수직관이 연결되는 수평관과 같게 한다. 해 설 1. 본문 해설 및 관련 법규 V (2.2.1 1 항 ~ 6 항) 우수배관에 설치된 트랩은 현장 여건에 따라 생략 가능함 ![image](/image/placeholder) 지붕 루프드레인 루프드레인 수평 오프셋관 우수수직관 (파이프샤프트) 우수수직관 (외벽면) 우수수평주관 드라이 45° 지표 에이리어 지표 하수도로 드라이 에이리어 드레인 배수맨홀 우수조 트랩 기기장치에서의 배수 우수용 배수펌프 배수수평주관 2. 용어 내용 없음 기계설비 기술기준 해설 (별표 06 국토교통부 221 | {}
ba408cf9-b1b8-4dd1-9e56-5f8f1d0a5ec9 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2.2.2 우수배수관 호칭지름 선정 (1) 호칭지름 기준 우수배수관 호칭지름은 [별표 8] 2.8 에 따른다. (2) 수직 벽 루프드레인과 우수관 호칭지름을 정할 때, 지붕으로 빗물이 흐르는 모든 수직 벽 면적의 1/2 을 수 평투영 지붕 면적에 더하여 옥내의 우수 수직관과 우수 수평관의 크기를 정한다. 해 설 1. 본문 해설 및 관련 법규 (1 항) [별표 8] 2.8 에 따름 2.8 우수배수관 (1) 옥내 우수 수직관과 수평 지관의 호칭지름은 그 지역의 기상자료에 의한 시간최대강우량을 기준으로 한 다. (2) 최대 수평투영 지붕 면적으로 선정한다. [별표 8] 2.8 (1) 기상청 날씨누리 기후자료 참고 Inzhvaltagowatortinavotating/of/penught13=08y0& V (2 항) 경사지붕과 외벽면 수평투영면적 산정 예 ![image](/image/placeholder) 비 비 외벽면적 30° 지붕 a[m2] 실면적 a[m2] 0 60° 수평투영면적 수평투영면적 A = a COS 60° A = a COS 0 [m2] = 0.5a[m2] 20 층 이상인 경우 10 개층 수직벽면적 + 10 개층당 1 개층 수직벽면적 예) 65 층 이면 => 10 + (65-20)/10 = 14.5 개층 2. 용어 내용 없음 --- 222 기계설비 기술기준 매뉴얼 | {}
ae478a0a-c061-490e-b9e2-3b4fa8eab4d8 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.2.3 우수배수관의 연결 (1) 사용 금지 우수 수직관은 오수관이나 배수관 또는 통기관으로 사용하지 않아야 하고, 오수관이나 배수관 또는 통기관도 우수 수직관으로 사용하지 않아야 한다. (2) 우수와 위생배수의 연결 건물의 위생배수관과 우수관을 완전히 분리한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 추가 설명 없음 V (2 항) 공동주택 내부에 설치된 배수구는 실외기실 그릴를 통해 유입되는 빗물 배수를 위한 배수구 이기 때문에 우수관과 연결하여 배수 가능함 2. 용어 내용 없음 ---- 2.2.4 집수정과 펌프장치 (1) 펌프 유량과 압력 집수정 펌프는 예상 사용조건에 맞는 유량과 압력을 가져야 한다. (2) 집수정 집수정은 점검이 가능하고 모든 배수가 집수정에 중력으로 흐를 수 있는 곳에 설계한다. (3) 배관 배출관은 차단밸브와 배수역류방지밸브를 갖추어야 한다. 배관과 이음쇠의 크기는 펌프 토출관과 같거나 커야 한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항 ~ 3 항) 추가 설명 없음 2. 용어 V 내용 없음 - --- 국토교통부 223 기계설비 기술기준 해설 (별표 06 | {}
e2cd5011-50e5-46e4-9306-11354d0f014b | 국내_기계설비_기술기준_매뉴얼_최종본 | 2.2.5 공동구 배수설비 (1) 집수정 집수정의 크기는 유입수를 30 분 이상 저장할 수 있어야 한다. 모래 등과 같은 이물질이 유입될 수 있는 경우에는 침사탱크와 이물질 거름 막 등을 설계하여 청소가 쉬운 구조로 한다. (2) 배수펌프 배수펌프는 수중모터펌프 형식으로 하고 전체 펌프의 유량은 시간최대 유입수량의 200% 이상으로 한다. (3) 수위계측기 집수정에는 수위계측기를 설치하여 배수펌프 기동 정지와 고수위 경보를 한다. (4) 유지보수 배수펌프를 유지보수 할 수 있는 공간이 있어야 하며, 배수펌프를 인력으로 인양하기 불가능할 경 우에는 상부에 펌프 인양장치를 설계한다. (5) 배관 배출관에 차단밸브와 배수역류방지밸브를 설계한다. 배관과 이음쇠의 크기는 펌프 토출관 이상으 로 한다. 해 설 1. 본문 해설 및 관련 법규 해당 기준은 공동구 전용 공사 등에 적용하며, 공동주택 공동구에는 해당하지 않음 2. 용어 내용 없음 - ---- ----- -- 224 기계설비 기술기준 매뉴얼 | {}
63adf1c9-494b-4a54-927b-cb0f711c589f | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 3. 오 · 배수 통기 및 우수배수설비 시공 3.1 일반사항 (1) 오 . 배수관의 원활한 흐름을 유지 할 수 있도록 구배를 주어야 하고, 유지보수 및 점검이 용이하 도록 설치한다. (2) 막힘, 정체에 따른 흐름의 정체가 일어날 수 있는 배관을 설치하지 않아야 한다. (3) 오 . 배수 배관에서 배수수직관의 호칭지름은 흐름방향으로 관을 축소해서 설치하지 않아야 한 다. (4) 우수배관은 타용도의 배관과 혼용 설치하지 않아야 하며, 우수 전용 단독관으로 설치하여 배수할 수 있도록 설치한다. (5) 청소구는 관내를 점검하고 청소할 수 있도록 설치하며 청소구 설치 위치에 작업을 할 수 있는 공 간을 확보해야 한다. (6) 통기 설비는 배수가 원활히 될 수 있는 통기 방식으로 오 , 배수 배관에 설치한다. (7) 모든 통기관은 관내의 물방울이 자연유하에 의해서 흐를 수 있도록 해야 하며, 역구배가 되지 않 도록 오 、 배수관에 연결해야 한다. (8) 배수용 배관설비는 2.1.1(1)의 기준에도 불구하고 구조체에 슬리브를 미리 매립이 어려운 경우에 는 감리업무수행자와 협의 하여 설치할 수 있다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 배수구배는 이 기준 2.1.2 (2)의 기준을 준수함 V (2 항 ~ 7 항) 추가 설명 없음 V (8 항) 해당 기준 준수가 어려운 사유를 명확히 하고, 해당 내용을 해당부분의 시공사진과 함께 준 공 도서 등에 표시하여 향후 유지관리자에게 전달되어야 함 2. 용어 V 내용 없음 --- ----- ---- -- 기계설비 기술기준 해설 (별표 06 국토교통부 225 | {}
008e5823-2d45-4317-ab2d-4219bf4a2fc0 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3.2 오 · 배수 통기설비 3.2.1 배관 (1) 일반 배수관 ① 기구와 배수관은 누수, 누기되지 않도록 접속한다. ② 공동주택 등 주거용 건물은 배수에 의한 유수 소음 차단을 위한 저소음 제품을 사용한다. ③ 배수 주관과 지관 등이 합류하는 경우는 반드시 45° 이내의 예각으로 하고 수평 기울기로 합류시 킨다. ④ 연관을 굽히는 경우는 단면이 원형을 잃지 않도록 가공하고 그 구부러진 부분에 다른 배수관을 접속시키지 않는다. ⑤ 배수수직관에는 필요에 따라 만수시험용 이음쇠를 설치한다. ⑥ 배수수직관의 최하부에는 도면 또는 특기에 따라 지지대를 설치한다. ⑦ 배수관에는 2 중트랩을 사용하지 않는다. ⑧ 배수수평주관 또는 수평지관에는 T 형 이음쇠, 크로스 이음쇠를 사용하지 않는다. ⑨ 배수계통 배관의 중간에는 유니언 또는 관 플랜지를 사용하지 않는다. ⑩ 옥내배수관의 방향 변환은 적정한 이형관을 사용하여 시공한다. ⑪ 동결의 염려가 있는 장소나 지역에서는 적절한 보호를 하며 건물의 외측에 노출시키거나 외벽의 중간에 은폐시켜 배관하지 않는다. ⑫ 배수관에는 구멍을 뚫어 나사를 내거나 용접하지 않는다. 해 설 1. 본문 해설 및 관련 법규 V (1 항 1 호) 추가 설명 없음 V (1 항 2 호) 공동주택 저소음 배수관은 「녹색건축 인증 기준」에 따른 녹색건축인증기준 해설서에 따라 최대소음도 차이 5 dB 이상인 배관 적용 시 적합한 것으로 함. 단, PS 실 내부에 설치된 배수 수직관은 저소음 배관 제외 가능함 「녹색건축 인증 기준」 7.9 화장실 급배수 소음 저소음형 배수관에는 배관 내에 소음저감을 목적으로 장치나 부품(재료 포함) 등을 설치하는 공법을 포함하 며, 동일한 장소(공동주택 화장실이나 이와 동등하게 구축된 시험용 주택의 화장실) 및 측정조건(동일한 변 기 타입, 동일한 배수량, 하부층의 천장마감이 없는 상태 등)에서 실시한 일반용 경질 폴리염화비 닐관(KS M 3404)과 측정대상 배수관(공법 포함)과의 최대 소음도(Lmax) 차이로서 판단함 출처 : 녹색건축인증기준 해설서_신축주거용_2016-5 V (1 항 3 호 ~ 6 호) 추가 설명 없음 V (1 항 7 호) 이중트랩으로 하면 트랩간의 배관부분이 폐쇄상태가 되어 공기가 배출될 장소가 없고, 관내에 압력 변동을 가져와 배수의 흐름에 악영향을 미치므로 아래의 예와 같이 배관하는 것은 금지함 다만, 두 트랩 사에에 도피 통기관을 두는 경우는 예외로 함 226 기계설비 기술기준 매뉴얼 | {}
7f3739d4-9f55-4238-9da9-ac641fd861ec | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 ![image](/image/placeholder) 세면기 실험싱크 세면기 실험싱크 드럼트랩 (잘못된 예) (바른 예) (a) 드럼트랩에 복수의 기구를 설치하는 경우 싱크 통기관 싱크 통기관 트랩피트 (잘못된 예) (바른 예) (b) 트랩피트로의 배관 (1 항 8 호 ~ 11 호) 추가 설명 없음 V (1 항 12 호) 이 기준은 자연 배수배관에 적용함 2. 용어 내용 없음 국토교통부 227 기계설비 기술기준 해설 (별표 06 | {}
0547fb9a-5d5f-42f3-a3b4-ff4015f31143 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3.2 오 · 배수 통기설비(계속) 3.2.1 배관(계속) (2) 통기관 ¦ ① 일반사항 ¦ ¦ --- ¦ ¦ 가. 통기수직관은 우수수직관으로 사용하지 않아야 한다. 나. 통기수직관의 상부는 그 상단을 단독으로 대기 중에 노출시키거나 또는 가장 높은 위치에 있 는 기구의 물넘침 수위에서 150 mm 이상 높은 위치에서 신정통기관에 연결한다. 다. 통기수직관의 하부는 가장 낮은 위치의 배수수평지관보다 낮은 위치에서 45° Y 형관을 사용하 여 배수수직관에 연결한다. 라. 수평주배수관에서 뽑아 낸 통기관은 수평주배수관의 중심선 상부에서 수직되지 않은 것은 45° 이내의 각도에서 분기하고 근처의 고정할 장소에 세워 올린 후, 그 배수계통의 가장 높은 위치에 있는 기구의 물넘침 수위로부터 150 mm 이상 높이에서 수평배관하거나 또는 통기지 관에 연결한다. 마. 간접배수의 통기는 단독배관으로 한다. ② 결합통기 결합통기 하단은 그 층에서 나오는 배수지관이 배수수직관에 접속하는 곳의 아래로부터 Y 형관을 사용하여 수직관에서 분기한다. 또 그 상단은 그 층의 바닥면에서 800 mm 이상 위쪽에서 Y 형 관을 사용하여 통기수직관에 연결한다. ③ 각개통기 가. 대변기나 기타 이와 유사한 기구류를 제외한 통기관은 트랩위어 보다 높은 위치에서 분기한 다. 나. 각개 통기관은 트랩위어에서 호칭지름의 2 배 이상 떨어진 지점에서 분기한다. ④ 루프통기 가. 배수수평주관의 최상류의 기구배수관이 접속한 직후의 하류 측의 위치에서 분기한다. 나. 루프 통기관은 통기 수직관 또는 신정 통기관에 연결하거나 단독으로 대기에 개방한다. ⑤ 신정통기 배수수직관에는 신정 통기관을 설치하며 호칭지름은 배수수직관의 호칭지름 이상으로 한다. ¦ 해 설 1. 본문 해설 및 관련 법규 V (2 항 1 호 가) 추가 설명 없음 V (2 항 1 호 나) 이 기준 [별표 6] 2.1.5 설명 참조 V (2 항 1 호 다, 라) 통기수직관의 하부와 배수수직관 연결 예시 228 기계설비 기술기준 매뉴얼 | {}
e34f5f68-75a3-4d8d-b7df-214593bc6e39 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 ![image](/image/placeholder) 신정통기관 D 최고 위치에 있는 기구의 오버 플로우선보다 150 mm 이상 (또는 직접 대기에 개구) 90° 이내 각에서 신정통기관에 접속 통기수직관 배수수직관 45° 이내 각도로 통기관 입상 (또는 배수수평주관으로부터 입상) 최하부와 배수수평지관보다 하부에서 입상 1.5~2 m 이상 V (2 항 1 호 마) 추가 설명 없음 V (2 항 2 호) 결합통기 예시 ![image](/image/placeholder) 45 배수수직관 800 mm 바닥면 b 결합통기관 배수수평지관 통기수직관 45° a a 는 b 보다 하단일 것 (2 항 3 호 ~ 5 호) 추가 설명 없음 2. 용어 내용 없음 국토교통부 229 기계설비 기술기준 해설 (별표 06 | {}
6fce69ff-efaf-48c0-aea8-c49a31b521e5 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3.2 오 · 배수 통기설비(계속) 3.2.1 배관(계속) (3) 간접 배수관 ① 기기, 장치의 배수 및 오버플로관은 KCS 31 30 25(3.10.2) 표 3.10-2 에 따른 표 2 에 따라서 간접 배수로 한다. ② 배관길이가 600 mm 를 넘는 간접배수관에는 그 기기 및 장치에 근접하여 트랩을 설치한다. ③ 간접배수관은 쉽게 청소 및 세척할 수 있도록 배관한다. ④ 간접배수를 받는 물받이 용기는 화장실, 세면실, 쉽게 접근할 수 없는 장소, 환기가 되지 않는 장 소 등에 설치하지 않는다. ⑤ 간접배수를 받는 물받이 용기를 바닥면 보다 낮게 설치하여 U 트랩을 사용하는 경우에는 그 청소 구를 바닥면까지 연장하여 설치한다. 표 2 간접배수 대상 기기(KCS 31 30 25(3.10.2) 표 3.10-2) ¦ 기기 및 장치의 종류 등 ¦ 기기 및 장치명 ¦ ¦ --- ¦ --- ¦ ¦ 냉장관련기기 ¦ 냉장고, 냉동차, 쇼케이스 등의 식품냉장, 냉동기기 ¦ ¦ 주방관련기기 ¦ 야채껍질 벗기는 기계, 쌀 씻는 기계, 찜기, 스팀테이블, 제빙기, 식품세척기, 소독기, 카운터 설것이대, 식품세척기, 식품세척용 싱크 ¦ ¦ 세탁관련기기 ¦ 세탁기, 탈수기 등의 세탁용 기기 ¦ ¦ 음수기 ¦ 음수기, 식료용 냉수기 ¦ ¦ 의료, 연구용기기 ¦ 증류수 장치, 멸균기, 소독기, 세척장치 등의 의료, 연구용 기기 ¦ ¦ 수영용 풀장 ¦ 풀장 자체의 배수, 주변에 설치된 오버플로의 배수, 주변 보도의 바닥배수 및 여과 장치의 역세수 등 ¦ ¦ 분수 ¦ 분수지 자체의 배수 및 오버플로 중에서 여과 장치의 역세수 등 ¦ ¦ 배관, 장치의 배수 ¦ 각종 탱크의 배수, 및 오버플로 입구의 배수, 펌프의 배수, 결로수 등의 배수, 각종 배관계통의 물빼기, 물자켓의 배수, 냉각탑, 공조기, 팬코일유닛 등의 배수, 증기계 통 등의 배수 ¦ 해 설 1. 본문 해설 및 관련 법규 V (3 항 1 호 ~ 5 호) 간접 배수관에 트랩을 설치하는 목적은 악취의 역류를 막기 위한 것으로, 상기 기준에도 불구하고 간접 배수관에서 악취의 역류가 발생되지 않는 것이 명확한 간 접 배수관에는 트랩을 설치하지 않을 수 있음 2. 용어 V 내용 없음 -- 230 기계설비 기술기준 매뉴얼 | {}
25f139ad-9245-4248-ac60-1358f3396112 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 3.2.2 오 · 배수 펌프 (1) 배수용 횡형원심펌프, 배수용 자흡식원심펌프 [별표 5] 3.2.2(1)의 급수용 원심펌프에 따른다. (2) 배수용 입형펌프 ① 집수정 내부 설치형 가. 받침대를 기초위에 수평으로 설치하고, 기초 볼트를 균등하게 조여 고정시킨다. 나. 펌프의 설치장소는 보수관리에 필요한 공간, 펌프의 반입 및 반출에 필요한 천장고가 있는 장 소로 하고 천장에 탈착용 훅을 설치한다. ② 집수정 외부 설치형 가. 펌프 흡입구와 배수탱크와 의 사이에는 차단밸브를 설치한다. 나. 배수탱크와 펌프케이싱 접속관이 배수탱크를 관통한 장소에는 플랜지가 달린 슬리브를 설치 하고 접속관과 슬리브 틈새는 코킹하여 배수탱크에서 누수가 없도록 한다. (3) 배수용 수중모터펌프 ① 펌프 케이싱의 외측에서 배수집수정 벽면과 바닥면까지의 거리는 200 mm 이상으로 한다. ② 흡입부의 하부에서 저수면까지의 거리는 300 mm 이상, 밑면에서 집수정 벽면까지 및 배수피트 바닥까지의 거리는 200 mm 이상으로 한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) [별표 5] 3.2.2 (1) 3.2.2 급수펌프 (1) 수평형 및 수직형 원심펌프는 패드의 휩 또는 처짐이 발생하지 않도록 주의 하여 기초 위에 수평 또는 수 직으로 고정하고, 기초 볼트의 조임은 균일하게 한다. V (2 항 1 호, 2 호) 추가 설명 없음 V (3 항 1 호, 2 호) 추가 설명 없음 2. 용어 V 내용 없음 --- ----- 국토교통부 231 기계설비 기술기준 해설 (별표 06 | {}
282b4e55-6cfb-45b5-868e-ebfa781f8f9b | 국내_기계설비_기술기준_매뉴얼_최종본 | 3.2.3 청소구 (1) 청소구는 청소가 쉬운 위치에 설치한다. 주위에 있는 벽, 바닥 및 대들보 등이 청소에 지장을 주는 장소에서는 청소구로부터 DN 65 이하의 관은 300 mm 이상, DN 75 이상의 관은 450 mm 이상 의 공간을 둔다. (2) 은폐배관의 청소구는 벽 또는 바닥 마감면과 동일면까지 연장하여 설치하며, 청소구의 위를 모르 타르, 석고, 반죽석회 등의 재료로 덮어서는 안 된다. 부득이 청소구를 은폐하는 경우에는 그 청소 구 전면 또는 상부에 뚜껑을 설치하거나 그 청소구에 쉽게 접근할 수 있는 위치에 점검구를 둔다. (3) 모든 청소구는 배수의 흐름과 반대 또는 직각으로 열 수 있도록 설치한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항 ~ 3 항) 추가 설명 없음 2. 용어 V 내용 없음 3.3 우수배수설비 (1) 우수배관은 옥외까지 단독으로 배관하여 배출할 수 있도록 시공한다. (2) 우수수직관을 배수수직관 또는 통기관과 겸용하는 방식으로 시공하지 않도록 한다. (3) 우수 수평주관을 부득이 합류식의 배수 수평주관에 접속하는 경우는 Y 형관을 수평으로 사용하고 이때 어느 배수 수직관의 접속점에서 3m 하류에 접속한다. (4) 온도변화, 건물구조 및 그 밖의 이유로 필요성이 인정되는 경우는 신축이음 또는 슬리브를 설치 한다. (5) 기타사항은 [별표 8] 3. 배관설비 시공에 따른다. 해 설 1. 본문 해설 및 관련 법규 V (1 항 ~ 3 항, 5 항) 추가 설명 없음 V (4 항) 건축물 현장의 상황과 여건에 따라 판단함 2. 용어 V 내용 없음 --- ○----- -- 232 기계설비 기술기준 매뉴얼 | {}
3d9c1341-01ea-4ed6-931e-5cb05706c549 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 [별표 7] 오수정화 및 물재이용설비의 설계 및 시공 기준 1. 오수정화 및 물재이용설비 일반사항 1.1 목적 이 기준은 건축물, 시설물 등에서 발생하는 오수를 침전과 분해 등의 방법으로 처리하는 오수정화 처 리시설과 건축물의 지붕면 등에 내린 빗물을 모아 재이용하는 빗물이용설비, 그리고 사용한 물을 음 용수 이외의 생활용수 및 공업용수 등으로 재활용하는 중수이용설비의 설치를 위하여 필요한 설계 및 시공 방법 등 세부 기술기준을 정함을 목적으로 한다. 해 설 이 기준의 목적은 「기계설비법」 제 14 조(기계설비 기술기준)과 같은 법 영 제 2 조 및 [별표 1]에 근 거하여, 건축물이나 시설물에 필요한 오수정화 및 물재이용설비의 설계 및 시공 시 기계설비의 안전과 성능을 확보하기 위하여 필요한 기술적 요건을 규정하기 위함 「기계설비법」 제 14 조(기계설비 기술기준) ① 국토교통부장관은 기계설비의 안전과 성능확보를 위하여 필요 한 기술기준(이하 "기술기준이라 한다)를 정하여 고시하여야 한다. 이를 변경하는 경우에도 또한 같다. 1.2 적용범위 이 기준은 건축물, 시설물 등에 다음의 설비와 시설을 설치하는 경우에 대하여 적용한다. 단, 배출기 준 등은 관련 법령과 설치 할 지역의 조례에 따른다. (1) 오수정화 처리시설 내의 기계설비 배관 및 장비 (2) 빗물재이용설비 (3) 중수이용설비 해 설 이 기준의 적용범위는 「기계설비법」 제 2 조제 1 호에 따른 건축물등에 같은 법 영 제 2 조에 따라 대 통령령으로 정한 오수정화 및 물재이용설비를 설치하는 경우 및 그와 관련된 부속설비들을 포함 함 「기계설비법」 제 2 조(정의) 1. "기계설비"란 건축물, 시설물 등(이하 "건축물등"이라 한다)에 설치된 기계 · 기 구 · 배관 및 그 밖에 건축물등의 성능을 유지하기 위한 설비로서 대통령령으로 정하는 설비를 말한다. 「기계설비법 시행령」 제 2 조(기계설비의 범위) 「기계설비법」(이하 "법"이라 한다) 제 2 조제 1 호에서 "대통령령 으로 정하는 설비"란 별표 1 의 설비를 말한다. 「기계설비법 시행령」 [별표 1] 기계설비의 범위 5. 오수정화 · 물재이용설비 : 건축물등에서 오수를 정화하여 배출하거나 정화된 물을 재이용하기 위하여 설 치된 기계 · 기구 · 배관 및 그 밖에 성능을 유지하기 위한 설비 국토교통부 233 기계설비 기술기준 해설 (별표 07 | {}
12840734-6da9-4110-a233-c92b901333d1 | 국내_기계설비_기술기준_매뉴얼_최종본 | 1.3 타 규정과 의 관계 다음의 규정과 이 기준에서 정하는 내용이 상이한 경우에는 해당 규정을 따른다. (1) KDS 31 30 30 오수처리설비 및 물재이용설비 설계기준 (2) KCS 31 30 30 오수정화 및 물재이용설비공사 표준시방서 해 설 이 기준과 타 규정 및 기준과 다른 경우에는 상기 규정에 명시된 내용을 따름 234 기계설비 기술기준 매뉴얼 | {}
46c7781c-d051-427c-88a6-da27652e3aec | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2. 오수정화 및 물재이용설비 설계 2.1 일반사항 건축물과 시설 등에서 발생하는 오수를 침전과 분해 등의 방법으로 처리하는 개인 하수처리시설과 건축물의 지붕면 등에 내린 빗물을 모아 재이용하는 빗물이용시설, 그리고 수자원 절약을 위한 중수 처리시설에 대하여 적용한다. 해 설 1. 본문 해설 및 관련 법규 이 기준의 적용범위는 「하수도법」 제 2 조제 1 호에 따른 건축물등에 같은 법 영 제 2 조에 따라 대통 령령으로 정한 오수정화 및 물재이용설비를 설치하는 경우 및 그와 관련된 부속설비들을 포함함 2. 용어 V 내용 없음 - 2.2 개인하수처리시설 오수를 배출하는 건축물이나 시설 등을 설치하는 자는 「하수도법」에 따른 「개인하수처리시설의 설 치기준」에 따라 단독 또는 공동으로 개인하수처리시설을 설치한다. 2.2.1 오수발생량 건축물의 용도별 오수발생량과 정화탱크 처리대상인원은 환경부 관련 고시 기준에 따른다. 2.2.2 성능기준 개인하수처리시설 제품의 구조와 규격, 재질, 성능기준은 「하수도법」에 따른다. 2.2.3 방류수 수질기준 개인하수처리시설의 방류수 수질기준은 「하수도법」에 따른다. 2.2.4 설치기준 개인하수처리시설의 세부 설치기준은 「하수도법」에 따른다. 2.2.5 배수펌프. 배수펌프의 유량은 시간최대 처리 수량을 30 분 이내에 배출할 수 있는 용량 이상으로 하고, 예비펌프 와 탈착장치를 구비한다. 2.2.6 냄새 오수정화탱크에서 취기 발생의 우려가 있는 경우에는 탈취장치를 설치한다. 해 설 1. 본문 해설 및 관련 법규 V 이 기준에서 「하수도법」은 「하수도법 시행령」 별표 1 의 6 을 말함 V (2.2.1)건축물의 용도별 오수발생량과 정화탱크 처리대상인원 국토교통부 235 기계설비 기술기준 해설 (별표 07 | {}
b9e197e6-d84f-4c06-aeb7-6ed31e6e6c90 | 국내_기계설비_기술기준_매뉴얼_최종본 | 「하수도법 시행령」 제 24 조(개인하수처리시설의 설치) ![image](/image/placeholder) 법 제 34 조제 4 항에 따른 개인하수처리시설의 설치기준은 다음 각 호의 구분에 따른다 1 일 오수발생량 오수처리시설 2 m2 초과 하수처리 Yes 구역 외 1 일 오수발생량 특별지역,상수도보호구역, 수변구역 또는 민원 발생이 2 m2 이하 우려되는 경우 No 합류식 하수관거지역 단독정화조 하수처리 구역 내 분류식 배수설비 하수관거 지역 예외 ① 하수처리구역 외 기존 정화조 120/100 이하의 오수발생량 증대의 경우 ② 하수처리구역 내 기존 정화조 200/100 이하의 오수발생량 증대의 경우 ⑤ 제 2 항부터 제 4 항까지의 규정에 따른 개인하수처리시설의 설치기준에 관한 오수발생량 산정기준은 환경 부장관이 정하여 고시한다. 환경부고시 제 2021-59 호 : 건축물의 용도별 오수발생량 및 정화탱크 처리대상인원 산정방법 V (2.2.2) 개인하수처리시설 제품의 구조와 규격, 재질, 성능기준 「하수도법 시행규칙」 제 55 조(개인하수처리시설 제조제품의 구조 및 규격 등의 기준) 법 제 52 조제 3 항에 따른 개인하수처리시설 제조제품의 구조 · 규격 · 재질 및 성능에 관한 기준은 별표 12 와 같다. [별표 12] 개인하수처리시설 제조제품의 구조·규격·재질 및 성능 기준 V (2.2.3) 개인하수처리시설의 방류수 수질기준 「하수도법 시행규칙」 제 3 조(개인하수처리시설의 설치) 법 제 7 조제 1 항에 따른 방류수수질기준은 다음 각 호와 같다. 1. 공공하수처리시설 · 간이공공하수처리시설의 방류수수질기준은 별표 1 과 같다. 2. 분뇨처리시설의 방류수수질기준은 별표 2 와 같다. 다만, 공공하수처리시설로 유입하여 처리하는 분뇨처 리시설은 분뇨처리시설의 방류수수질기준을 적용하지 아니한다. 3. 개인하수처리시설의 방류수수질기준은 별표 3 과 같다. 다만, 공공하수처리시설이나 「물환경보전법」 제 48 조에 따른 공공폐수처리시설로 유입하여 처리하는 개인하수처리시설은 개인하수처리시설의 방류수수질 기준을 적용하지 아니한다. [별표 1] 공공하수처리시설 · 간이공공하수처리시설의 방류수수질기준(제 3 조제 1 항제 1 호 관련) [별표 2] 분뇨처리시설의 방류수수질기준(제 3 조제 1 항제 2 호 관련) [별표 3] 개인하수처리시설의 방류수수질기준(제 3 조제 1 항제 3 호 관련) V (2.2.4) 개인하수처리시설 설치 기준 236 기계설비 기술기준 매뉴얼 | {}
1cb46ac3-271a-4755-846a-e5fd0e1d52a5 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 「하수도법 시행령」 제 24 조(개인하수처리시설의 설치) ③ 제 2 항에 따른 개인하수처리시설의 설치기준에 관한 세부 내용은 별표 1 의 5 와 같다. [별표 1 의 5] 개인하수처리시설의 설치 1. 개인하수처리시설의 규모는 처리대상 오수를 모두 처리할 수 있는 규모 이상이어야 한다. 2. 정화탱크는 법 제 52 조제 3 항에 따라 환경부령으로 정하는 구조 및 규격기준에 맞아야 한다. 3. 시설물의 윗부분이 밀폐된 경우에는 뚜껑(오수처리시설의 경우 지름 60 cm 이상, 정화탱크의 경우 처리 대상 인원이 10 명 이하는 45 cm 이상, 20 명 이하는 50 cm 이상, 30 명 이하는 55 cm 이상, 31 명 이상은 60 cm 이상)을 설치하되, 뚜껑은 밀폐할 수 있어야 하며, 잠금장치를 설치하거나 뚜껑 밑에 격자형의 철 망 등을 설치하는 등 안전하게 설치하여야 한다. 3 의 2. 시설물의 뚜껑이 보행자 또는 차량의 통행이 가능한 곳에 노출된 경우에는 주변과 구별될 수 있도록 색칠을 하고, 뚜껑의 상부에는 보행자 및 차량의 접근 주의 를 알리는 안내문을 새겨야 한다. 4. 시설물은 구조적으로 안정되어야 하고 천정·바닥 및 벽은 방수되어야 한다. 5. 시설물은 부식 또는 변형이 되지 아니하여야 한다. 6. 시설물은 발생가스를 배출할 수 있는 배출장치를 갖추어야 하되, 배출장치는 이물질이 유입되지 아니하 는 구조로 하며, 방충망을 설치하여야 한다. 7. 오수처리시설은 유입량을 24 시간 균등 배분할 수 있고 12 시간 이상 저류(貯留)할 수 있는 유량조정조를 설치하여야 한다. 다만, 1 일 처리용량이 100 m2 이상인 경우에는 10 시간 이상 저류할 수 있는 유량조정조 를 설치하여야 한다. 8. 시설물에는 악취를 방지할 수 있는 시설을 설치하여야 한다. 다만, 하수처리구역(합류식하수관로 설치지 역만 해당한다)에 설치된 1 일 처리대상인원 2 백명 이상인 정화탱크(대통령령 제 23464 호 하수도법 시행령 일부개정령 부칙 제 2 조에 따라 1 일 처리대상인원 1 천명 이상인 정화탱크 중 악취물질 제거시설을 갖추지 아니한 정화탱크를 포함한다)의 경우에는 배수설비[방류조(放流槽) 또는 배수탱크를 말한다]에 공기공급 장치 등 물에 녹아있는 악취물질을 제거하는 시설을 추가로 설치하여야 한다. 9. 시설물은 기계류로 인하여 발생되는 소음 및 진동이 생활환경에 지장이 없는 수준이어야 한다. 10. 오수배관은 폐쇄, 역류 및 누수를 방지할 수 있는 구조이어야 한다. 11. 시설물은 방류수수질검사를 위하여 시료를 채취할 수 있는 구조이어야 한다. 12. 콘크리트 외의 재질로 시설물을 제작·설치하는 경우에는 다음 각 목의 요건을 만족하여야 한다. 가. 지반 및 시설물 윗부분의 하중 등을 고려하여 시설물이 내려앉거나 변형 또는 손괴되지 아니하도록 콘 크리트로 바닥에 대한 기초공사를 하여야 하고, 시설물의 상부 또는 측면의 하중으로 인하여 시설물의 보강이 필요한 경우에는 콘크리트 등으로 해당 시설물의 상부 또는 측면에 슬래브 및 보호벽 등을 설치 하여야 한다. 나. 시설물을 원형으로 제작하는 경우에는 시설물이 수평을 유지할 수 있어야 한다. 13. 개인하수처리시설의 운영 중 일정기간 동안 오수발생량이 현저히 감소할 것으로 예상되는 학교·연수원 등에 개인하수처리시설을 설치하는 경우 오수가 적게 발생하는 기간에도 개인하수처리시설이 적정하게 운영될 수 있도록 계열화하여야 한다. V (2.2.5) 추가 설명 없음 V (2.2.6) 추가 설명 없음 2. 용어 V 내용 없음 - --- --- -- 기계설비 기술기준 해설 (별표 07 국토교통부 237 | {}
f2de9348-d29d-47a2-a94a-8a74ad5a2311 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2.3 빗물이용시설 2.3.1 집수시설 지붕이나 부지의 빗물을 모을 수 있는 집수시설을 설치한다. 2.3.2 여과 시설 처음 내린 빗물을 배제할 수 있는 장치나 빗물에 섞여 있는 이물질을 제거할 수 있는 여과 장치를 구 비한다. 2.3.3 빗물 저류탱크 처리시설에서 처리한 빗물을 증발 없이 일정 기간 저장할 수 있는 빗물 저류탱크를 구비해야 하고, 내부 청소가 쉬운 구조로 한다. 해 설 1. 본문 해설 및 관련 법규 V (2.3.1) 집수관, 루프드레인, 홈통받이 등 대상 집수면에 내리는 빗물을 보다 효과 적으로 모으기 위한 시설임 V (2.3.2) 빗물을 사용 용도에 적합한 수질로 유지하기 위해 여과, 소독 등의 방법으로 처리하는 시 설로 집수면의 종류 및 상태에 따라 초기 빗물을 배제하거나 여과 장치(필터, 모래여과, 쇄석여과 등)를 이용하여 처리 함 V (2.3.3) 집수한 빗물을 적합한 용량으로 저장하는 시설로 대상지역의 여건에 따라 재질 및 형식을 달리하고, 구조적 안전성을 확보해야 함 V (추가 1) 저장한 빗물을 사용 용도별로 보내거나 안전상의 이유로 하천 및 공공하수도로 방류하 는 송수·배수시설은 유지관리시 편의 성 및 사용량을 확인할 수 있도록 급수펌프, 상수보급(보충) 설비, 급·배수관, 활용설비, 유량계 및 제어설비를 포함해야 함 V (추가 2) 빗물이용시설과 중수도의 처리시설의 통합을 고려할 수 있으며, 유출지하수를 활용할 수 있는 경우에는 이를 빗물과 연계하여 경제성을 높일 수 있음 「물 재이용시설 설계 및 유지관리 가이드라인」 2013 2.2.3 용도별 수질기준 빗물이용에서의 수질기준은 중수도 수질기준과 하수처리수 재이용수 수질기준에 준용할 수 있다. 다만, 양 호한 빗물의 양호한 수질을 확보할 수 있는 측면을 감안하여 심미적 영향물질(pH, 탁도)의 제거와 미생물학 적 안전성(총대장균군)을 확보하도록 수질기준을 권장한다. 238 기계설비 기술기준 매뉴얼 | {}
281937a1-877a-4362-b6f5-5958c0de863f | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 ![image](/image/placeholder) 빗물이용시설 계통 사례 1 빗물유입 초기우수배제여과 장치 우수관로 상수유입 조경용수 우수조 집수정 출처 : https://blog.daum.net/gctech21/9 ![image](/image/placeholder) 빗물이용시설 계통 사례 2 우수유입 우수관로 빗물여과 스크린 보충수유입 우수관로 지영수증은 OH-Radical UFB System System (GAS+LIQUID) P Mixing Generator 재이용수공급펌프 비상방류펌프 AOPSystem 우수저장조 출처 : https://www.haesungeng.com 2. 용어 내용없음 국토교통부 239 기계설비 기술기준 해설 (별표 07 | {}
7ff02dbb-a861-4219-8da5-94cc9b05f7ac | 국내_기계설비_기술기준_매뉴얼_최종본 | 2.4 중수처리시설 2.4.1 처리시설 사용된 물을 용도에 맞는 수질로 처리할 수 있는 시설을 설치한다. 2.4.2 송수시설 처리한 물을 보낼 수 있는 펌프 , 송수관 등의 시설을 설치한다. 2.4.3 배수시설 처리한 물을 배수할 수 있는 배수관 등의 시설을 설치한다. 2.4.4 저류탱크 수량 부족에 대비하여 처리된 우수, 수처리 된 지하수 또는 시수 등 보급이 가능하도록 한다. 2.4.5 중수도의 수질기준 중수도의 용도별 수질기준은 「물의 재이용 촉진 및 지원에 관한 법률」에 따른다. 해 설 1. 본문 해설 및 관련 법규 V (2.4.1) 스크린설비, 유량조정조, 여과 장치, 소독장치, 처리탱크로 구성되며, 유지관리 및 소모자재 교체가 용이하도록 무인 자동제어설비를 고려할 수 있음. 주 원수가 건축물 내에서 발생되는 생 활잡배수나 주방배수 등을 포함하고 있어, 안정적인 처리수질과 악취저감 및 중수도 이용에 제한 이 없도록 탁도, 냄새, 색도 등 심미적 오염물질을 적극적으로 제거할 수 있어야 함 V (2.4.2) 중수도관, 펌프 및 밸브 그리고 유량계, 제어계측 등의 설비로 구성됨. 안정적인 급수와 유 지관리를 고려하여 각 중수도관의 수량과 관경, 연결관의 보급수량과 관경 등을 결정해야 하며, 특히, 사고 시 또는 재해 시 상수도를 보충수로 급수할 수 있도록 설계해야 함 V (2.4.3) 배수관, 배수펌프 및 밸브 그리고 오버플로우 배수가 가능하도록 구성됨. 배수과 정에서 중 수도 원수 또는 처리수가 오염되거나 변질되지 않도록 설계해야 함 V (2.4.4) 건축물의 기계실에 탱크 또는 건축 구조물로 구성됨. 내식성과 구조 안전성(내진성)을 고 려하여 설치해야 하며, 공기공급장치나 부상분리장치 등의 추가 설치를 고려할 수 있음 V (2.4.5) 중수도의 수질기준은 「물의 재이용 촉진 및 지원에 관한 법률」을 준수해야 함 240 기계설비 기술기준 매뉴얼 | {}
52b1f05f-34d5-418b-9fbf-d7390410bb36 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 물의 재이용 촉진 및 지원에 관한 법률 시행규칙 [별표 1] 중수도의 용도별 수질기준(제 8 조제 2 항 관련) ¦ 구분 ¦ 청소 · 화장실용수 ¦ 세척 · 살수용수 ¦ 조경용수 ¦ 친수용수 ¦ 하천 등 유지용수 ¦ 공업용수 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 총대장균군수 (개/100 ml) ¦ 불검출 ¦ 1 000 이하 ¦ 1 000 이하 ¦ 불검출 ¦ 1 000 이하 ¦ 수요자와 공급자간 협의 에 따라 정하되, 비고 2 의 기준을 따를 것 ¦ ¦ 결합잔류염소 (mg/L) ¦ 0.2 이상 ¦ - ¦ - ¦ 0.1 이상 ¦ - ¦ 수요자와 공급자간 협의 에 따라 정하되, 비고 2 의 기준을 따를 것 ¦ ¦ 탁도 (NTU) ¦ 2 이하 ¦ 2 이하 ¦ 2 이하 ¦ 2 이하 ¦ - ¦ 수요자와 공급자간 협의 에 따라 정하되, 비고 2 의 기준을 따를 것 ¦ ¦ 생물화학적 산소요구량 (BOD)(mg/L) ¦ 5 이하 ¦ 5 이하 ¦ 5 이하 ¦ 3 이하 ¦ 5 이하 ¦ 수요자와 공급자간 협의 에 따라 정하되, 비고 2 의 기준을 따를 것 ¦ ¦ 냄새 ¦ 불쾌하지 않을 것 ¦ 불쾌하지 않을 것 ¦ 불쾌하지 않을 것 ¦ 불쾌하지 않을 것 ¦ 불쾌하지 않을 것 ¦ 수요자와 공급자간 협의 에 따라 정하되, 비고 2 의 기준을 따를 것 ¦ ¦ 색도 (도) ¦ 20 이하 ¦ - ¦ - ¦ 10 이하 ¦ - ¦ 수요자와 공급자간 협의 에 따라 정하되, 비고 2 의 기준을 따를 것 ¦ ¦ 총질소 (T-N)(mg/L) ¦ - ¦ - ¦ - ¦ 10 이하 ¦ 20 이하 ¦ 수요자와 공급자간 협의 에 따라 정하되, 비고 2 의 기준을 따를 것 ¦ ¦ 총인 (T-P)(mg/L) ¦ - ¦ - ¦ - ¦ 0.5 이하 ¦ 0.5 이하 ¦ 수요자와 공급자간 협의 에 따라 정하되, 비고 2 의 기준을 따를 것 ¦ ¦ 수소이온농도 (pH) ¦ 5.8~8.5 ¦ 5.8~8.5 ¦ 5.8~8.5 ¦ 5.8~8.5 ¦ 5.8~8.5 ¦ 수요자와 공급자간 협의 에 따라 정하되, 비고 2 의 기준을 따를 것 ¦ ¦ 염화물 (mgCl/L) ¦ ¦ ¦ 250 이하 ¦ ¦ ¦ 수요자와 공급자간 협의 에 따라 정하되, 비고 2 의 기준을 따를 것 ¦ 비고 1. 항목별 수질검사는 「환경분야 시험 · 검사 등에 관한 법률」 제 6 조제 1 항제 5 호에 따른 수질오염물질 공정시험기준에 따라 검사하여야 한다. 2. 공업용수의 수질기준은 제품의 생산공정에 사용하는 경우에만 적용하며, 타 사업장으로 중수도 원수를 이송 후 처리하여 사용하는 경우 중수도 원수는 다음 각 목의 기준을 준수하여야 한다. 가. 법 제 9 조제 1 항 각 호의 시설물 또는 개발사업의 폐수배출시설에서 발생하는 폐수를 중수도 원수로 사용하는 경우: 「물환경보전법 시행규칙」 별표 13 에 따른 배출허용기준 나. 법 제 9 조제 1 항 각 호의 시설물 또는 개발사업에서 발생하는 오수를 중수도 원수로 사용하는 경우: 「하수도법 시행규칙」 별표 3 에 따른 오수처리시설의 방류수수질기준 V (추가 1) 원수의 수질 및 별도의 용도별 수질기준이 요구될 경우에는 약품침전, 활성탄처리, 가압 식 막여과 등 추가 설치를 고려할 수 있음 V (추가 2) 빗물이용시설과 중수도를 연계하여 처리시설의 중복 설치를 방지할 수 있음 국토교통부 241 기계설비 기술기준 해설 (별표 07 | {}
67f2e93f-3017-482f-8897-b6074003f479 | 국내_기계설비_기술기준_매뉴얼_최종본 | ![image](/image/placeholder) 중수도 계통 사례 1 배수유입 상수유입 수처리자동회전스크린 하수관로 한방 재이용수공급 LOT · 집수정 원수조 중수처리일체형여과 장치 처리수조 출처 : https://blog.daum.net/gctech21/8 중수도 계통 사례 2 ![image](/image/placeholder) 하수관로 브로워 보충수유입 흡인펌프 잡배수유입 P 큰운수용�애보 유량조정조 침지형여과 막조 반응조 처리수저장조 출처 : https://www.haesungeng.com 중수도 계통 사례 3 ![image](/image/placeholder) 우수유입 재이용수공급 우수관로 흡인펌프 초기우수 브로워 하수관로 배제스크린 스크린 우수관로 · 잡배수유입 유량조정조 P 배수펌프 비상방류펌프 우수이송펌프 재이용수공급펌프 원수이송펌프 우수저장조 반응조 처리수저장조 침지형여과 막조 유량조정조 출처 : https://www.haesungeng.com 2. 용어 내용없음 242 기계설비 기술기준 매뉴얼 | {}
7a693b99-8795-4863-9242-c90281bd9317 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 3. 오수정화 및 물재이용설비 시공 3.1 일반사항 (1) 오수처리시설의 시공에 직접 또는 간접으로 관련되는 시설공사에 대해서는 각각 해당하는 절의 규정에 따른다. (2) 탱크, 기기, 배관, 배선 등은 그 설치, 운전, 유지에 관하여 「수도법」, 「건축법」, 「하수도법」, 「물 환경보전법」, 「소음 · 진동관리법」, 「폐기물관리법」, 「전기사업법」 등의 관련 법규에 적합하도록 안전, 위생, 방호를 위한 시설, 장비를 설치한다. (3) 기기의 운전에 의해 발생하는 소음, 진동을 가능한 한 저감시키기 위하여 방진기초, 방진고무, 방 진이음 및 소음장치 등을 설치한다. (4) 통기와 배기를 위한 개구부는 우수, 토사 등의 유입을 방지할 수 있고, 또한 적설에 의해 폐쇄되지 않는 구조로 한다. 또한 곤충이 침입할 우려가 있는 부분에 설치할 경우는 방충망을 설치한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 「하수도법 시행규칙」 [별표 12] 개인하수처리시설 제조제품의 구조·규격·재질 및 성능 기준 및 [별표 1 의 5] 개인하수처리시설의 설치 및 「하수도법 시행령」 [별표 1 의 5]개인하수처리시설의 설치 기준을 참고하여 시공함 V (2 항) 「수도법」 [별표 1 의 2] 위생안전기준(제 24 조 관련), 「건축법」 제 5 장 건축물의 구조 및 재료 등, 「하수도법 시행령」 [별표 1 의 5] 개인하수처리시설의 설치 기준, 「물환경보전법」 [별표 7] 측 정기기의 종류 및 부착 대상(제 35 조제 1 항 관련), 「소음·진동관리법」 제 22 조의 2(공사장 소음측정 기기의 설치 권고), 제 40 조(방음시설의 성능과 설치 기준 등)을 참고하여 설치함 V (3 항) 이 기준 [별표 12]의 관련 내용을 참조하여 시공함 V (4 항) 오수처리시설의 개구부는 개별 설치하고 일반 통기관과 연결을 금지하며, 시설물은 발생가 스를 배출할 수 있는 배출장치(개구부등)을 갖추어야 하되, 배출장치는 이물질이 유입되지 아니하 는 구조로 하며, 방충망을 설치해야 함 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 통기 ¦ 배수를 원활히 하거나 배수에 의한 관내기압 변동에서 트랩 봉수를 보호하기 위해 또는 탱크류의 수위 변화에 의해 생기는 기압 변동을 조정하기 위해 배수관에 공기 를 유통시키는 것. 출처 : 대한건축학회 건축용어사전 ¦ 국토교통부 243 기계설비 기술기준 해설 (별표 07 | {}
406f0b30-7450-41fd-b646-8ffdff7566e7 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3.2 개인하수처리시설 (1) 스크린 ① 오수유도부의 하부는 평활한 상태를 유지하며, 스크린은 수도에 직각으로 설치하고 설치 각도는 수평면에 대해서 45~60°로 한다. ② 오수유도부에 유입되는 오수는 스크린을 통과 하도록 수위를 고려한다. ③ 유도부에 설치된 스크린장치 하부 및 측면은 유도된 오수의 이탈을 방지하기 위하여 내산성 재 질을 사용하여 밀실하게 설치한다. 해 설 1. 본문 해설 및 관련 법규 (1 항) 스크린은 침사지 전·후에 설치하여 침사지 및 계량장치를 통과 하는 오수 중 비교적 크기가 작은 협잡물까지 제거할 수 있어야 함 자동스크린 : 5 mm 의 스테인레스 강재로 제작 조목스크린 : 유효간격이 50 mm 이상인 것을 말하고 오수 중의 큰 협잡물을 제거하기 위해 설치 세목스크린 : 유효간격이 50 mm 미만인 것을 말함(보통 20 mm 정도) 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 스크린 ¦ 체로서, 혼합물을 선별하거나 모래 등을 입도(粒度)에 따라서 크고 작은 것을 걸러내 는 용구를 말한다. 동력으로 구동되는 회전체와 진동체 등이 있는데 체눈의 대소는 메시(mesh)로 나타내며, 가장 미세한 것을 여과 하는 것을 필터라고 한다. 출처 : 기계공학용어사전 ¦ --- 3.2 개인하수처리시설(계속) (2) 파쇄장치 파쇄장치의 유입 및 유출부는 수로에 밀착시키고, 누수 되지 않도록 설치한다. 해 설 1. 본문 해설 및 관련 법규 파쇄장치의 분체는 절삭날과 컷터바의 교체가 쉬운 구조로 하며, 감속기 부착형 전동기와 직결한 드럼형(회전드럼, 고무, 절삭낙, 컷터바 등)으로 하고, 돌 및 금속 이외의 고형물을 미세하게 자를 수 있는 것으로 함 2. 용어 V 내용 없음 244 기계설비 기술기준 매뉴얼 | {}
eb333551-572c-454d-a1b9-fb96e7026976 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 3.2 개인하수처리시설(계속) (3) 오수펌프 ① 탈착장치와 펌프의 연결을 정확히 하고, 탈착부를 패드에 고정할 때는 수평을 유지한다. ② 펌프의 인양을 원활히 하기 위하여 안내봉은 간격과 수직을 적절히 조절한다. ③ 펌프의 인양작업을 고려하여 맨홀의 크기를 결정한다. ④ 인양체인은 팽팽하게 당겨 상부에 고리를 설치하고 걸 수 있도록 한다. ⑤ 동력케이블은 적당히 당겨진 상태에서 더 이상 물속에 들어가지 않도록 하여 결선한다. 해 설 1. 본문 해설 및 관련 법규 V (1 호 ~ 5 호) 펌프는 온도 변화 및 외부에서 가해지는 힘과 모멘트 등을 견딜 수 있도록 설계하며, 2 대의 펌프가 병렬로 운전될 경우 각 펌프의 정격 유량을 벗어난 상태로 운전되는 상황에서도 부 적절한 소음이나, 진동 또는 축의 파손 등의 문제가 발생되지 않아야 함 2. 용어 V 내용 없음 3.2 개인하수처리시설(계속) (4) 폭기장치 ① 폭기장치는 탱크 내의 오수를 균등하게 교반할 수 있는 위치에 설치한다. ② 산기장치 가. 산기관과 산기노즐 등은 이탈하지 않도록 수심이 일정하고, 수평이 되도록 설치한다. 나. 산기장치는 공기의 분출에 의한 진동이 적고, 보수 및 점검이 용이하도록 설치한다. ③ 기계식 교반장치 주축은 폭기조의 중심부에서 수직이 되도록 하고, 또한 교반날개는 수위에 대 해서 적절한 위치가 되도록 고정해서 설치한다. ④ 수중 폭기장치 가. 급기관 또는 송기관에 설치된 제어밸브는 조작이 용이한 위치에 부착한다. 나. 급기관 또는 송기관의 도중에는 플랜지이음을 삽입해서 장치의 교체를 용이하게 한다. 다. 탱크의 천장에는 필요에 따라 중량물을 매달 수 있는 장치를 설치한다. 해 설 1. 본문 해설 및 관련 법규 국토교통부 245 기계설비 기술기준 해설 (별표 07 | {}
2d5853af-a781-4a4b-9d93-a3481d27e330 | 국내_기계설비_기술기준_매뉴얼_최종본 | V (1 호) 추가 설명 없음 V (2 호) 산기장치는 산기관과 산기노즐 등을 사용하여 균일하게 공기를 토출시킴과 동시에 높은 산 소 용해율로 일정하게 안정적인 폭기성능을 유지할 수 있도록 간격 및 높이를 일정하고 견고하게 설치해야 함. 오수 중에 협잡물이 엉키지 않는 구조로 하여 막힘이 일어나지 않도록 하며, 산기관 의 구멍은 수중에서 폐쇄될 가능성이 있으므로 송풍기에 공급되는 공기는 외부 공기를 사용하며 필요에 따라 여과 처리된 공기를 사용할 수 있어야 함 V (3 호) 기계식 교반장치의 주축은 폭기조의 중심부에서 수직이 되도록 설치하고, 교반날개는 수위 에 대해서 적절한 위치가 되도록 고정해서 설치해야 함 V (4 호) 수중 폭기장치는 흡기관, 펌프, 노즐 또는 송기관, 펌프, 노즐 등으로 구성되며, 조내의 혼합 액을 충분히 교반할 수 있는 구조이어야 함 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 폭기장치 ¦ 공업 용수 처리에 있어서는 기폭 장치와 같은 뜻이다. 활성 오니법에서 사용되는 장 치로는 탱크내에 설치된 것으로 산기식 에어레이션 탱크, 기계 교반식 에어레이션 탱크가 있다. 출처 : 환경공학용어사전 ¦ ¦ 산기장치 ¦ 활성 오니법 또는 플로테이션 등에 이용되는 것으로, 폭기가 충분히 이루어지도록 공기를 기포 상태로 만들어 오니 속에 분산시키는 장치를 말한다. 다공질인 세라믹 (석영 모래나 탄화규소 입자를 성형, 소결한 것) 제 산기판이나 산기관, 또는 노즐 상 태의 구멍을 설치한 송기관 등이 이용되고 있다. 출처 : 환경공학용어사전 ¦ ¦ 기계식 교반장치 ¦ 혼합과 플록형성 등을 목적으로 설치된 교반기(mixer)와 모터(motor)를 비롯하여 교 반조(mixing tank), 플록형성지 등을 구조물과 부속 설비를 포함한 제반 장치 계식 표면포기기, 수중교반식 포기기로 구분함 출처 : 물백과 사전 + 해설서 주 ¦ ¦ 수중 폭기장치 ¦ 공기식과 순 산소식이 있으며, 공기식의 경우 상향류, 하향류 폭기 방법 등 다양한 방 식이 있고, 순 산소식의 경우도 육상, 수상주입형 등이 있음(해설서 주) ¦ ○ 3.2 개인하수처리시설(계속) (5) 송풍기 ① 송풍기는 기초 윗면에 수평으로 설치하고, 진동에 따른 이격을 방지하기 위하여 기초 볼트를 조 인다. ② 진동 및 소음을 방지하기 위하여 방진 및 방음장치를 설치한다. ③ 연결덕트에는 진동에 따른 손실을 방지하기 위하여 플렉시블 조인트를 설치한다. ④ 벨트걸이의 경우는 벨트의 길이가 적당하게 되도록 본체 및 전동기의 위치를 조정한다. 해 설 1. 본문 해설 및 관련 법규 V (1 호) 송풍기는 고속회전에 의한 진동과 마모로 인한 고장이 발생하기 쉬우므로, 송풍기의 기초는 가능한 한 진동을 방지하는 구조이어야 함 246 기계설비 기술기준 매뉴얼 | {}
3618909d-f773-40fe-b493-2179a93a2291 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 (2 호) 송풍기의 구조는 송풍기는 고속회전으로 연속 운전할 때 허용한계를 초과 하면 진동, 베어링 의 온도 상승 등 악영향이 발생하므로 감시제어장치 등을 설치하여 장시간 연속운전 시 지장이 없어야 하며, 그 외는 이 기준 별표 12 에 따름 V (3 호, 4 호) 추가 설명 없음 V (추가) 송풍기의 종류 및 구조는 다음의 사항을 고려하여 선정해야 함 1) 송풍기는 장시간 운전되고 회전수가 높아서 마모와 고장 등이 발생하기 쉬우므로 송풍기의 용량 및 대수 는 동일 풍량 2 대 이상으로 하고 향후 증설계획 등을 고려하여야 한다. 2) 송풍기의 원동기의 동력은 소요공기량, 설치장소의 기압, 토출공기압, 온도 그리고 여유율 등을 고려하여 정한다. 2. 용어 V 내용 없음 - --- 3.2 개인하수처리시설(계속) (6) 접촉여재 ① 접촉여재는 변형 및 파손되지 않도록 주의 하고, 소정의 위치에 소정의 양을 충진한다. ② 고정상 접촉여재의 충진은 접촉함을 설치하여 충진한다. ③ 플라스틱재의 충진재를 사용하는 경우는 담배재나 용접불꽃 등의 화기에 의해서 손상되지 않도 록 충분히 주의 한다. ④ 고정상 접촉여재는 설치 후 오수의 흐름이 원활히 되도록 하여 접촉여재와 오수가 원활하게 접 촉되어 처리될 수 있도록 하기 위하여 적당한 간극을 유지한다. 해 설 1. 본문 해설 및 관련 법규 (1 호 ~ 4 호) 접촉여재는 직접폭기에 의한 파손 및 변형으로 인해 부상되거나 미생물막의 강제탈 락 등을 방지 위하여 폭기장치(산기관) 로 부터 적정 간격을 두고 설치하여야 하며, 반응조 내부 의 압력 및 오니의 인발 등의 과정에서도 접촉재가 변형되거나 파손 되지 아니하는 재질·구조(여 재틀 고정 등)로 설치해야 함 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 접촉여재 ¦ 접촉 여과 및 생물 접촉 여과 에 사용하는 망간 모래와 같이 작은 구멍이 많은 여과 재 출처 : 국어사전 ¦ --- 국토교통부 247 기계설비 기술기준 해설 (별표 07 | {}
4f964a2e-51cd-47af-91e2-5facae2f10e9 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3.2 개인하수처리시설(계속) (7) 회전원판 접촉장치 ① 회전이 원활하도록 전동기, 감속기, 주축의 축 등의 중심 및 수평조정을 정확히 유지한다. ② 스프로킷은 축에 견고하게 부착하고, 구동 측과 중동 측 스프로킷의 중심은 정확히 유지한다. ③ 축과 감속기와 의 간격은 체인피치의 30~50 배의 거리 이내로 설치하고, 베어링 설치부분은 회전 원판의 운전중량에 견딜 수 있는 구조로 한다. ④ 베어링베이스와 감속기베이스의 앵커는 회전원판의 이격이 발생되지 않도록 견고하게 설치한 다. 해 설 1. 본문 해설 및 관련 법규 V (1 호 ~ 4 호) 회전원판장치는 연결원판을 수평 방향의 축에 고정시켜 원판체의 40% 정도가 탱크 내의 수면 속에 잠기도록 하여 원판이 축과 함께 회전하면서 처리수중의 미생물 균을 막과 막사 이의 상으로 원판표면에 부착시켜 공기 중 노출시에는 산소를 흡수하고 수중에는 무기물의 산화, 분해시키는 형식이어야하고 모든 생물처리성능이 우수해야 함 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 회전원판(법) ¦ 생물막을 이용하여 하수를 처리하는 방식으로 회전원판이 폐수면 아래 40% 정도가 수면에 잠기도록 설치하여, 원판을 회전시키면서 회전판 위에 발생하는 호기성생물 을 이용하여 하수를 처리하는 방법 출처: 물백과 사전 ¦ ¦ 스프로킷 ¦ 체인을 걸어서 전동하는 톱니나 발톱이 달린 바퀴를 말한다. 출처 : 기계공학용어사전 ¦ --- 3.2 개인하수처리시설(계속) (8) 정량주입펌프 ① 흡입, 배출에 사용되는 호스는 PE 호스 혹은 PVC 관으로 하며, 외부의 충격에 의해 파손되지 않 도록 보양조치를 한다. ② 수평을 유지하도록 적정한 간격으로 고정하며, 다이어프램의 작동에 무리가 없도록 한다. 해 설 1. 본문 해설 및 관련 법규 정량주입펌프는 다음의 사항을 고려하여 설치해야 함 248 기계설비 기술기준 매뉴얼 | {}
dd89b37d-8f73-4be7-b871-00dece18d0bd | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 1) 정지 및 운전 중에도 투입량을 자동/수동으로 조절할 수 있어야 한다. 2) 유량 비례제어 신호에 의한 투입, 자동제어 등이 용이해야 한다. 3) 투입량 증감은 회전수 조절로서 자동으로 이루어져야 한다. 4) 약품 투입량을 측정할 수 있는 유량계가 부착되어야 한다. 5) 약품이 접하는 부위는 산에 강한 재질이어야 한다. 6) 다이어프램(diaphragm)은 국소적인 피로 파괴가 없어야 한다. 7) 펌프 헤드는 운전 시 진동과 소음이 없어야 하며, PVC 재질로 제작하여 충격 및 배관 하중 등에 여유가 있어야 한다. 8) 전 밀폐형으로서 급유가 완전하여야 하며 장시간 운전하는데 이상이 없어야 한다 2. 용어 내용 없음 - ---- ---- -- 3.2 개인하수처리시설(계속) (9) 월류 위어의 설치 월류 위어는 소정의 위치에 전 길이에 걸쳐서 수평으로 설치하고, 설치부가 누수되지 않도록 한다. 해 설 1. 본문 해설 및 관련 법규 월류 부하 30 m2/m 이하의 월류 위어를 설치하되, 맨홀 상부에서 설치 내역을 확인할 수 있는 구 조 및 청소가 용이하도록 설계해야 함 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 월류 위어 ¦ 기존 위어의 물을 저장하는 역할과 는 다르게 물이 평상시에도 위어의 정상부를 통과 하여 흘러넘치도록 설계된 위어(해설서 주) ¦ 3.2 개인하수처리시설(계속) (10) 찌꺼기 제거장치의 설치 찌꺼기 제거장치는 유입부에서 찌꺼기가 균등하게 흐르게 하고, 또한 그 수준을 거의 수면과 동일 수준으로 해서 물만 유입되지 않도록 설치한다. 해 설 1. 본문 해설 및 관련 법규 국토교통부 249 기계설비 기술기준 해설 (별표 07 | {}
8dc91281-a1d0-40ae-aaad-9aa6ec599407 | 국내_기계설비_기술기준_매뉴얼_최종본 | 찌꺼기(슬러지) 제거기(sludge scraper)를 설치할 경우, 탱크바닥의 기울기는 5/100 이상이 좋으 며, 찌꺼기(슬러지) 제거기를 설치하지 않을 경우 탱크바닥의 중앙에 호퍼를 설치하되 호퍼측벽의 기울기는 수평에 대하여 60° 이상으로 함 2. 용어 내용 없음 - 3.2 개인하수처리시설(계속) (11) 오니 인양기의 설치 ① 중심구동식 인양기 가. 침전조의 바닥에는 기기 본체의 설치 완료 후 두께 50 mm 정도의 마무리 모르타르(배합비 1 : 3)를 오니 인양기를 회전시키지 않는 상태에서 타설한다. 이 경우 플레이트 하단과 모르타 르면은 탱크의 전면에 걸쳐서 30 mm 이하로 하여 균일 간격을 유지시킨다. 나. 난간 고정 기초 볼트는 구체콘크리트의 철근에 용접한다. ② 체인 플레이트식 오니 인양기 가. 기초 볼트는 골조콘크리트의 철근에 용접한다. 단, 가이드레일 지지금속의 기초 볼트는 보링 앵커공법 등으로 설치한다. 나. 각종 레일은 탱크 중심에서 좌우로 나누어 소정의 위치에 수평으로 평행하게 설치한다. 다. 각축은 소정의 위치에 평행하고 탱크중심에 직각으로 설치한다. 라. 침전조의 바닥에 설치하는 레일은 중심 맞추기 및 수평, 평행도 등을 확인 후 매립부에 콘크리 트를 타설한다. 해 설 1. 본문 해설 및 관련 법규 V (1 호) 중심구동식 오니인양기는 구동장치, 점검복도, 레이크암, 오니인양판 등으로 이루어져 있으 며 필요에 따라 스컴 제거장치를 설치해야 함 구동장치의 감속기에는 안전장치를 갖추고 오니 인양판은 오니가 조및에 체류하지 않는 구조로 하고 침전오니를 똑같이 이동할 수 있도록 적절한 각도로 레이크암에 고정해야 함 V (2 호) 체인플레이트식 오니인양기는 구동장치, 오니 인양판, 가이드레일 등으로 이루어져 있으며 필요에 따라 스컴제거장치를 설치하고 구동용스프로킷 호일(구동장치측)에는 사핀등의 안정장치 를 설치해야 함 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 레이크암 ¦ 슬러지를 조 중앙의 피트로 긁어모아주는 장치(해설서 주) ¦ 250 기계설비 기술기준 매뉴얼 | {}
43f3f3d6-95bf-41f9-a339-e1fae6d81ce8 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 3.2 개인하수처리시설(계속) (12) 제어반의 설치 제어반은 정화탱크 외부나 별도의 실을 구획하여 그 내부에 설치하고, 설치 장소에는 급기 및 배기 시설을 설치하여 부식을 방지하고 고장 시 경보가 가능하도록 한다. 해 설 1. 본문 해설 및 관련 법규 제어반은 본체 계전기, 전원표시, 운전표시, 시동, 정지스위치 등으로 이루어져 있으며 필요에 따 라 누전차단기, 경보장치를 설치해야 함 2. 용어 V 내용 없음 국토교통부 251 기계설비 기술기준 해설 (별표 07 | {}
07f2ced0-56d6-4cb8-9bca-2536bbe56b33 | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 8] 배관설비의 설계 및 시공 기준 1. 배관설비 일반사항 1.1 목적 이 기준은 건축물, 시설물 등에 설치된 열원 및 냉난방설비, 공기조화설비, 급수 、 급탕설비 및 오 , 배수통기 、 우수배수설비 등에 필요한 각종 배관설비의 설계 및 시공 방법 등 세부 기술기준을 정함 을 목적으로 한다. 해 설 이 기준의 목적은 「기계설비법」 제 14 조(기계설비 기술기준)과 같은 법 영 제 2 조 및 [별표 2]에 근 거하여, 건축물이나 시설물에 필요한 배관설비의 설계 및 시공 시 기계설비의 안전과 성능을 확 보하기 위하여 필요한 기술적 요건을 규정하기 위함 「기계설비법」 제 14 조(기계설비 기술기준) ① 국토교통부장관은 기계설비의 안전과 성능확보를 위하여 필요 한 기술기준(이하 "기술기준이라 한다)를 정하여 고시하여야 한다. 이를 변경하는 경우에도 또한 같다. 1.2 적용범위 이 기준은 건축물, 시설물 등에 냉 , 온수, 냉각수, 증기, 냉매, 급수 , 급탕, 오 , 배수통기, 우수배수 등의 배관설비를 적용하는 경우에 대하여 적용한다. 해 설 이 기준의 적용범위는 「기계설비법」 제 2 조제 1 호에 따른 건축물등에 같은 법 영 제 2 조에 따라 대 통령령으로 정한 배관설비를 설치하는 경우 및 그와 관련된 부속설비들을 포함함 「기계설비법」 제 2 조(정의) 1. "기계설비"란 건축물, 시설물 등(이하 "건축물등"이라 한다)에 설치된 기계 · 기 구 · 배관 및 그 밖에 건축물등의 성능을 유지하기 위한 설비로서 대통령령으로 정하는 설비를 말한다. 「기계설비법 시행령」 제 2 조(기계설비의 범위) 「기계설비법」(이하 "법"이라 한다) 제 2 조제 1 호에서 "대통령령 으로 정하는 설비"란 별표 1 의 설비를 말한다. 252 기계설비 기술기준 매뉴얼 | {}
fbaa4632-8ac9-4d4d-9668-8ab452e9f635 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 1.3 타 규정과 의 관계 상이한 경우에는 해당 규정을 따른다. 다음의 규정과 이 기준에서 정하는 내용이 (1) KDS 31 25 25 배관설비 설계기준 (2) KDS 31 30 15 급수설비 설계기준 (3) KDS 31 30 20 급탕설비 설계기준 (4) KDS 31 30 25 배수통기설비 설계기준 (5) KDS 31 30 35 우수설비 설계기준 (6) KCS 31 20 15 배관설비공사 표준시방서 해 설 이 기준과 타 규정 및 기준과 다른 경우에는 상기 규정에 명시된 내용을 따름 국토교통부 253 기계설비 기술기준 해설 (별표 08 | {}
6cf359a9-d0e9-4bde-8dc5-fa27ba06d5d1 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 배관설비 설계 2.1 냉 · 온수 배관 2.1.1 일반사항 (1) 물 배관 시스템을 위한 배관과 구성품은 시스템 요구에 적합해야 한다. (2) 냉동기, 온수보일러, 흡수식 냉온수기, 빙축열유닛 및 열교환기를 통과 하는 유량은 장비 허용범 위를 벗어나지 않도록 한다. (3) 각 터미널 기기에 설계유량 분배가 용이하도록 배관방식을 선정한다. (4) 배관에는 냉 , 온수의 온도에 따라 신축이음을 설치하여 배관의 신축을 흡수하도록 한다. (5) 분기배관에는 차단밸브를 설치한다. (6) 배관의 최저부에는 물빼기 배관 및 밸브를 설치한다. 해 설 1. 본문 해설 및 관련 법규 (1 항) 물 배곤 시스템은 유량제어, 압력제어, 수처리 제어를 통해 시스템 요구에 적합해야 함 (2 항) 열원장비는 설계 유량을 확보하여 설계 온도차를 유지해야 할 수 있도록 배관을 설계 해야 함 (3 항) 유량 불균형으로 인한 냉난방 및 급수·급탕량의 불균형이 없도록 해야 하며, 대한설비공학 회의 기술인증을 받은 수배관설계 프로그램(https://www.sarekooky/ron/mainainj 을 사용하여 설 계할 수 있음 ![image](/image/placeholder) KOREAN 사탑인 대한설비공학회 학회소개 위원회 안내 회원정보 학술지 학술발표대회 학회자료검색 학회표준 알림광장 회원 로그인 아이디 RTS-SAREK 2021 대한설비공학회 동계학술발표대회 & 로그인 2021 년 제 9 회 HVAC 경진대회 비밀번호 (공조부하계산 프로그램) 초 회원가입 Q ID/PW 찾기 설비공학편람 제 4 판 발간 전자계산서 대한설비공학회 등록 민간자격 안내 일 개인회원 단체회원 우수기업회원 RTS-SAREK (공조부하계산 프로그램) 특별회원 SAREK 블로그 [*] 행사안내 학회소식 및 공지 학술지 대한설비공학회 50 주년 사이드맵 '지나온 50 년의 기억 그리고 다가올 50 년의 하게 공지 2022 년도 행사일정 2022-01-06 제 21 회 설비포럼 초청 (사전등록 후 입장 가... 2021-12-03 설비공학논문점 AIR-CONDITIONING AND REFRIGERATION HVACDESIGNAWARD 학술발표대회-발표자료 동영상 제작 매뉴얼 2021-10-27 CONTACT ASIA 2021 년도 동계학술발표대회(HVAC/유튜브콘텐... 2021-10-27 커미셔닝 전문가 교육 및자격시험 안내 2021-10-22 TOP Go ToMomepage TAB 전문기술인 보수교육(온라인) 안내 2021-10-05 7thIntemational Conference KJACR UACR 커미셔닝 전문가 보수교육(온라인) 안내 2021-10-05 on Saving Energy for Refrigeration ISSN ISSN andAir-Condtioning (ICSERA) TAB 평가시험 안내 2021-09-08 1229-6422 (Print) 2010-1325 (Print) Go to homepage 2021 년도 동계학술발표대회 논문 및 강연 모 2021 -08-24 2465-7611 (Online) 2010-1333 (Online) 하계학술발표대회 관련 휘닉스 호텔 언택트 2021-06-14 ACRA The 10th Asiam ConferenceonRetrigeration andAir-conditio 하계학술발표대회 세부일정 및 전시회 개최 2021-05-27 ApriBup 2011 Gotohomepage 회원동정 I 회원게시판 관련단체소식 PsyChart-SAREK GREEN REMODELING CHALLENGE (습공기선도 프로그램) [부고] 김병주 회원(냉동냉장수산업협동조합... 2022-01-06 그 린 리 모 델 링 텔 린 지 + [부고] 세일이엔에스(주) 김성주 대표 빙부상 2021-12-08 RTS-SAREK (공조부하계산 프로그램) 논문두고 논문구독신청 [부고] 강병하 전임회장(국민대학교) 부친상 2021-11-26 Hyd-SAREK [부고] 양보흡 처장(전, 한국토지주택공사 처... 2021-11-18 중 (냉난방수배관시스템 계산 S/W) 결제비용남부 RTS-SAREK 구매 [부고] 이송우 부사장(우원엠앤이) 장인상 2021-10-29 [부고] 이승폭 교수(연세대 건축공학과) 빙모... 2021 -09-19 ENERGY# 전자계산서 신청안내 설비공학관람 구매 패시브하우스 에너지해석 S/W) [부고] 이병희 대표(북경 부-스타) 부친상 2021-08-04 대한설비공학회 홈페이지 오른쪽 하단 프로그램 다운로드 V (4 항) 배관의 신축에 따른 배관의 손상을 방지해야 함 254 기계설비 기술기준 매뉴얼 | {}
fc677568-bfd3-475d-aad5-3eeafe6e50ed | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 (5 항, 6 항) 분기관의 차단밸브는 전체 시스템 중단을 사전에 방지하기 위하여 층별, 구역별 또는 용도별로 구분 설치하여 부분 고장에 따른 유지관리를 고려해야 함 2. 용어 V 내용 없음 -- --- -- 2.1.2 팽창관, 공기빼기관 (1) 냉 、 온수 밀폐배관 계통에는 물의 팽창 , 수축에 대비하여 팽창탱크를 설치하고, 압력식 팽창탱 크에는 감압밸브와 릴리프밸브를 설치한다. (2) 공기가 체류할 수 있는 배관계통에는 공기빼기밸브를 설치한다. (3) 이물질 배출 배수밸브의 크기는 주관 DN 25 이상인 것은 DN 25 이상으로 하고 그 외는 주관과 동일한 호칭지름으로 한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 팽창탱크의 설계와 시공은 이 기준 [별표 1] 2.7 과 3.7 을 참고함 V (2 항) 공기빼기밸브는 공기가 체류할 수 있는 배관계통의 가장 높은 곳에 설치함 V (3) 추가 설명 없음 2. 용어 ¦ 용어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 공기빼기밸브 ¦ 에어 릴리프밸브(air relief valve, ARV)의 일종. 압력 릴리프밸브나 진공 릴리프밸브 처럼 일정한 압력에 도달할 때 밸브가 열려 자동(또는 수동)으로 배관 내의 공기를 배출해 주는 밸브이다. 배관계통이나 밀폐된 용기, 방열기 등에서 발생하였거나 유입 된 공기를 배출시키지 않으면 유로가 차단되어 물이 흐르지 못하기 때문이다. 에어 벤트, 공기 빼기밸브 또는 자동 에어벤트 등으로 불려왔던 소형기구도 시간당 공기 유량이 제시되어 사이징이 가능하다면 넓은 의미에서 에어 릴리프밸브 범주에 들 수 있다. 출처: BPVC S-8, 배관공학(pp532-534) ¦ --- 기계설비 기술기준 해설 (별표 08 국토교통부 255 | {}
1b9fe67a-2904-42e8-9a57-dad86ca633d4 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2.1.3 기기주변 배관 (1) 기기와 의 모든 연결부에는 차단밸브를 설치한다. 또한 기기와 배관의 연결은 플랜지, 유니언, 그 루브 조인트, 기타 기계식 이음을 사용하여 배관의 손상 없이 기기의 탈착이 가능하도록 한다. (2) 냉동기주변 배관 ① 냉동기에 연결하는 배관에는 방진이음을 설치한다. 단, 흡수식 냉동기 및 흡수식 냉온수기는 제 외한다. ② 배관의 가장 낮은 부분에는 배수밸브를 설치한다. (3) 보일러주변 배관 온수보일러, 열교환기 등의 안전장치는 안전밸브와 팽창관을 병용한다. (4) 공기조화기 주변 배관 ① 공기조화기의 결로수 배수관에는 운전 중 봉수 깊이를 확보할 수 있는 배수트랩을 설치한다. ② 코일에 접속하는 냉 , 온수관의 가장 낮은 부분에 배수밸브를 설치한다. (5) 펌프주변 배관 ① 방진기가 설치된 모든 펌프의 토출구와 흡입구에는 방진이음을 설치한다. 방진기가 설치되지 않 은 진동이 적은 인라인 펌프에는 방진이음을 설치하지 않을 수 있다. ② 펌프의 입구와 출구에는 압력계를 설치한다. ③ 펌프 흡입구에는 이물질 인입 방지를 위하여 스트레이너를 설치한다. ④ 펌프 흡입구에는 흐름이 정상류가 되도록 일정 길이 이상의 직관을 설치하거나 펌프 석션디퓨저 를 설치한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 기기의 고장 등을 대비하여 유지관리를 위해 차단밸브를 설치하며, 분리와 조립이 간편한 것으로 해야 하며, 성능점검을 위한 밸런싱 밸브 및 유량, 온도, 차압 등을 계측할 수 있는 시험구 (Test Hole) 설치를 권장함 V (2 항 1 호) 진동이 발생하는 냉동기 주변 배관은 방진이음을 하며, 이 경우 이 기준 [별표 12]의 관 련 내용을 참조하여 시공함 V (2 항 2 호) 추가 설명 없음 V (3 항) 추가 설명 없음 V (4 항 1 호) 공기조화기 내외의 정압차 발생을 고려하여 설치 함 256 기계설비 기술기준 매뉴얼 | {}
eee224db-d0e1-4c2d-924c-10fdeb3f98fc | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 ![image](/image/placeholder) 배수 소켓 배수 배관 H AHU 기초 V (4 항 2 호) 추가 설명 없음 V (5 항 1 호) 이 기준 [별표 12]의 관련 내용을 참조하여 시공함 V (5 항 2 호, 3 호, 4 호) 추가 설명 없음 2. 용어 내용 없음 2.1.4 계기의 부착 (1) 열원기기의 냉수, 온수, 냉각수 공급 및 환수관의 직관부에는 온도계 및 압력계를 부착한다. (2) 온도계와 압력계는 바닥면에서 용이하게 볼 수 있는 위치에 설치한다. (3) 온도계와 압력계는 공기가 체류하지 않는 장소에 부착한다. 해 설 1. 본문 해설 및 관련 법규 (1 항) 기계설비 유지관리자 및 성능점검업자가 「기계설비 유지관리기준」에 따라 관련 값을 확인 하고 기록해야 하므로 신뢰성 있고 교정이 가능한 계기로 선정해야 하며, 온도계, 압력계의 눈금 은 사용 범위 전후를 크게 벗어나지 않는 측정범위를 가져야 함 (2 항) 유지관리자가 손쉽게 확인할 수 있는 위치에 설치해야 함 V (3 항) 배관 내 공기 흐름에 영향을 받지 않아야 함 2. 용어 V 내용 없음 국토교통부 257 기계설비 기술기준 해설 (별표 08 | {}
685abce8-943f-4030-a529-3047448dde9f | 국내_기계설비_기술기준_매뉴얼_최종본 | 2.1.5 배관 호칭지름 단위마찰손실과 유속을 기준으로 배관 호칭지름을 결정한다. 해 설 1. 본문 해설 및 관련 법규 배관 내 유속이 빠르면 관경을 작게 할 수 있으나, 단위 마찰손실 증가에 따른 펌프의 양정 및 동 력이 증가되어 펌프의 설치 및 운전비용이 증가하고, 유속이 느리면 배관 설치비가 높아지고 펌 프 설치비와 운전비는 낮아지므로 두 개의 요소를 고려하여 최적의 배관 지름을 선정해야 함 2. 용어 V 내용 없음 2.2 냉각수배관 2.2.1 일반사항 (1) 냉각탑을 겨울에 사용하는 경우는 냉각수의 동결을 방지하고, 냉각수 온도를 제어한다. (2) 여러 대의 냉각탑을 연결하여 사용하는 경우에는 각 냉각탑 간에 연통관을 설치한다. (3) 이외에는 2.1.1 을 따른다. 2.2.2 배관 호칭지름 단위마찰손실과 유속을 기준으로 호칭지름을 결정한다 해 설 1. 본문 해설 및 관련 법규 V (2.2.1 1 항) 동결방지를 위한 부동액 혼합 또는 동파방지열선을 설치하거나, 밀폐형 냉각탑 설치를 고려할 수 있음 V (2.2.1 2 항) 냉각탑의 불균일한 유량 분배로 인한 넘침 현상을 방지하기 위하여 하부 탱크 사이를 서로 연결하여 설치함 V (2.2.1 3 항) 추가 설명 없음 V (2.2.2) 2.1.5 설명 참조 2. 용어 V 내용 없음 258 기계설비 기술기준 매뉴얼 | {}
c7703572-3fb9-4fb0-b7cb-aa3b1769657b | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.3 증기배관 2.3.1 저압증기배관(100 kPa 미만) (1) 일반사항 ① 증기수평관의 기울기는 1/250 의 순기울기로 한다. 불가피하게 역기울기로 할 때는 그 길이를 최 소한으로 하고 1/80 의 역기울기로 한다. ② 분기배관에는 차단밸브의 설치를 고려한다. ③ 배관에는 신축량 및 배관 계통의 신축 흡수량을 고려하여 신축이음을 설치한다. ④ 증기수평관이 길어지는 경우에는 증기공급 초기에 발생하는 워터해머를 방지하기 위하여 약 30 m 간격으로 중간 트랩을 설치한다. ⑤ 순기울기 배관의 말단부에는 관말트랩을 설치한다. ⑥ 한랭지에서는 동결 방지를 위하여 증기관의 옥외 노출은 피하고, 가능한 피트 내 배관으로 한다. ⑦ 증기 분기관은 증기 횡주관의 상부에 연결한다. (2) 기기주변 배관 ① 보일러 주변 배관 가. 보일러 증기 공급관의 호칭지름은 보일러의 증기 출구 호칭지름 이상으로 하고, 보일러 상부 의 구조물까지의 거리는 1 200 mm 이상으로 한다. 나. 보일러 급수관은 보일러 보급수 연결 호칭지름 이상으로 한다. 다. 보일러의 배수는 간접배수로하고, 단독으로 배수구까지 연결한다. 라. 안전밸브 및 릴리프밸브의 배출관은 각각 옥외의 대기에 개방한다. 마. 안전밸브 및 릴리프밸브의 배출이 주변에 위험이나 손상을 주거나 통행을 방해하지 않아야 한 다. 바. 저압 보일러의 증기 출구에는 역류방지밸브를 설치하지 않는다. ② 증기코일, 방열기주변 배관 가. 코일 출구에서 트랩까지의 배관은 코일 출구의 호칭지름 크기 이상으로 한다. 나. 증기관의 분기관은 증기관의 응축수가 코일에 유입되지 않도록 상부 연결 배관으로 한다. 다. 외기전용 공기조화기의 증기가열 코일용 트랩은 동결의 우려가 없는 장소에 설치한다. (3) 배관 호칭지름 배관의 호칭지름은 허용마찰손실과 증기유량을 기준으로 결정한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항 1 호) 순기울기와 역기울기는 각각 1/250 이상, 1/80 이상으로 함 V (1 항 2 호) 분기배관에 설치된 유닛의 고장으로 인해 주배관에 영향을 주어서는 안됨 V (1 항 3 호) 사용온도와 배관의 재질을 고려함 기계설비 기술기준 해설 (별표 08 국토교통부 259 | {}
39c59be1-286b-4c67-862f-9c37bc834357 | 국내_기계설비_기술기준_매뉴얼_최종본 | 팽창계수(�) (mm/m°C) x 10-3 ¦ 재질 ¦ 온도범위(°C) ¦ 온도범위(°C) ¦ 온도범위(°C) ¦ 온도범위(°C) ¦ 온도범위(°C) ¦ 온도범위(°C) ¦ 온도범위(°C) ¦ 온도범위(°C) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 재질 ¦ < 0 ¦ 0~100 ¦ 0~200 ¦ 0~300 ¦ 0~400 ¦ 0~500 ¦ 0~600 ¦ 0~700 ¦ ¦ 탄소강 ¦ 12.8 ¦ 13.9 ¦ 14.9 ¦ 15.8 ¦ 16.6 ¦ 17.3 ¦ 17.9 ¦ - ¦ ¦ 합금강 ¦ 13.7 ¦ 14.5 ¦ 15.2 ¦ 15.8 ¦ 16.4 ¦ 17.0 ¦ 17.6 ¦ - ¦ ¦ 스텐레스강 ¦ 9.4 ¦ 20.0 ¦ 20.9 ¦ 21.2 ¦ 21.8 ¦ 22.3 ¦ 22.7 ¦ 23.0 ¦ 포화증기의 온도 ¦ bar g ¦ 1 ¦ 2 ¦ 3 ¦ 4 ¦ 5 ¦ 7.5 ¦ 10.0 ¦ 15 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ °C ¦ 120 ¦ 134 ¦ 144 ¦ 152 ¦ 159 ¦ 173 ¦ 184 ¦ 201 ¦ 출처 : Spirax Sarco Steam 가이드북 V (1 항 4 호) 증기공급 초기 응축수량의 증가에 따른 워터 해머 방지를 위해 트랩 설치 간격을 고려 함 V (1 항 5 호 ~ 7 호) 추가 설명 없음 V (2 항 1 호 가) 이 기준 [별표 15] 2.1(1) ⑥의 기준을 함께 고려해야 함 2.1 기계실 (1) 기계실 유지관리 공간 확보 ⑥ 기계실의 층고는 보수, 점검 및 교체에 지장이 없도록 다음을 고려하여 보 밑 유효높이를 확보한다. 가. 최대 장비 높이의 2 배 이상 나. 배관/덕트 등을 다단으로 설치할 경우 배관/덕트의 이격간격은 마감재 기준으로 배관의 경우 150 mm 이상, 덕트의 경우 300 mm 이상, 단 교차되는 부분은 제외한다. 다. 보일러실의 천장 높이는 보일러 상면에서 보 밑 천장까지 1.2 m 이상 확보한다. V (2 항 1 호 나, 마 ~ 바) 추가 설명 없음 V (2 항 1 호 다) 보일러 내부 음압 발생 시 배수 역류로 인한 고장 등을 방지하기 위함 V (2 항 1 호 라) 안전밸브 및 릴리프밸브의 배출관을 연도 등에 연결하여 배출하는 경우도 대기로 방 출하는 것으로 간주할 수 있음 V (2 항 2 호 가 ~ 다) 추가 설명 없음 V (3 항) 설비공학 편람, 제 4 판 제 4 권 제 7 장 증기설비 참조 2. 용어 V 내용 없음 260 기계설비 기술기준 매뉴얼 | {}
02990aa3-b357-47a8-b08a-2e08a5caccdb | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.3.2 고압증기배관(100 kPa 이상) (1) 일반사항 ① 증기압력에 의해 응축수를 밀어 올리는 트랩을 적용할 경우, 상승 높이는 트랩 전후 차압의 1/2 이내로 하고 트랩 출구 측에 역류방지밸브를 설치한다. ② 고압증기관은 증기용 밸브를 사용한다. ③ 사용압력 1 MPa 이상의 관에는 압력배관용 탄소강관 또는 고압배관용 탄소강관을 사용한다. (2) 기기주변 배관 기기주변 배관 선정은 2.3.1(2)에 따른다. (3) 배관 호칭지름 배관 호칭지름은 2.3.1(3)에 따른다. 해 설 1. 본문 해설 및 관련 법규 응축수 배출이 원활히 일어날 수 있도록 하고 특히 재증발로 인한 배출능력 저하를 고려해야 하 며, 증기 사용 장치에는 장치 내 공기 정체로 인한 전열 성능이 저하되지 않도록 공기빼기 밸브를 설치함 2. 용어 V 내용 없음 2.4 급수배관 급수관 호칭지름은 순간최대유량, 허용마찰손실 및 유속을 산정하고 배관 유량 선도 등을 활용하여 호칭지름을 결정한다. 해 설 1. 본문 해설 및 관련 법규 V 설비공학 편람, 제 4 판 제 5 권 위생·소방·환경 제 5 장 급수설비 참조 국토교통부 261 기계설비 기술기준 해설 (별표 08 | {}
d3f250b0-f4b0-412d-b2e4-86d014fe57d5 | 국내_기계설비_기술기준_매뉴얼_최종본 | 표 8 그룹 기준 기구급수부하단위 ¦ 기구명 ¦ 기구명 ¦ 단독주택 ¦ 아파트 등 공동주택 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 욕실그룹 (6L/회 세정탱크형 대변기사용) ¦ 1/2 욕실,파우더룸 ¦ 3.5 ¦ 2.5 ¦ ¦ 욕실그룹 (6L/회 세정탱크형 대변기사용) ¦ 1.0 욕실 ¦ 5.0 ¦ 3.5 ¦ ¦ 욕실그룹 (6L/회 세정탱크형 대변기사용) ¦ 1.5 욕실 ¦ 6.0 ¦ - ¦ ¦ 욕실그룹 (6L/회 세정탱크형 대변기사용) ¦ 2.0 욕실 ¦ 7.0 ¦ - ¦ ¦ 욕실그룹 (13L/회 세정탱크형 대변기사용) ¦ 1/2 욕실,파우더룸 ¦ 4.0 ¦ 3.0 ¦ ¦ 욕실그룹 (13L/회 세정탱크형 대변기사용) ¦ 1.0 욕실 ¦ 6.0 ¦ 5.0 ¦ ¦ 욕실그룹 (13L/회 세정탱크형 대변기사용) ¦ 1.5 욕실 ¦ 8.0 ¦ - ¦ ¦ 욕실그룹 (13L/회 세정탱크형 대변기사용) ¦ 2.0 욕실 ¦ 10.0 ¦ - ¦ ¦ 욕실그룹 ¦ 6L/회 세정탱크형 대변기사용 ¦ 6.0 ¦ 1.0 ¦ ¦ 욕실그룹 ¦ 13 L/회 세정탱크형 대변기사용 ¦ 8.0 ¦ 6.0 ¦ ¦ 주방그룹(싱크 및 식기세척기 사용) ¦ 주방그룹(싱크 및 식기세척기 사용) ¦ 2.0 ¦ 1.5 ¦ ¦ 세탁실그룹(세탁기 및 싱크 사용) ¦ 세탁실그룹(세탁기 및 싱크 사용) ¦ 5.0 ¦ 3.0 ¦ 주) 1. 욕실 그룹은 대변기 1 개 이상, 세면기 2 개까지, 욕조나 욕조/샤워 또는 샤워 1 개로 구성된 욕실 2. 1/2 욕실이나 파우더룸(powder room)은 대변기와 세면기 각 1 개를 갖춘 화장실을 말한다. 표 9 개별기구 기준 기구급수부하단위 ¦ 기구명 ¦ 접속관지름 DN ¦ 단독주택 ¦ 아파트등 공동주택 ¦ 상업용 건물 ¦ 다중이용시 설 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 대변기(세정밸브, 13 L/회) ¦ 25 ¦ 7.0 ¦ 7.0 ¦ 8.0 ¦ 10.0 ¦ ¦ 대변기(세정탱크, 13 L/회) ¦ 15 ¦ 3.0 ¦ 3.0 ¦ 5.5 ¦ 7.0 ¦ ¦ 대변기(세정밸브, 6 L/회) ¦ 25 ¦ 5.0 ¦ 5.0 ¦ 5.0 ¦ 8.0 ¦ ¦ 대변기(세정탱크, 6 L/회) ¦ 15 ¦ 2.5 ¦ 2.5 ¦ 2.5 ¦ 4.0 ¦ ¦ 소변기(3.8 L/회) ¦ 20 ¦ - ¦ - ¦ 4.0 ¦ 5.0 ¦ ¦ 소변기(3.8 L 이상/회) ¦ 20 ¦ - ¦ - ¦ 5.0 ¦ 6.0 ¦ ¦ 세면기 ¦ 10 ¦ 1.0 ¦ 0.5 ¦ 1.0 ¦ 1.0 ¦ ¦ 주방싱크(가정용) ¦ 15 ¦ 1.5 ¦ 1.0 ¦ 1.0 ¦ ¦ ¦ 식기세척기(가정용) ¦ 15 ¦ 1.5 ¦ 1.0 ¦ 1.5 ¦ ¦ ¦ 청소용 싱크 ¦ 15 ¦ - ¦ - ¦ 3.0 ¦ ¦ ¦ 세탁 싱크 ¦ 15 ¦ 2.0 ¦ 1.0 ¦ 2.0 ¦ ¦ ¦ 욕조/샤워 ¦ 15 ¦ 4.0 ¦ 3.0 ¦ - ¦ ¦ ¦ 샤워 ¦ 15 ¦ 2.0 ¦ 2.0 ¦ 2.0 ¦ ¦ ¦ 샤워(연속사용) ¦ 15 ¦ - ¦ - ¦ 5.0 ¦ ¦ ¦ 비데 ¦ 15 ¦ 1.0 ¦ 0.5 ¦ - ¦ ¦ ¦ 세탁기(가정용) ¦ 15 ¦ 4.0 ¦ 2.5 ¦ 4.0 ¦ ¦ ¦ 수음기 ¦ 10 ¦ - ¦ - ¦ 0.5 ¦ 0.75 ¦ ¦ 호스연결용 수도꼭지 ¦ 15 ¦ 2.5 ¦ 2.5 ¦ 2.5 ¦ ¦ ¦ 월풀욕조 ¦ 15 ¦ 1.0 ¦ 4.0 ¦ - ¦ ¦ 1. 표에 표시되지 않은 기구에 대해서는 사용빈도와 물소비 정도가 유사한 기구의 값을 적용한다. 2. 표의 값은 급탕에 필요한 급수량이 포함된 값이며, 중앙집중식 난방방식에서와 같이 급수, 급탕을 별도 배관으로 구분하여 공급하는 경우에 수치의 3/4 을 취한다. 3. 합산된 WSFUs 값을 기준으로 표 10 로부터 계통에 공급해야 할 급수량을 선정한다. 합산된 값이 0.5 이상이면 1 로(9.5 = 10) 0.4 이하는 버린다(9.4 = 9). 합산 결과 에 일치하는 값이 없을 때는 위로 근접하는 값을 취한다. 4. 접속관지름은 호칭지름 기준의 최소 관지름이다. 5. 상업용 건물이란 오피스, 공공시설, 호텔 등 숙박시설, 산업시설, 다층 건물 등 대중이용 시설 이외의 건물이나 시설을 말한다. 6. 다중이용시설이란 학교, 강당, 공연장, 영화관, 체육관, 운동경기장, 여객터미널 등으로 시간대 별로 물 사용이 집중되는 시설을 말한다. 7. 연속적으로 물 공급이 요구되는 수도꼭지나 기주가 있는 경우에는 그 기구에서 필요로 하는 유량만큼 또는 적당한 비율을 시스템의 전체 급수량에 가산한다. 262 기계설비 기술기준 매뉴얼 | {}
bba20871-9ff8-4418-8a50-8e191a78da88 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 표 10 동시사용 유량표, L/min ¦ 기구급수 부하단위 ¦ 세정탱크형 변기사용 1) ¦ 세정밸브형 변기사용 2) ¦ 기구급수 부하단위 ¦ 세정탱크형 변기사용 1) ¦ 세정밸브형 변기사용 2) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 3 ¦ 11 ¦ - ¦ 120 ¦ 185 ¦ 280 ¦ ¦ 4 ¦ 15 ¦ - ¦ 140 ¦ 201 ¦ 295 ¦ ¦ 5 ¦ 17 ¦ 83 ¦ 160 ¦ 216 ¦ 314 ¦ ¦ 6 ¦ 19 ¦ 87 ¦ 180 ¦ 231 ¦ 329 ¦ ¦ 7 ¦ 23 ¦ 91 ¦ 200 ¦ 246 ¦ 344 ¦ ¦ 8 ¦ 26 ¦ 95 ¦ 225 ¦ 265 ¦ 360 ¦ ¦ 9 ¦ 28 ¦ 98 ¦ 250 ¦ 284 ¦ 379 ¦ ¦ 10 ¦ 30 ¦ 102 ¦ 300 ¦ 322 ¦ 416 ¦ ¦ 11 ¦ 32 ¦ 106 ¦ 400 ¦ 397 ¦ 473 ¦ ¦ 12 ¦ 34 ¦ 110 ¦ 500 ¦ 473 ¦ 530 ¦ ¦ 13 ¦ 38 ¦ 112 ¦ 750 ¦ 643 ¦ 662 ¦ ¦ 14 ¦ 40 ¦ 114 ¦ 1000 ¦ 795 ¦ 795 ¦ ¦ 15 ¦ 42 ¦ 117 ¦ 1 250 ¦ 908 ¦ 908 ¦ ¦ 16 ¦ 45 ¦ 121 ¦ 1 500 ¦ 1 022 ¦ 1 022 ¦ ¦ 17 ¦ 47 ¦ 125 ¦ 1750 ¦ 1136 ¦ 1136 ¦ ¦ 18 ¦ 49 ¦ 127 ¦ 2000 ¦ 1230 ¦ 1 230 ¦ ¦ 19 ¦ 51 ¦ 129 ¦ 2500 ¦ 1 438 ¦ 1 438 ¦ ¦ 20 ¦ 53 ¦ 132 ¦ 3000 ¦ 1 646 ¦ 1 649 ¦ ¦ 25 ¦ 64 ¦ 144 ¦ 4000 ¦ 1 987 ¦ 1 987 ¦ ¦ 30 ¦ 76 ¦ 155 ¦ 5000 ¦ 2271 ¦ 2271 ¦ ¦ 40 ¦ 95 ¦ 178 ¦ 6000 ¦ 2460 ¦ 2 460 ¦ ¦ 50 ¦ 110 ¦ 193 ¦ 7000 ¦ 2650 ¦ 2650 ¦ ¦ 60 ¦ 125 ¦ 208 ¦ 8000 ¦ 2763 ¦ 2763 ¦ ¦ 80 ¦ 148 ¦ 235 ¦ 9000 ¦ 2877 ¦ 2877 ¦ ¦ 100 ¦ 167 ¦ 257 ¦ 10000 ¦ 2990 ¦ 2990 ¦ 주) 1. 여러 가지 기구가 혼재하는 계통에서 변기는 세정탱크 형(중력식 또는 압력식)이 설치되거나 또는 변기가 없는 경우의 급수량이나 일반적인 급탕량 선정에 적용한다. 2. 여러 가지 기구가 혼재하는 계통에서 변기는 세정밸브형이 설치되는 경우에 적용한다. 그림 11 기구급수부하단위에 의한 동시사용량 Chart Type: bar 0 500 1000 1500 2000 2500 3000 item_01 200/min 600/min 800/min 1000/min 1200/min 1400/min 1600/min (a) 동시사용유량 Chart Type: line 0 20 40 60 80 100 120 140 160 180 200 220 240 item_01 100Ω/min 120Ω/min 100Ω/min 20Ω/min 100Ω/min 220Ω/min 240Ω/min 260Ω/min 280Ω/min 300Ω/min 320Ω/min 340Ω/min 360Ω/min 기구급수부하단위수 (b) 동시사용유량 (일부확대) 주) 곡선 ①은 세척밸브(flush valve)가 않은 경우 곡선 ②는 세척탱크가 많은 경우에 적용한다. 국토교통부 263 기계설비 기술기준 해설 (별표 08 | {}
80b24223-c29d-4e5a-8b61-9d12bdf8db68 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 용어 ¦ 용어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 순간최대유량 ¦ 급수관에 접속된 기구의 사용 상태에 따라 그 급수관에 흐른다고 예상되는 유량 중 최대로 되는 순간 값을 말하며, 동시사용유량이라고도 한다.(해설서 주) ¦ 2.5 급탕배관 (1) 급탕배관 호칭지름 급탕관의 호칭지름은 급탕부하단위(FU) 값에 의한 순간최대유량으로 선정한다. (2) 환탕배관 호칭지름 환탕관의 유량은 급탕배관의 열손실을 구하여 계산하여 선정한다. 해 설 1. 본문 해설 및 관련 법규 (1 항) 설비공학 편람, 제 4 판 제 5 권 위생·소방·환경 제 6 장 급탕설비 참조 표 14 60°C 급탕의 기구급수부하단위(WSFU) ¦ ¦ 공동주택 ¦ 체육관 ¦ 병원 ¦ 호텔 기숙사 ¦ 공장 ¦ 사무소 ¦ 학교 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 개인세면기 ¦ 0.75 ¦ 0.75 ¦ 0.75 ¦ 0.75 ¦ 0.75 ¦ 0.75 ¦ 0.75 ¦ ¦ 공중세면기 ¦ - ¦ 1 ¦ 1 ¦ 1 ¦ 1 ¦ 1 ¦ 1 ¦ ¦ 샤워 ¦ 1.5 ¦ 1.5 ¦ 1.5 ¦ 1.5 ¦ 3.5 ¦ - ¦ 1.5 ¦ ¦ 욕조 ¦ 1.5 ¦ - ¦ 1.5 ¦ 1.5 ¦ - ¦ - ¦ - ¦ ¦ 주방싱크 ¦ 0.75 ¦ - ¦ 3 ¦ 1.5 ¦ 3 ¦ - ¦ 0.75 ¦ ¦ 청소싱크 ¦ 1.5 ¦ - ¦ 2.5 ¦ 2.5 ¦ 2.5 ¦ 2.5 ¦ 2.5 ¦ ¦ 수치료 욕조 ¦ - ¦ 5 ¦ - ¦ - ¦ - ¦ - ¦ - ¦ ¦ 식기세척기 ¦ 1.5 ¦ - ¦ ¦ ¦ ¦ ¦ ¦ 표 15 개략 급탕 기구급수부하단위(WSFU) ¦ 건물 종류 ¦ 기구급수부하단위(WSFU) ¦ ¦ --- ¦ --- ¦ ¦ 병원 ¦ 2.5/침상 ¦ ¦ 호텔 ¦ 2.5/객실 ¦ ¦ 사무소 ¦ 0.15/인 ¦ ¦ 초중고등학교 ¦ 0.30/학생 1) ¦ ¦ 공동주택 ¦ 3.00/호 ¦ 주) 1. 샤워 부하는 WSFU 에 가산한다. 2. 용어 내용 없음 264 기계설비 기술기준 매뉴얼 | {}
e10a75bf-5681-4ce6-bdb6-4d7b5430963a | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.6 오 · 배수배관 오 、 배수배관 호칭지름 산정은 최대 기구배수부하단위수(DFU)를 사용하여 산정한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 추가 설명 없음 2. 용어 ¦ 용어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 기구배수부하단위수 ¦ 기구배수부하단위(drainage fixture unit, DFU): 배수 시스템의 용량을 정확하게 구하 기 위하여 도입된 개념. DN 40 트랩이 달린 배수구를 사용하는 일반 세면기의 배수 속도는 약 7.5 GPM 으로, 이는 1 ft3/min 에 가까운 수치였으므로 1 ft3/min=1 DUF 로 정의 하였다. 그리고 다른 기구의 최대 배수량도 이 단위로 표시하도록 한 것이다. 출처: 위생설비공학. pp388-391 ¦ 2.7 통기배관 통기관의 최소 호칭지름은 배관길이와 연결되는 총 기구배수부하단위로 결정한다. 해 설 1. 본문 해설 및 관련 법규 (1 항) 2.6 참고 2. 용어 내용 없음 2.8 우수배수관 (1) 옥내 우수 수직관과 수평 지관의 호칭지름은 그 지역의 기상자료에 의한 시간최대강우량을 기준 으로 한다. (2) 최대 수평투영 지붕 면적으로 선정한다. 해 설 국토교통부 265 기계설비 기술기준 해설 (별표 08 | {}
a58c5f72-2fa3-4d1e-b777-8ebdbbca9675 | 국내_기계설비_기술기준_매뉴얼_최종본 | 1. 본문 해설 및 관련 법규 V (1 항, 2 항) 이 기준 [별표 6] 2.2.2 참조 2. 용어 V 내용 없음 2.9 냉매배관 (1) 냉매배관의 호칭지름 및 분기방법은 실내기의 합계용량과 같거나 크게 한다. (2) 냉매배관은 배관 최장 길이, 고저차 등의 배관길이 허용기준을 고려하여 선정한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항 ~ 2 항) 완성된 제품의 경우 제조사의 설계 기준을 따름 2. 용어 V 내용 없음 2.10 신축이음 (1) 관의 팽창, 수축을 충분히 흡수할 수 있도록 신축이음을 한다. (2) 배관의 신축량, 배관 호칭지름, 배관 공간, 사용압력 등에 따라 적합한 형식을 선정한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 이 기준 [별표 8] 2.3, 2.3.1 (1) 내용 참조 V (2 항) 추가 설명 없음 2. 용어 V 내용 없음 266 기계설비 기술기준 매뉴얼 | {}
13e5b7c8-f1e2-4425-9be8-ffd6094799c0 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 3. 배관설비 시공 3.1 냉 · 온수 및 냉각수 배관 3.1.1 일반사항 (1) 배관 시공 시 관의 신축을 고려하고, 균등한 기울기를 유지하며, 역기울기 및 공기발생 등 순환을 저해할 우려가 없도록 한다. (2) 관의 이음은 강관일 경우 DN 50 이하일 때는 나사이음, DN 65 이상일 때는 용접이음이나 다른 이음방식을 사용할 수 있다. (3) 배관계에서 공기가 체류할 우려가 있는 곳에는 공기빼기밸브를 설치한다. (4) 열원기기(냉동기, 보일러, 열교환기 등)에 안전밸브가 설치되어 있지 않은 경우에는 주배관의 적 절한 위치에 압력도피밸브와 배수 배관을 별도로 설치한다. (5) 주배관의 적절한 위치에 물채움을 위한 밸브와 물채움 높이를 확인할 수 있는 압력계를 설치한 다. 해 설 1. 본문 해설 및 관련 법규 V (1 항 ~ 5 항) 추가 설명 없음 2. 용어 V 내용 없음 3.1.2 관의 이음 (1) 관의 이음은 나사이음, 플랜지이음, 무용접 접합이음 또는 용접이음으로 한다. (2) 이음용 나사는 KS B 0222(관용 테이퍼나사)에 의한 나사로 한다. 이음에는 필요에 따라 이음재를 사용 할 수 있다. (3) 플랜지이음의 경우는 플랜지치수에 적합한 패킹을 사용한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항, 3 항) 추가 설명 없음 V (2 항) KS B 0222(관용 테이퍼나사) 국가표준인증 통합정보시스템 https://eloghtenc.com/agopendendoxical/19377924 2. 용어 국토교통부 267 기계설비 기술기준 해설 (별표 08 | {}
47f0241a-0386-42a4-98e4-79db03652a61 | 국내_기계설비_기술기준_매뉴얼_최종본 | 내용 없음 3.1.3 기울기 냉 、 온수와 냉각수 배관의 공급관은 역기울기, 환수관은 순기울기로 하고, 기울기는 1/250 이상으 로 한다. 해 설 1. 본문 해설 및 관련 법규 V 추가 설명 없음 2. 용어 내용 없음 --- 268 기계설비 기술기준 매뉴얼 | {}
f4a92ca6-4c88-46c8-9539-5a9efd867476 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 3.1.4 지지간격 및 기타 (1) 배관의 지지간격은 KCS 31 20 15(3.4) 표 3.4-1, KCS 31 20 15(3.12) 표 3.12-1 을 준용한 표 1 을 적용한다. (2) 실내의 수직관에는 각층마다 1 개소씩 신축을 방해하지 않는 흔들림 방지철물을 설치한다. (3) 동관 및 스테인리스강관을 지지할 때에는 절연조치를 해야 한다. 표 1 배관의 지지 간격(KCS 31 20 15(3.4) 표 3.4-1, KCS 31 20 15(3.12)) ¦ 배관 ¦ 적요 ¦ 적요 ¦ 적요 ¦ 간격 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 수직 관 ¦ 주철관 ¦ 직관 ¦ 직관 ¦ 1 개에 1 개소 ¦ ¦ 수직 관 ¦ 주철관 ¦ 이형관 ¦ 2 개 3 개 ¦ 어느 쪽이든 1 개소 중앙부에 1 개소 ¦ ¦ 수직 관 ¦ 강관 ¦ 강관 ¦ 강관 ¦ 각 층에 1 개소 이상 ¦ ¦ 수직 관 ¦ 연관, 경질 염화 비닐관, 동관 및 스테인리스강관 ¦ 연관, 경질 염화 비닐관, 동관 및 스테인리스강관 ¦ 연관, 경질 염화 비닐관, 동관 및 스테인리스강관 ¦ 각 층에 1 개소 이상 ¦ ¦ 수평배 관 ¦ 주철관 ¦ 직관 ¦ 직관 ¦ 1 개에 1 개소 ¦ ¦ 수평배 관 ¦ 주철관 ¦ 이형관 ¦ 이형관 ¦ 1 개에 1 개소 ¦ ¦ 수평배 관 ¦ 강관 ¦ DN 20 이하 DN 25 ~ 40 DN 50 ~ 80 DN 100 ~ 150 DN 200 이상 ¦ DN 20 이하 DN 25 ~ 40 DN 50 ~ 80 DN 100 ~ 150 DN 200 이상 ¦ 1.8 m 이내 2.0 m 이내 3.0 m 이내 4.0 m 이내 5.0 m 이내 ¦ ¦ 수평배 관 ¦ 연관 (길이 0.5 m 초과 시) ¦ 배관이 변형될 염려가 있는 곳에는 두께 0.4 mm 이상의 아연도 철판으로 반원형 받침대를 만들어 1.5 m 이내마다 지지한다. ¦ 배관이 변형될 염려가 있는 곳에는 두께 0.4 mm 이상의 아연도 철판으로 반원형 받침대를 만들어 1.5 m 이내마다 지지한다. ¦ 배관이 변형될 염려가 있는 곳에는 두께 0.4 mm 이상의 아연도 철판으로 반원형 받침대를 만들어 1.5 m 이내마다 지지한다. ¦ ¦ 수평배 관 ¦ 동관 ¦ DN 20 이하 DN 50 DN 25 ~ 40 DN 65 ~ 100 DN 125 이상 ¦ DN 20 이하 DN 50 DN 25 ~ 40 DN 65 ~ 100 DN 125 이상 ¦ 1.0 m 이내 2.0 m 이내 1,5 m 이내 2.5 m 이내 3.0 m 이내 ¦ ¦ 수평배 관 ¦ 경질 염화 비닐관 ¦ DN 16 이하 DN 20 ~ 40 DN 50 DN 65 ~ 125 DN 150 이상 ¦ DN 16 이하 DN 20 ~ 40 DN 50 DN 65 ~ 125 DN 150 이상 ¦ 0.75 m 이내 1.0 m 이내 1.2 m 이내 1.5 m 이내 2.0 m 이내 ¦ ¦ 수평배 관 ¦ 스테인리스관 (일반배관용, KSD3595) ¦ DN 20 이하 DN 25 ~ 40 DN 50 DN 65 ~ 100 DN 125 이상 ¦ DN 20 이하 DN 25 ~ 40 DN 50 DN 65 ~ 100 DN 125 이상 ¦ 1.0 m 이내 1.5 m 이내 2.0 m 이내 2.5 m 이내 3.0 m 이내 ¦ ¦ 냉매배관(동관) ¦ 냉매배관(동관) ¦ DN 20 이하 DN25 ~ 40 DN 50 DN 60 DN 80 DN 100 이상 ¦ DN 20 이하 DN25 ~ 40 DN 50 DN 60 DN 80 DN 100 이상 ¦ 1.5 m 이내 2.0 m 이내 2.5 m 이내 3.0 m 이내 3.5 m 이내 4.0 m 이내 ¦ 국토교통부 269 기계설비 기술기준 해설 (별표 08 | {}
f687df45-73ae-4a1d-96a5-a14668c60922 | 국내_기계설비_기술기준_매뉴얼_최종본 | 해 설 1. 본문 해설 및 관련 법규 V (1 항, 2 항) 추가 설명 없음 V (3 항) 이종 금속 접합에 따른 부식 방지 2. 용어 V 내용 없음 - ○----- - 3.2 온수온돌 배관 3.2.1 일반사항 (1) 설계에서 요구하는 배관간격이 유지되도록 하고, 온도변화에 따른 관의 신축을 고려하여 시공한 다. (2) 관의 굽힌 부분은 관의 변형 및 단면적 축소가 없도록 한다. (3) 축열재 충진 등의 작업 시 방열관이 변형되거나 밀리지 않도록 해야 하며, 방열관 및 단열층이 충 격 등에 의하여 변형 또는 손상되지 않도록 한다. (4) 코일배관 길이는 저항을 고려하여 결정하며, 온수분배기 주위 등 코일배관 조밀지역에는 과열방 지 조치를 한다. 3.2.2 관의 이음 (1) 매립부분에는 이음매가 없어야 하며, 부득이한 경우에는 이음부위의 처짐이나 접속불량 등으로 난방불량 및 누수가 발생하지 않도록 한다. (2) 이음부분을 위한 관의 절단은 관축에 직각이 되도록 하고, 절단면 가공을 하며, 관 내외부의 이물 질을 깨끗이 제거한 후 이음부분을 조립한다. 3.2.3 기울기 바닥배관은 수평을 유지하며, 역기울기 및 공기체류 등 온수순환을 저해할 우려가 없도록 한다. 3.2.4 지지간격 및 기타 (1) 방열관은 온도변화에 따라 변형, 신축, 이완 등으로 인한 기능 저하가 없도록 고정한다. (2) 방열관 작업 후 모르타르 마감 작업 전에 사용압력의 1.5 배 이상으로 구역별로 1 차 수압시험을 시행한다. 3.2.5 온수분배기 (1) 온수분배기 및 조절밸브류의 설치 위치는 조작, 점검, 보수가 쉬운 장소에 설치한다. (2) 온수분배기에는 공기빼기밸브를 설치하며, 필요한 경우 이물질 제거용 밸브도 추가하여 설치한 다. 해 설 1. 본문 해설 및 관련 법규 270 기계설비 기술기준 매뉴얼 | {}
9d790520-4d82-4c32-a076-e71bed396a15 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 V (3.2.1 1 항 ~ 3 항) 추가 설명 없음 V (3.2.1 4 항) 온수 분배기 등에서 배관 간격이 조밀하게 시공되는 공급 측에는 개별 배관의 단열 조 치 등을 통해 과열되지 않도록 함 V (3.2.2 ~ 3.2.4) 추가 설명 없음 V (3.2.5 1 항) 싱크대 하부에 설치하는 경우, 싱크 배수를 방해하지 않도록 함 V (3.2.5 2 항) 배관은 최대한 수평으로 설치하여 공기가 체류하지 못하도록 시공하는 것이 우선이며, 그럼에도 불구하고 공기체류가 예상되는 부분에는 공기빼기밸브를 설치해야 함 2. 용어 V 내용 없음 -- ○---- --- 3.3 증기배관 3.3.1 일반사항 (1) 시공은 모든 관의 온도변화에 따른 신축을 고려하여 배관하고, 팽창 시에는 배관의 각 부에 과대 한 응력이 걸리지 않도록 하며, 배관의 기울기를 유지하도록 한다. (2) 수평 순기울기 배관에서 호칭지름이 다른 관을 접속할 때에는 편심레듀서를 사용한다. (3) 수직관 아래 부분, 기타 각종장치와 연결되는 부분 등 필요한 장소에는 플랜지 이음쇠를 설치하여 관과 기기류의 분리가 쉽도록 한다. DN 50 이하의 노출 수평배관에는 유니언을 사용할 수 있다. (4) 실내에 노출된 벽면으로부터 간격은 나관 및 피복관에 있어서 모두 100 mm 이상으로 한다. (5) 진공환수식 난방의 수직 환수관에는 리프트 이음쇠를 사용한다. 리프트이음쇠의 흡상할 수 있는 1 단의 높이는 1.5 m 이내로 한다. (6) 증기주관의 말단, 입상관 하부 등 응축수가 체류할 우려가 있는 곳은 증기트랩을 설치한다. (7) 관 지지철물 및 고정철물은 온도변화에 따른 신축에 지장이 없는 것으로 한다. 3.3.2 관의 이음 (1) 관의 이음은 나사이음, 플랜지이음 또는 용접이음으로 한다. (2) 이음용 나사는 KS B 0222(관용 테이퍼나사)에 의한 나사로 한다. 이음에는 필요에 따라 이음재를 사용할 수 있다. (3) 플랜지이음의 경우는 플랜지치수에 적합한 패킹을 사용한다. 3.3.3 기울기 증기 공급관의 경우 순기울기(하향기울기)일 때에는 1/250 이상, 역기울기(상향기울기)일 때에는 1/80 이상으로 하며 환수관의 경우는 순기울기 1/200~1/300 로 한다. 3.3.4 지지간격 및 기타 (1) 배관의 지지간격은 표 1 에 따르며, 또한 곡부와 분기점에는 필요에 따라 지지한다. (2) 실내의 수직관에는 각층마다 최소 1 개소씩 관의 신축을 방해하지 않는 흔들림 방지철물을 설치 한다. (3) 수평관을 브래킷 등으로 밑에서 지지할 때에는 롤러 철물 등을 사용한다. 기계설비 기술기준 해설 (별표 08 국토교통부 271 | {}
d23a7e16-32b2-4b9d-93f4-0c796867ac86 | 국내_기계설비_기술기준_매뉴얼_최종본 | 해 설 1. 본문 해설 및 관련 법규 V (1 항) 추가 설명 없음 2. 용어 V 내용 없음 3.4 급수 · 급탕 배관 3.4.1 급수배관 (1) 관의 이음 ① 관의 이음은 나사이음, 플랜지이음, 용접이음, 무용접이음으로 한다. ② 관의 이음은 강관일 경우 DN 50 이하일 때는 나사이음, DN 65 이상일 때는 용접이음을 원칙으 로 하나 다른 이음방식을 사용할 수 있다 ③ 플랜지이음의 경우는 플랜지치수에 적합한 패킹을 사용한다. (2) 기울기 관 속의 물을 완전히 뺄 수 있도록 기울기를 주어야 하고, 공기가 모여 있는 곳이 없도록 시공한다. (3) 지지간격 및 기타 표 1 에 따른다. 3.4.2 급탕배관 (1) 관의 이음 3.4.1(1)에 따른다. (2) 기울기 3.4.1(2)에 따른다. (3) 지지간격 및 기타 표 1 에 따른다. 해 설 1. 본문 해설 및 관련 법규 V 추가 설명 없음 2. 용어 V 내용 없음 272 기계설비 기술기준 매뉴얼 | {}
8d3be0c0-0372-4631-8f5d-725034cf0852 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 3.5 냉매배관 3.5.1 배관일반 (1) 냉매배관은 장치의 기능이 떨어지지 않도록 팽창 및 수축을 고려하여 배관한다. (2) 관을 사용 전에 반드시 내면을 충분히 청소한 후 관 끝을 적당한 방법으로 막아 공사 중에 이물질 이 침입하는 것을 방지한다. (3) 분리할 필요가 있는 장소에는 플레어이음 또는 플랜지이음을 사용한다. 단, 플레어이음은 DN 20 이하의 관에만 사용한다. (4) 냉매분기관 및 배관사이즈는 연결되는 실내기의 합계용량에 맞게 제작업체의 자체 기준에 따른 다. (5) 라인분기관(Y 분기관)은 수평분기 또는 수직분기가 되도록 설치하고, 헤더분기관은 수평분기가 되도록 설치한다. 3.5.2 기울기 토출관 및 흡입 가스관은 냉매에 혼합되어 순환하는 냉동기유가 계통 내에 체류하는 일 없이 압축기 에 돌아오도록 고려한다. 수평관은 최소 1/400 이상의 앞 내림 기울기로 한다. 3.5.3 지지간격 지지간격은 표 1 에 따른다. 해 설 1. 본문 해설 및 관련 법규 완성된 제품의 경우 제조사의 설치 기준을 따름 2. 용어 V 내용 없음 ----- --- 기계설비 기술기준 해설 (별표 08 국토교통부 273 | {}
8a8d62cf-e0df-45af-9621-00243414fadc | 국내_기계설비_기술기준_매뉴얼_최종본 | 3.6 배관의 접합 3.6.1 일반사항 (1) 장비류 등과 연결되는 모든 배관은 그 운전중량이 장비에 직접 미치지 않도록 지지한다. (2) 배관의 시공 시 부식이 예상되는 부분에는 이종관의 절연부속, 방식 테이프 등을 사용하여 부식 을 방지하도록 한다. (3) 배관이 구조체 등을 통과 하여 슬리브 주위가 실내에 노출되어 마감이 필요한 경우에는 관좌금을 설치한다. 3.6.2 배관의 용접 접합 배관 용접은 용접기능사 자격증 소지자 또는 현장 용접 시험을 통과 한 자로 한다. (1) 강관 ① 강관의 용접 시공은 맞대기용접, 밀어넣기용접, 플랜지용접, 웰도렛(Weldolets) 등의 방법으로 한다. ② 백강관은 무용접을 원칙으로 하며, 용접 시 아연도금을 제거 후 실시한다. (2) 스테인리스 강관 TIG 용접 방식 등으로 용접하며, DN 50 이하의 배관은 선택적으로 소켓용접을 적용할 수 있다. 3.6.3 배관의 무용접 접합 (1) 동종관의 접합 배관재질 특성을 고려하여 적합한 무용접 접합을 한다. (2) 이종관의 접합 이종관의 접합은 KCS 31 20 15(3.2.2) 표 3.2-1 에 따른 표 2 를 적용한다. (3) 이중관 헤더 공법 ① 이중관의 곡률반경은 되도록 크게 하고, 굽힘 각도는 90° 이상으로 하며, 허용굽힘은 3 개소 이하 로 한다. ② 콘크리트 슬래브에 매설하는 경우는 하부 철근의 위에 설치하고, 상부 철근에 결속하고, 이중관 을 콘크리트 슬래브 위에 놓는 경우는 직선부는 1.5 m 마다 고정하고 굽힘부의 양끝에도 고정한 다. 표 2 이종관의 접합(KCS 31 20 15(3.2.2) 표 3.2-1) ¦ 접속 관종 ¦ 접속 관종 ¦ 적요 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 주철관 ¦ 강관 ¦ 각각의 이음을 코킹하여 나사접합 또는 플랜지 접합 ¦ ¦ 주철관 ¦ 연관 ¦ 각각의 이음을 코킹하여 납땜 또는 플랜지 접합 ¦ ¦ 주철관 ¦ 염화 비닐관 ¦ 각각의 이음을 코킹하여 TS 식 또는 고무링 접합 ¦ ¦ 강관 ¦ 스테인리스강관 ¦ 절연유니언, 절연플랜지에 의한 접합으로 하며 기타 이와 유사한 방 법의 절연조치 ¦ ¦ 강관 ¦ 동관 ¦ 어댑터를 사용하여 강관은 나사 접합, 동관은 용접 접합하고 절연유 니언 또는 절연플랜지를 사용하여 접합 ¦ ¦ 강관 ¦ 연관 ¦ 각각의 이음을 나사 접합 또는 땜납 접합 ¦ ¦ 강관 ¦ 염화 비닐관 ¦ 나사형 이음 또는 플랜지 접합 ¦ ¦ 연관 ¦ 동관 ¦ 납땜 접합 ¦ ¦ 연관 ¦ 염화 비닐관 ¦ 각각의 이음을 납땜 접합하여 접착제 접합 또는 고무링 접합 ¦ ¦ 동관 ¦ 스테인리스강관 ¦ 절연 유니언, 절연 플랜지에 의한 접합 ¦ 274 기계설비 기술기준 매뉴얼 | {}
86ed0d39-ce86-4059-9b1f-90816cd8ed72 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 해 설 1. 본문 해설 및 관련 법규 V 추가 설명 없음 2. 용어 내용 없음 국토교통부 275 기계설비 기술기준 해설 (별표 08 | {}
4da2491e-927d-4691-b262-4fb96eab884c | 국내_기계설비_기술기준_매뉴얼_최종본 | 3.7 배관의 수압시험 (1) 각 배관은 배관의 일부 또는 전체 배관 완료 후 수압시험 및 만수시험 등을 한다. 결로방지 및 보 온피복을 하는 배관, 은폐배관 또는 매설되는 배관들은 매설 전에 시험한다. (2) 각 시험의 기준 값은 KCS 31 20 15(3.15) 표 3.15-1 을 준용한 표 3 을 적용한다. (3) 배관의 시공이 완료되면 관내의 오염물질을 제거하기 위하여 주요 기기를 제거한 상태에서 세척 작업을 실시한다. 표 3 계통별 시험 기준(KCS 31 20 15(3.15) 표 3.15-1) ¦ 시험 방법 ¦ 시험 방법 ¦ 수압 · 만수 시험 ¦ 수압 · 만수 시험 ¦ 수압 · 만수 시험 ¦ 수압 · 만수 시험 ¦ 수압 · 만수 시험 ¦ 수압 · 만수 시험 ¦ 기압시험 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 최소압력 최소 유지 시간(min) ¦ 최소압력 최소 유지 시간(min) ¦ 1.0 MPa ¦ 사용압 력의 1.5 배 ¦ 설계도서에 기재된 펌 프 양정의 1.5 배 ¦ 가압송수 장치의 최 고 사용압 력의 1.5 배 ¦ 30 kPa ¦ 만수 ¦ 35 kPa ¦ ¦ 계 통 ¦ 계 통 ¦ 60 ¦ 60 ¦ 60 ¦ 60 ¦ 30 ¦ 30 ¦ 15 ¦ ¦ 증기 ¦ 증기 ¦ ¦ ○*1 ¦ ¦ ¦ ¦ ¦ ¦ ¦ 고온수 ¦ 고온수 ¦ ¦ ○*2 ¦ ¦ ¦ ¦ ¦ ¦ ¦ 냉·온수 냉각수 ¦ 냉·온수 냉각수 ¦ ¦ ○ *3 ○ *3 ¦ ¦ ¦ ¦ ¦ ¦ ¦ 온수온돌 ¦ 온수온돌 ¦ ¦ ○*3 ¦ ¦ ¦ ¦ ¦ ¦ ¦ 기름*4 ¦ 기름*4 ¦ ¦ ○ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 냉매*5 ¦ 냉매*5 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 급수 · 급탕 ¦ 직결 고가탱크이하 연결배관 양수관 ¦ ¦ ○*6 ¦ ○*6 ¦ ¦ ¦ ¦ ¦ ¦ 배 수 ¦ 건물 내 오수, 배수관 건물 내 빗물 배수관 배수펌프 토출관 ¦ ¦ ¦ ○*6 ¦ ¦ ○.... ○.... ¦ ········ ········ ¦ ¦ ¦ 통기 ¦ 통기 ¦ ¦ ¦ ¦ ¦ ○.... ¦ ········ ¦ ¦ ¦ ¦ ¦ 주 1) 압력은 배관의 최저부에서 측정한 것으로 한다. 2) 「수도법」의 규정이 있을 때는 이에 준한다. ¦ 주 1) 압력은 배관의 최저부에서 측정한 것으로 한다. 2) 「수도법」의 규정이 있을 때는 이에 준한다. ¦ 주 1) 압력은 배관의 최저부에서 측정한 것으로 한다. 2) 「수도법」의 규정이 있을 때는 이에 준한다. ¦ 주 1) 압력은 배관의 최저부에서 측정한 것으로 한다. 2) 「수도법」의 규정이 있을 때는 이에 준한다. ¦ 주 1) 압력은 배관의 최저부에서 측정한 것으로 한다. 2) 「수도법」의 규정이 있을 때는 이에 준한다. ¦ 주 1) 압력은 배관의 최저부에서 측정한 것으로 한다. 2) 「수도법」의 규정이 있을 때는 이에 준한다. ¦ 주 1) 압력은 배관의 최저부에서 측정한 것으로 한다. 2) 「수도법」의 규정이 있을 때는 이에 준한다. ¦ 비고 3) 중온수배관은 열사용시설 기준을 적용한다. *1 최소 0.5 MPa 로 한다. *2 최소 1.0 MPa 로 한다. *3 최소 1.0 MPa 로 한다. *4 「위험물 규제에 관한 시행령」, 동규칙 및 지방조례에 근거한 소정 의 시험 압력으로 할 수 있다. *5 「고압가스 안전관리법」에 정하는 기밀시험을 행한다. *6 최소 0.75 MPa 로 한다. 4) O........O 어느 쪽이든 O 표시에 해당하는 시험으로 한다. 해 설 276 기계설비 기술기준 매뉴얼 | {}
3c02d6cf-f53b-43c4-a35a-75cfb1c98e41 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 1. 본문 해설 및 관련 법규 V (1 항, 3 항) 추가 설명 없음 (2 항) 표 3 의 건물 내 오 · 배수배관, 우수배수관 및 통기관의 시험기준은 30 kPa 이상의 수압시험 이나 만수시험 또는 35 kPa 이상의 기압시험 중 하나로 함 2. 용어 V 내용 없음 국토교통부 277 기계설비 기술기준 해설 (별표 08 | {}
c9648b00-9f30-4671-aefd-cd1e21cf4790 | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 9] 덕트설비의 설계 및 시공 기준 1. 덕트설비 일반사항 1.1 목적 이 기준은 건축물, 시설물 등의 공기조화설비 및 환기설비에 필요한 덕트설비의 설계 및 시공 방법 등 세부 기술기준을 정함을 목적으로 한다. 해 설 이 기준의 목적은 「기계설비법」 제 14 조(기계설비 기술기준)과 같은 법 영 제 2 조 및 [별표 2]에 근 거하여, 건축물이나 시설물에 필요한 덕트설비의 설계 및 시공 시 기계설비의 안전과 성능을 확 보하기 위하여 필요한 기술적 요건을 규정하기 위함 「기계설비법」 제 14 조(기계설비 기술기준) ① 국토교통부장관은 기계설비의 안전과 성능확보를 위하여 필요 한 기술기준(이하 "기술기준이라 한다)를 정하여 고시하여야 한다. 이를 변경하는 경우에도 또한 같다. 1.2 적용범위 이 기준은 건축물, 시설물 등에 공기조화 및 환기용 덕트설비를 설치하는 경우에 대하여 적용한다. 해 설 이 기준의 적용범위는 「기계설비법」 제 2 조제 1 호에 따른 건축물등에 같은 법 영 제 2 조에 따라 대 통령령으로 정한 덕트설비를 설치하는 경우 및 그와 관련된 부속설비들을 포함함 「기계설비법」 제 2 조(정의) 1. "기계설비"란 건축물, 시설물 등(이하 "건축물등"이라 한다)에 설치된 기계 · 기 구 · 배관 및 그 밖에 건축물등의 성능을 유지하기 위한 설비로서 대통령령으로 정하는 설비를 말한다. 「기계설비법 시행령」 제 2 조(기계설비의 범위) 「기계설비법」(이하 "법"이라 한다) 제 2 조제 1 호에서 "대통령령 으로 정하는 설비"란 별표 1 의 설비를 말한다. 「기계설비법 시행령」 [별표 1] 기계설비의 범위 8. 덕트(duct)설비 : 건축물등에 설치된 기계 · 기구 · 배관 및 그 밖에 성능을 유지하기 위한 설비의 풍량 등 을 조절하고 급기(��) · 배기 및 환기 등을 위하여 설치된 설비 278 기계설비 기술기준 매뉴얼 | {}
fc742569-b33a-415c-a5de-7904365911a8 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 1.3 타 규정과 의 관계 다음의 규정과 이 기준에서 정하는 내용이 상이한 경우에는 해당 규정을 따른다. (1) KDS 31 25 20 환기설비 설계기준 (2) KDS 31 25 30 덕트설비 설계기준 (3) KCS 31 20 20 덕트설비공사 표준시방서 (4) KCS 31 25 20 환기설비공사 표준시방서 해 설 이 기준과 타 규정 및 기준과 다른 경우에는 상기 규정에 명시된 내용을 따름 국토교통부 279 기계설비 기술기준 해설 (별표 09 | {}
ea30d70b-67ea-49a3-867d-aa68c06d44dc | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 덕트설비 설계 2.1 일반사항 (1) 덕트 장단비는 4:1 이내가 되도록 한다. 단, 장단비를 초과 할 경우에는 보강조치를 한다. (2) 송풍기의 마찰손실이 적게 주경로 및 분기회로의 경로를 정한다. (3) 급기덕트의 곡관 덕트에서 덕트 폭의 6 배 거리 이내에 분기덕트를 설치할 경우에는 곡관부에 터 닝베인 등을 설치하여 분기점에서 정상류가 되도록 한다. (4) 덕트의 축소는 30°, 확대는 15° 이하로 완만하게 한다. (5) 직각으로 꺾이는 부분은 마찰손실이 적도록 곡률반경 1.5 이상의 엘보를 사용하거나 불가피한 경 우에 터닝베인을 설치한다. (6) 각 토출구와 흡입구에서 설계 풍량이 나올 수 있게 등속법, 등마찰손실법, 정압재취득법 등을 고 려하여 덕트 크기를 정해야 한다. (7) 별표 12 의 표 1 에 따른 실내허용소음 기준 이하가 되도록 소음장치를 고려하여 설계한다. (8) 소음이 민감한 덕트 계통에서는 마찰손실이 낮은 부속을 사용하고, 저속 덕트로 크기를 정한다. (9) 주 덕트 가까이에는 소음 발생이 우려되므로 말단기구를 설치해서는 안 된다. (10) 외기루버는 전면풍속 2 m/s 이하, 배기 루버는 전면풍속 2.5 m/s 이하를 기준으로 하고 루버의 개구율을 고려하여 루버의 크기를 산정한다. (11) 2.2 의 덕트 외 사용 용도에 따라 알루미늄 덕트, 글라스 파이버 덕트 등을 사용할 수 있다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 덕트 장단비는 4:1 을 초과 할 경우에는 인접실에 대해 이 기준 [별표 12] 2.1 의 소음기준을 함께 검토해야 함 V (2 항 ~ 5 항, 7 항 ~ 8 항, 10 항 ~ 11 항) 추가 설명 없음 V (6 항) 등속법, 등마찰손실법, 정압재취득법 등의 설계 방법은 설비공학 편람, 제 4 판 제 1 권 제 16 장 4.5 덕트 설계법 참조 V (9 항) 사람이 상주하지 않은 공간에서는 예외로 할 수 있음 V 기계설비 시공용 샵드로잉을 위한 Revit 기반 plug-in 프로그램(KMBIM)을 이용하여 덕트(배관)를 쉽고 빠르게 설계할 수 있으며, 해당 프로그램은 대한기계설비산업연구원 홈페이지 (http://www.krimfi.re.kr/)에서 구매하여 이용할 수 있음 280 기계설비 기술기준 매뉴얼 | {}
caebf183-4325-4fba-a0ad-f448fb27a5f7 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 ![image](/image/placeholder) HOME SITEMAP ENGLISH 검색어를 입력하세요 검색 KRIMFI KRIMFI PIE 대한기계설비산업연구원 연구활동 발간자료 산업동향 BIM 소개 알림마당 연구원소개 (기계설비배관단열 설계 프로그램) 연구개요 연구보고서 기계설비산업동 BIM 소개 KRIMFI 소식 인사말 연구현황 KRIMFI REVIEW �기술동향 자료실 언론보도 이사장 소개 연구논문 기타발간물 �정책동향 게시판(Q&A) 홍보자료 원장 소개 �경기동향 구매 신청 연구제안 및 문의 설립목적·연혁 비전·주요사업 조직·업무 CI 오시는 길 찾을 내용(E): 대한기계설비 전액 사항 ⑥ It ▶ 종류 대소문자구별(U) 온전한 낱말(인) 여러 드 책임급 연구원 초빙 공고 떡이쓰기 무서(J) 아무게 문자(1) 한글로 단위 찾기(A) 조건식 사용(� 닫기 방향: 아래족(�) 위쪽(1) 문서 전체(L) ··· 1994 연구보고서 KRIMFI 의 연구보고서 정보입니다. FW 산업동향 I 기계설비산업의 최신동향 자료입니다. 연구 보고서 MORE ▶ 전체 기술동향 정책동향 경기동향 MORE 대한기계설비산업연구원 홈페이지 상단 "BIM 소개" 행거 배치(단독, 다중) 간섭(장애물) 회피 9 ↑ B 0% 헤더 모델링 지정 레벨 까지 모델링 (냉온수 공급/환수, 증기) 헤더에 연결되는 배관의 사이즈 지정 헤더의 높이, 밸브의 높이 시스템 유형, 삽입 패밀리 지정 온도와 KMBIM 프로그램 화면 2. 용어 ¦ 용어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 전면풍속 ¦ 덕트기구의 실 개구면적에 대한 평균 풍속(해설서 주) ¦ 국토교통부 281 기계설비 기술기준 해설 (별표 09 | {}
ef836fa0-b652-47e3-b624-9b9bbaf876cc | 국내_기계설비_기술기준_매뉴얼_최종본 | 2.2 덕트 2.2.1 아연도금 강판제 및 알루미늄 아연합금도금 강판제 덕트 (1) 덕트의 호칭과 압력범위 덕트압력 분류에 의한 덕트 호칭과 압력범위는 KCS 31 20 20(3.2.1) 표 3.2-1 에 따른 표 1 을 적용 한다. 표 1 덕트의 호칭과 압력범위(KCS 31 20 20(3.2.1) 표 3.2-1) ¦ 압력분류에 의한 덕트 호칭 ¦ 압력 범위 ¦ 압력 범위 ¦ 유속 범위 (m/s) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 압력분류에 의한 덕트 호칭 ¦ 상용압력(Pa)주 1) ¦ 제한압력(Pa)주 2) ¦ 유속 범위 (m/s) ¦ ¦ 저압 덕트 ¦ +500 이하 -500 이하 ¦ +1 000 이하 -750 이하 ¦ 15 이하 ¦ ¦ 고압 1 덕트 ¦ +500~+1 000 이하 -500~-1 000 이하 ¦ + 1 500 이하 -1 500 이하 ¦ 20 이하 ¦ ¦ 고압 2 덕트 ¦ +1 000~+2 500 이하 -1 000~-2 000 이하 ¦ +3 000 이하 -2 500 이하 ¦ 20 이하 ¦ 주 1) 상용압력: 정상운전 상태에서 덕트 내의 최대 정압 주 2) 제한압력: 덕트 내 댐퍼를 급격히 폐쇄하여 압력이 일시적으로 상승하는 경우의 제한압력을 말한다. 해 설 1. 본문 해설 및 관련 법규 추가 설명 없음 2. 용어 V 내용 없음 282 기계설비 기술기준 매뉴얼 | {}
af60c273-4f6a-4c8e-8021-31a0e118a610 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 (2) 덕트의 판두께 ① 장방형 덕트 장방형 덕트는 앵글플랜지 공법 및 코너볼트 공법으로 하고, 덕트의 판두께는 KCS 31 20 20(3.2.1) 표 3.2-2 를 준용한 표 2 를 적용한다. 이형변의 경우에는 그 최대치수로 한다. ② CB(Cross Beading)덕트 CB 덕트의 판두께는 KCS 31 20 20(3.2.1) 표 3.2-3 을 준용한 표 3 을 적용한다. 이형변의 경우에 는 그 최대치수로 한다. ③ 스파이럴 덕트 직관은 아연도금철판 KS D 3506(용융 아연 도금 강판 및 강대)을 스파이럴 형태로 기계 제작한 것으로 호칭치수는 안지름을 표시하며 그 판 두께는 KCS 31 20 20(3.2.1) 표 3.2-4 를 준용한 표 4 를 적용한다. 표 2 장방형 덕트의 판두께(KCS 31 20 20(3.2.1) 표 3.2-2) ¦ 구분 ¦ 저압덕트(mm) ¦ 고압 1, 2 덕트(mm) ¦ 판 두께(mm) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 덕트의 장변 ¦ 450 이하 450 초과 750 이하 750 초과 1 500 이하 1 500 초과 2250 이하 2250 초과 ¦ - - 450 이하 450 초과 1 200 이하 1 200 초과 ¦ 0.5 0.6 0.8 1.0 1.2 ¦ 표 3 CB 덕트의 판두께(KCS 31 20 20(3.2.1) 표 3.2-3) ¦ 구분 ¦ 저압덕트(mm) ¦ 고압 1, 2 덕트(mm) ¦ 판 두께(mm) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 덕트의 장변 ¦ 450 이하 450 초과 750 이하 750 초과 1 500 이하 1 500 초과 2250 이하 2250 초과 ¦ - - 450 이하 450 초과 1 200 이하 1 200 초과 ¦ 0.5(0.45 주 1)) 0.5 0.6 0.8 1.0 ¦ 주 1) 판두께(0.45)는 주문생산만 가능 표 4 스파이럴 덕트의 판두께(KCS 31 20 20(3.2.1) 표 3.2-4) ¦ 덕트 압력구분 ¦ 저압덕트(mm) ¦ 고압 1, 2 덕트(mm) ¦ 판 두께(mm) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 덕트의 지름 ¦ 450 이하 450 초과 750 이하 750 초과 1 000 이하 1 000 초과 ¦ 200 이하 200 초과 600 이하 600 초과 800 이하 800 초과 1 000 이하 1 000 초과 ¦ 0.5 0.6 0.8 1.0 1.2 ¦ 해 설 1. 본문 해설 및 관련 법규 V 추가 설명 없음 국토교통부 283 기계설비 기술기준 해설 (별표 09 | {}
d99d0a42-987b-4e0e-a0f5-791bbc1eb2d1 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 용어 내용 없음 (3) 덕트의 행거 및 지지 ① 장방형 덕트의 행거 및 지지는 KCS 31 20 20(3.2.1) 표 3.2-20 을 준용한 표 5 를 적용한다. 가. 수평방향의 주덕트에는 흔들림 방지를 위하여 형강으로 12 m 이하의 간격으로 지지한다. 나. 주기계실 내에 설치하는 덕트(앵글공법, 슬라이드공법, 공판공법)의 장변이 450 mm 이하인 덕트의 행거 간격은 2 m 이내로 한다. 다. 주기계실 내에 설치하는 앵글공법, 슬라이드공법의 덕트의 장변이 450 mm 초과 하는 경우의 행거 간격은 2.5 m 이내로 한다. 라. 나, 다.의 경우에서도 덕트 윗변과 구조슬래브 아래 면과 의 공간이 750 mm 미만인 경우에는 표 5 의 값으로 하여도 된다. ② 스파이럴 덕트의 행거 및 지지는 KCS 31 20 20(3.2.1) 표 3.2-21 을 준용한 표 6 을 적용한다. 표 5 장방향 덕트의 행거 및 지지(KCS 31 20 20(3.2.1) 표 3.2-20) ¦ 덕트의 장변 (mm) ¦ 행거 ¦ 행거 ¦ 지지대 ¦ 최대간격(mm) ¦ 최대간격(mm) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 덕트의 장변 (mm) ¦ 형강치수 (mm) ¦ 봉강(지름) (mm) ¦ 형강치수 (mm) ¦ 앵글공법, 슬라이드공법 ¦ 공판공법 ¦ ¦ 750 이하 ¦ 25x25x3 ¦ 9 ¦ 25x25x3 ¦ 3 680 ¦ 3 000 ¦ ¦ 750 초과 1 500 이하 ¦ 30x30x3 ¦ 9 ¦ 30x30x3 ¦ 3 680 ¦ 3 000 ¦ ¦ 1 500 초과 2200 이하 ¦ 40x40x3 ¦ 9 ¦ 40x40x3 ¦ 3 680 ¦ 3 000 ¦ ¦ 2200 초과 ¦ 40x40x5 ¦ 9 ¦ 40x40x5 ¦ 3 680 ¦ - ¦ 표 6 스파이럴 덕트 행거 및 지지(KCS 31 20 20(3.2.1) 표 3.2-21) ¦ 호칭치수(mm) ¦ 행거 ¦ 행거 ¦ 지지대 ¦ 최대간격 (mm) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 호칭치수(mm) ¦ 평강치수(mm) ¦ 봉강(지름)(mm) ¦ 형강치수(mm) ¦ 최대간격 (mm) ¦ ¦ 1 250 이하 ¦ 25x3 ¦ 9 ¦ 25x25x3 ¦ 3000 ¦ 해 설 1. 본문 해설 및 관련 법규 추가 설명 없음 2. 용어 내용 없음 284 기계설비 기술기준 매뉴얼 | {}
8c0ce143-8833-4ad7-aed0-4b7d7fdb081c | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.2.2 스테인리스 강판제 덕트 (1) 덕트의 판 두께 ① 장방형 덕트 내부정압이 ±500 Pa 이내이고, 풍속이 15 m/s 이하인 경우 덕트의 판 두께는 KCS 31 20 20(3.2.2) 표 3.2-22 에 따른 표 7 을 적용한다. 이형관의 경우에는 그 최대치수로 한다. ② 스파이럴 덕트 직관은 스테인리스 강판을 스파이럴형으로 기계적으로 말아서 만든 것으로 호칭치수는 안지름을 기준으로 한다. 내부정압이 ±500 Pa 이내이고, 풍속이 15 m/s 이하인 덕트의 판 두께는 KCS 31 20 20(3.2.2) 표 3.2-23 에 따른 표 8 을 적용한다. 표 7 스테인리스 장방형 덕트의 판 두께(KCS 31 20 20(3.2.2) 표 3.2-22) ¦ 덕트의 장변(mm) ¦ 판 두께(mm) ¦ ¦ --- ¦ --- ¦ ¦ 750 이하 ¦ 0.5 ¦ ¦ 750 초과 1 500 이하 ¦ 0.6 ¦ ¦ 1 500 초과 2 200 이하 ¦ 0.8 ¦ ¦ 2 200 초과 ¦ 1.0 ¦ 표 8 스테인리스 스파이럴 덕트의 판 두께(KCS 31 20 20(3.2.2) 표 3.2-23) ¦ 호칭 치수(mm) ¦ 판 두께(mm) ¦ ¦ --- ¦ --- ¦ ¦ 600 이하 ¦ 0.5 ¦ ¦ 600 초과 800 이하 ¦ 0.6 ¦ ¦ 800 초과 1 000 이하 ¦ 0.8 ¦ 해 설 1. 본문 해설 및 관련 법규 추가 설명 없음 2. 용어 내용 없음 국토교통부 285 기계설비 기술기준 해설 (별표 09 | {}
d28a2a95-300a-4050-af23-ae0596be5eec | 국내_기계설비_기술기준_매뉴얼_최종본 | (2) 덕트의 행거 및 지지 ① 장방형 덕트의 행거 및 지지는 KCS 31 20 20(3.2.2) 표 3.2-28 을 준용한 표 9 를 적용한다. 가. 주기계실에 설치하는 덕트의 장변이 450 mm 이하의 덕트에 행거간격은 2 m 이내로 한다. 나. 주기계실에 설치하는 덕트의 장변이 450 mm 를 초과 하는 경우의 행거간격은 2.5 m 이내로 한다. 다. 가. 나. 의 경우에도 덕트의 윗변과 구조 슬래브 하면과 의 공간이 750 m 미만의 경우에는 표 9 의 값으로 할 수 있다. ② 스파이럴 덕트의 행거 및 지지는 KCS 31 20 20(3.2.2) 표 3.2-29 를 준용한 표 10 을 적용한다. 주기계실 내에 설치하는 덕트(앵글공법, 슬라이드공법, 공판공법)의 장변이 450 mm 이하인 경 우의 덕트의 행거 간격은 2 m 이내로 한다. 표 9 스테인리스 장방형 덕트의 행거 및 지지(KCS 31 20 20(3.2.2) 표 3.2-28) ¦ 덕트의 장변 (mm) ¦ 행거 ¦ 행거 ¦ 행거 ¦ 지지대 ¦ 지지대 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 덕트의 장변 (mm) ¦ 형강치수 (mm) ¦ 봉강 지름 (mm) ¦ 최대간격 (mm) ¦ 형강치수 (mm) ¦ 최대간격 (mm) ¦ ¦ 750 이하 ¦ 25x25x3 ¦ 9 ¦ 3 000 ¦ 25x25x3 ¦ 4 000 ¦ ¦ 750 초과 1 500 이하 ¦ 30x30x3 ¦ 9 ¦ 3 000 ¦ 30x30x3 ¦ 4 000 ¦ ¦ 1 500 초과 2 200 이하 ¦ 40x40x3 ¦ 9 ¦ 3 000 ¦ 40x40x3 ¦ 4 000 ¦ ¦ 2 200 초과 ¦ 40x40x5 ¦ 9 ¦ 3 000 ¦ 40x40x5 ¦ 4 000 ¦ 표 10 스테인리스 스파이럴 덕트의 행거 및 지지(KCS 31 20 20(3.2.2) 표 3.2-29) ¦ 호칭 치수 (mm) ¦ 행거 ¦ 행거 ¦ 행거 ¦ 지지대 ¦ 지지대 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 호칭 치수 (mm) ¦ 평강치수 (mm) ¦ 봉강(지름) (mm) ¦ 최대간격 (mm) ¦ 평가치수 (mm) ¦ 최대간격 (mm) ¦ ¦ 1 000 이하 ¦ 25x3 ¦ 9 ¦ 3 000 ¦ 25x25x3 ¦ 3 000 ¦ 해 설 1. 본문 해설 및 관련 법규 추가 설명 없음 2. 용어 내용 없음 286 기계설비 기술기준 매뉴얼 | {}
273c99a7-a704-4bd8-857d-d102a749e2cb | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.2.3 경질염화비닐판제 덕트 덕트의 내부정압은 ±3,000 Pa 이내로 하며, 풍속은 15 m/s 이하로 한다. 또, 덕트 내외의 공기온도 는 40°C 이하로 한다. (1) 덕트의 판 두께 ① 장방형 덕트 덕트의 판 두께(mm)는 KCS 31 20 20(3.2.3) 표 3.2-30 에 따른 표 11 을 적용하고 이형변의 경우 에는 그 최대의 치수로 한다. ② 원형 덕트 직관의 호칭치수는 안지름을 기준으로 하며, 덕트의 판 두께(mm)는 KCS 31 20 20(3.2.3) 표 3.2-31 에 따른 표 12 를 적용한다. 표 11 경질염화비닐판제 장방형 덕트의 판 두께(KCS 31 20 20(3.2.3) 표 3.2-30) ¦ 덕트의 장변 (mm) ¦ 정 압 [Pa] ¦ 정 압 [Pa] ¦ 정 압 [Pa] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 덕트의 장변 (mm) ¦ 1,500 이하 ¦ 1,500 이상 2,000 이하 ¦ 2,000 이상 3,000 이하 ¦ ¦ 500 이하 ¦ 3 ¦ 3 ¦ 4 ¦ ¦ 500 초과 1 000 이하 ¦ 4 ¦ 5 ¦ 5 ¦ ¦ 1 000 초과 1 500 이하 ¦ 5 ¦ 5 ¦ 5 ¦ ¦ 1 500 초과 2 000 이하 ¦ 5 ¦ 5 ¦ 5 ¦ ¦ 2 000 초과 3 000 이하 ¦ 6 ¦ 6 ¦ 6 ¦ 표 12 경질염화비닐판제 원형 덕트의 판 두께(KCS 31 20 20(3.2.3) 표 3.2-31) ¦ 호칭 치수 (mm) ¦ 정 압 [Pa] ¦ 정 압 [Pa] ¦ 정 압 [Pa] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 호칭 치수 (mm) ¦ 1500 이하 ¦ 1500 초과 2000 이하 ¦ 2 000 초과 3 000 이하 ¦ ¦ 300 이하 ¦ 3 ¦ 3 ¦ 3 ¦ ¦ 300 초과 500 이하 ¦ 3 ¦ 4 ¦ 4 ¦ 해 설 1. 본문 해설 및 관련 법규 추가 설명 없음 2. 용어 내용 없음 기계설비 기술기준 해설 (별표 09 국토교통부 287 | {}
288a3809-de60-4f92-8a9b-9044126c8506 | 국내_기계설비_기술기준_매뉴얼_최종본 | (2) 덕트의 이음매 ① 직관부는 4 변 굽힘가공으로 하고, 열풍용접 등에 의한 맞대기 또는 적합한 판접합으로 한다. ② 용접하는 판의 끝부분은 줄, 그라인더 등으로 각도 60~90°로 면가공을 한다. 해 설 1. 본문 해설 및 관련 법규 추가 설명 없음 2. 용어 내용 없음 (3) 덕트의 접속 ① 장방형 덕트의 접속은 KCS 31 20 20(3.2.3) 표 3.2-32 를 준용한 표 13 을 적용한다. ② 원형덕트의 접속 KS M 3402(수도용 경질 폴리염화비닐 이음관)의 냉간공법에 의하거나 또는 열풍용접 등에 의해 판접합으로 하며, 필요에 따라 KCS 31 20 20(3.2.3) 표 3.2-33 을 준용한 표 14 의 플랜지 접합으 로 한다. 표 13 경질염화비닐판제 장방형 덕트의 접속(KCS 31 20 20(3.2.3) 표 3.2-32) ¦ 덕트의 장변 (mm) ¦ 접합용 플랜지 ¦ 접합용 플랜지 ¦ 접합용 플랜지 ¦ 접합용 플랜지 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 덕트의 장변 (mm) ¦ 경질염화비닐제 앵글(mm) ¦ 최대간격 (mm) ¦ 접합용 볼트쥐) ¦ 접합용 볼트쥐) ¦ ¦ 덕트의 장변 (mm) ¦ 경질염화비닐제 앵글(mm) ¦ 최대간격 (mm) ¦ 호칭지름(mm) ¦ 피치(mm) ¦ ¦ 500 이하 ¦ 50x50x6 ¦ 4000 ¦ M8(M10) ¦ 100(75) ¦ ¦ 500 초과 1 000 이하 ¦ 60x60x7 ¦ 4 000 ¦ M8(M12) ¦ 100(75) ¦ ¦ 1 000 초과 1 500 이하 ¦ 60x60x7 ¦ 3 000 ¦ M8(M12) ¦ 100(75) ¦ ¦ 1 500 초과 2 000 이하 ¦ 60x60x7 ¦ 3 000 ¦ M8 ¦ 100 ¦ ¦ 2 000 초과 3 000 이하 ¦ 60x60x7 ¦ 2000 ¦ M8 ¦ 100 ¦ 주 1) 접합용 볼트 및 너트는 스테인리스강이며, ( )는 경질염화 비닐제 볼트이다. 표 14 경질염화비닐판제 원형 덕트의 접속(KCS 31 20 20(3.2.3) 표 3.2-33) ¦ 호칭치수 (mm) ¦ 접합용 플랜지주 2) ¦ 접합용 볼트주 1) ¦ 접합용 볼트주 1) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 호칭치수 (mm) ¦ 경질염화비닐제 앵글(mm) ¦ 호칭지름(mm) ¦ 피치(mm) ¦ ¦ 400 이하 ¦ 40x40x5 ¦ M8(M10) ¦ 100(75) ¦ ¦ 400 초과 500 이하 ¦ 50x50x6 ¦ M8(M10) ¦ 100(75) ¦ 주 1) ( )는 경질염화 비닐제 볼트이다. 2) 호칭치수 400 이하의 접합용 플랜지는 경질염화 비닐제 앵글대신 판 플랜지 40 w x 7 t 로 해도 된다. 288 기계설비 기술기준 매뉴얼 | {}
92e6d11d-14aa-49a4-b24f-7f60c9907397 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 해 설 1. 본문 해설 및 관련 법규 추가 설명 없음 2. 용어 내용 없음 (4) 덕트의 보강 보강은 보강재의 제작 및 가공은 접합용 플랜지에 준하지만, 경질염화비닐제 앵글은 열풍용접 등으 로 덕트에 설치하고 보강용 평강은 경질염화비닐제 앵글에 스테인리스 강제 볼트로 설치한다. 또, 볼트 및 너트는 경질염화비닐제를 사용하지 않는다. ① 장방형 덕트의 이음매 사이의 횡방향 보강은 KCS 31 20 20(3.2.3) 표 3.2-34 를 준용한 표 15 를 적용한다. ② 장방형 덕트의 이음사이의 종방향 보강은 KCS 31 20 20(3.2.3) 표 3.2-35 에 따른 표 16 을 적용 한다. 표 15 경질염화비닐판제 장방형 덕트의 이음매 사이 횡방향 보강(KCS 31 20 20(3.2.3) 표 3.2-34) ¦ 덕트의 장변(mm) ¦ 외 부 보 강주 1) ¦ 외 부 보 강주 1) ¦ 외 부 보 강주 1) ¦ 부착용 볼트주 1) ¦ 부착용 볼트주 1) ¦ 타이로드 에 의한 내부보강 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 덕트의 장변(mm) ¦ 경질염화비닐 제앵글(mm) ¦ 평강 (mm) ¦ 최대간격 (mm) ¦ 호칭지름 (mm) ¦ 피치 (mm) ¦ 타이로드 에 의한 내부보강 ¦ ¦ 500 이하 500 초과 1 000 이하 1 000 초과 1 500 이하 1 500 초과 2 000 이하 2 000 초과 3 000 이하 ¦ 50x50x6 60x60x7 60x60x7 60x60x7 60x60x7 ¦ - (50x4) 50x4 50x4 50x4 ¦ 1 000 (500) ¦ - (M8) M8 M8 M8 ¦ - (150) 150 150 150 ¦ - 1 개소 1 개소 2 개소 ¦ 주 1)( )내는 1.5 kPa 를 초과, 3.0 kPa 이하의 것 표 16 경질염화비닐판제 장방형 덕트의 이음매 사이 종방향 보강(KCS 31 20 20(3.2.3) 표 3.2-35) ¦ 덕트의 폭 (mm) ¦ 외 부 보 강 ¦ 외 부 보 강 ¦ 설치장소 ¦ 부착용 볼트 ¦ 부착용 볼트 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 덕트의 폭 (mm) ¦ 경질염화비닐 제 앵글(mm) ¦ 평강 (mm) ¦ 설치장소 ¦ 호칭지름 (mm) ¦ 피치 (mm) ¦ ¦ 2 000 초과 3 000 이하 ¦ 60x60x7 ¦ 50x4 ¦ 중앙에 1 개소 ¦ M8 ¦ 150 ¦ 해 설 국토교통부 289 기계설비 기술기준 해설 (별표 09 | {}
71bc976b-212a-434d-80c4-5fdb9045b79e | 국내_기계설비_기술기준_매뉴얼_최종본 | 1. 본문 해설 및 관련 법규 추가 설명 없음 2. 용어 내용 없음 (5) 덕트의 행거 및 지지 ① 장방형의 행거 및 지지는 KCS 31 20 20(3.2.3) 표 3.2-36 을 준용한 표 17 을 적용한다. ② 원형덕트의 행거와 지지는 KCS 31 20 20(3.2.3) 표 3.2-37 을 준용한 표 18 을 적용한다. 표 17 경질염화비닐판제 장방형 덕트의 행거 및 지지(KCS 31 20 20(3.2.3) 표 3.2-36) ¦ 덕트의 장변(mm) ¦ 행거 ¦ 행거 ¦ 행거 ¦ 지지대 ¦ 지지대 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 덕트의 장변(mm) ¦ 형강치수 (mm) ¦ 봉강(지름) (mm) ¦ 최대간격 (mm) ¦ 형강치수 (mm) ¦ 최대간격 (mm) ¦ ¦ 500 이하 ¦ 30x30x3 ¦ 9 ¦ 2 500 ¦ 30x30x3 ¦ 2 500 ¦ ¦ 500 초과 1 000 이하 ¦ 40x40x3 ¦ 9 ¦ 2 500 ¦ 40x40x3 ¦ 2 500 ¦ ¦ 1 000 초과 1 500 이하 ¦ 40x40x3 ¦ 9 ¦ 2 000 ¦ 40x40x3 ¦ 2 500 ¦ ¦ 1 500 초과 2 000 이하 ¦ 40x40x5 ¦ 9 ¦ 2 000 ¦ 40x40x5 ¦ 2 000 ¦ ¦ 2 000 초과 3 000 이하 ¦ 40x40x5 ¦ 9 ¦ 1 500 ¦ 40x40x5 ¦ 2 000 ¦ 표 18 경질염화비닐판제 원형 덕트의 행거 및 지지(KCS 31 20 20(3.2.3) 표 3.2-37) ¦ 호칭 치수 (mm) ¦ 행거 ¦ 행거 ¦ 행거 ¦ 지지대 ¦ 지지대 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 호칭 치수 (mm) ¦ 평강 (mm) ¦ 봉강 (mm) ¦ 최대간격 (mm) ¦ 형강치수 (mm) ¦ 최대간격 (mm) ¦ ¦ 300 이하 300 초과 500 이하 ¦ 30x3 40x3 ¦ 9x1 개소 9x2 개소 ¦ 4 000 4 000 ¦ 30x30x3 40x40x3 ¦ 4 000 4 000 ¦ 해 설 1. 본문 해설 및 관련 법규 추가 설명 없음 2. 용어 내용 없음 290 기계설비 기술기준 매뉴얼 | {}
cce95be7-256f-4230-a839-d621cb0bfc41 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.3 덕트 기기류 2.3.1 풍량조절댐퍼 (1) 풍량조절댐퍼는 수동식, 중력식, 전동식 등으로 설치하며 진동 및 소음이 없고, 개방 시 공기흐름 에 대한 저항이 적은 것으로 한다. (2) 분기덕트에는 풍량조절 댐퍼(VD)를 설치한다. 해 설 1. 본문 해설 및 관련 법규 추가 설명 없음 2. 용어 내용 없음 2.3 덕트 기기류(계속) 2.3.2 방화댐퍼 방화구획 관통부의 덕트에는 방화댐퍼를 설치한다. 해 설 1. 본문 해설 및 관련 법규 방화댐퍼는 「자동방화셔터, 방화문 및 방화댐퍼의 기준」을 만족하는 것으로 함 2. 용어 내용 없음 2.3 덕트 기기류(계속) 2.3.3 제어댐퍼 송풍기와 계통의 필요 정압을 확인하고 최대 정압과 최대 풍속에서 선정된 댐퍼가 운전에 지장이 없 는 구조로 댐퍼를 선정한다. 해 설 국토교통부 291 기계설비 기술기준 해설 (별표 09 | {}
e45a19f4-04bb-4ae7-9a1c-2b9436caf814 | 국내_기계설비_기술기준_매뉴얼_최종본 | 1. 본문 해설 및 관련 법규 V 추가 설명 없음 2. 용어 V 내용 없음 2.3 덕트 기기류(계속) 2.3.4 외기도입구 기계환기설비의 외기 도입구는 배기구와 가깝지 않도록 설계한다. (1) 강제 및 자연식 외기 도입구는 배기구, 도로, 골목, 주차장 및 하역장과 같이 유해 오염물질 발생 지점에서 수평방향으로 최소 3 m 이상 이격한다. 도로, 골목, 주차장 및 하역장과 같은 오염원으 로부터 7 m 상부에 외기도입구를 설치하면 수평이격거리는 3 m 이하로 유지할 수 있다. (2) 외기도입구가 유해물질 배출원의 3 m 내에 위치한 경우 외기도입구는 유해물질 배출원에서 최 소 1 m 이상 수직 이격한다. (3) 수해지역에 위치한 구조물의 외기도입구는 장비를 보호하기 위하여 예상수위상부에 설치한다. (4) 외부에 면하는 외기 도입구와 배기구는 교차오염을 방지하기 위하여, 1.5 m 이상의 이격거리를 확보하거나 이격거리가 짧은 경우, 외기도입구와 배기구의 방향이 90° 이상 변경된 위치에 설치 한다. 해 설 1. 본문 해설 및 관련 법규 V 2.3.4 의 기준은 공동주택 세대에는 적용하지 않음 V (1 항) 외기 도입구를 오염물질 발생지점에서 수평으로 3 m 이상 이격하여야 하나, 그 수직 높이 가 7 m 상부에 위치하는 경우에는 수평거리를 3 m 이하로 가능하도록 하며, 동일 계통상에 있지 않은 배기구에 대해서는 배출되는 공기에 성상(공기오염물질의 성분 및 농도 등)을 알 수 없기때 문에 (4)항보다 기준을 강화함 V (2 항) 외기 도입구가 수평거리 3 m 이상을 만족하는 경우에도 수직거리는 1 m 이상 이격을 해야 함 292 기계설비 기술기준 매뉴얼 | {}
7419c7d8-aac6-4925-a803-b8d0facfdcfd | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 ![image](/image/placeholder) 외기도입구 외기도입구 7 m 이상 유해 유해 오염물질 오염물질 최소 발생지점 발생지점 1 m 이상 3 m 이하 3 m 이상 예시 1 항 및 2 항 (3 항, 4 항) 추가 설명 없음 2. 용어 ¦ 용어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 이격거리 ¦ 루버나 그릴의 외곽 치수를 기준으로 한다.(해설서 주) ¦ 2.3 덕트 기기류(계속) 2.3.5 배기구 외기에 접한 배기구는 외부 풍압에 의해 배기능력이 저하되지 않는 구조를 갖추어야 하며 배기구의 위치는 토출배기에 의한 악영향을 미치거나 재순환 등을 방지하기 위하여 옥외 배기구의 위치, 토출 방향 등 건축 계획상의 고려와 함께 아래와 같이 최소이격거리를 유지한다. (1) 폭발성 또는 인화성의 증기, 악취가스 및 분진의 배기구 ① 건물경계선에서 9 m 이격 ② 인입 개구부에서 3 m 이격 ③ 외부벽체, 지붕에서 1.8 m 이격 ④ 배기방향에 직면한 가연성 벽체 및 외기도입구에서 9 m 이격 ⑤ 인접 지면 상부에서 3 m 이격 (2) 일반 건물 배기구 ① 건물 경계선에서 0.9 m ② 건물 출입문에서 0.9 m ③ 기계식 강제 외기도입구에서 3 m 해 설 1. 본문 해설 및 관련 법규 V 추가 설명 없음 국토교통부 293 기계설비 기술기준 해설 (별표 09 | {}
d3833f1a-95c3-4d3d-ad69-4074e9ae0ccd | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 용어 V 내용 없음 2.4 덕트와 송풍기의 연결 (1) 송풍기 흡입구에 연결하는 덕트는 송풍기 날개 지름의 4 배 이상 직선 덕트로 연결하거나, 날개 지 름 이상을 직선 덕트로 하고 엘보에 터닝 베인을 설치하여 정상류로 유입되게 한다. (2) 송풍기 출구 연결 덕트는 송풍기 출구 장변의 1.5 배 이상을 직선으로 유지시켜 송풍기 시스템 영 향을 최소화되도록 한다. (3) 대기로 토출하는 원심송풍기의 출구에는 송풍기 출구 장변의 1.5 배 이상의 직관 덕트를 설치해야 한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항 ~ 2 항) 해당 기준은 축류송풍기에 적용함 V (3 항) 해당 기준은 원심송풍기에 적용함 2. 용어 내용 없음 294 기계설비 기술기준 매뉴얼 | {}
349795d6-2887-4001-9ad7-ac9c86c6d9ca | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 3. 덕트설비 시공 3.1 일반사항 (1) 덕트는 구조적인 강도와 내구성이 있게 보강하여 설치해야 한다. (2) 플렉시블 덕트의 길이는 1.5 m 이하를 기본으로 하며 벽이나 바닥 또는 천장을 통과 해서는 안 된 다. 플렉시블 덕트는 처짐이나 굴곡이 발생하지 않도록 플렉시블 덕트에 폭 50 mm 의 받침대가 있는 행거를 설치하도록 한다. (3) 부식성 공기에 접하는 덕트는 부식을 방지하기 위해 PVC 나 스테인리스강 등 내식성 덕트로 해야 한다. (4) 기타 사항은 2.1 에 따른다. 해 설 1. 본문 해설 및 관련 법규 V 추가 설명 없음 2. 용어 내용 없음 3.2 덕트 3.2.1 아연도금 강판제 및 알루미늄 아연합금도금 강판제 덕트 아연도금 강판제 및 알루미늄 아연합금도금 강판제 덕트는 2.2.1 에 따른다. 3.2.2 스테인리스 강판제 덕트 스테인리스 강판제 덕트는 2.2.2 에 따른다. 3.2.3 경질염화비닐판제 덕트 경질염화비닐판제 덕트는 2.2.3 에 따른다. 해 설 1. 본문 해설 및 관련 법규 추가 설명 없음 2. 용어 내용 없음 --- 국토교통부 295 기계설비 기술기준 해설 (별표 09 | {}
43a964bf-414d-45a4-9b43-31b4a9dab1b4 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3.3 덕트 기기류 3.3.1 풍량조절댐퍼 (1) 기밀이 유지되고 조정이 쉽게 이루어질 수 있도록 설치한다. (2) 천정이나 샤프트 내에 댐퍼를 설치하는 경우에는 점검구를 설치하여 점검이 가능하도록 한다. (3) 댐퍼는 조작이 가능한 곳에 설치하며 분기 후에 설치할 경우에는 정상적인 기류가 흐를 수 있는 거리(덕트 폭의 2 배 이상)에 설치한다. 3.3.2 방화댐퍼 방화댐퍼의 설치는 KS F 2815(배연설비의 검사표준)에 따른다. 3.3.3 제어댐퍼 제어댐퍼는 2.3.3 에 따른다. 3.3.4 외기도입구 외기도입구는 2.3.4 에 따른다. 3.3.5 배기구 배기구는 2.3.5 에 따른다. 해 설 1. 본문 해설 및 관련 법규 V (3.3.1 1 항, 3 항) 추가 설명 없음 V (3.3.1 2 항) 이 기준 [별표 15] 2.4 (3) 참조 V (3.3.2 ~ 3.3.4) 추가 설명 없음 2. 용어 V 내용 없음 296 기계설비 기술기준 매뉴얼 | {}
fabf02c8-1e35-4efc-83ee-349505eb81e5 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 3.4 덕트와 송풍기의 연결 (1) 덕트와 접속하는 송풍기의 흡입측과 토출 측에는 플렉시블 이음을 설치한다. (2) 기타 덕트와 송풍기의 연결은 2.4 에 따른다. 해 설 1. 본문 해설 및 관련 법규 추가 설명 없음 2. 용어 내용 없음 3.5 공기조화 및 제연 덕트의 누기 시험 공기조화 및 제연덕트를 제작하여 설치한 후, 송풍기 가압방법으로 덕트 내부에 압력을 형성하여 기 밀 상태를 시험한다. (1) 시험장치는 송풍기, 풍량측정기구 및 압력측정기구로 구성하여 시험압력과 누기량을 측정한다. (2) 덕트 누기시험에 관한 내용은 한국설비기술협회 표준 SPS-KARSE B 0016 -178(공기조화용 덕 트누기 시험방법)에 따른다. 해 설 1. 본문 해설 및 관련 법규 V 추가 설명 없음 2. 용어 V 내용 없음 국토교통부 297 기계설비 기술기준 해설 (별표 09 | {}
b40251a8-6a03-4c5f-aeb7-3127c921b72a | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 10] 보온설비의 설계 및 시공 기준 1. 보온설비 일반사항 1.1 목적 이 기준은 건축물, 시설물 등에 설치되는 기계설비 배관 및 장비의 결로방지, 동파방지, 보온 및 보랭 등에 필요한 설계 및 시공 방법 등 세부 기술기준을 정함을 목적으로 한다. 해 설 이 기준의 목적은 「기계설비법」 제 14 조(기계설비 기술기준)과 같은 법 영 제 2 조 및 [별표 1]에 근 거하여, 건축물이나 시설물에 필요한 보온설비의 설계 및 시공 시 기계설비의 안전과 성능을 확 보하기 위하여 필요한 기술적 요건을 규정하기 위함 「기계설비법」 제 14 조(기계설비 기술기준) ① 국토교통부장관은 기계설비의 안전과 성능확보를 위하여 필요 한 기술기준(이하 "기술기준이라 한다)를 정하여 고시하여야 한다. 이를 변경하는 경우에도 또한 같다. 1.2 적용범위 이 기준은 건축물, 시설물 등에 설치되는 기기, 덕트 및 배관류의 결로방지, 동파방지, 보온 및 보랭 공사에 적용한다. 단, 특별한 명기가 없는 경우에 다음의 각 부분은 보온하지 않는다. 해 설 이 기준의 적용범위는 「기계설비법」 제 2 조제 1 호에 따른 건축물 등에 같은 법 영 제 2 조에 따라 대 통령령으로 정한 보온설비를 설치하는 경우 및 그와 관련된 부속설비들을 포함함 「기계설비법」 제 2 조(정의) 1. "기계설비"란 건축물, 시설물 등(이하 "건축물등"이라 한다)에 설치된 기계 · 기 구 · 배관 및 그 밖에 건축물등의 성능을 유지하기 위한 설비로서 대통령령으로 정하는 설비를 말한다. 「기계설비법 시행령」 제 2 조(기계설비의 범위) 「기계설비법」(이하 "법"이라 한다) 제 2 조제 1 호에서 "대통령령 으로 정하는 설비"란 별표 1 의 설비를 말한다. 「기계설비법 시행령」 [별표 1] 기계설비의 범위 7. 보온설비 : 건축물등에 설치된 기계 · 기구 · 배관 및 그 밖에 성능을 유지하기 위한 설비의 보온, 보냉, 결 로 및 동결 방지 등을 위하여 설치된 설비 298 기계설비 기술기준 매뉴얼 | {}
c1851565-2802-401f-9403-790b40069e6d | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 1.2 적용범위(계속) (1) 기기 ① 패키지형 및 유닛형의 공기조화기로 내부에 보온처리 된 것 ② 보랭처리 된 냉동기 ③ 회기(return air)용, 외기흡입(outdoor air)용, 배기(exhaust air)용으로 내부에 보온효과 가 있 는 흡음재를 내장한 챔버 내의 송풍기 ④ 오일탱크 및 가열하지 않는 오일 서비스 탱크 ⑤ 냉수, 냉 、 온수용 및 온수용 펌프 이외의 펌프 (1 항 1 호, 2 호) 제조사 기준에 따라 보온이 이루어진 기기는 추가 보온하지 않음. 단, 제조사의 기기 보온이 불충분한 경우에는 제조사에 추가 보온을 요청하거나 현장에서 추가 보온을 할 수 있음 예) 공조기 프레임 등에 결로가 발생하는 경우에는 제조사 또는 시공사에 의하여 프레임 등에 추 가 보온을 하여야 함 V (1 항 3 호) 충분한 단열 두께 이상의 흡음재가 설치되거나 단열이 이루어진 공조기 챔버 등의 내부 에 설치된 송풍기는 별도의 보온을 하지 않아도 됨 V (1 항 4 호 ~ 5 호) 추가 설명 없음 1.2 적용범위(계속) (2) 덕트 ① 공조되고 있는 실 및 그 천장 속의 회기 덕트 ② 덕트 보온과 동일 이상의 보온효과 가 있는 흡음재를 내장한 덕트 및 챔버 ③ 모든 면이 덕트 보온과 동일 이상의 보온효과 가 있는 소음기 및 소음엘보 ④ 환기(ventilation air)용 덕트(공기조화 공간을 지나는 외기 덕트는 결로 방지 보온한다) ⑤ 배기(exhaust air)용 덕트 ⑥ 제연설비의 급기 덕트 V (2 항 1 호 ~ 2 호, 4 호 ~ 6 호) 추가 설명 없음 V (2 항 3 호) 소음기와 소음 엘보는 일반적으로 2 면에는 흡음재가 부착되지만, 다른 2 면에는 흡음재 가 부착되지 않으며, 일부 구간에는 보온 두께가 충분하지 않으므로, 열 손실 및 결로 방지를 위하 여 보온을 해야 함 국토교통부 299 기계설비 기술기준 해설 (별표 10 | {}
a06621f8-b3a5-4042-920d-db1f3afe1ac0 | 국내_기계설비_기술기준_매뉴얼_최종본 | 1.2 적용범위(계속) (3) 배관, 밸브 및 플랜지 ① 방열기 주위 배관 ② 콘크리트 내에 매립되는 이중관, 배수관 및 가스배관 ③ 위생기구의 부속품에 해당되는 배관 ④ 급수관 및 배수관으로 동결심도 이하의 지중매설관 ⑤ 옥내 및 지하 피트 내에 급탕관의 신축이음 ⑥ 주방기기 및 순간온수기 주위 급수, 배수 및 급탕관 ⑦ 통기관(다만, 보온하는 배수관과 의 분기점에서 위쪽으로 100 mm 까지의 부분은 제외) ⑧ 오수처리시설 내의 설비의 배관 ⑨ 가열하지 않은 기름배관 ⑩ 냉동기 및 패키지형 공조기의 냉각수 배관 ⑪ 각종 탱크 류의 오버플로관 및 탱크 배수밸브 이하의 배수관 ⑫ 해당 배관의 단열 성능 조건 이상의 단열 효과 를 갖춘 급수, 급탕 이중관 배관 ⑬ 그 외 보온, 보랭, 결로, 동파 및 에너지 손실과 관련이 없는 배관 (3 항 1 호) 방열기에 연결되는 방열기 주위 배관은 난방에 도움을 줄 수 있으므로 보온을 하지 않아 도 무방하나, 화상을 입을 수 있거나 주변 건축 재료 또는 전기 재료에 손상을 줄 수 있는 경우에는 피해 방지를 위하여 보온해야 함 V (3 항 3 호) 위생기구의 부속품에 해당되는 배관이란 앵글 밸브에서 세면기로 연결되는 배관 등과 같이 실내에 노출되거나 전용 배관 상자 또는 배관 가리개 속에서 위생기구로 연결되는 배관으로 결로로 인한 피해가 발생하지 않는 배관을 말함 V (3 항 4 호) 지역별 동결 심도는 지역별 기상 자료를 기준으로 계산하여야 하나, 계산용 자료가 충분 하지 못한 경우에는 대한설비공학편람 1 권 기초편 제 12 장 기상 및 설계자료 3.12-4 표 5 난방계 산용 지역별 지중온도 참조할 수 있음 V (3 항 2 호, 5 호 ~ 13 호) 추가 설명 없음 300 기계설비 기술기준 매뉴얼 | {}
d3838368-f971-4cca-baac-1dd21f708326 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 표 5 난방계산용 지역별 지중온도 . 대한설비공학편람 1 권 기초편 제 12 장 기상 및 설계자료 ¦ 지명 ¦ 월평균 지표면온도 ¦ 월평균 지표면온도 ¦ 최대동결심도 a), cm ¦ 깊이에 따른 지중온도(1 월) ¦ 깊이에 따른 지중온도(1 월) ¦ 깊이에 따른 지중온도(1 월) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 지명 ¦ 최 저 ¦ 최 고 ¦ 최대동결심도 a), cm ¦ 0.5 m ¦ 1.5 m ¦ 3 m ¦ ¦ 서울 ¦ -2.3 ¦ 27.4 ¦ 67.0 ¦ 2.1 ¦ 8 ¦ 13.5 ¦ ¦ 인천 ¦ -1.2 ¦ 27.8 ¦ ¦ 3.2 ¦ 9.2 ¦ 13.9 ¦ ¦ 수원 ¦ -1.5 ¦ 27.1 ¦ 65.0(화성) ¦ 2.7 ¦ 8.3 ¦ 13.3 ¦ ¦ 춘천 ¦ -2.7 ¦ 27.5 ¦ 123.0 ¦ 1.5 ¦ 8.7 ¦ 14.1 ¦ ¦ 속초 ¦ -1 ¦ 26.4 ¦ 24.1(양양) ¦ 2 ¦ 6.6 ¦ 10.9 ¦ ¦ 강릉 ¦ 0.1 ¦ 26.8 ¦ 126.0 ¦ 4 ¦ 9.1 ¦ 13.8 ¦ ¦ 청주 ¦ -0.9 ¦ 27.7 ¦ 81.0(청원) ¦ 3 ¦ 7.7 ¦ 12.6 ¦ ¦ 추풍령 ¦ -1.1 ¦ 27.2 ¦ 84.0(김천) ¦ 2.7 ¦ ¦ ¦ ¦ 대전 ¦ -0.4 ¦ 28.2 ¦ 102.0(옥천) ¦ 2.5 ¦ 7.6 ¦ 13.7 ¦ ¦ 군산 ¦ 0.9 ¦ 28.8 ¦ 45.6 ¦ 4.7 ¦ 8.2 ¦ ¦ ¦ 전주 ¦ 0.8 ¦ 28.4 ¦ 47.8(완주) ¦ 4.1 ¦ 9 ¦ 13 ¦ ¦ 광주 ¦ 1.6 ¦ 28.2 ¦ 25.5(장성) ¦ 5.2 ¦ ¦ ¦ ¦ 제주 ¦ 5.1 ¦ 30 ¦ 33.4 ¦ 9.6 ¦ 13.7 ¦ 17.1 ¦ ¦ 대구 ¦ 0.5 ¦ 28.8 ¦ 86.0(구미) ¦ 4 ¦ 10.6 ¦ 13.1 ¦ ¦ 포항 ¦ 1.5 ¦ 29 ¦ 36.5 ¦ 6.1 ¦ 11.1 ¦ 15.2 ¦ ¦ 부산 ¦ 3.2 ¦ 29.3 ¦ ¦ 6.1 ¦ 12.5 ¦ 16.3 ¦ ¦ 울산 ¦ 2.4 ¦ 28.8 ¦ 39.0 ¦ 5.8 ¦ ¦ ¦ 주 1) 1981 년부터 2010 년의 30 년간 통계값이다. a) 최대동결심도는 11 년간(1991 ~ 2001)의 통계값이며, 통계값이 없는 지역은 주위 지역의 값을 표기하였다. ○ 1.3 타 규정과 의 관계 다음의 규정과 이 기준에서 정하는 내용이 상이한 경우에는 해당 규정을 따른다. (1) 「건축물의 설비기준 등에 관한 규칙」 (2) KCS 31 20 05 보온공사 표준시방서 해 설 V 추가설명 없음 기계설비 기술기준 해설 (별표 10) 국토교통부 301 | {}
398b76d6-0eab-4021-bf91-c225cb7a12bd | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 보온설비 설계 2.1 일반사항 (1) 보온두께는 보온재만의 두께를 말하며, 외장재 및 보조재의 두께는 포함하지 않는다. (2) 결로 및 동파방지가 동시에 필요할 경우의 보온두께는 두 가지 중에서 큰 쪽을 적용한다. (3) 보온과 보랭이 동시에 필요한 경우의 보온두께는 두 가지 중에서 큰 쪽을 적용한다. (4) 기기, 덕트 및 배관의 보온두께는 이 기준의 시공 장소 조건과 현저하게 다른 경우에는 KS F 2803(보온, 보랭공사의 시공기준)에 따른다. (5) 단열재는 단열성능, 화재안전성능에 대하여 국가공인시험기관의 시험성적서가 있는 것을 사용 한다. (6) 단열재는 사용 온도에 적합한 재료를 사용한다. 해당 단열재는 사용 온도에서 장시간 사용시에 형상, 강도 또는 물리적 특성이 변하지 않고 단열 성능이 유지되어야 한다. (7) 보랭의 경우, 보온재 표면 및 이음부 방습처리를 확실하게 하여 보온재 내로 습기 침투를 방지한다. (8) 표기된 보온두께는 최소 기준이며, 현장 여건 또는 제품 생산에 따라 그 이상 두께의 사용은 가능 하다. (9) 열전도율 0.030 W/m 、 K 이하의 보온재는 보온재 등급 "가" 항의 열전도율 0.034 W/m 、 K 를 기 준으로 해당 보온두께를 기준하여 열전도율에 비례한 보온두께를 사용할 수 있다. (10) 주위온도 30°C 이하는 건물 내에 위치한 기기, 배관, 덕트 등에 적용하며 주위온도 30°C 초과 는 옥외 설치 기기, 배관, 덕트 등에 적용한다. (11) 보온재의 시공두께는 시공 면에 침을 수직으로 찔러 그 두께를 검사하여 만족한다. 이 경우 두께 의 허용 오차는 3 mm 로 한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항 ~ 8 항, 10 항) 추가 설명 없음 V (9 항) 기준 적용 예시 사용하는 보온재의 열전도율이 0.026 W/m.K 인 경우, "가" 항의 기준 열 전도율이 0.034 W/m.K 이고 지 정된 보온 두께가 40 mm 이면, (0.026 / 0.034) X 40 mm = 30.6 mm 이상의 두께로 시공할 수 있음 V (11 항) 보온재의 시공두께의 허용 오차는 부분적으로 허용되는 오차를 말하며, 보온재 평균 두께는 규정된 시공 두께 이상으로 시공해야 함 2. 용어 V 내용 없음 302 기계설비 기술기준 매뉴얼 | {}
152147fd-fd80-4a5e-9872-56ec9544dda8 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.2 기기 2.2.1 보랭용 보랭용 보온재 등급별 보온두께는 KCS 31 20 05(2.3.2) 표 2.3-7, 표 2.3-8, 표 2.3-9 에 따른 표 1 을 적용한다. 표 1 보랭용 보온두께(KCS 31 20 05(2.3.2) 표 2.3-7, 표 2.3-8, 표 2.3-9) ¦ 보온재 등급 ¦ 보온재 열전도율의 범위 - W/m·K (KS L 9016 에 의한 20±5°C 시험조건에서 열전도율) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 보온재 등급 ¦ 보온재 열전도율의 범위 - W/m·K (KS L 9016 에 의한 20±5°C 시험조건에서 열전도율) ¦ 냉수펌프 등 1) ¦ 공기조화기 2) ¦ 송풍기 3) ¦ ¦ 가 ¦ 0.030 초과 0.034 이하 ¦ 40 ¦ 25 ¦ 25 ¦ ¦ 나 ¦ 0.035~0.040 ¦ 50 ¦ 25 ¦ 25 ¦ ¦ 다 ¦ 0.041~0.046 ¦ 60 ¦ 30 ¦ 30 ¦ ¦ 라 ¦ 0.047~0.051 ¦ 65 ¦ 35 ¦ 35 ¦ 주 1) 냉수, 냉·온수용 펌프, 탱크류 조건 : 내부온도 5~13°C, 주위온도 30°C 이하, 주위 상대습도 75% 미만 2) 공기조화기조건 : 내부온도 12~40°C, 외부온도 5~30°C, 주위 상대습도 75% 미만. 단, 옥외 설치 공기조 화기의 보온두께는 2 배 이상 3) 송풍기조건 : 내부온도 12~40°C, 외부온도 5~30°C, 주위 상대습도 75% 미만 해 설 1. 본문 해설 및 관련 법규 V 보온재 등급 가, 나, 다, 라는 건축물의 에너지절약 설계기준 별표 2 를 참조(이하 동일) 국토교통부 303 기계설비 기술기준 해설 (별표 10) | {}
cfb925c6-d3fa-4a8e-84bb-7a0da332e764 | 국내_기계설비_기술기준_매뉴얼_최종본 | 건축물의 에너지절약 설계기준 - 별표 2 ¦ 등급분류 ¦ 열전도율의 범위 시험조건에서 (KS L 9016 에 의한 20±5°C 열전도율) ¦ 열전도율의 범위 시험조건에서 (KS L 9016 에 의한 20±5°C 열전도율) ¦ 관련 표준 ¦ 단열재 종류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 등급분류 ¦ W/mK ¦ kcal/mh°C ¦ 관련 표준 ¦ 단열재 종류 ¦ ¦ 가 ¦ 0.034 이하 ¦ 0.029 이하 ¦ KS M 3808 ¦ - 압출법보온판 특호, 1 호, 2 호, 3 호 - 비드법보온판 2 종 1 호, 2 호, 3 호, 4 호 ¦ ¦ 가 ¦ 0.034 이하 ¦ 0.029 이하 ¦ KS M 3809 ¦ - 경질우레탄폼보온판 1 종 1 호, 2 호, 3 호 및 2 종 1 호, 2 호, 3 호 ¦ ¦ 가 ¦ 0.034 이하 ¦ 0.029 이하 ¦ KS L 9102 ¦ - 그라스울 보온판 48K, 64K, 80K, 96K, 120K ¦ ¦ 가 ¦ 0.034 이하 ¦ 0.029 이하 ¦ KS M ISO 4898 ¦ - 페놀 폼 I 종 A, II 종 A ¦ ¦ 가 ¦ 0.034 이하 ¦ 0.029 이하 ¦ KS M 3871-1 ¦ - 분무식 중밀도 폴리우레탄 폼 1 종(A, B), 2 종(A, B) ¦ ¦ 가 ¦ 0.034 이하 ¦ 0.029 이하 ¦ KS F 5660 ¦ - 폴리에스테르 흡음 단열재 1 급 ¦ ¦ 가 ¦ 0.034 이하 ¦ 0.029 이하 ¦ 기타 단열재로서 ¦ 열전도율이 0.034 W/mK (0.029 kcal/mh°C)이하인 경우 ¦ ¦ 나 ¦ 0.035 ~0.040 ¦ 0.030 ~0.034 ¦ KS M 3808 ¦ - 비드법보온판 1 종 1 호, 2 호, 3 호 ¦ ¦ 나 ¦ 0.035 ~0.040 ¦ 0.030 ~0.034 ¦ KS L 9102 ¦ - 미네랄울 보온판 1 호, 2 호, 3 호 - 그라스울 보온판 24K, 32K, 40K ¦ ¦ 나 ¦ 0.035 ~0.040 ¦ 0.030 ~0.034 ¦ KS M ISO 4898 ¦ - 페놀 폼 I 종 B, II 종 B, III 종 A ¦ ¦ 나 ¦ 0.035 ~0.040 ¦ 0.030 ~0.034 ¦ KS M 3871-1 ¦ - 분무식 중밀도 폴리우레탄 폼 1 종(C) ¦ ¦ 나 ¦ 0.035 ~0.040 ¦ 0.030 ~0.034 ¦ KS F 5660 ¦ - 폴리에스테르 흡음 단열재 2 급 ¦ ¦ 나 ¦ 0.035 ~0.040 ¦ 0.030 ~0.034 ¦ 기타 단열재로서 열전도율이 0.035~0.040 W/mK (0.030~ 0.034 kcal/mh°C)이하인 경우 ¦ 기타 단열재로서 열전도율이 0.035~0.040 W/mK (0.030~ 0.034 kcal/mh°C)이하인 경우 ¦ ¦ 다 ¦ 0.041 ~0.046 ¦ 0.035 ~0.039 ¦ KS M 3808 ¦ - 비드법보온판 1 종 4 호 ¦ ¦ 다 ¦ 0.041 ~0.046 ¦ 0.035 ~0.039 ¦ KS F 5660 ¦ - 폴리에스테르 흡음 단열재 3 급 ¦ ¦ 다 ¦ 0.041 ~0.046 ¦ 0.035 ~0.039 ¦ 기타 단열재로서 열전도율이 0.041~0.046 W/mK (0.035~0.039 kcal/mh°C)이하 인 경우 ¦ 기타 단열재로서 열전도율이 0.041~0.046 W/mK (0.035~0.039 kcal/mh°C)이하 인 경우 ¦ ¦ 라 ¦ 0.047 ~0.051 ¦ 0.040 ~0.044 ¦ 기타 단열재로서 열전도율이 0.047~0.051 W/mK (0.040~0.044 kcal/mh°C)이하 인 경우 ¦ 기타 단열재로서 열전도율이 0.047~0.051 W/mK (0.040~0.044 kcal/mh°C)이하 인 경우 ¦ V 열전도율 0.035~0.040 은 0.034 초과 0.040 이하, 0.041~0.046 은 0.040 초과 0.046 이하, 0.047~0.051 은 0.046 초과 0.051 이하를 의미한다. (이하 동일) 2. 용어 V 내용 없음 304 기계설비 기술기준 매뉴얼 | {}
fb12ac21-cd45-400c-b98c-4cd936b3b94d | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.2.2 보온용 보온용 보온재 등급별 보온두께는 KCS 31 20 05(2.3.2) 표 2.3-3, 표 2.3-4, 표 2.3-5, 표 2.3-6 에 따른 표 2 를 적용한다. 표 2 보온용 보온두께(KCS 31 20 05(2.3.2) 표 2.3-3, 표 2.3-4, 표 2.3-5, 표 2.3-6) ¦ 보온재 등급 ¦ 보온재 열전도율의 범위 - W/m·K (KS L 9016 에 의한 23±2°C 시험조건에서 열전도율) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 보온재 등급 ¦ 보온재 열전도율의 범위 - W/m·K (KS L 9016 에 의한 23±2°C 시험조건에서 열전도율) ¦ 보일러 등 1) ¦ 열교환기 등 2) ¦ 저압 증기헤더 등 3) ¦ 고압 증기헤더 등 4) ¦ ¦ 가 ¦ 0.030 초과 0.034 이하 ¦ 70 ¦ 40 ¦ 50 ¦ 50 ¦ ¦ 나 ¦ 0.035~0.040 ¦ 80 ¦ 50 ¦ 60 ¦ 60 ¦ ¦ 다 ¦ 0.041~0.046 ¦ 90 ¦ 60 ¦ 70 ¦ 70 ¦ ¦ 라 ¦ 0.047~0.051 ¦ 100 ¦ 65 ¦ 75 ¦ 75 ¦ 주 1) 보일러 및 연도조건 : 내부온도 300°C 이하, 주위온도 30°C 이하, 단, 단열 성능이 있는 이중 연도는 제외 2) 열교환기, 온수 펌프, 저탕탱크 및 팽창탱크조건 : 내부온도 100°C 이하, 주위온도 30°C 이하. 3) 저압증기헤더, 열교환기조건 : 내부온도 100°C 초과 150°C 이하, 주위 온도 30°C 이하 4) 고압증기 헤더, 열교환기조건 : 내부온도 150°C 초과 220°C 이하, 주위온도 30°C 이하 해 설 1. 본문 해설 및 관련 법규 추가 설명 없음 2. 용어 내용 없음 2.2.3 결로 방지용 급수탱크류의 결로방지를 위한 보온재 등급별 보온두께는 KCS 31 20 05(2.3.1) 표 2.3-1, 표 2.3-2 에 따른 표 3 을 적용한다. 표 3 결로 방지용 보온두께(KCS 31 20 05(2.3.1) 표 2.3-1, 표 2.3-2) ¦ 보온재 등급 ¦ 보온재 열전도율의 범위 - W/m·K (KS L 9016 에 의한 23±2°C 시험조건에서 열전도율) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 보온재 등급 ¦ 보온재 열전도율의 범위 - W/m·K (KS L 9016 에 의한 23±2°C 시험조건에서 열전도율) ¦ 경우 1) 일반적인 ¦ 다습한 장소의 경우 2) ¦ ¦ 가 ¦ 0.030 초과 0.034 이하 ¦ 20 ¦ 40 ¦ ¦ 나 ¦ 0.035~0.040 ¦ 25 ¦ 50 ¦ ¦ 다 ¦ 0.041~0.046 ¦ 30 ¦ 60 ¦ ¦ 라 ¦ 0.047~0.051 ¦ 30 ¦ 65 ¦ 주 1) 일반조건 : 탱크 내부 온도 15°C 이하, 주위온도 30°C 이하, 주위 상대습도 75% 미만 2) 다습조건 : 탱크 내부 온도 15°C 이하, 주위온도 30°C 초과 또는 주위 상대습도 75% 이상 국토교통부 305 기계설비 기술기준 해설 (별표 10) | {}
f46d7c65-540d-4259-b6bb-bdaa66a60a58 | 국내_기계설비_기술기준_매뉴얼_최종본 | 해 설 1. 본문 해설 및 관련 법규 이 기준 2.3 배관과 관련한 배관단열 설계 프로그램을 대한기계설비산업연구원 홈페이지 (http://www.krimfi.re.kr/)에서 다운 받아 설계할 수 있으며, 이 경우 배관의 내외부 조건 및 단열 두 께에 따른 열출입량을 계산할 수 있음 ![image](/image/placeholder) HOME SITEMAP ENGLISH 검색어로 입력하세요 검색 KRIMFI 연구활동 발간자료 산업동향 BIM 소개 알림마당 연구원소개 � KRIMFI PIE KMBIM 소개 체험 및 구매신청 대한기계설비산업연구원 건축기계설비설계용 BM TOOL 기계설비산업 기술발전을 위한 창조적 아이디어를 KMBIM 기계설비 시공용 삽드로잉을 위한 제공하여 산업 혁신의 창조적 패러다임을 제시하는 REVIT 기반의 PLUG 취 프로그램 Innovation Center 입니다. 바람이기 대한가게설비간실협회 KRIMFI 盟 연구보고서 KRIMFI 의 연구보고서 정보입니다. ん 산업동향 기계설비산업의 최신동협 자료입니다. 연구 보고서 MORE ★ 전체 기술동향 정책동향 경기동향 MORE '21 년 3/4 분기 실적 및 '21 년 4/4 분기 전망 2021-10-01 보충시장 어디에 OF 어림원 다른 [설문조사] 해외플랜트현장의 물공정거래 및 부당한 조치에 대한 가이 2021-08-02 경쟁력 25 일만 경영역강화방안 "보험법 「법인보험 21 년 2/4 분기 실적 및 21 년 3/4 분기 전달 2021-07-02 '21 년 1/4 분기 실적 및 '21 년 2/4 분기 전망 결과 2021-04-05 '20 년 4/4 분기 실적 및 21 년 1/4 분기 전망 결과 2021-01-05 '20 년 3/4 분기 실적 및 '20 년 4/4 분기 전망 결과 2020-10-05 20 년 2/4 분기 실적 및 20 년 3/4 분기 전망 결과 2020-06- 30 8 환자에 따른 기계 선비거셨어요 피해 ⑥ 아로사항 주사 전기 대한기계설비산업연구원 홈페이지 오른쪽 상단 프로그램 및 관련 매뉴얼 다운로드 PI 는 파일(F) 프로젝트(P) 옵션(O) 보고서 동결시간 예측 도움말(H) 배관 냉방 강관 배관지름 15 ⑥ 수평/수직 조건 조건 1 ↓ 수평 수직 �g100 층 동결시간 계산 구분 조건 결과 추가 열흐름방향 수평/ 0 수직 프로젝트 배관 종류 0.2 m/s 배관 내 열량 0 Cal 수평 호칭경 V I 수직 배관 열손실 0 Cal/h m 배관 내부온도 60.0 : °C 0 h 0 °C 주변온도 0.0 : °C 물의 무게 0 g 상대습도 60 : % 물의 비열 1.0 Cal/g K 주변 기류속도 0.2 : m/s 60 C 온도차 60 k 단열두께(개 단열재 열전도율 0.034 : W/m-K 정준 ) 단열재 두께 40 mm 시간 0 h 유효복사계수 0.70 에너지 절감률 0% 프로그램 화면 2. 용어 내용 없음 306 기계설비 기술기준 매뉴얼 | {}
f2fa9c82-4516-4d49-ad59-8a7c8bde8acb | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.3 배관 2.3.1 냉수관 및 냉·온수관 (1) 일반적인 냉수관, 냉·온수관, 밸브의 보온재 등급별 보온두께는 KCS 31 20 05(2.5) 표 2.5-6, 표 2.5-7 에 따른 표 4 를 적용한다. (2) 다습한 장소의 냉수관, 냉·온수관, 밸브의 보온재 등급별 보온두께는 KCS 31 20 05(2.5) 표 2.5-8, 표 2.5-9 에 따른 표 5 를 적용한다. 표 4 냉수관 등의 보온두께(일반적인 경우)(KCS 31 20 05(2.5) 표 2.5-6, 표 2.5-7) ¦ 보온재 등급 ¦ 보온재 열전도율의 범위 - W/m·K ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 보온재 등급 ¦ 보온재 열전도율의 범위 - W/m·K ¦ 저온 1) ¦ 저온 1) ¦ 일반 2) ¦ 일반 2) ¦ ¦ 보온재 등급 ¦ 보온재 열전도율의 범위 - W/m·K ¦ DN15~25 ¦ DN32 이상 ¦ DN15~25 ¦ DN32 이상 ¦ ¦ 가 ¦ 0.030 초과 0.034 이하 ¦ 25 ¦ 40 ¦ 20 ¦ 35 ¦ ¦ 나 ¦ 0.035~0.040 ¦ 30 ¦ 45 ¦ 25 ¦ 40 ¦ ¦ 다 ¦ 0.041~0.046 ¦ 35 ¦ 50 ¦ 30 ¦ 45 ¦ ¦ 라 ¦ 0.047~0.051 ¦ 40 ¦ 55 ¦ 35 ¦ 50 ¦ 주 1) 저온조건: 관내 수온 4°C 이상 6°C 미만, 주위온도 30°C 이하, 상대습도 75% 미만 2) 일반조건: 관내 수온 6~15°C, 주위온도 30°C 이하, 상대습도 75% 미만 3) 4°C 미만의 냉수는 특기 시방에 따름 표 5 냉수관 등의 보온두께(다습한 장소의 경우)(KCS 31 20 05(2.5) 표 2.5-8, 표 2.5-9) ¦ 보온재 등급 ¦ 보온재 열전도율의 범위 - W/m·K ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 보온재 등급 ¦ 보온재 열전도율의 범위 - W/m·K ¦ 다습저온 1) ¦ 다습저온 1) ¦ 다습저온 1) ¦ 다습일반 2) ¦ 다습일반 2) ¦ 다습일반 2) ¦ ¦ 보온재 등급 ¦ 보온재 열전도율의 범위 - W/m·K ¦ DN15~32 ¦ DN40~100 ¦ DN125 이상 ¦ DN15~32 ¦ DN40~100 ¦ DN125 이상 ¦ ¦ 가 ¦ 0.030 초과 0.034 이하 ¦ 35 ¦ 45 ¦ 65 ¦ 35 ¦ 45 ¦ 65 ¦ ¦ 나 ¦ 0.035~0.040 ¦ 40 ¦ 50 ¦ 75 ¦ 40 ¦ 50 ¦ 75 ¦ ¦ 다 ¦ 0.041~0.046 ¦ 45 ¦ 60 ¦ 90 ¦ 45 ¦ 60 ¦ 90 ¦ ¦ 라 ¦ 0.047~0.051 ¦ 50 ¦ 65 ¦ 100 ¦ 50 ¦ 65 ¦ 100 ¦ 주 1) 다습저온조건: 관내 수온 4°C 이상 6°C 미만, 주위온도 30°C 초과 또는 상대습도 75% 이상 2) 다습일반조건: 관내 수온 6~15°C, 주위온도 30°C 초과 또는 상대습도 75% 이상 3) 4°C 미만의 냉수는 특기 시방에 따름 해 설 1. 본문 해설 및 관련 법규 (표 4, 표 5 주 3) 4°C 미만의 냉수는 용도에 따라 적용에 차이가 있으므로, 해당 제품의 용도 및 특 성에 맞도록 브라인 및 냉수 등의 열 손실 및 결로 방지를 위하여 작성한 특기 시방에 따름 2. 용어 내용 없음 국토교통부 307 기계설비 기술기준 해설 (별표 10) | {}
47f760bb-9845-4832-9008-734a7eed6f89 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2.3.2 공조용 냉매관 공조용 냉매관의 보온두께는 KCS 31 20 05(2.5) 표 2.5-10 에 따른 표 6 을 적용한다. 표 6 냉매관의 보온두께(KCS 31 20 05(2.5) 표 2.5-10) ¦ 종별 ¦ 종별 ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 종별 ¦ 종별 ¦ 냉매관 지름(mm) ¦ 냉매관 지름(mm) ¦ 냉매관 지름(mm) ¦ 냉매관 지름(mm) ¦ 냉매관 지름(mm) ¦ 냉매관 지름(mm) ¦ 냉매관 지름(mm) ¦ 냉매관 지름(mm) ¦ 냉매관 지름(mm) ¦ 냉매관 지름(mm) ¦ 냉매관 지름(mm) ¦ ¦ 종별 ¦ 종별 ¦ 6.35 ¦ 9.52 ¦ 12.7 ¦ 15.88 ¦ 19.05 ¦ 22.22 ¦ 25.4 ¦ 28.58 ¦ 31.8 ¦ 34.92 ¦ 38.1 ¦ ¦ 압축기 옥외 열펌프 ¦ 가스관 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ ¦ 압축기 옥외 열펌프 ¦ 액관 ¦ 7.5 ¦ 7.5 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ ¦ 압축기 옥외 냉방전 용 ¦ 가스관 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ ¦ 압축기 옥외 냉방전 용 ¦ 액관 ¦ 7.5 ¦ 7.5 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ ¦ 압축기 옥내 열펌프 ¦ 가스관 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ ¦ 압축기 옥내 열펌프 ¦ 액관 ¦ 7.5 ¦ 7.5 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ ¦ 압축기 옥내 냉방전 용 ¦ 가스관 ¦ 7.5 ¦ 7.5 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ ¦ 압축기 옥내 냉방전 용 ¦ 액관 ¦ 7.5 ¦ 7.5 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 10 ¦ 주 1) 냉매관 지름 40mm 이상 및 공조용 이외의 냉매관의 보온재 및 보온두께는 공사시방서에 따른다. 2) 냉매 온도에 의한 손상 또는 변형이 발생하지 않는 보온재를 사용한다. 해 설 1. 본문 해설 및 관련 법규 공동주택 냉매배관 매립 등의 시공문제로 보온두께를 만족하기 어려운 경우, 기계설비감리업무수 행자의 승인을 받는다면 예외로 함 2. 용어 V 내용 없음 308 기계설비 기술기준 매뉴얼 | {}
6a2fe9a0-9985-43b8-8c50-66092a43e15a | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.3.3 급수관 및 배수관 급수관 및 배수관 등의 결로 방지를 위한 보온재 등급별 보온두께는 KCS 31 20 05(2.5) 표 2.5-1, 표 2.5-2 에 따른 표 7 을 적용한다. 표 7 급수관 등의 보온두께(KCS 31 20 05(2.5) 표 2.5-1, 표 2.5-2) ¦ 보온재 등급 ¦ 보온재 열전도율의 범위 - W/m·K (KS L 9016 에 의한 23±2°C°C 시험조건에서 열전도율) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 보온재 등급 ¦ 보온재 열전도율의 범위 - W/m·K (KS L 9016 에 의한 23±2°C°C 시험조건에서 열전도율) ¦ 일반 1) ¦ 일반 1) ¦ 다습 2) ¦ 다습 2) ¦ 다습 2) ¦ ¦ 보온재 등급 ¦ 보온재 열전도율의 범위 - W/m·K (KS L 9016 에 의한 23±2°C°C 시험조건에서 열전도율) ¦ DN15~80 ¦ DN100 이상 ¦ DN15~25 ¦ DN32~300 ¦ DN350 이상 ¦ ¦ 가 ¦ 0.030 초과 0.034 이하 ¦ 20 ¦ 35 ¦ 20 ¦ 35 ¦ 45 ¦ ¦ 나 ¦ 0.035~0.040 ¦ 25 ¦ 40 ¦ 25 ¦ 40 ¦ 50 ¦ ¦ 다 ¦ 0.041~0.046 ¦ 30 ¦ 45 ¦ 30 ¦ 45 ¦ 60 ¦ ¦ 라 ¦ 0.047~0.051 ¦ 35 ¦ 50 ¦ 35 ¦ 50 ¦ 65 ¦ 주 1) 일반조건 : 관내 수온 15°C 이하, 주위온도 30°C 이하, 상대습도 75% 미만 2) 다습조건 : 관내 수온 15°C 이하, 주위온도 30°C 초과 또는 상대습도 75% 이상 해 설 1. 본문 해설 및 관련 법규 공동주택 등에 설치하는 개별 가스보일러, 세대 급탕 열교환기 등의 기기 주위 배관은 해당 제조 사에서 제안하는 배관 설치 간격에 따라 보온두께 적용 가능함. 단, 외기에 직접 노출 되거나 동 파가 우려되는 경우 발열선, 배관커버 등의 조치를 해야 함 2. 용어 V 내용 없음 기계설비 기술기준 해설 (별표 10) 국토교통부 309 | {}
7ba3f014-7c43-4f62-b7d6-6a6792cc1106 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2.3.4 급탕관, 온수관 및 증기관 급탕관, 온수관, 증기관의 보온재 등급별 보온두께는 KCS 31 20 05(2.5) 표 2.5-3, 표 2.5-4, 표 2.5-5 에 따른 표 8 을 적용한다. 표 8 온수관 등의 보온두께(일반의 경우)(KCS 31 20 05(2.5) 표 2.5-3, 표 2.5-4, 표 2.5-5) ¦ 보 온 재 등 급 ¦ 보온재 열전도율의 범위 - W/m-K (KS L 9016 에 의한 23±2°C°C 시험조건에서 열전도율) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 보 온 재 등 급 ¦ 보온재 열전도율의 범위 - W/m-K (KS L 9016 에 의한 23±2°C°C 시험조건에서 열전도율) ¦ 일반 1) ¦ 일반 1) ¦ 일반 1) ¦ 중온 2) ¦ 중온 2) ¦ 중온 2) ¦ 고온 3) ¦ 고온 3) ¦ 고온 3) ¦ ¦ 보 온 재 등 급 ¦ 보온재 열전도율의 범위 - W/m-K (KS L 9016 에 의한 23±2°C°C 시험조건에서 열전도율) ¦ DN 15~40 ¦ DN 50~125 ¦ DN 150 이상 ¦ DN 15~40 ¦ DN 50~125 ¦ DN 150 이상 ¦ DN 15~40 ¦ DN 50~125 ¦ DN 150 이상 ¦ ¦ 가 ¦ 0.030 초과 0.034 이하 ¦ 20 ¦ 35 ¦ 45 ¦ 35 ¦ 45 ¦ 70 ¦ - ¦ ¦ - ¦ ¦ 나 ¦ 0.035~0.040 ¦ 25 ¦ 40 ¦ 50 ¦ 40 ¦ 50 ¦ 80 ¦ - ¦ ¦ - ¦ ¦ 다 ¦ 0.041~0.046 ¦ 30 ¦ 45 ¦ 60 ¦ 45 ¦ 60 ¦ 90 ¦ - ¦ ¦ - ¦ ¦ 라 ¦ 0.047~0.051 ¦ 35 ¦ 50 ¦ 65 ¦ 50 ¦ 65 ¦ 100 ¦ - ¦ ¦ - ¦ 주 1) 일반 조건: 관내 수온 90°C 이하, 주위온도 30°C 이하 2) 중온 조건: 관내 수온 91~120°C, 주위온도 30°C 이하 3) 고온 조건: 관내 수온 121~220°C, 주위온도 30°C 이하 해 설 1. 본문 해설 및 관련 법규 공동주택 등에 설치하는 개별 가스보일러, 세대 급탕 열교환기 등의 기기 주위 배관은 해당 제조 사에서 제안하는 배관 설치 간격에 따라 보온두께 적용 가능함. 단, 외기에 직접 노출 되거나 동 파가 우려되는 경우 발열선, 배관커버 등의 조치를 해야 함 2. 용어 V 내용 없음 2.3.5 급수관 및 수도계량기보호함의 설치기준 외기에 노출된 배관 또는 그밖에 동파가 우려되는 배관 및 수도계량기 보호함의 설치기준은 「건축물 의 설비기준 등에 관한 규칙」제 18 조제 3 호 및 별표 3 의 2 에 따른다. 해 설 1. 본문 해설 및 관련 법규 「건축물의 설비기준 등에 관한 규칙」 310 기계설비 기술기준 매뉴얼 | {}
2fe298c8-f521-452e-ad9f-f279a6102374 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 「건축물의 설비기준 등에 관한 규칙」 제 18 조(먹는물용 배관설비) 영 제 87 조제 2 항에 따라 건축물에 설치하는 먹는물용 배관설비의 설치 및 구조 는 다음 각 호의 기준에 적합해야 한다. 3. 급수관 및 수도계량기는 얼어서 깨지지 아니하도록 별표 3 의 2 의 규정에 의한 기준에 적합하게 설치할 것 「건축물의 설비기준 등에 관한 규칙」 [별표 3 의 2] 급수관 및 수도계량기보호함의 설치기준(제 18 조제 3 호관 련) 1. 급수관의 단열재 두께(단위 : mm) ¦ DN 설치장소 ¦ DN 설치장소 ¦ 20 미만 ¦ 20 이상 ~ 50 미만 ¦ 50 이상 ~ 70 미만 ¦ 70 이상 ~ 100 미만 ¦ 100 이상 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ·외기에 노출된 배관 ·옥상 등 그밖에 동파가 우려되는 건축물의 부위 ¦ 설계용 외기온도(°C) ¦ 20 미만 ¦ 20 이상 ~ 50 미만 ¦ 50 이상 ~ 70 미만 ¦ 70 이상 ~ 100 미만 ¦ 100 이상 ¦ ¦ ·외기에 노출된 배관 ·옥상 등 그밖에 동파가 우려되는 건축물의 부위 ¦ -10 미만 ¦ 200 (50) ¦ 50 (25) ¦ 25 (25) ¦ 25 (25) ¦ 25 (25) ¦ ¦ ·외기에 노출된 배관 ·옥상 등 그밖에 동파가 우려되는 건축물의 부위 ¦ -5 미만 ~ -10 ¦ 100 (50) ¦ 40 (25) ¦ 25 (25) ¦ 25 (25) ¦ 25 (25) ¦ ¦ ·외기에 노출된 배관 ·옥상 등 그밖에 동파가 우려되는 건축물의 부위 ¦ 0 미만 ~ -5 ¦ 40 (25) ¦ 25 (25) ¦ 25 (25) ¦ 25 (25) ¦ 25 (25) ¦ ¦ ·외기에 노출된 배관 ·옥상 등 그밖에 동파가 우려되는 건축물의 부위 ¦ 0 이상 유지 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ 20 ¦ 1) ( )은 기온강하에 따라 자동으로 작동하는 전기 발열선이 설치하는 경우 단열재의 두께를 완화할 수 있는 기준 2) 단열재의 열전도율은 0.04 kcal/m2·h·°C 이하인 것으로 한국산업표준제품을 사용할 것 3) 설계용 외기온도:법 제 59 조제 2 항의 규정에 의한 에너지 절약설계기준에 따를 것 2. 수도계량기보호함(난방공간내에 설치하는 것을 제외한다) 가. 수도계량기와 지수밸브 및 역지밸브를 지중 혹은 공동주택의 벽면 내부에 설치하는 경우에는 콘크리트 또는 합성수지제 등의 보호함에 넣어 보호할 것 나. 보호함 내 옆면 및 뒷면과 전면판에 각각 단열재를 부착할 것(단열재는 밀도가 높고 열전도율이 낮은 것으로 한국산업표준제품을 사용할 것) 다. 보호함의 배관입출구는 단열재 등으로 밀폐하여 냉기의 침입이 없도록 할 것 라. 보온용 단열재와 계량기 사이 공간을 유리섬유 등 보온재로 채울 것 마. 보호통과 벽체사이틈을 밀봉재 등으로 채워 냉기의 침투를 방지할 것 2. 용어 V 내용 없음 기계설비 기술기준 해설 (별표 10) 국토교통부 311 | {}
eef493e5-90c8-4f27-be0d-23a436f40ac8 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2.4 덕트 2.4.1 장방형 및 원형덕트 장방형 및 원형덕트(노출, 은폐)의 보온재 등급별 보온두께는 KCS 31 20 05(2.4) 표 2.4-1, 표 2.4-2, 표 2.4-3, 표 2.4-4 에 따른 표 9 를 적용한다. 표 9 장방형 및 원형(노출, 은폐) 덕트 보온두께(KCS 31 20 05(2.4) 표 2.4-1, 표 2.4-2, 표 2.4-3, 표 2.4-4) ¦ 보온재 등급 ¦ 보온재 열전도율의 범위 一 W/m·K (KS L 9016 에 의한 23±2°C 시험조건에서 열전도율) ¦ 보온두께(mm) ¦ 보온두께(mm) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 보온재 등급 ¦ 보온재 열전도율의 범위 一 W/m·K (KS L 9016 에 의한 23±2°C 시험조건에서 열전도율) ¦ 장방형 1) ¦ 원형 2) ¦ ¦ 가 ¦ 0.030 초과 0.034 이하 ¦ 20 ¦ 20 ¦ ¦ 나 ¦ 0.035~0.040 ¦ 25 ¦ 25 ¦ ¦ 다 ¦ 0.041~0.046 ¦ 30 ¦ 30 ¦ ¦ 라 ¦ 0.047~0.051 ¦ 35 ¦ 35 ¦ 주 1) 장방형 덕트(노출, 은폐) 조건: 내부온도 10~40°C, 외부온도 5~30°C, 외부 상대습도 75% 미만 2) 원형 덕트(노출, 은폐) 덕트 조건: 내부온도 10~40°C, 외부온도 5~30°C, 주위 상대습도 75% 미만 해 설 1. 본문 해설 및 관련 법규 V 추가 설명 없음 2. 용어 V 내용 없음 312 기계설비 기술기준 매뉴얼 | {}
dcb0eff1-0ac2-4f12-919d-17e96d94e39e | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.4.2 제연덕트 (1) 제연덕트의 보온재 등급별 보온두께는 KCS 31 20 05(2.4) 표 2.4-5 에 따른 표 10 을 적용한다. (2) 제연덕트 보온재 화재안전 난연성능은 표 11 에 따른다. (3) 제연덕트 보온재 설치부위는 관련 화재안전기준에 따른다. 표 10 제연덕트 보온두께(KCS 31 20 05(2.4) 표 2.4-5) ¦ 보온재 등급 ¦ 보온재 열전도율의 범위 一 W/m-K (KS L 9016 에 의한 23±2°C 시험조건에서 열전도율) ¦ 보온두께(mm) ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 보온재 등급 ¦ 보온재 열전도율의 범위 一 W/m-K (KS L 9016 에 의한 23±2°C 시험조건에서 열전도율) ¦ 제연⑪ ¦ ¦ 가 ¦ 0.030 초과 0.034 이하 ¦ 25 ¦ ¦ 나 ¦ 0.035~0.040 ¦ 25 ¦ ¦ 다 ¦ 0.041~0.046 ¦ 25 ¦ ¦ 라 ¦ 0.047~0.051 ¦ 25 ¦ 주 1) 제연 덕트 조건: 내부온도 10~40°C, 외부온도 5~30°C, 주위 상대습도 75% 미만 표 11 제연덕트 보온재의 화재안전 난연성능 ¦ 제연설비 ¦ 기준 ¦ 등급 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ NFSC 501 ¦ 거실 제연으로 내열성(석면재료는 제외한다)의 단열재로 유효한 것으로 「건축법」에 따른 난연재료 성능 이상으로 단열처리한다. ¦ 불연재료, 준불연재료, 난연재료 ¦ ¦ NFSC 501A ¦ 특별피난계단의 계단실 및 부속실 제연설비로 불연재료(석면재료 를 제외한다)의 단열재로 유효한 단열처리 한다. ¦ 불연재료 ¦ 해 설 1. 본문 해설 및 관련 법규 추가 설명 없음 2. 용어 내용 없음 2.4.3 주방후드 배기덕트 공동주택의 결로가 우려되는 주방후드의 직배기 덕트는 보온을 해야 한다. 해 설 1. 본문 해설 및 관련 법규 국토교통부 313 기계설비 기술기준 해설 (별표 10) | {}
23532ed9-e26f-4a77-b66c-d578e026cf51 | 국내_기계설비_기술기준_매뉴얼_최종본 | V (2.4.3) 공동주택의 결로가 우려되는 주방후드의 직배기 덕트는 2.4.1 의 표 9 에 따라 보온함 V (2.4.3) 시공 중 설계변경 등의 불가피한 이유로 인한 주방 직배기덕트의 보온두께 확보가 어려운 경우, 기계설비감리업무수행자의 승인을 득한 경우에 한하여 예외로 할 수 있으며, 단, 이 경우에 도 최소 보온두께는 10 mm 이상으로 함 2. 용어 V 내용 없음 ![image](/image/placeholder) 2.5 동파방지 발열선 2.5.1 동파방지 노출형 급수배관 등 동파가 우려되는 배관에는 동결방지밸브를 설치하거나 발열선을 보온재와 배관 사이에 설치한다. 2.5.2 구조 (1) 발열선은 연속병렬 저항체로서 온도변화에 따라 자동으로 발열량이 조절되는 기능을 갖는 자율 온도 제어형 정온전선(self temperature regulating heating cable)이어야 한다. (2) 발열선은 케이블 길이를 임의 로 절단 피복층을 쉽게 벗겨 사용할 수 있는 제품으로 케이블을 겹 쳐 사용하더라도 국부과 열, 소손 등이 발생되지 않아야 한다. (3) 발열선은 KC, UL, FM, EX 표시 시스템인증제품 또는 동등 이상의 시스템인증제품으로 다음 사 항에 따른다. ① 발열량은 사용전압 220 V. 배관 표면온도에 따라 10~30 W/m 중 설계 도면에 표기된 발열량을 기준한다. ② 최고 연속 사용온도는 65°C 로 한다. ③ 최대 순간 사용온도는 85°C 로 한다. (4) 발열선의 피복재질은 방수, 방습성에 강하고 내구성이 있는 제품으로 한다. 2.5.3 제어반 배관의 동파방지와 에너지절감을 위하여 발열선의 주위 온도 감지기능, 작동온도 조절기능 및 작동 상태 표시기능을 갖추어야 한다. 해 설 1. 본문 해설 및 관련 법규 V (2.5.2 1 항) 정온전선은 전선 절연체의 온도 변화에 따른 저항 변동에 의하여 발열량을 조정해야 함 V (2.5.2) 전선 자체에서 자율 온도 제어가 이루어지지 않는 정열 전선은 자동 온도 제어 시스템이 갖 추어 져 있어도 화재 위험을 피하기 위하여 건물 내 배관에는 사용하지 않음. 건물 외 배관 또는 장 치의 동파 방지를 위한 정열 전선은 설계자의 판단 하에 적용할 수 있음 V (2.5.2 3 항) 1 호 ~ 3 호의 조건에 대한 1 개 이상의 인증을 받아야 함 314 기계설비 기술기준 매뉴얼 | {}
7015f84d-ff4e-4e79-a8f8-04cbeab781d5 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 KC(Korea Certification) : 해당 제품이 대한한국의 전기전자 제품에 대한 안전 요구사항을 준수하고 있음을 의미하며, 한국표준협 회의 승인을 받은 한국 소재 인증기관이 발행함. 전기전자 제품 제조 및 유통업체는 표준 절차를 완료한 후 KC 마크를 적용할 수 있음 참고 - http://jangps/20thtpit/oh.ch/conalut=Ashence8/ UL(Underwriters Laboratories) : 미국 최초의 안전 규격 개발 기관이자 글로벌 안전 과학 회사로서, 제품 안전 시험 및 인증 발행, 환경 시 험, 제품 성능 시험, 헬스 케어 및 의료기기 인증 발행, 교육 및 세미나 등의 서비스를 제공하고 있음 참고 - https://ul.org/ FM(Factory Mutual) : 공장 및 공장 재산을 독점적으로 보장하기 위해 조직된 상호 보험 회사 참고 - https://www.fmglobal.com/ EX(ATEX; ATmosphere EXplosible) : 방폭지역에서 사용되는 전기기기에 대한 국제인증서 참고 - http/www.btotpterfiationoversavontantaking-co 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 동결방지밸브 (freeze protection valve) ¦ 얼기 직전에 배관 내 물을 빼(drain) 주다가 다시 온도가 상승하면 닫혀 물이 항상 동 결온도 이상으로 유지되도록 조절하는 밸브. 외부로부터의 동력이 불필요한, 내장형 (builtin type) 자력식 밸브. 내부 유체온도 감지형과 외기온도 감지형이 있다. 출처: 설비공학편람 제 4 권, pp5.30-30~5.30-31 ¦ 기계설비 기술기준 해설 (별표 10 국토교통부 315 | {}
387134da-50fa-47e1-a524-681f88ed5ea5 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 보온설비 시공 3.1 일반사항 (1) 건축물의 방화구획, 방화벽, 기타 법규로 지정된 칸막이 또는 벽 등을 관통하는 배관, 덕트 등의 틈새 부분에 대해서는 내화성능 인정을 받은 불연재료로 충전한다. (2) 「건축법」, 「소방시설공사업법」과 「화재예방, 소방시설 설치 유지 및 안전관리에 관한 법규」 등 의 법규상 불연공법이 요구되어지는 곳은 불연재 또는 불연재에 준하는 내화성능이 있는 보온재, 외장재 및 보조재를 사용하여 피복 시공한다. (3) 보온재의 이음 부분은 틈새가 없도록 시공하고 겹침 부위의 이음선이 동일선 상에 있지 않도록 한다. (4) 아스팔트 펠트와 정형용 원지의 겹쳐 감는 폭은 30 mm 이상으로 한다. (5) 외장용 테이프류의 겹쳐 감는 폭은 15 mm 이상으로 하고, 입상관일 때는 아래에서 위쪽으로 감 아 올라간다. 단, 폴리에틸렌 필름의 경우는 1/2 겹침 감기를 한다. 수평배관인 경우에는 900 mm 간격으로 수직배관은 600 mm 간격으로 알루미늄 밴드를 감아서 외장용 테이프가 풀리지 않도록 한다. (6) 금속판 등을 감아 마무리 하는 경우 관, 원형덕트의 직관부, 장방형덕트 및 각형 탱크 류는 시임 (Seam)이음으로 하고, 관 및 원형덕트의 굽힘부는 형태에 맞게 제작 또는 공장가공에 의한 성형 품으로 한다. 이음매는 삽입이음으로 하되 탱크류는 필요에 따라 겹침부위에 나사못으로 고정할 수 있다. 옥외 및 옥내 다습한 곳의 이음매 및 나사못 부위는 밀봉재로 마감한다. (7) 보온핀의 부착 수는 장방형 덕트의 경우는 300 mm 간격에 최소한 밑면 및 측면은 2 개, 윗면은 1 개로 한다. 흡음재 내장의 경우는 1 m2 당 30 개 정도로 하고, 모양에 따라 필요한 곳에 보온핀을 부 착한다. (8) 옥내 노출배관의 바닥 관통부는 보온재의 보호를 위하여 바닥에서 최소 150 mm 높이까지 아연 철판 또는 스테인리스 밴드 등으로 피복한다. (9) DN 80 이상의 냉수 및 냉·온수 배관의 지지부는 보온두께와 같은 목재, 칼슘실리케이트, 보온 지 지철물, 합성수지제 등의 지지대로 설치하고, 그 위에 행거밴드 또는 U-볼트로 고정하여 보온재 를 넣은 다음 외장재로 마감한다. (10) 옥내노출관의 보온 변형부분과 분기굴곡부 등에는 밴드로 고정한다. 밴드 폭은 20 mm 이상으 로 한다. (11) 보온을 필요로 하는 기기의 문 및 점검구 등은 개폐에 지장이 없고, 보온효과 가 감소하지 않도록 시공한다. (12) 밸브 및 플랜지의 보온시공은 배관 시공에 따르고, 노출 주철밸브 류의 외장재는 KS F 2803(보 온, 보냉공사의 시공기준) 등을 적용한다. (13) 배관보온용으로 보온통의 사용이 어려운 곳은 동질의 보온대 및 보온판 등을 사용한다. (14) 냉수 배관 또는 결로 방지용 배관은 보온재가 대기와 직접 접촉하지 못하도록 방습재료로 마감 한다. (15) 배관의 보온마감재 외부에는 배관의 용도와 흐름 방향을 표시한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항, 3 항, 5 항 ~ 6 항, 8 항, 10 항 ~ 11 항, 13 항 ~ 15 항) 추가 설명 없음 316 기계설비 기술기준 매뉴얼 | {}
daefcc54-1073-4e2e-a062-f9d9c7cbfc9f | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 V (2 항) 「소방시설공사업법」, 「화재예방, 소방시설 설치 유지 및 안전관리에 관한 법규」 등을 말함 V (4 항) 아스팔트 펠트와 정형용 원지는 사용하는 경우에 해당됨 V (7 항) 보온 핀의 부착 수는 보온재가 덕트 표면에서 탈락되는 것을 방지하기 위한 목적으로 보온 재의 전체 면을 덕트에 접착제로 부착하는 경우에는 보온 핀의 부착 수가 적용되지 않음 - 보온 핀은 스폿 용접형 보온 핀을 사용할 수 있으며, 접착제 형 또는 점착 테이프형 보온 핀을 사용할 경우 에는 덕트 내부 최고 온도에서 지속적인 접착력을 유지할 수 있어야 함 예) 주방 배기 덕트 보온, 제연 배기 덕트 보온, 또는 발전기 배기 덕트 보온 등과 같이 고온의 배기가 이루어 지는 덕트의 보온 핀은 사용 온도에서 장기간 사용에 적합한 성능을 갖춘 접착제 또는 점착 테이프를 사 용해야 함 V (9 항) 냉수 및 냉·온수 배관의 지지부는 다음의 내용을 참조할 수 있음 - DN 80 이상의 배관 지지부에서 철재 안장 대신 목재, 경질 폴리우레탄 폼, 또는 경질 실리카 보온재 등 강 도가 충분한 단열 성능을 가진 재질도 사용할 수 있음 - 보온재의 눌림을 방지하기 위한 것이 목적이므로, U-밴드 또는 크램프로 배관 및 보온재를 고정할 경우에 는 그 목적에 부합되도록 전 둘레에 대하여 보강이 이루어져야 함 ![image](/image/placeholder) 달대 조임 넛 지지 넛 방습지 보온재 보호새들 DN 80 이상 ![image](/image/placeholder) 스테인리스강밴드 볼트 보온재 배관 보호새들 300 DN 80 미만 V (12 항) 밸브보온은 배관 보온과 동일한 재료를 사용할 수 있으며, 공장제작의 경우 단단한 블록과 성형제로 밸브 형상에 맞는 것을 이용함 조립은 현장에서 이루어지며 외부 마감재는 배관 보온재와 동일한 것을 사용하거나 메스틱이나 시멘트, 보강 섬유 등을 사용할 수 있음 해체나 재사용을 용이하게 하기 위하여 자켓으로 하는 경우에는 금속제나 비금속제를 사용할 수 있다. 냉수용 밸브의 경우에는 투습방지 시공을 해야 함 2. 용어 V 내용 없음 - 국토교통부 317 기계설비 기술기준 해설 (별표 10) | {}
bd69c8f1-c0a3-487b-89c7-7abd7834d17c | 국내_기계설비_기술기준_매뉴얼_최종본 | 3.2 기기보온 미네랄울 및 유리면의 사용구분과 재료 및 시공순서는 KCS 31 20 05(3.2) 표 3.2-1 을 준용한 표 12 를 적용한다. 표 12 기기별 보온 시공 순서(KCS 31 20 05(3.2) 표 3.2-1) ¦ 시공 종별 ¦ 사용 구분 ¦ 재료 및 시공 순서 ¦ 비고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ a ¦ 급수 탱크류 ¦ 1) 보온핀 또는 접착제 2) 미네랄울 및 유리면 보온재 3) 아스팔트 펠트 또는 폴리에틸렌 필름 4) 아연철선 또는 철판망 5) 금속판 ¦ - 각형탱크의 경우에는 원칙적으로 철판망을 사용한다. ¦ ¦ b ¦ 보일러, 연도 ¦ 1) 보온핀 또는 스폿 용접 2) 미네랄울 및 유리면 보온재 3) 아연철선 4) 철망 또는 철판망 5) 금속판 ¦ - 각형연도의 경우에는 원칙적으로 철판망을 사용한다. ¦ ¦ C ¦ 증기 헤더 열교환기 저탕탱크 온수탱크 급수, 온수팽창탱크 ¦ 1) 보온핀 2) 미네랄울 및 유리면 보온재 3) 아연철선 4) 철망 또는 철판망 금속판 5) ¦ - 보온핀은 필요장소에만 사용한 다. - 각형탱크의 경우에는 원칙적으로 철판망을 사용한다. ¦ ¦ d ¦ 냉동기 ¦ 1) 보온핀 또는 접착제 2) 미네랄울 및 유리면 보온재 3) 아스팔트 펠트 또는 폴리에틸렌 필름 4) 아연철선 5) 금속판 ¦ ¦ ¦ e ¦ 급수, 냉·온수펌프 헤더 및 탱크류 ¦ 1) 보온핀 또는 접착제 2) 미네랄울 및 유리면 보온재 3) 아스팔트 펠트 또는 폴리에틸렌 필름 4) 아연철선(철판망) 5) 금속판 ¦ - 각형탱크의 경우에는 원칙적으로 철판망을 사용한다. ¦ ¦ f ¦ 공기조화기 송풍기(냉풍용) ¦ 1) 보온핀 2) 미네랄울 및 유리면 보온재 3) 철판망 4) 금속판 및 불연, 준불연재판 ¦ ¦ 주 1) 냉·온수 발생기의 재생기 보온은 보일러에 준하여 시행한다, 2) 시공종별의 f 의 시공에 있어서 공기조화기 내면에 위치하는 경우는 보온 제외한다. 3) 아연철선은 보온재의 고정에 필요한 경우에 적용한다. 4) 메탈라스, 철망, 또는 철판망은 보온재의 비산 또는 유실을 방지하기 위하여 필요한 경우에 적용한다. 5) 다른 보온재는 공사시방서에 따른다. 해 설 1. 본문 해설 및 관련 법규 V (표 12 주 5) 다른 보온재는 미네랄울 또는 유리면 보온재 이외의 보온재를 말함(이하 전체 보온 시공 순서 동일) V (e) 시공 시 다음의 내용을 참조할 수 있음 318 기계설비 기술기준 매뉴얼 | {}
93eb30e5-c1c5-4ff6-91bc-098370c7f0e6 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 펌프류는 펌프 하우징 주위에 상자형으로 보온한다. 상자형은 보온재의 끝단이 드러나지 않도록 이음부를 이용하여 바닥과 측면을 성형하여 시공한다. 측면사이와 측면과 하부사이의 이음부는 유리면류의 경우 접착 제와 띠로 감싸 연결하며 고무발포보온재는 접착제로 부착한다. 이때 이음부분에 대한 기밀시공과 틈새에 대한 투습방지 코팅 또는 베이퍼베리어 자켓을 시공한다. ![image](/image/placeholder) 2. 용어 내용 없음 국토교통부 319 기계설비 기술기준 해설 (별표 10 | {}
664e976c-5014-4731-a564-f32387a09d06 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3.3 배관보온 3.3.1 결로방지보온 급수관, 배수관 등의 결로방지 및 급탕관, 온수관, 기름 및 증기관의 보온 시공 순서는 KCS 31 20 05(3.4.1) 표 3.4-1 을 준용한 표 13 을 적용한다. 표 13 급수관 등의 보온 시공 순서(KCS 31 20 05(3.4.1) 표 3.4-1) ¦ 시공 종별 ¦ 사용 구분 ¦ 재료 및 시공 순서 ¦ 비고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ a ¦ 옥내 노출 배관 ¦ 1) ALGC 부착 미네랄울, ALGC 부착 유리면 보온재 2) 베이퍼배리어 점착테이프 3) 외장재 4) 밴드 ¦ ¦ ¦ b ¦ 천장내, 파이프 샤프트 등의 옥내 은폐 배관 ¦ 1) ALGC 부착 미네랄울, ALGC 부착 유리면 보온재 2) 베이퍼배리어 점착테이프 ¦ ¦ ¦ C ¦ 지하층, 지하피트 내 배관(트렌치, 피트 내를 포함) ¦ 1) ALGC 부착 미네랄울, ALGC 부착 유리면 보온재 2) 베이퍼배리어 점착테이프 3) 외장재 4) 밴드 ¦ ¦ ¦ d ¦ 옥외 노출 및 욕실, 주방 등의 다습한 장소의 배관 ¦ 1) ALGC 부착 미네랄울, ALGC 부착 유리면 보온재 2) 베이퍼배리어 점착테이프외장재 및 밴드 3) 밀봉재 ¦ ¦ 주 1) 급탕관 등을 부득이 지중 매설하는 경우에는 시공종별 c 에 아스팔트 펠트를 추가 한다. 2) ALGC 는 보온재에 별도 부착할 수 있다. 3) 다른 보온재는 공사시방서에 따른다. 해 설 1. 본문 해설 및 관련 법규 ALGC(Aluminum Glass Cloth)는 방습지(베이퍼 배리어) 알루미늄 포일을 말하며, 투습 (습기 침 투) 방지가 필요한 경우에 적용함 V ALK(Aluminum Kraft)는 투습의 악영향이 적은 경우에 사용함 V 방습지는 배관 외부의 습기가 보온재로의 침투를 방지하기 위한 목적으로 사용되며, 크래프트지 + 알루미늄 은박지 + 유리섬유 실 + PE 필름 (폴리에틸렌 필름)으로 구성됨 V 방습지 점착테이프에는 이 중 크래프트지가 제외되고 점착제가 추가됨 V 크래프트지는 종이로 마감재의 형상을 유지하는 목적 외에 보온재 내의 습기를 흡수하여 결로를 감소시키는 부수적인 역할이 있으나, 불연 또는 난연 처리가 용이하지 않으며, 외부로부터의 습기 침투 방지 (방습) 처리가 완벽하면 종이 대신 합성수지를 사용할 수 있음 알루미늄 은박지는 습기 침투를 방지할 수 있으나 쉽게 파손될 수 있으므로 유리섬유 실로 파손 을 감소시킬 수 있음 ALGC 의 가장 바깥에 적용되는 PE 필름은 추가적인 투습 방지 기능 외에도, 바늘 같은 뾰쪽한 물 질로 찔렀다가 뺐을 때, 재료의 탄성으로 스스로 구멍을 메꾸어 습기 침투를 완화하는 목적으로 사용됨 이하 보온 시공 전체 동일 320 기계설비 기술기준 매뉴얼 | {}
2c618511-8353-4ace-bb6b-a4f35ffc4b62 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2. 용어 V 내용 없음 3.3.2 냉수관, 냉·온수관 및 냉매관 보온 냉수관, 냉·온수관 및 냉매관의 보온 시공 순서는 KCS 31 20 05(3.4.2) 표 3.4-2 를 준용한 표 14 를 적용한다. 표 14 냉수관 등의 보온 시공 순서(KCS 31 20 05(3.4.2) 표 3.4-2) ¦ 시공 종별 ¦ 사용 구분 ¦ 재료 및 시공 순서 ¦ 비고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ e ¦ 옥내 노출 배관 ¦ 1) ALGC 부착 미네랄울, ALGC 부착 유리면 보온재 2) 베이퍼배리어 점착테이프 3) 외장재 4) 밴드 ¦ ¦ ¦ f ¦ 옥내 노출 배관 ¦ 1) 발포 폴리에틸렌 보온재, 고무발포 보온재 2) 접착제 및 부착재 3) 외장재 4) 밴드 ¦ = 정형이 유지되는 보온재 또는 외장재의 경우 4)를 제외할 수 있다. - 보온재의 길이 방향 및 가로 방향 이음 부 위는 접착제 이음 후 부착재를 사용하여 틈새가 발생하지 않도록 시공하여 결로를 방지한다. ¦ ¦ g ¦ 천장 내, 파이프 샤프트 등의 옥내 은폐배관 ¦ 1) ALGC 부착 미네랄울, ALGC 부착 유리면 보온재 베이퍼배리어 점착테이프 2) ¦ - ¦ ¦ h ¦ 천장 내, 파이프 샤프트 등의 옥내 은폐배관 ¦ 1) 발포 폴리에틸렌 보온재, 고무발포 보온재 2) 접착제 및 부착재 3) 외장재 4) 밀봉재 ¦ - 정형이 유지되는 보온재 또는 외장재의 경우 4)를 제외할 수 있다. - 보온재의 길이 방향 및 가로 방향 이음 부 위는 접착제 이음 후 부착재를 사용하여 틈새가 발생하지 않도록 시공하여 결로를 방지한다. ¦ ¦ i ¦ 옥외 노출 배관 ¦ 1) ALGC 부착 미네랄울, ALGC 부착 유리면보온재 2) 베이퍼배리어 점착테이프 3) 알루미늄, 함석, 칼라 함석 또는 스테인리스스틸 가공 판재 등 4) 밀봉재 ¦ ¦ ¦ j ¦ 옥외 노출 배관 ¦ 1) 발포 폴리에틸렌 보온재, 고무발포 보온재 2) 접착제 및 부착재 3) 외장재 4) 밀봉재 ¦ ¦ ¦ k ¦ 지하층, 지하피트 내 배관(트렌치, 피트 내를 포함) ¦ 1) ALGC 부착 미네랄울, ALGC 부착 유리면보온재 2) 베이퍼배리어 점착테이프 3) 폴리에틸렌 필름 또는 아스팔트 펠트 4) 외장재 5) 밴드 ¦ - 점검이 용이하고 다습한 장소가 아닌 경 우 3)을 제외하고 정형이 유지되는 경우 5)를 제외할 수 있다. ¦ ¦ I ¦ 지하층, 지하피트 내 배관(트렌치, 피트 내를 포함) ¦ 1) 발포 폴리에틸렌 보온재, 고무발포 보온재 2) 접착제 및 부착재 3) 외장재 ¦ ¦ ¦ m ¦ 욕실, 주방 등의 다습한 장소의 배관 ¦ 1) ALGC 부착 미네랄울, ALGC 부착 유리면보온재 2) 베이퍼배리어 점착테이프 3) 외장재 4) 밀봉재 5) 밴드 ¦ - 옥내 노출의 경우는 3) 및 4)를 제외한다. ¦ ¦ n ¦ 욕실, 주방 등의 다습한 장소의 배관 ¦ 발포 폴리에틸렌 보온재, 고무발포 보온재 1) 2) 접착제 및 부착재 3) 외장재 4) 밀봉재 ¦ ¦ 주 1) 냉매용 동배관의 보온은 f, h, j, l, 및 n 에 따른다. 2) 냉수 및 냉·온수용 옥내 노출 배관으로 DN 65 이상의 밸브, 스트레이너 등은 나사못 등에 의해 탈착이 용 이한 금속제 또는 성형 합성수지재 덮개로 외장을 마감한다. 3) ALGC 는 보온재에 별도 부착할 수 있다. 4) 다른 보온재는 공사시방서에 따른다. 국토교통부 321 기계설비 기술기준 해설 (별표 10) | {}
687b597c-948c-4e84-90da-199507a65b1d | 국내_기계설비_기술기준_매뉴얼_최종본 | 해 설 1. 본문 해설 및 관련 법규 다음의 내용을 참조하여 시공할 수 있음 1. 투습 방지를 위하여 ALGC 시용 시 가로 방향 세로 방향 이음부를 베이퍼베리어 점착테이프로 틈새없이 기밀 시공한다. 고무발포제품을 사용하는 경우에도 가로 방향과 원주 방향에 접착제를 이용하여 기밀이 완전하도록 한다. 2. 유리섬유보온통 등의 단열재를 사용하는 경우 길이방향의 보온재는 4 개마다 베이퍼댐을 설치하고 이음 부속 등의 끝단이나 맞대기 이음 부분은 이음밀봉재로 기밀을 하고 투습방지용 코팅이나 접착테이프 등 으로 감싼다. 3. 냉수 배관의 플랜지나 밸브류, 행거류, 순환펌프 등에서의 보온은 가능한 성형제품을 사용하고 현장시공 을 하더라도 투습방지를 위하여 이음부에 대한 기밀 시공을 한다. 2. 용어 내용 없음 3.4 덕트보온 3.4.1 장방형 덕트 보온 장방형 덕트의 보온 시공 순서는 KCS 31 20 05(3.3.1) 표 3.3-1 을 준용한 표 15 를 적용한다. 표 15 장방형 덕트의 보온 시공 순서(KCS 31 20 05(3.3.1) 표 3.3-1) ¦ 시공 종별 ¦ 사용 구분 ¦ 재료 및 시공 순서 ¦ 비고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ a ¦ 옥내 노출 덕트 ¦ 1) 보온핀 2) ALGC 부착 미네랄울, ALGC 부착 유리면 보온재 3) 베이퍼배리어 점착 테이프 4) 접착제 5) 외장재 및 밀봉재 6) 코너비드 7) 밴드 ¦ ¦ ¦ b ¦ 천장내 등 옥내 은폐 덕트 ¦ 1) 보온핀 2) ALGC 부착 미네랄울, ALGC 부착 유리면 보온재 3) 베이퍼배리어 점착 테이프 4) 밀봉재 5) 코너비드 및 알루미늄 또는 PP 밴드 ¦ ¦ ¦ C ¦ 옥외 노출 및 욕실, 주방 등 다습한 장소의 덕트 ¦ 1) 보온핀 2) ALGC 부착 미네랄울, ALGC 부착 유리면 보온재 3) 베이퍼배리어 점착 테이프 4) 외장재 5) 밀봉재 ¦ ¦ 주 1) 댐퍼, 플렉시블 커넥터 및 플랜지 부분(보강을 포함)은 보온재로 적합하게 시공한다. 2) 아연철선 및 철판망은 보온재의 고정에 필요한 경우에 적용한다. 3) ALGC 는 보온재에 별도 부착할 수 있다. 4) 다른 보온재는 공사시방서에 따른다. 322 기계설비 기술기준 매뉴얼 | {}
d5f3d463-19c4-40a5-a431-71a036bc55b0 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 해 설 1. 본문 해설 및 관련 법규 추가 설명 없음 2. 용어 V 내용 없음 3.4.2 원형덕트 보온 원형 덕트의 보온시공 순서는 KCS 31 20 05(3.3.2) 표 3.3-2 를 준용한 표 16 을 적용한다. 표 16 원형 덕트의 보온 시공 순서(KCS 31 20 05(3.3.2) 표 3.3-2) ¦ 시공 종별 ¦ 사용 구분 ¦ 재료 및 시공 순서 ¦ 비고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ d ¦ 옥내 노출 덕트 ¦ 1) ALGC 부착 미네랄울, ALGC 부착 유리면 보온재 2) 베이퍼배리어 점착 테이프 3) 접착제 4) 외장재 및 밀봉재 5) 밴드 ¦ ¦ ¦ e ¦ 천장내 등 옥내 은폐덕트 ¦ 1) ALGC 부착 미네랄울, ALGC 부착 유리면 보온재 2) 베이퍼배리어 점착테이프 3) 알루미늄 또는 PP 밴드 ¦ ¦ ¦ f ¦ 옥외 노출 및 욕실, 주방 등 다습한 장소의 덕트 ¦ 1) ALGC 부착 미네랄울, ALGC 부착 유리면 보온재 2) 베이퍼배리어 점착테이프 3) 외장재 및 밀봉재 4) 알루미늄 또는 PP 밴드 ¦ ¦ 주 1) ALK(aluminum kraft): 알루미늄 + 크래프트지, ALGC(aluminum glass cloth): 알루미늄 + 크래프트지 + PE 필름 + 유리직물 2) 아연철선은 보온재의 고정에 필요한 경우에 적용한다. 3) ALK 또는 ALGC 는 보온재에 별도 부착할 수 있다. 4) 메탈라스, 철망, 또는 철판망은 보온재의 비산 또는 유실을 방지하기 위하여 필요한 경우에 적용한다. 5) 다른 보온재는 공사시방서에 따른다. 해 설 1. 본문 해설 및 관련 법규 V 추가 설명 없음 2. 용어 V 내용 없음 국토교통부 323 기계설비 기술기준 해설 (별표 10) | {}
1d150c93-c34c-4bbd-8061-e8bee701dd45 | 국내_기계설비_기술기준_매뉴얼_최종본 | ○ 3.4.3 제연덕트 보온 제연 덕트의 보온시공 순서는 KCS 31 20 05(3.3.3) 표 3.3-3 을 준용한 표 17 을 적용한다. 표 17 제연덕트의 시공 순서(KCS 31 20 05(3.3.3) 표 3.3-3) ¦ 시공 종별 ¦ 사용 구분 ¦ 재료 및 시공 순서 ¦ 비고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ g ¦ 은폐 장방형 및 원형 덕트 ¦ 1) 보온핀 또는 스폿 용접 2) ALK 또는 ALGC 부착 미네랄울, ALGC 부착 유리면 보온재 3) 알루미늄 점착테이프 4) 알루미늄 밴드 또는 철망 ¦ - 원형 덕트의 경우는 1) 보온핀 을 제외한다. ¦ 주 1) ALK 또는 ALGC 는 보온재에 별도 부착할 수 있다. 2) 다른 보온재는 공사시방서에 따른다. 해 설 1. 본문 해설 및 관련 법규 추가 설명 없음 2. 용어 내용 없음 - ------- ---- 3.4.4 소음 내장재 덕트 및 체임버의 소음내장재의 시공 순서는 KCS 31 20 05(3.3.4) 표 3.3-4 을 준용한 표 18 을 적용 한다. 표 18 소음 내장재 시공 순서(KCS 31 20 05(3.3.4) 표 3.3-4) ¦ 시공 종별 ¦ 사용 구분 ¦ 재료 및 시공 순서 ¦ 비고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ h ¦ 소음 내장재 ¦ 1) 보온핀, 스폿 용접 또는 접착제 2) 미네랄울 및 유리면 흡음재 3) 유리면표 또는 네오프렌 등의 코팅 4) 소음 내장재 접합부 밀봉(내부 코팅제 사용 시) 5) 철망 또는 펀칭메탈 ¦ ¦ 주 1) 다른 흡음재는 공사시방서에 따른다. 324 기계설비 기술기준 매뉴얼 | {}
b7645b8b-ec1f-436c-a511-ae45eaaae37a | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 해 설 1. 본문 해설 및 관련 법규 추가 설명 없음 2. 용어 내용 없음 3.5 동파방지 발열선 기계설비 착공 전 확인 대상 건축물의 현장배치기술인은 동파가 예상되는 배관의 발열선 시공 시 다 음의 사항을 준수하였는지 여부를 확인한다. (1) 발열선은 동파가 예상되는 다음의 배관에 적용한다. ① 지하주차장을 통과 하는 소화수 배관, 습식소방밸브 ② 지하주차장을 통과 하는 급수, 급탕관 ③ 외기와 면하는 수도계량기 ④ 옥상 정수위밸브 및 주위배관 ⑤ 개별 가스보일러 하부 급수, 급탕관(매립배관 포함) ⑥ 기타 동파가 예상되는 필요한 부분 (2) 발열선의 배관 부착 시 일자 시공을 원칙으로 하고, 발열량 부족으로 인해 돌려감기를 할 경우에 는 발열선 간격을 최소 150 mm 이상으로 하되, 30 mm 이하 배관은 돌려 감기 시공을 금지한다. 그 외 돌려감기 시공할 경우에는 제조사 최소 곡률 반경을 확인한 후 시공한다. (3) 발열선의 끝과 시작 그리고 고정 시에는 내열성 테이프를 사용하고, 남은 발열선을 묶어 놓거나 잘라 사용하지 않는다. (4) 발열선 보온 시 난연 또는 불연성 재질을 사용하고, 화재 확산이 예상되는 경우에는 반드시 불연 성 보온재나 배관 케이싱으로 보호하여 외부에 노출되지 않도록 한다. (5) 발열선 차단기 용량은 제조사의 최대 사용 길이에 따라 선정한다. (6) 최대 순간 사용 온도가 85°C 이상일 경우 자동으로 전원이 차단되고 중앙제어반 또는 관리실로 경보가 되도록 한다. 다만, 공동주택의 급수·급탕계량기함에 설치하는 콘센트형은 동작램프 및 자체경보 알림장치를 갖추어야 한다. (7) 보온 작업 후에는 '발열선 주의 표시 를 부착하고 열선 근처에서 용접작업은 절대 금지한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 해당 지역과 현장 여건을 고려하여 동파가 우려되는 배관에 열선을 적용함 V (1 항 1 호, 2 호) 지하주차장을 통과 하는 배관 중 외기로부터 50m 이내에 설치되어 동파가 예상되 는 배관 부위를 말함 국토교통부 325 기계설비 기술기준 해설 (별표 10) | {}
5854eae9-cfa2-44da-b89b-1205d9e76948 | 국내_기계설비_기술기준_매뉴얼_최종본 | (1 항 5 호) 개별 가스보일러가 건축물 내 보일러실에 설치되어 배관보온 시 동파우려가 없을 경우, 설치 제외 가능. V (2 항 ~ 5 항) 추가 설명 없음 V (6 항) 공동주택에서 보일러 하부, 급수계량기 등에 콘센트형 동파방지 발열선을 사용하는 경우에 도 최대 순간 사용 온도가 85°C 이상일 경우 동작 차단 기능이 있어야 하며, 동작 및 전원 표시 등 이 있어야 함. 단, 해당사양에 적합한 구매 가능한 제품이 없는 경우, 기계설비감리업무수행자의 승인에 따라 예외로 허용할 수 있음 V (7 항) '발열선 주의 표시'에는 '허가받은 기술자 외 작업 금지' 문구를 추가하고, 유지관리를 위해 해당 내용을 「기계설비 기술기준」 제 15 조 및 「기계설비 유지관리기준」 제 6 조에 따른 유지관리 지침서에 반영해야 함 2. 용어 V 내용 없음 326 기계설비 기술기준 매뉴얼 | {}
ff066faf-de19-4184-b8e0-d5cbc4f9576b | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 [별표 11] 자동제어설비의 설계 및 시공 기준 1. 자동제어설비 일반사항 1.1 목적 이 기준은 건축물, 시설물 등에 설치되는 자동제어 설비, 건물에너지관리시스템, 원격검침설비 및 기타 제어설비의 규격, 품질성능 등 효율성 제공에 필요한 설계 및 시공 방법 등 세부 기술기준을 정 함을 목적으로 한다. 해 설 이 기준의 목적은 「기계설비법」 제 14 조(기계설비 기술기준)과 같은 법 영 제 2 조 및 [별표 1]에 근 거하여, 건축물이나 시설물에 필요한 자동제어설비의 설계 및 시공 시 기계설비의 안전과 성능을 확보하기 위하여 필요한 기술적 요건을 규정하기 위함 「기계설비법」 제 14 조(기계설비 기술기준) ① 국토교통부장관은 기계설비의 안전과 성능확보를 위하여 필요 한 기술기준(이하 "기술기준이라 한다)를 정하여 고시하여야 한다. 이를 변경하는 경우에도 또한 같다. 1.2 적용범위 이 기준은 건축물, 시설물 등에 다음의 자동제어 설비가 설치되는 경우에 대하여 적용한다. (1) 중앙관제설비 (2) 건물에너지관리시스템 (3) 현장제어설비 (4) 원격검침설비 (5) 공동주택 자동제어 해 설 이 기준의 적용범위는 「기계설비법」 제 2 조제 1 호에 따른 건축물등에 같은 법 영 제 2 조에 따라 대 통령령으로 정한 자동제어설비를 설치하는 경우 및 그와 관련된 부속설비들을 포함함 「기계설비법」 제 2 조(정의) 1. "기계설비"란 건축물, 시설물 등(이하 "건축물등"이라 한다)에 설치된 기계 · 기 구 · 배관 및 그 밖에 건축물등의 성능을 유지하기 위한 설비로서 대통령령으로 정하는 설비를 말한다. 「기계설비법 시행령」 제 2 조(기계설비의 범위) 「기계설비법」(이하 "법"이라 한다) 제 2 조제 1 호에서 "대통령령 으로 정하는 설비"란 별표 1 의 설비를 말한다. 「기계설비법 시행령」 [별표 1] 기계설비의 범위 9. 자동제어설비 : 건축물등에 설치된 기계 · 기구 · 배관 및 그 밖에 성능을 유지하기 위한 설비의 감시, 제 어.관리 및 통제 등을 위하여 설치된 설비 국토교통부 327 기계설비 기술기준 해설 (별표 11) | {}
1d1b67f3-786c-483e-9a94-c400bfe3a6ab | 국내_기계설비_기술기준_매뉴얼_최종본 | 1.3 타 규정과 의 관계 다음의 규정과 이 기준에서 정하는 내용이 상이한 경우에는 해당 규정을 따른다. (1) 「에너지이용합리화법 시행규칙」 (2) KDS 31 35 10 중앙관제설비 설계기준 (3) KDS 31 35 12 건물에너지관리 시스템 설계기준 (4) KDS 31 35 15 현장제어설비 설계기준 (5) KDS 31 35 20 원격검침설비 설계기준 (6) KCS 31 35 10 중앙관제 설비공사 표준시방서 (7) KCS 31 35 12 건물에너지관리시스템 설치공사 표준시방서 (8) KCS 31 35 15 현장제어설비공사 표준시방서 (9) KCS 31 35 20 원격검침설비공사 표준시방서 (10) KCS 31 35 25 공동주택자동제어설비공사 표준시방서 해 설 V 이 기준과 타 규정 및 기준과 다른 경우에는 상기 규정에 명시된 내용을 따름 「에너지이용 합리화법 시행규칙」 제 1 조(목적) 이 규칙은 「에너지이용 합리화법」 및 같은법 시행령에서 위임된 사항과 그 시행에 필요한 사항을 규정함 을 목적으로 한다. 「기계설비 설계기준」 KDS 31 35 10 (중앙관제설비 설계기준) 이 기준의 목적은 건물의 쾌적한 실내 환경을 유지하면서 센서, 계측장비, 분석소프트웨어 등을 활용하여 효율적인 에너지 사용량 관리 및 분석을 통하여 에너지 절약이나 운전방법을 개선하는 방안을 제시하기 위함이다. 「기계설비 설계기준」 KDS 31 35 12 (건물에너지관리 시스템 설계기준) 이 기준의 목적은 건물의 쾌적한 실내 환경을 유지하면서 센서, 계측장비, 분석 소프트웨어 등을 활용하여 효율적인 에너지 사용량 관리 및 분석을 통하여 에너지 절약이나 운전 방법을 개선하는 방안을 제시하기 위함이다. 「기계설비 설계기준」 KDS 31 35 15 (현장제어설비 설계기준) 이 기준은 현장에 설치되어 자동제어를 필요로 하는 각종 장비나 시스템의 제어, 감시, 운전 상태, 데이터 검출, 설계 등을 목적으로 한다. 「기계설비 설계기준」 KDS 31 35 20 (원격검침설비 설계기준) 이 기준은 건축물에서 사용하는 급수, 급탕, 가스, 열에너지 등에 대한 사용량을 건축물에 설치된 원격검침 유닛을 이용하여 자동으로 검침하는 방식에 대한 것으로 기준으로 일반적인 사항은 KDS 31 35 05(1. 일 반사항)에 따른다. 「기계설비설계공사 표준시방서」 KCS 31 35 10 (중앙관제 설비공사 표준시방서) 중앙 관제 설비인 중앙 제어 및 감시 장치, 현장 제어 장치(DDC 또는 PLC), 입출력 모듈(I/O module) 및 현장 검출/조작기기,네트워크 구성상 필요에 따라 허브, 리피터, 라우터 등의 보조 장치 등에 적용한다. 328 기계설비 기술기준 매뉴얼 | {}
4e3afdb8-7caa-4b10-9d89-0430ded1f956 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 「기계설비설계공사 표준시방서」 KCS 31 35 12 (건물에너지관리시스템 설치공사 표준시방서) 건물에너지관리시스템(이하 BEMS 라 한다) 구축 전반에 관한 일반적인 사항을 규정함을 목적으로 하며 건물에너지관리시스템 구축 공사를 통해 설비와 에너지를 통합관리 할 수 있는 시스템으로 구성한다. 「기계설비설계공사 표준시방서」 KCS 31 35 15 (현장제어설비공사 표준시방서) 이 기준은 자동제어설비공사의 현장제어설비공사에 적용하며 다음의 내용을 포함한다. (1) 감지기류, 제어기류 설치공사 (2) 배선 및 배관공사 (3) 현장 제어반의 설치 및 중앙 제어반과 의 연결공사 (4) 시운전 조정 및 시운전 「기계설비설계공사 표준시방서」 KCS 31 35 20 (원격검침설비공사 표준시방서) 이 기준은 주거용 건축물의 원격자동검침 설비공사에 적용하며 난방, 급수, 정수, 급탕의 유량 및 가스량 등을 검침하기 위한 계량기와 이와 관련된 공사에 적용한다. 「기계설비설계공사 표준시방서」 KCS 31 35 25 (공동주택자동제어설비공사 표준시방서) 공동주택 자동제어설비공사는 홈네트워크 시스템, 개별난방 자동제어설비공사, 지역난방 자동제어공사, 통합 검침설비 공사, 제설장치공사 및 연료전지공사에 대하여 적용한다. 2. 자동제어설비 설계 2.1 일반사항 (1) 확장성이 있어야 한다. (2) 편리성이 있어야 한다. (3) 표준성 , 호환성이 있어야 한다. (4) 경제성이 있어야 한다. (5) 신뢰성이 있어야 한다. 해 설 1. 본문 해설 및 관련 법규 (1 항) 확장성이란 자동제어 소프트웨어에 포함되어 있는 관제점의 확장성, 원격제어장치(DDC)의 입출력 모듈의 확장성을 의미함 KDS 31 35 10 : 2021 중앙관제설비 4.1 중앙관제장치의 설계 기준 (1) 확장성 ① 시스템 기능, 구성, 용량이 설비와 환경에 대응 할 수 있어야 한다. ② 설비의 추가 변경에도 용이하게 대응할 수 있어야 한다. V (2 항) 사용의 편리성 국토교통부 329 기계설비 기술기준 해설 (별표 11) | {}
05a48f44-38ec-4b92-8c9a-0b671785d2cd | 국내_기계설비_기술기준_매뉴얼_최종본 | KDS 31 35 10 : 2021 중앙관제설비 4.1 중앙관제장치의 설계 기준 (2) 사용의 편리성 ① 조작 설정의 용이성이 있어야 한다. ② 정보 데이터의 실 시간성이 있어야 한다. ③ 정보 데이터의 판별의 용이성이 있어야 한다. V (3 항) 표준성 · 호환성이란 자동제어 프로토콜(규격)이 표준화된 규격인지에 대한 여부를 의미하 며, 표준화된 규격에는 BACnet 이나 Modbus 등이 있으며, 적용기준은 설계도서에 따름 KDS 31 35 10 : 2021 중앙관제설비 4.1 중앙관제장치의 설계 기준 (3) 시스템의 표준성 ① 보수 체제가 확보가 되어야 한다. ② 보수 부품의 공급이 원활하여야 한다. ③ 자료가 정비되어 있어야 한다. V (4 항) 비용 KDS 31 35 10 : 2021 중앙관제설비 4.1 중앙관제장치의 설계 기준 (4) 비용 ① 장치 공사의 효율이 높은 시스템이어야 한다. ② 보수에 드는 비용이 낮아야 한다. V (5 항) 추가 설명 없음 2. 용어 내용 없음 2.2 중앙관제설비 2.2.1 감시 시스템 설비의 운전 상태를 확인할 수 있는 현장제어반을 설치하고 중앙제어반으로 데이터 전송이 가능하 도록 한다. 2.2.2 중앙관제실 건축물 내에 통합 중앙관제실을 설치하는 경우는 설치된 기계설비, 전력설비, 조명설비, 소방설비, 방범설비, 건물에너지관리시스템 등 감시 및 제어를 통합할 수 있어야 한다. 해 설 1. 본문 해설 및 관련 법규 330 기계설비 기술기준 매뉴얼 | {}
1135dbf6-6837-46f1-a52e-62fa82a0bf65 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 (2.2.1) 설비의 운전 상태를 확인할 수 있는 현장제어반을 설치하고 중앙제어반으로 데이터전이 가능한 정합장치가 구비되어야 한다. 감시 시스템은 하위로 원격제어장치(DDC)나 개별 설비의 컨트롤러와 연결되며, 상위로 SI(시스템 통합), FMS(시 설관리시스템), BEMS(에너지관리시스템)과 연동하고, 외부로 인터넷을 통한 원격접속 서비스를 선택적으로 지원함 KDS 31 35 10 : 2021 중앙관제설비 4.2 감시 시스템 설비의 운전 상태를 확인할 수 있는 현장제어반을 설치하고 중앙제어반으로 데이터 전이 가능한 정합장치 가 구비되어야 한다. V (2.2.2) 중앙관제실은 운영자의 근무환경 및 장비배치를 고려하여 충분한 공간을 확보하고, 원활 환 내부 배선을 위해 악세스 플로어 등을 계획함 KDS 31 35 10 : 2021 중앙관제설비 4.3 중앙제어실(감시 및 제어센터) (1) 설치되는 실의 용도는 사무실과 동일하여야 한다. (2) 건물의 규모와 시설관리의 효율성을 감안하여 설치하고 근무자의 휴식공간을 설치한다. (3) 건축물 내에 통합 중앙제어실을 설치하는 경우는 설치된 기계설비, 전기설비, 조명설비, 소방설비, 방범 설비, 승강기설비 등 감시 및 제어를 통합할 수 있어야 한다. 2. 용어 V 내용 없음 국토교통부 331 기계설비 기술기준 해설 (별표 11) | {}
5d5685f8-91a0-4e11-b8d9-5381df6deded | 국내_기계설비_기술기준_매뉴얼_최종본 | 2.3 건물에너지관리시스템 2.3.1 건물에너지관리시스템 설계기준 (1) 시스템 개요 ① 건물에너지관리시스템(BEMS: building energy management system)은 건축물, 시설물의 에너지 사용량파악과 설비운전 추이를 종합 분석하여 에너지를 절감할 수 있게 하는 기능과 원 격검침 및 열원별 에너지 사용량 감시 기능을 통합한다. ② 건물자동화 시스템의 계측 、 계량 데이터를 장기간 수집 보존하여 운전관리자나 설계자에게 수 집한 데이터를 알기 쉽게 정리 가공하는 기능과 그 기능을 이용해 평가 、 해석하는 행위를 지원 할 수 있는 시스템을 구현해야 한다. (2) 시스템 기본 기능 ① 데이터 수집 및 표시 기능 ② 정보감시 ③ 데이터 조회 ④ 에너지소비 현황 분석 ⑤ 설비의 성능 및 효율 분석 ⑥ 실내외 환경 정보 제공 ⑦ 에너지 소비량 예측 ⑧ 에너지 비용 조회 및 분석 ⑨ 제어시스템 연동 2.3.2 단위제어시스템 인터페이스 (1) 기계설비 자동제어 시스템 (2) 전력제어 시스템 (3) 승강설비 시스템 2.3.3 소프트웨어 (1) 에너지 사용량에 영향을 주는 모든 장치나 시스템에 에너지를 관리하는 소프트웨어 사용을 고려 한다. (2) 건물에너지관리시스템(BEMS)을 설치하는 경우에는 전체 에너지사용량의 5% 이상인 열원 및 냉 난방설비, 공조 및 반송설비 등의 에너지사용량을 모니터링 가능하도록 한다. 해 설 1. 본문 해설 및 관련 법규 V (2.3.1 1 항) 건물에너지관리시스템은 PC 나 서버 하드웨어, BEMS 소프트웨어, 에너지 계측기(유량 계, 열량계, 가스미터, 수도미터, 전력량계, 온도센서, 풍량측정기 등), 관제점 수신을 위한 DDC 및 이것을 서로 연결하는 배관배선공사, BEMS 소프트웨어에 대한 커스터마이징으로 구성됨 V (2.3.1 1 항, 2 항) 332 기계설비 기술기준 매뉴얼 | {}
10f7c424-600a-4b8e-9545-839c45b267af | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 KDS 31 35 12 : 2021 건물에너지관리시스템 4.1.3 시스템 기본 기능 (1) 시스템 기능 ① 데이터 수집 및 표시기능 : 수집한 건물에너지 소비 및 관련 데이터를 알기 쉽게 컴퓨터 화면 등을 통해 표시하는 기능을 갖추어야 한다. 단위는 국제표준단위계를 따른다. ② 정보감시 : 운영자가 에너지 소비에 관한 기준값이나 에너지 사용설비의 운전범위 등을 입력하는 기능을 갖추어야 한다. ③ 데이터 조회 : 운영자가 원하는 기간 동안의 건물에너지 소비 및 관련 데이터와 정보를 표 또는 그래프로 제공하는 기능을 갖추어야 한다. ④ 에너지소비 현황 분석 : 운영자가 건물에너지 소비 현황을 쉽게 파악할 수 있도록 다음과 같은 항목에 대한 분석 기능을 갖추어야 한다. ⑤ 설비의 성능 및 효율 분석 : 운영자가 건물에서 운용되는 각종 설비의 운전상태와 성능을 쉽게 파악할 수 있도록 분석하는 기능을 갖추어야 한다. ⑥ 실내외 환경 정보 제공 : 기후와 실내 환경 퉁 건물에너지 소비와 밀접한 관련이 있는 정보를 제공하는 기능을 갖추어야 한다. ⑦ 에너지 소비량 예측 : 에너지를 절약하고 건물과 설비의 계획 적인 운영에 도움을 주기 위하여 건물의 에 너지 소비량을 예측하는 기능을 제공하는 기능을 갖추어야 한다. ⑧ 에너지 비용 조회 및 분석 : 건물의 에너지 소비에 따른 비용 분석 정보의 제공을 위해 다음과 같은 기능 을 포함하여야 한다. - 에너지 비용 체계 선택 - 에너지 비용 단가 수정 - 기간별 에너지 비용 조회 - 예상 에너지 비용 조회 ⑨ 제어시스템 연동 : 자체적으로 제어기능을 수행하거나 그렇지 못한 경우에는 건물자동화시스템과 연동하 여 자동으로 제어하는 기능을 갖추어야 한다. V (2.3.2) 단위제어시스템 인터페이스 대상은 설비제어, 전력제어, 조명제어, 원격검침, 신재생에너 지시스템, 단위 냉난방시스템, 환기시스템 등이 있음 V (2.3.2 1 항) 기계설비 자동제어 시스템 KDS 31 35 12 : 2021 건물에너지관리시스템 4.2.1 기계설비 자동제어 시스템 (1) 개방형 프로토콜 통신 가능하도록 구성한다. (2) 최소한 다음의 에너지 관련 자료를 제공할 수 있게 설계되어야 한다. - 유량 - 온도 - 열량 - 전력량 (3) 에너지 통합관리 시스템과 데이터를 공유하여 자동제어 운영 최적화로 실질적인 에너지 절감효과 를 거 둘 수 있도록 운영할 수 있도록 설계되어야한다. (4) 계측범위별 데이터를 집계하여, 상태감시용 1 초 단위, 이상감지 및 성능데이터용 1 분 단위, 에너지데이터 용 15 분단위로 에너지관리시스템에 제공하여야 한다. V (2.3.2 2 항) 전력제어 시스템 국토교통부 333 기계설비 기술기준 해설 (별표 11) | {}
f0afda54-4eba-417f-a722-37bbe3eb9f64 | 국내_기계설비_기술기준_매뉴얼_최종본 | KDS 31 35 12 : 2021 건물에너지관리시스템 4.2.2 전력제어 시스템 (1) 전력량계는 개방형 프로토콜 통신 가능하도록 구성한다. (2) 전력제어, 조명제어, 원격검침, 무정전전원장치, 태양광 발전장치 등은 개방형 표준 프로토콜 인터페이스 로 구성한다. (3) 에너지관리를 위한 구성 범위는 조닝별, 층별로 계획함을 기본으로 하되, 발주자 요구 사항을 반영한다. (4) 계측범위별 전력량(kWh) 데이터를 집계하여 15 분단위로 에너지관리시스템에 제공하여야 한다. V (2.3.2 3 항) 승강설비 시스템 KDS 31 35 12 : 2021 건물에너지관리시스템 4.2.3 승강설비 시스템 (1) 전력량계는 승강설비 중앙관제 시스템으로 호기별 전력량 데이터가 취합되어야 한다. (2) 승강설비 중앙관제시스템은 개방형 프로토콜 통신이 가능하도록 구성한다. (3) 에너지관리를 위한 범위는 발주자 요구사항을 반영한다. (4) 계측범위별 전력량(kWh) 데이터를 집계하여 15 분단위로 에너지관리시스템에 제공하여야한다. V (2.3.3) 소프트웨어 KDS 31 35 12 : 2021 건물에너지관리시스템 4.3 소프트웨어 (1) 에너지 사용량에 영향을 주는 모든 장치나 시스템에 에너지를 관리하는 소프트웨어를 고려해야 하며 주 요 기능은 다음과 같다 - 효율 감시 및 기록 - 에너지 사용량 감시 및 기록 : 종류별, 용도별, 시간별 - 변동추이 곡선 - 에너지 사용량 평가 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 인터페이스 ¦ 서로 다른 두 시스템이나 장치, 소프트웨어를 서로 이어 주는 장치 혹은 이에 따른 엔지니어링을 의미함(해설서 주) ¦ <p id='486' data-category='paragraph' style='font-size:14px'></p> 334 기계설비 기술기준 매뉴얼 | {}
b6c31f61-2ccb-4d58-bd18-935acee1914f | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.4 현장제어설비 2.4.1 열원 및 냉난방설비 (1) 열원 및 냉난방설비 제어 일반사항 열원 및 냉난방설비의 기동 , 정지는 기기 부속반(현장제어반)에서 직접 조작한다. 단, 중앙감시할 경우 중앙 감시반에서 원격 제어 할 수 있게 하며 열원 및 냉난방설비의 대수제어를 행할 시는 중앙 감시반에서 원격 조작을 한다. (2) 열원 및 냉난방설비 제어 설계 ① 시스템 제어 ② 냉각탑 제어 ③ 냉수 급수, 환수 헤더의 차압 제어 ④ 냉열원 장비 인터페이스 해 설 1. 본문 해설 및 관련 법규 V (1 항) 자동제어시스템은 열원 및 냉난방설비의 기동 · 정지가 가능하도록 프로그램을 구성하고, 중앙감시반에서의 임의 조작이나 스케줄 제어를 선택적으로 사용할 수 있도록 로직을 구성함 KDS 31 35 15 : 2021 현장제어설비 4.1 열원설비 (1) 열원설비 제어 일반사항 열원설비의 기동/정지는 기기 부속반(현장제어반)에서 직접 조작한다. 단, 중앙감시 할 경우 중앙 감시반에 서 원격 제어 할 수 있게 하며 열원설비의 대수제어를 행할 시는 중앙 감시반에서 원격 조작을 할 수 있어 야 한다. V (2 항) 열원설비 제어 설계 기계설비 기술기준 해설 (별표 11) 국토교통부 335 | {}
0859ea54-fcd7-40d3-8bcd-70afc8a3ec85 | 국내_기계설비_기술기준_매뉴얼_최종본 | KDS 31 35 15 : 2021 현장제어설비 4.1 열원설비 (2) 열원설비 제어 설계 ① 펌프 시스템의 대수 제어 펌프 시스템의 제어 설계는 정속펌프만의 대수제어 또는 변속펌프를 사용하여 제어하는 방법을 적용한다. ② 냉동기 시스템의 대수 제어 냉동기 시스템의 대수제어는 부하의 특성에 적합하게 냉수 순환량과 냉수를 공급하기 위해 냉동기의 개별 용량제어, 냉수 펌프제어, 냉수의 공급 및 환수 헤더 차압제어 등이 함께 고려되어야 한다. ③ 냉각탑 제어 냉각탑은 냉각수 온도를 감지해서 냉각탑 팬 운전 제어를 수행하여 냉각수 온도를 일정하게 유지시킨다. ④ 냉수 급수, 환수 헤더의 차압제어 냉수 급수, 환수 헤더의 차압제어는 헤더 차압을 검출하여 헤더 바이패스 밸브를 조절한다. ⑤ 보일러시스템 제어 가. 증기보일러의 운전은 원칙적으로 별도의 현장 제어반에서 직접(수동) 조작하게 설치하여야하며, 비상시 는 보일러가 자동 정지되도록 제어시스템이 구성되어야 한다. 나. 응축수 탱크의 보급수 제어는 전동 2 방 변이나 2 위치 제어밸브를 사용하며 고수위, 저수위를 감시하여 야 한다. ⑥ 열교환기 제어 열교환기는(Heat Exchanger)항상 온수가 일정한 온도로 공급되도록 온도제어를 한다. (3) 자동제어 설계의 고려 사항 ① 냉동기 인터페이스 냉동기 제어반에서는 냉동기 기동/정지, 상태 및 경보 접점을 제공한다. 만약 냉동기와 통신방식으로 자동제 어 감시반에서 인터페이스 할 경우 냉동기 공급 업체와 의 협의 를 통하여 관련 프로토콜을 개방하거나 개방 형 프로토콜을 사용하여 자동제어 중앙 감시반과 인터페이스 할 수 있도록 한다. ② 냉열원 장비 인터록 냉열원 장비 관련 연동 제어 동작은 냉동기 공급 업체에서 제어 관련 시퀀스를 제공한다. 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 차압제어 ¦ 차압을 검출하여 그 값으로 다른 것을 조절하거나 차압을 유지하기 위한 제어를 의 미함(해설서 주) ¦ --- ----- ---- 2.4 현장제어설비(계속) 2.4.2 공기조화설비 공기조화설비 제어 설계는 다음의 사항을 고려한다. (1) 기동 , 정지 (2) 실내 온 , 습도 제어 (3) 엔탈피 제어 (4) 댐퍼 및 풍량 제어 (5) 화재 감지 및 연동제어 해 설 336 기계설비 기술기준 매뉴얼 | {}
8aecf710-993a-4c1c-b87a-2cc2b991cf0a | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 1. 본문 해설 및 관련 법규 V (1 항) 실내에 요구되는 온 · 습도 설정값을 유지하기 위하여 냉난방 밸브나 댐퍼, 가스밸브 등을 제어하는 것을 말함 KDS 31 35 15 : 2021 현장제어설비 4.2 공기조화기 (2) 공기조화기 제어 설계 ① 기동: 중앙감시반에서 급기팬을 기동하면 공조가 시작되도록 한다. 이때 시간 지연 기능을 두어 기동 시 에는 외기용 댐퍼모터가 먼저 동작하도록 한다. ⑩ 정지: 급기팬과 환기팬을 정지하고 냉방 밸브, 난방 밸브, 외기 댐퍼, 배기 댐퍼는 닫힘으로 설정하고 환기 댐퍼는 열림으로 설정한다. ⑪ 중앙감시반 주요 관제점: 급기팬/환기팬 기동/정지 및 운전상태 감시, 화재 경보감시, 혼합공기 온도 감 시, 필터 차압 감시, 환기 온,습도 감시, 급기 온도,습도 감시, 외기 온,습도 감시 V (2 항) 공기조화기 제어 설계 : 실내 온 · 습도 제어 KDS 31 35 15 : 2021 현장제어설비 4.2 공기조화기 (2) 공기조화기 제어 설계 ② 실내 온도 제어: 정풍량 단일 덕트 방식은 환기덕트에 설치된 온도검출기의 검출온도에 따라 냉방밸브와 난방밸브를 비례 제어한다. ③ 실내 습도 제어: 환기덕트 또는 실내에 설치된 습도검출기의 검출습도에 의해 가습밸브를 2 위치 또는 비 례 제어하여 실내 습도를 일정하게 유지시킨다. V (3 항) 외기의 엔탈피가 순환공기의 엔탈피 보다 작을 때, 외기를 냉방용 에너지원으로 적용하여 에너지 사용량을 절감하는 제어 방법을 말함 KDS 31 35 15 : 2021 현장제어설비 4.2 공기조화기 (2) 공기조화기 제어 설계 ⑦ 엔탈피 제어: 환절기 외기 냉방 시 환기덕트에 설치된 온·습도 검출기 와 외기 온·습도 검출기 엔탈피를 연산 비교하여 외기 엔탈피가 실내 엔탈피보다 낮은 경우 엔탈피 제어에 의한 댐퍼의 상호 연동 비례 제 어로 실내 상태를 유지시킨다. V (4 항) 공기조화기 제어 설계 : 댐퍼 및 풍량 제어 KDS 31 35 15 : 2021 현장제어설비 4.2 공기조화기 (2) 공기조화기 제어 설계 ④ 환절기 댐퍼 제어: 외기, 배기, 환기 댐퍼는 엔탈피 제어에 의해 상호 연동 비례 제어 한다. ⑤ 동하절기 시 댐퍼 제어: 외기, 배기 댐퍼는 최소 개도치 열림, 환기댐퍼는 역동작 된다. ⑥ 워밍업 제어 시 댐퍼 제어: 외기, 배기 댐퍼는 완전 닫힘, 환기 댐퍼는 완전 열려 실내가 일정 온도에 도달 시까지 운전된다. V (5 항) 화재 감지용 센서(열 혹은 연기 감지기)나 화재수신반으로부터 화재 경보를 전달받아 화재 상황에 상응하는 자동제어 연동 운전(제연 급배기 송풍기 기동 · 정지)를 하는 것을 말함 국토교통부 337 기계설비 기술기준 해설 (별표 11) | {}
bd0e473d-201c-4547-abc1-4ddd99b8a1a7 | 국내_기계설비_기술기준_매뉴얼_최종본 | KDS 31 35 15 : 2021 현장제어설비 4.2 공기조화기 (2) 공기조화기 제어 설계 ⑧ 화재 감지: 환기 덕트에 설치된 이온화 연기검출기의 감지에 의해 급기, 환기팬을 정지시키고, 중앙감시 반에 화재 경보 신호를 보낸다. ⑨ 풍량 제어: 급기 및 환기 덕트에 설치된 풍량측정기와 급기덕트 내 설치된 정압 검출기는 덕트 내 풍량 및 정압을 검출하여 가변전압가변주파수(VVVF)방법 등으로 급기팬과 환기팬을 제어한다. 2. 용어 V 내용 없음 2.4 현장제어설비(계속) 2.4.3 환기설비 환기설비 제어 설계는 다음의 사항을 고려한다. (1) 배기 송풍기나 급기 송풍기의 기동 및 정지를 해야 한다. (2) 주차장에 있는 배기 송풍기는 일산화탄소 및 미세먼지에 의한 환기량 제어를 한다. (3) 발전기실의 송풍기는 발전장치와 연동한다. (4) 기계실, 전기실, 펌프실 등의 환기 송풍기 제어는 전동기 제어반에서 수행한다. (5) 화재 발생 시 송풍기는 화재 경보신호에 의하여 정지시킨다. 해 설 1. 본문 해설 및 관련 법규 V (1 항, 2 항, 3 항, 5 항) 환기 설비 제어 설계 KDS 31 35 15 : 2021 현장제어설비 4.3 환기설비 (1) 환기 설비 제어 설계 ① 배기팬이나 급기 팬의 기동 및 정지를 해야 한다. ② 주차장에 있는 배기 팬은 일산화탄소에 의한 환기량 제어를 한다. ③ 발전기실의 환풍기는 발전장치와 연동되게 한다. ④ 화재 발생시 팬은 화재 경보신호에 의하여 정지 시킨다. 338 기계설비 기술기준 매뉴얼 | {}
5e874229-adf9-44c1-8808-dc9dfe63f7ca | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 KDS 31 35 15 : 2021 현장제어설비 4.3 환기설비 (2) 지하 주차장 환기 ① 지하 주차장 환기 설비 구성 가. 지하 주차장 환기는 관련법에서 요구하는 환기설비를 내용으로 하며 주차장 구조 및 형태에 따라 관련법 에 적합하도록 설치한다. 나. 주차장 내부 일산화탄소 농도는 주차장을 이용하는 차량이 가장 빈번한 시각의 전후 8 시간 평균치를 25 ppm 이하로 유지하도록 한다. ② 지하 주차장 환기 설비의 자동제어 구성 가. 수동 조작에 의한 개별 기동/정지 나. CO 검출기 및 타이머에 의한 연동 다. 지하주차장 팬의 기동/정지, 상태의 원격 제어 라. 유인팬은 배기팬과 연동 (2 항 ~ 3 항) 주차장 내부 일산화탄소 농도는 주차장의 용도에 따라 관련법령에서 정하는 기준 이 하로 유지하도록 함(다중이용시설 실내주차장 : 25ppm, 공동주택 지하주차장 : 차량이 가장 빈번 한 시각의 전후 8 시간 평균치 50ppm 이하) V (4 항) 펌프실, 기계실 환기 KDS 31 35 15 : 2021 현장제어설비 4.3 환기설비 (3) 펌프실, 기계실 환기 ① 펌프실 환기팬의 제어는 전동기 제어반에서 수행한다. ② 기계실 환기팬의 제어는 전동기 제어반에서 수행한다. ③ 펌프실, 기계실 환기 설비의 자동제어 구성은 제어방식 및 현장여건에 따른다. V (5 항) 추가 설명 없음 2. 용어 V 내용 없음 기계설비 기술기준 해설 (별표 11) 국토교통부 339 | {}
aa52f58a-f340-4ea2-b6e2-526cac468385 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2.4 현장제어설비(계속) 2.4.4 위생설비 (1) 급수설비 제어 ① 가압급수방식의 제어 ② 고가탱크 방식의 제어 (2) 급탕설비 제어 ① 중앙식 급탕 제어 ② 개별식 급탕 제어 (3) 배수설비 ① 배수펌프는 기동정지제어 또는 순차제어 방식으로 한다. ② 침수방지를 위하여 경보시스템을 갖추어야 한다. (4) 빗물이용설비 빗물이용설비의 자동제어는 저장된 빗물을 재활용수로 사용하기 위한 제어설비와 빗물을 건물 밖 으로 배제시키기 위한 제어설비를 갖추도록 한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 급수설비 제어 KDS 31 35 15 : 2021 현장제어설비 4.4 위생설비 (1) 급수설비 제어 급수설비는 저수탱크에 저장된 물을 고가탱크로 양수하거나 가압 방식으로 직접 배관에 공급하는 방식을 주로 이용하므로 이 경우의 수위 제어와 압력 조절을 위한 제어설비를 갖춘다. ① 가압급수방식의 제어 급수압력 및 급수량의 변화에 대응하기 위해 펌프의 대수제어, 순차제어, 회전수제어 및 이것을 조합한 제어 방법 등을 적용한다. ② 고가탱크 방식의 제어 가. 지하저수탱크에 설치된 액면지시 조절 장치의 신호에 의해서 정수위 조절밸브를 제어시켜 탱크 내의 수위를 일정하게 유지시킨다. 나. 고가탱크에 설치된 액면지시 조절 장치의 신호에 의해 급수펌프의 운전대수를 결정하여 기동/정지시 켜 탱크 내 수위를 일정하게 유지시킨다. ③ 중앙감시반 관제점 가. 지하저수탱크 수위계측 나. 지하저수탱크 고·저수위 경보 감시 다. 고가탱크 수위 계측 라. 고가탱크 고·저수위 경보 감시 마. 급수 펌프 기동/정지 및 운전상태 감시 바. 배관 내 공급측 압력 감시 사. 정수위밸브 동작 감시 340 기계설비 기술기준 매뉴얼 | {}
dad7826b-b7a8-481a-8aef-443ede83ea3c | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 자동제어 설계의 고려사항 가. 수위조절기는 정수의 경우 플로트 타입이나 전극봉 방식을 이용한다. 나. 지하저수탱크 갈수위시에는 급수 펌프가 동작되지 않도록 상호 연동하여 공회전을 방지할 수 있도록 제어한다. 다. 급수펌프의 경우 급수사용량에 따라 유량이 적을 때는 1 대의 펌프만 운전하고 급수량이 증가하면 필요 한 대수만큼 펌프를 차례로 가동할 수 있도록 제어한다. 라. 펌프의 기동/정지 순서를 일정시간마다 차례로 교대시켜 각 펌프의 운전시간을 균등하게 함으로써 장 비전체의 수명을 연장할 수 있도록 제어한다. 마. 저수탱크나 고가탱크의 고수위경보의 경우 큰 피해가 우려되므로 관리소나 경비실 등 관리인원이 상주 하는 곳에 경광등이나 문자메시지서비스(SMS: Short Message Service) 등으로 위험을 알릴 수 있는 장 치를 설치한다. (2 항 1 호) 급탕설비 제어 KDS 31 35 15 : 2021 현장제어설비 4.4 위생설비 (2) 급탕설비 ① 급탕설비 제어 일반사항 급탕순환펌프가 기동되면, 설정한 급탕 설정온도에 맞춰 급탕 공급배관에 설치된 온도검출기의 검출온도에 의해 가열밸브를 비례제어하여 급탕공급 온도를 일정하게 유지시킨다. ② 급탕설비 제어 설계 가. 급탕 공급배관에 설치된 온도검출기의 검출온도에 의해 가열밸브를 비례제어하여 급탕공급 온도를 일 정하게 유지시킨다. 나. 온수를 필요로 하는 시간만큼 스케줄에 의해 급탕 순환펌프의 기동/정지를 제어한다. KCS 31 35 25 : 2021 공동주택자동제어설비공사 2.7.2 온도조절장치 2) 개별난방 실내온도조절기 실내온도조절기는 디지털방식으로 다음과 같은 기능을 갖추어야 한다. ① 작동기능 거실용은 실내 온도조절, 다른 방 실내온도조절, 외출/예약/타이머 기능과 난방 및 급탕 전용, 경고램프(에러 표시 코드포함) 또는 경보음,정지 등의 기능이 있어야 한다. 각 실용은 실내 온도조절, 경고램프(에러 표시 코드포함) 또는 경보음, 타이머 등의 기능이 있어야 한다. ② 표시기능 거실용은 난방, 급탕, 작동 표시 보일러 on/off 및 저수위가 표시되고 실내온도, 설정온도, 외출/예약/타이머 등은 액정으로 표시되어 야간에도 식별이 가능하게 한다. 각 실용은 난방 및 보일러 on/off 작동이 표시되고 실내온도, 설정온도 등은 액정으로 표시되어야한다. ③ 설정기능 거실용은 자체 및 다른 방 난방온도 설정과 예약기능이 있어야 하며 정전 또는 전원 off 후 재동작시에도 이 전의 운전 상태를 유지한다. 각 실용은 자체 난방온도 설정기능이 있어야 하며 정전 또는 전원 off 후 재동작 시에도 이전의 운전 상태를 유지한다. ④ 외관 거실용은 제조업체별로 상이할 수 있으나 인접 전기스위치 등과 조화되어야 한다. V (3 항) 배수설비 제어 국토교통부 341 기계설비 기술기준 해설 (별표 11) | {}
0d79835c-6e93-4a33-bf7f-eeda7a4dbe15 | 국내_기계설비_기술기준_매뉴얼_최종본 | KDS 31 35 15 : 2021 현장제어설비 4.4 위생설비 (3) 배수설비 ④ 자동제어 설계의 고려사항 가. 펌프의 기동/정지 순서를 일정시간마다 차례로 교대시켜 각 펌프의 운전시간을 균등하게 함으로써 장 비전체의 수명을 연장할 수 있도록 제어한다. 나. 현장 여건에 따라서 대기 개념 없이 고수위 시에는 2 대를 동시에 운전하고, 일정 수위가 되면 한 대만 운전하다가 저수위시에 2 대의 펌프를 정지하는 스텝 제어를 한다. 다. 물이 넘칠 경우 기계실과 같이 큰 피해가 우려되는 경우 관리소나 경비실 등 관리 인원이 상주하는 곳 에 경광등이나 문자 메시지 등으로 위험을 알릴 수 있는 장치를 설치한다. 라. 배수탱크에 설치되는 수위조절기는 오뚜기 방식을 사용한다. 마. 기계실, 펌프실의 경우 큰 피해가 우려되므로 관리소나 경비실 등 관리인원이 상주하는 곳에 경광등이 나 문자메시지서비스(SMS:Short Message Service)등으로 위험을 알릴 수 있는 장치를 설치한다. V (4 항) 우수설비 제어 설계 KDS 31 35 15 : 2021 현장제어설비 4.4 위생설비 (4) 우수설비 ② 우수설비 제어 설계 우수 저류탱크에 설치된 액면지시조절계의 신호에 의해서 조절밸브를 제어하여 저류탱크 내의 수위를 일 정하게 유지시킨다. 2. 용어 V 내용 없음 2.5 원격검침설비 2.5.1 검침 대상 (1) 전력 사용량 검침 (2) 수도 사용량 검침 (3) 가스 사용량 검침 (4) 열사용량 검침 해 설 1. 본문 해설 및 관련 법규 V (1 항 ~ 4 항) 추가 설명 없음 342 기계설비 기술기준 매뉴얼 | {}
a68cfa14-0117-436c-8b7a-cb3e91722d70 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 KDS 31 35 20 : 2021 원격검침설비 4.2 검침 대상 (1) 전력 사용량 검침 건축물에서 사용하는 모든 전기사용량은 전자식 전력량계의 디지털 또는 펄스(pulse) 신호를 원격검침 유닛 에서 받아 전력량을 검침한다. (2) 수도 사용량 검침 건축물에서 사용한 모든 수도사용량은 원격식 수도메타의 디지털 또는 펄스 신호를 원격검침 유닛에서 받 아 수도량을 검침한다. (3) 가스 사용량 검침 건축물에서 사용한 모든 가스사용량은 원격식 가스계량기의 디지털 또는 펄스 신호를 원격검침 유닛에서 받아 가스량을 검침한다. (4) 열량 검침 건축물의 각 세대에서 사용하는 열량을 원격식 열량계의 디지털 또는 펄스 신호를 원격검침 유닛에서 받아 열량을 검침한다. 2. 용어 V 내용 없음 ![image](/image/placeholder) 2.5 원격검침설비(계속) 2.5.2 자동제어 설계의 고려 사항 (1) 검침 기본 사항 ① 건축물별 자료 구성 ② 일자별 자료 ③ 시간대별 자료 ④ 월간사용량 정리 ⑤ 장치별 상태 점검 (2) 운용 소프트웨어 기능 ① 사용금액, 징수 기초 자료 ② 자체 진단 기능 ③ 정전 시 사용량 검침 ④ 유사 시 수동 검침 (3) 시스템 구성 ① 원격식 계량기 ② 세대 원격검침장치 ③ 중계장치 ④ 주제어 장치 ⑤ 원격 자동 검침 서버 해 설 기계설비 기술기준 해설 (별표 11) 국토교통부 343 | {}
47949ada-9c24-4386-a6f7-edfcadba9362 | 국내_기계설비_기술기준_매뉴얼_최종본 | 1. 본문 해설 및 관련 법규 V (1 항) 추가 설명 없음 V (2 항) 원격검침설비설계의 고려 사항 KDS 31 35 20 : 2021 원격검침설비 4.3 원격검침설비설계의 고려 사항 (2) 운용 소프트웨어 기능 ① 기초 자료 원격검침시스템 운영에 필요한 기초자료 등록을 위한 소프트웨어를 필요로 하며, 주요 자료는 기본자료 등 록, 데이터정합장치 코드 등록, 원격검침 유닛 등록, 사용자 등록, 검침항목 설정 등이 있다. 사용금액 징수 를 위한 기초자료의 생성과 구성은 관련법규 및 기준을 따라야 하며 임의 로 가공해서는 안 된다. ② 자체 진단 기능 원격검침 유닛의 경년변화, 고장 등을 감지할 수 있는 고장진단 알고리즘을 구현하고 중앙컴퓨터에서 원격 감시가 가능하도록 한다. ③ 정전 시 사용량 검침 ④ 유사 시 수동 검침 V (3 항) 원격검침설비설계의 고려 사항 KDS 31 35 20 : 2021 원격검침설비 4.3 원격검침설비설계의 고려 사항 (3) 시스템 구성 ① 원격식 계량기 : 전기, 수도, 가스, 열량, 온수 등의 사용량을 표시하고 일반적으로 사용량에 비례하는 디 지털 또는 펄스신호를 발생하여 세대 원격장치로 전송한다. ② 세대 원격검침장치 : 각 계량기(전기, 가스, 수도, 온수, 난방)의 모든 데이터 값을 디지털 또는 펄스신호로 받아 적산하여 사용량을 표시하고 일반적으로 사용량 데이터를 저장하여 중앙관제 장치로 전송한다. ③ 중계 장치 : 각 세대 원격장치로부터 중앙관제장치에 송출되는 사용량 데이터 신호를 받아서 중계한다. ④ 주제어 장치 : 세대 각 유닛으로부터 전송된 데이터 신호를 종합 처리하여 중앙관제 장치로 송출한다. ⑤ 원격 자동 검침 서버 : 세대 각 유닛으로부터 전송된 데이터를 분석 연산하여 사용량의 적산, 청구서 발행 등의 업무를 자동 전산처리하고 데이터를 분석하여 검침오류, 계통 이상 등 관련설비 이상 유무를 확인하 며 시설물 관리에 필요한 각종 데이터를 기록 보관하는 역할을 수행할 수 있도록 일반적으로 다음과 같이 구성하여야 한다. 가. 중앙처리장치(CPU) 나. 모니터(VDT, CRT, LCD, PDP, LED 패널 등) 다. 프린터 라. 소프트웨어 (가) 시간대별 사용량 데이터 수신 데이터베이스 처리 및 저장 (나) 요금 계산 및 내역 조회 (다) 청구서 발행 (라) 기타 마. 무정전 전원 장치(UPS) 2. 용어 V 내용 없음 344 기계설비 기술기준 매뉴얼 | {}
49e3d03e-ab58-4e2d-ae40-bca0d41d4b3c | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.6 공동주택 자동제어설비 (1) 중앙감시반 2.2 에 따른다. (2) 현장제어반 2.4 에 따른다. 해 설 1. 본문 해설 및 관련 법규 V (1 항 ~ 2 항) 추가 설명 없음 2. 용어 V 내용 없음 국토교통부 345 기계설비 기술기준 해설 (별표 11) | {}
c56ff6de-8e65-4340-b9bb-584067336096 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 자동제어설비 시공 3.1 중앙관제설비 중앙관제설비 장치는 형식, 중량, 설치장소에 적합한 방법으로 견고하게 설치한다. 해 설 1. 본문 해설 및 관련 법규 KCS 31 35 10 : 2021 원격검침설비 3.2 중앙제어 및 감시장치, 현장제어장치 설치 3.2.1 탁상형 장치 탁상형 장치의 설치대는 흔들리거나 넘어지지 않도록 한다. 3.2.2 자립형 장치 (1) 베이스로 구조용 형강을 사용할 경우에는 윗면이 수평이 되도록 설치한 후에 볼트로 바닥 면에 견고히 고정한다. (2) 제어반을 고정된 베이스 위에 부착하고 인접한 제어반 상호간에 틈이 발생되지 않도록 라이너 등을 이용 하여 조정한 뒤 볼트로 고정한다. 3.2.3 벽걸이형 장치 (1) 벽걸이형 장치는 그 중량 및 설치 장소에 적합한 방법으로 설치한다. (2) 중량이 무거운 것 및 설치 방법이 특수한 것은 공사 전에 설치 상세도를 제출한다. 2. 용어 V 내용 없음 ---- --- 3.2 건물에너지관리시스템 3.2.1 건물에너지관리시스템 (1) 건물에너지관리시스템은 도면 및 특기 사양에 표시된 대로 완전하게 설치해야 하며 사용될 시스 템은 특기사양에서 보여주고 있는 건물에너지관리시스템기능을 만족해야 한다. (2) 건물에너지관리시스템(BEMS)은 「건축물의 에너지절약설계기준」 제 11 조제 6 호에 따른 '[별표 12] 「건물에너지관리시스템(BEMS) 설치 기준」등에 따라 규정하고 있는 설치기준을 충족해야 한 다. 3.2.2 계측기 (1) 전력량계는 선정된 제조사의 설치 방법에 따라 설치한다. (2) 초음파 유량계 등은 배관 호칭지름에 10 배 이상의 직선 관에 설치한다. (3) 증기 열량계는 선정된 제조사의 설치 방법에 따라 설치한다. 해 설 346 기계설비 기술기준 매뉴얼 | {}
3d9e2446-aac9-477c-bc5f-13c9892d8036 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 1. 본문 해설 및 관련 법규 KCS 31 35 12 : 2021 건물에너지관리시스템 설치공사 3.2 건물에너지관리시스템 설치 건물에너지관리시스템은 도면 및 특기 사양에 표시된 대로 완전하게 설치하여야 하며 사용될 SYSTEM 은 특 기사양에서 보여주고 있는 건물에너지관리시스템기능을 만족해야 한다. 3.3 계측기 설치공사 (1) 전력량계는 제조사의 설치 방법에 따라 설치한다. (2) 초음파 유량계는 배관 지름(D)에 10 배 이상의 직선 관에 설치한다. (3) 증기 열량계는 제조사의 설치 방법에 따라 설치한다. V (3.2.1 1 항) 「녹색건축물 조성 지원법」, 「공공기관 에너지이용 합리화 추진에 관한 규정」, 「건축 물 에너지효율등급 인증」, 「제로에너지 건축물 인증 기준」, 「건축물의 에너지 절약 설계기준」을 따름 V (3.2.1 2 항) 건물에너지관리시스템(BEMS) 설치 기준 「녹색건축물 조성 지원법」 제 6 조의 2(녹색건축물 조성사업 등) ① 정부는 기본계획을 시행하기 위하여 다음 각 호의 사업에 필요한 비 용을 회계연도마다 세출예산에 계상(計 上)하기 위하여 노력하여야 한다. 14. 건축물에너지관리시스템 활성화 및 확산 · 보급 사업 ② 제 1 항제 14 호의 "건축물에너지관리시스템"이란 건축물의 쾌적한 실내환경 유지와 효율적인 에너지 관리 를 위하여 에너지 사용내역을 모니터링하여 최적화된 건축물에너지 관리방안을 제공하는 계측 · 제어 · 관리 · 운영 등이 통합된 시스템을 말한다. 「건축물의 에너지절약설계기준」 제 11 조제 6 호, [별표 12] 건물에너지관리시스템(BEMS) 설치 기준 ¦ 항 목 ¦ 항 목 ¦ 설치 기준 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ 데이터 수집 및 표시 ¦ 대상건물에서 생산 · 저장 · 사용하는 에너지를 에너지원별(전기/연료/열 등)로 데이터 수집 및 표시 ¦ ¦ 2 ¦ 정보감시 ¦ 에너지 손실, 비용 상승, 쾌적성 저하, 설비 고장 등 에너지관리에 영향을 미치는 관련 관제값 중 5 종 이상 1)에 대한 기준값 입력 및 가시화 ¦ ¦ 3 ¦ 데이터 조회 ¦ 일간, 주간, 월간, 년간 등 정기 및 특정 기간을 설정하여 데이터를 조회 ¦ ¦ 4 ¦ 에너지소비 현황 분석 ¦ 2 종 이상의 에너지원단위 2)와 3 종 이상의 에너지용도에 대한 에너지소비 현황 및 증감 분석 ¦ ¦ 5 ¦ 설비의 성능 및 효율 분석 ¦ 에너지사용량이 전체의 5%이상인 모든 열원설비 기기별 성능 및 효율 분 석 ¦ ¦ 6 ¦ 실내외 환경 정보 제공 ¦ 온도, 습도 등 실내외 환경정보 제공 및 활용 ¦ ¦ 7 ¦ 에너지 소비 예측 ¦ 에너지사용량 목표치 설정 및 관리 ¦ ¦ 8 ¦ 에너지 비용 조회 및 분석 ¦ 에너지원별 사용량에 따른 에너지비용 조회 ¦ ¦ 9 ¦ 제어시스템 연동 ¦ 1 종 이상의 에너지용도에 사용되는 설비의 자동제어 연동 ¦ 1) 에너지 손실, 비용 상승, 쾌적성 저하, 설비 고장 등 건물의 에너지관리에 영향을 미치는 관련 관제값 중 5 종 이상 1. 에너지원별 사용량 기준값 2. CO2 농도 상한치 3. 실내습도 쾌적성범위 4. 냉동기 COP 하한값 5. 냉온수 공급온도 범위 등 2) 2 종 이상의 에너지원단위 1. 단위면적당 에너지소비량 2. 1 인당 에너지소비량 3. (병원)병상당 에너지소비량 4. (판매)단위 매출당 에너지 소비량 등 기계설비 기술기준 해설 (별표 11) 국토교통부 347 | {}
b8240daa-c5cc-4025-900a-4a86e8b9d30f | 국내_기계설비_기술기준_매뉴얼_최종본 | (3.2.1 2 항) BEMS 설치기준은 건축물의 에너지절약설계기준을 따르며, 에너지사용량 계측 대상 및 계측량 세부 기준은 한국에너지공단의 "에너지관리시스템 설치확인업무 운영규정"의 "건물에 너지관리시스템 설치확인 기준"의 "건물에너지관리시스템 세부 평가기준"을 따른다. V (3.2.2 1 항 ~ 3 항) 추가 설명 없음 2. 용어 내용 없음 3.3 현장제어설비 3.3.1 기기설치 (1) 제어반이나 장치를 설치 후 운영 전까지 장기간 방치될 경우에는 먼지나 습기 등으로 인한 기능 저하를 방지하기 위하여 보호(덮개, 막 등) 조치한다. (2) 압력 조절기 또는 검출기를 덕트 등에 설치하여 정압을 검출할 때에는 압력 변동이 적은 위치를 선정하여 설치하고, 검출기의 말단이 유체의 흐름에 대하여 직각이 되도록 한다. (3) 조작기, 조절밸브 및 조절댐퍼 ① 전동식 밸브는 유체의 흐름 방향을 확인하여 구동축에 수직이 되도록 부착한다. ② 덕트에 설치하는 댐퍼 축 및 전동기의 구동축은 수평으로 견고하게 설치하고, 덕트와 의 접속 시 에는 프레임이 변형되지 않도록 유의 한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) KCS 31 35 15 : 2021 현장제어설비공사 3.1 일반사항 (5) 제어반이나 장치를 설치한 후 운전 시 까지 장기간 방치될 경우에는 먼지나 습기 등으로 인한 기능 저하 를 방지하기 위해 보호 조치한다. V (2 항) KCS 31 35 15 : 2021 현장제어설비공사 3.2.1 조절기 및 검출기 (8) 압력 조절기 또는 검출기를 덕트 등에 설치하여 정압을 검출할 때에는 압력 변동이 적은 위치를 선정하 여 설치하고, 검출기의 말단이 유체의 흐름에 대하여 직각이 되도록 한다. V (3 항) 348 기계설비 기술기준 매뉴얼 | {}
867436f4-7f37-4e8c-8b3c-f4a40736ced2 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 KCS 31 35 15 : 2021 현장제어설비공사 3.2.2 조작기, 조절밸브 및 조절댐퍼 (1) 전동식 밸브는 유체의 흐름 방향을 확인하여 구동축에 수직이 되도록 부착한다. 부득이 하게 경사가 졌 을 경우에도 전동기 축은 수평이 되게 설치한다. (5) 덕트에 설치하는 댐퍼 축 및 전동기의 구동 축은 수평으로 견고하게 설치하고, 덕트와 의 접속시에는 프 레임이 변형되지 않도록 유의 한다. (3 항 1 호) 전동식 밸브의 구동기는 응축수 등의 외부 유체가 밸브 연결부를 따라 구동기 내부로 들어오지 않도록 설치함 (3 항 2 호) 댐퍼 구동기의 구동력은 허용되는 적용 댐퍼 크기 및 마찰력을 충분히 고려하여 선정하 고, 비상시 현장에서 직접 조작 가능한 수동 조작 스위치를 포함함 2. 용어 V 내용 없음 3.3.2 제어반 (1) 제어반의 설치 시에는 보수 관리에 필요한 공간을 확보한다. (2) 제어반의 기초 높이는 50~100 mm 로 하고, 벽체 및 지지대에 견고하게 고정한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) KCS 31 35 15 : 2021 현장제어설비공사 3.3 제어반의 설치 (2) 제어반의 설치 시에는 보수 관리에 필요한 공간을 확보하고 이동, 전도, 탈락현상 등이 발생되지 않도록 기초 볼트 등으로 슬래브나 벽체 등에 견고하게 고정시킨다. (2 항) 옥외형 제어반의 경우, 방청 처리된 방수형 외함을 적용하고, 벽체 설치형 제어반은 벽체에 견고하게 설치하며 기초를 제외하고, 바닥 설치형 제어반은 기초 높이를 50~100mm 로 함 KCS 31 35 15 : 2021 현장제어설비공사 3.3 제어반의 설치 (5) 제어반의 기초 높이는 50~100 mm 로 한다 2. 용어 V 내용 없음 국토교통부 349 기계설비 기술기준 해설 (별표 11) | {}
d2b94198-4b5c-4d87-8d8f-06b5b3b1f38b | 국내_기계설비_기술기준_매뉴얼_최종본 | 3.3.3 시공 구분 자동제어공사의 시공 구분은 KCS 31 35 15(3.7)을 준용한 표 1 ~ 표 4 를 적용한다. 표 1 자동제어 공사와 기계설비배관 공사 구분 ¦ 번 호 ¦ 제어장치 ¦ 기계설비배관공사 ¦ 기계설비배관공사 ¦ 기계설비배관공사 ¦ 자동제어공사 ¦ 자동제어공사 ¦ 자동제어공사 ¦ 자동제어공사 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 번 호 ¦ 제어장치 ¦ 검출기 설치구 ¦ 검출 배관구 설치 ¦ 조절밸브 몸체설치 ¦ 발신기 조작기 검출기 설치 ¦ 검출 배관 ¦ 계기 또는 설치 ¦ 제어용 전기 배관, 배선 ¦ ¦ 1 ¦ 온도검출기 ¦ ○ ¦ ○ ¦ ○ ○ ¦ ○ ¦ ○ ¦ ○ ○ ¦ ○ ¦ ¦ 2 ¦ 차압검출기 ¦ ¦ ○ ¦ ○ ○ ¦ ○ ¦ ○ ¦ ○ ○ ¦ ○ ¦ ¦ 3 ¦ 유량스위치 ¦ ○ ¦ ○ ¦ ○ ○ ¦ ○ ¦ ○ ¦ ○ ○ ¦ ○ ¦ ¦ 4 ¦ 조절밸브 ¦ ¦ ○ ¦ ○ ○ ¦ ○ ¦ ○ ¦ ○ ○ ¦ ○ ¦ ¦ 5 ¦ 액면조절기 ¦ ○ ¦ ○ ¦ ○ ○ ¦ ○ ¦ ○ ¦ ○ ○ ¦ ○ ¦ ¦ 6 ¦ 계량기 ¦ ¦ ○ ¦ ○ ○ ¦ ¦ ○ ¦ ○ ○ ¦ ○ ¦ 표 3 자동제어 공사와 전기설비공사 구분 ¦ 번 호 ¦ 제어장치 ¦ 전기설비공사 ¦ 전기설비공사 ¦ 전기설비공사 ¦ 전기설비공사 ¦ 전기설비공사 ¦ 전기설비공사 ¦ 전기설비공사 ¦ 자동제어공사 ¦ 자동제어공사 ¦ 자동제어공사 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 번 호 ¦ 제어장치 ¦ UPS 용 전원 제공 ¦ 일반 전원 제공 ¦ AC24V 전원 제공 ¦ 접지 설치 및 제공 ¦ 동력 공급 및 설치 ¦ 비상 전원 제공 ¦ 필요 전원 인입 공사 ¦ 제어용 전기 배관 배선 ¦ 기기 자체 설치 ¦ 제어반 설치 ¦ ¦ 1 2 3 ¦ 현장제어반 원격제어반 중앙감시반 ¦ ○ O ¦ O ¦ O ¦ ○ O O ¦ ¦ ¦ ○ O O ¦ ○ ○ O ¦ ¦ ○ O ○ ¦ 표 4 자동제어 공사와 기계설비 장비간의 연동공사 구분 ¦ 항목 ¦ 기계설비 장비 제작사 ¦ 기계설비 장비 제작사 ¦ 기계설비 장비 제작사 ¦ 기계설비 장비 제작사 ¦ 자동제어공사 ¦ 자동제어공사 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 항목 ¦ 자 체 제어반 ¦ 자체제어반 배선/배관 ¦ 제 어 용 접점제공 ¦ 인터페이스 통신제공 ¦ 제어용 제어반 ¦ 인터페이스 작업 ¦ ¦ 냉동기 ¦ ○ ¦ ○ ¦ ○ ¦ ○ ¦ ○ ¦ ○ ¦ ¦ 보일러 ¦ ○ ¦ ○ ¦ ○ ¦ ○ ¦ ○ ¦ ○ ¦ ¦ PAC ¦ ○ ¦ ○ ¦ ○ ¦ ○ ¦ ○ ¦ ○ ¦ ¦ 항온항습기 ¦ O ¦ O ¦ ○ ¦ ○ ¦ ○ ¦ O ¦ 주 1) 다만, 화재경보 및 제연에 필요한 배관 및 배선은 방재설비공사 업체에서 시공한다. 해 설 1. 본문 해설 및 관련 법규 표 4 이외의 단위시스템(수처리시스템, EHP 시스템, 환기유니트, 지열시스템, 빙축열시스템 등)이 자동제어와 연동되는 경우에는, 단위시스템의 데이터 송출부(컨트롤러의 통신포트 또는 접점)에 350 기계설비 기술기준 매뉴얼 | {}
d9beb737-4e0b-4bdc-8443-a6ee4d5f8dc9 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 서 자동제어 시스템으로 제공되는 통신 프로토콜이나 접점 확인이 필요함 2. 용어 V 내용 없음 3.4 원격검침설비 3.4.1 원격식 계량기(난방, 급탕) (1) 원격식 계량기와 스트레이너는 흐름의 방향과 계량기 외면에 표시된 화살표 방향이 일치되도록 설치한다. (2) 원격식 계량기와 스트레이너는 주배관에 수평으로 설치되도록 하며 스트레이너는 계량기 앞에 설치한다. (3) 원격식 유량계의 전후 직선 배관부의 최소 길이 ① 유량계 이전은 5D 이상 또는 설치유량계의 요구 직관 길이로 한다. ② 유량계 이후는 3D 이상 또는 설치유량계의 요구 직관 길이로 한다. (4) 무선형인 경우 무선모듈을 내장하여 검침데이터를 무선으로 세대 전송장치에 전송한다. 3.4.2 원격식 계량기와 세대 전송장치에 연결하는 전선의 보호장치 (1) 보호관의 과도한 밴딩을 금한다. 배관 호칭지름 축소 방지를 위하여 굴곡반경은 안지름 6 배 이상 유지하고 90°를 초과 해서는 안 된다. (2) 결선 후 제어선 각각에 열수축 튜브를 끼워 열을 가하여 기밀을 유지한다. 해 설 1. 본문 해설 및 관련 법규 V (3.4.1 1 항 ~ 3 항) 추가 설명 없음 V (3.4.2 1 항 ~ 3 항) 추가 설명 없음 2. 용어 V 내용 없음 국토교통부 351 기계설비 기술기준 해설 (별표 11) | {}
acbce8c1-e502-4cb3-81f3-7064cb99c8e1 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3.5 공동주택 자동제어설비 (1) 중앙감시반 3.1 에 따른다. (2) 현장제어반 3.3 에 따른다. (3) 온도조절기의 설치 수직, 수평으로 설치하고 센서 연결 시 주의 하여 기능에 지장이 없도록 한다. (4) 공동주택에서 전자식 원격검침시스템을 설치하는 경우, 패턴 변화 등에 따른 세대 누수(급수, 급 탕, 난방) 검지기능 시스템을 설치해야 한다. (5) 공동주택에서 열회수형 환기장치와 주방후드는 RS-232, RS-485, Modbus, BACnet 등의 통신 망을 이용하여 통합제어 되어야 한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항 ~ 3 항) 추가 설명 없음 V (4 항) 원격검침을 통한 유수 패턴변화로 누수 검지시스템은 현재 특허 출원이 되어있어 논란의 여지가 있으므로, 현장 여건에 맞게 선별적으로 적용할 수 있도록 함 V (5 항) 공동주택 세대 내에서 환기설비(열회수형 환기장치 등)와 주방후드가 연동 제어될 수 있도 록 시스템을 갖추어야 함 352 기계설비 기술기준 매뉴얼 | {}
2f81f59d-0a44-4038-9a95-f4ee0b3e79a4 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ RS-232 ¦ 미니컴퓨터나 마이크로컴퓨터 체계에 주로 사용되는 비동기식 전송을 위한 케이블 조직, 터미널 인쇄기, 플로터 같은 주변 장치들이 주 컴퓨터와 각각의 선으로 연결되 어, 데이터 통신을 할 수 있는 표준 장비를 말한다. 출처 : 지형 공간정보체계 용어사전 ¦ ¦ RS-485 ¦ RS-232, RS-422 의 확장 버전으로, 홈 네트워크를 지원하는 일종의 직렬 통신 프로토 콜 표준. RS-232 는 전송 속도가 낮고 전송 거리가 짧다. 이를 보완하기 위해 개발된 RS-422 는 한 개의 마스터 장치와 슬레이브 장치 간에 데이터를 주고 받는 방식으로 통신한다. 반면, RS-485 는 모든 장치들이 같은 라인에서 데이터 전송 및 수신을 할 수 있다. 통 상 2 개의 선을 사용하여 반이중(half duplex) 통신 방식으로 사용하나 2 개의 RS-485 통신망을 사용하면 전이중(full duplex) 통신도 가능하다. 이를 4 선(4-wire) 또는 전이 중 RS-485 라고 한다. 또한 RS-485 는 최대 드라이버·리시버 수가 각각 32 개에 이르고, 최대 속도 10Mbps 에 최장 거리 1.2km 까지 네트워크 구축이 가능하다 출처 : IT 용어사전, 한국정보통신기술협회 ¦ ¦ Modbus ¦ 정보·통신 공장 기반 제품들 사이에 정보를 교환하기 위하여 1978 년에 개발된 통신 규약. 데이터 교환 및 피엘시(PLC) 시스템들 사이의 통신 정보를 위한 표준 출처 : 네이버 국어사전 ¦ ¦ BACnet =빌딩 자동화 제어망 Building Automation and Control NETworks ¦ ANSI/ASHRAE 표준 135-1995 로 미국표준협회(ANSI)와 ASHRAE 에 의해 채택된 빌딩 자동화용 통신 프로토콜. 건물 자동 제어와 관련된 용도로 공조 장치 등의 빌딩 자동 화 시스템에서 주로 다루는 정보 처리에 대해 규정하고 있다. 서로 다른 제품들이 상 호 동작할 수 있도록 전송망을 다수 정의 함으로써 시스템 구축에 더 많은 유연성을 제공해 서로 다른 제품 상호 간에도 원활한 통신이 가능하다. 특징은 여러 종류의 랜 기술 사용, 18 가지 객체 정의, 객체를 통한 자료의 표현과 공유, 5 가지 범주의 32 가지 서비스 등을 표준화한 것이다. 출처 : IT 용어사전, 한국정보통신기술협회 ¦ 국토교통부 353 기계설비 기술기준 해설 (별표 11) | {}
c5cc4c33-de02-4aae-a994-6e433d61a44b | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 12] 방음 · 방진 · 내진 설비의 설계 및 시공 기준 1. 방음 · 방진 · 내진 설비 일반사항 1.1 목적 이 기준은 건축물, 시설물 등에 설치된 기계설비의 운전으로 인한 소음 , 진동의 발생과 전달 감소를 통하여 시설물의 수명 연장과 쾌적한 실내환경 조성, 그리고 지진으로 인한 기계설비의 파손 및 기능 상실 방지 등 안전 확보를 위하여 필요한 설계 및 시공 방법 등 세부 기술기준을 정함을 목적으로 한 다. 해 설 이 기준의 목적은 「기계설비법」 제 14 조(기계설비 기술기준)과 같은 법 영 제 2 조 및 [별표 1]에 근 거하여, 건축물이나 시설물에 필요한 방음 · 방진 · 내진 설비의 설계 및 시공 시 기계설비의 안전 과 성능을 확보하기 위하여 필요한 기술적 요건을 규정하기 위함 「기계설비법」 제 14 조(기계설비 기술기준) ① 국토교통부장관은 기계설비의 안전과 성능확보를 위하여 필요 한 기술기준(이하 "기술기준이라 한다)를 정하여 고시하여야 한다. 이를 변경하는 경우에도 또한 같다. 1.2 적용범위 이 기준은 건축물, 시설물 등에 방음 , 방진 、 내진설비를 설치하는 경우에 대하여 적용한다. 해 설 이 기준의 적용범위는 「기계설비법」 제 2 조제 1 호에 따른 건축물등에 같은 법 영 제 2 조에 따라 대 통령령으로 정한 방음 · 방진 · 내진 설비를 설치하는 경우 및 그와 관련된 부속설비들을 포함함 「기계설비법」 제 2 조(정의) 1. "기계설비"란 건축물, 시설물 등(이하 "건축물등"이라 한다)에 설치된 기계 · 기 구 · 배관 및 그 밖에 건축물등의 성능을 유지하기 위한 설비로서 대통령령으로 정하는 설비를 말한다. 「기계설비법 시행령」 제 2 조(기계설비의 범위) 「기계설비법」(이하 "법"이라 한다) 제 2 조제 1 호에서 "대통령령 으로 정하는 설비"란 별표 1 의 설비를 말한다. 「기계설비법 시행령」 [별표 1] 기계설비의 범위 10. 방음 · 방진 · 내진설비 : 건축물등에 설치된 기계 · 기구 · 배관 및 그 밖에 성능을 유지하기 위한 설비의 소음, 진동, 전도 및 탈락 등을 방지하기 위하여 설치된 설비 354 기계설비 기술기준 매뉴얼 | {}
237afbdd-dcff-4f11-aecd-58e3df9ecb36 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 1.3 타 규정과 의 관계 다음의 규정과 이 기준에서 정하는 내용이 상이한 경우에는 해당 규정을 따른다. (1) 「 주택건설기준 등에 관한 규정」 (2) KDS 31 50 15 방진설비 설계기준 (3) KDS 41 17 00 건축물 내진설계기준 (4) KCS 31 50 10 05 방음설비공사 표준시방서 (5) KCS 31 50 10 10 방진설비공사 표준시방서 해 설 V 이 기준과 타 규정 및 기준과 다른 경우에는 상기 규정에 명시된 내용을 따름 V 이외 관련 아래의 관련 기준을 따름 (6) KDS 31 50 10 방음설비 설계기준 (7) KDS 14 20 54 콘크리트용 앵커 설계기준 (8) KCS 31 50 10 15 내진설비공사 표준시방서 국토교통부 355 기계설비 기술기준 해설 (별표 12 | {}
df0292fe-b304-4316-aeb3-302970665d36 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 방음 · 방진 · 내진 설비 설계 2.1 방음설비 (1) 장비의 발생소음은 제조사의 발생소음을 기준으로 설계한다. (2) KCS 31 50 10 05(1.1) 표 1.1-1 에 따른 표 1 의 NC 실내허용소음기준에 따른 중심주파수별 값 이 하가 유지될 수 있도록 방음설비(흡음형소음기, 소음챔버, 능동형소음기, 흡음덕트 등)를 선정한 다. (3) NC 실내허용소음기준에 따른 중심주파수별 값은 KDS 31 50 10(4.3) 표 4.3-1 에 따른 표 2 와 같 다. 표 1 실내허용소음기준(KCS 31 50 10 05(1.1) 표 1.1-1) ¦ dB(A) ¦ 20 ¦ 25 ¦ 30 ¦ 35 ¦ 40 ¦ 45 ¦ 50 ¦ 55 ¦ 60 ¦ 70 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ NC ¦ 10-15 ¦ 15-20 ¦ 20-25 ¦ 25-30 ¦ 30-35 ¦ 35-40 ¦ 40-45 ¦ 45-50 ¦ 50-55 ¦ 60-65 ¦ ¦ 슴튬 ¦ 무향실 ¦ 아나운 서 스튜디 오 ¦ 랏디올 오 ¦ 스튬디 ¦ 주 조정실 ¦ 일반 사무실 ¦ ¦ ¦ ¦ ¦ ¦ 집회홀 ¦ ¦ 음악당 ¦ 극장 ¦ 무대극 장 ¦ 영화관, 과학관 ¦ 영화관, 과학관 ¦ 로비 ¦ ¦ ¦ ¦ ¦ 병원 ¦ ¦ 청력 시험실 ¦ 특별 병실 ¦ 수술실 병원 ¦ 진찰실 ¦ 검사실 ¦ 대합실 ¦ ¦ ¦ ¦ ¦ 호텔 주택 ¦ ¦ ¦ ¦ 서재 ¦ 침실 객실 ¦ 연회장로비 ¦ 연회장로비 ¦ ¦ ¦ ¦ 사무실 일반 응접실 일반사무실 전산실 소 회의 실 도서 공권자 공회당 무기관 열람실 체육관 옥내스포츠시설 학교회 음악 강당 연구실 교실 예배당 보통교실 ¦ 상업용 ¦ ¦ ¦ 음악당 서점 ¦ ¦ ¦ 공장 ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ ¦ ¦ ¦ 미술품점 ¦ 은행 레스토 랑 ¦ 사정 ¦ 제어낼 ¦ 복도 표 2 NC 소음기준별 중심주파수 음압레벨(KDS 31 50 10(4.3) 표 4.3-1) ¦ NC-곡선 ¦ 1/1 옥타브밴드 중심주파수(Hz) ¦ 1/1 옥타브밴드 중심주파수(Hz) ¦ 1/1 옥타브밴드 중심주파수(Hz) ¦ 1/1 옥타브밴드 중심주파수(Hz) ¦ 1/1 옥타브밴드 중심주파수(Hz) ¦ 1/1 옥타브밴드 중심주파수(Hz) ¦ 1/1 옥타브밴드 중심주파수(Hz) ¦ 1/1 옥타브밴드 중심주파수(Hz) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ NC-곡선 ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1k ¦ 2k ¦ 4k ¦ 8k ¦ ¦ NC-65 ¦ 80 ¦ 75 ¦ 71 ¦ 68 ¦ 66 ¦ 64 ¦ 63 ¦ 62 ¦ ¦ NC-60 ¦ 77 ¦ 71 ¦ 67 ¦ 63 ¦ 61 ¦ 59 ¦ 58 ¦ 57 ¦ ¦ NC-55 ¦ 74 ¦ 67 ¦ 62 ¦ 58 ¦ 56 ¦ 54 ¦ 53 ¦ 52 ¦ ¦ NC-50 ¦ 71 ¦ 64 ¦ 58 ¦ 54 ¦ 51 ¦ 49 ¦ 48 ¦ 47 ¦ ¦ NC-45 ¦ 67 ¦ 60 ¦ 54 ¦ 49 ¦ 46 ¦ 44 ¦ 43 ¦ 42 ¦ ¦ NC-40 ¦ 64 ¦ 56 ¦ 50 ¦ 45 ¦ 41 ¦ 39 ¦ 38 ¦ 37 ¦ ¦ NC-35 ¦ 60 ¦ 52 ¦ 45 ¦ 40 ¦ 36 ¦ 34 ¦ 33 ¦ 32 ¦ ¦ NC-30 ¦ 57 ¦ 48 ¦ 41 ¦ 35 ¦ 31 ¦ 29 ¦ 28 ¦ 27 ¦ ¦ NC-25 ¦ 54 ¦ 44 ¦ 37 ¦ 31 ¦ 27 ¦ 24 ¦ 22 ¦ 21 ¦ ¦ NC-20 ¦ 51 ¦ 40 ¦ 33 ¦ 26 ¦ 22 ¦ 19 ¦ 17 ¦ 16 ¦ ¦ NC-15 ¦ 47 ¦ 36 ¦ 29 ¦ 22 ¦ 17 ¦ 14 ¦ 12 ¦ 11 ¦ 356 기계설비 기술기준 매뉴얼 | {}
8c3e7f14-b411-4f2e-9ee2-1bdd3c5b4029 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 해 설 1. 본문 해설 및 관련 법규 V (1 항) 제조사의 발생 소음 기준 「KDS 31 50 10 방음설비 설계기준」 4.2 장비 발생소음 산정 1) 장비의 발생소음은 제조사의 발생소음을 기준으로 설계한다. 단 제조사의 발생소음자료를 얻을 수 없는 경우에는 대한설비공학편람 제 3 권, SMACNA HVAC sound and vibration manual 또는 ASHRAE Handbook HVAC Application 의 장비 발생소음 계산식을 참조한다. V (2 항) 방음설비 선정 「KCS 31 50 10 05 방음설비공사」 1.1 적용범위 (1) 이 기준은 공조용 소음기, 소음챔버 및 방음루버의 설계 및 제작, 시공 등의 방음공사에 적용한다. -방음설비의 대상은 흡음형소음기, 소음챔버, 능동형소음기, 흡음덕트 및 방음루버 등 공조용으로 적용되 는 방음장치를 의미한다. (3) 공조용 소음기, 소음챔버 및 방음루버를 설계 할 시에는 각 실의 특성에 따라 권장하는 NC(Noise Criteria) 레벨을 초과 하지 않도록 설계를 하고 시공한다. 또한, 방음설계 시 유효 안전치 5 dB 를 가한 후 예상치 못한 소음에 대해 안전값을 두어야 한다. (4) 덕트 소음기의 승인도면에는 권장하는 NC 레벨에 유효 안정치 5 dB 을 감안한 소음기 선정계산서가 첨 부되어야 한다. NC 레벨의 기준치는 아래 표 1.1-1 에 준한다. - 표 1 실내허용소음기준은 실용도에 따라 상기 표에 해당하는 실내허용 소음을 참조하여 설계하며 방음 계산시에는 유효 안전치 5 dB 를 가만하여 적용한여야 한다. V (3 항) NC 실내허용소음기준 「KDS 31 50 10 방음설비 설계기준」 4.3 실내 허용소음 기준 결정 (1) 실 용도에 맞는 실내 허용소음기준을 적용하며 그 기준은 NC (Noise Criteria)실내 허용소음기준을 원칙 으로 한다. 단 건축물 설계요구서에 의해 다른 기준 (NR, PNC 등)을 적용하여 계산 할 수 있다. (2) NC 실내 허용소음기준에 따른 중심주파수별 값 이하가 유지될 수 있도록 덕트 소음기를 선정하여야 한 다. 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ NC 실내 허용 소음 기준 ¦ NC 는 건물의 용도별로 어느 정도 소음의 크기가 그 실의 기능에 지장을 주지 않는가 에 대해 소음의 변동정도, 노출시간대 및 주파수별 청감을 고려하여 제안되었다. 미 국에서는 NC 기준을 사용하고 유럽에서는 NR 기준을 사용하며 거의 유사하게 적용된 다.(상기 표는 NC 소음기준곡선별 1/1 중심주파수 음압레벨) 출처 : 설비공학편람 제 3 권 공기조화 응용 제 6 편 29 장 소음과 진동 제어 ¦ 국토교통부 357 기계설비 기술기준 해설 (별표 12 | {}
0aad5e5c-9272-4f70-8c18-c7674043eba5 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2.2 방진설비 (1) 장비의 강제진동수 및 장비발생진동레벨은 제조사의 강제진동수 및 장비발생진동레벨을 기준으 로 설계한다. (2) 방진기의 수량은 장비의 설치 형상, 무게중심의 위치 등에 따라 다르므로 제조사의 고정 위치 및 수량 자료를 근거로 편심이 최소화 되도록 적용한다. (3) 방진 스프링 행거는 격리 된 장비 또는 천장 설치형 장비의 움직임을 최소화하기 위하여 천장면 에 가깝게 설치하고 사전 스프링을 압축하고 전산로드를 고정 할 수 있도록 설계 적용한다. (4) 입상배관의 열팽창 및 수축으로 인한 변형량은 방진 스프링 지지에서 추가 변위량을 수용할 수 있도록 설계한다. (5) 배관의 진동은 배관 플렉시블 커넥터와 방진행거, 입상방진 스프링에서 진동을 제어할 수 있도록 적용한다. 해 설 1. 본문 해설 및 관련 법규 (1 항) 강제진동수 및 장비발생진동레벨을 기준으로 설계 ![image](/image/placeholder) 「KDS 31 50 15 방진설비 설계기준」 4.1 방진설비 설계절차 장비 강제진동수 회전수(RPM) 장비 발생진동레벨 예측 제품중량, 베이스, 보유수 중 장비운전하중 량, 기동시 반력, 기타 배관 부속 장치류 스프링 방진기 & 행거 방진고무 마운트 방진기 수량 및 지지개수, 방진기 모델 선정 방진패드 위치 선정 이중바닥 시스템 방진기 운전 변위량 및 고유진동수 산출 진동 전달을 및 방진기 진동저감량 계산 방진 효율 상출 장비 발생 진동레벨 바닥의 진동레벨 예측 -방진기 진동저감량 V (2~3 항) 추가 설명 없음 V (4 항) 추가 변위량을 수용할 수 있도록 설계함 358 기계설비 기술기준 매뉴얼 | {}
b8d9906b-12a5-4afb-aa52-58c584ce0755 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 「KDS 31 50 15 방진설비 설계기준」 4.10 방진 설계 시 유의 사항 (4) 입상배관의 방진 앵커, 방진 가이드들은 배관의 좌굴을 방지하고 진동으로 발생한 구조체 전달음 저감하 기 위하여 적절하게 설치층을 배분하고 방진 스프링과 조합하여 적용한다. (5) 입상배관의 열팽창 및 수축으로 인한 변형량은 방진 스프링 지지에서 추가 변위량을 수용 할 수 있도록 설계하며 다음 식으로 구한다. E= 1,000Lx Cx △t (4.10-1) 여기서, E : 배관의 팽창량(mm) L : 배관의 길이(m), ⌀: 평균열팽창계수(mm/mm°C) △t : 온도변화(최종온도-초기온도, °C) V (5 항) 배관의 진동 제어 「KDS 31 50 15 방진설비 설계기준」 4.10 방진 설계 시 유의 사항 (8) 장비에 의해 발생 된 기계적 진동과 유체 유동 진동 및 소음이 배관을 통해 전달되지 않도록 장비 최 근 접 위치에 플렉시블커넥터를 설계 적용한다. (9) 배관의 진동은 유연한 배관 플렉시블 커넥터와 방진행거, 입상방진 스프링에서 진동을 제어 할 수 있도 록 설계 적용해야 한다. 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 강제진동수 ¦ 장비의 강제진동수(fg)는 장비의 분당회전수(rpm)로부터 다음 식에 의해 구한다. fa = rpm /60 (Hz) 출처 : KDS 31 50 15 방진설비 설계기준 4.2 ¦ ¦ 장비발생 진동레벨 ¦ 장비 진동레벨의 감각보정회로를 통하여 측정된 진동가속도레벨의 지시치로서 장비 발생진동레벨(VAL)은 다음 식을 이용하거나 설계자의 계산 방식에 따라 산출한다. Arms VAL = 20log (dB) Are f 여기서 Arms : 측정대상 진동의 가속도 실효치(m/s2) Are f : 기준 진동의 가속도 실효치(10-5 m/s2) 출처 : KDS 31 50 15 방진설비 설계기준 4.2 ¦ 기계설비 기술기준 해설 (별표 12 국토교통부 359 | {}
dfd29ad8-45bf-4103-b98c-388c26db542b | 국내_기계설비_기술기준_매뉴얼_최종본 | 2.3 내진설비 (1) 지진발생 시 전도 및 탈락으로 인하여 내 、 외부의 인명에 손상을 줄 수 있는 기계설비는 내진설 비에 의하여 안정성을 확보해야 한다. (2) 기계설비의 지지부, 정착부, 연결부 등이 지진거동에 의한 수평력인 등가정적하중과 상대변위에 견디도록 설계되어야 한다. (3) 설계의 적정성은「건축법」시행령 제 91 조의 3 제 2 항제 2 호에 따른 관계전문기술자와 협의 해야 하 며, 내진설계 책임구조기술사가 승인해야 한다. (4) 내진설비 적용범위 ① 기계설비 내진설비 기준은 KDS 41 17 00(18.4)에 따르며, 중요도계수(�)가 1.5 인 다음의 기계 설비로 한정한다. 가. 인명안전 등을 위해 지진 후에도 반드시 기능해야 하는 기계설비 나. 내진특등급에 해당하는 구조물에서 시설물의 지속적인 기능수행을 위해 필요하거나 손상 시 시설물의 지속적인 가동에 지장을 줄 수 있는 기계설비 ② 위의 규정에 속하지 않는 기계설비 내진설계는 건축주(발주자)와 협의 에 따른다. (5) 등가정적하중의 산정 지진발생 시 수평진동으로 인하여 장비가 흔들리거나 설치 위치의 이동이 발생하는데 이때 장비를 거동시키는 동적에너지를 정적에너지로 등가화하여 산정한 것이 등가정적하중이며, KDS 41 17 00(내진설계기준)에 따라 설계해야 한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 추가 설명 없음 V (2 항) 기계설비의 내진은 등가정적하중과 상대변위에 견디도록 설계함 「KDS 41 17 00 건축물 내진설계기준」 18.4.1 기계 및 전기 비구조요소 일반사항 기계 및 전기 비구조요소와 그 지지부는 18.4 의 규정에 따라 설계하여야 한다. 설계계수는 표 18.4-1 중 적 절한 값을 선택한다. 기계 및 전기 비구조요소의 지지부와 정착부는 18.5 의 규정을 따른다. 「KDS 41 17 00 건축물 내진설계기준」 18.4.2.3 지지부 (1) 기계 및 전기비구조요소의 지지부가 표준규격을 따를 경우, 지지부는 실험을 통해 결정된 정격하중 혹은 기준에 의한 지진하중 중의 하나를 사용하여 설계할 수 있다. 또한 설계 시 가정과 같이 하중이 전달되게 하기 위해 필요할 경우 지지부의 강성도 설계되어야 한다. (2) 지지부는 18.2.3 에 의해 산정되는 각 지점사이의 상대변위를 수용할 수 있게 설계되어야 한다. V (3 항) 관계 전문기술자 협의 360 기계설비 기술기준 매뉴얼 | {}
f2105a0a-b93a-40dd-b92f-c8ad2b7235fa | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 「건축법 시행령」 제 91 조의 3(관계전문기술자와 의 협력) ① 생략 ② 연면적 10 000 m2 이상인 건축물(창고시설은 제외한다) 또는 에너지를 대량으로 소비하는 건축물로서 국 토교통부령으로 정하는 건축물에 건축설비를 설치하는 경우에는 국토교통부령으로 정하는 바에 따라 다 음 각 호의 구분에 따른 관계전문기술자의 협력을 받아야 한다. 2. 급수 · 배수(��) · 배수(��) · 환기 · 난방 · 소화 · 배연 · 오물처리 설비 및 승강기(기계 분야만 해당한 다): 「기술사법」에 따라 등록한 건축기계설비기술사 또는 공조냉동기계기술사 「KDS 41 17 00 건축물 내진설계기준」 18.1.3.3 설계의 검토와 승인 개별 비구조요소의 공인된 설계기준에 따라 내진설계를 수행하고 내진설계책임구조기술자가 이를 승인하는 경우 비구조요소의 내진설계는 구조체의 내진설계와 분리하여 수행될 수 있다. 이때 설계계산서 혹은 시험 성적서를 근거로 시공상세도가 작성되어야 하며 내진설계책임구조기술자에 의해 검토 및 승인되어야 한다. V (4 항) 내진설비 적용범위 「KDS 41 17 00 건축물 내진설계기준」 18.1.1 적용범위 (1) 중요도계수 I 가 1.5 인 비구조요소 (2) 파라펫, 건물외부의 치장 벽돌 및 외부치장마감석재 위의 규정에 속하지 않는 비구조요소의 내진설계 여부는 건축주와 의 협의 에 따른다. 「KDS 41 17 00 건축물 내진설계기준」 18.1.2 중요도계수 비구조요소의 중요도계수 Ip 는 1.0 으로 한다. 단, 다음에 해당할 경우 Ip 를 1.5 로 한다. (1) 소화배관과 스프링클러 시스템 등 인명안전을 위해 지진 후에도 반드시 기능하여야 하는 비구조요소. 또 한 피난경로상의 계단, 캐노피, 비상유도등, 중량칸막이벽 등 손상시 피난경로확보에 지장을 주는 비구조 요소와 대형 창고형 매장 등에 설치되어 일반대중에게 개방된 적재장치 (2) 규정된 저장용량 이상의 독성, 맹독성, 폭발위험 물질을 저장하거나 지지하는 비구조요소 (3) 표 2.2-1 의 내진특등급에 해당하는 구조물에서 시설물의 지속적인 기능수행을 위해 필요하거나 손상시 시설물의 지속적인 가동에 지장을 줄 수 있는 비구조요소 V (4 항) 내진등급 설정의 일반적인 기준 표 2.2-1 내진등급과 중요도계수 ¦ 건축물의 중요도 1) ¦ 내진등급 ¦ 내진설계 중요도계수(I�) ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 중요도(특) ¦ 특 ¦ 1.5 ¦ ¦ 중요도(1) ¦ I ¦ 1.2 ¦ ¦ 중요도(2), (3) ¦ II ¦ 1.0 ¦ ¦ 1) KDS 41 10 05(3.)에 따름. ¦ 1) KDS 41 10 05(3.)에 따름. ¦ 1) KDS 41 10 05(3.)에 따름. ¦ V (5 항) 등가정적하중 계산식에 따른 설계지진력 계산 기계설비 기술기준 해설 (별표 12 국토교통부 361 | {}
6e8fe8a1-3aea-4314-bffe-1aeeebedfc1a | 국내_기계설비_기술기준_매뉴얼_최종본 | 「KDS 41 17 00 건축물 내진설계기준」 18.2.1 등가정적하중 18.2.1.1 수평설계지진력 지진에 의한 수평방향 등가정적하중 는 식 (18.2-1)에 의하여 산정한다. 지진하중이 아닌 다른 하중이 Fp 를 초과 하여 그에 따라 설계될 경우에도 이 절의 상세나 제한규정은 적용되어야 한다. 0.4ap SDS Wp Fp 1+2 름) Rlp Fp 는 다음의 값을 초과 할 필요는 없다. Fp = 1.6SDs Ip Wp 그러나 는 다음의 값 이상이 되어야 한다. Fp = 0.3 SDs Ip Wp 여기서, Fp : 비구조요소 질량 중심에 작용하는 설계지진력 ap : 비구조요소의 증폭계수(표 18.3-1 또는 표 18.4-1) Ip : 비구조요소의 중요도계수 h : 구조물의 밑면으로부터 지붕층의 평균높이 Rp : 표 18.3-1 또는 표 18.4-1 에 규정된 비구조요소의 반응수정계수 SDS : 4.2 에 따라 결정한 단주기에서의 설계스펙트럼가속도 Wp : 비구조요소의 작동상태를 고려한 중량 2 : 구조물의 밑면으로부터 비구조요소가 부착된 높이 2 = 0 : 구조물의 밑면 이하에 비구조요소가 부착된 경우 z = h : 구조물의 지붕층 이상에 비구조요소가 부착된 경우 (18.2-1) (18.2-2) (18.2-3) 2. 용어 V 내용 없음 --- --- ---- 362 기계설비 기술기준 매뉴얼 | {}
53ddbc13-7bc6-4e09-875c-54985d276fd2 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 3. 방음 · 방진 · 내진 설비 시공 3.1 방음설비 (1) 덕트 소음기 및 소음챔버와 덕트의 연결부분은 기밀유지가 되어야 한다. (2) 덕트 소음기 및 소음챔버를 천장에 행거로드로 연결할시 하단부에 '�'앵글, 또는 'C '찬넬 등의 철재류 틀로 설치한다. (3) 가능한 소음기의 위치는 공조실 내부에 설치되도록 하며, 공조실 내부에 설치되지 않는 경우 덕 트투과 소음 저감대책을 수립한다. (4) 건축의 벽체 개구부에 설치되는 방음루버는 벽면과 의 틈새가 없도록 충진재를 채워 넣고 실리콘 실란트로 충진한다. (5) 덕트 소음기, 소음챔버 및 방음루버의 치수 검사를 실시할 때는 각각의 치수에 대한 허용오차는 제시된 치수에 ±5% 이내이어야 한다. (6) 「주택건설기준 등에 관한 규정」 제 43 조에 따라 공동주택의 배수용 배관을 층하배관공법(배관을 바닥 슬래브 아래에 설치하여 아래층 세대 천장으로 노출시키는 공법을 말한다)으로 설치하는 경 우에는 일반용 경질염화비닐관을 설치하는 경우보다 같은 측정조건에서 5 데시벨 이상 소음 차단 성능이 있는 저소음형 배관을 사용해야 한다. 해 설 1. 본문 해설 및 관련 법규 (1 항 ~ 2 항, 5 항) 추가 설명 없음 V (3 항) 덕트투과 소음저감대책 수립 「KCS 31 50 10 05 방음설비공사」 3.1 시공 일반 (3) 가능한 소음기의 위치는 공조실 내부에 설치되도록 한다. 부득이 공조실의 벽체에 걸쳐 지거나 실내의 천정에 설치 될 경우에는 덕트 투과 소음에 대한 저감대책을 위하여 공조기와 소음기 연결 구간 및 소음기 이후의 일정구간까지 덕트 표면에 2 mm 차음시트를 설치한다. 4) 소음기 내부의 기류통과 유속에 의한 자생 소음에 대한 저감대책을 위해 2 mm 차음시트를 챔버나 덕트 표면에 설치한 후 유리섬유 밀도 48 kg/m2 로 외부 보온마감을 실시하도록 한다. V (4 항) 충진재를 채워 놓고 실리콘 실란트로 충진 「KCS 31 50 10 05 방음설비공사」 3.1 시공 일반 (5) 소음기가 벽체에 걸쳐 있을 경우 기류흐름에 발생된 진동과 공조기의 진동전달로 공조실 벽면의 진동 발 생 요인이 될 수 있으므로 벽체와 20 mm 이상의 공간이 있어야 하고 그 공간에는 충진재(유리섬유 밀도 48 kg/m2 이상)를 채워 넣고 양쪽 표면에 실리콘 실란트로 충분히 채워 넣고 마감한다. ![image](/image/placeholder) 구조벽체 건축벽체 실란트 코킹 건축벽체 실리콘 마감 (D 20mm 이상) 20 백업재 충진 15 방음루버 소음기 G/W or P/E 흡음재 스플리터 (32K 이상) 방음루버 공기층 -소음기 및 방음루버 설치 단면- 기계설비 기술기준 해설 (별표 12 국토교통부 363 | {}
c633b8c3-ff87-40e6-8e54-479af30ed83c | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 용어 내용 없음 3.2 방진설비 3.2.1 냉동기 및 냉 , 온수 유닛 (1) 장비의 하중이 방진장치에 균등하게 작용하여 설치된 네오프렌패드의 변위가 일어나는지를 확 인한다. (2) 방진스프링 마운트를 사용한 경우에는 수평계를 이용하여 레벨조절을 실시하며 임시로 고정된 고정대는 레벨조절이 완료되면 제거하여 방진 기능이 상실되지 않도록 확인한다. 해 설 1. 본문 해설 및 관련 법규 (1 항) 네오프렌패드 「KCS 31 50 10 10 방진설비공사」 2.1.1 바닥설치형 (5) 기초 콘크리트 패드와 접촉되는 하부 하우징에는 3~6 mm 두께의 KS M 6617 로 성형한 네오프렌 패드 가 부착되어 기초 콘크리트 패드와 격리시켜야 한다. ![image](/image/placeholder) 방진패드 -장비 하부 방진패드 설치 도면 및 설치 모습- V (2 항) 방진스프링 마운트 364 기계설비 기술기준 매뉴얼 | {}
64811f3b-a564-46da-a509-d3834ce68b0f | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 ![image](/image/placeholder) 플렉시블 커넥터 56 제한형 스프링 방진마운트 -장비 하부 스프링 방진스프링 마운트 설치 도면 및 설치 모습- 2. 용어 내용 없음 3.2 방진설비(계속) 3.2.2 냉각탑 (1) 냉각탑에 설치되는 방진스프링은 운전 하중의 변화를 흡수하기 위하여 높이제한 장치를 갖춘 방 진장치를 설치한다. (2) 냉각탑용 스프링의 하중은 위치별 각각의 하중이 서로 다르므로 설계 및 승인자료를 충분히 검토 한 후 설계된 위치에 적절한 방진장치를 배열하여 설치한다. (3) 냉각탑용 방진스프링의 앵커볼트 삽입 깊이는 최소 50 mm 이상 기초콘크리트에 매설한다. 해 설 1. 본문 해설 및 관련 법규 (1 항) 높이제한 장치를 갖춘 방진장치 ![image](/image/placeholder) 제한형 스프링마운트 사례 수직변위를 제한하기 위한 제한볼트가 있으며 배관이나 장비의 설치 시 중량과 운전 시 중량이 크게 변화는 경우 배관에 작용하는 응력을 최소화하기 위하여 사용 (2 항) 적절한 방진장치를 배열하여 설치하고, 냉각탑과 연결되는 부위에는 고무 커넥터, 플렉시블 호스커넥터, TPC 등을 설치함 국토교통부 365 기계설비 기술기준 해설 (별표 12 | {}
c140ada7-460a-42c8-b56f-12fbad2a88a3 | 국내_기계설비_기술기준_매뉴얼_최종본 | 「KCS 31 50 10 10 방진설비공사」 2.2 냉각탑 방진 (2) 냉각탑은 장비의 가동 시(on)와 정지 시(off) 그리고 동절기 물을 배수함으로써 발생하는 중량변화로 인 해 배관 연결 부위에 손상을 입힐 수 있으므로 수직이동 제한장치가 있는 수직 제한형 방진 스프링마운트 를 설치한다. ![image](/image/placeholder) Ⓡ (5) 냉각탑과 연결되는 부위에는 네오프렌 합성고무 커넥터를 설치한다. (6) 냉각탑은 옥외에 노출되어 설치됨으로 냉각탑을 지지하는 방진스프링 마운트 및 하우징에 내산성 및 내 후성이 좋은 재료로 도장한다. (3 항) 추가 설명 없음 2. 용어 내용 없음 3.2 방진설비(계속) 3.2.3 공기조화기 및 송풍기 (1) 공기조화기 및 송풍기에 사용되는 방진스프링은 각각의 하중이 서로 다르므로 설계 및 승인자료 를 검토한 후 설계된 위치에 적절한 스프링 마운트를 배열하여 설치한다. (2) 공기조화기 및 송풍기에 사용하는 방진장치나 방진고무는 어느 한쪽에 과도한 응력이 가해지지 않도록 레벨 조정기기를 사용하여 조정한다. (3) 송풍기의 전압의 대소에 따라 상당히 큰 수평밀림이 발생될 수 있음으로 장비 내부 부속장치를 보호하기 위하여 수평밀림 방진기를 장비 중앙 위치에 정확히 설치한다. (4) 방진스프링을 설치한 후 수평계를 이용하여 레벨조절을 실시하며 임시로 고정된 고정대는 레벨 조절이 완료되면 제거하여 방진 기능이 상실되지 않도록 확인한다. (5) 방진스프링 하부 앵커볼트의 삽입 깊이는 최소 50 mm 이상 기초 콘크리트에 매설한다. 해 설 1. 본문 해설 및 관련 법규 (1 항 ~ 2 항) 추가 설명 없음 V (3 항) 수평밀림방지기 설치 366 기계설비 기술기준 매뉴얼 | {}
aba8e866-4301-495a-bed4-7436d0270905 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 송풍기의 구동부와 연결덕트부에 유연한 이음부재로 연결된 경우 수평밀림 힘을 제어 할 수 있도록 수평 밀 림방지기를 설치한다. ![image](/image/placeholder) -수평밀림방지기- ![image](/image/placeholder) -수평밀림방지기 적용 사례- V (4 항 ~ 5 항) 3.2.2 참조 2. 용어 내용 없음 ---- -- 3.2 방진설비(계속) 3.2.4 기계실 배관 및 덕트 (1) 배관이나 덕트에 설치될 방진행거나 방진마운트는 설계도서와 방진 효율 계산서를 보고 설치한 다. (2) 배관의 열팽창과 수축이 심한 곳에 설치하는 방진마운트는 수축과 팽창을 흡수할 수 있는 정적변 위를 가진 마운트이어야 하고, 강성이 있는 철구조물과 함께 설치한다. (3) 배관계통이나 덕트계통에 설치한 방진기의 정적 처짐이 적절하게 변위가 되고 있는지 육안으로 확인한다. (4) 방진스프링 행거로 배관이나 덕트를 지지할 경우에는 행거로드가 수직이 되도록 한다. 설치 여건 이 수직으로 할 수가 없을 경우에는 배관이나 덕트를 좌우로 흔들어 스프링이 배관 및 덕트에 접 촉이 되지 않는 것을 확인하고, 스프링이 이탈하지 않는 것을 반드시 확인한다. 해 설 1. 본문 해설 및 관련 법규 (1 항) 방진 효율 계산서 국토교통부 367 기계설비 기술기준 해설 (별표 12 | {}
8aaf72f0-e71e-4e76-b86d-2d8bf1e67ad3 | 국내_기계설비_기술기준_매뉴얼_최종본 | ![image](/image/placeholder) ○설 치지구명 테스트단지 ○설 계일시 1999.6.11 ○장비번호 o 주 요제원 흡입관경 토 출관경 양 정 동 력 ) 1 강제 진동수 회전수 (Hz) 2. 장비 중량 (카탈로그상의 중량) g (kg) 3.베이스규격 (kg) 4.보유수 중량 (장비중 량의 30%) (kg) 5.토출수압중량 관경 양정 (kg) 6.운전중량 (2+3+4+5)*안전율(1,3) (kg) 7. 방진재 모델 방진재 갯수 (개) 방진재 종류 개당 담당중 량 (kg) 선정 방진재의 담당 중량 (kg) * 개당 사용하중은 1DD /150/200/300/500/750/1000 에서 직상 규격 산정 8.스프링상수 방진재 변위 량 (mm) (kg/mm) * KS 1653 의 밀폐형 방진기는 변위가 25mm 임, 시중 스프링 방진재는 일반적으로 변위량 25mm. 9.정적변위량 운전시 변위량 : (방진재지지중량/ 스프링상수) (m ) 정지시 변위량 ) 10,고유진동수 *fn=15.7V(1/8) (Hz) 11.진동수비 *f/fn 값이 3 보다 크거나 같으면 유효 12.전달율(T) 13.방진효율 * 방진 효율이 80% 이상이면 유효 (%) 14,소음감쇠량 (dB) 15.결과 차진레 벨(dB) 방진재 규격(kg) 수량(개) 정적변위 진동수비 방진 효율 주) : 사용자 입력창, : 계산결과 출력창 출처 : 방진설계 표준 양식 - 설비 기계실의 방음 · 방진 설계지침에 관한 연구(대한주택공사 주택연구소) V (2 항) 수축과 팽창을 흡수할 수 있는 정적변위를 가진 마운트 ![image](/image/placeholder) ![image](/image/placeholder) -변위조절이 가능한 방진마운트 수평배관 설치 모습- V (3 항 ~ 4 항) 추가 설명 없음 2. 용어 내용 없음 368 기계설비 기술기준 매뉴얼 | {}
248bedb3-aa18-4aac-8f93-70935bc4a969 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 3.2 방진설비(계속) 3.2.5 입상배관 (1) 입상배관의 설계도서 및 승인자료를 기준으로 설치한다. (2) 입상배관에 설치되는 앵커지점은 입상배관의 정적하중과 동적하중(수축 및 팽창력, 좌굴응력 등), 기타 모든 응력이 작용하는 기준지점으로 고정시켜야 한다. 앵커지점에 설치되는 클램프는 입상배관 표면에 용접을 한다. (3) 방진스프링마운트의 설치 시 입상배관의 수축과 팽창으로 발생되는 응력과 배관자중을 지지하 기 위하여 클램프와 배관 표면에 점용접을 한 후 양쪽의 클램프 체결볼트를 조여 준다. (4) 입상배관에 방진장치를 설치한 후 해당 층에 설치되어 있는 스프링 마운트의 변위를 조절한다. 그러나 과도한 힘을 가하여 앵커지점에 그 응력이 가해지지 않도록 유의 한다. 해 설 1. 본문 해설 및 관련 법규 (1 항) 추가 설명 없음 V (2 항) 앵커지점 「KCS 31 50 10 10 방진설비공사」 2.6 입상배관 방진장치 (2) 앵커지점에는 배관 및 물 무게를 고려한 전체하중이 충분히 지지 될 수 있도록 방진클램프와 방진기를 적용하여 고정한다. (3) 앵커 방진기 내부에는 고하중 네오프렌으로 분리되어 있고, 압축 전단 하중을 충분히 받을 수 있어야 하 며, 표준 정적변위는 2~3 mm 이내이어야 한다. ![image](/image/placeholder) 고하중 네오프렌 -방진기 하단과 입상배관가대, 배관과 방진클램프 용접- - 앵커 방진기 - (3 항) 입상관 방진 마운트의 설치 「KCS 31 50 10 10 방진설비공사」 2.6 입상배관 방진장치 (4) 방진스프링의 정적변위는 최소 50 mm 개방형 스프링 마운트를 사용하고, 입상배관의 앵커지점으로 집 중되는 배관의 정적하중 및 동적하중을 좌우 스프링마운트가 가진력 및 진동을 흡수하도록 한다. ![image](/image/placeholder) 스프링 하부 용접 ![image](/image/placeholder) 방진스프링 레벨링 방진 스프링 설치 완료 - - 방진 스프링 마운트 설치 모습 국토교통부 369 기계설비 기술기준 해설 (별표 12) | {}
aa86691d-dead-48d7-a3f0-6c508e29550d | 국내_기계설비_기술기준_매뉴얼_최종본 | V (4 항) 스프링마운트의 변위 「KCS 31 50 10 10 방진설비공사」 3.6 입상배관 방진장치 (4) 입상배관에 방진장치를 설치 한 후 해당 층에 설치되어 있는 스프링 마운트를 적절히 조절한다. 그러나 과도한 힘을 가하여 앵커지점에 그 응력이 가해지지 않도록 유의 한다. (5) 가이드 방진기를 설치하기 위한 클램프는 그 내부의 가이드 바와 배관 바깥지름이 2~3 mm 의 간격을 유 지할 수 있도록 설치한다. ![image](/image/placeholder) 조정 변위 수 + ◇ ◇ 수 ◇ ◆ � + � SPRING SLAB SLAB 레벨 조정전 레벨 조정후 -스프링 방진기의 레벨조정- ![image](/image/placeholder) -방진클램프 내부 가이드 바 부착형 설치모습- 2. 용어 내용 없음 3.2 방진설비(계속) 3.2.6 펌프 관성베이스 (1) 펌프 기초 콘크리트 표면에 50 mm 높이의 벽돌 또는 단단한 각목을 놓고 그 위에 관성베이스를 설치한다. (2) 설계도서 및 방진계산서에 따른 방진마운트를 각각의 위치에 설치한 후, 바닥에 앵커볼트로 방진 마운트를 고정시킨다. (3) 콘크리트 레미콘 또는 레미탈을 관성베이스에 넣고, 관성베이스의 배수구가 콘크리트에 매설되 지 않도록 한다. (4) 플렉시블 커넥터에는 장비 또는 배관의 하중이 작용하지 않아야 한다. (5) 펌프의 연결된 커넥터 이전 배관의 지지는 방진베이스 내에 설치한다. 해 설 1. 본문 해설 및 관련 법규 (1 항) 관성베이스 설치 370 기계설비 기술기준 매뉴얼 | {}
674fdade-adc7-421e-8db9-42434a203072 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 「KCS 31 50 10 10 방진설비공사」 2.7 펌프관성베이스 방진 (1) 펌프의 운전 시 발생되는 진동을 흡수 및 차단하기 위하여 관성베이스를 사용한다. 이 관성베이스는 펌 프 및 모터의 무게보다 최소 2~5 배의 하중을 갖는 유근 콘크리트 관성베이스로 한다. (2) 콘크리트 유근 관성베이스는 방진스프링 KS B 1563 방진스프링마운트로 지지하도록 한다. 지상층에 펌 프가 설치될 경우에는 해당 층 바닥의 건축구조물 정적 처짐보다 최소 1 배 이상의 정적변위를 갖는 스프 링 마운트를 사용한다. ![image](/image/placeholder) -펌프방진베이스 설치모습-KS B 1563(개방형)- 펌프방진베이스 설치모습-KS B 1563(밀폐형)- (2 항) 추가 설명 없음 V (3 항) 관성베이스 작업 「KCS 31 50 10 10 방진설비공사」 3.7 펌프관성베이스 방진 장치 (4) 양생이 잘 된 것을 확인 후 펌프를 설치한다. 또는 펌프 설치를 한 후 콘크리트를 타설하여도 무방하다. 다만 관성 베이스 내 콘크리트가 충분히 양생된 후 후속작업을 진행한다. (5) 콘크리트 타설시 콘크리트가 방진 스프링 마운트 속으로 들어가지 않도록 비닐 등으로 잘 보호한다. ![image](/image/placeholder) 0 콘크리트 타설 콘크리트 타설 비닐 밀봉 펌프 드레인 (05) 비닐 밀봉 장비 기초 콘크리트 임시받침대 콘크리트 양생 방진스프링 마운트 -펌프 방진베이스 내 콘크리트 타설시 주의 사항 - (4 항) 플렉시블 커넥터 「KCS 31 50 10 10 방진설비공사」 2.7 펌프관성베이스 방진 (4) 펌프의 흡입구와 토출구에 KS M 6617 로 성형한 플렉시블 커넥터를 사용할 경우에는 입상 되는 흡입배 관 및 토출배관이 굴곡현상이 발생하지 않도록 수직으로 정확히 설치한다. ![image](/image/placeholder) -펌프 배관 및 플렉시블 커넥터 연결 모습- ![image](/image/placeholder) -고무 플렉시블 커넥터- V (5 항) 방진베이스 내에 설치 국토교통부 371 기계설비 기술기준 해설 (별표 12 | {}
80959585-464f-420a-845c-7ab82388859d | 국내_기계설비_기술기준_매뉴얼_최종본 | 「KCS 31 50 10 10 방진설비공사」 2.7 펌프관성베이스 방진 (8) 펌프의 흡입, 토출측 연결 배관 또는 엘보의 지지대가 펌프 방진 베이스 내에 설치되지 못 할 경우 연결 배관이나 엘보의 하단부에 추가적으로 방진 장치를 설치한다. ![image](/image/placeholder) -흡입 토출 배관 펌프 방진베이스에 고정 설치 모습- ![image](/image/placeholder) 누수받침대 플렉시블 커넥터 )다 DRAIN 장비 기초 콘크리트 PUMP BASE 스프링 고무 마운트 배관 추가 방진장치 적용 모습- - 2. 용어 내용 없음 3.2 방진설비(계속) 3.2.7 잭업 이중바닥시스템 (1) 잭업 마운트가 설치될 바닥은 이물질이 없도록 깨끗하게 청소를 한 후 수평레벨의 차가 많은 곳 에는 추가적으로 수평을 확보한다. (2) 배수구 및 배관, 덕트는 주위 여건을 고려하여 설치 전에 슬리브를 설치한다. (3) 잭업 이중바닥 시스템은 기존벽체 및 기둥과 격리시킨다. (4) 잭업 마운트로 상승된 이중바닥의 표면은 수평을 확보한다. 해 설 1. 본문 해설 및 관련 법규 (1 항) 잭업 이중바닥시스템은 정형화된 잭업 마운트를 이용하여 공기층을 형성하고 이중바닥을 형성하므로 수평레벨 편차가 큰 곳은 최대한 바닥수평이 유지 될 수 있도록 조치 후 잭업 마운트 를 설치해야 함 ![image](/image/placeholder) 잭업마운트 수평작업 필요 잭업마운트 비닐시트 설치 - 잭업마운트 설치 조건(수평 레벨)- (2 항 ~ 3 항) 잭업 이중바닥시스템은 상승된 이중바닥을 구성하는 것이 매우 중요하며 이중바닥과 주변벽체, 배수구, 관통 배관, 덕트등이 상승된 바닥과 구조적으로 안전하게 격리되어야 함 372 기계설비 기술기준 매뉴얼 | {}
49514908-20ca-4e53-98a2-742043cf3db4 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 「KCS 31 50 10 10 방진설비공사」 2.8 잭업 이중바닥 시스템 (2) 잭업마운트는 구상흑연 주철품 또는 엔지니어링 플라스틱 (PE)으로 만든 컵형태의 하우징과 내부에 KS M 6617 로 성형하여 만들어진 고무마운트, KS D 3506 을 가공한 볼트가 내장되어 있어야 한다. (3) 잭업마운트 상부에는 KS M 6617 로 성형한 고무마개를 사용하여 콘크리트 타설시 콘크리트가 볼트 홀에 들어가지 않도록 한다. (4) 기존 바닥의 표면과 이중바닥의 콘크리트가 상호 이격 될 수 있도록 0.08 mm 의 두께를 갖는 비닐을 기 존 바닥 표면에 깔아야 한다. ![image](/image/placeholder) 코킹마감 코킹마감 미장마감 배수구 건축마감 건축마감 코킹마감 덕트 의원 배관 의원 유 30 주변격리 아이소 핑크 아이소 핑크 덕트보온재 배관 배수구 하부강판 덕트 설치 상세도 배수구 설치 상세도 배관 설치 상세도 -잭업마운트 바닥 관통부분 설치 상세도 V (4 항) 상승된 이중 바닥 표면 「KCS 31 50 10 10 방진설비공사」 3.8 잭업 이중바닥장치 (6) 잭업 마운트로 상승된 이중바닥의 표면은 수평계를 이용하여 수평이 되도록 조절하며 리프팅 후 잭업볼 트 구멍에는 코킹을 채워 넣어 이물질이 들어가지 않도록 마감한다. ![image](/image/placeholder) 고무마개 상부 보강철근 잭업하우징 고무마개 제거 잭업마운트 잭업마운트 상부 구멍 책업고무마운트 실란트 코킹 마감 하부 보강철근 잭업마운트 구멍 -잭업마운트 설치과 정 모습- 2. 용어 내용 없음 3.2 방진설비(계속) 3.2.8 방진방음 매트시스템 (1) 방진방음 매트가 설치될 바닥은 이물질이 없도록 깨끗하게 청소를 한 후 수평레벨의 차가 많은 곳에는 추가적으로 수평을 확보한다. (2) 배수구 및 배관, 덕트는 주위 여건을 고려하여 설치 전에 슬리브를 설치한다. (3) 방진방음 매트가 설치되는 바닥의 콘크리트 표면은 건조된 상태에서 시공한다. (4) 방진방음 매트 시스템은 기존벽체 및 기둥과 격리시킨다. 해 설 국토교통부 373 기계설비 기술기준 해설 (별표 12 | {}
70a6c605-ff97-4020-9e34-4729c5f093a4 | 국내_기계설비_기술기준_매뉴얼_최종본 | 1. 본문 해설 및 관련 법규 11 V (1 항) 방진방음 매트가 설치되는 바닥 조건 잭업시스템과 동일함 ![image](/image/placeholder) 수평작업 필요 비닐시트 설치 방진방음매트 방진방음매트 - 방진방음 매트 설치 조건(수평 레벨)- V (2 항, 3 항) 잭업 이중바닥시스템은 상승된 이중바닥을 구성하는 것이 매우 중요하며 이중바닥과 주변벽체, 배수구, 관통 배관, 덕트등이 상승된 바닥과 구조적으로 안전하게 격리되어야 함 「KCS 31 50 10 10 방진설비공사」 2.9 방진방음 매트 시스템 (2) 방진방음 매트는 KS M ISO 7214 시험방법에 준한 시험 결과 효율이 입증된 제품을 적용하며, 중요 소재 는 폴리우레탄, 네오프렌, EVA 등을 발포한 고분자 화학 구성제품 이어야 한다. (3) 방진방음 매트는 장비 및 부속지지물 콘크리트 등의 전체 중량을 충분히 지지 할 수 있도록 밀도와 색상 으로 구분하며 장비의 설치 기준에 따라 공조실에는 25 mm, 냉각탑 하부는 50 mm 적층 구조로 적용한 다. (4) 방진방음 매트의 표준 두께는 25 mm 를 기본으로 하며 소음·진동에 민감한 구역에 설치 될 경우 적층으 로 50 mm 를 구성하여 사용할 수 있다. Chart Type: bar 실란트 코킹 방진방음메트 (25T, 220K) 아이소 핑크 싱란트 코킹 Duct 쉬쉬쉬운데 주변 격리 벽체 item_01 100Not specified 100Not specified 200Not specified 200Not specified 200Not specified 100Not specified 100Not specified 100Not specified 100Not specified 덕트 설치 상세도 ![image](/image/placeholder) 장비 배수구 배관 공조기 U-BOLT& 고정 철지지물 실란트 코킹 ⑪ 바닥 배수구 유리섬유 충진 마감 미장 마감 ○장비 기초 °C 8 방 8 진 4 4 PIPE V 4 1. 배관격리(보온재마감), 배관 슬리브 장비주변 배수구 설치 상세도 배관 설치 상세도 -방진방음 매트 바닥 관통부분 설치 상세도 V (4 항) 콘크리트 표면은 건조된 상태에서 시공 「KCS 31 50 10 10 방진설비공사」 3.9 방진방음 매트 시스템 (4) 이중바닥의 모든 주변벽과 기둥 주위에는 높이 150~200 mm, 두께 20 mm 의 발포 폴리스티렌 단열재을 접착시킨 후 격리시킨다. 2. 용어 내용 없음 374 기계설비 기술기준 매뉴얼 | {}
ec665c07-0d8e-466b-9116-de775e482b99 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 3.2 방진설비(계속) 3.2.9 플렉시블 커넥터 (1) 연결되는 배관과 수평, 수직이 일치해야 한다. (2) 설치 완료 후 커넥터의 길이는 제품의 표준길이를 유지한다. 해 설 1. 본문 해설 및 관련 법규 (1 항) 추가 설명 없음 V (2 항) 플렉시블 커넥터 설치 「KCS 31 50 10 10 방진설비공사」 2.10 네오프렌 합성 플렉시블 커넥터 (1) 각종 구동체에 접속되어 있는 배관에는 KS M 6617 로 성형한 네오프렌 재질의 플렉시블 커넥터를 설치 한다. (4) 커넥터와 배관의 체결 시 배관 관경 100 mm 이상의 배관은 KS D 3503 로 제작된 제어봉을 필히 설치한 다. 「KCS 31 50 10 10 방진설비공사」 3.7 펌프관성베이스 방진 장치 (6) 관성베이스 위에 펌프 및 부대시설(배관, 밸브 등)이 설치된 후 펌프 가동 시 순간적으로 큰 변위가 일어 날 수가 있으므로 플렉시블 커넥터에 반드시 제어봉 및 브라켓을 설치하고 하단부 플랜지에 체결하는 이 중너트의 유효공간을 최소 10 mm 간격이 유지되도록 확인한다. (설치 시 원래 커넥터의 표준길이 +10mm 상태 유지하도록 한다) ![image](/image/placeholder) 신장(팽창) (최소 5mm) 신장(팽창)제어 최소 10mm 압축(최소 5mm) 커넥터 커넥터 설치시 길이 신장(팽창) 운전시 -플렉시블커넥터 제어봉 및 브라켓 설치 모습- 2. 용어 V 내용 없음 국토교통부 375 기계설비 기술기준 해설 (별표 12 | {}
55a14026-2379-4b05-8a93-68efa32731bd | 국내_기계설비_기술기준_매뉴얼_최종본 | 3.3 내진설비 3.3.1 장비류 (1) 장비를 기초에 직접 설치하는 경우 지진거동에 의한 등가정적하중에 견디도록 앵커볼트를 설계 한다. (2) 장비가 방진스프링으로 탄성지지된 경우 등가정적하중에 의해 이탈되지 않도록 이동 방지형 내 진스토퍼를 설치한다. 장비에 모멘트가 작용하는 경우 전도 방지형 내진스토퍼를 설치한다. (3) 콘크리트, 벽돌 등에 설치되는 후설치 앵커의 뽑힘 인장강도, 부착강도, 전단강도는 KDS 14 20 54(콘크리트용 앵커 설계기준)의 규정에 따라 모의 지진실험에 근거하여 평가되어야 하며, 공인 기관의 인증서에 의해 공개된 것이어야 한다. (4) 장비와 연결되는 배관은 상대변위를 흡수할 수 있도록 설계한다. 해 설 1. 본문 해설 및 관련 법규 (1 항) 장비 기초 설치 시 앵커볼트 설계 「KDS 41 17 00 건축물내진설계기준」 18.5 비구조요소의 정착부 (2) 콘크리트에 묻히는 정착부의 내력은 KDS 14 20 54 콘크리트용 앵커 설계기준에 따르며, KDS 14 20 54 에서 규정하지 않은 사항은 공인된 설계기준에 따를 수 있다. 단, KDS 14 20 54 의 4.1 설계 일반 (3)⑥은 "④와 ⑤의 조건을 만족하지 못하는 경우, 앵커 또는 앵커 그룹은 초과 강도계수 ��에 의해 증대된 지진하 중 E 에 대하여 설계되어야 한다."로 수정하여 적용한다. (4) 콘크리트에 설치되는 후설치 앵커의 뽑힘 인장강도, 부착강도, 전단강도는 KDS 14 20 54 의 규정에 따 라 모의 지진실험에 근거하여 평가되어야 하며, 공인기관의 인증서에 의해 공개된 것이어야 한다. 또한 조 적조에 설치되는 후설치 앵커는 공인된 설계기준의 규정에 따라 내진인증된 것이어야 한다. V (2 항) 이동, 전도 방지형 내진 스토퍼 「KDS 41 17 00 건축물내진설계기준」 18.4.2.3 지지부 (6) 진동격리장치를 가진 비구조요소는 수평방향으로 변위제한장치(범퍼)를 가져야 하며, 전도방지를 위해 필요할 경우 수직방향으로도 구속되어야 한다. 진동격리장치의 덮개와 변위제한장치는 연성이 있는 재료 를 사용하여야 한다. 범퍼와 비구조요소사이에는 충격하중을 감소시키기 위해 적절한 두께를 가진 점탄 성 혹은 이와 유사한 재질의 패드가 사용되어야 한다. 「KCS 31 50 10 15 내진설비공사」 2.1.1 바닥설치형 (4) 장비와 기초 콘크리트 사이에 방진패드가 설치 된 경우 내진력이 있는 이동 방지형 또는 전도 방지형 내 진 스토퍼를 설치하며, 장비와 기초 콘크리트 사이에 방진스프링이 설치 된 경우 지진완충기나 이동 또는 전도 방지형 내진 스토퍼를 설치한다. (5) 공조기가 송풍기 박스 분리형 일 때에는 이동방지형 내진스토퍼 및 지진완충기를 설치한다. ![image](/image/placeholder) -이동방지형 내진스토퍼- ![image](/image/placeholder) -전도방지형 내진스토퍼- ![image](/image/placeholder) -지진완충기(전방향)- (3 항) 지진거동에 의해 이탈되지 않도록 설계 376 기계설비 기술기준 매뉴얼 | {}
002810c3-d3de-42bb-a027-2a9b9e14e141 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 진동 또는 반복하중을 받는 장비 기초의 설계는 상부구조의 사용상 지장이 없도록 하고 또한 주위에 미치는 영향도 고려하여 내진하중과 함께 책임건축구조기술자가 결정해야 한다. V (4 항) 상대변위를 흡수 할 수 있도록 설계 「KDS 41 17 00 건축물내진설계기준」 18.2.3 상대변위 비구조요소가 수용해야 할 지진에 의한 상대변위 DpI 는 다음과 같이 계산한다. DpI= DPIE (18.2-6) 여기서, IE : 2.2 의 중요도계수 Dp: 아래 (1)과 (2)의 규정에 의해 산정되는 상대변위 (1) 동일한 구조물 또는 구조시스템상의 수직 위치가 ェ와 y 인 두 연결점에 대하여 Dp 는 다음과 같이 계산한 다. Dp = SxA -SyA (18.2-7) 혹은 Dp 는 7.3.3 의 응답스펙트럼해석법 혹은 7.3.4.2 의 선형시간이력해석에 의해 구해진 값을 사용할 수 있 다. Dp 는 다음 값을 초과 할 필요는 없다. △⌀A Dp = (X- Y) (18.2-8) hs ェ (2) 독립된 2 개의 구조물 또는 구조시스템상의 수직 위치가 각각 ェ와 y 인 두 연결점에 대하여 Dp 는 다음과 같이 계산한다. (18.2-9) Dp = ¦Sza¦ + ¦SyB Dp 는 다음 값을 초과 할 필요는 없다. X△AA Y△aB Dp = + (18.2-10) hsx hsx 여기서, Dp : 비구조요소가 수용해야 할 지진에 의한 상대변위 hsx : 허용층간변위를 정의 하기 위하여 사용된 층고 SxA⌀ SyA, SyB : 식 (7.2-13)에 의해 산정된 구조물 A 또는 B 상의 수직위치 x 또는 y 에서의 변위 X : 구조물 밑면으로부터 상부부착지점 x 까지의 높이 Y : 구조물 밑면으로부터 하부부착지점 y 까지의 높이 △a A⌀ △aB : 8.2.3 에 규정된 구조물 A 또는 B 의 허용층간변위 「KCS 31 50 10 15 내진설비공사」 1.1 적용범위 (12) 배관의 변형을 최소화하고 기계설비 주요 부품사이의 유연성을 증가시킬 필요가 있는 위치에 지진분리 이음을 설치하도록 한다. 「소방시설의 내진설계 기준」 제 3 조(정의) 8. "지진분리장치"란 지진 발생 시 건축물 지진분리이음 설치 위치 및 지상에 노출된 건축물과 건축물 사이 등에서 발생하는 상대변위 발생에 대응하기 위해 모든 방향에서의 변위를 허용하는 커플링, 플렉시블 조 인트, 관부속품 등의 집합체를 말한다. ![image](/image/placeholder) -지진분리장치 설치모습 - -수평변위 발생 시 제어모습- -수직변위 발생 시 제어모습- 국토교통부 377 기계설비 기술기준 해설 (별표 12 | {}
80127b03-3db4-4517-b7ab-da259c114eb8 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 프라잉 효과 ¦ 기계적 연결재를 사용한 인장 접합부에서 외력의 작용선과 연결재의 위치와 편심에 의해 접합 끝부분에 생기는 외력 방향의 2 차 응력에 의한 효과 출처 : 학교시설 내진성능평가 및 보강 매뉴얼, 교육부 Applied force FT Applied force ↑ Q Q Prying Bolt force Prying force forces FB FB Bolt force ¦ ¦ 상대변위 ¦ 기준점에 대한 다른 임의 부분이나 임의 질점의 거리의 변화 출처: 토목용어사전 [ relative displacement 相��位 1 여기에서는 비구조요소가 수용해야 할 지진에 의한 값으로 KDS 41 17 00 18.2.3 상 대변위를 참조 ¦ 3.3 내진설비(계속) 3.3.2 배관 및 덕트 (1) 수평배관 및 덕트는 등가정적하중과 상대변위에 견디도록 설계한다. (2) 콘크리트에 설치되는 후설치 앵커의 뽑힘 인장강도, 부착강도, 전단강도는 KDS 14 20 54(콘크리 트용 앵커 설계기준)의 규정에 따라 모의 지진실험에 근거하여 평가되어야 하며, 공인기관의 인증 서에 의해 공개된 것이어야 한다. (3) 배관 및 덕트가 탄성지지된 경우 등가정적하중에 견디는 와이어를 사용할 수 있으며, 이때 배관 및 덕트의 상방향 움직임도 구속되도록 설계한다. 배관 연결장치와 건축물 부착 장치는 공인된 시 험을 통하여 그 성능을 증명한다. (4) 구조물이 서로 분리되어 있고 서로 다른 거동을 하는 두 구조체를 사이를 배관 및 덕트가 통과 하 는 경우 구조체 사이의 상대변위를 흡수할 수 있는 유연한 이음을 설치한다. (5) 다층건물의 바닥을 관통하는 입상배관은 층간 상대변위를 흡수할 수 있는 구조이어야 한다. 해 설 1. 본문 해설 및 관련 법규 (1 항) 추가 설명 없음 V (2 항) 앵커의 설계기준 및 공인기관의 인증 378 기계설비 기술기준 매뉴얼 | {}
d04fad8d-344e-47b8-9724-0e3950a2c02f | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 「KDS 41 17 00 건축물내진설계기준」 18.5 비구조요소의 정착부 (2) 콘크리트에 묻히는 정착부의 내력은 KDS 14 20 54 콘크리트용 앵커 설계기준에 따르며, KDS 14 20 54 에 서 규정하지 않은 사항은 공인된 설계기준에 따를 수 있다. 단, KDS 14 20 54 의 4.1 설계 일반 (3)⑥은 "④ 와 ⑤의 조건을 만족하지 못하는 경우, 앵커 또는 앵커 그룹은 초과 강도계수 �에 의해 증대된 지진하중 E 에 대하여 설계되어야 한다."로 수정하여 적용한다. 「KCS 31 50 10 15 내진설비공사」 3.8 시험 및 검사 (1) 각종 내진제품에는 공인기관의 내진 시험 성적서를 제출한다. V (3 항) 배관 및 덕트의 움직임이 구속되도록 설계 「KCS 31 50 10 15 내진설비공사」 기계실의 배관 및 덕트 내진장치 (1) 배관이나 덕트에 설치되는 내진장치는 낙하 및 변형을 최소화하기 위하여 설치하며 설계도서와 내진 승인 자료를 보고 설치한다. (2) 방진스프링 행거로서 배관이나 덕트를 지지할 경우에는 행거로드가 수직이 되도록 설치하고 강성보강을 위해 내진로드로 보강하며 일정한 간격으로 클램프로 고정하고 설치 여건이 수직으로 할 수가 없을 경우에 는 내진 케이블 또는 내진 브라켓을 설치한다. (3) 방진스프링 마운트로 배관이나 덕트를 지지하는 경우에도 내진 케이블 또는 내진 브라켓을 서로 엇갈리게 (45°) 설치하며 건축구조물과 철지지물에 충분한 내진력을 가진 앵커볼트를 천장면에 설치한다. V (4 항) 구조물이 서로 분리되어 다른 거동을 하는 경우 「KDS 41 17 00 건축물내진설계기준」 18.4.2.1 기계 비구조요소 (2) 구조체사이 지점의 상대변위에 의해 서로 연결된 설비배관으로부터 비구조요소에 하중이 전달될 가능성 도 검토되어야 한다. (3) HVACR(난방, 환기, 공기조화, 냉장기기)의 파이프 혹은 배관이 구조물에 연결되어 있고 서로 상대변위가 발생하는 경우 또한 면진구조물에서 면진층을 통과 하는 파이프와 배관의 경우 18.2.3 에 의한 상대변위 요 구량을 수용할 수 있도록 설계되어야 한다. HVACR(난방, 환기, 공기조화, 냉장기)설비는 아래의 고려사항을 포함하는 인증절차를 만족하는 경우 내진성 능을 만족하는 것으로 인정한다. (1) 구동부 및 동력부의 내진성능은 진동대 실험을 통해 검증한다. (2) 구동부가 아닌 부분의 요구량은 R⌀/Ip = 1.0 에 근거한 해석에 의해 산정한다. (3) 해석을 통해 구동부가 아닌 부분의 내진능력을 평가할 경우 이 기준을 적용한다. 「KDS 41 17 00 건축물내진설계기준」 18.4.6 파이프 및 배관시스템 다른 요소와 의 연결부에 상대변위를 수용하기 위한 상세가 사용되지 않은 경우 유연한 연결부가 사용되어야 한다. 배관시스템의 수평보강의 필요성과 보강부재크기를 결정할 때 밸브, 스트레이너, 트랩, 펌프, 공기분리기 및 탱크와 같이 배관에 단단히 연결되고 지지되는 요소는 배관 시스템의 일부로 고려한다. 만약 이들 요소가 중 량으로 인해 독립적으로 보강되지만 배관이 보강되지 않은 경우 상대변위를 수용할 수 있도록 설계되어야 한 다. V (5 항) 층간 상대변위를 흡수할 수 있는 구조 기계설비 기술기준 해설 (별표 12 국토교통부 379 | {}
370796c1-3821-49d5-b52c-a04200a9e8f9 | 국내_기계설비_기술기준_매뉴얼_최종본 | 「KCS 31 50 10 15 내진설비공사」 1.1 적용범위 (12) 배관의 변형을 최소화하고 기계설비 주요 부품사이의 유연성을 증가시킬 필요가 있는 위치에 지진분리 이음을 설치하도록 한다. (13) 건축물 내의 신축이음 설치위치 및 타 구조물과 연계하여 기계배관이 연결되는 위치(인입부 등)에는 전 후좌우 방향의 변위를 수용할 수 있도록 지진분리이음을 설치한다 2.6 입상배관 내진장치 (1) 입상배관은 지진으로 인하여 배관의 수평방향으로 과다한 변형이 발생 되는 것을 억제하고 동시에 건축물 의 층간변위에 해당하는 변위를 수용하도록 건축구조체와 함께 움직이도록 한다. 2. 용어 V 내용 없음 380 기계설비 기술기준 매뉴얼 | {}
a0d580ed-968d-41cd-a22b-74253ce55b58 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 [별표 13] 플랜트설비의 설계 및 시공 기준 1. 목적 이 기준은 플랜트설비의 안전과 성능 확보를 위하여 필요한 설계 및 시공 방법 등 세부 기술기준을 정함을 목적으로 한다. 해 설 이 기준의 목적은 「기계설비법」 제 14 조(기계설비 기술기준)과 같은 법 영 제 2 조 및 [별표 1]에 근 거하여, 건축물이나 시설물에 필요한 플랜트설비의 설계 및 시공 시 기계설비의 안전과 성능을 확보하기 위하여 필요한 기술적 요건을 규정하기 위함 「기계설비법」 제 14 조(기계설비 기술기준) ① 국토교통부장관은 기계설비의 안전과 성능확보를 위하여 필요 한 기술기준(이하 "기술기준이라 한다)를 정하여 고시하여야 한다. 이를 변경하는 경우에도 또한 같다. 2. 적용범위 (1) 이 기준은 영 [별표 1] 제 11 호에 따른 플랜트설비의 설계 및 시공에 적용한다. (2) 플랜트설비 내 부속된 건축물의 기계설비와 플랜트설비의 생산 및 공정을 지원하기 위한 기계설 비는 이 기준 [별표 1]부터 [별표 12]까지 및 [별표 15]에 따른다. 해 설 V 이 기준의 적용범위는 「기계설비법」 제 2 조제 1 호에 따른 건축물등에 같은 법 영 제 2 조에 따라 대 통령령으로 정한 플랜트설비를 설치하는 경우 및 그와 관련된 부속설비들을 포함함 「기계설비법」 제 2 조(정의) 1. "기계설비"란 건축물, 시설물 등(이하 "건축물등"이라 한다)에 설치된 기계 · 기 구 · 배관 및 그 밖에 건축물등의 성능을 유지하기 위한 설비로서 대통령령으로 정하는 설비를 말한다. 「기계설비법 시행령」 제 2 조(기계설비의 범위) 「기계설비법」(이하 "법"이라 한다) 제 2 조제 1 호에서 "대통령령 으로 정하는 설비"란 별표 1 의 설비를 말한다. 「기계설비법 시행령」 [별표 1] 기계설비의 범위 11. 건축물등에서 생산물의 제조 · 생산 · 이송 및 저장이나 오염물질의 제거 및 저장 등을 위하여 설치된 기계 · 기구 · 배관 및 그 밖에 성능을 유지하기 위한 설비 V (2 항) 플랜트설비 내 부속된 건축물에 열원 및 냉난방설비, 공기조화설비, 위생설비 등이 있는 경 우에는 [별표 1] ~ [별표 12] 및 [별표 15]를 적용해야 함 V (2 항) 플랜트설비 내 부속된 건축물과 플랜트설비 내 작업자 환경 조성을 위한 냉낸방 공조, 위생 등의 설비에는 [별표 1] ~ [별표 12] 및 [별표 15]를 적용해야 함 국토교통부 381 기계설비 기술기준 해설 (별표 13 | {}
b0bde697-6a43-4906-9d09-562f3510ec62 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 플랜트설비 기술기준 지진, 화재, 폭발, 누출사고 등의 재난에 대응하는 플랜트설비 안전기준을 별도로 정하여 운영할 수 있다 해 설 V 이 기준의 에너지, 화공, 환경, 철강 및 기타 플랜트설비에 대하여 지진, 화재, 폭발, 누출사고 등과 관련한 안전기준은 이 기준 제 24 조(재검토기한) 등에 따라 구체적인 내용을 별도로 정하여 운영할 수 있으며, 다음의 사항이 포함된 기준과 절차를 수립할 예정임 1) 화재, 폭발, 지진 등 유형별 재난에 대비한 기준 수립 - 플랜트 종류 및 용도별로 화재·폭발·지진 등 재난 유형에 따른 설계·시공·유지관리·상황대처에 필요한 기준 수립 2) 내·외부 위험 요인 분석 및 대책 마련을 위한 기준 수립 - 플랜트 종류 및 용도별 잠재적 위험도 평가를 위한 취급물질의 종류와 특성, 노후도 등을 고려 한 기준 수립 - 내부 위험 요인에 기반한 화재, 폭발, 지진 등 외부 위험 요인에 대응하는 기준 수립 3) 플랜트 설비 안전평가 및 점검 절차 수립 - 내·외부 위험 요인 분석에 기반한 위험도 평가 및 점검 절차 수립 3.1 에너지 플랜트설비 (1) 석탄 및 석유, 가스 등의 연소, 핵분열 및 핵융합에 의한 열에너지와 물의 낙차에 의한 위치에너지 로 터빈 및 발전기를 구동시켜 전기에너지로 변화시키는 설비를 말한다. (2) 석유, 가스, 광물 등 각종 에너지 、 자원의 탐사 、 개발, 전처리, 변환 및 전환, 기존 유 、 가스채굴 방식과 다른 방식으로 채굴(셰일가스, 오일샌드, 석탄가스화 등 비전통 에너지) 또는 생산하기 위 한 설비를 말한다. (3) 신재생에너지를 생산하거나 이용하는 설비 또는 이를 활용하여 전기를 생산하는 설비를 말한다. 3.2 화공 플랜트설비 석유화학, 원유 및 가스처리설비, 원유정제설비, 일반화학설비 등을 생산하거나 처리하는 설비를 말 한다. 3.3 환경 플랜트설비 (1) 상하수도, 담수화, 하수종말처리, 폐수종말처리, 소각처리, 음식물처리 설비를 말한다. (2) 염분을 포함하는 해수나 염수에서 염분을 제거하거나 각종 오폐수에서 오염원을 적절한 수준으 로 제거하여 음용수 또는 용도별 용수로 처리하는 설비를 말한다. (3) 도시나 단지 등에서 발생하는 폐기물을 수집처리 、 활용하는 설비를 말한다. (4) 플랜트 건설 및 운영상 발생하는 온실가스 등을 포집 , 활용하는 기술을 말한다. 3.4 철강 플랜트설비 제철, 비철을 함유하는 광물로부터 다양한 철강제품을 생산 또는 가공하는 제철, 제강 설비를 말한 다. 3.5 기타 플랜트설비 그 밖의 플랜트설비를 말한다. 382 기계설비 기술기준 매뉴얼 | {}
4d605a15-868f-45b5-b333-127a6a9fbfea | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 해 설 V (3.3 1 항) '상하수도'는 수도법 제 3 조에 따른 '수도시설'과 및 하수도법 제 2 조에 따른 '하수도'를 말 한다. V (3.3 1 항) '담수화'는 수도법 제 3 조에 따른 '해수담수화시설'을 말한다. V (3.3 1 항) '하수종말처리'는 하수도법 제 2 조에 따른 '공공하수처리시설'을 말한다. V (3.3 1 항) '폐수종말처리'는 물환경보전법 제 2 조에 따른 '공공폐수처리시설'을 말한다. V (3.3 1 항) '소각처리, 음식물처리'는 폐기물관리법 제 2 조에 따른 '폐기물처리시설'을 말한다. 국토교통부 383 기계설비 기술기준 해설 (별표 13 | {}
b29b1045-8143-44a5-9d93-e98e33762f0e | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 14] 특수설비의 설계 및 시공 기준 1. 목적 이 기준은 특수설비의 안전과 성능 확보를 위하여 필요한 설계 및 시공 방법 등 세부 기술기준을 정 함을 목적으로 한다.. 해 설 V 이 기준의 목적은 「기계설비법」 제 14 조(기계설비 기술기준)과 같은 법 영 제 2 조 및 [별표 1]에 근 거하여, 건축물이나 시설물에 필요한 특수설비의 설계 및 시공 시 기계설비의 안전과 성능을 확 보하기 위하여 필요한 기술적 요건을 규정하기 위함 「기계설비법」 제 14 조(기계설비 기술기준) ① 국토교통부장관은 기계설비의 안전과 성능확보를 위하여 필요 한 기술기준(이하 "기술기준이라 한다)를 정하여 고시하여야 한다. 이를 변경하는 경우에도 또한 같다. 2. 적용범위 이 기준은 영 [별표 1] 제 12 호에 따른 특수설비의 설계 및 시공에 적용한다. 해 설 V 이 기준의 적용범위는 「기계설비법」 제 2 조제 1 호에 따른 건축물등에 같은 법 영 제 2 조에 따라 대 통령령으로 정한 특수설비를 설치하는 경우 및 그와 관련된 부속설비들을 포함함 「기계설비법」 제 2 조(정의) 1. "기계설비"란 건축물, 시설물 등(이하 "건축물등"이라 한다)에 설치된 기계 · 기 구 · 배관 및 그 밖에 건축물등의 성능을 유지하기 위한 설비로서 대통령령으로 정하는 설비를 말한다. 「기계설비법 시행령」 제 2 조(기계설비의 범위) 「기계설비법」 (이하 "법"이라 한다) 제 2 조제 1 호에서 "대통령령 으로 정하는 설비"란 별표 1 의 설비를 말한다. 「기계설비법 시행령」 [별표 1] 기계설비의 범위 12. 특수설비 가. 건축물등에서 냉동 · 냉장, 항온.항습(온도와 습도를 일정하게 유지시키는 것), 특수청정(세균 또는 먼 지 등을 제거하는 것), 생활폐기물 집하 및 이송, 전자파 차단 등을 위하여 설치된 기계 · 기구 · 배관 및 그 밖에 성능을 유지하기 위한 설비 나. 청정실(실내공간의 오염물질 등을 없애거나 줄이기 위하여 공기정화시설 등의 설비가 설치된 방), 자 동창고(물건이 나가고 들어오는 모든 일을 컴퓨터가 자동적으로 제어하고 관리하는 창고), 집진기(먼지 를 모으는 기기), 무대기계장치, 기송관(���: 압축 공기를 써서 물건을 운반하는 기계) 등의 설비와 그 설비를 위하여 설치된 기계 · 기구 · 배관 및 그 밖에 성능을 유지하기 위한 설비 384 기계설비 기술기준 매뉴얼 | {}
e02df777-ac03-460c-8ff2-dfe9b47bda49 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 3. 특수설비 기술기준 3.1 냉동냉장 설비 냉동냉장설비의 시공은 건설기준코드(KCS 31 40 00)를 따른다. 해 설 국가건설기준센터(https://www.kra.re.co//re/ince) -> [설비코드] - > [표준시방서] KCS 31 40 00(냉동냉장설비공사) 내용에 따름 3.2 청정실 설비 청정실 설비의 설계 및 시공은 건설기준코드(KDS 31 50 20, KCS 31 50 20) 클린룸 기준을 따른다. (1) 산업용 클린룸 (2) 병원용(바이오) 클린룸 해 설 국가건설기준센터(https://www.krs.re.of/ha/lices) -> [설비코드] -> [설계기준] KCS 31 50 20(클린룸설비) 및 [표준시방서] KCS 31 50 20(클린룸설비공사) 내용에 따름 3.3 생활폐기물 이송관리 및 자동집하시설 생활폐기물 이송관리 및 자동집하시설의 설계 및 시공은 건설기준코드(KDS 31 90 45, KCS 31 90 45)를 따른다. (1) 이송관로설비 (2) 집하시설 해 설 국가건설기준센터(https://www.krs.re.or/re/ince/ince) -> [설비코드] -> [설계기준] KCS 31 90 45(생활폐기물 이송관로 및 자동집하시설 설계) 및 [표준시방서] KCS 31 90 45 05(생활폐기물 이 송관로 및 집하시설공사 일반사항, KCS 31 90 45 10(생활폐기물 이송관로 및 부속설비공사), KCS 31 90 45 15(생활폐기물 자동집하시설 및 부속 설비공사), KCS 31 90 45 20(생활폐기물 이송관로 및 집하시설 자동제어 설비공사) 내용에 따름 국토교통부 385 기계설비 기술기준 해설 (별표 14 | {}
150a2c1b-ae5d-409e-98eb-85ca45d582e2 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3.4 건널목 차단기 설비 건널목 차단기 설비는「국토교통부고시 제 2019-132 호 철도시설의 기술기준」제 71 조(건널목 안전설 비) 및 제 72 조(차단기 설치)기준에 따라 설치해야 한다. 해 설 「철도시설의 기술기준」 제 71 조(건널목 안전설비) ① 건널목 안전설비는 별표 2 의 건널목 종류별 안전설비 설치기준에 따라 설치하여 야 한다. ② 건널목 안전설비는 정전의 경우에도 일정시간 동안 기능에 이상이 없도록 작동하여야 한다. ③ 건널목 안전설비는 낙뢰 및 이상전압이 유입될 경우 기기를 보호할 수 있는 설비를 갖추어야 한다. ④ 건널목 주변의 각종 장애물 등으로 인한 건널목 사고를 예방하기 위하여 다음 각 호의 안전설비를 필요 한 개소에 설치하여야 한다. 1. 지장물 검지장치 2. 출구측 차단봉검지기 3. 정시간제어기 4. 고장검지 및 감시장치 5. 정보 분석장치 6. 그 밖에 필요하다고 판단되는 장치 제 72 조(차단기 설치) ① 차단기는 지형여건상 부득이한 경우를 제외하고는 도로에서 선로를 바라볼 때 우측 에 설치하되, 열차운행에 지장을 주지 않아야 한다. ② 차단기는 고압전선으로부터 1.5 m 이상의 거리를 두고 설치되어야 한다. 3.5 철도기계신호 설비 철도기계신호설비는 「국토교통부고시 제 2019-132 호 철도시설의 기술기준」제 9 조(철도신호제어설 비의 안전성 분석 등), 제 96 조(철도신호제어설비의 구조), 제 97 조(철도안전설비와 의 연계), 제 99 조 (철도신호제어설비)기준에 따라 설치해야 한다. 해 설 386 기계설비 기술기준 매뉴얼 | {}
39f46c86-795d-4f84-a463-c624070dcd76 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 「철도시설의 기술기준」 제 9 조(철도신호제어설비의 안전성 분석 등) 철도신호제어설비의 안전성 분석 및 안전대책을 검증할 때에는 다음 각 호의 사항을 고려하여 수행하여야 한다. 1. 열차제어장치는 연동장치 등과 연계하여 정할 것 2. 전체시스템 요구사항을 바탕으로 설정하여 안전요구사항의 달성기준을 제시할 것 3. 안전성 분석을 수행할 경우에는 최소한 철도시설의 시스템운영, 환경조건, 적용조건 및 운영조건 등의 위 험원을 도출할 것 4. 인적요인에 의하여 철도안전에 영향을 미칠 수 있는 위험원을 도출할 것 5. 철도신호제어설비를 구성하는 기본기능, 대상 장치의 내·외부 인터페이스, 운영시나리오 등을 대상으로 위험원을 도출할 것 6. 도출된 위험원의 원인분석 및 위험도(위험원으로 인한 사고의 심각도와 발생빈도의 조합을 말한다)를 통 하여 철도신호제어설비의 안전성이 허용될 수 있는 안전수준으로 제어되고 있음을 정량적 수치 또는 판 단논리로 입증할 것 제 96 조(철도신호제어설비의 구조) 철도신호제어설비의 주요 장치를 제작·설치할 때에는 다음 각 호의 사항 을 준수하여야 한다. 1. 기능, 인터페이스 등에 대한 무결성을 스스로 진단·감시·저장되어야 하며, 장애가 발생하면 안전상태로 전 환될 것 2. 장치를 설계·개발하는 과정에서 오류 등이 발생되지 않도록 소프트웨어의 분석·시험 및 검증을 수행할 것 3. 중요한 정보를 지속적으로 안전하게 전송할 것 4. 교체 및 철거가 쉬울 것 제 97 조(철도안전설비와 의 연계) 철도신호제어설비는 선로 또는 승강장에서의 철도사고를 방지하고 그 영향 을 차단할 수 있도록 다음 각 호의 철도안전설비와 연계되어야 한다. 1. 차축온도검지장치 등 선로의 안전설비 2. 비상정지버튼 등 승강장 안전설비 3.6 전자파차단 설비 전자파차단 설비는 「과학기술정보통신부고시 제 2019-4 호 전자파인체보호기준」을 준수해야 하며, 그 외의 사항은 발주자의 시방 등을 적용한다. 해 설 기계설비 기술기준 해설 (별표 14) 국토교통부 387 | {}
457acf80-28c5-408c-b29d-ff4e120ca3d2 | 국내_기계설비_기술기준_매뉴얼_최종본 | 「전자파인체보호기준」 제 1 조(목적) 이 고시는 「전파법」제 47 조의 2 제 1 항의 규정에 의하여 전자파 인체보호기준(이하 "인체보호기준 "이라 한다)에 관하여 필요한 사항을 규정함을 목적으로 한다. 제 2 조(정의) 이 기준에서 사용하는 용어의 정의 는 다음 각 호와 같다. 1. "전자기장"이라 함은 전기장과 자기장의 총칭을 말한다. 2. "전기장"이라 함은 전하(��)에 의해 변화된 그 주위의 공간상태를 말한다. 3. "자기장"이라 함은 자석상호간, 전류상호간, 또는 자석과 전류사이에 힘이 작용하는 공간상태를 말한다. 4. "전기장강도"라 함은 전기장 내의 한 점에 있는 단위 양전하에 작용하는 힘을 말한다. 5. "자속밀도"라 함은 운동하는 전하의 운동속도에 비례하는 힘을 유발하는 벡터량을 말한다. 6. "자기장강도"라 함은 선형적이고 등방성을 갖는 매질내의 자속밀도를 주어진 주파수에 대한 매질의 투자 율로 나눈 것을 말한다. 7. "전력밀도"라 함은 전자파의 진행방향에 수직인 단위면적을 통과 하는 전력을 말한다. 8. "전자파흡수율(SAR, W/kg)"이라 함은 생체조직에 흡수되는 단위질량 당 에너지율을 말한다. 9. "실효치(rms)"라 함은 정현파 신호의 크기 제곱의 시간에 따른 평균값의 평방근을 말한다. 10. "일반인"이라 함은 전자기장에 노출되고 있는 사실을 모르거나 조치를 취할 수 없는 자를 말하며 의료목 적으로 노출 받는 자는 제외한다. 11. "직업인"이라 함은 직무상 작업수행 과정에서 자신이 전자기장에 노출되고 있음을 알고 있고 이의 잠재 적인 위험성을 알고 주의 하도록 훈련받은 자를 말한다. 12. "전자파노출"이라 함은 인체의 전부 또는 일부가 전자기장에 노출되는 것을 말한다. 제 3 조(전자파강도기준) ① 일반인에 대한 전자파노출은 [별표 1]에 규정된 전기장강도와 자기장강도 또는 자 속밀도와 전력밀도 값을 초과 하지 않아야 한다. ②직업인에 대한 전자파노출은 [별표 2]에 규정된 전기장강도와 자기장강도 또는 자속밀도와 전력밀도 값을 초과 하지 않아야 한다. ③제 1 항 및 제 2 항의 규정에 불구하고 60Hz 주파수대역의 전기설비(송전선로)는 이를 적용하지 아니한다. 제 4 조(전자파흡수율기준) 전자파흡수율(SAR)의 최댓값은 [별표 3]에 규정된 값을 초과 하지 않아야 한다. [별표 1] 일반인에 대한 전자파강도기준(제 3 조제 1 항 관련) [별표 2] 직업인에 대한 전자파강도기준(제 3 조제 2 항 관련) [별표 3] 전자파흡수율(SAR)기준(제 4 조 관련) 3.7 무대기계장치 설비 무대기계장치 설비는 발주자의 시방 등을 적용한다. 해 설 무대기계장치 설비의 발주자 시방 등에는 다음의 내용을 포함하여야 함 - 시공 중 안전관련 사항 - 유지관련 사항 388 기계설비 기술기준 매뉴얼 | {}
aa4ab35c-232b-4526-8be8-1071d9e006f2 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 3.8 자동창고 설비 자동창고 설비는 발주자의 시방 등을 적용한다. 해 설 자동창고 설비의 발주자 시방 등에는 다음의 내용을 포함하여야 함 - 시공 중 안전관련 사항 - 유지관련 사항 3.9 집진기 설비 집진기 설비는 발주자의 시방 등을 적용하며, 특고압 전기집진의 경우에는「산업통상자원부고시 제 2019-45 호 전기설비 기술기준」제 71 조(특고압 전기집진 응용장치 등의 시설)을 준수해야 한다. 해 설 「전기설비 기술기준」 제 71 조 (특고압 전기집진 응용장치 등의 시설) 사용전압이 특고압의 전기집진장치정전도장장치(������ 置)·전기탈수장치·전기 선별장치 그 밖의 전기집진 응용장치 및 이에 특고압의 전기를 공급하기 위한 전기 설비는 제 50 조 및 제 53 조에도 불구하고 옥측 또는 옥외에는 시설하여서는 아니 된다. 다만, 그 전기설비 의 충전부의 위험성을 고려하여 감전 또는 화재의 우려가 없도록 시설하는 경우는 그러하지 아니하다. 3.10 스크린도어 설비 스크린도어 설비는 발주자의 시방 등을 적용하며, 「국토교통부고시 제 2019-132 호 철도시설의 기술 기준」제 99 조(철도신호제어설비) 제 1 호제 5 항에 따라 철도신호제어설비와 연계해야 한다. 해 설 기계설비 기술기준 해설 (별표 14 국토교통부 389 | {}
641ae6a6-25c4-4698-9074-48360ed0349c | 국내_기계설비_기술기준_매뉴얼_최종본 | 「철도시설의 기술기준」 제 99 조(철도신호제어설비) ① 철도신호제어설비를 설치하기 위해서는 다음 각 호와 같이 열차에 설치되는 차내 신호제어설비와 의 적합성을 확인하여야 한다. 1. 열차위치검지방법 및 성능 2. 상용제동을 포함한 여러 가지 제동성능 3. 데이터 전송방법 4. 운전석의 신호정보표시 및 조작 5. 스크린도어장치 등 승강장 안전장치와 의 연계 등 ② 신호기 장치는 다음 각 호를 고려하여 설치하여야 한다. 1. 설치위치는 열차진행방향 중앙 또는 좌측에 설치하는 것을 원칙으로 하고 충분한 확인거리를 확보할 것 2. 데이터 정보를 전송할 때 오류가 없도록 할 것 ③ 철도신호제어설비는 설치지역의 환경조건, 작업자의 안전한 이동 및 승객의 안전한 탈출을 고려하여 설 치하여야 한다. ④ 철도신호제어설비는 주변에 설치되어 있는 다른 시설물 또는 장치가 안전하게 작동되는 것을 방해하지 아니하여야 하고, 다른 시설물 또는 장치로부터 방해받지 아니하도록 충분한 간격을 두고 설치하여야 한 다. ⑤ 케이블을 포함한 철도신호설비는 화재, 열차탈선 및 침입으로 인한 피해를 최소화되도록 설치하여야 한 다. ⑥ 철도신호제어설비는 외부인이 임의 로 취급할 수 없도록 보호장치를 설치하여야 한다. ○ 3.11 문서반송(기송관 등) 설비 문서반송 설비는 발주자의 시방 등을 적용한다. 해 설 문서발송 설비의 발주자 시방 등에는 다음의 내용을 포함하여야 함 - 시공 중 안전관련 사항 - 유지관련 사항 - ○---- -- 3.12 진공청소 설비 진공청소 설비는 발주자의 시방 등을 적용한다. 해 설 진공청소 설비의 발주자 시방 등에는 다음의 내용을 포함하여야 함 - 시공 중 안전관련 사항 - 유지관련 사항 390 기계설비 기술기준 매뉴얼 | {}
0f4cd3a0-8360-4894-a65c-185a193bcca7 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 3.13 분수 설비 분수 설비는 발주자의 시방 등을 적용한다. 해 설 분수 설비의 발주자 시방 등에는 다음의 내용을 포함하여야 함 - 시공 중 안전관련 사항 - 유지관련 사항 3.14 수영장 설비 수영장 설비는 발주자의 시방 등을 적용한다. 해 설 수영장 설비의 발주자 시방 등에는 다음의 내용을 포함하여야 함 - 시공 중 안전관련 사항 - 유지관련 사항 ---- - - 3.15 이송 설비 엘리베이터, 에스컬레이터, 무빙워크, 덤웨이터, 기계식주차설비 등 사람 또는 물품을 이송하는 설 비는 발주자의 시방 등을 적용한다. 해 설 이송 설비의 발주자 시방 등에는 다음의 내용을 포함하여야 함 - 시공 중 안전관련 사항 - 유지관련 사항 국토교통부 391 기계설비 기술기준 해설 (별표 14 | {}
1cf89414-1a78-44e9-9fcf-87eae94fc35c | 국내_기계설비_기술기준_매뉴얼_최종본 | [별표 15] 기계설비 유지관리를 고려한 설계기준 1. 기계설비 유지관리 일반사항 (1) 기계설비 설계 , 시공 시에는 장비, 배관, 덕트, 각종 부속품 등의 내구연한을 고려하여 유지관리 가 용이하도록 한다. (2) 기계설비 설계 、 시공 시에는 기계설비의 통합, 분리, 변경이 용이하며, 부분 보수, 변경, 교체 시 타 시설의 영향을 최소화하고, 개별제어 또는 통합제어 등이 가능하도록 한다. 해 설 1. 본문 해설 및 관련 법규 V 이 기준의 목적은 「기계설비법」 제 1 조(목적)에 따라 '기계설비의 안전하고 효율적인 유지관리를 위하여 필요한 사항을 정함'에 있어, 같은 법 영 제 2 조(기계설비의 범위)의 기계설비가 설치된 건 축물등을 제 16 조(기계설비 유지관리기준의 고시)와 같은 법 규칙 제 7 조에 따라 유지관리 하는데 필요한 공간 등을 확보하기 위하여 필요한 사항을 규정하기 위함 V (1 항) 건축물등에 설치된 기계설비의 수명은 일반적으로 건축물등의 수명보다 짧으므로 추후 설 치된 기계설비를 수리 및 교체하거나, 리모델링하는 상황을 고려하여 설계 및 시공해야 함 V (2 항) 건축물이 장수명화 됨에 따라 사용용도가 변경되는 경우, 기계설비의 변경이 용이하도록 설 계, 시공해야 하며, 이 경우 타 시설 특히, 건축 구조물의 훼손이 최소화되도록 설계 및 시공해야 함 V 이 기준은 [별표 13] 플랜트설비, [별표 14] 특수설비와 같이 제조 및 생산을 위한 기계설비에 대해 서는 적용하지 않음 2. 용어 V 내용 없음 392 기계설비 기술기준 매뉴얼 | {}
2e9ac188-2128-4569-91e4-668b9578b060 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2. 기계설비 유지관리 공간 (1) 기계설비의 장비, 배관, 덕트 등의 설치를 위한 기계실, 피트, 샤프트, 공동구 등은 점검, 보수, 교 체를 위한 공간 및 층고를 확보한다. (2) 공용시설의 배관, 장비 등을 전용시설 내에 설치하지 않는다. (3) 기계설비 전용의 배관, 장비 등을 타설비의 전용시설 내에 설치하지 않는다. 단, 설치가 필요한 경 우에는 누수 방지대책을 수립하여 설치한다. (4) 기계설비 배관, 덕트 등은 샤프트 또는 피트를 배치하여 설치하며, 구조체 내에 매립하지 않는다. 단, 매립할 경우 [별표 5] 3.1(4), [별표 6] 2.1.1(1) 및 3.1(8)에 따른다. 해 설 1. 본문 해설 및 관련 법규 V (1 항) 기계설비가 설치되는 기계실, 피트, 샤프트, 공동구 등의 공간은 장비와 배관의 설치 및 준 공 후 보수, 점검, 교체에 지장이 없도록 공간을 확보해야 하며, 자세한 내용은 이 기준의 각 세부 기준을 따름 V (2 항) 건축물 내 설치되는 기계설비는 공용부와 전용부를 명확하게 구분하여야 하며, 공용부 점검 시 전용부의 침입, 훼손 등이 발생하지 않도록 함 V (3 항) 건축물 내 설치되는 기계설비 중 장비 및 부속에 물을 사용하는 기계설비는 소방, 전기, 통신 등 타 시설의 전용시설 내에 설치를 금하며, 부득이하게 설치해야 하는 경우에는 누수 방지 대책 등을 마련하고 해당 건축물등의 감리 승인을 득해야 함 V (4 항) 기계설비 배관, 덕트 등은 구조체 내에 매립하지 않고 별도의 공간(기계실, 피트, 샤프트 등) 에 설치하는 것을 원칙으로 하나, 다음에 해당하는 경우에는 예외로 함 「기계설비 기술기준」 [별표 5] 3.1 일반사항 (4) 「주택건설기준 등에 관한 규정」 제 43 조에 따라 급수급탕 배관은 콘크리트 구조체 안에 매설하여서는 안 된다. 다만, 다음의 어느 하나에 해당하는 경우에는 그러하지 아니하다. ① 배관이 바닥면 또는 벽면 등을 직각으로 관통하는 경우 ② 구조안전에 지장이 없는 범위에서 덧관 등을 사용하여 미리 매설하여 배관하는 경우 ③ 배관의 매설이 부득이하다고 감리업무수행자에게 사전 승인한 경우로서 배관의 부식을 방지하고 그 수 선 및 교체가 쉽도록 하여 배관을 설치하는 경우 「기계설비 기술기준」 [별표 6] 2.1 오 · 배수 통기설비 2.1.1 일반사항 (1) 콘크리트구조체에 배관을 매설하거나 배관이 콘크리트구조체를 관통할 경우에는 「건축물의 설비기준 등에 관한 규칙」제 17 조제 2 항제 6 호에 따라 구조체에 덧관을 미리 매설하는 등 배관의 부식을 방지하고 수 선 및 교체가 용이하도록 한다. 「기계설비 기술기준」 [별표 6] 3.1 일반사항 (8) 배수용 배관설비는 2.1.1(1)의 기준에도 불구하고 구조체에 슬리브를 미리 매립이 어려운 경우에는 감리 업무수행자와 협의 하여 설치할 수 있다. 2. 용어 국토교통부 393 기계설비 기술기준 해설 (별표 15 | {}
9c2ae0c7-fc05-4606-80a9-aa1d2ae86dd3 | 국내_기계설비_기술기준_매뉴얼_최종본 | ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 기계실 ¦ 열원설비, 냉난방설비, 기기제어장치 등 각종 기계설비를 집중적으로 설치하는 장소 (해설서 주) ¦ ¦ 피트 ¦ 상.하층이나 외부로 유체를 이송하기 위한 주배관, 주덕트, 밸브류 등이 집중적으로 설치된 유지관리 점검 및 보수를 위한 수평적 소규모 공간(해설서 주) ¦ ¦ 샤프트 ¦ 설비의 사용을 위한 배관 공간으로 건축물에서 수직 방향으로 구성된 배관.배선이 집중적으로 수납된 공간 (PS, PD, EPS, TPS 등)(해설서 주) ¦ ¦ 공동구 ¦ 도시가스, 전력, 통신, 상하수도, 지역 냉난방 등의 공공기반시설을 수용하기 위해 지 하에 설치하는 구조물 출처 : 건축용어대사전, 기문당 ¦ ○ -- 2.1 기계실 (1) 기계실 유지관리 공간 확보 기계실은 장비와 배관의 설치 및 준공 후 보수, 점검, 교체에 지장이 없도록 충분한 유지관리 공간과 층고를 확보한다. 단, 건축, 전기 등 타 공종과 충분히 협의 해야 한다. ① 기계실의 모든 장비는 정비 및 교체에 필요한 공간을 확보한다. ② 장비와 장비 사이는 대형 장비를 기준으로 장비 폭의 1/2 이상 또는 최소 900 mm 이상을 이격 하여 배치한다. ③ 장비와 벽체 사이는 900 mm 이상 이격한다. ④ 모든 장비는 타 장비의 해체 없이 반출입이 가능하도록 이격하여 배치하며, 반출입 주 통로는 최 대 장비 폭보다 900 mm 이상의 공간을 확보한다. ⑤ 기계실의 장비 배치는 배관, 덕트 길이를 최소화하여 운전비용을 절감할 수 있도록 하며, 빈번한 점검이 필요한 장비는 출입구나 감시실에 가까이 배치한다. ⑥ 기계실의 층고는 보수, 점검 및 교체에 지장이 없도록 다음을 고려하여 보 밑 유효높이를 확보한 다. 가. 최대 장비 높이의 2 배 이상 나. 배관/덕트 등을 다단으로 설치할 경우 배관/덕트의 이격간격은 마감재 기준으로 배관의 경우 150 mm 이상, 덕트의 경우 300 mm 이상, 단 교차되는 부분은 제외한다. 다. 보일러실의 천장 높이는 보일러 상면에서 보 밑 천장까지 1.2 m 이상 확보한다. ⑦ 기계실의 장비는 냉온열원, 급수용 등 용도별로 구획하여 배치한다. ⑧ 기계설비용 MCC 판넬은 중앙감시반에서 접근이 용이한 곳에 배치한다. 해 설 1. 본문 해설 및 관련 법규 V 해당 기준은 공동주택 세대 내 보일러실, 실외기실에는 적용하지 않음 V (1 항 1 호) 기계실 내의 유지관리 공간과 층고를 확보함에 있어 장비와 배관의 설치 및 준공 후 보 수, 점검, 교체 등을 효과 적으로 수행할 수 있도록 건축, 전기 등 타 공종과 충분히 협의 해야 함 V (1 항 2 호) 두 개의 장비 중 상대적으로 큰 장비를 기준으로, 장비 폭의 1/2 이상 또는 900 mm 이 상 중에서 설계자의 판단에 따라 결정하며, 캐스케이드 보일러와 같이 패키지화한 기계설비의 경 394 기계설비 기술기준 매뉴얼 | {}
50236ab5-60de-4185-846c-d14a92b64f8a | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 우 패키지 전체를 하나의 장비로 간주함 V (1 항 3 호) 장비와 벽체에 설치된 마감재부터 900 mm 이상을 이격해야 함 V (1 항 4 호) 장비 반출입을 위한 주 통로에 대한 규정으로, 모든 장비는 설치 및 준공 후 보수, 점검, 교체 등의 작업시 반출입에 의해 타 장비에 영향을 주지 않도록 하고, 이때 최대 주 통로는 최대 장비 폭보다 900 mm 이상의 공간을 확보하여야 함 V (1 항 5 호) 기계실 내 장비 배치는 배관 및 덕트 이송에 따른 운반 및 열손실 등을 고려하여야 하 며, 유지관리 빈도가 높은 장비는 출입구나 유지관리자가 육안으로 감시가 가능한 실 가깝게 배 치해야 함 (1 항 6 호 가) 최대 장비 높이는 장비 자체의 높이로 기초는 제외하며, 물탱크의 경우에는 「수도법 시행령」 9 의 2 [별표 3 의 2] 「저수탱크의 설치기준」에 따름 단, 최대 높이 장비 상부의 배관/덕트 등의 설치 시 1 항 6 호 나의 조건 및 2.2 피트 2 항의 기준을 모두 만족하여 유지관리를 원활히 수행할 수 있을 경우에는 기계설비감리업무수행자와 협의 를 거쳐 최대 장비높이의 2 배 기준을 적용하지 않을 수 있음 V (1 항 6 호 나) 배관/덕트의 이격 간격에서 마감재 기준이란 이 기준 [별표 10] 보온설비의 설계 및 시공 기준을 만족해야 함 V (1 항 6 호 다) 보일러실을 따로 설치하는 경우에 해당하며, 보일러 연도의 설치 등을 고려하여 보 일러 상면과 보밑 사이의 공간을 확보함 V (1 항 7 호, 8 호) 유지관리를 용이하게 하기위해 유사 용도의 장비별로 조닝하여 배치하고 각 장비 의 판넬은 중앙감시반에서 유지관리자가 접근이 용이하도록 배치해야 함 시공 도중 설계변경 등의 불가피한 이유로 이격 간격 및 유지관리 공간을 확보하기 어려운 경우, 기계설비감리업무수행자의 승인을 받는다면 예외로 할 수 있음 ![image](/image/placeholder) 장비폭 장비폭 1/2 장비폭 900 (W) or 900 (W) 900 기계실 벽체 ※ ※ 장비 예시 : 1 항 2 호, 3 호 국토교통부 395 기계설비 기술기준 해설 (별표 15) | {}
cd461031-b51e-401d-b947-bdb23c7b2735 | 국내_기계설비_기술기준_매뉴얼_최종본 | ![image](/image/placeholder) ⓒ ⓐ ⓑ ⓐ ⓑ ⓐ ⓑ ⓐ ⓑ ⓐ ⊙ 800 ⓒ 中 認 = 此 ⓔ 2440 1700 2440 1700 2440 관리동선 ⑥ 、 료 、 ⓐ : 장비 폭 ⓑ : ⓐ/2 이상 또는 900 mm 이상 소 ⓒ : 900 mm 이상 ⓑ ⓓ : 반출입 통로 공간 (최대 ⓐ + 900 mm 이상) ⓔ : 장비 반출입문 : 최대 ⓐ 이상 1800 ⓒ 예시 : 1 항 4 호 ![image](/image/placeholder) 배관/덕트 이격거리 준수 200 1700 맨홀 1 000 ■ 500 X 700 보 2300 3100 6800 6 100 4 500 3800 3000 600 200 ↓ [저수탱크] [급탕탱크] [증기 보일러] 예시 : 1 항 6 호 2. 용어 내용 없음 396 기계설비 기술기준 매뉴얼 | {}
f6156c88-5846-43b9-b839-c53b3224fe73 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.1 기계실(계속) (2) 장비 반출입 공간 확보 장비반입구 및 반입통로는 추후 장비교체를 고려하여 배치하고, 장비반입구에는 평상시 다른 구조 물 혹은 시설을 고정 설치하지 않으며, 지상 및 지하 모두 반출입이 용이한 장소에 배치한다. ① 장비반입구의 크기는 설치장비 최대 폭과 길이보다 900 mm 이상의 공간을 확보한다. ② 주차장 차량 출입로 등을 이용하여 모든 장비의 반출입이 가능한 경우에는 장비반입구를 설치하 지 않아도 된다. 해 설 1. 본문 해설 및 관련 법규 (2 항 1 호) 장비반입구에 대한 규정으로, 지상 및 지하에서 반출입이 용이한 장소에 배치하며, 설 치장비 최대 폭과 길이보다 900 mm 이상의 공간을 확보해야 함 (2 항 2 호) 2.1 (2) ①의 규정에도 불구하고 주차장 차량 출입로, 일반출입문 등 다른 입구를 통해 반출입이 가능한 경우에는 예외로 함 ![image](/image/placeholder) 450 장비 (L) 450 450 장비 3 可以 450 예시 : 2 항 1 호 2. 용어 내용 없음 2.1 기계실(계속) (3) 기계실의 배치 기계실 위치는 기계실 배관, 반송동력, 장비의 최고사용압력, 유지관리 등을 고려하여 정하고, 가능 한 배관, 덕트 길이가 최소화 되는 장소에 배치하며, 장비의 교체, DA(dry area)의 연결, 관리자의 피난경로 등을 종합적으로 고려하여 배치한다. 단 집단에너지 의무 사용지역은 수용가 시설기준에 따른다. 국토교통부 397 기계설비 기술기준 해설 (별표 15 | {}
9e544ab8-c6ef-4b10-a89d-39cb488bcacc | 국내_기계설비_기술기준_매뉴얼_최종본 | 해 설 1. 본문 해설 및 관련 법규 건축물등에 기계실을 배치하는 경우에는 건축, 전기 등 타 공종과 충분히 협의 해야 하며, 이때 유 지관리 및 기계설비의 효율을 고려해야 하며, 주로 지하에 위치하는 기계실의 특성상 화재 등 비 상상황 시 유지관리자의 피난 등 안전사항을 종합적으로 고려해야 함 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ DA(dry area) ¦ 채광, 환기, 방습 등의 목적으로 지하실 외측에 설치하는 개방공간 출처 : 건축구조용어사전, 대한건축학회 ¦ ¦ 집단에너지 ¦ 「집단에너지사업법」에 따라 해당지역에서는 집단에너지시설 이외의 열생산시설을 설치하는 경우 허가를 받도록 규정하고 있다.(해설서 주) ¦ 2.1 기계실(계속) (4) 기타사항 ① 일반장비의 기초는 바닥마감에서 200 mm 이상으로 하며, 물탱크는 바닥마감에서 600 mm 확 보한다. 단, 공기조화기의 기초는 바닥마감에서 300 mm 이상 또는 응축수의 배수에 지장이 없 는 높이로 한다. ② 기계실의 배수 집수정은 침수방지를 고려하여 필요 크기와 개수를 배치하며, 트렌치를 설치하여 집수를 계획한다. ③ MCC 판넬 위, 전산시설, MDF 실 등에는 수배관을 설치하지 않는다. 단, 설치가 필요한 경우에는 누수 방지대책을 수립하여 설치한다. ④ 저수탱크 상부에는 오배수 배관을 설치하지 않도록 한다. 해 설 1. 본문 해설 및 관련 법규 V (4 항 1 호) 이 기준 외의 장비 기초 높이는 이 기준과 유사한 장비 기초 높이를 참조하여 설치함 398 기계설비 기술기준 매뉴얼 | {}
01c09e3f-0694-4ecb-a926-d50dcaf182cf | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 Chart Type: bar 장이기초 갑기존 갑자동차이상 장이기초 5Not specified 0Not specified 24Not specified 일반장비 13.3Not specified 0.8Not specified 0.4Not specified 저수조(H) 29Not specified 0.3Not specified 0.0Not specified 기능 14.6Not specified 0.9Not specified 0.6Not specified 600 이상 13.5Not specified 0.4Not specified 0.3Not specified 저수탱크 14.6Not specified 0.9Not specified 55Not specified V (4 항 2 호) 추가 설명 없음 국토교통부 399 기계설비 기술기준 해설 (별표 15) | {}
bc67a583-bde8-42b3-9770-be25741e10d3 | 국내_기계설비_기술기준_매뉴얼_최종본 | V (4 항 3 호) 배관 누수로 인한 전기 및 통신시설의 피해를 방지하기 위한 것으로, 부득이하게 설치 해야하는 경우에는 대책을 마련하고 해당 건축물등의 감리 승인을 득해야 함 V (4 항 4 호) 오배수관 누수로 인한 저수탱크 내 식수 오염방지를 위한 기준이며, 수도법 시행규칙 [별표 3 의 2] 저수탱크의 설치기준에 모두 만족할 경우에는 이 기준을 만족한 것으로 봄 2. 용어 V 내용 없음 --- 2.2 피트 (1) 피트의 기본계획 ① 피트는 배관 및 전기설비의 교차점 또는 분기점에는 교차공간과 통행로의 높이 등을 고려하여 구조물의 규격을 산정한다. ② 피트의 통로 유효높이(배관 등의 시설물 설치 이하의 공간을 권장)는 1.8 m 이상, 통로의 유효폭 은 1.2 m 이상으로 한다. 해 설 1. 본문 해설 및 관련 법규 V (1 항 1 호) 유지관리를 위해 사람이 출입하는 피트를 대상으로 하며, 단열재 미설치 및 밸브, 댐퍼 등의 미설치 등 유지관리가 필요 없는 피트의 경우 예외로 할 수 있음 V (1 항 2 호) 피트는 기계설비 배관과 전기설비와 의 교차 또는 분기가 되는 상황을 고려하여 유지관 리를 위한 통행로의 높이와 폭을 결정하며, 이 경우 피트의 높이는 최소 1.8 m 이상, 통로 폭은 최 소 1.2 m 이상으로 해야 함. 또한 배관의 유지보수 및 결로수 배수를 위한 트렌치 또는 배수구를 설치해야함 400 기계설비 기술기준 매뉴얼 | {}
016d1fd5-efa5-463d-8a7f-697a576e7b2d | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 ![image](/image/placeholder) 200 150 1 200 150 200 조명 전기설비 등 통로 이상 800 내부환기 트렌치 결로수 배출 예시 : 1 항 2 호, 3 항 1 호 ~ 3 호 2. 용어 내용 없음 2.2 피트(계속) (2) 배관 및 덕트의 이격 간격 확보 ① 배관과 배관 사이는 마감재 설치 후 기준으로 150 mm 이상, 배관과 벽체 및 상부 구조체 사이는 200 mm 이상으로 한다. ② 덕트와 덕트 사이는 마감재 설치 후 기준으로 300 mm 이상, 덕트와 벽체 및 상부 구조체 사이는 400 mm 이상으로 한다. 다만, 원형덕트의 지름이 600 mm 이하 경우에는 배관의 이격거리기준 을 따른다. 덕트와 배관 사이는 마감재 설치 후 기준으로 150 mm 이상으로 한다. 해 설 1. 본문 해설 및 관련 법규 (2 항 1 호 ~ 3 호) 피트 내부에서 배관과 배관, 덕트와 덕트, 덕트와 배관은 유지관리를 위해 이 기 준을 만족해야하며, 이때 마감재 설치 후 기준은 이 기준 [별표 10] 보온설비의 설계 및 시공 기준 국토교통부 401 기계설비 기술기준 해설 (별표 15) | {}
96cb4fdf-0d6f-4ef6-a130-4955a90f0a1f | 국내_기계설비_기술기준_매뉴얼_최종본 | 을 만족해야 함 시공 도중 설계변경 등의 불가피한 이유로 이격 간격을 만족하기 어려운 경우, 기계설비감리업무 수행자의 승인을 받는다면 예외로 할 수 있음 ![image](/image/placeholder) 200 400 1 단 150 1 단 2 단 150 300 3 단 2 단 [배관] [덕트] 예시 : 2 항 1 호 ~ 5 호 2. 용어 내용 없음 2.2 피트(계속) (3) 기타사항 ① 피트 내부는 환기가 될 수 있도록 계획한다. ② 피트는 외부로부터 물이 유입되지 않아야 하며, 결로수를 배출할 수 있는 구조로 한다. 피트는 원활한 유지관리를 위해 적절한 조명설비를 설치한다. 해 설 1. 본문 해설 및 관련 법규 (3 항 1 호) 일반적으로 자연환기가 불가능한 피트 공간에 적용하며, 기계환기를 통해 공기오염, 결 402 기계설비 기술기준 매뉴얼 | {}
6248a6c3-ccc4-404a-8d4b-b0f61b9926c5 | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 로, 곰팡이 발생 등을 방지하여 기계설비를 보호함과 동시에 유지관리 및 성능점검 시 유지관리 자에게 건강상 위해를 끼치지 않아야 함 환기횟수는 3~5 회/hr 로 권장하며, 피트의 상황에 따라 다르므로 설계자의 판단에 따라 결정하도 록 함 (3 항 2 호) 피트는 기계설비 외 전기 및 통신설비가 함께 설치되는 공간으로 빗물 및 지하수 등에 의한 누수 피해가 없는 구조로 설계, 시공해야 함 V (3 항 3 호) 점검이 필요한 부위(밸브, 배관 분기부위, 배관 연결부위 등)가 있는 곳에는 점멸이 가능 한 조명 설비(100 lx 이상 권장)를 설치하여야 함 2. 용어 V 내용 없음 2.3 샤프트 (1) 샤프트 기본계획 기계설비 샤프트는 사용처 인근에 배치해야 하며, 배관의 점검 및 보수, 교체가 용이하게 이루어질 수 있도록 설치한다. 해 설 1. 본문 해설 및 관련 법규 (1 항) 기계설비 배관 등은 최종 사용처까지 길이를 최소한으로 하여 에너지 손실 및 유지관리 요 소를 줄이고, 샤프트를 통한 점검 및 보수, 교체가 용이해야 함(이 기준 2.3 (4) (5)의 내부관리 샤 프트와 외부관리 샤프트 참조) 2. 용어 V 내용 없음 국토교통부 403 기계설비 기술기준 해설 (별표 15) | {}
9ed094f3-77ef-48f9-b0b3-285c33530c82 | 국내_기계설비_기술기준_매뉴얼_최종본 | 2.3 샤프트(계속) (2) 샤프트 내 배관 및 덕트의 설치간격 ① 샤프트 내에 설치되는 각종 배관 및 덕트는 설치간격 및 유지관리를 위한 적정 유효폭을 확보한 다. ② 마감재 설치 후 기준으로 배관과 배관 사이는 150 mm 이상, 배관과 벽체 사이는 200 mm 이상 으로 한다. ③ 입상배관에 층배관의 분기 및 이에 따른 밸브 등의 설치는 관리가 용이한 위치에서 분기한다. ④ 마감재 설치 후 기준으로 덕트와 덕트 사이는 300 mm 이상, 덕트와 벽체 사이는 400 mm 이상 으로 한다. 다만, 원형덕트의 지름이 600 mm 이하 경우에는 배관의 이격거리기준을 따른다. ⑤ 덕트와 배관 사이는 마감재 설치 후 기준으로 150 mm 이상으로 한다. 해 설 1. 본문 해설 및 관련 법규 V (2 항 1 호 ~ 5 호) 샤프트 내부에서 배관과 배관, 덕트와 덕트, 덕트와 배관은 유지관리를 위해 이 기준을 만족해야하며, 이 때 마감재 설치 후 기준은 이 기준 [별표 10] 보온설비의 설계 및 시공 기준을 만족해야 함 V 샤프트 내 배관 또는 덕트와 면한 벽이 유지관리 등의 작업 시 탈부착을 손쉽게 할 수 있는 등 유 지관리에 문제가 없는 경우에는 배관과 벽체 사이, 덕트와 벽체 사이의 간격을 예외로 할 수 있음 V 단열재 미설치 및 밸브, 댐퍼 등의 미설치 등 유지관리가 필요 없는 샤프트의 배관 및 덕트의 설 치 간격은 예외로 할 수 있음 V 공동주택, 오피스텔, 생활형 숙박시설 등 세대 내 샤프트와 같이 배수배관과 배기덕트만 설치되는 경우에는 예외로 할 수 있음 V 시공 도중 설계변경 등의 불가피한 이유로 샤프트 내 공간확보가 어려운 경우, 기계설비감리업무 수행자의 승인을 받는다면 예외로 할 수 있음 V 아래 그림과 같이 방화댐퍼를 샤프트와 분리하여 설치하는 경우 샤프트 내 배관 및 덕트의 설치 간격 기준 적용의 예외로 할 수 있음 404 기계설비 기술기준 매뉴얼 | {}
4609dda6-96bc-4f21-928d-39af06a1fb5a | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 KCS 31 20 20 : 2021 덕트설비공사 3.1.5 방화구획의 관통부 처리 방화구획의 관통부에는 방화댐퍼를 부착한다. 덕트와 슬리브사이에는 내화충전재로 충진한다. 방화구획부 에 방화댐퍼 설치가 곤란하여 방화구획과 떨어진 경우에는 방화구획과 댐퍼 사이의 덕트는 1.6 mm 이상의 강판제로 한다. ![image](/image/placeholder) 방화댐퍼 FUSE ◎ ◎ LINKAGE AIR FLOW 실내 CHECKER 1.6 mm 벽체형 슬리브 2. 용어 내용 없음 2.3 샤프트(계속) (3) 배관 및 덕트의 배치계획 설비배관 및 덕트의 배치는 원칙적으로 설비재의 내구성을 감안하여, 내구수명이 긴 배관 및 덕트 는 샤프트의 안쪽에, 내구수명이 짧은 배관 및 덕트는 통로 쪽에 배치한다. 해 설 1. 본문 해설 및 관련 법규 시공 도중 설계변경 등의 불가피한 이유로 점검구의 크기를 만족하기 어려운 경우, 기계설비감리 업무수행자의 승인을 받는다면 예외로 할 수 있음 V (3 항) 기계설비 배관의 내구성은 다음을 참조할 수 있음 국토교통부 405 기계설비 기술기준 해설 (별표 15 | {}
164eb845-bed4-4203-be12-a5a56e80e7af | 국내_기계설비_기술기준_매뉴얼_최종본 | 공동주택관리법 시행규칙 [별표 1] 장기수선계획의 수립기준(제 7 조제 1 항 및 제 9 조 관련) 4. 급수·가스·배수 및 환기설비 ¦ 구분 ¦ 공사종별 ¦ 수선방법 ¦ 수선주기 (년) ¦ 수선율 (%) ¦ 비고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 가. 급수설비 ¦ 1) 급수펌프 2) 고가탱크 (STS, 합성수지) 3) 급수관(강관) ¦ 전면교체 전면교체 전면교체 ¦ 10 25 15 ¦ 100 100 100 ¦ 고효율에너지 기자재 적용 (전동기 포함) ¦ ¦ 나. 가스설비 ¦ 1) 배관 2) 밸브 ¦ 전면교체 전면교체 ¦ 20 10 ¦ 100 100 ¦ ¦ ¦ 다. 배수설비 ¦ 1) 펌프 2) 배수관(강관) 3) 오배수관(주철) 4) 오배수관[폴리염화비 닐(PVC)] ¦ 전면교체 전면교체 전면교체 전면교체 ¦ 10 15 30 25 ¦ 100 100 100 100 ¦ ¦ ¦ 라. 환기설비 ¦ 환기팬 ¦ 전면교체 ¦ 10 ¦ 100 ¦ ¦ 5. 난방 및 급탕설비 ¦ 구분 ¦ 공사종별 ¦ 수선방법 ¦ 수선주기 (년) ¦ 수선율 (%) ¦ 비고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 가. 난방설비 ¦ 1) 보일러 2) 급수탱크 3) 보일러수관 4) 난방순환펌프 5) 난방관(강관) 6) 자동제어 기기 7) 열교환기 ¦ 전면교체 전면교체 전면교체 전면교체 전면교체 전체교체 전면교체 ¦ 15 15 9 10 15 20 15 ¦ 100 100 100 100 100 100 100 ¦ 고효율에너지 기자재 적용 (전동기 포함) 밸브류 포함 ¦ ¦ 나. 급탕설비 ¦ 1) 순환펌프 2) 급탕탱크 3) 급탕관(강관) ¦ 전면교체 전면교체 전면교체 ¦ 10 15 10 ¦ 100 100 100 ¦ 고효율에너지 기자재 적용 (전동기 포함) ¦ 2. 용어 내용 없음 2.3 샤프트(계속) (4) 내부관리 샤프트 유지관리 공간 확보 ① 설비 샤프트는 내부에서 관리가 용이한 샤프트로 설치한다. ② 유지관리를 위하여 배관 전면부와 구조물 사이의 유효폭은 900 mm 이상으로 한다. 해 설 1. 본문 해설 및 관련 법규 V (4 항 2 호) 시공 도중 설계변경 등의 불가피한 이유로 유효폭을 만족하기 어려운 경우, 기계설비감 406 기계설비 기술기준 매뉴얼 | {}
d1d18bed-9a36-4c5a-b070-de7ea8c5998c | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 리업무수행자의 승인을 받는다면 예외로 할 수 있음 V (4 항 1 호 ~ 2 호) 내부관리 샤프트의 설계 예는 다음과 같음 ![image](/image/placeholder) 200 150 150 150 200 ④ ③ ② 1 400 ○ ○ 이상 ① 보급수관 150 900 이상 ② 우수관 ③ 펌핑관 ⑤ ④ 통기관 400 이상 ⑤ 증기공급관 150 ⑥ 증기응축수관 ⑥ ⑦ 급수관 ⑧ 급탕관 150 ⑨ 환탕관 ⑩ 배수관 ⑦ 150 150 200 ⑪ 오수관 / 150 ⑫ 정화조 배기덕트 ⑧ ○ 200 ⑨ 200 ⑪ 점검구 600 x1,600 예시 : 2 항 1 호 ~ 5 호, 4 항 2 호 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 내부관리 샤프트 ¦ 샤프트의 규모가 커서 관리자가 샤프트 내에 들어가 유지관리 작업이 이루어져야 하 는 일반적인 형태의 샤프트(해설서 주) ¦ ![image](/image/placeholder) 2.3 샤프트(계속) (5) 외부관리 샤프트 유지관리 공간 확보 외부관리 샤프트의 경우 샤프트 내의 모든 시설을 외부에서 용이하게 관리 할 수 있어야 한다. 해 설 1. 본문 해설 및 관련 법규 (5 항) 외부관리 샤프트의 설계 예는 다음과 같음 국토교통부 407 기계설비 기술기준 해설 (별표 15) | {}
4a55a0fc-e77d-461f-89dd-16e4ff7c0217 | 국내_기계설비_기술기준_매뉴얼_최종본 | ![image](/image/placeholder) 200 150 150 150 200 200 건식 벽체 예시 : 5 항 2. 용어 ¦ 용 어 ¦ 해 설 ¦ ¦ --- ¦ --- ¦ ¦ 외부관리 샤프트 ¦ 샤프트 내 설치하는 배관, 덕트의 수가 적거나, 건축적인 이유로 충분한 샤프트 면적 을 확보하지 못해 내부관리 샤프트를 설치할 수 없는 경우 관리자가 외부에서 유지 관리 등의 작업이 가능한 샤프트(해설서 주) ¦ 2.4 점검구 등 (1) 피트 점검구 ① 건물 중간에 설치된 피트의 점검구는 폭 600 mm 이상, 높이 1 600 mm 이상의 출입문 방식으로 계획할 것을 권장하며, 최소 600 mm x 600 mm 이상으로 한다. ② 최하층의 피트 점검구는 600 mm x 900 mm 이상으로 한다. 해 설 1. 본문 해설 및 관련 법규 (1 항 1 호) 피트의 점검구는 이 기준을 만족해야 하며, 단, 시공 도중 설계변경 등의 불가피한 이유 로 점검구의 크기를 만족하기 어려운 경우, 기계설비감리업무수행자의 승인을 받는다면 예외로 할 수 있음 2. 용어 내용 없음 ---- 408 기계설비 기술기준 매뉴얼 | {}
1c5ec33f-d180-409c-ba3f-e0c6775b59bb | 국내_기계설비_기술기준_매뉴얼_최종본 | 3. 기계설비 기술기준 해설 2.4 점검구 등(계속) (2) 샤프트 점검구 ① 내부관리 샤프트에 설치되는 점검구의 크기는 600 mm x 1 600 mm 이상으로 한다. ② 외부관리 샤프트에 설치되는 점검구의 크기는 600 mm x 600 mm 이상으로 한다. ③ 공동주택(「건축법」 시행령 [별표 1]) 등의 전용공간 내부 샤프트의 배관 및 덕트의 유지관리 점검 이 유효한 경우와 배기덕트 등은 점검구 설치를 제외할 수 있다. 해 설 1. 본문 해설 및 관련 법규 V (2 항 1 호 ~ 2 호) 샤프트의 점검구는 이 기준을 만족해야 함(이 기준 2.3 (4) (5)의 내부관리 샤프트 와 외부관리 샤프트 참조) V (2 항 2 호) 외부관리 샤프트의 점검구 높이는 작업자가 서서 작업이 가능하도록 점검구를 설치함 V (2 항 3 호) 공동주택, 오피스텔 처럼 세대내 샤프트와 같이 배수배관과 배기덕트만 설치되는 샤프 트의 경우에는 점검구 설치를 예외로 할 수 있음 V 시공 도중 설계변경 등의 불가피한 이유로 점검구의 크기를 만족하기 어려운 경우, 기계설비감리 업무수행자의 승인을 받는다면 예외로 할 수 있음 2. 용어 V 내용 없음 --- --- 2.4 점검구 등(계속) (3) 천장 점검구 ① 천장 점검구의 설치 가. 덕트 내 각종 댐퍼 설치 부위에 설치한다. 나. 오 、 배수 배관의 90° 분기 부분(청소구 설치 부위)에 설치한다. 다. 각종 배관 중 관리용 밸브가 설치된 부분에 설치한다. 라. 기타 유지관리가 필요한 개소에 설치한다. 마. 천장 속에 장비가 설치되고 점검이 필요한 부분에 설치한다. ② 점검구의 크기는 600 mm x 600 mm 이상으로 한다. 해 설 1. 본문 해설 및 관련 법규 (3 항 1 호 가 ~ 마) 천장 마감재 탈부착이 쉽거나, 천장 카세트형 장비 등 점검구가 필요 없는 장비 의 경우에는 또는 주거공간의 침실 및 거실 등의 경우에는 점검구 설치를 제외할 수 있음 국토교통부 409 기계설비 기술기준 해설 (별표 15 | {}
ff8dd0e2-8cb1-4a85-a8f5-81fa3591bb8f | 국내_기계설비_기술기준_매뉴얼_최종본 | (3 항 2 호) 천장의 점검구 한 면의 길이가 기준을 충족하기 어려운 경우에는 면적으로 환산하여 적 용할 수 있으며, 천장의 일부를 탈착하여 점검구로 사용할 수 있는 경우에는 점검구 설치를 하지 않을 수 있음 2. 용어 V 내용 없음 410 기계설비 기술기준 매뉴얼 | {}
331dac31-0b39-4aff-a569-2e748726e071 | 국내_기계설비_기술기준_매뉴얼_최종본 | 부 록 1. 기계설비 기술기준 ···· ·············412 2. 기계설비 기술기준 그림 해설 ···418 3. 관련기관 연락처 ········421 4. 별지 서식 등 ··········431 - 기계설비 기술기준 별지서식[제 1 호 ~ 제 6 호] - 기계설비법 시행규칙 별지서식[제 4 호 ~ 제 9 호] - 검토서 및 첨부서류 작성양식 | {}
ed09e2b4-d045-4cc2-b0dd-8d47e0d331d1 | 국내_기계설비_기술기준_매뉴얼_최종본 | 기계설비 기술기준 [시행 2021. 6. 7.] [국토교통부고시 제 2021-851 호, 2021. 6. 7., 제정.] 국토교통부(건설산업과), 044-201-3540 제 1 장 총 칙 제 1 조(목적) 이 고시는 「기계설비법」 제 14 조에 따라 기계설비의 안전과 성능확보를 위하 여 필요한 기술기준과 같은 법 제 15 조에 따른 기계설비의 착공 전 확인과 사용 전 검사에 관하여 필요한 사항을 규정함을 목적으로 한다. 제 2 조(정의) 이 고시에서 사용하는 용어의 정의 는 다음과 같다. 1. "기계설비"란 「기계설비법」 (이하 "법"이라 한다) 제 2 조제 1 호에 따른 설비로서 「기계설 비법 시행령」 (이하 "영"이라 한다) 별표 1 의 구분에 따른 설비를 말한다. 2. "기계설비공사"란 「건설산업기본법」 제 2 조제 4 호에 따른 건설공사 중 기계설비와 관련 된 공사를 말한다. 3. "기계설비설계자"란 「건설기술 진흥법」 제 26 조에 따른 건설기술용역사업자, 「엔지니어 링산업 진흥법」 제 21 조에 따른 엔지니어링사업자, 「기술사법」 제 6 조에 따른 기술사사무 소 또는 「건축사법」 제 23 조에 따른 건축사사무소 등에 소속되어 기계설비공사의 설계 업 무를 수행하는 자를 말한다. 4. "기계설비시공자"란 「건설산업기본법」 제 9 조에 따라 건설업을 등록하고 기계설비공사 를 하는 자를 말한다. 5. "기계설비감리업무수행자"란 「건설산업기본법」 제 2 조제 8 호, 「건설기술 진흥법」 제 2 조제 5 호, 「건축법」 제 2 조제 15 호, 「주택법」 제 43 조 및 기타 관계 법령에 따라 기계설비 공사와 관련된 건설사업관리 및 감리업무 등을 수행하는 자를 말한다. 6. "현장배치기계설비기술인"이란 「건설산업기본법」 제 40 조 및 같은 법 시행령 제 35 조에 따라 기계설비공사 현장에 배치된 건설기술인을 말한다. 7. "현장배치기계설비감리인"이란 「건설기술 진흥법 시행령」 제 60 조에 따라 기계설비공사 현장에 배치되어 제 5 호에 따른 기계설비공사의 감리업무를 수행하는 건설기술인, 「건축 법」 제 25 조에 따른 공사감리자 또는 「주택법」 제 43 조에 따른 감리자를 말한다. 제 3 조(적용범위) 이 고시는 기계설비공사의 설계, 시공 및 감리에 대하여 적용한다. 제 4 조(기술기준의 준수) 기계설비설계자, 기계설비시공자 및 기계설비감리업무수행자 등은 기술기준을 준수해야 한다. 제 5 조(다른 규정과 의 관계) 기계설비 기술기준 및 기계설비의 착공 전 확인, 사용 전 검사와 관련하여 다른 법령에 특별한 규정이 있는 경우를 제외하고는 이 고시에서 정하는 바에 따 른다. 412 기계설비 기술기준 매뉴얼 | {}
c0645a2a-b40a-43e9-bd0c-68efb97b67a1 | 국내_기계설비_기술기준_매뉴얼_최종본 | 제 2 장 기계설비의 설계 및 시공기준 제 1 절 일반사항 제 6 조(기계설비 설계의 일반원칙) 기계설비는 다음 각 호의 기준에 따라 설계한다. 1. 기계설비의 시공, 감리, 유지관리 등 전 과정을 고려하여 합리적으로 설계할 것 2. 공정관리에 지장이 없고 하자 책임 구분이 용이하도록 기계설비와 건축 등 타 분야의 공종을 구분하여 설계할 것 3. 에너지 절약을 위한 설계 및 환경친화적인 설비의 우선 사용을 검토할 것 4. 신기술 및 신공법의 적용 가능 여부를 검토할 것 제 7 조(기계설비 시공의 일반원칙) 기계설비는 다음 각 호의 기준에 따라 시공한다. 1. 기계설비공사의 공정표, 시공계획서 등을 준수할 것 2. 기계설비 설계도면, 시방서, 부하 및 장비선정계산서(이하 "설계도서"라 한다) 등을 충분 히 검토하여 현장 여건에 맞는 적절한 시공계획을 수립할 것 3. 기계설비가 그 기능을 충분히 발휘할 수 있도록 설계도서, 시공상세도 등에 적합하게 시공할 것 제 8 조(기계설비의 설계 및 시공 기준) 기계설비의 구분에 따른 설계 및 시공기준은 다음 각 호와 같다. 1. 열원설비 및 냉난방설비 : 별표 1 2. 공기조화설비 : 별표 2 3. 환기설비 : 별표 3 4. 위생기구설비 : 별표 4 5. 급수 · 급탕설비 : 별표 5 6. 오배수 · 통기 및 우수배수설비 : 별표 6 7. 오수정화 · 물재이용설비 : 별표 7 8. 배관설비 : 별표 8 9. 덕트설비 : 별표 9 10. 보온설비 : 별표 10 11. 자동제어설비 : 별표 11 12. 방음 · 방진 · 내진설비 : 별표 12 13. 플랜트설비 : 별표 13 14. 특수설비 : 별표 14 제 9 조(유지관리를 고려한 설계 및 시공) ① 기계설비는 효율적인 유지관리를 위하여 다음 각 호의 기준에 따라 설계 및 시공한다. 1. 기계설비를 구성하는 장비, 배관, 덕트 및 각종 부속품의 유지관리가 용이하도록 할 것 2. 필요한 경우 기계설비의 유지관리비용 분담, 개별제어 또는 통합제어 등이 가능하도록 할 것 3. 점검구 등 기계설비의 유지관리를 위한 최소한의 공간 이상을 확보할 것 ② 제 1 항에 따른 기계설비 유지관리를 고려한 설계 및 시공기준은 별표 15 와 같다. 국토교통부 413 | {}
c53af377-338c-485a-b720-f17fb9c5361f | 국내_기계설비_기술기준_매뉴얼_최종본 | 제 10 조(기계설비 설계대가 적용 등) 법 제 15 조제 1 항에 따른 기계설비공사를 발주한 자(이하 "발주자"라 한다)는 이 고시에서 정하는 기계설비 설계에 대하여 「건설기술 진흥법」 제 37 조 또는 「엔지니어링산업 진흥법」 제 31 조에 따른 적정한 대가를 지급해야 하며, 이를 하도급하는 경우에는 「하도급거래 공정화에 관한 법률」 제 4 조를 준수해야 한다. 제 2 절 세부사항 제 11 조(시공계획서) ① 기계설비시공자는 기계설비공사의 착공 전에 시공계획서를 작성하여 기계설비감리업무수행자의 승인을 받아야 한다. ② 기계설비시공자는 중량물의 반입설치 등 위험 공종이 포함되는 기계설비공사에 대한 시공계획서를 작성하는 경우에는 공사 방법, 사용 장비 및 공종별 세부 안전대책을 명시해 야 한다. 제 12 조(시공상세도면의 작성 등) ① 기계설비시공자는 기계설비공사의 시공 정확도 및 품질 향상과 공사현장의 안전 확보를 위하여 필요한 경우 「건설기술 진흥법」 제 48 조제 4 항제 2 호에 따른 시공상세도면을 작성하여 기계설비감리업무수행자의 승인을 받아야 한다. ② 발주자는 기계설비시공자가 제 1 항에 따른 시공상세도면을 작성하였을 때에는 「엔지니 어링산업 진흥법」 제 31 조에 따른 적정한 대가를 지급해야 한다. 제 13 조(공정표) ① 기계설비시공자는 기계설비공사의 착공 전에 공정표를 작성하여 기계설 비감리업무수행자의 승인을 받아야 한다. ② 기계설비시공자는 제 1 항에 따른 공정표가 변경될 경우 즉시 변경공정표를 작성하고 기 계설비감리업무수행자의 승인을 받아야 한다. 제 14 조(현장안전관리 등) ① 발주자 및 기계설비시공자는 기계설비공사 현장의 안전관리 및 산업재해 예방을 위해 「산업안전보건법」 및 「산업안전보건기준에 관한 규칙」 에서 정한 제반 기준을 준수해야 한다. ② 발주자는 기계설비공사 현장의 안전관리 및 산업재해 예방을 위해 「산업안전보건법」 제 72 조에 따른 산업안전보건관리비를 공사금액에 계상해야 한다. 제 15 조(유지관리지침서) ① 기계설비시공자는 기계설비공사를 완료한 후 「기계설비 유지관 리기준」 제 6 조에 따른 유지관리지침서를 작성하여 기계설비감리업무수행자에게 제출해야 한다. ② 기계설비감리업무수행자는 제 1 항에 따른 유지관리지침서의 기계설비 유지관리기준 적 합 여부를 확인한 뒤 발주자에게 제출해야 하며, 보완이 필요한 사항에 대하여 기계설비시 공자에게 보완을 요청할 수 있다. 제 16 조(기계설비의 시공 등) ① 기계설비공사는 다음 각 호의 사항을 반영하여 시공한다. 1. 공사 현장에는 시공 및 안전관리에 필요한 울타리와 가설사무실 등을 설치할 것 2. 화기를 사용하는 현장에는 불연 재료를 사용한 울타리를 설치하는 등 화재 예방을 위해 필요한 조치를 할 것 3. 가설공사의 종류, 규모, 장소 및 공기를 고려하여 적합한 재료를 사용한 기계설비공사용 비계를 적절한 구조로 설치하며, 세부 기준은 비계공사 표준시방서(KCS 21 60 00)에 따를 것 414 기계설비 기술기준 매뉴얼 | {}
bb820b81-e784-49e0-a011-bda2d32fa4e0 | 국내_기계설비_기술기준_매뉴얼_최종본 | 4. 기계설비공사를 위한 기기 및 설비의 반입과 반출이 용이하며 안전한 구조로 설치된 작 업용 통로를 확보할 것 5. 공사 현장에는 작업자의 추락 또는 설비의 낙하 등 안전사고를 방지하기 위하여 필요한 제반 시설물을 공사 진행에 지장이 없도록 설치할 것 6. 가스관, 상수도관, 하수도관, 전기관 등 공사 현장의 장애물 및 매설물을 이설 또는 철 거할 경우 그 규모와 범위는 설계도서에 따를 것 7. 공사용 및 시험용 전력, 용수, 배수 및 기타 공사에 필요한 설비의 시공은 공사 진행에 지장이 없도록 할 것 8. 이 고시에서 규정하고 있지 않는 사항에 대해서는 현장 여건을 고려하여 기계설비감리 업무수행자와 협의 하여 정할 것 ② 기타 기계설비공사에 대한 부대공사는 다음 각 호의 사항을 반영하여 시공한다. 1. 기계설비공사에 따른 토공사, 철근콘크리트공사, 미장공사, 방수공사 및 강재공사는 각 각 토공사 표준시방서(KCS 11 20 00), 콘크리트공사 표준시방서(KCS 14 20 00) 및 건축 공사 표준시방서(KCS 41 00 00)를 따를 것 2. 기계설비공사에 따른 건축전기설비의 공사는 「건축전기설비 설계기준」 등 관련 규정 을 따를 것 제 3 장 기계설비의 착공 전 확인과 사용 전 검사 제 17 조(대상 건축물등의 확인) 영 제 11 조에 따른 기계설비의 착공 전 확인과 사용 전 검사 의 대상 건축물등의 연면적 및 바닥면적은 다음 각 호의 기준에 따라 계산한다. 1. 연면적 : 「건축법 시행령」 제 119 조제 1 항제 4 호에 따른 연면적 2. 바닥면적 : 「건축법 시행령」 제 119 조제 1 항제 3 호에 따른 바닥면적 제 18 조(착공 전 확인 절차 등) ① 특별자치시장 · 특별자치도지사 · 시장 · 군수 · 구청장(구청 장은 자치구의 구청장을 말하며, 이하 "시장 · 군수 · 구청장"이라 한다)은 영 제 12 조제 1 항에 따라 기계설비공사 착공 전 확인신청서를 받은 경우에는 해당 설계도서의 내용이 제 8 조에 따른 기계설비의 설계 기준에 적합하게 작성되었는지 확인해야 한다. ② 시장 · 군수 · 구청장은 기계설비공사 착공 전 확인신청서가 다음 각 호의 내용에 따라 올바르게 작성되었는지 확인해야 한다. 1. 신청인(건축주) : 발주자 또는 그 대리인 2. 공사현장 명칭 및 주소 : 기계설비공사 현장의 명칭 및 주소 3. 공사의 종류 : 기계설비공사의 종류 4. 구조 및 용도 : 건축허가서에 기재된 해당 건축물등의 구조 및 용도 5. 건축면적 및 연면적/규모(층) : 건축허가서에 기재된 건축면적 및 연면적 등 6. 건축허가번호 및 허가일 : 건축허가서에 기재된 건축허가번호 및 허가일 7. 착공 및 준공예정일 : 기계설비공사의 착공 및 준공예정일 8. 기계설비설계자 : 제 2 조제 3 호에 따른 기계설비설계자 9. 기계설비시공자 : 제 2 조제 4 호에 따른 기계설비시공자(하도급의 경우 하도급자를 포함한 다) 10. 기계설비감리업무수행자 : 제 2 조제 5 호에 따른 기계설비감리업무수행자 국토교통부 415 | {}
f43ee0c6-3726-4fbe-8cf7-2dcb13b3b8a2 | 국내_기계설비_기술기준_매뉴얼_최종본 | 11. 현장배치기계설비기술인 : 제 2 조제 6 호에 따른 현장배치기계설비기술인 12. 현장배치기계설비감리인 : 제 2 조제 7 호에 따른 현장배치기계설비감리인 제 19 조(기계설비감리업무수행자의 확인 등) ① 기계설비설계자 또는 기계설비시공자는 기계 설비공사를 시작하기 전에 별지 제 1 호서식의 기계설비 착공 전 확인표를 작성하여 기계설 비감리업무수행자에게 제출해야 한다. ② 기계설비감리업무수행자는 제 1 항에 따라 제출받은 서류의 적합성을 확인하여 기계설비 가 제 8 조에 따른 설계기준에 적합하게 설계되었는지 검토해야 한다. ③ 기계설비감리업무수행자는 제 2 항에 따른 검토를 마친 경우에는 별지 제 2 호서식의 기계 설비 착공적합 확인서를 작성하고, 이를 제 1 항에 따라 제출받은 서류와 함께 발주자에게 제출해야 한다. ④ 기계설비시공자는 기계설비공사를 끝낸 경우 기계설비의 성능 및 안전평가를 수행하고, 다음 각 호의 서류를 작성하여 기계설비감리업무수행자에게 제출해야 한다. 1. 별지 제 3 호서식의 기계설비 사용 전 확인표 2. 별지 제 4 호서식의 기계설비 성능확인서 3. 별지 제 5 호서식의 기계설비 안전확인서 ⑤ 기계설비감리업무수행자는 제 4 항에 따른 성능 및 안전평가에 입회하여 기계설비가 제 8 조에 따른 시공기준에 적합하게 시공되었는지 검토해야 한다. ⑥ 기계설비감리업무수행자는 제 4 항에 따라 제출받은 서류의 적합성을 확인하고 제 5 항에 따른 검토를 마친 경우에는 별지 제 6 호서식의 기계설비 사용적합 확인서를 작성하고, 이를 제 4 항에 따라 제출받은 서류와 함께 발주자에게 제출해야 한다. 제 20 조(사용 전 검사 절차 등) ① 시장 · 군수 · 구청장은 영 제 13 조제 1 항에 따라 기계설비 사용 전 검사신청서를 받은 경우에는 해당 기계설비공사가 제 8 조에 따른 기계설비의 시공 기준에 적합하게 시공되었는지 검사해야 한다. ② 시장 · 군수 · 구청장은 기계설비공사 사용 전 검사신청서가 다음 각 호의 내용에 따라 올바르게 작성되었는지 확인해야 한다. 1. 신청인(건축주) : 발주자 또는 대리인 2. 기계설비시공자 : 제 2 조제 4 호에 따른 기계설비시공자(하도급의 경우 하도급자를 포함) 3. 기계설비감리업무수행자 : 제 2 조제 5 호에 따른 기계설비감리업무수행자 4. 건축허가번호 및 허가일 : 건축허가서에 기재된 건축허가번호 및 허가일 5. 공사의 종류 : 기계설비공사의 종류 6. 구조 및 용도 : 건축허가서에 기재된 해당 건축물등의 구조 및 용도 7. 건축면적 및 연면적/규모(층수) : 건축허가서에 기재된 건축면적 및 연면적 등 8. 착공일 및 완공일 : 기계설비공사의 착공 및 완공일 9. 검사 희망 연월일 : 기계설비공사의 사용 전 검사 희망일 제 21 조(업무매뉴얼 제작 및 배포) 국토교통부장관은 착공 전 확인과 사용 전 검사 업무의 효 율적인 집행과 관계 행정기관 및 이해당사자 간의 민원 해소 등을 위하여 업무매뉴얼을 제 작하여 배포할 수 있다. 416 기계설비 기술기준 매뉴얼 | {}
6a25411f-0dd8-43e9-b981-5b6beeb75238 | 국내_기계설비_기술기준_매뉴얼_최종본 | 제 4 장 보 칙 제 22 조(기술기준의 관리 등) ① 국토교통부장관은 이 고시를 개정하거나 폐지하려는 경우에 는 관계 중앙행정기관, 지방자치단체의 장 또는 기계설비 관련 단체의 의견을 수렴해야 한 다. ② 국토교통부장관은 이 고시에 대한 개정 업무를 효율적으로 수행하기 위하여 국내외 관 련 자료의 수집, 조사 및 연구 등을 실시할 수 있다. 이 경우 전문성이 요구되는 시험 · 조 사 · 연구가 필요한 경우 그 업무의 일부를 관련 전문연구기관 등에 의뢰할 수 있다. 제 23 조(기계설비 기술기준에 대한 특례) 신기술 · 신공법의 도입이 필요하거나, 공사의 특성 및 현장 여건에 따라 이 고시에서 규정하고 있지 않는 기계설비 설계 · 시공기준을 적용할 필요가 있다고 인정되는 경우에는 발주자와 기계설비감리업무수행자가 협의 하여 이 고시 의 일부를 적용하지 아니할 수 있다. 제 24 조(재검토기한) 국토교통부장관은 이 고시에 대하여 「훈령 · 예규 등의 발령 및 관리에 관한 규정」 에 따라 2021 년 7 월 1 일을 기준으로 매 3 년이 되는 시점(매 3 년째의 6 월 30 일까지를 말한다)마다 그 타당성을 검토하여 개선 등의 조치를 해야 한다. 부칙 <제 2021-851 호, 2021. 6. 7.> 제 1 조(시행일) 이 고시는 발령한 날부터 시행한다. 제 2 조(기계설비 설계 및 시공 기준에 관한 적용례) 제 2 장에 따른 기계설비의 설계 및 시공에 관한 기준은 이 고시 시행 이후 설계계약을 체결하는 기계설비공사부터 적용한다. 제 3 조(기계설비 착공 전 확인 등에 관한 적용례) 제 18 조부터 제 20 조까지는 이 고시 시행 이 후 설계계약을 체결하는 기계설비공사부터 적용한다. 국토교통부 417 | {}
27221100-e81b-43a7-9212-d38cfd61a6be | 국내_기계설비_기술기준_매뉴얼_최종본 | 기계설비 기술기준 그림 해설 [제 1 장] 총칙 ![image](/image/placeholder) 제 1 조(목적) 제 3 조(적용범위) · 기계설비 안전 및 성능확보 · 착공 전 확인/사용 전 검사 필요 사항 규정 제 4 조(기술기준의 준수) 기계설비설계자 제 2 조(정의) · "기계설비설계자"란 「건설기술 진흥법」 제 기계설비시공자 26 조에 따른 건설기술용역사업자, 「엔지니어 링산업 진흥법」 제 21 조에 따른 엔지니어링사 기계설비감리업무수행자 업자, 「기술사법」 제 6 조에 따른 기술사사무소 또는 「건축사법」 제 23 조에 따른 건축사사무 소 등에 소속되어 기계설비공사의 설계 업무 를 수행하는 자를 말한다. · "기계설비시공자"란 「건설산업기본법」 제 9 조에 따라 건설업을 등록하고 기계설비공사 를 하는 자를 말한다. · "기계설비감리업무수행자"란 「건설산업기 본법」 제 2 조제 8 호, 「건설기술 진흥법」 제 2 조 제 5 호, 「건축법」 제 2 조제 15 호, 「주택법」 제 그외 43 조 및 기타 관계 법령에 따라 기계설비공사 와 관련된 건설사업관리 및 감리업무 등을 수 · 발주자 행하는 자를 말한다. · "현장배치기계설비기술인"이란 「건설산업 · 시장, 군수, 구청장 기본법」 제 40 조 및 같은 법 시행령 제 35 조에 따라 기계설비공사 현장에 배치된 건설기술 인을 말한다. 제 5 조(다른 규정과 의 관계) "현장배치기계설비감리인"이란 「건설기술 진흥법 시행령」 제 60 조에 따라 기계설비공사 현장에 배치되어 제 5 호에 따른 기계설비공사 의 감리업무를 수행하는 건설기술인, 「건축법」 제 25 조에 따른 공사감리자 또는 「주택법」 제 43 조에 따른 감리자를 말한다. [제 2 장] 기계설비의 설계 및 시공기준(1/2) 제 1 절 일반사항 ![image](/image/placeholder) 제 6 조(기계설비 설계의 일반원칙) 제 8 조(기계설비의 설계 및 시공기준) · 시공, 감리, 유지관리 등 전 과정 합리적 설계 · 열원설비 및 냉난방설비 : 별표 1 · 공정관리 지장없고, 하자 책임 구분 용이하도 · 공기조화설비 : 별표 2 록 타 분야의 공종 구분하여 설계 · 환기설비 : 별표 3 · 에너지 절약, 환경친화적 설비 우선 사용 검토 · 위생기구설비 : 별표 4 · 신기술 및 신공법 적용 가능 여부 검토 · 급수 · 급탕설비 : 별표 5 · 오배수 · 통기 및 우수배수설비 : 별표 6 · 오수정화 · 물재이용설비 : 별표 7 · 배관설비 : 별표 8 · 덕트설비 : 별표 9 · 보온설비 : 별표 10 · 자동제어설비 : 별표 11 · 방음 · 방진 · 내진설비 : 별표 12 · 플랜트설비 : 별표 13 · 특수설비 : 별표 14 제 7 조(기계설비 시공의 일반원칙) 제 9 조(유지관리를 고려한 설계 및시공) 제 10 조(기계설비 설계대가 적용등) · 공정표, 시공계획서 등 준수 · 장비, 배관, 덕트 및 각종 부속품 유지관리 용 · 발주자 : 「건설기술 진흥법」 제 37 조 또는 「엔 설계도서 등을 충분히 검토, 현장 여건에 맞는 이 지니어링산업 진흥법」 제 31 조에 따른 적정 대 시공계획 수립 · 유지관리비용 분담, 개별제어 또는 통합제어 가 지급 기능 발휘 위해 설계도서, 시공상세도 등에 적 등이 가능할 것 · 하도급의 경우 : 「하도급거래 공정화에 관한 합하게 시공 · 점검구 등 기계설비 유지관리를 위한 최소한 법률」 제 4 조 준수 공간 확보: 별표 15 418 기계설비 기술기준 매뉴얼 | {}
c9de2fd9-f29c-4b36-ae88-2e0250440913 | 국내_기계설비_기술기준_매뉴얼_최종본 | [제 2 장] 기계설비의 설계 및 시공기준(2/2) 제 2 절 세부사항 ![image](/image/placeholder) 제 14 조(현장안전관리 등) = 산업안전보건법 및 산업안전보건기준에 관한 규 칙 준수 안전관리 및 산업재해 예방을 위해 산업안전보건 관리비 공사비에 반영 제 11 조(시공계획서) 제출 · 착공 전 시공계획서 작성 · 위험공종 공사방법, 사용장비 및 안전대책 반영 제출 제 12 조(시공상세도면의 작성등) · 시공 정확성, 품질향상, 안전확보 필요시 · 발주자는 대가 지급 제 16 조(기계설비의 시공등) 제 13 조(공정표) · 공사현장의 시공 및 안전에 필요한 조치 · 착공 전 공정표 및 변경공정표 · 기계설비의 반입, 반출이 용이하도록 통로 확보 제출 · 현장 장애물, 매설물의 이설 또는 철거에 필요한 제 15 조(유지관리지침서) 조치 · 건축, 전기 등 기타 관련 규정에 따라 필요한 조치 · 준공도면, 시방서, 부하계산서, 운용매뉴얼 등 [제 3 장] 기계설비의 착공 전 확인과 사용 전 검사(1/2) ![image](/image/placeholder) 제 19 조(기계설비감리업무수행자의 확인 등) 제 18 조(착공 전 확인 절차등) · 기계설비착공적합확인표 · 기계설비사용적합확인표 제 20 조(사용 전 검사 절차등) 기술기준 별지 제 1 호서식 기술기준 별지 제 3 호서식 . 기계설비공사 설계도서 사본 기계설비공사 준공설계도서 사본 · 기계설비성능확인서 · 기계설비설계자 등록증 사본 기계설비사용적합확인서 기술기준 별지 제 4 호서식 · 기계설비 착공 전 확인신청서 에너지이용합리화법에 따른 검사증 · 기계설비안전확인서 시행규칙 별지 제 4 호서식 · 고압가스안전관리법에 따른 완성검사 기술기준 별지 제 5 호서식 증 기계설비공사 착공 전 확인신청 · 기계설비착공적합확인서 · 기계설비사용적합확인서 · 기계설비 사용 전 검사신청서 기술기준 별지 제 2 호서식 기술기준 별지 제 6 호서식 시행규칙 별지 제 7 호서식 기계설 사용 전 검사신청서 전송 제출 관한 동북(신고)번호 기재물이 감리경우 구성하 보장 회사 "현질 응용 번호 검사 위험 FE 공서의 종류 구호 일 용도 일자인 부칙 건축산육 생명혁/대표(중부) 해결하는 해냄을 현금을 2021. 6. 7 시행 반월일 이후 설계계약 충분이었 베이스프매 1 장, 같은 합 시행령 제 11 조제 1 항 : 공부 8 사용규칙 특별자치시장 특별자치도지사 · 시장 · 군수 자치구구청장 에 적용 전환합니다. 특별자치시장 특별자치도지사 시장 + 군수 · 자치구구청장 제출 국토교통부 419 | {}
78262f7f-85cd-4308-a17a-c5a8c6acfaf5 | 국내_기계설비_기술기준_매뉴얼_최종본 | [제 3 장] 기계설비의 착공 전 확인과 사용 전 검사(2/2) ![image](/image/placeholder) 제 17 조(대상 건축물등의 확인) 제 21 조(업무매뉴얼 제작 및 배포) · 연면적 : 「건축법 시행령」 제 119 조제 1 항제 4 · 목적 : 착공 전 확인과 사용 전 검사 업무의 효 호에 따른 연면적 율적인 집행과 관계 행정기관 및 이해당사자 바닥면적 : 「건축법 시행령」 제 119 조제 1 항제 간의 민원 해소 3 호에 따른 바닥면적 연면적 = a1 + a2 + b 2 층_바닥면적(a2) 1 층 바닥면적(a1) 기계설비 기술기준 매뉴얼 지하층 바닥면적(b) 01 기계설비공사 업무의 절차와 방법 최 종 본 기계설비법 시행령 [별표 5] · 용도별 건축물 중 연면적 1 만제곱 이상 2022. 04. 11. 기록불행 시흥 7 주세 · 에너지 대량소비 건축물 아파트 및 연립주택 건축법 시행령 별표 1 바닥면적 합계 5 백제곱미터 이상 건축물 국토교통부 냉동/냉장/항은항습 or 특수청정 목욕장, 놀이형시설(실내물놀이) - 바닥면적 합계 2 천제곱미터 이상 건축물 기숙사, 의료시설, 유스호스텔, 숙박시설 · 바닥면적 합계 3 천제곱미터 이상 건축물 판매시설, 연구소, 업무시설 지하역사 및 연면적 2 천제곱 이상 지하도 상가 [제 4 장] 보칙 및 부칙 ![image](/image/placeholder) 보칙 부칙 제 22 조(기술기준의 관리등) 제 1 조(시행일) · 고시의 개정/폐지 시 관계 중앙행정기관, 지방 · 발령 일부터 시행 자치단체의 장 또는 기계설비 관련 단체의 의 견을 수렴해야 함 · 전문성이 요구되는 시험 · 조사 · 연구가 필요 제 2 조(기계설비 설계 및 시공 기준에 관한 적용례) 한 경우 그 업무의 일부를 관련 전문연구기관 · 제 2 장에 따른 기계설비의 설계 및 시공에 관한 기 등에 의뢰 가능 준은 이 고시 시행 이후 설계계약을 체결하는 기 계설비공사부터 적용 CASE 2 를 기준으로 함 설계계약 A 설계계약 B 제 23 조(기계설비 기술기준에 대한 특례) CASE 1 발주자 + 건축 건축 + 기계설비 · 신기술 · 신공법 도입 필요, 공사의 특성 및 현 건축설계 장 여건에 따라 이 고시에서 규정하고 있지 설계계약 A 설계계약 B 않는 기계설비 설계 · 시공기준을 적용할 필요 CASE 2 발주자 + 건축 건축 + 기계설비 가 있다고 인정되는 경우에는 발주자와 기계 건축설계 설비감리업무수행자가 협의 하여 이 고시의 일 부를 적용하지 아니할 수 있다 기술기준 부재 20.04.18 21.06.07 법 시행 기술기준 고시 제 23 조(기계설비 기술기준에 대한 특례) 제 3 조(기계설비 착공 전 확인 등에 관한 적용례) . 2021 년 7 월 1 일을 기준으로 매 3 년이 되는 시 · 제 18 조부터 제 20 조까지는 이 고시 시행 이후 설 점(매 3 년째의 6 월 30 일까지를 말한다)마다 계계약을 체결하는 기계설비공사부터 적용한다. 그 타당성을 검토하여 개선 등 조치 해야 함 420 기계설비 기술기준 매뉴얼 | {}
bef8059c-0dc7-4f6e-b0ec-37268e5575f0 | 국내_기계설비_기술기준_매뉴얼_최종본 | 관련기관 연락처 ※ 관련기관의 부서와 연락처는 해당 기관의 사정에 따라 변경될 수 있음 ¦ 구분 ¦ 구분 ¦ 부서 명 ¦ 소재지 ¦ 연락처 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 서 울 특 별 시 ¦ 강동구청 ¦ 건축과 공공건축팀 ¦ (05397) 서울특별시 강동구 성내로 3 가길 19 ¦ 02-3425-6104 ¦ ¦ 서 울 특 별 시 ¦ 강남구청 ¦ 건축과 건축시설팀 ¦ (06090) 서울특별시 강남구 학동로 426 (삼성동) ¦ 02-3423-6174 ¦ ¦ 서 울 특 별 시 ¦ 강북구청 ¦ 건축과 공공시설팀 ¦ (01071) 서울특별시 강북구 도봉로 89 길 13 (수유동) ¦ 02-901-6908 ¦ ¦ 서 울 특 별 시 ¦ 강서구청 ¦ 건축과 건축시설팀 ¦ (07658) 서울특별시 강서구 화곡로 302 (화곡동) ¦ 02-2600-6881 ¦ ¦ 서 울 특 별 시 ¦ 관악구청 ¦ 건축과 건축시설팀 ¦ (08832) 서울특별시 관악구 관악로 145 (봉천동) ¦ 02-879-6422 ¦ ¦ 서 울 특 별 시 ¦ 광진구청 ¦ 건축과 건축시설팀 ¦ (05026) 서울특별시 광진구 자양로 117 (자양동) ¦ 02-450-7728 ¦ ¦ 서 울 특 별 시 ¦ 구로구청 ¦ 건축과 공공건축팀 ¦ (08284) 서울특별시 구로구 가마산로 245 (구로동, 구로구청) ¦ 02-860-2252 ¦ ¦ 서 울 특 별 시 ¦ 금천구청 ¦ 건축과 공공건축팀 ¦ (08611) 서울특별시 금천구 시흥대로 73 길 70 ¦ 02-2627-1644 ¦ ¦ 서 울 특 별 시 ¦ 노원구청 ¦ 건축과 공공건축팀 ¦ (01689) 서울특별시 노원구 노해로 437(상계동) ¦ 02-2116-0607 ¦ ¦ 서 울 특 별 시 ¦ 도봉구청 ¦ 건축과 건축시설팀 ¦ (01331) 서울특별시 도봉구 마들로 656(방학동) ¦ 02-2091-3674 ¦ ¦ 서 울 특 별 시 ¦ 동대문구청 ¦ 건축과 건축시설팀 ¦ (02565) 서울특별시 동대문구 천호대로 145 (용두동) ¦ 02-2127-4575 ¦ ¦ 서 울 특 별 시 ¦ 동작구청 ¦ 건축과 건축시설팀 ¦ (06928) 서울특별시 동작구 장승배기로 161 (노량 진 2 동 47-2) ¦ 02-820-9837 ¦ ¦ 서 울 특 별 시 ¦ 마포구청 ¦ 건축과 건축시설팀 ¦ (03937) 서울특별시 마포구 월드컵로 212 (성산동) ¦ 02-3153-9433 ¦ ¦ 서 울 특 별 시 ¦ 서대문구청 ¦ 건축과 공공시설물팀 ¦ (03718) 서울특별시 서대문구 연희로 248 (연희동) ¦ 02-330-8988 ¦ ¦ 서 울 특 별 시 ¦ 서초구청 ¦ 건축과 건축시설팀 ¦ (06750) 서울특별시 서초구 남부순환로 2584 (서 초동) ¦ 02-2155-6856 ¦ ¦ 서 울 특 별 시 ¦ 성동구청 ¦ 건축과 건축시설팀 ¦ (04750) 서울특별시 성동구 고산자로 270 ¦ 02-2286-5644 ¦ ¦ 서 울 특 별 시 ¦ 성북구청 ¦ 건축과 공공건축팀 ¦ (02848) 서울특별시 성북구 보문로 168 (삼선동 5 가) ¦ 02-2241-2928 ¦ ¦ 서 울 특 별 시 ¦ 송파구청 ¦ 건축과 건축시설팀 ¦ (05552) 서울특별시 송파구 올림픽로 326 (신천동) ¦ 02-2147-3031 ¦ ¦ 서 울 특 별 시 ¦ 양천구청 ¦ 건축과 공공시설팀 ¦ (08095) 서울특별시 양천구 목동동로 105 (신정동) ¦ 02-2620-3544 ¦ ¦ 서 울 특 별 시 ¦ 영등포구청 ¦ 건축과 공공건축팀 ¦ (07260) 서울특별시 영등포구 당산로 123 ¦ 02-2670-3696 ¦ ¦ 서 울 특 별 시 ¦ 용산구청 ¦ 건축과 공공건축팀 ¦ (04390) 서울특별시 용산구 녹사평대로 150 (이태 원동) ¦ 02-2199-7524 ¦ 국토교통부 421 | {}
9f61ede8-ad5d-49f9-a4c1-2c3599e02679 | 국내_기계설비_기술기준_매뉴얼_최종본 | ¦ ¦ 구분 ¦ 부서 명 ¦ 소재지 ¦ 연락처 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 서 울 특 별 시 ¦ 은평구청 ¦ 건축과 공공건축팀 ¦ (03384) 서울특별시 은평구 은평로 195 (녹번동) ¦ 02-351-7544 ¦ ¦ 서 울 특 별 시 ¦ 종로구청 ¦ 건축과 공공건축팀 ¦ (03152) 서울특별시 종로구 종로 1 길 36 ¦ 02-2148-2804 ¦ ¦ 서 울 특 별 시 ¦ 중구청 ¦ 건축과 건축시설팀 ¦ (04558) 서울특별시 중구 창경궁로 17 (예관동) ¦ 02-3396-5822 ¦ ¦ 서 울 특 별 시 ¦ 중랑구청 ¦ 건축과 공공건축팀 ¦ (02043) 서울특별시 중랑구 봉화산로 179 (신내동) ¦ 02-2094-2313 ¦ ¦ 부 산광역 시 ¦ 강서구청 ¦ 도시개발국 안전관리과 ¦ (46702) 부산시 강서구 낙동북로 477 ¦ 051-970-2397 ¦ ¦ 부 산광역 시 ¦ 기장군청 ¦ 안전도시국 창조건축과 ¦ (46077) 부산시 기장군 기장읍 기장대로 560 ¦ 051-709-4598 ¦ ¦ 부 산광역 시 ¦ 금정구청 ¦ 안전도시국 ¦ (46274) 부산시 금정구 중앙대로 1777 ¦ 051-519-4678 ¦ ¦ 부 산광역 시 ¦ 남구청 ¦ 안전도시국 건축과 ¦ (48452) 부산시 남구 못골로 19 ¦ 051-607-4595 ¦ ¦ 부 산광역 시 ¦ 동구청 ¦ 도시관리국 안전도시과 ¦ (48781) 부산시 동구 구청로 1 ¦ 051-449-4634 ¦ ¦ 부 산광역 시 ¦ 동래구청 ¦ 안전도시국 건축과 ¦ (47885) 부산시 동래구 명륜로 94 번길 55 ¦ 051-550-4521 ¦ ¦ 부 산광역 시 ¦ 부산진구청 ¦ 건축과 건축물관리계 ¦ (47193) 부산시 부산진구 시민공원로 30 ¦ 051-605-8605 ¦ ¦ 부 산광역 시 ¦ 북구청 ¦ 안전도시국 건축과 ¦ (46504) 부산시 북구 낙동대로 1570 번길 33 ¦ 051-309-4596 ¦ ¦ 부 산광역 시 ¦ 사상구청 ¦ 도시건설국 건설과 ¦ (46985) 부산시 사상구 학감대로 242 ¦ 051-310-4732 ¦ ¦ 부 산광역 시 ¦ 사하구청 ¦ 안전도시국 건설과 ¦ (49328) 부산시 사하구 낙동대로 398 번길 12 ¦ 051-220-4662 ¦ ¦ 부 산광역 시 ¦ 서구청 ¦ 건축과 건축계 ¦ (49247) 부산시 서구 구덕로 120 ¦ 051-240-4595 ¦ ¦ 부 산광역 시 ¦ 수영구청 ¦ 안전도시국 건축과 ¦ (48305) 부산시 수영구 남천동로 100 ¦ 051-610-4596 ¦ ¦ 부 산광역 시 ¦ 연제구청 ¦ 안전도시국 건축과 ¦ (47605) 부산시 연제구 연제로 2 ¦ 051-665-5072 ¦ ¦ 부 산광역 시 ¦ 영도구청 ¦ 도시안전국 건설과 ¦ (49011) 부산시 영도구 태종로 423 ¦ 051-419-4676 ¦ ¦ 부 산광역 시 ¦ 중구청 ¦ 건축과 ¦ (48926) 부산시 중구 중구로 120 ¦ 051-600-4665 ¦ ¦ 부 산광역 시 ¦ 해운대구청 ¦ 도시안전국 건축과 ¦ (48095) 부산시 해운대구 중동 2 로 11 ¦ 051-749-4742 ¦ ¦ 대 구광역 시 ¦ 중구청 ¦ 건축주택과 건축시설팀 ¦ (41908) 대구 중구 국채보상로 139 길 1 ¦ 053-661-2955 ¦ ¦ 대 구광역 시 ¦ 동구청 ¦ 건축주택과 공공시설팀 ¦ (41185) 대구 동구 아양로 207 ¦ 053-662-2263 ¦ ¦ 대 구광역 시 ¦ 서구청 ¦ 건축주택과 시설팀 ¦ (41777) 대구 서구 국채보상로 257 ¦ 053-663-2963 ¦ ¦ 대 구광역 시 ¦ 남구청 ¦ 건축과 청사시설팀 ¦ (42429) 대구 남구 이천로 51 ¦ 053-664-2832 ¦ 422 기계설비 기술기준 매뉴얼 | {}
5d26ab93-203b-4a87-8b2c-2225e6c781f7 | 국내_기계설비_기술기준_매뉴얼_최종본 | ¦ 구분 ¦ 구분 ¦ 부서 명 ¦ 소재지 ¦ 연락처 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 대 구 광역 시 ¦ 북구청 ¦ 건축주택과 공공시설팀 ¦ (41590) 대구 북구 옥산로 65 ¦ 053-665-2972 ¦ ¦ 대 구 광역 시 ¦ 수성구청 ¦ 건축과 건축 2 팀 ¦ (42086) 대구 수성구 달구벌대로 2450 ¦ 053-666-2952 ¦ ¦ 대 구 광역 시 ¦ 달서구청 ¦ 건축과 건축 1 팀 ¦ (42731) 대구 달서구 학산로 45 ¦ 053-667-2946 ¦ ¦ 대 구 광역 시 ¦ 달성군청 ¦ 건축과 공공시설팀 ¦ (42974) 대구 달성군 논공읍 달성군청로 33 ¦ 053-668-2025 ¦ ¦ 인천광역 시 ¦ 중구청 ¦ 건축과 공동주택팀 ¦ (22315) 인천광역시 중구 신포로 27 번길 80 (관동 1 가) ¦ 032-760-7478 ¦ ¦ 인천광역 시 ¦ 동구청 ¦ 건축과 공공시설팀 ¦ (22556) 인천광역시 동구 금곡로 67 (송림동) ¦ 032-770-6646 ¦ ¦ 인천광역 시 ¦ 미추홀구청 ¦ 건축과 건축행정팀 ¦ (22169) 인천광역시 미추홀구 독정이로 95 ¦ 032-880-4442 ¦ ¦ 인천광역 시 ¦ 남동구청 ¦ 건축과 건축안전팀 ¦ (21589) 인천광역시 남동구 소래로 633 (만수동) ¦ 032-453-8424 ¦ ¦ 인천광역 시 ¦ 부평구청 ¦ 건축과 건축팀 ¦ (21354) 인천광역시 부평구 부평대로 168 ¦ 032-509-6876 ¦ ¦ 인천광역 시 ¦ 서구청 ¦ 건축과 건축관리팀 ¦ (22726) 인천광역시 서구 서곶로 307 (심곡동, 서 구청) ¦ 032-560-4641 ¦ ¦ 인천광역 시 ¦ 연수구청 ¦ 경제지원과 산업지원팀 ¦ (21967) 인천광역시 연수구 원인재로 115 (동춘동) ¦ 032-749-7802 ¦ ¦ 인천광역 시 ¦ 계양구청 ¦ 공공시설과 공공설비팀 ¦ (21067) 인천광역시 계양구 계산새로 88 (계산동) ¦ 032-450-8324 ¦ ¦ 인천광역 시 ¦ 옹진군청 ¦ 기계설비 담당 ¦ (22193) 인천광역시 미추홀구 매소홀로 120 (용현 동) ¦ 032-899-2114 ¦ ¦ 인천광역 시 ¦ 강화군청 ¦ 기계설비 담당 ¦ (23031) 인천광역시 강화군 강화읍 강화대로 394 ¦ 032-930-3114 ¦ ¦ 광주 광역 시 ¦ 동구청 ¦ 건축과 건축허가팀 ¦ (61466) 광주광역시 동구 서남로 1(서석동) ¦ 062-608-2862 ¦ ¦ 광주 광역 시 ¦ 서구청 ¦ 건축과 건축안전팀 ¦ (61928) 광주광역시 서구 경열로 33(농성동) ¦ 062-350-4872 ¦ ¦ 광주 광역 시 ¦ 남구청 ¦ 건축과 도시계획과 ¦ (61687) 광주광역시 남구 봉선로 1(주월동) ¦ 062-607-3933 ¦ ¦ 광주 광역 시 ¦ 북구청 ¦ 시설지원과 기계전기팀 ¦ (61187) 광주광역시 북구 우치로 77 (용봉동) ¦ 062-410-6786 ¦ ¦ 광주 광역 시 ¦ 광산구청 ¦ 건축과 건축안전팀 ¦ (62430) 광주광역시 광산구 광산로 29 번길 15(송정 동) ¦ 062-960-3698 ¦ ¦ 전라 남 도 ¦ 광양시청 ¦ 건축과 건축지도팀 ¦ (57785) 전남 광양시 시청로 33(중동) ¦ 061-797-2888 ¦ ¦ 전라 남 도 ¦ 나주시청 ¦ 건축허가과 건축허가팀 ¦ (58263) 전남 나주시 시청길 22(송월동) ¦ 061-339-7253 ¦ ¦ 전라 남 도 ¦ 목포시청 ¦ 건축행정과 건축허가팀 ¦ (58613) 전남 목포시 양을 로 203(용당동) ¦ 061-270-8468 ¦ ¦ 전라 남 도 ¦ 순천시청 ¦ 건축과 건축물관리팀 ¦ (57956) 전남 순천시 장명로 30(장천동) ¦ 061-749-5888 ¦ ¦ 전라 남 도 ¦ 여수시청 ¦ 허가민원과 건축허가팀 ¦ (59675) 전남 여수시 시청로 1(학동) ¦ 061-659-4104 ¦ 국토교통부 423 | {}
c18c695b-11b5-4efe-a813-05459ca1e148 | 국내_기계설비_기술기준_매뉴얼_최종본 | ¦ ¦ 구분 ¦ 부서 명 ¦ 소재지 ¦ 연락처 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 전라 남 도 ¦ 강진군청 ¦ 일자리창출과 일자리경제팀 ¦ (59228) 전남 강진군 강진읍 탐진로 111(남성리) ¦ 061-430-3064 ¦ ¦ 전라 남 도 ¦ 고흥군청 ¦ 기계설비 담당 ¦ (59542) 전남 고흥군 고흥읍 고흥군청로 1 ¦ 061-830-5114 ¦ ¦ 전라 남 도 ¦ 곡성군청 ¦ 민원실 OK 민원 2 팀 ¦ (57536) 전남 곡성군 곡성읍 군청로 50(읍내리) ¦ 061-360-2623 ¦ ¦ 전라 남 도 ¦ 구례군청 ¦ 종합민원과 복합민원팀 ¦ (57656) 전남 구례군 구례읍 봉성로 1(봉남리) ¦ 061-780-2346 ¦ ¦ 전라 남 도 ¦ 담양군청 ¦ 도시디자인과 건축계 ¦ (57339) 전남 담양군 담양읍 추성로 1371(객사리) ¦ 061-380-3244 ¦ ¦ 전라 남 도 ¦ 무안군청 ¦ 건축과 건축허가팀 ¦ (58532) 전남 무안군 무안읍 무안로 530(성동리) ¦ 061-450-5728 ¦ ¦ 전라 남 도 ¦ 보성군청 ¦ 도시개발과 건축계 ¦ (59455) 전남 보성군 보성읍 송재로 165(보성리) ¦ 061-850-5593 ¦ ¦ 전라 남 도 ¦ 신안군청 ¦ 민원봉사과 건축계 ¦ (58827) 전남 신안군 압해읍 천사로 1004(신장리) ¦ 061-240-8294 ¦ ¦ 전라 남 도 ¦ 영광군청 ¦ 종합민원실 건축팀 ¦ (57036) 전남 영광군 영광읍 중앙로 203(무령리) ¦ 061-350-5475 ¦ ¦ 전라 남 도 ¦ 영암군청 ¦ 도시개발과 건축시설팀 ¦ (58415) 전남 영암군 영암읍 군청로 1(동무리) ¦ 061-470-2474 ¦ ¦ 전라 남 도 ¦ 완도군청 ¦ 민원봉사과 주택건축팀 ¦ (59124) 전남 완도군 완도읍 청해진남로 51(군내리) ¦ 061-550-5382 ¦ ¦ 전라 남 도 ¦ 장성군청 ¦ 민원봉사과 건축팀 ¦ (57219) 전남 장성군 장성읍 영천로 200(영천리) ¦ 061-390-7473 ¦ ¦ 전라 남 도 ¦ 장흥군청 ¦ 민원봉사과 건축팀 ¦ (59328) 전남 장흥군 장흥읍 장흥로 21(건산리) ¦ 061-860-5672 ¦ ¦ 전라 남 도 ¦ 진도군청 ¦ 민원봉사과 건축팀 ¦ (58915) 전남 진도군 진도읍 철마길 25(성내리) ¦ 061-540-3666 ¦ ¦ 전라 남 도 ¦ 함평군청 ¦ 민원봉사실 건축지도팀 ¦ (57149) 전남 함평군 함평읍 중앙길 200(함평리) ¦ 061-320-1621 ¦ ¦ 전라 남 도 ¦ 해남군청 ¦ 건설과 주택행정팀 ¦ (59028) 전남 해남군 해남읍 군청길 4(성내리) ¦ 061-540-5163 ¦ ¦ 전라 남 도 ¦ 화순군청 ¦ 행복민원과 건축민원팀 ¦ (58112) 전남 화순군 화순읍 동헌길 23(훈리) ¦ 061-379-3473 ¦ ¦ 대 전광역 시 ¦ 동구청 ¦ 기계설비 담당 ¦ (34691) 대전시 동구 동구청로 147(가오동) ¦ 042-251-4114 ¦ ¦ 대 전광역 시 ¦ 중구청 ¦ 건설과 건설팀 ¦ (34939) 대전시 중구 중앙로 100(대흥동) ¦ 042-606-6807 ¦ ¦ 대 전광역 시 ¦ 서구청 ¦ 건축과 건축행정팀 ¦ (35238) 대전시 서구 둔산서로 100(둔산동) ¦ 042-288-3716 ¦ ¦ 대 전광역 시 ¦ 유성구청 ¦ 건설과 건설관리팀 ¦ (34139) 대전시 유성구 대학로 211 ¦ 042-611-2479 ¦ ¦ 대 전광역 시 ¦ 대덕구청 ¦ 건설과 건설행정팀 ¦ (34443) 대전시 대덕구 대전로 1033 번길 20(오정 동) ¦ 042-608-5232 ¦ ¦ 충 청 남 도 ¦ 천안시청 ¦ 건축디자인과 건축정책팀 ¦ (31162) 충남 천안시 서구 번영로 156 ¦ 042-521-5698 ¦ ¦ 충 청 남 도 ¦ 공주시청 ¦ 건설과 건설개발팀 ¦ (32552) 충남 공주시 봉황로 1 ¦ 041-840-8318 ¦ 424 기계설비 기술기준 매뉴얼 | {}
740f9859-1eba-4061-8c21-f3ec42e22951 | 국내_기계설비_기술기준_매뉴얼_최종본 | ¦ 구분 ¦ 구분 ¦ 부서 명 ¦ 소재지 ¦ 연락처 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 충청 남 도 ¦ 당진시청 ¦ 회계과 청사관리팀 ¦ (31773) 충남 당진시 시청 1 로 1(수청동) ¦ 041-350-4862 ¦ ¦ 충청 남 도 ¦ 보령시청 ¦ 건설과 건설행정팀 ¦ (33483) 충남 보령시 성주산로 77 ¦ 041-930-3813 ¦ ¦ 충청 남 도 ¦ 아산시청 ¦ 건설과 건설행정팀 ¦ (31512) 충남 아산시 시민로 456 ¦ 041-540-2615 ¦ ¦ 충청 남 도 ¦ 서산시청 ¦ 기계설비 담당 ¦ (31974) 충남 서산시 관아문길 1(읍내동) ¦ 041-660-2442 ¦ ¦ 충청 남 도 ¦ 논산시청 ¦ 건설과 건설정책팀 ¦ (32987) 충남 논산시 시민로 210 번길 9(내동) ¦ 041-746-6173 ¦ ¦ 충청 남 도 ¦ 계룡시청 ¦ 건설과 건설행정팀 ¦ (32823) 충남 계룡시 장안로 46(금암동) ¦ 042-840-2551 ¦ ¦ 충청 남 도 ¦ 금산군청 ¦ 기계설비 담당 ¦ (32733) 충남 금산군 금산읍 군청길 13 ¦ 041-750-2114 ¦ ¦ 충청 남 도 ¦ 부여군청 ¦ 도시건측과 건축팀 ¦ (33168) 충남 부여군 부여읍 사비로 33 ¦ 041-830-2397 ¦ ¦ 충청 남 도 ¦ 서천군청 ¦ 도시건축과 건축팀 ¦ (33638) 충남 서천군 서천읍 군청로 57 ¦ 041-950-4033 ¦ ¦ 충청 남 도 ¦ 청양군청 ¦ 건설도시과 건설행정팀 ¦ (33323) 충남 청양군 청양읍 문화예술로 222 ¦ 041-940-2362 ¦ ¦ 충청 남 도 ¦ 홍성군청 ¦ 허가건축과 건축팀 ¦ (32228) 충남 홍성군 홍성읍 아문길 27 ¦ 041-630-1471 ¦ ¦ 충청 남 도 ¦ 예산군청 ¦ 건설교통과 건설행정팀 ¦ (32435) 충남 예산군 예산읍 군청로 22 ¦ 041-339-7653 ¦ ¦ 충청 남 도 ¦ 태안군청 ¦ 건설과 재무팀 ¦ (32144) 충남 태안군 태안읍 군청로 1(남문리) ¦ 041-670-2750 ¦ ¦ 경 상남 도 ¦ 창원시청 ¦ 건설도로과 건설지원계 ¦ (51435) 경남 창원시 의창구 중앙대로 151 ¦ 055-225-4415 ¦ ¦ 경 상남 도 ¦ 진주시청 ¦ 건설하천과 건설행정팀 ¦ (52789) 경남 진주시 동진로 155 ¦ 055-749-8785 ¦ ¦ 경 상남 도 ¦ 거제시청 ¦ 도로과 도로행정팀 ¦ (53257) 경남 거제시 계룡로 125 ¦ 055-639-4465 ¦ ¦ 경 상남 도 ¦ 김해시청 ¦ 건설과 건설행정팀 ¦ (50924) 경남 김해시 김해대로 2401 ¦ 055-330-3787 ¦ ¦ 경 상남 도 ¦ 밀양시청 ¦ 건설과 건설행정계 ¦ (50420) 경남 밀양시 밀양대로 2047 ¦ 055-359-5255 ¦ ¦ 경 상남 도 ¦ 사천시청 ¦ 건축과 건축관리팀 ¦ (52539) 경남 사천시 용현면 시청로 77 ¦ 055-831-3210 ¦ ¦ 경 상남 도 ¦ 양산시청 ¦ 건설하천과 건설행정팀 ¦ (50624) 경남 양산시 중앙로 39 ¦ 055-392-279 ¦ ¦ 경 상남 도 ¦ 통영시청 ¦ 건설과 건설행정팀 ¦ (53040) 경남 통영시 통영해안로 515 ¦ 055-650-5523 ¦ ¦ 경 상남 도 ¦ 고성군청 ¦ 건설과 건설행정계 ¦ (24735) 강원 고성군 간성읍 고성중앙길 9 ¦ 055-670-2753 ¦ ¦ 경 상남 도 ¦ 하동군청 ¦ 도시건축과 건축민원팀 ¦ (52333) 경남 하동군 하동읍 군청로 23 ¦ 055-880-2106 ¦ ¦ 경 상남 도 ¦ 창녕군청 ¦ 건설교통과 건설행정팀 ¦ (50317) 경남 창녕군 창녕읍 군청길 1 ¦ 055-530-1743 ¦ 국토교통부 425 | {}
00b3f138-1b1b-49c0-9689-15997020f7ca | 국내_기계설비_기술기준_매뉴얼_최종본 | ¦ 구분 ¦ 구분 ¦ 부서 명 ¦ 소재지 ¦ 연락처 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 경 상남 도 ¦ 산청군청 ¦ 도시교통과 주택담당팀 ¦ (52221) 경남 산청군 산청읍 산엔청로 1 ¦ 055-970-7322 ¦ ¦ 경 상남 도 ¦ 남해군청 ¦ 건설교통과 건설관리팀 ¦ (52425) 경남 남해군 남해읍 망운로 9 번길 12 ¦ 055-860-3444 ¦ ¦ 경 상남 도 ¦ 함안군청 ¦ 건설교통과 건설행정팀 ¦ (52043) 경남 함안군 가야읍 말산로 1 ¦ 055-580-2603 ¦ ¦ 경 상남 도 ¦ 합천군청 ¦ 건설과 건설행정팀 ¦ (50231) 경남 합천군 합천읍 동서로 119 ¦ 055-930-3442 ¦ ¦ 경 상남 도 ¦ 거창군청 ¦ 건설과 건설팀 ¦ (50132) 경남 거창군 거창읍 중앙로 103 ¦ 055-940-3532 ¦ ¦ 경 상남 도 ¦ 의령군청 ¦ 건설과 건설행정팀 ¦ (52140) 경남 의령군 의령읍 충익로 63 ¦ 055-570-3604 ¦ ¦ 경 상남 도 ¦ 함양군청 ¦ 기계설비 담당 ¦ (50036) 경남 함양군 함양읍 고운로 35 ¦ 055-960-5114 ¦ ¦ 울 산광역 시 ¦ 중구청 ¦ 건설과 건설행정계 ¦ (44475) 울산 중구 단장골길 1 ¦ 052-290-3814 ¦ ¦ 울 산광역 시 ¦ 북구청 ¦ 건설과 기전계 ¦ (44248) 울산 북구 산업로 1010 ¦ 052-241-7852 ¦ ¦ 울 산광역 시 ¦ 남구청 ¦ 건설과 건설행정계 ¦ (44701) 울산 남구 돋질로 233 ¦ 052-226-5815 ¦ ¦ 울 산광역 시 ¦ 동구청 ¦ 건설과 건설행정계 ¦ (44021) 울산 동구 봉수로 155 ¦ 052-209-3636 ¦ ¦ 울 산광역 시 ¦ 울주군청 ¦ 건설과 건설행정계 ¦ (44959) 울산 울주군 청량읍 군청로 1 ¦ 052-204-2324 ¦ ¦ 경 기 도 ¦ 수원시청 ¦ 건축과 건축물관리팀 ¦ (16490) 경기도 수원시 팔달구 효원로 241 ¦ 031-228-3137 ¦ ¦ 경 기 도 ¦ 고양시청 ¦ 건축디자인과 건축안전관리센터 ¦ (10460) 경기도 고양시 덕양구 고양시청로 10 ¦ 031-8075-345 8 ¦ ¦ 경 기 도 ¦ 용인시청 ¦ 주택국 건축과 ¦ (17019) 경기도 용인시 처인구 중부대로 1199 ¦ 031-324-2399 ¦ ¦ 경 기 도 ¦ 성남시청 ¦ 건축안전관리과 기계설비팀 ¦ (13437) 경기도 성남시 중원구 성남대로 997 ¦ 031-729-4923 ¦ ¦ 경 기 도 ¦ 부천시청 ¦ 건축허가과 지역건축팀 ¦ (14547) 경기도 부천시 길주로 210 ¦ 032-625-3543 ¦ ¦ 경 기 도 ¦ 화성시청 ¦ 건축관리과 ¦ (18274) 경기도 화성시 시청로 159 ¦ 031-5189-732 0 ¦ ¦ 경 기 도 ¦ 안산시청 ¦ 건축디자인과 ¦ (15335) 경기도 안산시 단원구 화랑로 387 ¦ 031-481-2632 ¦ ¦ 경 기 도 ¦ 남양주시청 ¦ 건축과 건축물관리팀 ¦ (12232) 경기도 남양주시 경춘로 1037 ¦ 031-590-2771 ¦ ¦ 경 기 도 ¦ 안양시청 ¦ 건축과 건축행정팀 ¦ (14053) 경기도 안양시 동안구 시민대로 235 ¦ 031-8045-567 8 ¦ ¦ 경 기 도 ¦ 평택시청 ¦ 건축관리팀 ¦ (17901) 경기도 평택시 경기대로 245 ¦ 031-8024-418 2 ¦ ¦ 경 기 도 ¦ 시흥시청 ¦ 건축과 지역건축안전센터 ¦ (14998) 경기도 시흥시 시청로 20 ¦ 031-310-3847 ¦ ¦ 경 기 도 ¦ 파주시청 ¦ 건설과 건설행정팀 ¦ (10932) 경기도 파주시 시청로 50 ¦ 031-940-4646 ¦ 426 기계설비 기술기준 매뉴얼 | {}
b2d52f02-52e7-4b93-b6a8-6c51c843b94d | 국내_기계설비_기술기준_매뉴얼_최종본 | ¦ ¦ 구분 ¦ 부서 명 ¦ 소재지 ¦ 연락처 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 경 기 도 ¦ 의정부시청 ¦ 주택과 공동주택승인팀 ¦ (11622) 경기도 의정부시 시민로 1 ¦ 031-828-4494 ¦ ¦ 경 기 도 ¦ 김포시청 ¦ 건축과 ¦ (10109) 경기도 김포시 사우중로 1 ¦ 031-980-2391 ¦ ¦ 경 기 도 ¦ 광주시청 ¦ 건설과 공정건설조사팀 ¦ (12738) 경기도 광주시 행정타운로 50 ¦ 031-760-2946 ¦ ¦ 경 기 도 ¦ 광명시청 ¦ 건축허가팀 ¦ (14234) 경기도 광명시 시청로 20 ¦ 02-1680-2883 ¦ ¦ 경 기 도 ¦ 군포시청 ¦ 건축과 ¦ (15829) 경기도 군포시 청백리길 6 ¦ 031-390-0381 ¦ ¦ 경 기 도 ¦ 하남시청 ¦ 건설과 건설행정 ¦ (12951) 경기도 하남시 대청로 10 ¦ 031-790-5225 ¦ ¦ 경 기 도 ¦ 오산시청 ¦ 건축과 건축관리팀 ¦ (18132) 경기도 오산시 성호대로 141 ¦ 031-8036-793 7 ¦ ¦ 경 기 도 ¦ 양주시청 ¦ 건축지도팀 ¦ (11498) 경기도 양주시 부흥로 1533 ¦ 031-8082-668 1 ¦ ¦ 경 기 도 ¦ 이천시청 ¦ 지역건축안전센터 ¦ (17379) 경기도 이천시 부악로 40 ¦ 031-644-2679 ¦ ¦ 경 기 도 ¦ 구리시청 ¦ 건축과 건축팀 ¦ (11954) 경기도 구리시 아차산로 439 ¦ 031-550-2392 ¦ ¦ 경 기 도 ¦ 안성시청 ¦ 건축과 건축안전팀 ¦ (17586) 경기도 안성시 시청길 25 ¦ 031-678-2877 ¦ ¦ 경 기 도 ¦ 포천시청 ¦ 건축신고팀 ¦ (11147) 경기도 포천시 중앙로 87 ¦ 031-538-2395 ¦ ¦ 경 기 도 ¦ 의왕시청 ¦ 건축관리팀 ¦ (16075) 경기도 의왕시 시청로 11 ¦ 031-345-3469 ¦ ¦ 경 기 도 ¦ 양평군청 ¦ 건축과 ¦ (12554) 경기도 양평군 양평읍 군천앞길 2 ¦ 031-770-2512 ¦ ¦ 경 기 도 ¦ 여주시청 ¦ 허가건축과 건축민원 1 팀 ¦ (12619) 경기도 여주군 세종로 1 ¦ 031-887-2633 ¦ ¦ 경 기 도 ¦ 동두천시청 ¦ 건축과 ¦ (11317) 경기도 동두천시 방죽로 23 ¦ 031-860-2446 ¦ ¦ 경 기 도 ¦ 가평군청 ¦ 건설행정팀 ¦ (12417) 경기도 가평군 가평읍 석봉로 181 ¦ 031-580-2423 ¦ ¦ 경 기 도 ¦ 과천시청 ¦ 건축과 건축안전팀 ¦ (13806) 경기도 과천시 관문로 69 ¦ 02-3677-2399 ¦ ¦ 경 기 도 ¦ 연천군청 ¦ 건축과(공동주택) 건축과(일반건축) ¦ (11017) 경기도 연천군 연천읍 연천로 220 ¦ 031-839-2401 031-839-2391 ¦ ¦ 강원 도 ¦ 춘천시청 ¦ 건축과 주택허가팀 ¦ (24347) 강원도 춘천시 시청길 11 ¦ 033-250-3182 ¦ ¦ 강원 도 ¦ 원주시청 ¦ 건축과 건축물관리팀 ¦ (26384) 강원도 원주시 시청로 1(무실동) ¦ 033-737-3481 ¦ ¦ 강원 도 ¦ 강릉시청 ¦ 주택과 공공시설팀 ¦ (25522) 강원도 강릉시 강릉대로 33 ¦ 033-640-5402 ¦ ¦ 강원 도 ¦ 동해시청 ¦ 건설과 건설행정팀 ¦ (25755) 강원도 동해시 천곡로 77 ¦ 033-539-8802 ¦ ¦ 강원 도 ¦ 태백시청 ¦ 건축과 건축지적팀 ¦ (26023) 강원도 태백시 태붐로 21 ¦ 033-550-2449 ¦ 국토교통부 427 | {}
f1440611-cf83-45b8-87e2-74970dd6713a | 국내_기계설비_기술기준_매뉴얼_최종본 | ¦ ¦ 구분 ¦ 부서 명 ¦ 소재지 ¦ 연락처 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 강 원 도 ¦ 속초시청 ¦ 건축과 건축허가팀 ¦ (24826) 강원도 속초시 중앙로 183 ¦ 033-639-2769 ¦ ¦ 강 원 도 ¦ 삼척시청 ¦ 건축과 건축팀 ¦ (25914) 강원도 삼척시 중앙로 296 ¦ 033-570-3404 ¦ ¦ 강 원 도 ¦ 홍천군청 ¦ 건설방재과 건설행정팀 ¦ (25121) 강원도 홍천군 홍천읍 석화로 93 ¦ 033-430-2905 ¦ ¦ 강 원 도 ¦ 횡성군청 ¦ 안전건설과 건설행정팀 ¦ (25220) 강원도 횡성군 횡성읍 태기로 15 ¦ 033-340-2535 ¦ ¦ 강 원 도 ¦ 영월군청 ¦ 안전건설과 건설기술관리팀 ¦ (26235) 강원도 영월군 영월읍 하송로 64 ¦ 033-370-2794 ¦ ¦ 강 원 도 ¦ 평창군청 ¦ 허가과 허가행정팀 ¦ (25374) 강원도 평창군 평창읍 군청길 77 ¦ 033-330-2435 ¦ ¦ 강 원 도 ¦ 정선군청 ¦ 건설과 건설행정팀 ¦ (26131) 강원도 정선군 정선읍 봉양 3 길 21 ¦ 033-560-2162 ¦ ¦ 강 원 도 ¦ 철원군청 ¦ 건설도시과 건설행정팀 ¦ (24040) 강원도 철원군 갈말읍 삼부연로 51 ¦ 033-450-4898 ¦ ¦ 강 원 도 ¦ 양구군청 ¦ 안전건설과 건설행정팀 ¦ (24522) 강원도 양구군 양구읍 관공서로 38 ¦ 033-480-2732 ¦ ¦ 강 원 도 ¦ 인제군청 ¦ 건설과 건설행정팀 ¦ (24631) 강원도 인제군 인제읍 인제로 187 번길 8 ¦ 033-460-2091 ¦ ¦ 강 원 도 ¦ 고성군청 ¦ 건설도시과 건설행정팀 ¦ (24735) 강원도 고성군 간성읍 고성중앙길 9 ¦ 033-680-3392 ¦ ¦ 강 원 도 ¦ 양양군청 ¦ 건설과 건설행정팀 ¦ (25023) 강원도 양양군 양양읍 군청길 1 ¦ 033-670-2772 ¦ ¦ 강 원 도 ¦ 화천군청 ¦ 안전건설과 건설지원팀 ¦ (24125) 강원도 화천군 화천읍 화천새싹길 45 ¦ 033-440-2483 ¦ ¦ 충 청 북 도 ¦ 청주시청 ¦ 차량등록사업소 검사팀 ¦ (28542) 충북 청주시 상당구 상당로 155 ¦ 043-201-4935 ¦ ¦ 충 청 북 도 ¦ 충주시청 ¦ 건축과 공공건축지원팀 ¦ (27339) 충북 충주시 으뜸로 21(금릉동) ¦ 043-850-6426 ¦ ¦ 충 청 북 도 ¦ 제천시청 ¦ 일자리경제과 에너지관리팀 ¦ (27188) 충북 제천시 내토로 295(천남동) ¦ 043-641-6642 ¦ ¦ 충 청 북 도 ¦ 보은군청 ¦ 안전건설과 건설행정팀 ¦ (28937) 충북 보은군 보은읍 군청길 38 ¦ 043-540-3414 ¦ ¦ 충 청 북 도 ¦ 옥천군청 ¦ 도시교통과 도시재생팀 ¦ (29032) 충북 옥천군 옥천읍 중앙로 99 ¦ 043-730-3562 ¦ ¦ 충 청 북 도 ¦ 영동군청 ¦ 건설교통과 건설관리팀 ¦ (29140) 충북 영동군 영동읍 동정로 1 ¦ 043-740-3504 ¦ ¦ 충 청 북 도 ¦ 증평군청 ¦ 재무과 재산관리팀 ¦ (27927) 충북 증평군 증평읍 광장로 88 ¦ 043-835-3792 ¦ ¦ 충 청 북 도 ¦ 진천군청 ¦ 건설교통과 건설행정팀 ¦ (27832) 충북 진천군 진천읍 상산로 13 ¦ 043-539-3652 ¦ ¦ 충 청 북 도 ¦ 괴산군청 ¦ 환경과 환경자원팀 ¦ (28026) 충북 괴산군 괴산읍 임꺽정로 90 ¦ 043-830-2773 ¦ ¦ 충 청 북 도 ¦ 음성군청 ¦ 건축과 건축물관리팀 ¦ (27690) 충북 음성군 음성읍 중앙로 173 ¦ 043-871-5863 ¦ ¦ 충 청 북 도 ¦ 단양군청 ¦ 안전건설과 도로팀 ¦ (27010) 충북 단양군 단양읍 중앙 1 로 10 ¦ 043-420-2863 ¦ 428 기계설비 기술기준 매뉴얼 | {}
d5d33ad1-a131-46b6-ae0d-658a58ed1550 | 국내_기계설비_기술기준_매뉴얼_최종본 | ¦ ¦ 구분 ¦ 부서명 ¦ 소재지 ¦ 연락처 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 전라 북 도 ¦ 전주시청 ¦ 건축과 건축정책팀 ¦ (54994) 전북 전주시 완산구 노송광장로 10 ¦ 063-281-2458 ¦ ¦ 전라 북 도 ¦ 군산시청 ¦ 건축경관과 건축허가계 ¦ (54078) 전북 군산시 시청로 17 ¦ 063-454-4312 ¦ ¦ 전라 북 도 ¦ 익산시청 ¦ 주택과 건축민원계 ¦ (54622) 전북 익산시 인북로 32 길 1 ¦ 063-859-5543 ¦ ¦ 전라 북 도 ¦ 정읍시청 ¦ 건축과 건축기술지원팀 ¦ (56180) 전북 정읍시 충정로 234 ¦ 063-539-5866 ¦ ¦ 전라 북 도 ¦ 남원시청 ¦ 건축과 건축허가팀 ¦ (55738) 전북 남원시 시청로 60 ¦ 063-620-6582 ¦ ¦ 전라 북 도 ¦ 김제시청 ¦ 건축과 건축관리팀 ¦ (54386) 전북 김제시 중앙로 40 ¦ 063-540-3742 ¦ ¦ 전라 북 도 ¦ 완주군청 ¦ 건축과 건축행정팀 ¦ (55352) 전북 완주군 용진읍 지암로 61 ¦ 063-290-2867 ¦ ¦ 전라 북 도 ¦ 진안군청 ¦ 기계설비 담당 ¦ (55434) 전북 진안군 진안읍 중앙로 67 ¦ 063-430-2114 ¦ ¦ 전라 북 도 ¦ 무주군청 ¦ 기계설비 담당 ¦ (55517) 전북 무주군 무주읍 주계로 97 ¦ 063-320-2114 ¦ ¦ 전라 북 도 ¦ 장수군청 ¦ 민원과 건축팀 ¦ (55634) 전북 장수군 장수읍 호비로 10 ¦ 063-350-2287 ¦ ¦ 전라 북 도 ¦ 임실군청 ¦ 기계설비 담당 ¦ (55927) 전북 임실군 임실읍 수정로 30 ¦ 063-640-2114 ¦ ¦ 전라 북 도 ¦ 고창군청 ¦ 종합민원과 건축팀 ¦ (56428) 전북 고창군 고창읍 중앙로 245 ¦ 063-560-2401 ¦ ¦ 전라 북 도 ¦ 부안군청 ¦ 민원과 건축허가팀 ¦ (56305) 전북 부안군 부안읍 당산로 91 ¦ 063-580-4330 ¦ ¦ 전라 북 도 ¦ 순창군청 ¦ 민원과 건축계 ¦ (56039) 전북 순창군 순창읍 경천로 33 ¦ 063-650-1437 ¦ ¦ 경 상북 도 ¦ 포항시청 ¦ 건축디자인과 건축안전팀 ¦ (37683) 경북 포항시 남구 시청로 1 ¦ 054-270-3578 ¦ ¦ 경 상북 도 ¦ 구미시청 ¦ 건축과 건축관리팀 ¦ (39281) 경북 구미시 송정대로 55 ¦ 054-480-5514 ¦ ¦ 경 상북 도 ¦ 경주시청 ¦ 주택과 건축관리팀 ¦ (38102) 경북 경주시 양정로 260 ¦ 054-760-2659 ¦ ¦ 경 상북 도 ¦ 경산시청 ¦ 건축과 건축행정팀 ¦ (38617) 경북 경산시 남매로 159 ¦ 053-810-5542 ¦ ¦ 경 상북 도 ¦ 칠곡군청 ¦ 건축디자인과 건축디자인팀 ¦ (39888) 경북 칠곡군 왜관읍 군청 1 길 80 ¦ 054-979-6844 ¦ ¦ 경 상북 도 ¦ 안동시청 ¦ 건축과 건축지도팀 ¦ (36691) 경북 안동시 퇴계로 115 ¦ 054-840-5455 ¦ ¦ 경 상북 도 ¦ 김천시청 ¦ 건축디자인과 건축시설팀 ¦ (39532) 경북 김천시 시청 1 길 1 ¦ 054-420-6896 ¦ ¦ 경 상북 도 ¦ 울진군청 ¦ 기계설비 담당 ¦ (36323) 경북 울진군 울진읍 울진중앙로 121 ¦ 054-782-1501 ¦ ¦ 경 상북 도 ¦ 상주시청 ¦ 건축과 신고 1 팀 ¦ (37211) 경북 상주시 상산로 223 ¦ 054-537-7618 ¦ ¦ 경 상북 도 ¦ 문경시청 ¦ 건축디자인과 건축계 ¦ (36982) 경북 문경시 당교로 225 ¦ 054-550-6352 ¦ 국토교통부 429 | {}
eb7be004-0361-4e7a-8c32-d4fa05b59eb0 | 국내_기계설비_기술기준_매뉴얼_최종본 | ¦ 구분 ¦ 구분 ¦ 부서 명 ¦ 소재지 ¦ 연락처 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 경 상북 도 ¦ 영천시청 ¦ 도시계획과 도시계획계 ¦ (38856) 경북 영천시 시청로 16 ¦ 054-330-6356 ¦ ¦ 경 상북 도 ¦ 영주시청 ¦ 건축과 건축행정팀 ¦ (36132) 경북 영주시 시청로 1 ¦ 054-639-6944 ¦ ¦ 경 상북 도 ¦ 의성군청 ¦ 민원과 건축계 ¦ (37337) 경북 의성군 의성읍 군청길 31 ¦ 054-830-6363 ¦ ¦ 경 상북 도 ¦ 청도군청 ¦ 민원과 건축디자인계 ¦ (38330) 경북 청도군 화양읍 청화로 70 ¦ 054-370-6354 ¦ ¦ 경 상북 도 ¦ 성주군청 ¦ 기계설비 담당 ¦ (40022) 경북 성주군 성주읍 성주로 3200 ¦ 054-933-0021 ¦ ¦ 경 상북 도 ¦ 고령군청 ¦ 기계설비 담당 ¦ (40138) 경북 고령군 대가야읍 왕릉로 55 ¦ 054-954-2201 ¦ ¦ 경 상북 도 ¦ 영덕군청 ¦ 도시디자인과 건축디자인팀 ¦ (36429) 경북 영덕군 영덕읍 군청길 116 ¦ 054-730-6353 ¦ ¦ 경 상북 도 ¦ 군위군청 ¦ 민원봉사과 건축계 ¦ (39013) 경북 군위군 군위읍 군청로 200 ¦ 054-380-6355 ¦ ¦ 경 상북 도 ¦ 예천군청 ¦ 건축과 건축행정팀 ¦ (36826) 경북 예천군 예천읍 충효로 111 ¦ 054-650-6941 ¦ ¦ 경 상북 도 ¦ 울릉군청 ¦ 지역개발과 주택건축팀 ¦ (40222) 경북 울릉군 울릉읍 도동 2 길 66 ¦ 054-790-6337 ¦ ¦ 경 상북 도 ¦ 영양군청 ¦ 종합민원과 건축팀 ¦ (36537) 경북 영양군 영양읍 군청길 37 ¦ 054-680-6351 ¦ ¦ 경 상북 도 ¦ 봉화군청 ¦ 종합민원과 건축관리팀 ¦ (36239) 경북 봉화군 봉화읍 봉화로 1111 ¦ 054-679-6464 ¦ ¦ 경 상북 도 ¦ 청송군청 ¦ 종합민원과 건축팀 ¦ (37427) 경북 청송군 청송읍 군청로 51 ¦ 054-870-6353 ¦ ¦ 제주 도 ¦ 제주시청 ¦ 건설과 건설행정팀 ¦ (63208) 제주시 광양 9 길 10 ¦ 064-728-3748 ¦ ¦ 제주 도 ¦ 서귀포시청 ¦ 건설과 건설행정팀 ¦ (63584) 서귀포시 중앙로 105 ¦ 064-760-3077 ¦ 430 기계설비 기술기준 매뉴얼 | {}
fc205eae-4e7b-4515-bf10-f8638e02c494 | 국내_기계설비_기술기준_매뉴얼_최종본 | ■ 기계설비 기술기준 [별지 제 1 호 서식] ¦ 기계설비 착공 전 확인표 ¦ 기계설비 착공 전 확인표 ¦ 기계설비 착공 전 확인표 ¦ 기계설비 착공 전 확인표 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 구 분 ¦ 확 인 항 목 ¦ 해당여부 ¦ 확인결과 ¦ ¦ 일 반 ¦ 기계설비기술기준 제 6 조에 따른 기계설비설계원칙 적용 여부 확인 ¦ [] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 1] ¦ 지역난방 의무고시지역 적용 여부 확인 ¦ [] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 1] ¦ 냉난방 설계기준 온도 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 1] ¦ 냉각탑 수처리 설비 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 1] ¦ 축열시설 40%이상 부분냉방식 적용 여부 확인 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ [별표 1] ¦ 열교환기 안전밸브 설치 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 1] ¦ 팽창탱크 배관의 역류방지밸브 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 1] ¦ 펌프 효율은 KS 규격 이상 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 1] ¦ 항온항습기 비상전원 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 2] ¦ 건축물의 규모 및 형태에 따른 공기조화 조닝 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 2] ¦ 팬코일의 열수요 변화 대응 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 3] ¦ 건축물 및 시설물의 필요 환기량 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 3] ¦ 시설 용도에 맞는 환기방식 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 3] ¦ 환기설비의 열교환 효율 기입 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 4] ¦ 위생기구 종류에 따른 사용조건 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 4] ¦ 설치장소와 이용자의 편의 성 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 4] ¦ 위생설비별 절수기능 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 5] ¦ 음료용 급수의 음용수 전용 공급 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 5] ¦ 저수조 최대급수량에 따른 오버플로관 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 5] ¦ 급탕탱크방식의 팽창탱크 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 6] ¦ 오배수 집수정크기 적정 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 6] ¦ 오배수 배관 청소구 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 6] ¦ 집수정 펌프 배관과 토출관 배관 크기 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 7] ¦ 하수도법에 따른 개인하수처리시설의 설치기준 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 7] ¦ 오수발생량과 정화조 처리대상인원의 고시기준 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 7] ¦ 빗물저류조 시설 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 8] ¦ 냉온수배관의 신축이음 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 [] 적합 [] 부적합 ¦ ¦ [별표 8] ¦ 용도에 맞는 배관 선정 및 호칭지름 적용 여부 확인 고압증기배관의 압력배관 적용 여부 확인 ¦ [ ] [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 9] ¦ 사용용도에 따른 덕트 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 9] ¦ 외기도입구와 배기구 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 10] ¦ 배관 및 덕트 등 보온설비 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 10] ¦ 수도계량기보호함의 보온 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 10] ¦ 동파방지 열선 적용 및 이상 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 11] ¦ 경보 및 감시시스템 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ [별표 11] ¦ 원격검침 시스템 적용 여부 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 방음 ·방진· 내진 등 적용 여부 확인 ¦ ¦ [] 적합 [] 부적합 ¦ ¦ ¦ [ ] ¦ ¦ ¦ ¦ [별표 12] [별표 15] ¦ 기계설비 유지관리를 고려한 설계 적용 여부 확인 ¦ [] 현장배치기계설비기술인 ¦ [] 적합 [] 부적합 확인일 ¦ ¦ 구 분 기계설비 ¦ 회사명/대표자 (인) ¦ (인) ¦ ¦ ¦ 설계자 기계설비 ¦ ¦ ¦ ¦ 시공자 (인) (인) 작성방법: 해당여부 및 확인결과 에 V 표시를 한다. 210mmX297mm[백상지 80g/m2] | {}
ccf64577-fc39-4155-be21-7c57b37300d8 | 국내_기계설비_기술기준_매뉴얼_최종본 | ■ 기계설비 기술기준 [별지 제 2 호서식] 기계설비 착공적합 확인서 ¦ 기계설비 감리업무 수행자 ¦ 상 호 ¦ ¦ 기계설비 감리 관련 등록번호 ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기계설비 감리업무 수행자 ¦ 대 표 자 ¦ (서명 또는 인) ¦ 전 화 번 호 ¦ ¦ ¦ 공사명 ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 건축허가번호 ¦ ¦ ¦ ¦ ¦ 현장배치 기계설비감리인 ¦ (서명 또는 인) ¦ 작 성 일 ¦ · ¦ ¦ 확 인 내 용 ¦ 해당여부 ¦ 확인결과 ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ 1. 기계설비 일반 ¦ 1) 기계설비 설계원칙 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 2) 기계설비 시공원칙 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 3) 유지관리 고려한 설계 및 시공 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ 2. 기계설비 설계 및 시공기준 ¦ 1) 열원 및 냉난방설비 [별표 1] ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 2) 공기조화설비 [별표 2] ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 3) 환기설비 [별표 3] ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 4) 위생기구설비 [별표 4] ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 5) 급수·급탕설비 [별표 5] ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 6) 오·배수통기 및 우수배수설비 [별표 6] ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 7) 오수정화 및 물재이용설비 [별표 7] ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 8) 배관설비 [별표 8] ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 9) 덕트설비 [별표 9] ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 10) 보온설비 [별표 10] ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 11) 자동제어설비 [별표 11] ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 12) 방음·방진·내진설비 [별표 12] ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 첨부서류 : 기계설비 착공 전 확인표 ¦ 첨부서류 : 기계설비 착공 전 확인표 ¦ 종합 검토의 견 작성 방법 : 1. 기계설비 착공전 확인표를 확인하여 작성 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 한다. ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 2. 해당하는 ¦ ¦ --- ¦ ¦ 곳에 V 표시를 한다. ¦ 210mmX297mm[백상지 80g/m2] | {}
60a6c48c-a0d8-44bc-b358-268a2427df4a | 국내_기계설비_기술기준_매뉴얼_최종본 | ■ 기계설비 기술기준 [별지 제 3 호서식] (1 쪽) ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 1] 열원 및 냉난방설비 ¦ [별표 1] 열원 및 냉난방설비 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ 열원 및 냉난방설비(1/2) ¦ 위치 ¦ ¦ ¦ ¦ 공 종 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 자 재 ¦ 주요기자재 선정 및 사용은 적합한가 ¦ 주요기자재 선정 및 사용은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 냉동기, 냉온수기 설치는 기술기준에 적합한가 ¦ 냉동기, 냉온수기 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 보일러 설치는 기술기준에 적합한가 ¦ 보일러 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 항온항습기, 열펌프 설치는 기술기준에 적합한가 ¦ 항온항습기, 열펌프 설치는 기술기준에 적합한가 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 패키지 에어컨 설치는 기술기준에 적합한가 ¦ 패키지 에어컨 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 냉각탑 설치는 기술기준에 적합한가 ¦ 냉각탑 설치는 기술기준에 적합한가 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 펌프 설치는 기술기준에 적합한가 ¦ 펌프 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 열교환기 설치는 기술기준에 적합한가 ¦ 열교환기 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 탱크류 설치는 기술기준에 적합한가 ¦ 탱크류 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 장비별 배관 접속은 기술기준에 적합한가 ¦ 장비별 배관 접속은 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 열원기기의 명판 및 마감상태는 적합한가 ¦ 열원기기의 명판 및 마감상태는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 열원기기류의 작동과 성능은 적합한가 ¦ 열원기기류의 작동과 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 (인) ¦ ¦ 확인일 ¦ ¦ 회사명(상호) ¦ ¦ ¦ ¦ ¦ ¦ 회사명(상호) ¦ ¦ ¦ (인) ¦ (인) ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/m2 ] | {}
e512992e-dbcf-4dd0-aa4d-ecf1f2d8141f | 국내_기계설비_기술기준_매뉴얼_최종본 | (2 쪽) ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 1] ¦ [별표 1] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ 신재생에너지설비 ¦ 신재생에너지설비 ¦ ¦ 공 종 ¦ 열원 및 냉난방설비(2/2) ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ 1 ¦ [ ] 적합 [] 부적합 ¦ ¦ 자 재 ¦ 주요기자재 선정 및 사용은 적합한가 ¦ 주요기자재 선정 및 사용은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 지열 설비의 설치는 기술기준에 적합한가 ¦ 지열 설비의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 태양열 설비의 설치는 기술기준에 적합한가 ¦ 태양열 설비의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 연료전지 설비의 설치는 기술기준에 적합한가 ¦ 연료전지 설비의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 배관 계통과 장비의 연결 상태는 기술기준에 적합한가 ¦ 배관 계통과 장비의 연결 상태는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 탱크류(급수, 급탕, 팽창탱크 등)의 설치는 기술기준에 적합한가 ¦ 탱크류(급수, 급탕, 팽창탱크 등)의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 밸브류, 기기류 설치는 기술기준에 적합한가 ¦ 밸브류, 기기류 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 연료전지실의 환기설비 설치는 기술기준에 적합한가 ¦ 연료전지실의 환기설비 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 동파방지, 과열방지 등의 조치는 기술기준에 적합한가 ¦ 동파방지, 과열방지 등의 조치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 장비명판, 계통도 표지 등 마감상태는 기술기준에 적합한가 ¦ 장비명판, 계통도 표지 등 마감상태는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 신재생(지열, 태양열, 연료전지) 설비의 작동과 성능은 적합한가 ¦ 신재생(지열, 태양열, 연료전지) 설비의 작동과 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 ¦ 확인일 ¦ 확인일 ¦ ¦ 회사명(상호) ¦ ¦ ¦ (인) ¦ (인) ¦ ¦ 회사명(상호) ¦ ¦ ¦ (인) ¦ (인) ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/m2 ] | {}
479fdd78-c7b8-43d9-a0e2-920cb00970d6 | 국내_기계설비_기술기준_매뉴얼_최종본 | (3 쪽) ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 2] 공기조화설비 ¦ [별표 2] 공기조화설비 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 공 종 ¦ 공기조화설비 ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 자 재 ¦ 주요기자재 선정 및 사용은 적합한가 ¦ 주요기자재 선정 및 사용은 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 공기조화기의 설치는 기술기준에 적합한가 ¦ 공기조화기의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 팬코일유닛의 설치는 기술기준에 적합한가 ¦ 팬코일유닛의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 방열기의 설치는 기술기준에 적합한가 ¦ 방열기의 설치는 기술기준에 적합한가 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 온수온돌난방의 설치는 기술기준에 적합한가 ¦ 온수온돌난방의 설치는 기술기준에 적합한가 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 배관 및 덕트 등의 연결상태는 기술기준에 적합한가 ¦ 배관 및 덕트 등의 연결상태는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 밸브 및 계측기기류 설치는 기술기준에 적합한가 ¦ 밸브 및 계측기기류 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 보온 및 마감상태는 기술기준에 적합한가 ¦ 보온 및 마감상태는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 공기조화기의 작동은 적합한가 ¦ 공기조화기의 작동은 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 온수온돌난방설비의 공기빼기작동은 적합한가 ¦ 온수온돌난방설비의 공기빼기작동은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 ¦ 확인일 ¦ 확인일 ¦ ¦ 회사명(상호) ¦ ¦ ¦ (인) ¦ (인) ¦ ¦ 회사명(상호) ¦ ¦ ¦ (인) ¦ (인) ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/m2 ] | {}
7cc3b4c3-8399-4b23-ac9e-ab8291685177 | 국내_기계설비_기술기준_매뉴얼_최종본 | (4 쪽) ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 3] 환기설비 ¦ [별표 3] 환기설비 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 공 종 ¦ 환기설비 ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ ] ¦ [ ] 적합 [ ] 부적합 ¦ ¦ 자 재 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ [ ] ¦ [ 1 적합 [] 부적합 ¦ ¦ 시 공 ¦ 송풍기의 설치는 기술기준에 적합한가 ¦ 송풍기의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 열회수형 환기장치의 설치는 기술기준에 적합한가 ¦ 열회수형 환기장치의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 주차장 배기송풍기는 기술기준에 적합한가 ¦ 주차장 배기송풍기는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 송풍기의 방진장치 설치는 기술기준에 적합한가 ¦ 송풍기의 방진장치 설치는 기술기준에 적합한가 ¦ [ 1 ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 환기장치의 공기흡입구와 배기구 설치는 기술기준에 적합한가 ¦ 환기장치의 공기흡입구와 배기구 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 송풍기와 덕트 등의 연결상태는 기술기준에 적합한가 ¦ 송풍기와 덕트 등의 연결상태는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 송풍기의 작동과 성능은 적합한가 ¦ 송풍기의 작동과 성능은 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 ¦ 확인일 ¦ 확인일 ¦ ¦ 회사명(상호) ¦ ¦ ¦ (인) ¦ (인) ¦ ¦ 회사명(상호) ¦ ¦ ¦ (인) ¦ (인) ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/m2] | {}
d8a22ed1-9968-423c-a95a-68737983cb36 | 국내_기계설비_기술기준_매뉴얼_최종본 | (5 쪽) ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 4] ¦ [별표 4] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ 위생기구설비 ¦ 위생기구설비 ¦ ¦ 공 종 ¦ 위생기구설비 ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 자 재 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 대변기의 설치는 기술기준에 적합한가 ¦ 대변기의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 세면기의 설치는 기술기준에 적합한가 ¦ 세면기의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 소변기의 설치는 기술기준에 적합한가 ¦ 소변기의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 욕조의 설치는 기술기준에 적합한가 ¦ 욕조의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 악세사리(수건걸이, 거울, 선반, 청소도구함, 잡지꽂이 등) 설치는 기술기준에 적합한가 ¦ 악세사리(수건걸이, 거울, 선반, 청소도구함, 잡지꽂이 등) 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 급수전 및 배수기구의 설치는 기술기준에 적합한가 ¦ 급수전 및 배수기구의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 급수구, 배수구 주변처리 등 설치는 기술기준에 적합한가 ¦ 급수구, 배수구 주변처리 등 설치는 기술기준에 적합한가 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 위생기구의 접속상태는 기술기준에 적합한가 ¦ 위생기구의 접속상태는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 고정상태, 외부손상상태 등 마감상태는 기술기준에 적합한가 ¦ 고정상태, 외부손상상태 등 마감상태는 기술기준에 적합한가 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 위생기구의 급수 및 배수 성능은 적합한가 ¦ 위생기구의 급수 및 배수 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 위생기구의 작동과 성능은 적합한가 ¦ 위생기구의 작동과 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 ¦ ¦ 확인일 ¦ ¦ 회사명(상호) ¦ ¦ ¦ (인) ¦ (인) ¦ ¦ 회사명(상호) ¦ ¦ ¦ ¦ ¦ ¦ (인) 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 ¦ (인) 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 ¦ (인) 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 ¦ (인) 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 ¦ (인) 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 ¦ 210mmX297mm[백상지 80g/m2] | {}
378b4c22-d9eb-49bb-8be5-cea0273ba226 | 국내_기계설비_기술기준_매뉴얼_최종본 | (6 쪽) ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 5] ¦ [별표 5] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ 급수·급탕설비 ¦ 급수·급탕설비 ¦ ¦ 공 종 ¦ 급수·급탕설비 ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 자 재 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 급수펌프의 설치는 기술기준에 적합한가 ¦ 급수펌프의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 급탕펌프의 설치는 기술기준에 적합한가 ¦ 급탕펌프의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 저수조(고가, 지하 등)의 설치는 기술기준에 적합한가 ¦ 저수조(고가, 지하 등)의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 장비류의 배관 접속상태는 기술기준에 적합한가 ¦ 장비류의 배관 접속상태는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 역류방지밸브 등 세대 인입급수관 기기류의 설치는 기술기준에 적합한가 ¦ 역류방지밸브 등 세대 인입급수관 기기류의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 음용수 배관, 음수기 등의 설치는 기술기준에 적합한가 ¦ 음용수 배관, 음수기 등의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 개별급탕기기(순간온수기) 급탕가열장치 등 설치는 기술기준에 적합한가 ¦ 개별급탕기기(순간온수기) 급탕가열장치 등 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 수격방지기의 설치는 기술기준에 적합한가 ¦ 수격방지기의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 급탕배관의 신축이음은 기술기준에 적합한가 ¦ 급탕배관의 신축이음은 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 급수·급탕설비의 마감상태는 기술기준에 적합한가 ¦ 급수·급탕설비의 마감상태는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 급수의 유량 및 수압 성능은 적합한가 ¦ 급수의 유량 및 수압 성능은 적합한가 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 급탕의 온도 및 수압 성능은 적합한가 ¦ 급탕의 온도 및 수압 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 ¦ 확인일 ¦ 확인일 ¦ ¦ 회사명(상호) ¦ ¦ ¦ (인) ¦ (인) ¦ ¦ 회사명(상호) ¦ (인) ¦ ¦ ¦ ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/m2 ] | {}
96354adb-e31d-4f8b-a499-8519b32ca571 | 국내_기계설비_기술기준_매뉴얼_최종본 | (7 쪽) ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 6] ¦ [별표 6] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ 오·배수 통기/우수배수설비 ¦ 오·배수 통기/우수배수설비 ¦ ¦ 공 종 ¦ 오·배수 통기 및 우수배수설비 ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 자 재 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 오·배수배관의 설치는 기술기준에 적합한가 ¦ 오·배수배관의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 통기배관의 설치는 기술기준에 적합한가 ¦ 통기배관의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 우수배수관의 설치는 기술기준에 적합한가 ¦ 우수배수관의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 위생기구, 배수구 등과 의 접속상태는 기술기준에 적합한가 ¦ 위생기구, 배수구 등과 의 접속상태는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 동파우려 개소에 대한 방동조치는 기술기준에 적합한가 ¦ 동파우려 개소에 대한 방동조치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 통기관 외부 마감기구의 설치는 기술기준에 적합한가 ¦ 통기관 외부 마감기구의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 오·배수관과 우수배수관의 분리 시공 상태는 기술기준에 적합한가 ¦ 오·배수관과 우수배수관의 분리 시공 상태는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 배관 내외부의 청소 등 마감상태는 기술기준에 적합한가 ¦ 배관 내외부의 청소 등 마감상태는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 오·배수관 및 우수배수관의 수밀성과 배수성능은 적합한가 ¦ 오·배수관 및 우수배수관의 수밀성과 배수성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 우수관의 통기 성능은 적합한가 ¦ 우수관의 통기 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 침수 등 비상시를 대비한 설비는 기술기준에 적합한가 ¦ 침수 등 비상시를 대비한 설비는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 ¦ 확인일 ¦ 확인일 ¦ ¦ 회사명(상호) ¦ ¦ ¦ (인) ¦ (인) ¦ ¦ 회사명(상호) ¦ ¦ ¦ (인) ¦ (인) ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/m2] | {}
3a98e62e-2b0e-495e-b8ad-5ea3365678ed | 국내_기계설비_기술기준_매뉴얼_최종본 | (8 쪽) ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 7] ¦ [별표 7] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ 오수정화 및 물재이용설비 ¦ 오수정화 및 물재이용설비 ¦ ¦ 공 종 ¦ 오수정화 및 물재이용설비 ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 자 재 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 오수정화설비의 설치는 기술기준에 적합한가 ¦ 오수정화설비의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 빗물이용설비의 설치는 기술기준에 적합한가 ¦ 빗물이용설비의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 중수처리설비의 설치는 기술기준에 적합한가 ¦ 중수처리설비의 설치는 기술기준에 적합한가 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 펌프류의 설치는 기술기준에 적합한가 ¦ 펌프류의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 송풍기의 설치는 기술기준에 적합한가 ¦ 송풍기의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 밸브류, 기기류 등의 설치는 기술기준에 적합한가 ¦ 밸브류, 기기류 등의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 장비계통도, 명판부착 등 외부 마감상태는 기술기준에 적합한가 ¦ 장비계통도, 명판부착 등 외부 마감상태는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 오수정화설비의 수처리 성능은 적합한가 ¦ 오수정화설비의 수처리 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 물재이용설비의 수처리 성능은 적합한가 ¦ 물재이용설비의 수처리 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 중수처리설비의 수처리 성능은 적합한가 ¦ 중수처리설비의 수처리 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 ¦ 확인일 ¦ 확인일 ¦ ¦ 회사명(상호) ¦ (인) ¦ ¦ ¦ ¦ ¦ 회사명(상호) (인) ¦ ¦ ¦ ¦ ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/m2 ] | {}
48f56787-dcac-4f69-a0d5-b6360fef7d60 | 국내_기계설비_기술기준_매뉴얼_최종본 | (9 쪽) ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 8] 배관설비 ¦ [별표 8] 배관설비 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ ¦ ¦ ¦ 공 종 ¦ 배관설비 ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 자 재 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 냉난방배관, 증기배관의 설치는 기술기준에 적합한가 ¦ 냉난방배관, 증기배관의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 냉각수, 냉·온수 배관의 설치는 기술기준에 적합한가 ¦ 냉각수, 냉·온수 배관의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 각종 장비류(펌프, 냉동기 등) 접속부분의 설치는 기술기준에 적합한가 ¦ 각종 장비류(펌프, 냉동기 등) 접속부분의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 난방급탕 및 증기배관 신축이음의 설치는 기술기준에 적합한가 ¦ 난방급탕 및 증기배관 신축이음의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 밸브류, 기기류 등의 설치는 기술기준에 적합한가 ¦ 밸브류, 기기류 등의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 배관의 경로, 고정 상태는 기술기준에 적합한가 ¦ 배관의 경로, 고정 상태는 기술기준에 적합한가 ¦ I ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 배관의 구배 등이 적절하며, 유체의 흐름은 적합한가 ¦ 배관의 구배 등이 적절하며, 유체의 흐름은 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 배관의 유량분배는 적합한가 ¦ 배관의 유량분배는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 ¦ ¦ 확인일 ¦ ¦ 회사명(상호) ¦ ¦ (인) ¦ ¦ ¦ ¦ 회사명(상호) ¦ ¦ (인) ¦ ¦ ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/m2 ] | {}
bcbc9dd1-64d3-4d86-ac10-66f8a3cf54be | 국내_기계설비_기술기준_매뉴얼_최종본 | (10 쪽) ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 9] ¦ [별표 9] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ ¦ ¦ 덕트설비 ¦ 덕트설비 ¦ ¦ 공 종 ¦ 덕트설비 ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 자 재 ¦ 주요기자재 선정 및 사용은 적합한가 ¦ 주요기자재 선정 및 사용은 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 덕트 고정상태는 기술기준에 적합한가 ¦ 덕트 고정상태는 기술기준에 적합한가 ¦ [ 1 ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 덕트기구(디퓨저, 그릴, 외기구, 배기구 등) 설치는 기술기준에 적합한가 ¦ 덕트기구(디퓨저, 그릴, 외기구, 배기구 등) 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 방화구획 관통부의 F.D 설치는 기술기준에 적합한가 ¦ 방화구획 관통부의 F.D 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 덕트와 장비의 접속부분(플렉시블 조인트 등) 설치는 기술기준에 적합한가 ¦ 덕트와 장비의 접속부분(플렉시블 조인트 등) 설치는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 덕트 외면 손상여부 등 마감상태는 기술기준에 적합한가 ¦ 덕트 외면 손상여부 등 마감상태는 기술기준에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 덕트의 풍량은 설계기준 풍량에 적합한가 ¦ 덕트의 풍량은 설계기준 풍량에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 덕트와 장비 연결부분의 소음 및 진동 방지 상태는 적합한가 ¦ 덕트와 장비 연결부분의 소음 및 진동 방지 상태는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 (인) ¦ 확인일 ¦ 확인일 ¦ ¦ 회사명(상호) ¦ ¦ ¦ ¦ ¦ ¦ 회사명(상호) ¦ ¦ ¦ ¦ ¦ ¦ (인) 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 ¦ (인) 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 ¦ (인) 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 ¦ (인) 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 ¦ (인) 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 ¦ 210mmX297mm[백상지 80g/m2 ] | {}
602944b5-3666-4835-afb9-ac484dbc4476 | 국내_기계설비_기술기준_매뉴얼_최종본 | (11 쪽) ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 10] ¦ [별표 10] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ 보온설비 ¦ 보온설비 ¦ ¦ 공 종 ¦ 보온설비 ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 자 재 ¦ 주요기자재 선정 및 사용은 적합한가 ¦ 주요기자재 선정 및 사용은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 배관 보온재의 설치는 기술기준에 적합한가 ¦ 배관 보온재의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 장비 보온재의 설치는 기술기준에 적합한가 ¦ 장비 보온재의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 밸브, 기기류, 탱크류 등의 보온재의 설치는 기술기준에 적합한가 ¦ 밸브, 기기류, 탱크류 등의 보온재의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 보온 및 비보온 개소의 구별은 기술기준에 적합한가 ¦ 보온 및 비보온 개소의 구별은 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 방화구획 등 관통부 주변 시공은 기술기준에 적합한가 ¦ 방화구획 등 관통부 주변 시공은 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 발열선의 설치는 기술기준에 적합한가 ¦ 발열선의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 발열선의 과열방지에 대한 조치는 기술기준에 적합한가 ¦ 발열선의 과열방지에 대한 조치는 기술기준에 적합한가 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 보온관의 유로표지부착, 장비명판 식별여부 등 마감상태는 기술기준에 적합한가 ¦ 보온관의 유로표지부착, 장비명판 식별여부 등 마감상태는 기술기준에 적합한가 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 계량기함등의 동파방지는 기술기준에 적합한가 ¦ 계량기함등의 동파방지는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 배관류의 방동, 방로, 보온 성능은 적합한가 ¦ 배관류의 방동, 방로, 보온 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 장비류의 방동, 방로, 보온 성능은 적합한가 ¦ 장비류의 방동, 방로, 보온 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 열선 화재안전 등의 과열방지 조치는 적합한가 ¦ 열선 화재안전 등의 과열방지 조치는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 ¦ 확인일 ¦ 확인일 ¦ ¦ 회사명(상호) ¦ ¦ ¦ (인) ¦ (인) ¦ ¦ 회사명(상호) ¦ ¦ ¦ (인) ¦ (인) ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/m2] | {}
dbfb4cb3-0804-4759-b2a8-e8661779b849 | 국내_기계설비_기술기준_매뉴얼_최종본 | (12 쪽) ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 11] ¦ [별표 11] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ ¦ ¦ 자동제어설비 ¦ 자동제어설비 ¦ ¦ 공 종 ¦ 자동제어설비 ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 자 재 ¦ 주요기자재는 승인된 제품이며, 선정은 적합한가 ¦ 주요기자재는 승인된 제품이며, 선정은 적합한가 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 중앙관제설비의 설치는 기술기준에 적합한가 ¦ 중앙관제설비의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 건물에너지 관리시스템 설치는 기술기준에 적합한가 ¦ 건물에너지 관리시스템 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 현장제어설비 설치는 기술기준에 적합한가 ¦ 현장제어설비 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 원격검침설비 설치는 기술기준에 적합한가 ¦ 원격검침설비 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 공동주택 자동제어설비 설치는 기술기준에 적합한가 ¦ 공동주택 자동제어설비 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 자동제어 배관, 배선의 설치는 기술기준에 적합한가 ¦ 자동제어 배관, 배선의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 장비별 연동 및 인터록은 기술기준에 적합한가 ¦ 장비별 연동 및 인터록은 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 중앙관제설비의 작동과 성능은 적합한가 ¦ 중앙관제설비의 작동과 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 건물에너지 관리시스템의 작동과 성능은 적합한가 ¦ 건물에너지 관리시스템의 작동과 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 현장제어설비의 작동과 성능은 적합한가 ¦ 현장제어설비의 작동과 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 원격검침설비의 누수감지시스템의 작동과 성능은 적합한가 ¦ 원격검침설비의 누수감지시스템의 작동과 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 공동주택 자동제어설비의 작동과 성능은 적합한가 ¦ 공동주택 자동제어설비의 작동과 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 각 장비별 개별제어 및 통합제어 성능은 적합한가 (stand-alone and integrated) ¦ 각 장비별 개별제어 및 통합제어 성능은 적합한가 (stand-alone and integrated) ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 (인) ¦ 확인일 ¦ 확인일 ¦ ¦ 회사명(상호) ¦ ¦ ¦ ¦ ¦ ¦ 회사명(상호) ¦ ¦ ¦ ¦ ¦ ¦ (인) 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 ¦ (인) 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 ¦ (인) 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 ¦ (인) 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 ¦ (인) 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 ¦ 210mmX297mm[백상지 80g/m2 ] | {}
4d79d956-3efa-42a8-b334-db6438bd58bf | 국내_기계설비_기술기준_매뉴얼_최종본 | (13 쪽) ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ [별표 12] ¦ [별표 12] ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기계설비 사용 전 확인표 ¦ 기계설비 사용 전 확인표 ¦ 세부공종 ¦ 방음·방진·내진설비 ¦ 방음·방진·내진설비 ¦ ¦ 공 종 ¦ 방음·방진·내진설비 ¦ 위치 ¦ ¦ ¦ ¦ 구 분 ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 검 사 항 목 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ ¦ 도 서 ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ 준공도서는 기술기준에 적합한가 (준공도면, 시방서) ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 자 재 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ 주요기자재 선정 및 검수서류는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 각종 장비의 방음·방진설비 설치는 기술기준에 적합한가 ¦ 각종 장비의 방음·방진설비 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 각종 장비의 내진설비 설치는 기술기준에 적합한가 ¦ 각종 장비의 내진설비 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 배관의 방음·방진·내진 설비는 기술기준에 적합한가 ¦ 배관의 방음·방진·내진 설비는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 방음·방진 기초설비 및 보강재의 설치는 기술기준에 적합한가 ¦ 방음·방진 기초설비 및 보강재의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 내진기초설비 및 보강재의 설치는 기술기준에 적합한가 ¦ 내진기초설비 및 보강재의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 방음·방진·내진설비의 공간배치는 기술기준에 적합한가 ¦ 방음·방진·내진설비의 공간배치는 기술기준에 적합한가 ¦ I ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 이중바닥(잭업) 시스템의 설치는 기술기준에 적합한가 ¦ 이중바닥(잭업) 시스템의 설치는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 시 공 ¦ 방음·방진·내진설비의 마감상태는 기술기준에 적합한가 ¦ 방음·방진·내진설비의 마감상태는 기술기준에 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 각종 장비의 방음설비 성능은 적합한가 ¦ 각종 장비의 방음설비 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 각종 장비의 방진설비 성능은 적합한가 ¦ 각종 장비의 방진설비 성능은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 각종 장비의 내진설비 성능은 적합한가 ¦ 각종 장비의 내진설비 성능은 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 성 능 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ 유지관리 ¦ 유지관리공간은 적합한가 ¦ 유지관리공간은 적합한가 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ 구 분 ¦ 기계설비시공자 ¦ 현장배치기계설비기술인 (인) ¦ ¦ 확인일 ¦ ¦ 회사명(상호) ¦ ¦ ¦ ¦ ¦ ¦ 회사명(상호) (인) ¦ ¦ ¦ ¦ ¦ 주) 현장배치기계설비기술인(원도급자, 하도급자)이 다수인 경우에는 모두가 확인해야 함 210mmX297mm[백상지 80g/m2 ] | {}
785116c9-a98c-430f-8fbf-b10ca57c288e | 국내_기계설비_기술기준_매뉴얼_최종본 | 기계설비 기술기준 [별지 제 4 호서식] 기계설비 성능확인서 상 호 시공면허등록번호 기계설비 시 공 자 대 표 자 (서명 또는 인) 전 화 번 호 공 사 명 건축허가번호 현장배치 (서명 또는 인) 작 성 일 기계설비기술인 검 사 항 목 및 내 용 (해당항목만 V 기재) 해당여부 검사결과 비 고 1. 열원 및 냉난방설비 계통 1) 열원 장비 [ ] [] 적합 [] 부적합 2) 냉난방 펌프 [ ] [] 적합 [] 부적합 2. 공기조화/환기 계통 1) 공기조화기 [ ] [] 적합 [] 부적합 2) 송풍기 [ ] [] 적합 [] 부적합 3) 단말기기(팬코일, 방열기 등) [] [] 적합 [] 부적합 4) 환기장치(환기유니트 등) [ ] [] 적합 [] 부적합 5) 덕트 계통 [ ] [] 적합 [] 부적합 6) 배관 계통 [ ] [] 적합 [] 부적합 3. 위생기구/급수급탕/오배수통기 계통 1) 위생 펌프 [ ] [] 적합 [] 부적합 2) 배관 계통 [ ] [] 적합 [] 부적합 4. 오수정화, 중수도, 빗물처리 계통 1) 오수정화설비 [ ] [] 적합 [] 부적합 2) 중수도설비 [ ] [] 적합 [] 부적합 3) 빗물처리설비 [ ] [] 적합 [] 부적합 5. 자동제어 계통 1) 중앙제어설비 [ ] [] 적합 [] 부적합 2) 현장제어설비 [ ] [] 적합 [] 부적합 3) 건물에너지관리시스템(BENS) [ ] [] 적합 [] 부적합 4) 원격검침설비 [ ] [] 적합 [] 부적합 6. 방음방진내진 계통 1) 장비 [ ] [] 적합 [] 부적합 2) 덕트계통 [ ] [] 적합 [] 부적합 3) 배관계통 [ ] [] 적합 [] 부적합 210mmX297mm[백상지 80g/m2] | {}
8220e2b4-1329-41af-84d4-c2566caf116e | 국내_기계설비_기술기준_매뉴얼_최종본 | 기계설비 기술기준 [별지 제 5 호서식] 기계설비 안전확인서 ¦ 기계설비 시공자 ¦ 상 호 ¦ ¦ 시공면허등록번호 ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 기계설비 시공자 ¦ 대 표 자 ¦ (서명 또는 인) ¦ 전 화 번 호 ¦ ¦ ¦ 공 사 명 ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 건축허가번호 ¦ ¦ ¦ ¦ ¦ 현장배치 기계설비기술인 ¦ (서명 또는 인) ¦ 작 성 일 ¦ ¦ 검 사 항 목 및 내 용 해당여부 검사결과 비 고 ¦ (해당항목만 V 기재) ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 보일러실의 일산화탄소 감지기, 경보기는 적합한가 ¦ [ ] ¦ [ ] 적합 [ ] 부적합 ¦ ¦ ¦ 보일러의 안전장치는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 냉동기는 친환경냉매를 사용하기에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 냉동기의 안전장치는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 탱크류 안전밸브 설치는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 환기장치의 외기도입구 및 배기구는 안전에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 실외기는 안전에 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 냉각탑의 냉각수에 레지오넬라균 번식방지 조치는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 저수조 청소 완료(필증)는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 저수조 물넘침에 대비하여 배수시설과 알람시설은 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 음용수는 수질기준에 적합한가(시험성적서) ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 급수, 급탕 등의 역류방지 장치는 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 급탕가열장치의 온도 및 압력에 대한 안전장치는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 교차배관으로 인한 오염발생 방지조치는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 각 위생기구에 공급되는 급수압은 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 물배관 및 계량기의 동파방지 조치는 적합한가 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 동파방지 발열선의 과열시 전원차단 및 경보시설은 적합한가 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ 210mmX297mm[백상지 80g/m2 ] | {}
225b8277-f880-4cb4-a816-93f7496a3c19 | 국내_기계설비_기술기준_매뉴얼_최종본 | ■ 기계설비 기술기준 [별지 제 6 호서식] 기계설비 사용적합 확인서 기계설비 ¦ 감리업무 수행자 ¦ 상 호 ¦ ¦ 기계설비 감리 관련 등록번호 ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 감리업무 수행자 ¦ 대 표 자 ¦ (서명 또는 인) ¦ 전 화 번 호 ¦ ¦ ¦ 공사명 ¦ 공사명 ¦ ¦ ¦ ¦ ¦ 건축허가번호 ¦ 건축허가번호 ¦ ¦ ¦ ¦ ¦ 현장배치 기계설비감리인 ¦ 현장배치 기계설비감리인 ¦ (서명 또는 인) 작 성 일 ¦ (서명 또는 인) 작 성 일 ¦ ¦ ¦ 검 사 항 목 및 내 용 (해당항목만 V 기재) ¦ 검 사 항 목 및 내 용 (해당항목만 V 기재) ¦ 해당여부 ¦ 검사결과 ¦ 비 고 ¦ ¦ 1. 기계설비 유지관리 공간 계획 ¦ 1. 기계설비 유지관리 공간 계획 ¦ 1. 기계설비 유지관리 공간 계획 ¦ 1. 기계설비 유지관리 공간 계획 ¦ 1. 기계설비 유지관리 공간 계획 ¦ ¦ 1) 기계실 ¦ 1) 기계실 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 2) 피트 ¦ 2) 피트 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 3) 샤프트 ¦ 3) 샤프트 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 4) 점검구 ¦ 4) 점검구 ¦ [ ] ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 2. 기계설비 기술기준 ¦ 2. 기계설비 기술기준 ¦ 2. 기계설비 기술기준 ¦ 2. 기계설비 기술기준 ¦ 2. 기계설비 기술기준 ¦ ¦ 1) 열원 및 냉난방설비 ¦ 1) 열원 및 냉난방설비 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 2) 공기조화설비 ¦ 2) 공기조화설비 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 3) 환기설비 ¦ 3) 환기설비 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 4) 위생기구설비 ¦ 4) 위생기구설비 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 5) 급수 · 급탕설비 ¦ 5) 급수 · 급탕설비 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 6) 오·배수통기 및 우수배수설비 ¦ 6) 오·배수통기 및 우수배수설비 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 7) 오수정화 및 물재이용설비 ¦ 7) 오수정화 및 물재이용설비 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 8) 배관설비 ¦ 8) 배관설비 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 9) 덕트설비 ¦ 9) 덕트설비 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 10) 보온설비 ¦ 10) 보온설비 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 11) 자동제어설비 ¦ 11) 자동제어설비 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 12) 방음·방진·내진설비 ¦ 12) 방음·방진·내진설비 ¦ [ 1 ¦ [ ] 적합 [] 부적합 ¦ ¦ ¦ 3. 기계설비 안전 및 성능 확인 ¦ 3. 기계설비 안전 및 성능 확인 ¦ 3. 기계설비 안전 및 성능 확인 ¦ 3. 기계설비 안전 및 성능 확인 ¦ 3. 기계설비 안전 및 성능 확인 ¦ ¦ 1) 기계설비 성능 확인 ¦ 1) 기계설비 성능 확인 ¦ [ 1 ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 2) 기계설비 안전 확인 ¦ 2) 기계설비 안전 확인 ¦ [ ] ¦ [] 적합 [] 부적합 ¦ ¦ ¦ 첨부사항 1. 기계설비 사용 전 확인표 2. 기계설비 성능확인서 3. 기계설비 안전확인서 ¦ 첨부사항 1. 기계설비 사용 전 확인표 2. 기계설비 성능확인서 3. 기계설비 안전확인서 ¦ 첨부사항 1. 기계설비 사용 전 확인표 2. 기계설비 성능확인서 3. 기계설비 안전확인서 ¦ 첨부사항 1. 기계설비 사용 전 확인표 2. 기계설비 성능확인서 3. 기계설비 안전확인서 ¦ 첨부사항 1. 기계설비 사용 전 확인표 2. 기계설비 성능확인서 3. 기계설비 안전확인서 ¦ ¦ 종합 검토의 견 ¦ ¦ ¦ ¦ ¦ 210mmX297mm[백상지 80g/m2] | {}
cd409ba0-e215-48ad-b30b-3da1168d215c | 국내_기계설비_기술기준_매뉴얼_최종본 | 기계설비법 시행규칙 [별지 제 4 호서식] <개정 2022. 2. 25.> 기계설비공사 착공 전 확인신청서 ※ 색상이 어두운 칸은 신청인이 적지 않습니다. (앞 쪽) ¦ 접수번호 ¦ 접수일 ¦ 처리일 ¦ 처리기간 ¦ 14 일 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 신청인 (건축주) ¦ 성명(기관 또는 법인 명칭) ¦ 대표자 ¦ 대표자 ¦ 대표자 ¦ ¦ 신청인 (건축주) ¦ 주소 (전화번호: ¦ 주소 (전화번호: ¦ 주소 (전화번호: ¦ 주소 (전화번호: ¦ ¦ 공사 현장 명칭 ¦ ¦ ¦ ¦ ¦ ¦ 공사 현장 주소 ¦ ¦ ¦ ¦ ¦ ¦ 공사의 종류 ¦ ¦ ¦ ¦ ¦ ¦ 구조 및 용도 ¦ ¦ ¦ ¦ ¦ ¦ 건축면적 ¦ 제곱미터 ¦ 연면적/규모(층) ¦ 제곱미터/지하 층, 지상 층 ¦ 제곱미터/지하 층, 지상 층 ¦ ¦ 건축허가번호 ¦ ¦ 건축허가일 ¦ ¦ ¦ ¦ 착공 예정일 ¦ ¦ 준공예정일 ¦ 준공예정일 ¦ 준공예정일 ¦ ¦ 기계설비 설계자 ¦ 상호 ¦ 기계설비 설계 관련 등록(신고)번호 ¦ 기계설비 설계 관련 등록(신고)번호 ¦ 기계설비 설계 관련 등록(신고)번호 ¦ ¦ 기계설비 설계자 ¦ 대표자 (서명 또는 인) ¦ 전화번호 ¦ 전화번호 ¦ 전화번호 ¦ ¦ 기계설비 설계자 ¦ 영업소 소재지 ¦ 영업소 소재지 ¦ 영업소 소재지 ¦ 영업소 소재지 ¦ ¦ 기계설비 설계자 ¦ 도급 계약일 ¦ 도급 계약일 ¦ 도급 계약일 ¦ 도급 계약일 ¦ ¦ 기계설비 시공자 ¦ 상호 ¦ 공사업 등록 번호 ¦ 공사업 등록 번호 ¦ 공사업 등록 번호 ¦ ¦ 기계설비 시공자 ¦ 대표자 (서명 또는 인) ¦ 전화번호 ¦ 전화번호 ¦ 전화번호 ¦ ¦ 기계설비 시공자 ¦ 영업소 소재지 ¦ 현장 배치 기계설비기술인 ¦ 현장 배치 기계설비기술인 ¦ 현장 배치 기계설비기술인 ¦ ¦ 기계설비 시공자 ¦ 도급 계약일 ¦ 도급 계약일 ¦ 도급 계약일 ¦ 도급 계약일 ¦ ¦ 기계설비 감리업무 수행자 ¦ 상호 ¦ 기계설비 감리 관련 등록(신고)번호 ¦ 기계설비 감리 관련 등록(신고)번호 ¦ 기계설비 감리 관련 등록(신고)번호 ¦ ¦ 기계설비 감리업무 수행자 ¦ 대표자 (서명 또는 인) ¦ 전화번호 ¦ 전화번호 ¦ 전화번호 ¦ ¦ 기계설비 감리업무 수행자 ¦ 영업소 소재지 ¦ 현장배치기계설비감리인 ¦ 현장배치기계설비감리인 ¦ 현장배치기계설비감리인 ¦ ¦ 기계설비 감리업무 수행자 ¦ 도급 계약일 ¦ 도급 계약일 ¦ 도급 계약일 ¦ 도급 계약일 ¦ 「기계설비법」 제 15 조제 1 항, 같은 법 시행령 제 12 조제 1 항 및 같은 법 시행규칙 제 5 조제 1 항에 따라 위와 같이 기계설비공사 착공 전 확인을 신청합니다. 년 월 일 신청인 (서명 또는 인) 특별자치시장 · 특별자치도지사 · 시장 · 군수 · 자치구구청장 귀하 ¦ 첨부서류 ¦ 1. 기계설비공사 설계도서 사본 2. 기계설비설계자 등록증 사본 3. 「건축법」 등 관계 법령에 따라 기계설비에 대한 감리업무를 수행하는 자가 확인한 기계설비 착공 적합 확인서 ¦ ¦ --- ¦ --- ¦ ¦ 작 성 방 법 ¦ ¦ --- ¦ ¦ 기계설비시공자는 그 시공자 모두를 적으며, 하도급의 경우 하도급자를 포함하여 적습니다. ¦ 210mmX297mm[백상지(80g/m2) 또는 중질지(80g/m2)] | {}
87dc83c3-c919-4b91-a58e-ad52f629e3d3 | 국내_기계설비_기술기준_매뉴얼_최종본 | (뒤쪽) ¦ 처리절차 ¦ 처리절차 ¦ ¦ --- ¦ --- ¦ ¦ 이 신청서는 아래와 같이 처리됩니다. ¦ 이 신청서는 아래와 같이 처리됩니다. ¦ ¦ 신청인 ¦ 처리기관 ¦ ¦ 신청인 ¦ 특별자치시 · 특별자치도 · 시 · 군 · 구청 ¦ ¦ 신청서 발급 ¦ 접수 설계도서 확인 대장정리 기계설비공사 착공 전 확인 결과 통보서 ¦ 210mmX297mm[백상지(80g/m2)] | {}
1d44ad38-cbec-4a95-8903-19aa4d6af471 | 국내_기계설비_기술기준_매뉴얼_최종본 | 기계설비법 시행규칙 [별지 제 5 호서식 ] 기계설비공사 착공 전 확인 결과 통보서 발급번호 : 신 청 인 전화번호 (건축주) 주 소 기계설비설계자 전화번호 주 소 건축허가 건축현장명 번호 (소재지) 검토의 견 보완사항 관련 근거 (기술기준 등) ¦ 확인자 ¦ 소속 ¦ ¦ 성명 ¦ (서명 또는 인) ¦ 전화번호 ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ 「기계설비법」 제 15 조, 같은 법 시행령 제 12 조제 3 항 및 같은 법 시행규칙 제 5 조제 2 항에 따라 위와 같이 기계설비공사 착공 전 확인 결과 를 통보합니다. ※ 「기계설비법」 제 15 조제 1 항에 따라 발주자는 설계도서가 기술기준에 적합한지를 반드시 확인받아야 하며, 기계설비 사용 전 검사 결과 기술기준에 부적합한 사항이 있을 경우 이를 보완하지 않으면 재시공 등의 불이익이 있으니 반드시 보완 후 착공 해야 합니다. 년 월 일 특별자치시장 · 특별자치도지사 · 시장 · 군수 · 자치구구청장 직인 210mmX297mm[백상지(80g/m2) 또는 중질지(80g/m2)] | {}
23ed71cf-5bb3-4d9c-b1d8-7b5938f3a764 | 국내_기계설비_기술기준_매뉴얼_최종본 | ■ 기계설비법 시행규칙 [별지 제 6 호서식] 기계설비공사 착공 전 확인업무 관리대장 ¦ 일련 번호 ¦ 신청인 (건축주) ¦ 신청인 (건축주) ¦ 기계설비설계자 ¦ 기계설비설계자 ¦ 건축현장 ¦ 건축현장 ¦ 건축현장 ¦ 건축현장 ¦ 건축현장 ¦ 건축현장 ¦ 처리 ¦ 처리 ¦ 처리 ¦ 처리 ¦ 처리 ¦ 처리 ¦ 처리 ¦ 처리 ¦ 비 고 번 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 일련 번호 ¦ ¦ ¦ ¦ ¦ 건축현장 ¦ 건축현장 ¦ 건축현장 ¦ 건축현장 ¦ 건축현장 ¦ 건축현장 ¦ 착공 전 확인 ¦ 착공 전 확인 ¦ 착공 전 확인 ¦ 착공 전 확인 ¦ 착공 전 확인 ¦ 사용 전 검사 ¦ 사용 전 검사 ¦ 사용 전 검사 ¦ 비 고 번 ¦ ¦ 일련 번호 ¦ 성명 (기관 또 는 법인 명칭) ¦ 대표자 ¦ 상호 ¦ 기계설비 설계 관련 등록번호 ¦ 현장명 ¦ 현장 주소 ¦ 공사의 종류 ¦ 구조 및 용도 ¦ 건축 면적 ¦ 연면적/ 규모(층 수) ¦ 접수 일 ¦ 검토 자 ¦ 검토 의견 ¦ 통보서 발급 번호 ¦ 통 보 일 ¦ 접수 일 ¦ 확인증 검사 발급일 ¦ ¦ 인증 검사확 호 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ※ 검토의 견: 적합, 부적합(보완 필요) 작성 297mm X210mm[백상지(80g/m2) ] | {}
d0eb5d37-d82d-41e5-baf6-255704679d61 | 국내_기계설비_기술기준_매뉴얼_최종본 | 기계설비법 시행규칙 [별지 제 7 호서식] <개정 2021 2. 2.> 기계설비 사용 전 검사신청서 ※ 색상이 어두운 칸은 신청인이 적지 않습니다. (앞쪽) ¦ 접수번호 ¦ ¦ 접수일 ¦ 발급일 ¦ ¦ 처리기간 14 일 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 신청인 (건축주) ¦ 성명(기관 또는 법인 명칭) ¦ 대표자 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 신청인 (건축주) ¦ 주소 (전화번호: ) ¦ 주소 (전화번호: ) ¦ ¦ 기계설비 시공자 ¦ 상호 ¦ 공사업 등록번호 ¦ ¦ 기계설비 시공자 ¦ 대표자 (서명 또는 인) ¦ 전화번호 ¦ ¦ 기계설비 시공자 ¦ 영업소 소재지 ¦ 현장 배치 기계설비기술인 ¦ ¦ 기계설비 감리업무 수행자 ¦ 상호 ¦ 기계설비 감리 관련 등록(신고)번호 ¦ ¦ 기계설비 감리업무 수행자 ¦ 대표자 (서명 또는 인) ¦ 전화번호 ¦ ¦ 기계설비 감리업무 수행자 ¦ 영업소 소재지 ¦ 현장 배치 기계설비감리인 ¦ ¦ 건축허가 번호 ¦ ¦ 검사 현장 명칭 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 건축허가 번호 ¦ 검사 현장 주소 ¦ ¦ ¦ 공사의 종류 ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 구조 및 용도 ¦ ¦ ¦ ¦ ¦ 건축면적 ¦ 제곱미터 ¦ 연면적/규모(층수) ¦ 제곱미터/지하_ 층, 지상 층 ¦ ¦ 착공일 ¦ ¦ 완공일 ¦ ¦ ¦ 검사 희망 연월일 ¦ ¦ ¦ ¦ 「기계설비법」 제 15 조제 1 항, 같은 법 시행령 제 13 조제 1 항 및 같은 법 시행규칙 제 6 조제 1 항에 따라 기계설비 사용 전 검사를 신청합니다. 년 월 일 신 청 인 (서명 또는 인) 특별자치시장 · 특별자치도지사 · 시장 · 군수 · 자치구구청장 귀하 ¦ 첨부서류 ¦ 1. 기계설비공사 준공설계도서 사본 2. 「건축법」 등 관계 법령에 따라 기계설비에 대한 감리업무를 수행한 자가 확인한 기계설비 사용 적합 확인서 3. 「기계설비법 시행령」 제 13 조제 1 항 각 호에 대한 검사 결과 서(해당하는 검사 결과 가 있는 경우에만 제출합니다) ¦ 료 수 수 없 음 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ 작 성 방 법 ¦ ¦ --- ¦ --- ¦ 1. 연면적은 건축허가서상의 연면적을 적습니다. 2. 기계설비시공자는 그 시공자 모두를 적으며, 하도급의 경우 하도급자를 포함하여 적습니다. 210mmX297mm[백상지(80g/m2) 또는 중질지(80g/m2)] | {}
c2df2d05-ed00-4b5f-adb0-eb841d114a45 | 국내_기계설비_기술기준_매뉴얼_최종본 | (뒤쪽) 처 리 절 차 Chart Title: 이 신청서는 아래와 같이 처리됩니다. Chart Type: line 중계설비 사용 전 검사 확인증 발급 틔별자치시ᆞ특별자치도ᆞ시ᆞ군ᆞ구청 0.4 년 접 수 0.6 년 기계설비 0.0 년 사용 전 검사 확인증 착성 0.6 년 210mmX297mm[백상지(80g/ m2) 또는 중질지(80g/m2) ] | {}
4480b03d-cf4d-4699-9d70-d73c99228251 | 국내_기계설비_기술기준_매뉴얼_최종본 | 기계설비법 시행규칙 [별지 제 8 호서식] 기계설비 사용 전 검사 확인증 ¦ 신청인 (건축주) ¦ 성명(기관 또는 법인 명칭) ¦ 대표자 전화번호 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 신청인 (건축주) ¦ 주소 ¦ 주소 ¦ ¦ 기계설비 시공자 ¦ 상호 ¦ 공사업 등록번호 ¦ ¦ 기계설비 시공자 ¦ 대표자 ¦ 전화번호 ¦ ¦ 기계설비 시공자 ¦ 영업소 소재지 ¦ 영업소 소재지 ¦ ¦ 기계설비 감리업무 수행자 ¦ 상호 ¦ 기계설비 감리 관련 등록번호 ¦ ¦ 기계설비 감리업무 수행자 ¦ 대표자 ¦ 전화번호 ¦ ¦ 기계설비 감리업무 수행자 ¦ 영업소 소재지 ¦ 영업소 소재지 ¦ ¦ 검사 결과 ¦ 건축허가번호 ¦ 검사 현장 명칭 ¦ ¦ 검사 결과 ¦ 건축허가번호 ¦ 검사 현장 주소 ¦ ¦ 검사 결과 ¦ 검사 연월일 ¦ 검사 연월일 ¦ ¦ 검사 결과 ¦ 검사자 소속: ¦ 성명: (서명 또는 인) ¦ ¦ 검사 결과 ¦ 판정 ¦ 판정 ¦ 「기계설비법」 제 15 조, 같은 법 시행령 제 13 조제 3 항 및 같은 법 시행규칙 제 6 조제 2 항에 따라 위와 같이 기계설비 사용 전 검사 확인증을 발급합니다. 년 월 일 직인 특별자치시장 · 특별자치도지사 · 시장 · 군수 · 자치구구청장 210mmX297mm[백상지(120g/m2)] | {}
c751be2d-2640-4de2-ba76-6615e826b2f2 | 국내_기계설비_기술기준_매뉴얼_최종본 | 기계설비법 시행규칙 [별지 제 9 호서식] 기계설비 사용 전 검사 확인증 발급대장 ¦ 일련 번호 ¦ 신청인(건축주) ¦ 신청인(건축주) ¦ 건축 현장 ¦ 건축 현장 ¦ 건축 현장 ¦ 건축 현장 ¦ 건축 현장 ¦ 건축 현장 ¦ 처리 ¦ 처리 ¦ 처리 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 일련 번호 ¦ 성명 (기관 또는 법인 명칭) ¦ 대표자 ¦ 현장명 ¦ 현장 주소 ¦ 공사의 종류 ¦ 구조 및 용도 ¦ 건축 면적 ¦ 연면적/ 규모(층수) ¦ 검사 연월일 ¦ 발급 연월일 ¦ 담당자 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 297mmX210mm[백상지(80g/m2)] | {}
5889d2e9-623c-495c-9997-8331dd01d4dc | 국내_기계설비_기술기준_매뉴얼_최종본 | ■ 기계설비 착공 전 확인 검토표 작성양식 예시 ¦ 기계설비 착공 전 확인 검토표 ¦ 기계설비 착공 전 확인 검토표 ¦ 기계설비 착공 전 확인 검토표 ¦ 기계설비 착공 전 확인 검토표 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 구분 ¦ 검 사 항 목 ¦ 해당 해 당 근 거 여부 ¦ 첨부 서류 ¦ ¦ 별표 1 ¦ 지역난방 의무고시지역 적용 여부 확인 ¦ [ ] ¦ ¦ ¦ 별표 1 ¦ 냉난방 설계기준 온도 적용 여부 확인 ¦ [ 1 ¦ ¦ ¦ 별표 1 ¦ 냉각탑 수처리 설비 적용 여부 확인 ¦ [ ] ¦ ¦ ¦ 별표 1 ¦ 축열시설 40%이상 부분냉방식 적용 여부 확인 ¦ [ 1 ¦ ¦ ¦ 별표 1 ¦ 열교환기 안전밸브 설치 적용 여부 확인 ¦ [ ] ¦ ¦ ¦ 별표 1 ¦ 팽창탱크 배관의 역류방지밸브 적용 여부 확인 ¦ [ ] ¦ ¦ ¦ 별표 1 ¦ 펌프 효율은 KS 규격 이상 적용 여부 확인 [ 1 ¦ ¦ ¦ ¦ 별표 1 ¦ 항온항습기 비상전원 적용 여부 확인 [ ] ¦ ¦ ¦ ¦ 별표 2 ¦ 건축물의 규모 및 형태에 따른 공기조화 조닝 적용 여부 확인 ¦ [ 1 ¦ ¦ ¦ 별표 2 ¦ 팬코일의 열수요 변화 대응 적용 여부 확인 ¦ [ 1 ¦ ¦ ¦ 별표 3 ¦ 건축물 및 시설물의 필요 환기량 적용 여부 확인 ¦ [ ] ¦ ¦ ¦ 별표 3 ¦ 시설 용도에 맞는 환기방식 적용 여부 확인 [ ] ¦ ¦ ¦ ¦ 별표 3 ¦ 환기설비의 열교환 효율 기입 적용 여부 확인 ¦ [ ] ¦ ¦ ¦ 별표 4 ¦ 위생기구 종류에 따른 사용조건 적용 여부 확인 ¦ [ 1 ¦ ¦ ¦ 별표 4 ¦ 설치장소와 이용자의 편의 성 적용 여부 확인 ¦ [ ] ¦ ¦ ¦ 별표 4 ¦ 위생설비별 절수기능 적용 여부 확인 ¦ [ 1 ¦ ¦ ¦ 별표 5 ¦ 음료용 급수의 음용수 전용 공급 여부 확인 ¦ [ ] ¦ ¦ ¦ 별표 5 ¦ 저수조 최대급수량에 따른 오버플로관 적용 여부 확인 ¦ [ ] ¦ ¦ ¦ 별표 5 ¦ 급탕탱크방식의 팽창탱크 적용 여부 확인 ¦ [ 1 ¦ ¦ ¦ 별표 6 ¦ 오배수 집수정크기 적정 여부 확인 ¦ [ ] ¦ ¦ ¦ 별표 6 ¦ 오배수 배관 청소구 적용 여부 확인 ¦ [ 1 ¦ ¦ ¦ 별표 6 ¦ 집수정 펌프 배관과 토출관 배관 크기 확인 ¦ [ 1 ¦ ¦ ¦ 별표 7 ¦ 하수도법에 따른 개인하수처리시설의 설치기준 적용 여부 확인 ¦ [ 1 ¦ ¦ ¦ 별표 7 ¦ 오수발생량과 정화조 처리대상인원의 고시기준 적용 여부 확인 ¦ [ 1 ¦ ¦ ¦ 별표 7 ¦ 빗물저류조 시설 적용 여부 확인 ¦ [ 1 ¦ ¦ ¦ 별표 8 ¦ 냉온수배관의 신축이음 적용 여부 확인 ¦ [ ] ¦ ¦ ¦ 별표 8 ¦ 용도에 맞는 배관 선정 및 호칭지름 적용 여부 확인 ¦ [ ] ¦ ¦ ¦ 별표 8 ¦ 고압증기배관의 압력배관 적용 여부 확인 ¦ [ 1 ¦ ¦ ¦ 별표 9 ¦ 사용용도에 따른 덕트 적용 여부 확인 [ ] ¦ ¦ ¦ ¦ 별표 9 ¦ 외기도입구와 배기구 적용 여부 확인 ¦ [ ] ¦ ¦ ¦ 별표 10 ¦ 배관 및 덕트 등 보온설비 적용 여부 확인 ¦ [ ] ¦ ¦ ¦ 별표 10 ¦ 수도계량기보호함의 보온 적용 여부 확인 [ ] ¦ ¦ ¦ ¦ 별표 10 ¦ 동파방지 열선 적용 및 이상 여부 확인 [ 1 ¦ ¦ ¦ ¦ 별표 11 ¦ 경보 및 감시시스템 적용 여부 확인 ¦ [ ] ¦ ¦ ¦ 별표 11 ¦ 원격검침 시스템 적용 여부 확인 ¦ [ 1 ¦ ¦ ¦ 별표 12 ¦ 방음 ·방진· 내진 등 적용 여부 확인 [ ¦ ] ¦ ¦ | {}
806bdc7e-b94f-410c-9be9-ac17e650033f | 국내_기계설비_기술기준_매뉴얼_최종본 | ■ 기계설비 사용 전 검사 검토표 작성양식 예시 기계설비 사용 전 검사 검토표[별표 1 열원 및 냉난방] ¦ 구분 ¦ 검 사 항 목 ¦ 해당 여부 ¦ ¦ 해 당 근 거 ¦ 첨부 서류 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도서 ¦ 준공도서는 기술기준에 적합한가(준공 도면, 시방서) ¦ [ ] ¦ ¦ ¦ ¦ ¦ 자재 ¦ 주요기자재 선정 및 사용은 적합한가 ¦ [ 1 ¦ ¦ ¦ ¦ ¦ 시공 ¦ 1. 냉동기, 냉온수기 설치는 기술기준에 적합한가 ¦ [ ] ¦ 1-1 ¦ ¦ ¦ ¦ 시공 ¦ 1. 냉동기, 냉온수기 설치는 기술기준에 적합한가 ¦ [ ] ¦ 1-2 ¦ ¦ ¦ ¦ 시공 ¦ 2. 보일러 설치는 기술기준에 적합한가 ¦ [ ] ¦ 2-1 ¦ ¦ ¦ ¦ 시공 ¦ 2. 보일러 설치는 기술기준에 적합한가 ¦ [ ] ¦ 2-2 ¦ ¦ ¦ ¦ 시공 ¦ 3. 항온항습기, 열펌프 설치는 기술기준 에 적합한가 ¦ [ ] ¦ 3-1 ¦ ¦ ¦ ¦ 시공 ¦ 3. 항온항습기, 열펌프 설치는 기술기준 에 적합한가 ¦ [ ] ¦ 3-2 ¦ ¦ ¦ ¦ 시공 ¦ 3. 항온항습기, 열펌프 설치는 기술기준 에 적합한가 ¦ [ ] ¦ 3-3 ¦ ¦ ¦ ¦ 시공 ¦ 4. 패키지 에어컨 설치는 기술기준에 합한가 ¦ 적 [ 1 ¦ 4-1 ¦ ¦ ¦ ¦ 시공 ¦ 4. 패키지 에어컨 설치는 기술기준에 합한가 ¦ 적 [ 1 ¦ 4-2 ¦ ¦ ¦ ¦ 시공 ¦ 4. 패키지 에어컨 설치는 기술기준에 합한가 ¦ 적 [ 1 ¦ 4-3 ¦ ¦ ¦ ¦ 시공 ¦ 5. 냉각탑 설치는 기술기준에 적합한가 ¦ [ ] ¦ ¦ ¦ ¦ ¦ 시공 ¦ 6. 펌프 설치는 기술기준에 적합한가 ¦ [ ] ¦ ¦ ¦ ¦ ¦ 시공 ¦ 7. 열교환기 설치는 기술기준에 적합한가 ¦ [ ] ¦ ¦ ¦ ¦ ¦ 시공 ¦ 8. 탱크류 설치는 기술기준에 적합한가 ¦ [ ] ¦ ¦ ¦ ¦ ¦ 시공 ¦ 9. 장비별 배관 접속은 기술기준에 적합 한가 ¦ [ 1 ¦ ¦ ¦ ¦ ¦ 시공 ¦ 10. 열원기기의 명판 및 마감상태는 적 합한가 ¦ [ ] ¦ ¦ ¦ ¦ ¦ 성능 ¦ 열원기기류의 작동과 성능은 적합한가 ¦ [ 1 ¦ ¦ ¦ ¦ ¦ 성능 ¦ 제작사의 성능시험 성적서는 적합한가 ¦ [ 1 ¦ ¦ ¦ ¦ ¦ 유지 관리 ¦ 유지관리(운전관리 등) 지침서는 적합한가 ¦ [ ] ¦ ¦ ¦ ¦ ¦ 유지 관리 ¦ 유지관리공간은 적합한가 ¦ [ 1 ¦ ¦ ¦ ¦ | {}
b035a048-5d91-4dec-bdc5-e563e4958cae | 국내_기계설비_기술기준_매뉴얼_최종본 | 기계설비 착공 전 확인 첨부서류-검토서 작성양식 예시 ¦ 첨부 00 기계설비 착공 전 확인 검토서 ¦ 첨부 00 기계설비 착공 전 확인 검토서 ¦ 첨부 00 기계설비 착공 전 확인 검토서 ¦ 첨부 00 기계설비 착공 전 확인 검토서 ¦ 첨부 00 기계설비 착공 전 확인 검토서 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1.현 장 명 ¦ ¦ ¦ ¦ ¦ ¦ 2.작 성 자 ¦ 회사이름 ¦ 회사이름 ¦ ¦ 작성인 ¦ ¦ 3.작성항목 ¦ 착공 전 확인표 ¦ 별표 ¦ ¦ ¦ ¦ 3.작성항목 ¦ 착공 전 확인표 ¦ 구분 ¦ ¦ ¦ ¦ 3.작성항목 ¦ 기계설비 기술기준 매뉴얼 ¦ 기계설비 기술기준 ¦ ¦ ¦ ¦ 3.작성항목 ¦ 기계설비 기술기준 매뉴얼 ¦ 착공 전 확인 판단기준 ¦ ¦ ¦ ¦ 4.작성내용 5. 첨부파일 ¦ ¦ ¦ ¦ ¦ 210mmX297mm[백상지 80g/m2] | {}
c957d35f-8433-4117-8a45-9075efa1f911 | 국내_기계설비_기술기준_매뉴얼_최종본 | 기계설비 사용 전 검사 첨부서류-검토서 작성양식 예시 ¦ 첨부 00 ¦ 기계설비 사용 전 검사 검토서 ¦ 기계설비 사용 전 검사 검토서 ¦ 기계설비 사용 전 검사 검토서 ¦ 기계설비 사용 전 검사 검토서 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1.현 장 명 ¦ ¦ ¦ ¦ ¦ ¦ 2.작 성 자 ¦ 회사이름 ¦ 회사이름 ¦ ¦ 작성인 ¦ ¦ 3.작성항목 ¦ 사용 전 확인표 ¦ 별표 ¦ ¦ ¦ ¦ 3.작성항목 ¦ 사용 전 확인표 ¦ 구분 ¦ ¦ ¦ ¦ 3.작성항목 ¦ 기계설비 기술기준 매뉴얼 ¦ 기계설비 기술기준 ¦ ¦ ¦ ¦ 3.작성항목 ¦ 기계설비 기술기준 매뉴얼 ¦ 사용 전 검사 판단기준 ¦ ¦ ¦ ¦ 4.작성내용 ¦ ¦ ¦ ¦ ¦ ¦ 4.작성내용 ¦ ¦ ¦ ¦ ¦ ¦ 5.첨부파일 ¦ ¦ ¦ ¦ ¦ ¦ 6.검 토 자 ¦ 기계설비 감리업무수행자 ¦ ¦ 현장배치 기계설비 감리인 ¦ ¦ ¦ 6.검 토 자 ¦ 검토일 ¦ ¦ 검토의 견 ¦ ¦ ¦ 6.검 토 자 ¦ 본 기계설비 사용 전 검사 검토서가 「기계설비 기술기준」 관련사항에 따라 적합하게 작성되었음을 확인함 현장배치기계설비감리인 : (인) ¦ 본 기계설비 사용 전 검사 검토서가 「기계설비 기술기준」 관련사항에 따라 적합하게 작성되었음을 확인함 현장배치기계설비감리인 : (인) ¦ 본 기계설비 사용 전 검사 검토서가 「기계설비 기술기준」 관련사항에 따라 적합하게 작성되었음을 확인함 현장배치기계설비감리인 : (인) ¦ 본 기계설비 사용 전 검사 검토서가 「기계설비 기술기준」 관련사항에 따라 적합하게 작성되었음을 확인함 현장배치기계설비감리인 : (인) ¦ 210mmX297mm[백상지 80g/m2] | {}
6e7cd8f4-ff0c-43ff-9bc6-3ecc5898eea5 | 국내_기계설비_기술기준_매뉴얼_최종본 | 기계설비 착공 전 확인 첨부서류- 작성양식 예시 첨부 00 기계설비 착공 전 확인 첨부서류 00 ¦ 1.현 장 명 ¦ ¦ ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 2.작 성 자 ¦ 회사이름 ¦ 회사이름 ¦ ¦ 작성인 ¦ ¦ ¦ 3. 작성항목 ¦ 착공 전 확인표 ¦ 착공 전 확인표 ¦ ¦ ¦ ¦ ¦ 3. 작성항목 ¦ 기계설비 기술기준 매뉴얼 ¦ 착공 전 확인 판단기준 ¦ ¦ ¦ ¦ | {}
5f722c15-cd41-4257-a4a2-1d21f55d963d | 국내_기계설비_기술기준_매뉴얼_최종본 | 기계설비 사용 전 검사 첨부서류- 작성양식 예시 첨부 00 기계설비 사용 전 검사 첨부서류 00 ¦ 1.현 장 명 ¦ ¦ ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 2.작 성 자 ¦ 회사이름 ¦ 회사이름 ¦ ¦ 작성인 ¦ ¦ ¦ 3. 작성항목 ¦ 사용 전 확인표 ¦ 사용 전 확인표 ¦ ¦ ¦ ¦ ¦ 3. 작성항목 ¦ 기계설비 기술기준 매뉴얼 ¦ 사용 전 검사 판단기준 ¦ ¦ ¦ ¦ | {}
371cfea2-feee-4b77-a3dc-2d80b1c11c39 | 국내_기계설비_기술기준_매뉴얼_최종본 | 기계설비 기술기준 매뉴얼 최 종 본 2022. 05. | {}
844c8003-7652-4907-8a7d-82d071b21b04 | KSCIEC60079-1_2024확인_KR | KSKSKSKS KS C IEC 60079-1 KSKSKSK KSKSKS KSKSK KSKS KSK K KS 폭발성 분위기 - 제 1 부: 내압방폭용기 "d"에 의한 기기 보호 KS C IEC 60079-1 :2014 산 업 표 준 심 의 회 2019 년 1 월 25 일 개정 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
e2f5b468-ed2c-40f6-84e9-38e3f18692c7 | KSCIEC60079-1_2024확인_KR | KS CIEC 60079-1:2014 심 의 : 전기응용 기술심의 회 성 명 근 무 처 직 위 (회 장) 신판석 홍익대학교 교 수 (위 원) 권오화 케이아이씨테크 대 표 김갑일 명지대학교 교 수 김재희 우리엔지니어링 대 표 박효성 한국화학융합시험연구원 연 구 위 원 박현주 한국전력공사 전력연구원 책 임 연 구 원 서호선 KR 지식재산법률사무소 대 표 이주철 (주)건일이엔지 연 구 소 장 임영민 한국전자기술연구원 수 석 연 구 원 장우진 서울과 학기술대학교 교 수 조두희 한국전자통신연구원 책 임 연 구 원 남택주 디티앤씨 고 문 (간 사) 채예린 국가기술표준원 표준정책국 전기전자정보표준과 연 구 사 원안작성협력 : 방폭전기설비 전문위원회 성 명 근 무 처 직 위 (대표전문위원) 김 두 현 충북대학교 교 수 (위 원) 김 기 회 한국가스안전공사 처 장 김 지 훈 방폭기술정보 소 장 박 동 선 한국산업안전보건공단 차 장 최 상 원 (사)과학기술연우연합회 이 사 최 용 원 한국산업기술시험원 센 터 장 강 정 일 한국산업안전보건공단 차 장 (간 사) 이 기 호 한국산업안전보건공단 차 장 표준열람 : e 나라표준인증(http://www.slandard.go.kr) 제 정 자 : 산업표준심의 회 위원장 담당부처 : 산업통상자원부 국가기술표준원 제 정 : 2001 년 10 월 8 일 개 정 : 2019 년 1 월 25 일 심 의 : 산업표준심의 회 전기응용 기술심의 회 원안작성협력 : 방폭전기설비 전문위원회 이 표준에 대한 의견 또는 질문은 e 나라표준인증 웹사이트를 이용하여 주십시오. 이 표준은 산업표준화법 제 10 조의 규정에 따라 매 5 년마다 산업표준심의 회에서 심의 되어 확인, 개정 또는 폐지됩니다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
225796d9-c5f4-41e5-8746-33676b8a4c2c | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 목 차 머 리 말 ··················································· ·········· iV 개 요 ...... V 1 적용범위(Scope) ····· 1 2 인용표준(Normative references) ··················· ····· 1 3 용어와 정의(Terms and definitions) ....... 1 4 기기보호등급(Equipment protection level, EPL) ................................... ······ 4 4.1 일반사항(General) 4 4.2 보호등급 "da"의 요구사항(Requirements for level of protection "da") 4 4.3 보호등급 "db"의 요구사항(Requirements for level of protection "db") .......... ··· 5 4.4 보호등급 "dc"의 요구사항(Requirements for level of protection "dc") ........... ····· 5 5 내압방폭 접합부(Flameproofjoints) 6 5.1 일반 요구사항(General requirements) ·················· 6 5.2 비나사 접합부(Non-threadedjoints) 7 5.3 나사 접합부(Threaded joints) 14 5.4 개스킷(O-링을 포함) (Gaskets (including O-rings)) 15 5.5 모세관을 사용하는 기기(Equipment using capillaries) ...... ····· 17 6 밀봉 접합부(Sealed joints) 17 6.1 고착 접합부(Cemented joints) 17 6.2 용융 유리 접합부(Fused glass joints) ··················· 18 7 조작축(Operation rods) ······· 18 8 샤프트 및 베어링에 대한 추가 요구사항(Supplementaryrequirements for shafts and bearings) ········ 18 8.1 샤프트의 접합부(Joints of shafts). ................ ....... 18 8.2 베어링(Bearings) - ................................ 21 9 투광성 부품(Light-transmitting parts) ....... 21 10 내압방폭용기의 일부를 형성하는 통기 및 배수 장치 (Breathing and draining devices which form part of a flameproof enclosure) 22 10.1 일반사항(General) 22 10.2 통기 또는 배수용 개구부(Openings for breathing or draining) ······ 22 10.3 재료 성분 제한(Composition limits) 22 10.4 치수(Dimensions) ・・・・・・・ 22 10.5 측정 가능한 경로를 가진 엘리먼트(Elements with measurable paths) 22 10.6 측정 불가능한 경로를 가진 엘리먼트(Elements with non-measurable paths) ···················· 22 10.7 분리형 장치(Removable devices) ·············· 23 10.8 기계적 강도(Mechanical strength) 23 10.9 방폭부품으로 사용하는 경우의 통기 장치 및 배수 장치(Breathing devices and draining devices when used as Ex components) ·············· ···· 23 11 패스너 및 개구부(Fasteners and openings) ·················· ············· 27 12 재료(Materials) ·················· 28 13 내압방폭용기의 인입부(Entries for flameproof enclosures) .... ············ 29 13.1 일반사항(General) ·················· 29 -i- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
e229a6de-fa8c-43f9-9f35-c02258b150b3 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 13.2 나사 구멍(Threaded holes) 29 13.3 비나사 구멍(그룹 1 만 해당됨)(Non-threaded holes (for Group I only)) 30 13.4 케이블 글랜드(Cable glands) 30 13.5 전선관 밀봉 장치(Conduit sealing device) 31 13.6 플러그와 소켓 및 케이블 커플러(Plugs and sockets and cable couplers) 31 13.7 부싱(Bushings) 32 13.8 블랭킹 엘리먼트(Blanking elements) 32 14 검증 및 시험(Verification and tests) ·············· 32 15 형식 시험(Type tests) 33 15.1 일반사항(General) 33 15.2 용기의 내압시험(Tests of ability of the enclosure to withstand pressure) 34 15.3 내부 점화에 의한 인화시험(Test for non-transmission of an internal ignition) 38 15.4 통기 및 배수 장치가 있는 내압방폭용기의 시험(Tests of flameproof enclosures with breathing and draining devices) 42 15.5 "dc" 장치에 대한 시험(Tests for"dc" devices) 44 16 일상시험(Routine test) 45 16.1 일반사항(General) 45 16.2 용접 구조가 없는 용기(Enclosures not incorporating a welded construction) ・・・・・・・・・・・・・ ···· 46 16.3 용접 구조가 있는 용기(Enclosures incorporating a welded construction) 46 16.4 특정 내압방폭용기에만 적용되지 않는 부싱(Bushings not specific to one flameproofenclosure) 46 16.5 적합 기준(Acceptance criteria) 47 16.6 배치시험(Batch testing) 47 17 그룹 I 용 개폐장치(Switchgear for Group 1) 47 17.1 일반사항(General) 47 17.2 분리 수단(means of isolation) 47 17.3 문 또는 덮개(Doors or covers) 48 18 램프홀더 및 램프 캡(Lampholders and lamp caps) 48 18.1 일반사항(General) .... 48 18.2 램프 이완 방지장치(Device preventing lamps working loose) 48 18.3 원통형 캡이 있는 램프의 홀더 및 캡(Holders and caps for lamps with cylindrical caps) 48 18.4 나사형 캡이 있는 램프용 홀더(Holders for lamps with threaded caps) 49 19 비금속 용기 및 용기의 비금속 부(Non-metallic enclosures and non-metallic parts of enclosures). .... 49 19.1 일반사항(General) 49 19.2 용기 내부 표면의 내트래킹성 및 연면거리(Resistance to tracking and creepage distances on internal surfaces of the enclosure walls) 49 19.3 형식 시험 요구사항(Requirements for type tests) 49 19.4 화염침식시험(Test of erosion by flame) ....... 50 20 표시(Marking) 50 20.1 일반사항(General) 50 20.2 주의 및 경고 표시(Caution and warning markings) 50 20.3 정보 표시(Informative markings) 50 21 사용설명서(Instructions) 51 부속서 A (규정) 통기 및 배수장치의 주름 리본 엘리먼트와 멀티 스크린 엘리먼트에 대한 추가 요 구사항 .... ..... 52 -ii- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
30967fec-8c03-4c27-9302-71dff7cabb8a | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 부속서 B (규정) 경로를 측정할 수 없는 통기 및 배수장치 엘리먼트에 대한 추가 요구사항 ········· 53 B.1 소결금속 엘리먼트(Sintered metal elements) 53 B.2 압축 금속와 이어 엘리먼트(Pressed metal wire elements) 53 B.3 발포금속 엘리먼트(Metal foam elements) 54 부속서 C (규정) 내압방폭 인입 장치에 대한 추가 요구사항 55 C.1 일반사항(General) 55 C.2 구조 요구사항(Constructional requirements) .... 55 C.3 형식 시험(Type tests) ········· .. 59 부속서 D (규정) 방폭부품용 빈 내압방폭용기 ........ 64 D.1 일반사항(General) 64 D.2 서언(Introductory remarks) 64 D.3 방폭부품 용기 요구사항(Ex component enclosure requirements) 64 D.4 방폭기기 인증서 준비를 위한 방폭부품 용기 인증서의 활용(Utilization of an Ex component enclosure certificate to prepare an equipment certificate) 66 부속서 E (규정) 내압방폭 "d" 용기에 사용되는 전지 및 배터리 (Cells and batteries used in flameproof "d" enclosures) 67 E.1 서언(Introductory remarks) 67 E.2 허용되는 전기화학 시스템(Acceptable electrochemical systems) 67 E.3 내압방폭용기 내부 전지(또는 배터리)에 대한 일반 요구사항 (General requirements for cells (or batteries) inside flameproof enclosures) 68 E.4 안전 장치의 배치(Arrangement of safety devices). 68 E.5 내압방폭용기 내부 2 차 전지의 재충전(Recharging of secondarycells inside flameproof enclosures) 70 E.6 보호 다이오드의 정격 및 보호 장치의 신뢰성(Rating of protection diodes and reliability of protection devices) ·························· ......................... 71 부속서 F (참고) 나사 및 너트의 기계적 특성 ...... 72 부속서 G (규정) 내부 누출원(컨테인먼트 시스템)이 있는 내압방폭용기의 추가 요구사항 ・・・・・・・・・ 73 G.1 일반사항(General) 73 G.2 누출 조건(Release conditions) 73 G.3 컨테인먼트 시스템의 설계 요구사항(Design requirements for the containment system) 74 G.4 컨테인먼트 시스템에 대한 형식 시험(Type tests for the containment system) ······· ......... 75 부속서 H (규정) 컨버터 공급 내압방폭 "d"형 회전기기에 대한 요구사항 77 H.1 일반사항(General) 77 H.2 베어링 설치 요구사항(Construction requirements for bearings) 77 H.3 온도 요구사항(Temperature requirements) 77 참고문헌 ...... 78 KS C IEC 60079-1:2014 해 설 .......... ......... 79 -iii- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
9882a681-6746-4be3-834d-d04d97bd5b27 | KSCIEC60079-1_2024확인_KR | KS CIEC 60079-1:2014 머 리 말 이 표준은 산업표준화법 관련 규정에 따라 산업표준심의 회의 심의 를 거쳐 개정한 한국산업표준이다. 이에 따라 KS C IEC 60079-1:2007(2012 년 발행)는 개정되어 이 표준으로 바뀌었다. 이 표준의 내용 일부 또는 전부는 저작권법에 따른 보호대상이 되는 저작물이 될 수 있다. 이 표준의 내용 일부 또는 전부가 ISO · IEC 등에서 제정한 표준을 참고하여 제정 또는 개정된 경우, 해당 표준의 저작권을 보유하고 있는 ISO · IEC 등의 저작권 보호 규정 등에 따라 보호되어야 한다. 이 표준의 일부가 기술적 성질을 가진 특허권, 출원공개 이후의 특허출원, 실용신안권 또는 출원공개 후의 실용신안등록출원에 저촉될 가능성이 있다는 것에 주의 를 환기한다. 관계 중앙행정기관의 장과 산업표준심의 회는 이러한 기술적 성질을 가진 특허권, 출원공개 이후의 특허출원, 실용신안권 또는 출원공개 후의 실용신안등록출원에 관계되는 확인에 대하여 책임을 지지 않는다. -iv- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
76ca8ba7-c8e0-4514-8894-c97f39cce179 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 개 요 이 표준은 2014 년 제 7 판으로 발행된 IEC 60079-1, Explosive atmospheres Part 1: Equipment protection by flameproof enclosures "d" 및 Corrigendum 1(2018)을 기초로 기술적 내용 및 대응국제표 준의 구성을 변경하지 않고 작성한 한국산업표준이다. - V - 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
9cc9fe71-a542-416f-b0fa-ad516492c3c6 | KSCIEC60079-1_2024확인_KR | 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
dded4b13-2e5e-4eff-be94-be4c71e547c2 | KSCIEC60079-1_2024확인_KR | 한국산업표준 KS C IEC 60079-1:2014 폭발성 분위기 - 제 1 부: 내압방폭용기 "d"에 의한 기기 보호 Explosive atmospheres - Part 1: Equipment protection by flameproof enclosures "d" 1 적용범위(Scope) KS C IEC 60079 의 이 부는 폭발성 가스 분위기에서 사용하는 내압방폭용기 "d" 기기의 구조 및 시험 에 관한 요구사항을 규정한다. 이 표준은 KS C IEC 60079-0 의 일반 요구사항을 보완하고 수정한다. 이 표준의 요구사항이 KS C IEC 60079-0 의 요구사항과 상충하는 경우, 이 표준의 요구사항이 우선한다. 2 인용표준(Normative references) 다음의 인용표준은 전체 또는 부분적으로 이 표준의 적용을 위해 필수적이다. 발행연도가 표기된 인 용표준은 인용된 판만을 적용한다. 발행연도가 표기되지 않은 인용표준은 최신판(모든 추록을 포함) 을 적용한다. KS C IEC 60061(모든 부), 호환성 및 안전성 제어를 위한 게이지 및 램프 캡과 소켓 KS C IEC 60079-0, 폭발성 분위기 - 제 0 부: 기기 - 일반 요구사항 KS C IEC 60079-7, 폭발성 분위기 - 제 7 부: 안전증 방폭구조 "e" KS C IEC 60079-11, 폭발성 분위기 - 제 11 부: 본질 안전 방폭 구조 "i" KS C IEC 60079-15, 폭발성 분위기 - 제 15 부: 비점화 방폭 구조 "n" IEC 60127(all parts), Miniature fuses ISO 965-1, ISO general-purpose metric screw threads - Tolerances - Part 1: Principles and basic data ISO 965-3, ISO general-purpose metric screw threads - Tolerances - Part 3: Deviations for constructional screw threads ISO 2738, Sintered metal materials, excluding hardmetals - Permeable sintered metal materials Determination of density, oil content and open porosity ISO 4003, Permeable sintered metal materials - Determination of bubble test pore size ISO 4022, Permeable sintered metal materials - Determination of fluid permeability ANSI/ASME B1.20.1, Pipe threads, general purpose(inch)[관용나사, 일반 용도(인치)] 3 용어와 정의(Terms and definitions) 이 표준의 목적을 위하여 KS C IEC 600079-0 에 규정된 용어와 정의 및 다음을 적용한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 1 | {}
5f402cc2-4963-4d8a-8152-e8fd146a47e3 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 비고 폭발성 분위기에 적용되는 그 밖의 정의 는 IEC 60050-426[1]1)에서 확인할 수 있다. 3.1 내압방폭용기 "d"(flameproof enclosure "d") 폭발성 가스 분위기를 점화시킬 수 있는 부품이 들어 있는 용기로 내부 폭발로 발생하는 압력을 견 디며, 용기 주변의 폭발성 가스 분위기로 폭발의 전파를 방지할 수 있는 용기 3.2 체적(volume) 용기 내부의 전체 체적 비고 1 작동을 위해 필수적인 내용물이 있는 용기의 경우, 고려할 체적은 나머지 빈 공간만 해당된다. 비고 2 조명 기기의 경우, 체적은 램프가 설치되지 않은 상태로 결정한다. 3.3 내압방폭 접합부 또는 화염경로(flameproof joint or flamepath) 용기에서 두 면이 서로 접하는 또는 용기가 결합되는 부분으로, 용기 내부에서 폭발이 용기 주위를 둘러싼 폭발성 가스 분위기로 화염이 전파되지 않도록 방지하는 부분 3.4 내압방폭 접합부의 길이(width of flameproof joint) L 용기의 내부에서 외부까지 내압방폭 접합부를 통과 하는 최단 경로 비고 이 정의 는 나사 접합부에는 적용하지 않는다. 3.5 거리(distance) 1 내압방폭용기를 조립하기 위한 패스너(fastener)를 넣는 구멍으로 인해 내압방폭 접합부의 길이(L)가 중단되는 경우, 내압방폭 접합부를 통하는 최단 경로 3.6 내압방폭 접합부의 틈새(gap of flameproof joint) i 전기기기의 용기가 조립되었을 때 내압방폭 접합부 해당 표면 사이의 거리 비고 원통 접합부를 형성하는 원통형 표면의 경우, 틈새는 구멍과 원통형 부품 지름 사이의 차이이다. 3.7 최대실험안전틈새[maximum experimental safe gap(for an explosive mixture)] MESG IEC 60079-20-1[2]에서 명시한 조건에 따라 시험을 10 회 실시하는 동안 화염전파가 발생하지 않는 길 이가 25 mm 인 접합부의 최대 틈새 3.8 샤프트(shaft) 회전 운동의 전달을 위해 사용되는 원형 단면을 가진 부품 1) 대괄호 안의 내용은 참조문헌을 참조한다. 2 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
99da8a2c-6e07-4dd5-a96f-4ecda0939c3d | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 3.9 조작축(operating rod) 회전 또는 직선 또는 이 둘이 조합된 형태의 제어된 움직임을 전달하기 위해 사용되는 부품 3.10 압력중첩(pressure-piling) 용기의 구획 또는 분할된 공간에서, 예를 들어 다른 구획 또는 분할 공간의 1 차 점화에 의한, 예압된 가스 혼합물의 점화 결과 3.11 단순조작 문 또는 덮개(quick-acting door or cover) 레버를 움직이거나 휠(wheel)을 회전하는 등의 단순조작으로 개폐 가능한 장치가 있는 문 또는 덮개 비고 이러한 장치는 두 단계로 작동하도록 배열한다. · 잠금 또는 잠금 해제를 위한 단계 · 열림 또는 닫힘을 위한 단계 3.12 나사형 패스너로 고정되는 문 또는 덮개(door or cover fixed by threaded fasteners) 열거나 닫기 위해 한 개 이상의 나사형 패스너(나사, 스터드 볼트 또는 너트)의 조작이 필요한 문 또 는 덮개 3.13 나사형 문 또는 덮개(threaded door or cover) 나사 내압방폭접합부에 의해 내압방폭용기에 조립되는 문 또는 덮개 3.14 통기장치(breathing devie) 방폭구조를 유지하면서 용기 주변 분위기와 용기 내부 분위기의 순환을 가능하게 하는 장치 3.15 배수장치(draining device) 방폭구조를 유지하면서 용기 내부의 액체를 외부로 내보낼 수 있도록 하는 장치 3.16 방폭기기 블랭킹 엘리먼트(Ex equipment blanking element) 그룹 I 또는 그룹 II 에서 사용되는 나사형 블랭킹 엘리먼트 및 그룹 I 에서 사용되는 비나사형 블랭킹 엘리먼트로서 다음과 같다. 사용하지 않은 인입부를 막는 목적이고 용기와 개별적으로 시험되며 기기 인증서를 가지며 추가 검토 없이 용기에 장착 가능 비고 1 이는 KS C IEC 60079-0 에 따른 방폭부품 블랭킹 엘리먼트에 대한 부품인증을 배제하는 것은 아니다. 블랭킹 엘리먼트에 대한 예시는 그림 C.1 참조 비고 2 비나사형 블랭킹 엘리먼트는 그룹 II 기기에 적용하지 않는다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 3 | {}
c5fab197-6d39-4383-8fc5-05f63b3d809b | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 3.17 방폭기기 나사 어댑터(Ex equipment thread adapter) 용기로부터 분리하여 시험되었으나 기기 인증서를 가지며 추가 검토 없이 용기에 설치할 수 있는 나 사 어댑터 비고 이는 KS C IEC 60079-0 에 따른 방폭부품 나사 어댑터에 대한 부품인증을 배제하는 것은 아니 다. 나사 어댑터에 대한 예시는 그림 C.3 참조 3.18 방폭부품 용기(Ex cpmponent enclosure) 내부의 부품을 지정하지 않고 방폭부품 인증서가 있는 빈 내압방폭용기로서 해당 형식 시험을 반복 하지 않고 기기 인증서에 통합할 수 있다. 4 기기보호등급(Equipment protection level, EPL) 4.1 일반사항(General) 내압방폭용기 'd'의 전기기기는 다음 중 하나에 해당해야 한다. 보호등급 "da"(EPL "Ma" 또는 "Ga") 보호등급 "db"(EPL "Mb" 또는 "Gb") 보호등급 "dc"(EPL "Gc") 이 표준의 요구사항은, 달리 언급하지 않은 한 모든 보호등급(level of protection)에 적용해야 한다. 4.2 보호등급 "da"의 요구사항(Requirements for level of protection "da") 보호등급 "da"는 휴대용 인화성 가스 감지기의 촉매 센서에만 적용 가능하다. 다음의 사항은 보호등급 "da"의 추가적인 특정 요구사항으로 이 표준의 요구사항을 수정 또는 보충 한다. 내부 빈 공간의 체적(free internal volume)은 5cm3 을 초과 해서는 안 된다. 센서로 들어가는 전기적 도체에는 6 절에 따라 용기 벽체에 직접적으로 밀봉 접합(sealed joint)을 적용해야 한다. 센서의 통기장치는 10 절에 적합해야 하며, 용기의 벽면에 접합되어(6.1 에 따른 고착 접합 또는 소 결 접합 등) 틈새가 없도록 하거나 추가적인 기계적 고정 수단(스웨이징 등)을 사용하여 용기의 벽면에 압입해야 한다. 최대 소비 전력이 그룹 I 에 대해서 3.3 W, 그룹 II 에 대해서는 1.3 W 로 제한되는 보호등급 "ia"의 회로로부터 전력이 공급되어야 하고 비고 촉매 소자는 보통 높은 온도에서 작동한다. 전력 소모가 증가하여 정상 작동 수준을 초과 하 면 해당 소자가 개방회로가 된다. 따라서 요구되는 전력의 제한은 외부 표면온도의 제한을 제공한다. 15.3 또는 15.4.4(해당하는 경우)에 따른 인화시험은 표 1 에 따라 그 시험 횟수를 증가시킨다. 4 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
be1bd59f-06dd-44ad-8577-3a3db34b9053 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 표 1 - 보호등급 "da"의 인화시험 횟수 ¦ 기기 그룹 ¦ 인화시험 횟수 ¦ ¦ --- ¦ --- ¦ ¦ I ¦ 50 회 ¦ ¦ IIA ¦ 50 회 ¦ ¦ IIB ¦ 50 회 ¦ ¦ IIC ¦ 수소 50 회, 아세틸렌 50 회 ¦ 4.3 보호등급 "db"의 요구사항(Requirements for level of protection "db") 보호등급 "da" 및 "dc"에 대한 특정한 요구사항을 제외하고, 이 표준의 모든 기타 요구사항들을 보호 등급 "db"에 적용한다. 4.4 보호등급 "dc"의 요구사항(Requirements for level of protection "dc") 4.4.1 일반사항(General) 보호등급 "dc"에 대한 요구사항은 전기 스위치 접점이 있는 전기기기 및 방폭부품에 적용할 수 있으 며 4.4.2 ~ 4.4.3 에 나와 있다. 4.4.2 "dc" 장치의 구조(Construction of "dc" devices) 4.4.2.1 일반사항(General) 4.4.2.2 에서 4.4.2.5 까지의 요구사항은 5 절에서 13 절까지의 요구사항을 대체한다. 현장 배선에 연결하 기 위한 보호등급 "dc"의 기기에 대해서는 13 절을 적용한다. 4.4.2.2 내부 빈 공간의 체적(Free internal volume) 내부 빈 공간의 체적은 20 cm3 을 초과 해서는 안 된다. 4.4.2.3 밀봉 보호(Seal protection) 기기의 외부 용기로 사용되지 않는 보호등급 "dc"의 용기는 밀봉(seals)의 손상 없이 정상적인 취급 및 조립 작업을 견딜 수 있어야 한다. 보호등급 "dc"의 용기가 기기의 외부 용기로도 사용되는 경우, KS C IEC 60079-0 의 용기에 대한 요구사항을 적용한다. 4.4.2.4 연속사용온도 요구사항(Continuous operating temperature (COT) requirements) 주입형 밀봉재 및 몰딩(encapsulating) 컴파운드는 최저 사용온도보다 같거나 낮고 최고 사용온도보 다 적어도 10K 이상 높은 연속사용온도(COT)의 범위를 가져야 한다. 4.4.2.5 정격(Ratings) 장치는 최대 정격을 교류 또는 직류 690 V 및 16 A 로 제한한다. 4.4.3 "dc" 장치의 시험(Tests for "dc" devices) 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 5 | {}
411ad2d5-3a80-49c8-80ba-0faf1239944a | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 보호등급 "dc"를 포함한 장치의 경우, 부품들은 15.5 에서 규정하는 형식 시험을 받아야 한다. 시험 이 후, 장치나 부품에는 육안으로 보이는 손상의 흔적이 없어야 하며, 외부 점화가 일어나서는 안 되고 스위치 접점이 열린 상태에서 아크의 발생이 남아 있어서는 안 된다. 5 내압방폭 접합부(Flameproof joints) 5.1 일반 요구사항(General requirements) 영구적으로 닫혀 있거나 때때로 개방되도록 설계된 모든 내압방폭 접합부는 압력이 없는 상태에서 5 절의 해당 요구사항을 만족해야 한다. 접합부의 설계는 접합부에 적용되는 기계적 제약 조건에 적합해야 한다. 5.2 부터 5.5 까지 제시된 치수들은 화염경로(flamepath)의 필수 파라미터를 명시하고 있으며, 아래 열 거한 사항을 적용할 때 반영한다(예: 기기 내부 점화에 의한 인화시험을 만족시키기 위해). 문서에 명시된 내압방폭 접합부의 최소 길이가 관련 최소값보다 크거나 - 문서에 명시된 내압방폭 접합부의 최대 틈새가 관련 최대값보다 작거나 문서에 명시된 내압방폭 접합부의 결합된 나사산의 수가 관련 최소값 이상이어야 한다. 비고 1 KS C IEC 60079-0 에서 정의 하는 문서란 전기기기의 폭발 안전 측면에서 완전하고 정확한 사 양을 제공하는 문서로 정의 한다. 기기의 인증번호는 KS C IEC 60079-0 의 표시 요구사항에 따라 접미사 "X"를 포함하여야 하며 인증서 와 사용설명서에 기재되는 특정사용조건(specific condition of use)에는 다음 중 하나를 상세히 설명하 여야 한다. 내압방폭 접합부의 치수를 상세히 기재, 또는 내압방폭 접합부의 치수가 상세히 기재된 특정 도면, 또는 내압방폭 접합부의 치수에 관한 정보는 원 제조자에게 문의 하도록 명시된 특정 지침, 또는 내압방폭 접합부가 수리 대상이 아니라는 특정 표시 비고 2 KS C IEC 60079-0 은 "X" 표시에 대한 대안으로 기기에 대한 권고표시(advisory marking)를 허 용한다. 접합부 표면은 부식으로부터 보호될 수 있다. 페인트 도장 또는 분체 코팅 마감은 허용되지 않는다. 만약 재료 및 적용 방법이 접합부의 방폭 성 능에 악영향을 주지 않음이 입증된다면 다른 코팅 재료를 사용할 수 있다. 반고체 왁스 또는 미네랄 오일 등과 같은 부식방지 그리스는 조립 전 접합부 표면에 사용될 수 있다. 이러한 그리스는 시간이 경과 함에 따라 경화되지 않아야 하며 휘발성 용제를 함유하지 않고, 접합부 표면에 부식을 유발하지 않는 종류를 사용해야 한다. 적합성의 검증은 그리스 제조사의 사양서에 따 라야 한다. 접합부 표면에는 전기 도금을 할 수 있다. 금속 도금을 할 경우, 다음 사항을 따라야 한다. 두께가 0.008 mm 이하인 경우, 추가 검토가 필요하지 않다. - 두께가 0.008 mm 를 초과 하는 경우, 도금층이 없는 최대 틈새가 접합부 요구사항에 부합해야 하며 6 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
4c01446a-2b88-4fa0-ae28-31b02d273f93 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 도금층 없이 존재할 수 있는 틈새 치수를 기준으로 인화시험을 실시해야 한다. 5.2 비나사 접합부(Non-threaded joints) 5.2.1 접합부의 길이(Width of joints, L) 접합부의 길이는 표 2 및 표 3 에 주어진 최소값 이상이어야 한다. 체적이 2 000 cm3 을 넘지 않는 금속제 내압방폭용기에 압입(press-fitted)되는 원통형 금속 부품의 접 합부 길이는, 다음 사항을 만족하는 경우, 5 mm 까지 줄일 수 있다. a) 15 절에 따른 형식시험 중 이탈 방지를 위해 억지끼워맞춤에만 의존하지 않게 설계하고 b) 가장 헐거운 억지끼워맞춤을 고려한 상태로 조립부는 KS C IEC 60079-0 에 따른 충격시험 요구사 항에 만족하며 c) 접합부의 길이가 측정되는 압입 부의 바깥지름은 60 mm 를 초과 하지 않아야 한다. 비고 금속제 내압방폭용기에 비금속제 부품을 압입하는 것을 금지하지는 않는다. 이러한 다른 조합 의 경우에는 표 2 또는 표 3 의 최소 접합부 길이 요건을 적용한다. 5.2.2 틈새(Gap, i) 접합부 표면 사이에 틈새가 존재한다면 이 틈새는 표 2 와 표 3 에 주어진 최대값을 초과 하지 않아야 한다. 접합부 표면은 그 평균거칠기 Ra 가 6.3 �m 를 초과 하지 않아야 한다. 비고 평균거칠기는 ISO 468 을 기반으로 한다. 측정은 시각적으로 표준시편과 비교하여 이루어질 수 있다. 단순조작 문 또는 덮개(quick-acting doors or covers) 이외의 플랜지 접합부의 경우, 상대 부품의 평면 도 공차(flatness tolerances)에 의해 생성된 것 이외의 접합면 사이에 의도적인 틈새는 없어야 한다. 그룹 I 의 전기기기의 경우, 수시로 개방될 수 있도록 설계된 문 또는 덮개의 플랜지 접합부의 틈새를 직접 또는 간접적으로 점검할 수 있어야 한다. 그림 1 은 내압방폭 접합부의 간접 점검을 위한 구조 의 예시를 보인다. X-Axis: 평면에 있을 것 Chart Type: bar 덮개 접합면 너비 덮개의 표면과 못은 같은 내압방폭 용기 8L 3L 1L 구멍에 삽입된 원통형 1L 1L 1L 자리츔 못 1L 1L 1L 그림 1 - 그룹 I 내압방폭 접합면을 간접적으로 점검하기 위한 구조 예시 7 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
a8b9fd88-f341-45c9-a3a0-7fe1162ae0dd | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 5.2.3 마개 접합부(Spigot joints) 마개 접합에서 접합부의 길이를 결정할 때는 다음 중 하나를 고려해야 한다. 원통 부와 평면 부(그림 2a 참조). 이 경우, 틈새는 표 2 및 표 3 에 주어진 최대값을 초과 하지 않 아야 한다. 원통 부(그림 2b 참조)만 있는 경우, 평면 부는 표 2 및 표 3 의 요구사항에 적합하지 않아도 된다. 비고 개스킷이 있는 경우, 5.4 를 참조한다. ![image](/image/placeholder) 그림 2a - 원통부 및 평면부가 있는 경우 ![image](/image/placeholder) 그림 2b - 원통부만 있는 경우 식별부호 L=c +d(l, IIA, IIB, IIC) c ≥ 6.0 mm (IIC) ≥ 3.0 mm (I, IIA, IIB) d ≥ 0.50 L (IIC) f ≤ 1.0 mm (I, IIA, IIB, IIC) 1 용기 내부 그림 2 - 마개 접합부 5.2.4 접합면의 구멍(Holes in joint surfaces) 5.2.4.1 일반사항(General) 평면 접합이나 접합의 평면부분 또는 부분적 원통부 표면(5.2.6 참조)이 내압방폭용기의 부품을 조립 하기 위한 나사 패스너의 통과 를 위한 구멍에 간섭을 받는 경우, 구멍의 가장자리까지 거리 l 은 다음 과 같거나 더 커야 한다. a) 6 mm, 접합부 길이 L 이 12.5 mm 미만인 경우 b) 8 mm, 접합부 길이 L 이 12.5 mm 이상 25 mm 미만인 경우 c) 9 mm, 접합부 길이 L 이 25 mm 이상인 경우 비고 패스너의 간극 구멍(clearance holes)에 대한 요구사항은 KS C IEC 60079-0 에서 명시되어 있다. 거리 1 은 다음과 같이 결정한다. 8 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
a7535056-3396-4cd6-8585-e840fafa6d0f | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 5.2.4.2 용기 외부에 구멍이 있는 플랜지 접합부(그림 3 및 그림 5 참조) 거리 l 은 용기 내부에서 각 구멍까지의 거리로 측정한다. 5.2.4.3 용기 내부에 구멍이 있는 플랜지 접합부(그림 4 참조) 거리 l 은 용기 외부에서 각 구멍까지의 거리로 측정한다. 5.2.4.4 구멍의 가장자리까지 원통부와 평면부를 가진 마개 접합(그림 6 참조) 거리 l 은 다음과 같이 정한다. f 가 1 mm 이하이고 원통부의 틈새가 기기그룹 I 및 기기그룹 IIA 에서 0.2 mm 이하, 기기그룹 IIB 에서 0.15 mm, 기기그룹 IIC(감소된 틈새)에서 0.1 mm 이하인 경우, 원통부 길이 a 와 평면부 길이 b 의 합 위의 조건 중 하나가 충족되지 않은 경우, 평면부 길이 b 만 단독으로 적용 ![image](/image/placeholder) 용기내부 L ![image](/image/placeholder) 용기내부 L 그림 3- 플랜지 접합면의 구멍, 예시 1 그림 4- 플랜지 접합면의 구멍, 예시 2 ![image](/image/placeholder) 용기내부 L 그림 5- 플랜지 접합면의 구멍, 예시 3 ![image](/image/placeholder) b 용기내부 a i ≤ 0.20 mm(I, IIA) i ≤ 0.15 mm(IIB) i ≤ 0.10 mm(IIC) 그림 6- 마개 접합면의 구멍, 예시 1 9 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b58ff8e2-82ea-4f39-a8c9-1fe37bc807af | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 ![image](/image/placeholder) 용기내부 그림 7 - 마개 접합면의 구멍, 예시 2 ![image](/image/placeholder) L 용기내부 그림 8 - 마개 접합면의 구멍, 예시 3 5.2.4.5 평면 접합부가 허용되는 경우(5.2.7 참조), 구멍의 가장자리까지 평면부로만 구성(그림 7 과 그 림 8 참조)된 마개 접합 거리 l 은 구멍이 용기의 바깥에 위치한 경우(그림 7 참조) 용기 내부에서 구멍 사이의 평면부의 길이 에 해당하며, 또는 구멍이 용기의 안쪽에 위치한 경우(그림 8 참조) 구멍에서 용기의 외부까지 평면 부의 길이에 해당한다. 5.2.5 원뿔 접합부(Conical joints) 접합부가 원뿔면을 포함하는 경우, 접합부의 길이 및 접합부 표면에 수직한 틈새는 표 2 및 표 3 의 관련 값을 준수해야 한다. 틈새는 원뿔 부분 전체에 걸쳐 균일하여야 한다. 그룹 IIC 전기기기의 경 우, 원뿔 각도는 5°를 초과 하지 않아야 한다. 비고 원뿔의 각도는 원뿔의 주축과 원뿔 표면 사이의 각을 말한다. 5.2.6 부분적으로 원통 면이 있는 접합부(그룹 IIC 에서는 허용되지 않음) (Joints with partial cylindrical surfaces (not permitted for Group IIC)) 부분적으로 원통 면을 구성하는 두 부분 사이에는 의도적인 틈새가 없어야 한다(그림 9a 참조). 접합부의 길이는 표 2 의 요구사항을 준수하여야 한다. 내압방폭 접합부를 형성하는 두 부분의 원통 면의 지름 및 허용 오차는 표 2 에서 주어진 원통 접합 부의 틈새 관련 요구사항을 준수해야 한다. 10 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
e5fbc3ec-bae3-4337-b666-297e1759b7f8 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 ![image](/image/placeholder) 그림 9a - 부분적으로 원통 면이 있는 접합부의 예 T Y≥5T Y 시험 길이 = 1.5 Y T≥ 1.25 mm a = 60°(±5°) 그림 9b - 톱니 접합의 예 그림 9 - 접합부 구조의 예 5.2.7 아세틸렌 분위기에서 플랜지 접합부(Flanged joints for acetylene atmospheres) 아세틸렌을 함유하는 폭발 가스 분위기에서 사용하는 그룹 IIC 전기기기에서의 플랜지 접합부는 다 음 조건을 모두 만족할 때만 허용한다. 틈새 i≤ 0.04 mm 길이 L ≥ 9.5 mm 체적 ≤500 cm3 5.2.8 톱니 접합부(Serrated joints) 톱니 접합부는 표 2 및 표 3 의 요구사항을 준수할 필요는 없지만 다음을 만족해야 한다. 최소 5 개 이상 완전 체결된 톱니 피치가 1.25 mm 이상 체결각도는 60°(±5°) 11 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
46f70eee-31f9-49de-87c2-ac2f3da54660 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 톱니 접합은 작동 중에 고정된 접합부에만 사용하여야 한다. 톱니 접합부는 a) 제조자의 최대 구조 틈새(ic)를 기준으로 15.3 에 명시된 것과 같이 결합 톱니 사이 의 시험 틈새(iE) 및 b) 감소된 시험 길이(Y/1.5)로 하여 15.3 의 시험 요구사항을 만족하여야 한다. 제조자의 최대 구조 틈새가 동일한 길이(피치와 톱니 개수의 곱으로 결정되는)의 플랜지 접합부에 대 한 표 2 또는 표 3 의 값과 다른 경우, 5.1 의 "사용 조건"의 요구사항을 적용한다. 그림 9b 를 참조 5.2.9 다단 접합부(Multi-step joints) 다단 접합은 경로의 방향이 90° 土 5°로 2 회 이상 변하고 3 개 이상의 인접한 세그먼트(segments)로 구성하여야 한다. 다단 접합은 표 2 또는 표 3 의 요구사항을 준수할 필요는 없지만 각 세그먼트의 시험 길이를 제조자 가 명시한 설계 최소 길이의 75% 이하로 줄인 상태로 15.3 의 시험 요구사항을 만족하여야 한다. 다단 접합이 있는 내압방폭용기의 경우, 기기의 인증번호는 KS C IEC 60079-0 의 표기 요구사항에 따 라 "X" 접미사를 포함하여야 하며 인증서 상의 특정사용조건에는 다음 중 하나가 상세히 설명되어야 한다. 내압방폭 접합부의 치수를 상세히 기재, 또는 내압방폭 접합부의 치수를 상술한 특정 도면, 또는 내압방폭 접합부의 치수에 관한 정보는 원 제조업체에 문의 하도록 명시된 특정 지침, 또는 내압방폭 접합부가 수리 대상이 아니라는 특정 표시 비고 1 KS C IEC 60079-0 는 "X" 표시의 대안으로 기기상에 권고표시(advisory marking) 사용을 허용 한다. 비고 2 다단 접합은 이 표준에서 설명하는 회전축 래버린스 접합과 구별된다(8.1.3 참조). 12 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
b0ccbba6-062a-4e07-bf47-4d4ccb939f19 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 표 2- 그룹 1, IIA, IIB 용기에 대한 접합부의 최소 길이 및 최대 틈새 ¦ 접합 종류 ¦ 접합 종류 ¦ 접합부 최소 길이 L mm ¦ 최대 틈새 mm ¦ 최대 틈새 mm ¦ 최대 틈새 mm ¦ 최대 틈새 mm ¦ 최대 틈새 mm ¦ 최대 틈새 mm ¦ 최대 틈새 mm ¦ 최대 틈새 mm ¦ 최대 틈새 mm ¦ 최대 틈새 mm ¦ 최대 틈새 mm ¦ 최대 틈새 mm ¦ 최대 틈새 mm ¦ 최대 틈새 mm ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 접합 종류 ¦ 접합 종류 ¦ 접합부 최소 길이 L mm ¦ 체적 cm3 Vs 100 ¦ 체적 cm3 Vs 100 ¦ 체적 cm3 Vs 100 ¦ 체적 cm3 100 < Vs 500 ¦ 체적 cm3 100 < Vs 500 ¦ 체적 cm3 100 < Vs 500 ¦ 체적 cm3 500 < V ≤2 000 ¦ 체적 cm3 500 < V ≤2 000 ¦ 체적 cm3 500 < V ≤2 000 ¦ 체적 cm3 2000< V≤5750 ¦ 체적 cm3 2000< V≤5750 ¦ 체적 cm3 2000< V≤5750 ¦ 체적 cm3 V > 5 750 ¦ 체적 cm3 V > 5 750 ¦ 체적 cm3 V > 5 750 ¦ ¦ 접합 종류 ¦ 접합 종류 ¦ 접합부 최소 길이 L mm ¦ I ¦ IIA ¦ IIB ¦ I ¦ IIA ¦ IIB ¦ I IIA ¦ IIB ¦ ¦ I ¦ IIA IIB ¦ ¦ I ¦ IIA ¦ IIB ¦ ¦ 플랜지, 원통 또는 마개 접합 ¦ 플랜지, 원통 또는 마개 접합 ¦ 6 ¦ 0.30 0.30 0.20 ¦ 0.30 0.30 0.20 ¦ 0.30 0.30 0.20 ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ ¦ 플랜지, 원통 또는 마개 접합 ¦ 플랜지, 원통 또는 마개 접합 ¦ 9.5 ¦ 0.35 0.30 0.20 ¦ 0.35 0.30 0.20 ¦ 0.35 0.30 0.20 ¦ 0.35 0.30 0.20 ¦ 0.35 0.30 0.20 ¦ 0.35 0.30 0.20 ¦ 0.08 0.08 0.08 ¦ 0.08 0.08 0.08 ¦ 0.08 0.08 0.08 ¦ - 0.08 0.08 ¦ - 0.08 0.08 ¦ - 0.08 0.08 ¦ - 0.08 - ¦ - 0.08 - ¦ - 0.08 - ¦ ¦ 플랜지, 원통 또는 마개 접합 ¦ 플랜지, 원통 또는 마개 접합 ¦ 12.5 ¦ 0.40 0.30 0.20 ¦ 0.40 0.30 0.20 ¦ 0.40 0.30 0.20 ¦ 0.40 0.30 0.20 ¦ 0.40 0.30 0.20 ¦ 0.40 0.30 0.20 ¦ 0.40 0.30 0.20 ¦ 0.40 0.30 0.20 ¦ 0.40 0.30 0.20 ¦ 0.40 0.20 0.15 ¦ 0.40 0.20 0.15 ¦ 0.40 0.20 0.15 ¦ 0.40 0.20 0.15 ¦ 0.40 0.20 0.15 ¦ 0.40 0.20 0.15 ¦ ¦ 플랜지, 원통 또는 마개 접합 ¦ 플랜지, 원통 또는 마개 접합 ¦ 25 ¦ 0.50 0.40 0.20 ¦ 0.50 0.40 0.20 ¦ 0.50 0.40 0.20 ¦ 0.50 0.40 0.20 ¦ 0.50 0.40 0.20 ¦ 0.50 0.40 0.20 ¦ 0.50 0.40 0.20 ¦ 0.50 0.40 0.20 ¦ 0.50 0.40 0.20 ¦ 0.50 0.40 0.20 ¦ 0.50 0.40 0.20 ¦ 0.50 0.40 0.20 ¦ 0.50 0.40 0.20 ¦ 0.50 0.40 0.20 ¦ 0.50 0.40 0.20 ¦ ¦ 회전 전기기기의 축 글랜드의 원통 접합 ¦ 슬리브 베어링 ¦ 6 ¦ 0.30 0.30 0.20 ¦ 0.30 0.30 0.20 ¦ 0.30 0.30 0.20 ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ ¦ ¦ 회전 전기기기의 축 글랜드의 원통 접합 ¦ 슬리브 베어링 ¦ 9.5 ¦ 0.35 0.30 0.20 ¦ 0.35 0.30 0.20 ¦ 0.35 0.30 0.20 ¦ 0.35 0.30 0.20 ¦ 0.35 0.30 0.20 ¦ 0.35 0.30 0.20 ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ ¦ 회전 전기기기의 축 글랜드의 원통 접합 ¦ 슬리브 베어링 ¦ 12.5 ¦ 0.40 0.35 0.25 ¦ 0.40 0.35 0.25 ¦ 0.40 0.35 0.25 ¦ 0.40 0.30 0.20 ¦ 0.40 0.30 0.20 ¦ 0.40 0.30 0.20 ¦ 0.40 0.30 0.20 ¦ 0.40 0.30 0.20 ¦ 0.40 0.30 0.20 ¦ 0.40 0.20 - ¦ 0.40 0.20 - ¦ 0.40 0.20 - ¦ 0.40 0.20 - ¦ 0.40 0.20 - ¦ ¦ ¦ 회전 전기기기의 축 글랜드의 원통 접합 ¦ 슬리브 베어링 ¦ 25 ¦ 0.50 0.40 0.30 ¦ 0.50 0.40 0.30 ¦ 0.50 0.40 0.30 ¦ 0.50 0.40 0.25 ¦ 0.50 0.40 0.25 ¦ 0.50 0.40 0.25 ¦ 0.50 0.40 0.25 ¦ 0.50 0.40 0.25 ¦ 0.50 0.40 0.25 ¦ 0.50 0.40 0.20 ¦ 0.50 0.40 0.20 ¦ 0.50 0.40 0.20 ¦ 0.50 0.40 0.20 ¦ 0.50 0.40 0.20 ¦ ¦ ¦ 회전 전기기기의 축 글랜드의 원통 접합 ¦ 슬리브 베어링 ¦ 40 ¦ 0.60 0.50 0.40 ¦ 0.60 0.50 0.40 ¦ 0.60 0.50 0.40 ¦ 0.60 0.50 0.30 ¦ 0.60 0.50 0.30 ¦ 0.60 0.50 0.30 ¦ 0.60 0.50 0.30 ¦ 0.60 0.50 0.30 ¦ 0.60 0.50 0.30 ¦ 0.60 0.50 0.25 ¦ 0.60 0.50 0.25 ¦ 0.60 0.50 0.25 ¦ 0.60 0.50 0.25 ¦ 0.60 0.50 0.25 ¦ ¦ ¦ 회전 전기기기의 축 글랜드의 원통 접합 ¦ 구름 베어링 ¦ 6 ¦ 0.45 0.45 0.30 ¦ 0.45 0.45 0.30 ¦ 0.45 0.45 0.30 ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ ¦ ¦ ¦ 회전 전기기기의 축 글랜드의 원통 접합 ¦ 구름 베어링 ¦ 9.5 ¦ 0.50 0.45 0.35 ¦ 0.50 0.45 0.35 ¦ 0.50 0.45 0.35 ¦ 0.50 0.40 0.25 ¦ 0.50 0.40 0.25 ¦ 0.50 0.40 0.25 ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ - - - ¦ ¦ ¦ 회전 전기기기의 축 글랜드의 원통 접합 ¦ 구름 베어링 ¦ 12.5 ¦ 0.60 0.50 0.40 ¦ 0.60 0.50 0.40 ¦ 0.60 0.50 0.40 ¦ 0.60 0.45 0.30 ¦ 0.60 0.45 0.30 ¦ 0.60 0.45 0.30 ¦ 0.60 0.45 0.30 ¦ 0.60 0.45 0.30 ¦ 0.60 0.45 0.30 ¦ 0.60 0.30 0.20 ¦ 0.60 0.30 0.20 ¦ 0.60 0.30 0.20 ¦ 0.60 0.30 0.20 ¦ 0.60 0.30 0.20 ¦ ¦ ¦ 회전 전기기기의 축 글랜드의 원통 접합 ¦ 구름 베어링 ¦ 25 ¦ 0.75 0.60 0.45 ¦ 0.75 0.60 0.45 ¦ 0.75 0.60 0.45 ¦ 0.75 0.60 0.40 ¦ 0.75 0.60 0.40 ¦ 0.75 0.60 0.40 ¦ 0.75 0.60 0.40 ¦ 0.75 0.60 0.40 ¦ 0.75 0.60 0.40 ¦ 0.75 0.60 0.30 ¦ 0.75 0.60 0.30 ¦ 0.75 0.60 0.30 ¦ 0.75 0.60 0.30 ¦ 0.75 0.60 0.30 ¦ ¦ ¦ 회전 전기기기의 축 글랜드의 원통 접합 ¦ 구름 베어링 ¦ 40 ¦ 0.80 0.75 0.60 ¦ 0.80 0.75 0.60 ¦ 0.80 0.75 0.60 ¦ 0.80 0.75 0.45 ¦ 0.80 0.75 0.45 ¦ 0.80 0.75 0.45 ¦ 0.80 0.75 0.45 ¦ 0.80 0.75 0.45 ¦ 0.80 0.75 0.45 ¦ 0.80 0.75 0.40 ¦ 0.80 0.75 0.40 ¦ 0.80 0.75 0.40 ¦ 0.80 0.75 0.40 ¦ 0.80 0.75 0.40 ¦ ¦ 최대 틈새를 정할 때는 KS A ISO 80000-1[3]에 따라 반올림한 구조상의 값을 고려해야 한다. 비고 이 KS C IEC 60079-1 개정판의 경우, 기존 표 2 의 "V>2 000"에서 "2 000 < Vs 5 750"과 "V > 5 750" 등 세로 열 2 개가 추가되었다. 이 세부 구분은 기존에는 존재하지 않았던 접합면 최소 길이 L 9.5 mm 에서 플랜지, 원통 또는 마개 접합의 최소 틈새 치수를 도입하기 위한 것 이다. 구체적으로, 내용적이 "2 000 < V≤5 750"에서 그룹 IIA 와 그룹 IIB 에는 "0.08"값을, 그리 고 체적이 "V> 5 750"에서 그룹 IIA 에는 "0.08"을 도입했다. 이러한 최대 틈새 값과 관련된 체 적 세부 구분은 ANSI/UL 1203[4]에 기재되어 있는 미국 Class 1, Division 1 내압방폭 틈새를 기 반으로 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. 13 | {}
4543166f-f01c-4766-a93b-62b02671fa7a | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 표 3- 그룹 IIC 용기에 대한 접합부의 최소 길이 및 최대 틈새 ¦ 접합 종류 ¦ 접합 종류 ¦ 접합부 최소 길이 L mm ¦ 최대 틈새 mm ¦ 최대 틈새 mm ¦ 최대 틈새 mm ¦ 최대 틈새 mm ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 접합 종류 ¦ 접합 종류 ¦ 접합부 최소 길이 L mm ¦ 체적 cm3 Vs 100 ¦ 체적 cm3 100 < Vs 500 ¦ 체적 cm3 500 < V≤2000 ¦ 체적 cm3 V> 2 000 ¦ ¦ 플랜지 접합 a ¦ 플랜지 접합 a ¦ 6 9.5 15.8 25 ¦ 0.10 0.10 0.10 0.10 ¦ - 0.10 0.10 0.10 ¦ - 0.04 0.04 ¦ - 0.04 ¦ ¦ 마개 접합 (그림 2a) ¦ c≥ 6 mm ≥ 0.5 L L= C+ d fs 1 mm ¦ 12.5 25 40 ¦ 0.15 0.18b 0.20c ¦ 0.15 0.18b 0.20c ¦ 0.15 0.18b 0.20c ¦ - 0.18b 0.20c ¦ ¦ 원통 접합 마개 접합 (그림 2b) ¦ 원통 접합 마개 접합 (그림 2b) ¦ 6 9.5 12.5 25 40 ¦ 0.10 0.10 0.15 0.15 0.20 ¦ 0.10 0.15 0.15 0.20 ¦ - - 0.15 0.15 0.20 ¦ - 0.15 0.20 ¦ ¦ 구름 베어링이 있는 회전 전기기기 축 글 랜드의 원통 접합 a 평면 접합은 5.2.7 에 부합하는 아세틸렌과 공기의 폭발성 혼합물에만 허용된다. b f<0.5 mm 인 경우, 원통부의 최대 틈새는 0.20 mm 로 증가 C f<0.5mm 인 경우, 원통부의 최대 틈새는 0.25 mm 로 증가 ¦ 구름 베어링이 있는 회전 전기기기 축 글 랜드의 원통 접합 a 평면 접합은 5.2.7 에 부합하는 아세틸렌과 공기의 폭발성 혼합물에만 허용된다. b f<0.5 mm 인 경우, 원통부의 최대 틈새는 0.20 mm 로 증가 C f<0.5mm 인 경우, 원통부의 최대 틈새는 0.25 mm 로 증가 ¦ 6 9.5 12.5 25 40 ¦ 0.15 0.15 0.25 0.25 0.30 ¦ 0.15 0.25 0.25 0.30 ¦ 0.25 0.25 0.30 ¦ 0.25 0.30 ¦ 최대 틈새를 정할 때는 KS A ISO 80000-1[3]에 따라 반올림한 구조상의 값을 고려해야 한다. 5.3 나사 접합부(Threaded joints) 나사 접합부는 표 4 또는 표 5 의 요구사항을 만족하여야 한다. 표 4- 원통형 나사 접합부 ¦ 피치 ¦ ≥ 0.7 mma ¦ ¦ --- ¦ --- ¦ ¦ 나사 형상과 결합 품질 ¦ ISO 965-1 과 ISO 965-3b 에 따라 중간 또는 정밀 공차 ¦ ¦ 체결 나사산 수 체결 깊이 ¦ ≥5 ¦ ¦ ¦ ≥ 5 mm ¦ ¦ 체적 ≤ 100 cm3 체적 > 100 cm3 ¦ ≥ 8 mm ¦ a 피치가 2 mm 를 초과 할 경우, 전기기기가 15.3 에 따른 폭발 인화시험을 통과 할 수 있도록 특별 한 제조상의 사전조치가 필요할 수도 있다(예를 들어 체결 나사산 수를 증가). b 제조자가 정한 나사 접합 길이가 표 9 에서 정하는 값으로 감소하여 15.3 에 따른 폭발 인화시험 을 통과 하는 경우, 나사 형상 또는 결합 품질이 ISO 965-1 과 ISO 965-3 에 부합하지 않은 원형 나사 접합도 허용한다. 14 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b52bbf6f-f383-4f98-91df-3ec618f38e99 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 표 5- 테이퍼 나사 접합부 a,c ¦ 각 부분의 나사산 수 ¦ ≥5b ¦ ¦ --- ¦ --- ¦ ¦ a 내부 및 외부 나사산은 공칭 크기가 같아야 한다. b 나사산은 ANSI/ASME B1.20.1 의 NPT 요구사항을 만족해야 하며 렌치로 조일 수 있어야 한다. 외부 나사부는 다음이 제공되어야 한다. 1) 유효 나사산 길이는 "L2" 치수보다 작지 않아야 하며 2) 단붙이(shoulder)가 제공될 경우, 단붙이와 나사산 끝 간의 길이는 "L4" 치수보다 작지 않아 야 한다. 내부 나사산은 L1 플러그 게이지를 사용해 "플러시(flush)"에서 "2 산 여유(2 turns large)"로 측정되야 한다. C 내부와 외부 나사부가 최소 4.5 개가 완전히 맞물린 테이퍼 나사 접합으로 구성되는 경우, 이 표 의 각주 b 요구사항들을 적용할 필요는 없다. ¦ a 내부 및 외부 나사산은 공칭 크기가 같아야 한다. b 나사산은 ANSI/ASME B1.20.1 의 NPT 요구사항을 만족해야 하며 렌치로 조일 수 있어야 한다. 외부 나사부는 다음이 제공되어야 한다. 1) 유효 나사산 길이는 "L2" 치수보다 작지 않아야 하며 2) 단붙이(shoulder)가 제공될 경우, 단붙이와 나사산 끝 간의 길이는 "L4" 치수보다 작지 않아 야 한다. 내부 나사산은 L1 플러그 게이지를 사용해 "플러시(flush)"에서 "2 산 여유(2 turns large)"로 측정되야 한다. C 내부와 외부 나사부가 최소 4.5 개가 완전히 맞물린 테이퍼 나사 접합으로 구성되는 경우, 이 표 의 각주 b 요구사항들을 적용할 필요는 없다. ¦ ¦ 비고 내압방폭 인입 장치에 적용할 수 있는 테이퍼 나사 요구사항에 대해서는 부속서 C 를 참조 할 것. ¦ 비고 내압방폭 인입 장치에 적용할 수 있는 테이퍼 나사 요구사항에 대해서는 부속서 C 를 참조 할 것. ¦ 5.4 개스킷(O-링을 포함) (Gaskets (including O-rings)) 예를 들어 습기 또는 먼지의 침투 또는 유체의 누설을 막기 위해 압축성 또는 탄성 재료의 개스킷이 사용되는 경우, 이는 보충적 성격으로 적용되어야 하며 내압방폭 접합부 길이 결정에 고려하지 않는다. 개스킷은 다음이 만족되도록 장착하여야 한다. a) 허용 틈새 및 플랜지 접합부의 길이 또는 마개 접합부의 평면부가 유지되고 b) 원통 접합부 또는 마개 접합 원통부의 최소 길이가 압축 전과 후에 유지되어야 한다. 이 요구사항은 케이블글랜드(13.4 참조) 또는 금속 실링 개스킷 또는 금속 외피가 있는 난연성 압축 성 재료로 된 실링 개스킷을 사용하는 접합부에는 적용하지 않는다. 이러한 개스킷은 방폭구조에 기 여를 하며, 이 경우 평면부의 각 표면 사이의 틈새는 압착 후에 측정하여야 한다. 원통부의 최소 길 이는 압착 전, 후 동일하게 유지하여야 한다. 그림 10 에서 그림 16 을 참조 ![image](/image/placeholder) 2 그림 10 - 개스킷 사용, 예시 1 ![image](/image/placeholder) 1 2 Z 그림 11 - 개스킷 사용, 예시 2 15 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
a85c0bec-425d-4ea8-921b-c2df2e99d5a7 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 ![image](/image/placeholder) 3 그림 12 - 개스킷 사용, 예시 3 ![image](/image/placeholder) L 2 그림 14- 개스킷 사용, 예시 5 ![image](/image/placeholder) 식별부호 1 용기 내부 2 O-링 3 개스킷 4 금속 또는 금속외피 개스킷 ![image](/image/placeholder) 3 그림 13 - 개스킷 사용, 예시 4 ![image](/image/placeholder) L 그림 15 - 개스킷 사용, 예시 6 16 그림 16 - 개스킷 관련 요구사항의 그림, 예시 7 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
52d762a5-6407-4b53-ad0c-da32f18c7c00 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 5.5 모세관을 사용하는 기기(Equipment using capillaries) 모세관은 내부의 지름을 0 으로 간주하여 원통형 접합부에 대한 표 2 또는 표 3 에 주어진 틈새 치수 를 준수하거나 또는 모세관이 이 표에서 주어진 틈새를 만족하지 못하는 경우, 15.3 에 따라 내부점화 에 의한 인화 시험을 실시하여 평가하여야 한다. 6 밀봉 접합부(Sealed joints) 6.1 고착 접합부(Cemented joints) 6.1.1 일반사항(General) 내압방폭용기의 일부(parts)는 용기의 벽면에 직접 고착 접합하여 분리 가능하지 않은 조립체로 하거 나 고착 접합부를 손상시키지 않고 조립체가 하나의 단위로 교체할 수 있도록 금속 프레임에 고착 접합할 수 있다. 고착 재료, 준비, 적용 및 경화 조건(예: 시간, 온도 등) 등은 KS C IEC 60079-0 에 따라 준비된 문서 에 포함하여야 한다. 생산품을 대표하고 고착 접합부가 변경되지 않은 시료를 평가 및 시험에 사용하여야 한다. 고착 접합부를 포함하고 있는 5 절에 따른 내압방폭 접합부가 고착제 없이 15.3 에 따른 시험을 실시 한 경우, 6 절의 요구사항을 충족할 필요는 없다. 6.1.2 기계적 강도(Mechanical strength) 고착 접합부는 단지 고착 접합부가 형성하는 내압방폭용기의 밀봉을 보장하기 위한 것이다. 접합부 의 기계적 강도는 고착제 단독의 접착력에 의존하지 않도록 구조를 설계하여야 한다. 고착 접합부를 고정하기 위한 보충적인 기계적 수단은 설치 또는 유지보수 중에 문 또는 덮개의 개방으로 손상되어 서는 안 된다. 고착 접합부에 대하여 아래의 시험을 실시하여야 한다. a) 생산품을 대표하는 2 개 이 시료에 15.2.3.2 에 따라 물을 이용하여 내압시험을 실시한다. 시험 중인 시료 아래에 놓인 흡습지(blotting paper)에 누출의 흔적이 없는 경우, 시험이 만족한 것으 로 본다. b) 위의 a)에서 사용된 동일한 시료 또는 별도의 2 개 시료 세트에 대하여 KS C IEC 60079-0 에 따른 용기에 관한 시험을 실시하여야 한다. 연속하여 이 시료에 15.2.3.2 에 따라 물을 이용하여 내압시 험을 실시한다. 시험 중인 시료 아래에 놓인 흡습지에 누출의 흔적이 없는 경우, 시험이 만족한 것으로 본다. 비고 KS C IEC 60079-0 에서 용기에 관한 시험은 각 시료에 수행되는 시험 횟수를 다르게 하여 시료 2 개 세트 또는 시료 4 개 세트로 할 수 있다. 6.1.2 의 b)의 시료에 대한 시험 결과 로 흡습지에 누출이 있을 경우, 용기에 관한 시험과 수압시험을 실시 후 누수가 일어난 1 개 시료의 고착 접합부에 대하여 아래의 시험을 차례로 실시한다. - 시료에 수정을 가하지 않은 상태로 19.4 에 따른 화염침식시험 - 시료에 수정을 가하지 않은 상태로 15.3.2.1 에 따른 인화시험, 또는 기기그룹에 적용 가능한 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 17 | {}
177e4894-3984-4530-b7b3-9605c36e5734 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 15.3.3.3 또는 15.3.3.4 에 따른 인화시험 고착 접합부는 이 인화시험이 만족스럽다면 적합한 것으로 판정한다. 6.1.2 를 준수하기 위해 기준압력의 1.5 배 또는 3 배가 필요한 경우, 고착 접합부에 대한 일상내압시험 (16 절에 따른)을 수행하여야 한다. 6.1.3 고착 접합부 길이(Width of cemented joints) 체적이 V 인 내압방폭용기의 내부에서 외부로 고착 접합을 통하는 최단 경로는 다음과 같아야 한다. ¦ ≥3 mm, ¦ V≤ 10 cm3 인 경우 ¦ ¦ --- ¦ --- ¦ ¦ ≥6 mm, ¦ 10 cm3 < V= 100 cm3 인 경우 ¦ ¦ ≥10 mm, ¦ V> 100 cm3 인 경우 ¦ 6.2 용융 유리 접합부(Fused glass joints) 6.2.1 일반사항(General) 용융 유리 접합부는 용융된 유리를 금속 프레임에 적용하여 유리와 금속 프레임 사이에 화학적 또는 물리적 접합을 시키는 유리 대 금속 접합부이다. 6.2.2 용융 유리 접합부의 길이(Width of fused glass joints) 내압방폭용기의 내부에서 외부로 용융 유리 접합을 통하는 경로는 3 mm 이상이어야 한다. 7 조작축(Operation rods) 조작축이 내압방폭용기의 벽을 관통하는 경우, 다음 요구사항을 만족하여야 한다. 조작축 지름이 표 2 및 표 3 에 규정된 접합부의 최소 길이를 초과 하는 경우, 접합부의 길이는 조 작축 지름 이상이어야 하나 25 mm 를 초과 하지 않아도 된다. 정상적인 사용 상태에서 마모로 지름 방향의 틈새가 확대되기 쉬운 경우, 교체 가능한 부싱 등의 사용으로 원래 상태로 복귀를 용이하게 하기 위한 적절한 배치가 이루어 져야 한다. 다른 방법으 로, 마모로 인한 틈새의 확대는 8 절에 부합하는 베어링의 사용으로 방지할 수 있다. 8 샤프트 및 베어링에 대한 추가 요구사항(Supplementary requirements for shafts and bearings) 8.1 샤프트의 접합부(Joints of shafts) 8.1.1 일반사항(General) 회전 전기기기 샤프트의 내압방폭 접합부는 정상 사용 중 마모가 일어나지 않도록 구성해야 한다. 이러한 내압방폭 접합부는 다음과 같을 수 있다. 원통 접합부(그림 17 참조) 래버린스(labyrinth) 접합부(그림 18 참조) 18 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
0b2e7cdb-6f79-495e-9391-6ec75ac41415 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 플로팅 글랜드(floating gland) 접합부(그림 19 참조) 8.1.2 원통 접합부(Cylindrical joints) 원통 접합부가 그리스를 유지하기 위한 홈(grooves)이 있는 경우, 홈을 포함하는 부분은 내압방폭 접 합부의 길이를 결정할 때 고려하지 않으며 또한 접합부를 간섭하지 않아야 한다(그림 17 참조). 회전 전기기기 샤프트의 최소 반지름 틈새 k(그림 20 참조)는 0.05 mm 이상이어야 한다. 8.1.3 래버린스 접합부(Labyrinth joints) 표 2 및 표 3 의 요구사항을 충족하지 않는 래버린스 접합부는 14 절부터 16 절까지 규정된 시험을 만 족할 경우 이 표준의 요구사항을 준수하는 것으로 간주할 수 있다. 회전 전기기기 샤프트의 최소 반지름 틈새 k(그림 20 참조)는 0.05 mm 이상이어야 한다. 8.1.4 플로팅 글랜드 접합부(Joints with floating glands) 글랜드의 최대 플로팅 정도의 결정은 베어링 공차 및 제조자가 지정한 베어링 마모 허용치를 고려하 여야 한다. 글랜드는 샤프트와 함께 반지름 방향 및 샤프트 상에서 샤프트 방향으로 자유롭게 움직 일 수 있지만 샤프트와 동심 상태를 유지해야 한다. 글랜드의 회전을 차단하는 장치가 있어야 한다 (그림 19 참조). 플로팅 글랜드는 그룹 IIC 의 전기기기에 허용되지 않는다. ![image](/image/placeholder) 그리스 밀폐용 홈 그림 17 - 회전 전기기기 샤프트의 원통 접합부의 예 19 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
8f81296c-c51e-4a6e-a182-90f7dd1718ea | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 ![image](/image/placeholder) 그림 18 - 회전 전기기기 축의 래버린스 접합부의 예 ![image](/image/placeholder) 식별부호 ¦ 1 ¦ 틈새 ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 2 ¦ 글랜드 ¦ 회전 고정부 ¦ 그림 19 - 회전 전기기기 샤프트의 플로팅 글랜드 접합부의 예 20 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
2b170010-5366-498d-83fe-ac24a3972612 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 ![image](/image/placeholder) k m D 식별부호 ¦ k ¦ 마찰 없이 허용되는 최소 반지름 틈새 ¦ ¦ --- ¦ --- ¦ ¦ m ¦ k 를 고려한 최대 반지름 틈새 ¦ ¦ D-d ¦ 지름 틈새 ¦ 그림 20 - 회전 전기기기의 샤프트 글랜드 접합부 8.2 베어링(Bearings) 8.2.1 슬리브 베어링(Sleeve bearings) 슬리브 베어링과 관련된 샤프트 글랜드의 내압방폭 접합부는 슬리브 베어링 자체의 접합부에 더하여 제공되어야 하며 접합부 길이는 최소한 샤프트 지름 이상이되 25 mm 를 넘지 않아야 한다. 원통 또는 래버린스 내압방폭 접합부가 슬리브 베어링이 있는 회전 전기기기에 사용되는 경우, 고정 자와 회전자 사이의 공극이 제조자가 지정한 최소 반지름 틈새 k(그림 20 참조)보다 클 때는 접합면 중 적어도 한 면이 스파크가 발생하지 않는 금속(예: 납 함유 황동)이어야 한다. 이 비스파크 금속의 최소 두께는 공극(air gap)보다 커야 한다. 슬리브 베어링은 그룹 IIC 의 전기기기에 허용되지 않는다. 8.2.2 구름 베어링(Rolling-element bearings) 구름 베어링이 설치된 샤프트 글랜드의 경우, 최대 반지름 틈새 m(그림 20 참조)은 표 2 및 표 3 에 서 해당 글랜드에서 허용된 최대 틈새의 2/3 를 초과 하지 않아야 한다. 비고 1 조립 상태에서 모든 부품이 동시에 최악의 치수로 존재하지 않을 것임이 인정된다. m 및 k 검증에는 "RMS"와 같은 공차에 대한 통계적 기법이 필요할 수 있다. 비고 2 제조자의 m 과 k 값 계산을 검증하는 것은 이 표준의 요구사항은 아니다. 또한 m 과 k 값의 측정에 의한 검증은 이 표준의 요구사항이 아니다. 9 투광성 부품(Light-transmitting parts) 유리 이외의 투광성 부품에 대해서는 이 표준 19 절의 요구사항을 적용한다. 비고 투광성 부품을 장착할 때 부품에 기계적 내부 응력을 발생시키는 재료는 투광성 부품의 파손 21 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c1e63480-0b36-461c-9f24-b5e924ed82bf | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 을 야기할 수 있다. 10 내압방폭용기의 일부를 형성하는 통기 및 배수 장치 (Breathing and draining devices which form part of a flameproof enclosure) 10.1 일반사항(General) 통기 및 배수장치는 장착된 용기의 내부 폭발로 인해 발생한 압력을 견딜 수 있고 용기를 둘러싸고 있는 폭발성 분위기로 폭발이 전달되는 것을 방지할 수 있는 투과 성 부품을 포함해야 한다. 통기 및 배수장치는 또한 화염 차단 성능에 영향을 주는 영구적 변형이나 손상 없이 내압방폭용기 내부에서의 폭발에 의한 동적 영향을 견뎌야 한다. 통기 및 배수장치가 그 표면에서 연속적인 연소 를 견뎌야 하는 것은 아니다. 이러한 요구사항들은 소리를 전송하는 장치에도 동일하게 적용되지만 다음 장치에는 적용되지 않는다. 내부 폭발에 의한 압력을 저감하는 장치 공기와 폭발성 혼합물을 형성할 수 있고 대기압의 1.1 배를 초과 하는 압력의 가스를 포함하는 압 력 라인과 함께 사용되는 장치 10.2 통기 또는 배수용 개구부(Openings for breathing or draining) 통기 또는 배수를 위한 개구부는 플랜지 접합부의 틈새를 의도적으로 확대하여 형성해서는 안 된다. 비고 환경 오염물질(먼지 또는 페인트 축적 등)은 통기 및 배수 장치의 작동 불능을 야기할 수 있다. 10.3 재료 성분 제한(Composition limits) 장치에 사용되는 재료의 성분 제한은 직접적으로 명시하거나 기존 부품 명세서에 언급해야 한다. 아세틸렌을 함유하는 폭발성 가스 분위기에서 사용하기 위한 통기 또는 배수 장치의 부품은 아세틸 라이드 형성을 제한하기 위해 질량 기준으로 구리가 60 %를 넘어서는 안 된다. 10.4 치수(Dimensions) 통기 및 배수 장치 및 그 구성품의 치수를 명시하여야 한다. 10.5 측정 가능한 경로를 가진 엘리먼트(Elements with measurable paths) 틈새(interstices) 및 측정 가능한 경로의 길이는 부품이 14 절에서 16 절까지의 시험을 만족하는 경우 표 2 및 표 3 에 주어진 값을 따르지 않아도 된다. 주름리본 엘리먼트(crimped ribbon elements) 및 다중 스크린 엘리먼트(multiple screen elements)에 대 한 추가 요구사항들은 부속서 A 에 있다. 10.6 측정 불가능한 경로를 가진 엘리먼트(Elements with non-measurable paths) 부품을 통과 하는 경로가 측정 불가능한 경우(예: 소결 금속 부품), 해당 부품은 부속서 B 의 관련 요 구사항을 따라야 한다. 22 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
508c9147-33d9-4ebe-99fa-ea4a8d1c5881 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 이러한 부품들은 특정 재료에 대한 표준 방법 및 특정 제조 방법에 따라 밀도 및 기공 크기에 따라 분류된다(부속서 B 참조). 10.7 분리형 장치(Removable devices) 10.7.1 일반사항(General) 분해 가능한 장치의 경우, 장치를 다시 조립할 때 구멍이 작아지거나 확대되지 않도록 설계하여야 한다. 10.7.2 엘리먼트의 설치 방법(Mounting arrangements of the elements) 통기 및 배수 엘리먼트는 다음과 같은 방법으로 소결되거나 다른 적절한 방법을 통해 고정되어야 한 다. 용기의 일부분을 형성하기 위해 용기에 직접적으로 고정하거나 적합한 장착 부품(mounting component)에 고정하고 이 부품을 용기에 클램핑 또는 나사 형태로 삽입 가능한 구조로 하여 부품을 하나의 단위로 교체 가능하도록 하는 방법 이에 대한 대안으로, 부품은 예를 들어 5.2.1 에 따라 압입(press-fitted) 등을 통해 내압방폭 접합부를 형성할 수 있다. 이 경우, 부품이 14 절에서 16 절까지의 형식 시험을 만족한다면, 부품의 표면 거칠기 가 5.2.2 를 만족할 필요는 없다는 점을 제외하고는 5 절의 해당 요구사항들을 적용하여야 한다. 필요한 경우, 클램핑 링 또는 이와 유사한 수단을 사용하여 용기와 의 일체성을 유지할 수 있다. 통기 또는 배수 엘리먼트는 다음과 같은 방법으로 장착할 수 있다. - 내부에서 장착, 이 경우 나사 및 클램핑 링의 접근은 내부에서만 가능해야 한다. - 용기 외부에서 장착, 이 경우 패스너는 11 절에 적합해야 한다. 10.8 기계적 강도(Mechanical strength) 통기 및 배수 장치 그리고 해당하는 경우, 가드는 정상적으로 장착된 상태에서 KS C IEC 60079-0 에 따른 충격시험에 적합해야 한다. 10.9 방폭부품으로 사용하는 경우의 통기 장치 및 배수 장치(Breathing devices and draining devices when used as Ex components) 10.9.1 일반사항(General) 방폭부품으로 평가하는 통기 및 배수 장치에는 10.1 에서 10.7 까지에 추가하여 다음 요구사항을 적용 해야 한다. 10.9.2 엘리먼트 및 부품의 장착 방법(Mounting arrangements of the elements and components) 통기 및 배수 엘리먼트는 소결되거나 또는 6 절에 따라 시멘트 접합되거나, 장착 부품을 형성하기 위 해 적절한 방법으로 장착 부에 고정하여야 한다. 23 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
2ba4e6f4-1033-4649-acdb-a365bde4a564 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 장착 부품(components)은 5 절 및 6 절 그리고 해당하는 경우, 11 절의 관련 요구사항에 따라 교체 가 능한 구성단위로서 용기에 클램핑 또는 패스너로 고정되거나 나사결합으로 용기에 고정하여야 한다. 10.9.3 방폭부품으로 사용하는 통기 및 배수 장치에 대한 형식 시험(Type tests for breathing and draining devices used as Ex components) 10.9.3.1 일반사항(General) 시험 중인 시료 장치의 부착은 내압방폭용기에 일반적으로 설치되는 것과 같은 방식으로 시험 지그 (test rig enclosure) 끝에서 이루어져야 한다. 시험은 10.8 의 충격시험 후 10.9.3.2 에서 10.9.3.4 에 따라 시료에 대해 수행되어야 한다. 충격시험은 시료가 시험 지그의 끝 부분을 형성하는 판에 장착될 때 시험 지그와 분리하여 시료에 수행할 수 있다. 경로를 측정할 수 없는 장치의 경우, 시료의 최대기포시험 기공크기(maximum bubble test pore size)는 명시된 최대기포시험 기공크기의 85 % 이상이어야 한다. B.1.2 를 참조 10.9.3.2 온도 시험(Thermal tests) 10.9.3.2.1 일반사항(General) 10.9.3 의 기포시험 후에, 방폭부품용 통기 및 배수 장치는 사용하고자 하는 내압방폭용기의 최대 부 피를 기준으로 온도 시험을 실시하되 그림 21 의 시험 지그 부피 이상이어야 한다. 비고 그림 21 의 시험 지그를 사용할 때 최대 부피는 약 2.5L 이다. 단일 내압방폭용기에 복수로 사용되는 통기 및 배수 장치는 용기와 함께 추가적으로 시험을 해야 한다. 10.9.3.2.2 시험 절차(Test procedure) 용기의 체적이 2.5 L 이하인 경우, 그림 21 과 같이 4 개의 섹션으로 구성된 시험 지그를 조립하여 사 용하여야 하며 시험 절차를 다음과 같이 수행해야 한다. a) 점화원은 지그 인입부 및 시료가 장착된 끝 판의 안쪽에서 50 mm 에 위치시킨다. b) 시험 혼합물은 15.4.3.1 에 적합해야 한다. c) 시험 중 시료의 외부 표면온도를 관찰하여야 한다. d) 모든 시료는 제조자의 문서에 명시한 바와 같이 작동되어야 한다. 5 회의 시험 후, 폭발성 혼합물 은 외부로부터 충분한 시간 동안, 최소 10 분 동안, 시료에 유지되도록 하여 시료의 표면에서 지속 적인 연소가 일어날 수 있도록 하여 시료의 외부 표면 온도를 높이거나 시료 바깥 표면으로 열 전달이 이루어질 수 있도록 한다. 비고 10 분 시험 기간 후 시료 외부 표면의 온도는 10.9.3.3.3 에 따라 온도 등급을 결정하는 데 사용된다. e) 시험은 장치(시료)가 사용되는 가스 그룹에 대한 각 가스 혼합물에 대해 5 회 수행되어야 한다. 24 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
7e359d72-d065-41cd-8695-effa27c06507 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 ![image](/image/placeholder) Base section with: Section 1 Section 2 Section 3 Section 4 174 500 500 500 500 IG ⌀40 (internal) TS PT IG IG Exh. ⌀75 (internal) 식별부호 ¦ TS ¦ 시험 시료의 위치 ¦ ¦ --- ¦ --- ¦ ¦ I ¦ 인입부 ¦ ¦ Exh. ¦ 배출부 ¦ ¦ IG ¦ 점화원 ¦ ¦ PT ¦ 압력 변환기 ¦ 그림 21 - 통기 및 배수 장치용 시험 지그 용기의 체적이 2.5 L 보다 큰 경우, 의도된 체적의 대표적인 용기를 사용해야 하며, 시험 절차를 다음 과 같이 수행하여야 한다. 1) 시험 혼합물은 15.4.3.1 에 적합해야 한다. 2) 시험 중 시료의 외부 표면온도를 관찰하여야 한다. 3) 모든 시료는 제조자의 문서에 명시한 바와 같이 작동되어야 한다. 5 회의 시험 후, 폭발성 혼합물 은 외부로부터 충분한 시간 동안, 최소 10 분 동안, 시료에 유지되도록 하여 시료의 표면에서 지속 적인 연소가 일어날 수 있도록 하여 시료의 외부 표면 온도를 높이거나 시료 바깥 표면으로 열 전달이 이루어질 수 있도록 한다. 4) 시험은 장치(시료)가 사용되는 가스 그룹에 대한 각 가스 혼합물에 대해 5 회 수행되어야 한다. 10.9.3.2.3 적합 기준(Acceptance criteria) 온도 시험 중에 화염 전파가 발생하지 않아야 하며 지속적인 연소가 관찰되지 않아야 한다. 장치는 화염 억제 특성(flame-arresting properties)에 영향을 줄 수 있는 열적 또는 기계적 손상 또는 변형이 없어야 한다. 장치(시료)의 측정된 외부 표면 온도 상승 분에 1.2 의 안전계수 곱하고 장치의 최고 서비스온도 (service temperatures)를 더하여 전기기기의 온도 등급을 결정한다. 비고 10.9 의 시험 중 하나라도 통과 하지 못한 통기 및 배수 장치는 부품으로서의 평가에서 제외한 다. 다만, 내압방폭용기와 함께 사용되는 경우, 15.4 에 따라 특정 용기와 함께 시험한다. 10.9.3.3 폭발 인화시험(Test for non-transmission of an internal ignition) 10.9.3.3.1 일반사항(General) 10.9.3 에 따른 기포 시험 후, 이 시험은 그림 21 에 나와 있는 표준 시험지그에서 수행하여야 하며 다 음과 같은 추가 및 수정과 함께 15.4.4 에 따라 수행한다. 25 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
e51c3664-baa5-48c8-bb62-f90c4e91e473 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 10.9.3.3.2 시험 절차(Test procedure) 점화원의 위치는 그림 21 과 같아야 한다. a) 인입부 끝쪽 b) 시료가 장착된 끝 판의 안쪽에서 50 mm 지점 해당 시험의 목적상, 시험 지그는 그림 21 에 따라 각 가스 그룹별로 조립되어야 하며 다음과 같은 섹션 개수를 가져야 한다. - 그룹 I 및 그룹 IIA: 시험 지그 조립의 1 개 섹션 - 그룹 IIB 및 그룹 IIC: 시험 지그 조립의 4 개 섹션 시험 지그 내부의 가스 혼합물을 점화하여야 하며 시험은 각 점화 지점에서 5 회 실시한다. 측정 가능한 경로 또는 측정 불가능한 경로를 갖는 그룹 1, 그룹 IIA 및 그룹 IIB 의 통기 및 배수 장 치에 대해서는 15.3.2 의 폭발 인화시험을 실시하여야 한다. 측정 가능한 경로를 갖는 그룹 IIC 의 통기 및 배수 장치에 대해서는 15.3.3 및 15.4.4.3.2 또는 15.4.4.3.3 의 폭발 인화시험을 실시하여야 한다. 측정 불가능한 경로를 갖는 그룹 IIC 의 통기 및 배수 장치에 대해서는 15.4.4.3.2(방법 A) 또는 15.4.4.3.3(방법 B)의 폭발 인화시험을 실시하여야 한다. 10.9.3.3.3 적합 기준(Acceptance criteria) 시험 도중 시험 챔버(test chamber)로 불꽃이 전달되지 않아야 한다. 10.9.3.4 통기 및 배수 장치의 내압 성능 시험(Test of the ability of the breathing and draining device to withstand pressure) 10.9.3.4.1 시험 절차(Test procedure) 각 가스 그룹의 기준 시험 압력은 다음과 같다. ¦ - ¦ 그룹 I ¦ 1 200 kPa ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ - ¦ 그룹 IIA ¦ 1 350 kPa ¦ ¦ ¦ ¦ ¦ ¦ - ¦ 그룹 IIB ¦ 2 500 kPa ¦ ¦ - ¦ 그룹 IIC ¦ 4 000 kPa ¦ 시험 목적으로 통기 및 배수 장치 내부 표면에 얇고 유연한 막(membrane)을 설치한다. 기준압력은 부품이 의도된 가스 그룹에 대해 위에 주어진 관련 압력 중 하나를 적용한다. 다음과 같은 내압시험 중 하나를 적용하여야 한다. 최소 10 초간 기준압력의 1.5 배. 이후 각 부품에 대해 일상시험을 수행한다. 최소 10 초간 기준압력의 4 배. 이 시험이 성공적일 경우, 제조자는 일상시험을 하지 않아도 된다. 10.9.3.4.2 적합 기준(Acceptance criteria) 26 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
7ad19549-4598-43f2-accb-0db9d6789bb4 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 내압시험 후, 장치는 방폭성능에 영향을 미치는 영구적인 변형 또는 손상이 없어야 한다. 10.9.4 방폭부품 인증서(Ex component certificate) 방폭부품 인증서는 형식 시험을 거친 내압방폭용기에 부착하기 위해 통기 및 배수 장치를 적절히 선 정하는 데 필요한 세부사항을 사용제한표(schedule of limitations)에 포함시켜야 한다. 사용제한표는 최 소한 다음 사항을 포함하여야 한다. a) 40 °C 또는 표시된 더 높은 주위온도(ambient temperature)로 보정된 형식시험을 통하여 확인된 최 고표면온도 b) 비금속 용기 및 용기의 비금속 부품에 대한 서비스온도 범위 c) 2.5L 보다 큰 경우, 허용되는 용기의 최대 부피(온도 시험 기준) d) 각 방폭 부품은 다음을 기술하는 제조자 선언과 함께 인증서 사본을 첨부해야 한다는 요구사항 인증 조건 준수 해당하는 경우, 재료, 최대기포시험 기공크기 및 최소 밀도의 확인 e) 해당하는 경우, 특수한 장착 방법 11 패스너 및 개구부(Fasteners and openings) 11.1 외부에서 접근 가능하고 내압방폭용기를 조립하기 위하여 필요한 패스너는 다음과 같아야 한다. 그룹 I 의 경우, 헤드 보호형(head shrouded)이거나 카운터보어 구멍(counter-bored holes)이 제공되 거나 또는 기기의 구조상 본질적으로 보호가 되는 KS C IEC 60079-0 의 요구사항에 따른 특수 패 스너이여야 한다. 그룹 II 의 경우, KS C IEC 60079-0 의 요구사항에 부합하는 특수 패스너이여야 한다. 비고 그룹 I 의 경우, 시라우딩(shrouding) 또는 카운터 보링(counter-boring)을 요구하는 목적은 패스 너 헤드를 충격으로부터 기본적으로 보호하기 위해서이다. 11.2 플라스틱 재료 또는 경금속의 패스너는 허용되지 않는다. 11.3 15 절에 규정된 형식 시험을 수행함에 있어서 제조자가 명시한 나사와 너트를 사용하여야 한다. 시험 중 사용되는 나사 또는 너트의 특성 등급(property class) 또는 항복응력 및 그 유형은 다음 중 하나와 같이 한다. 표 14, a)에 따라 기기에 표시한다. - 관련 인증서에 특정사용조건으로 명시한다. 비고 나사 및 너트의 기계적 특성에 관한 추가 세부사항은 부속서 F 를 참조할 것. 11.4 스터드(studs)는 11.3 에 적합해야 하며 견고하게 고정되어야 한다. 즉, 용접 또는 리벳 또는 다 른 동등한 효과 적인 방법으로 용기에 영구적으로 고정하여야 한다. 11.5 패스너가 벽과 내압방폭 접합부를 형성하고 용기로부터 분리할 수 없는 경우(예를 들어 용접, 리벳팅 또는 다른 동등한 효과 적인 방법)가 아니면 내압방폭용기의 벽을 관통해서는 안 된다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 27 | {}
e214abbf-0325-474b-852e-ff9508c4b63d | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 11.6 내압방폭용기의 벽을 관통하지 않는 나사 또는 스터드 용 구멍의 경우, 내압방폭용기 벽면의 남 은 두께는 나사 또는 스터드 공칭 지름의 1/3 이상, 최소 3mm 이상이어야 한다. 11.7 나사가 용기 벽면의 막힌 구멍(blind holes)에 완전히 조여졌을 때, 와셔가 끼워지지 않은 상태에 서 적어도 하나의 완전 나사산이 구멍 바닥에 여유로 남아 있어야 한다. 11.8 전선 인입을 위한 구멍 이외에 푸시버튼과 같은 장치를 선택적으로 설치하기 위해 내압방폭용 기 벽면에 구멍을 만들 수 있다. 이러한 선택 사양의 장치가 제조 당시 설치되지 않은 경우, 용기의 방폭성능이 유지될 수 있는 장치로 구멍을 막아야 한다. 비고 이러한 구멍을 위한 나사산의 형태는 인입 장치(entry devices)에 대하여 규정된 것에 국한되지 않는다(13 절 참조). 11.9 나사산으로 된 문 또는 덮개는 6 각 소켓 세트 스크루 또는 동등한 효과 가 있는 방법으로 추가 로 고정하여야 한다. 12 재료(Materials) 12.1 내압방폭용기는 14 절부터 16 절까지의 관련 시험을 만족해야 한다. 12.2 여러 개의 내압방폭용기가 함께 조립되는 경우, 이 표준의 요구사항을 각각의 용기에 적용하며, 특히 이들 용기를 분리하는 칸막이와 칸막이를 통과 하는 모든 부싱 및 조작축에도 적용한다. 12.3 용기가 여러 개의 상호 연결된 격실(compartments)을 포함하거나 내부 부품의 배치로 인하여 세분되는 경우, 압력 및 압력 상승 속도가 정상보다 커질 수 있다. 이러한 현상은 구조적으로 가능한 한 배제되도록 하여야 한다. 이러한 현상을 피할 수 없는 경우, 발 생하는 높은 응력을 고려하여 용기구조에 반영하여야 한다. 12.4 주철을 사용할 경우, 재료의 품질 등급이 150 이상이어야 한다. 비고 주철의 품질 등급 150 은 ISO 185 에서 규정되어 있다. 12.5 액체의 분해로 인해 산소를 생성할 위험이 있거나 용기가 설계된 것보다 더 위험한 폭발성 혼 합물이 있는 경우, 이러한 액체는 내압방폭용기에 사용해서는 안 된다. 그러나 용기가 생성되는 폭발 성 혼합물에 대하여 14 절에서 16 절까지의 시험을 통과 한 경우에는 해당 액체를 사용할 수 있다. 다 만, 주위의 폭발 분위기는 그 전기기기가 사용되는 그룹에 적합해야 한다. 12.6 그룹 I 의 내압방폭용기에서 공기 중에 아크를 발생할 수 있고 16 A 를 초과 하는 정격전류로 인한 전기적 응력을 받는(회로 차단기, 접촉기, 아이솔레이터와 같은 스위칭 기기에서) 절연 물질의 비교 트래킹 지수(comparative tracking index)는 CTI 400 M 이상이어야 한다. 비고 CTI 는 KS C IEC 60112 에 따라 결정한다. 그러나 위 절연재가 이 시험을 통과 하지 못한 경우, 부피가 빈 용기의 총 부피의 1 % 이내로 제한되 거나 적절한 검출 장치를 사용하여 절연 물질이 분해되어 위험 상태에 이르기 전에 용기로 공급되는 전원을 1 차측에서 차단할 수 있는 경우에는 사용할 수도 있다. 이러한 장치의 존재와 유효성은 검증 되어야 한다. 28 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
dc1989d2-b9eb-45f3-844a-13ba390d5b2d | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 12.7 내압방폭용기는 아연 또는 아연 함량이 80 % 이상인 아연합금으로 제조되어서는 않된다. 비고 아연 및 아연 합금은 특히 덥고 습한 공기에서 급속하게 열화되는 경향이 있다(특히 인장 강 도). 또한 대부분의 다른 금속보다 반응성이 높다. 따라서 위의 제한 사항이 만들어졌다. 12.8 아세틸렌을 함유한 폭발성 가스분위기에서, 용기 또는 외부에 장착되는 방폭 부품의 용기가 구 리 또는 구리 합금으로 제조된 경우 용기는 다음과 같아야 한다. 주석, 니켈, 또는 다른 물질로 코팅되어야 한다. 합금의 최대 구리 함량을 60 %로 제한하여야 한다. 부속서 C 에 규정된 내압방폭형 인입 장치는 코팅 또는 구리 함량 제한을 요구하는 용기의 표면으로 간주하지 않는다. 비고 아세틸렌 분위기에서 구리 사용의 제한하는 것은 기기 표면에 아세틸라이드가 형성되어 마찰 또는 충격으로 점화될 수 있기 때문이다. 13 내압방폭용기의 인입부(Entries for flameproof enclosures) 13.1 일반사항(General) 모든 인입부가 이 조항의 관련 요구사항을 충족하고 다음 중 하나를 만족하는 경우에 용기의 내압방 폭 성능은 유지된다. ISO 965-1 및 ISO 965-3 에 따라 미터 암나사의 공차 등급이 6H 이상의 등급이고 모든 모따기 (chamfer) 또는 언더컷(undercut)이 외부 벽면에서 최대 깊이 2mm 이내로 제한 길이가 최소 8 mm 이고 최소 8 개의 완전한 나사산을 갖춘 미터 수나사. 나사산에 언더컷이 있는 경우, 요구되는 체결 나사산 길이를 보장하기 위해 탈착 불가능한 비압축성 와셔 또는 그에 상응 하는 장치를 설치하여야 함. 비고 1 최소 8 개의 완전 나사산을 요구하는 것은 모따기 또는 언더컷의 존재를 고려하여 나사 인입 부에 부품을 설치할 때 최소 5 개의 완전한 나사결합이 이루어질 수 있게 하기 위함이다. 표 5 에 따른 NPT 암나사 - 표 5 에 따른 NPT 수나사 그룹 I 에만 적용하는 경우, 5.2 에 따른 비나사 접합부 비고 2 이 요구사항은 제조자에 의해 용기의 일부로 제공되는 일체형 케이블 글랜드 또는 유사 인 입 장치에는 적용하지 않는다. 13.2 나사 구멍(Threaded holes) 케이블 글랜드 또는 전선관 인입용 용기의 나사 구멍은 나사 형식 및 크기가 M25 또는 1/2NPT 처럼 식별되어야 한다. 이러한 식별은 다음과 같은 방법으로 이루어질 수 있다. 표 15 에 따라 구멍 인접부에 특정 나사산의 형식 및 크기를 표시 표 15 에 따라 명판에 특정 나사산의 형식 및 크기를 표시 표 15 에 따라 명판 상에 관련 참조 표시를 하고 사용설명서에 특정 나사산 형식 및 크기를 표시 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 29 | {}
813ca140-9471-451d-92e6-888c948d4546 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 제조자는 해당 전기기기의 문서에 다음 사항을 명시하여야 한다. a) 설치할 수 있는 인입부의 위치 b) 최대 허용되는 인입부의 개수 어댑터를 사용되는 경우, 각 인입부에는 1 개의 나사 어댑터만 사용할 수 있다. 블랭킹 엘리먼트는 어 댑터와 함께 사용할 수 없다. 13.3 비나사 구멍(그룹 I 만 해당됨)(Non-threaded holes (for Group 1 only)) 그룹 I 의 경우, 케이블 글랜드 또는 부싱의 설치를 위한 평(나사산이 없는) 구멍은 해당 전기기기 문 서에 다음을 명시해야 한다. a) 플랜지, 원통 또는 마개 접합부의 최소 길이 "L" 및 최대 틈새 b) 설치용 스터드 또는 볼트 규격(지름, 나사산, 인장 강도, 길이, 헤드 종류, 토크 등) 및 위치(피치 지름 및 간격) c) 고정 판(keeper plate) 및 관련 패스너, 치수 요건 및 위치(수량, 글랜드를 지지하기 위한 구멍의 간격, 지름, 결합 수단) d) 재료, 패스너 등의 최소 인장 강도 요구사항(기기의 기준압력에 근거) e) 용기 구멍에 대한 최대 및 최소 나사산 맞물림 개수 f) 패스너가 정확하게 맞물리고, 해당하는 경우 11.7 에 따라 구멍 하단에 정확한 공간이 허용되도록 패스너 헤드 아래 고정판의 두께를 감안한 패스너 길이에 관한 정보 그림 22 는 문서화하는 방법의 예시를 제공한다. ¦ 인입부 공칭 치수 ¦ 최대 구멍 지름 ¦ 최소 글랜드 지름 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 50.8 ¦ 50.96 ¦ 50.56 ¦ ¦ 63.5 ¦ 63.62 ¦ 63.22 ¦ ¦ 76.2 ¦ 76.35 ¦ 75.95 ¦ ¦ 95.3 ¦ 95.40 ¦ 95.00 ¦ ¦ 108 ¦ 108.10 ¦ 107.70 ¦ ¦ 114.3 ¦ 114.50 ¦ 114.10 ¦ Chart Type: bar 최대 구멍(bore) 지름 최소 글랜드 지름 최소 요소 요소 화염경로 0-링(옵션) item_01 12.5 13.5 10.5 2 3 재료 세부사항과 최소 인장강도는 명시되어야 하며 문서에 표로 작성할 수 있다. 패스너 구멍의 드릴 구멍 깊이, 고정 판 세부사항(두께, 형상, 인장강도), 고정 패스너의 수량 및 위치를 제공해야 한다. 그림 22 - 문서화 예시 13.4 케이블 글랜드(Cable glands) 일체형이든 또는 분리형이든 케이블 글랜드는 이 표준의 요구사항, 부속서 C 의 관련 요구사항을 충 족해야 하며 용기와 결합할 경우 5 절에 규정된 접합부의 길이와 틈새에 적합하여야 한다. 케이블 글랜드가 용기와 일체형이거나 특정 용기와 사용되는 경우, 해당 용기의 일부로 시험해야 한다. 분리형 케이블 글랜드는 다음을 만족하여야 한다. a) 나사형 방폭기기 케이블 글랜드 및 비나사형 방폭기기 케이블 글랜드(그룹 I 에만 해당)는 기기로 30 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
43656036-4d44-4a63-95cc-34a9369761fb | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 평가할 수 있다. 이러한 케이블 글랜드는 15.1 또는 16 절의 일상시험을 적용할 필요는 없다. b) 다른 케이블 글랜드는 방폭부품으로만 평가될 수 있다. c) 해당하는 경우, 13.2 또는 13.3 에 따라 구멍에 장착하기 위한 충분한 정보를 문서로 제공하여야 한다. 13.5 전선관 밀봉 장치(Conduit sealing device) 13.5.1 일체형이든 또는 분리형이든 전선관 밀봉 장치는 이 표준의 요구사항, "케이블 글랜드"를 "전선 관 밀봉 장치"로 대체하여 C.2.1.2 와 C.3.1.2 의 요구사항을 충족해야 하며 용기와 결합할 경우 5 절에 규정된 접합부의 길이와 틈새에 적합하여야 한다. 비고 이러한 구조는 재사용을 금지하므로, 전선관 밀봉 장치는 컴파운드가 경화된 후 밀봉성능을 방 해하지 않고 장착 및 제거될 수 있어야 한다는 C.2.1.2 의 요구사항을 적용할 수 없다. 전선관 밀봉 장치가 용기와 일체형이거나 특정 용기와 사용되는 경우, 해당 용기의 일부로 시험해야 한다. 분리형 전선관 밀봉 장치는 다음을 만족하여야 한다. 나사형 방폭기기 전선관 밀봉 장치는 기기로 평가할 수 있다. 이러한 전선관 밀봉 장치는 15.2 또 는 16 절의 일상시험을 적용할 필요는 없다. 다른 전선관 밀봉 장치는 방폭부품으로만 평가될 수 있다. 13.2 에 따라 구멍에 장착하기 위한 충분한 정보를 문서로 제공하여야 한다. 13.5.2 전선관 인입부는 그룹 II 의 전기기기에 대해서만 허용된다. 13.5.3 경화 컴파운드를 사용하는 스토핑 박스와 같은 밀봉 장치는 내압방폭용기의 일부 또는 인입 부에 인접한 상태로 제공되어야 한다. 부속서 C 에 규정하는 밀봉시험을 만족해야 한다. 평가된 밀봉 장치는 기기 제조자가 제공한 사용설명서에 따라 설치자 또는 기기의 사용자가 적용할 수 있다. 비고 밀봉 장치는 장치가 용기에 직접적으로 또는 커플링에 필요한 보조장치(accessory necessary for coupling)를 통해 고정될 때 내압방폭용기의 인입부에 즉시 장착된 것으로 간주된다. 실링 컴파운드 및 적용 방법은 스토핑 박스 또는 완성된 내압방폭용기의 인증서에 명시되어야 한다. 실링 컴파운드와 내압방폭용기 사이의 스토핑 박스 부분은 내압방폭용기로 취급한다. 즉, 접합부는 5 절의 요구사항을 만족하여야 하고, 조립부체는 15.3 에 따라 폭발 인화시험을 실시해야 한다. 용기(또는 최종 용도의 용기)와 가장 가까운 밀봉면에서 용기(또는 최종 용도의 용기) 외벽까지의 거 리는 가능한 한 작아야 하며 전선관의 크기 또는 50mm 중 더 작은 값 이하이어야 한다. 13.6 플러그와 소켓 및 케이블 커플러(Plugs and sockets and cable couplers) 13.6.1 내압방폭용기에 부착된 플러그 및 소켓은 플러그 및 소켓의 두 부분이 분리되어 있어도 장착 되는 용기의 내압방폭 특성을 변경시키지 않도록 구성 및 장착되어야 한다. 13.6.2 플러그와 소켓 및 케이블 커플러의 내압방폭용기의 내압방폭 접합부 길이 및 틈새(5 절 참조) 는 접지 또는 본딩 또는 KS C IEC 60079-11 을 따르는 회로의 부품 접촉부(contacts) 이외의 접촉부가 분리되는 순간에 존재하는 부피에 의해 결정되어야 한다. 31 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
0031f338-924f-47af-9c3a-1fbea9d24e3b | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 13.6.3 플러그와 소켓 및 케이블 커플러의 경우, 플러그와 소켓 또는 케이블 커플러가 함께 연결되었 을 때와 접지 또는 본딩 또는 KS C IEC 60079-11 을 따르는 회로의 부품 접촉부 이외의 접촉부가 분 리되는 순간 모두 내부에서 폭발이 발생하였을 때 내압방폭 특성이 유지되어야 한다. 13.6.4 부하의 스위칭(switching of the load)과 플러그와 소켓의 분리 사이에 시간 지연을 보장하는 인 터록 스위치에 연결되지 않은 경우, 플러그와 소켓은 정격 전압과 정격 전류의 시험회로를 개방하는 동안 아크 소호 기간(arc-quenching period)까지 내압방폭 성능을 유지하여야 한다. 교류 회로의 경우, 시험회로의 역률은 기기에 저항성 부하만 연결하도록 표시되어 있지 않은 한 0.6 이하이어야 한다. 13.6.5 13.6.2 에서 13.6.4 까지의 요구사항은 11.1 에 따른 특수 패스너로 함께 고정되고 표 14, b)에 따른 표시가 있는 플러그와 소켓 또는 케이블 커플러에는 적용하지 않는다. 13.7 부싱(Bushings) 부싱은 일체형이든 분리형이든 상관없이 이 표준의 요구사항, 부속서 C 의 관련 요구사항을 충족해야 하며 용기상에 5 절에서 규정한 접합부 길이 및 틈새를 만족하여야 한다. 부싱이 용기와 일체형이거나 용기에 특정된 경우, 부싱은 해당 용기의 일부로서 시험하여야 한다. 부싱이 분리형인 경우, 다음과 같아야 한다. a) 그룹 I 또는 그룹 II 용 나사형 방폭기기 부싱과 그룹 I 용 비나사형 방폭기기 부싱은 기기로 평가할 수 있다. 이러한 부싱은 15.2 의 시험 또는 16 절의 일상시험을 실시할 필요는 없다. b) 다른 부싱은 방폭부품으로만 평가할 수 있다. c) 해당하는 경우, 13.2 또는 13.3 에 따라 구멍에 쉽게 장착할 수 있도록 설명서에 충분한 정보를 제 공하여야 한다. 13.8 블랭킹 엘리먼트(Blanking elements) 제조자의 결정에 따라 내압방폭용기에 제공된 인입부가 상시 사용을 의도하는 것이 아닌 경우, 내압 방폭용기의 성능이 유지되도록 방폭기기 블랭킹 엘리먼트 또는 방폭부품 블랭킹 엘리먼트로 막아야 한다. 방폭기기 또는 방폭부품 블랭킹 엘리먼트는 부속서 C 를 만족해야 한다. 방폭부품 블랭킹 엘리먼트는 해당 방폭기기 인증서에 명시된 것만 사용이 적합하다. 블랭킹 엘리먼트는 나사 어댑터와 함께 사용해서는 안 된다. 해당하는 경우, 13.2 또는 13.3 에 따라 구멍에 쉽게 장착할 수 있도록 설명서에 충분한 정보를 제공 하여야 한다. 14 검증 및 시험(Verification and tests) 내압방폭구조 "d"의 경우, 검증 및 시험에 관한 KS C IEC 60079-0 의 요구사항에 아래의 요구사항들을 추가 적용한다. KS C IEC 60079-0 에 명시된 최고표면온도의 결정은 이 표준의 표 6 에 정의 된 조건 하에서 실시하여 32 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
1c5bfa90-d8ad-495c-9c91-b0553c42e977 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 야 한다. 표 6- 최고표면온도 결정 조건 ¦ 전기기기의 유형 ¦ 과부하 또는 오작동 상태 ¦ ¦ --- ¦ --- ¦ ¦ 등기구(안정기 없음.) ¦ 없음. ¦ ¦ 전자기식 안정기(electro-magnetic ballasts) 등기구 ¦ Un + 10% 다이오드로 모의 시험 한 정류기 영향 ¦ ¦ 전기식 안정기(electronic ballasts) 등기구 ¦ 산업기기에 대한 해당 표준에 명시된 조건 ¦ ¦ 전동기(motors) ¦ 없음. ¦ ¦ 저항기 (resistors) ¦ 없음. ¦ ¦ 전자석 (electromagnets) ¦ Un 및 최악의 공극(worst-case air-gap) 상태 ¦ ¦ 기타 기기 ¦ 산업기기에 대한 해당 표준에 명시된 조건 ¦ ¦ 비고 시험 전압 및 전류는 KS C IEC 60079-0 의 최고표면온도 요구사항을 참조할 것. ¦ 비고 시험 전압 및 전류는 KS C IEC 60079-0 의 최고표면온도 요구사항을 참조할 것. ¦ 15 형식 시험(Type tests) 15.1 일반사항(General) 형식 시험은 다음 순서에 따라 수행하여야 한다. a) KS C IEC 60079-0 에 따라 용기에 대한 시험을 수행한 또는 수행하지 않은 한 개의 시료에 대하여 15.2.2 에 따라 폭발압력(기준압력)을 결정; b) KS C IEC 60079-0 에 따라 용기에 대한 시험을 수행한 시료 중 하나에 대해 15.2.3 에 따라 내압시 험(overpressure test)을 실시; 그리고 c) 한 개의 시료에 대하여 15.3 에 따라 내부 점화에 의한 인화시험을 실시하되 이때 이 시료는 KS C IEC 60079-0 에 따른 용기에 대한 시험을 수행한 또는 수행하지 않은 그리고 위 b) 시험을 수행한 또는 수행하지 않은 시료 일 수 있다. 비금속 용기 또는 용기의 비금속 부분에 대해서는, 위의 시험 순서를 이 표준의 비금속 용기 및 용 기의 비금속 부분에 대한 요구사항에 따라 수정한다. 시험의 순서는 정적 또는 동적 내압시험을 인화시험 후 또는 시료의 기계적 강도에 영향을 미치는 다른 시험을 이미 적용한 다른 시료에 대해 실시할 수 있다는 점에서 위 시험 순서와 다를 수 있다. 어떠한 경우에도 내압시험 후 용기의 접합부는 영구 변형이 없어야 하며 용기에는 방폭구조에 영향 을 미치는 손상이 없어야 한다. 용기는 일반적으로 내부에 모든 기기가 장착된 상태로 시험하여야 한다. 다만, 이와 동등한 것으로 대체할 수도 있다. 용기가 제조자가 명시한 상세한 장착 배열로 다른 유형의 기기 및 부품을 사용할 수 있도록 설계된 경우, 용기를 빈 채로 시험하는 것이 폭발 압력의 형성에 가장 엄격한 조건이며 KS C IEC 60079-0 의 다른 안전 요구사항을 준수한다면 용기를 빈 채로 시험할 수 있다. 용기가 내부 부품의 일부가 없는 상태에서 사용할 수 있도록 설계된 경우, 가장 엄격하다고 판단되 는 조건에서 시험을 실시하여야 한다. 두 경우 모두, 인증서에 내부에 설치가 허용되는 기기의 종류 와 설치방법을 명시하여야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 33 | {}
1167f488-4e47-4eeb-a404-ce8e4335b339 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 내압방폭용기의 탈착이 가능한 부품의 접합부는 최악의 조립 조건에서 시험되어야 한다. 15.2 용기의 내압시험(Tests of ability of the enclosure to withstand pressure) 15.2.1 일반사항(General) 이 시험의 목적은 용기가 내부 폭발의 압력을 견딜 수 있는지 확인하는 것이다. 용기는 15.2.2 및 15.2.3 에 따라 시험되어야 한다. 이 시험은 용기의 방폭성능을 무효화시키는 영구 변형이나 손상이 발생하지 않을 경우 만족스러운 것으로 간주한다. 또한 접합부는 영구적으로 확대되어서는 안 된다. 15.2.2 폭발 압력(기준압력)의 결정(Determination of explosion pressure (reference pressure)) 15.2.2.1 일반사항(General) 기준압력은 이 시험 동안 관찰된 대기 압력에 대한 최대평활압력(maximum smoothed pressure)의 최 고 값이다. 평활(smoothing) 처리에는 5 kHz 土 0.5 kHz 의 3 dB 포인트를 갖는 로우 패스 필터(low- pass filter)를 사용하여야 한다. -20 °C 미만의 주위온도(ambient temperature)에서 사용하기 위한 전기기기의 경우, 기준압력은 다음 방법 중 하나에 의해 결정한다. - 모든 전기기기에 대하여, 기준압력을 최소 주위온도보다 높지 않은 온도에서 결정한다. 모든 전기기기에 대하여, 기준압력을 표준 주위온도(normal ambient temperature)에서 결정하되 증 가된 압력의 규정된 시험 혼합물을 사용하여 결정한다. 시험 혼합물의 절대압력(absolute pressure) (P, kPa)은 Ta.min(°C)을 사용하여 다음 식에 따라 계산한다. P= 100[293 / (Ta,min+ 273)] kPa 용기의 빈 체적이 3 L 이하인 단순한 내부 형상(부속서 D 참조)의 압력중첩(pressure-piling)이 발 생하지 않을 것으로 간주되는 회전 전기기기(전동기, 발전기 및 회전 속도계 등) 이외의 전기기기 에 대하여, 기준압력은 규정된 시험 혼합물을 사용하여 표준 주위온도에서 측정하되 표 7 에 제시 된 "감소된 주위 조건에 대한 시험계수"에 의해 증가된 기준압력을 갖는 것으로 가정해야 한다. 용기의 빈 체적이 10 L 이하인 단순한 내부 형상(부속서 D 참조)의 압력중첩이 발생하지 않을 것 으로 간주되는 회전 전기기기(전동기, 발전기 및 회전 속도계 등) 이외의 전기기기에 대하여, 기준 압력은 규정된 시험 혼합물을 사용하여 표준 주위온도에서 측정하되 표 7 에 제시된 "감소된 주위 조건에 대한 시험계수"에 의해 증가된 기준압력을 갖는 것으로 가정해야 한다. 이 대안 하에서, 15.2.3.2 에 따른 내압시험을 위한 시험 압력은 증가된 기준압력의 4 배가 되어야 한다. 1.5 배의 일 상시험은 허용되지 않는다. 표 7 - 감소된 주위 조건에 대한 시험계수 ¦ 최저 주위온도 °C ¦ 시험계수 ¦ ¦ --- ¦ --- ¦ ¦ ≥ -20 (비고 참조) ¦ 1.0 ¦ ¦ ≥-30 ¦ 1.37 ¦ ¦ ≥-40 ¦ 1.45 ¦ ¦ ≥-50 ¦ 1.53 ¦ ¦ ≥ -60 ¦ 1.62 ¦ 34 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
ad5f0556-c28d-4e75-aa17-897a973afa93 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 ¦ 비고 이 표는 KS C 에서 ¦ IEC 60079-0 에 명시된 표준 주위온도 범위(standard ambient temperaturerange) 사용하도록 설계된 기기에 적용한다. ¦ ¦ --- ¦ --- ¦ ¦ 내압방폭용기 내부의 온도가 ¦ 정격 주위온도보다 현저히 낮을 수 있는 경우를 고려해야 한다. ¦ 15.2.2.2 각 시험은 용기 내부의 폭발성 혼합물을 점화시키고 폭발에 의해 발생되는 압력을 측정하는 것으로 구성된다. 혼합물은 하나 또는 그 이상의 점화원에 의해 점화되어야 한다. 그러나 용기 안에 폭발성 혼합물을 점화시킬 수 있는 스파크를 생성시키는 장치가 있는 경우, 이 장치를 사용해 폭발을 일으킬 수 있다 (이때, 장치의 최대 설계 전력을 사용할 필요는 없다). 폭발 중에 발생되는 압력을 각 시험 중에 측정하고 기록하여야 한다. 점화원의 위치와 압력 기록 장 치의 위치는 최고 압력을 발생시키는 조합을 찾기 위해 시험소의 재량에 맡긴다. 분리 가능한 개스 킷이 제조자에 의해 제공될 때, 이를 용기에 장착한 상태로 시험해야 한다. 회전 장치와 같이 심각한 난류를 발생시켜 기준압력의 증가를 야기할 수 있는 용기 내부 장치에 의 한 지속적인 영향을 고려하여야 한다. 15.2.2.3 을 참조 시험 횟수 및 사용되는 폭발성 혼합물(대기압에서 공기와 의 부피비)은 다음과 같다. - 그룹 I 전기기기: (9.8±0.5) % 메탄으로 3 회 시험 - 그룹 IIA 전기기기: (4.6±0.3) % 프로판으로 3 회 시험 - 그룹 IIB 전기기기: (8±0.5) % 에틸렌으로 3 회 시험 - 그룹 IIC 전기기기: (14±1) % 아세틸렌으로 5 회 시험 및 (31 ±1) % 수소로 5 회 시험 15.2.2.3 회전 전기기기는 정지 및 구동 상태로 시험하여야 한다. 구동 시험을 실시할 경우, 자체 동 력 또는 보조 모터에 의해 구동시킬 수 있다. 최소 시험 속도는 기기의 최대 정격속도의 90 % 이상 이어야 한다. 비고 모터가 컨버터 구동형인 경우, 제조자 지정 정격속도는 종종 현재 및 향후 컨버터의 응용 모두 를 포함한다. 모든 모터는 적어도 2 개의 압력센서(transducers)로 시험하여야 하며, 하나는 모터 각 끝 부분의 엔드 턴 영역(end-turn area)에 위치시킨다. 점화는 차례대로 모터의 양쪽 끝에서 모터가 정지 및 작동할 때 시작되어야 한다. 이렇게 하면 최소 일련의 4 회 시험이 수행된다. 모터와 연결되어 있으나 밀봉되 지 않은 단자함이 있는 경우에는 3 개의 압력센서를 설치하고 추가 시험을 고려해야 한다. 15.2.2.4 그룹 IIB 의 경우, 내압방폭용기의 시험 중 압력중첩이 발생할 수 있는 경우, 해당 가스 그룹 에 대해 15.2.2.2 의 각 가스로 최소 5 회 시험을 실시해야 한다. 그 후에 (24±1) % 수소/메탄 (85/15) 의 혼합물을 사용하여 최소 5 회 시험을 반복해야 한다. 비고 1 이 반복 시험을 수행할 필요성은 (1) 압력중첩이 발생하지 않을 경우, 에틸렌이 최악의 대표 압력을 초래하고 (2) 압력중첩이 발생하는 경우는 그렇치 않다는 원칙에 기초한다. 따라서 이러한 전제 하에서, 압력중첩이 발생할 경우, (24± 1) % 수소/메탄 (85/15)의 혼합물로 추가 시험을 포함한다. 비고 2 (1) 동일한 환경 설정에서 일련의 시험 중에 측정된 압력 값이 1.5 배 이상으로 차이나거나 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 35 | {}
4aae1920-e0f7-489e-842f-369219dee5a0 | KSCIEC60079-1_2024확인_KR | KS CIEC 60079-1:2014 (2) 압력 상승시간(pressure rise time)이 5 ms 미만인 경우에 압력중첩이 있는 것으로 가정한 다. 아래 2 개의 그래프는 압력 상승 시간을 어떻게 고려해야 하는지에 대한 지침을 제공한다. 아래 두 그래프를 참조할 때 압력상승시간은 압력의 최대 상승률 지점에서 경과 시간을 기 준으로 한다. 이는 보통 최대 압력의 10 %와 90 % 사이에서 경과 된 시간이다. 실제 파형은 그림 23 과 같이 규칙적인 모양을, 또는 그림 24 처럼 불규칙한 모양을 나타낼 수 있다. 압력 상승 시간을 결정할 때, 그림 24 의 파형 시작부분의 완만한 부분은 제외한다. Chart Type: bar 입력 상승 시간 압력 샹승 률 보건 ᆞ 폿발 입력 곡선 0% 0% 100% 압력 상승 시간 0% 100% 0% 그림 24 - 비규칙적인 파형의 예 15.2.2.5 단일 가스용으로 표기된 전기기기의 경우, 최고 폭발 압력을 형성할 수 있는 대기압의 공기 와 해당 가스의 혼합물로 최소 5 회 폭발 시험을 실시해야 한다. 이러한 전기기기는 해당 기기 그룹 이 아닌 단일 가스에 대해서만 평가하여야 한다. 비고 폭발 압력이 가장 높은 공기와 의 혼합물을 결정하기 위해 인화 가능범위에서 실시한 일련의 시험이 사용된다. 특정 가스의 배제가 요구되는 경우, 인증번호는 KS C IEC 60079-0 의 표시 요구사항에 따라 'X' 접미 사를 포함하여야 하며 인증서의 특정사용조건에 이 배제 사항을 자세히 설명하여야 한다. 용기가 특정 가스에 대한 시험뿐만 아니라 이 가스의 하위 가스 그룹에 대한 시험을 실시한 경우, 특정 가스 및 하위 가스 그룹에 대한 이중 표시(double marking)를 적용할 수 있다(예: IIB + H2). 15.2.3 내압시험(Overpressure test) 36 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
aae613b8-1917-4205-b24c-32c1981fe533 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 15.2.3.1 일반사항(General) 이 시험은 동등하다고 판단되는 다음 방법 중 한 가지 방법으로 실시하여야 한다. 15.2.3.2 내압시험 - 첫 번째 방법(정적)(Overpressure test - First method (static)) 적용하는 상대 압력은 다음과 같다. 기준압력의 1.5 배; 또는 - 일상내압시험(routine overpressure testing)을 적용하지 않는 용기의 경우, 기준압력의 4 배; 또는 - 일상내압시험이 일괄시험(batch test)으로 대체된 용기의 경우, 기준압력의 3 배(16.6 참조); 또는 기기가 작아 기준압력을 결정하기 곤란한 경우, 표 8 에서 주어진 압력. 표 8- 소형 기기에 대한 상대 압력 ¦ 체적 cm3 ¦ 그룹 ¦ 압력 a kPa ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ ≤10 ¦ 1, IIA, IIB, IIC ¦ 1 000 ¦ ¦ >10 ¦ I ¦ 1 000 ¦ ¦ >10 ¦ IIA, IIB ¦ 1 500 ¦ ¦ >10 ¦ IIC ¦ 2 000 ¦ ¦ a -20 °C 이하의 주위온도에 사용되도록 설계된 기기의 경우, 상기 압력은 표 7 에 명시된 시험 계 수에 의해 증가되어야 한다. ¦ a -20 °C 이하의 주위온도에 사용되도록 설계된 기기의 경우, 상기 압력은 표 7 에 명시된 시험 계 수에 의해 증가되어야 한다. ¦ a -20 °C 이하의 주위온도에 사용되도록 설계된 기기의 경우, 상기 압력은 표 7 에 명시된 시험 계 수에 의해 증가되어야 한다. ¦ 압력의 인가 시간은 10 초 이상이어야 한다. 시험은 해당하는 경우, 각 시료에 대해 한 번 수행한다. 내압시험은 시험 결과 가 15.2.1 에 적합하고 용기의 벽면을 통한 누설이 없는 경우, 만족스러운 것으 로 간주한다. 비고 이러한 시험을 위해 일반적으로 비압축성 매체가 사용된다. 공기 또는 불활성 가스와 같은 압 축성 매체를 사용하는 경우 용기의 파괴는 신체적 상해나 재산 피해를 야기할 수 있다. 15.2.3.3 내압시험 - 두 번째 방법(동적)(Overpressure test - Second method (dynamic)) 동적 시험은 용기에 가하는 최대 압력이 기준압력의 1.5 배가 되도록 수행한다. 15.2.2.2 에서 규정된 혼합가스로 시험을 수행할 때, 기준압의 1.5 배에 해당하는 폭발 압력이 형성되 도록 혼합가스를 미리 압축할 수 있다. 시험은 1 회만 실시회되 그룹 IIC 의 전기기기에 대해서는 각 가스에 대해 3 회씩 실시한다. 비고 상호 연결된 챔버를 가진 제품의 경우, 각 구획(compartment)에서 반드시 한번의 점화가 시작 될 필요는 없다. 필요하다고 고려되는 각 구성에 대해 시험을 실시한다. 한 구획에서의 높은 압력은 전파(propagation) 가능성을 줄이는 반면 낮은 압력은 전파 가능성을 높일 수 있다. 내압시험은 15.2.1 에 적합할 경우, 만족스러운 것으로 간주한다. 37 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
3963e969-68c1-4f9d-a9cd-7717f6349fd9 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 15.3 내부 점화에 의한 인화시험(Test for non-transmission of an internal ignition) 15.3.1 일반사항(General) 개스킷(5.4 참조)은 제거되어야 한다. 약간의 그리스가 남아 있을 수 있지만, 과도한 그리스는 제거되 어야 한다(5.1 참조). 용기를 시험 챔버 안에 넣는다. 동일한 폭발성 혼합물을 동일한 압력에서 용기 와 시험 챔버에 유입시킨다. 시료의 나사 접합부 화염경로의 길이[체결(engagement)]는 표 9 에 따라 감소되어야 한다. 시료의 마개, 원통 및 플랜지 접합부 화염경로의 길이는 제조자가 명시한 최소 길이의 115 %를 초과 하지 않아야 한다. 접합부의 길이(L)가 원통부로만 구성(그림 2b 참조)된 마개 접합부의 평면부 틈새는 그룹 I 및 그룹 IIA 의 경우 1 mm 이상의 값으로, 그룹 IIB 의 경우 0.5 mm 이상의 값으로, 그리고 그룹 IIC 의 경우 0.3 mm 이상으로 확대되어야 한다. 시험 시료의 틈새 요구사항은 15.3.2(그룹 1, 그룹 IIA 및 그룹 IIB 의 경우) 및 15.3.3(그룹 IIC 의 경우) 에 포함된다. 나사 접합부 이외의 화염경로가 있고 60 °C 이상의 주위온도에 사용하기 위한 기기의 경우, 인화시험 은 다음 조건 중 하나에 따라 수행한다. 명시된 최고 주위온도 이상의 온도; 또는 - 표 10 의 계수에 따라 증가된 압력에서 규정된 시험 혼합물을 사용하여 표준 주위온도; 또는 시험 틈새 iE 를 표 10 의 계수에 따라 증가시킨 상태로 표준 대기압 및 온도. 용기가 다른 온도 계수를 갖는 다른 재료로 구성되고 이것이 틈새 치수에 영향을 미치는 경우(예: 금속 프레임과 함께 원통 틈새를 형성하는 유리창의 경우), 다음 중 하나를 인화시험에 적용하여야 한다. 20 °C 에서의 최대 구조 틈새 및 명시된 최고 주위온도 Ta,max 에서 틈새의 확대를 고려하여 계산된 최대 틈새 ic,T 는 Ta,max 에서 계산된 최대 틈새의 90 % 이상으로 시험 틈새 iE 를 증가시킴으로써 검 증하여야 한다. 20 °C 에서의 최대 구조 틈새 및 명시된 최고 주위온도 Ta,max 에서 틈새의 확대를 고려하여 계산된 최대 틈새 iC,T 는 규정된 시험 혼합물을 다음 식에 따라 가압하여 검증하여야 한다. Pv = (iC,T/iE) x (0.9) 38 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
64e130cd-e21f-47e5-8145-436ef96b1c68 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 표 9- 인화시험을 위한 나사 접합부 길이의 감소 ¦ 나사 접합부 유형 ¦ 길이 감소 ¦ 길이 감소 ¦ 길이 감소 ¦ 길이 감소 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 나사 접합부 유형 ¦ 그룹 1, IIA, IIB 15.3.2 ¦ 그룹 1, IIA, IIB 15.3.2 ¦ 그룹 IIC 15.3.3 ¦ 그룹 IIC 15.3.3 ¦ ¦ 나사 접합부 유형 ¦ 15.3.2.1 ¦ 15.3.2.2 ¦ 15.3.3.2 ¦ 15.3.3.3 또는 15.3.3.4 ¦ ¦ 나사산의 형태 및 끼워맞춤 품질이 보통급 이 상으로 ISO 965-1 및 ISO 965-3 에 부합하는 원 통형 ¦ 감소 없음. ¦ 감소 없음. ¦ 감소 없음. ¦ 감소 없음. ¦ ¦ 나사산의 형태 또는 끼워맞춤 품질이 ISO 965- 1 및 ISO 965-3 에 부합하지 않는 원통형 ¦ 1/3 ¦ 1/2 ¦ 1/2 ¦ 1/3 ¦ ¦ NPT ¦ 감소 없음. ¦ 감소 없음. ¦ 감소 없음. ¦ 감소 없음. ¦ 표 10 - 압력 또는 시험 틈새(iE)를 증가시키기 위한 시험계수 ¦ 최대 온도 °C ¦ 그룹 I 12.5 % CH4/H2 ¦ 그룹 IIA 55 % H2 ¦ 그룹 IIB 37 % H2 ¦ 그룹 IIC 27.5 % H2 7.5% C2H2 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 60 ¦ 1.00 ¦ 1.00 ¦ 1.00 ¦ 1.00 ¦ ¦ 70 ¦ 1.06 ¦ 1.05 ¦ 1.04 ¦ 1.11 ¦ ¦ 80 ¦ 1.07 ¦ 1.06 ¦ 1.05 ¦ 1.13 ¦ ¦ 90 ¦ 1.08 ¦ 1.07 ¦ 1.06 ¦ 1.15 ¦ ¦ 100 ¦ 1.09 ¦ 1.08 ¦ 1.06 ¦ 1.16 ¦ ¦ 110 ¦ 1.10 ¦ 1.09 ¦ 1.07 ¦ 1.18 ¦ ¦ 120 ¦ 1.11 ¦ 1.10 ¦ 1.08 ¦ 1.20 ¦ ¦ 125 ¦ 1.12 ¦ 1.11 ¦ 1.09 ¦ 1.22 ¦ 그룹 IIC 의 경우, 15.3.3 에 따른 시험계수는 위의 시험계수와 더불어 시험 압력 또는 시험 틈새에 적 용되어야 한다. 단일 가스용으로 표시된 전기기기는 고려된 단일 가스가 해당하는 기기 그룹에 기초하여 인화시험을 수행하여야 한다. 기기가 표 11 에서 명시된 거리보다 짧은 거리에서 시험이 된 경우, 이 기기의 인증서에 장애물의 최 소 거리를 명시하여야 한다. 또한 기기는 표 15 에 따라 표시할 수 있다. 표 11 - 내압방폭구조 "d" 플랜지 개구부에서 장애물까지의 최소 거리 ¦ 가스 그룹 ¦ 최소 거리 mm ¦ ¦ --- ¦ --- ¦ ¦ IIA ¦ 10 ¦ ¦ IIB ¦ 30 ¦ ¦ IIC ¦ 40 ¦ 비고 KSCIEC 60079-14 는 플랜지(평면) 접합부가 있는 방폭구조 "d"로 설계된 기기의 설치를 제한 한다. 구체적으로, 기기가 해당 조건으로 시험되지 않은 한, 플랜지 접합부는 표 11 에 명시한 치수보다 기기의 일부가 아닌 고형 물체(solid objects)에 더 가까이 설치해서는 안 된다. 39 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f1b4e774-0bba-4021-b482-efba89217477 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 비고 단순 형상 이외의 경우, 여러번의 시험 구성(multiple test configurations)을 사용하여 인화여부를 확인한다. 15.3.2 그룹 1, IIA 및 IIB 전기기기(Electrical equipment of Groups 1, IIA and IIB) 15.3.2.1 용기의 시험 틈새 iE 는 제조자의 도면에 명시된 최대 구조 틈새 ic 의 90% 이상이어야 한다 (0.9 ic≤ iES ic). 사용되는 폭발성 혼합물의 대기압에서 공기와 의 체적비는 다음과 같다. - 그룹 I 전기기기: (12.5±0.5) % 메탄-수소[(58± 1) % 메탄 및 (42± 1)% 수소](MESG = 0.8 mm) - 그룹 IIA 전기기기: (55 ±0.5) % 수소(MESG = 0.65 mm) - 그룹 IIB 전기기기: (37 ±0.5) % 수소(MESG = 0.35 mm) 비고 이 시험을 위해 선택된 폭발성 혼합물은 접합부가 알려진 안전여유(margin of safety)를 가지고 내 부 폭발에 의한 화염의 전파를 방지함을 보장한다. 이 안전여유 K 는 해당 그룹 대표 가스의 최 대실험안전틈새(maximum experimental safe gap)와 선택된 가스의 최대실험안전틈새의 비이다. 1.14 그룹 I 전기기기: K= = 1.42(메탄) 0.8 0.92 - 그룹 IIA 전기기기: K= = 1.42(프로판) 0.65 0.65 그룹 IIB 전기기기: K= = 1.85(에틸렌) 0.35 대안으로, 시험 시료의 틈새가 위의 조건을 충족시키지 못할 경우, 다음 방법 중 하나를 사용하여 내 부 점화에 의한 인화시험을 실시할 수 있다. 표 12 에 주어진 것보다 작은 MESG 값을 갖는 가스/공기 혼합물 표 12 - 가스/공기 혼합물 ¦ 그룹 ¦ iE/ic ¦ 혼합물 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 그룹 I ¦ ≥0.75 ≥0.6 ¦ (55 ± 0.5) % 수소 (50 ±0.5) % 수소 ¦ ¦ 그룹 IIA ¦ ≥0.75 ≥0.6 ¦ (50 ±0.5) % 수소 (45 ±0.5) % 수소 ¦ ¦ 그룹 IIB ¦ ≥0.75 ≥0.6 ¦ (28 ± 1.0) % 수소 (28 ± 1.0) % 수소 절대압력 140 kPa 에서 ¦ - 다음 공식에 따라 정상 시험 혼합물을 선가압 Pk = °Cx0.9 iE 여기에서 Pk : 선가압 계수(precompression factor) 40 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
6de3dfc6-29b6-4731-94e6-268910a41f5a | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 15.3.2.2 그룹 IIA 와 그룹 IIB 의 용기가 15.3.2.1 의 시험으로 인해 파괴되거나 손상될 수 있는 경우, 제조자가 명시한 최대 값 이상으로 틈새를 증가시켜 시험을 수행할 수 있다. 틈새의 확대 계수는 그 룹 IIA 전기기기의 경우 1.42, 그룹 IIB 의 전기기기의 경우는 1.85 이다. 용기 및 시험 챔버에서 사용 되는 폭발성 혼합물은 대기압에서 공기와 의 체적비는 다음과 같다. - 그룹 IIA 전기기기: (4.2±0.1) % 프로판 - 그룹 IIB 전기기기: (6.5± 0.5) % 에틸렌 15.3.2.3 15.3.2.1 또는 15.3.2.2 에 따른 시험은 각 시험 배치를 고려하여 5 회 실시하여야 한다. 점화 가 시험 챔버로 전파하지 않으면 시험 결과 가 만족스러운 것으로 간주한다. 15.3.3 그룹 IIC 전기기기(Electrical equipment of Group IIC) 15.3.3.1 일반사항(General) 이 시험에는 15.3.3.2, 15.3.3.3 또는 15.3.3.4 의 시험을 사용할 수 있으며, 점화가 시험 챔버로 전달되 지 않으면 만족스러운 것으로 간주한다. 비고 아래의 방법은 안전계수 1.5 및 최소 시험 틈새 90 %와 동등하다. 이것은 압력을 높이거나 시 험 틈새 치수를 늘리거나 시험 혼합물의 산소를 증가시킴으로써 이루어진다. 15.3.3.2 첫 번째 방법 - 시험 틈새 증가에 의한 시험(First method - Testing by increased test gap) 나사 접합부 이외의 접합부의 모든 틈새는 1.35 ic≤ie≤1.5ic 로 증가시키되 플랜지 접합부는 최소 0.1 mm 이상으로 한다. 여기에서 iE : 시험 틈새 ic : 제조자의 도면에 명시된 최대 구조 틈새 대기압에서 공기와 의 체적비가 다음과 같은 폭발성 혼합물을 용기 및 시험 챔버에 사용하여야 한다. a) (27.5± 1.5) % 수소 b) (7.5± 1) % 아세틸렌 각 시험 배치를 고려하여 5 회의 시험을 각 혼합물에 대하여 실시하여야 한다. 기기가 수소 단독 또 는 아세틸렌 단독 사용을 목적으로 하는 경우, 시험은 해당 가스 혼합물로만 수행하여야 한다. 비고 롤러 베어링(roller element bearings)을 사용하는 회전기기의 샤프트 글랜드 원통 접합부가 있는 시험 시료를 준비할 때, 시험 틈새 iE 는 8.2.2 에 따른 반지름 틈새가 아닌 표 2 또는 표 3 의 지 름 틈새를 기준으로 한다. 15.3.3.3 두 번째 방법 - 압력 증가에 의한 시험(Second method - Testing by increased pressure) 용기는 다음 식에 따라 시험 틈새 iE 로 시험하여야 한다. 0.9 ic≤iE≤ic 대기압의 1.5 배에 해당하는 압력으로 첫 번째 방법에 대해 특정된 가스 혼합물 중 하나로 용기와 시 험 챔버를 채운다. 41 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
faf68488-b026-4a10-b1e4-56c6ed1e5552 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 시험은 각 폭발성 혼합물에 대해 5 회 실시하여야 한다. 또는 시험 시료의 틈새가 위의 조건을 충족시키지 못할 경우, 다음 방법을 사용할 수 있다. 다음 공식에 따라 표준 시험 혼합물의 선가압: Pk = 드 x1.35 iE 여기에서 Pk:선가압 계수 비고 롤러 베어링을 사용하는 회전기기의 샤프트 글랜드 원통 접합부가 있는 시험 시료를 준비할 때, 시험 틈새 iE 는 8.2.2 에 따른 반지름 틈새가 아닌 표 2 또는 표 3 의 지름 틈새를 기준으로 한다. 15.3.3.4 세 번째 방법 - 시험 가스의 산소 농축에 의한 시험(Third method - Testing by oxygen enr ichment of test gases) 용기의 시험 틈새 iE 는 제조자의 도면에 명시된 최대 구조 틈새 ic 의 90 % 이상이어야 한다(0.9ic����ic). 사용되는 시험 혼합물의 대기압에서 공기와 의 체적비는 다음과 같다. a) (40 ± 1) % 수소, (20±1) % 산소 및 나머지는 질소 b) (10 ± 1) % 아세틸렌, (24± 1) % 산소 및 나머지는 질소 시험은 각 시험 혼합물에 대해 5 회 실시하여야 한다. 수소에서만 사용을 목적으로 하는 기기의 경우, 시험 혼합물 a)로만 실시한다. 15.3.3.5 단일 생산 제품에 대한 시험 횟수(Number of tests for single piece production) 단일 생산 제품의 전기기기는 변화 없는 시험 틈새 및 대기압에서 15.3.3.2 에 규정된 각각의 폭발성 혼합물로 5.1 의 치수 요구사항을 적용하여 각 시험 구성을 고려하여 총 5 회 시험을 실시하여야 한다. 15.4 통기 및 배수 장치가 있는 내압방폭용기의 시험(Tests of flameproof enclosures with breathing and draining devices) 15.4.1 일반사항(General) 10.7.2 의 충격시험 후 시료에 대하여 다음의 순서로 15.4.2 에서 15.4.4 까지의 시험을 실시하여야 한다. 경로를 측정할 수 없는 장치의 경우, 시료의 최대기포시험기공크기(maximum bubble test pore size)는 명시된 최대기포시험기공크기의 85 % 이상이어야 한다. 부속서 B 참조 15.4.2 용기의 내압시험(Tests of ability of the enclosure to withstand pressure) 15.4.2.1 시험은 15.2 에 따라 다음과 같은 추가 및 수정을 통해 이루어져야 한다. 15.4.2.2 15.2.2 에 따라 폭발 압력을 결정하기 위해 통기 및 배수 장치는 플러그(solid plugs)로 교체 해야 한다. 42 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
a520f7e4-6675-4f85-90f6-94f84a0a524b | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 15.4.2.3 15.2.3 에 따른 내압시험을 수행할 때 통기 및 배수 장치의 내부 표면에 얇은 가요성 멤브레 인(예: 얇은 플라스틱 시트)을 설치해야 한다. 내압시험 후, 장치는 방폭구조에 영향을 줄 수 있는 영 구 변형이나 손상이 없어야 한다. 비고 얇은 가요성 멤브레인의 목적은 장치의 강도에 영향을 미치지 않고 시험 중 누출을 최소화하 는 것이다. 15.4.3 온도시험(Thermal tests) 15.4.3.1 시험 절차(Test procedure) 장치(들)가 장착된 용기는 15.4.4.2 의 방법에 따라 시험해야 하지만 점화원은 가장 불리한 열적 결과 를 주는 위치에 놓고 시험하여야 한다. 장치(들)의 외부 표면의 온도를 시험 중 관찰하여야 한다. 시험은 5 회를 실시한다. 사용되는 시험 혼 합물은 대기압에서 공기와 의 체적비가 (4.2± 0.1) % 프로판을 사용한다. 추가적으로, 아세틸렌에 사용 하기위한 장치의 경우, 대기압에서 공기와 의 체적비가 (7.5±1.0) % 아세틸렌을 사용한다. 잠재적으로 위험한 가스의 강제된 또는 유도된 흐름이 발생할 수 있는 용기는 시험 중에 장치와 용 기를 통해 가스가 흐를 수 있도록 배치되어야 한다. 환기 또는 샘플링 시스템은 제조자의 문서에 명시된 대로 작동되어야 한다. 각 5 회의 시험 후, 외부 폭발성 혼합물을 충분한 시간 동안 유지하여 장치 표면에서 있을 수 있는 지속적인 연소가 가능하도 록 하여야 한다(예를 들어, 최소 10 분 동안 유지하여 장치의 외부 표면 온도를 높이거나 외부 표면으 로 열이 전달되도록 한다). 비고 10 분 시험 시간 후의 외부 표면 온도는 15.4.3.2 에 따라 온도등급을 결정하는 데 사용된다. 15.4.3.2 적합 기준(Acceptance criterion) 연속적인 연소는 관찰되지 않아야 한다. 화염이 전파되지 않아야 한다. 장치의 측정된 외부 표면 온 도 상승에 1.2 의 안전계수를 곱하고 장치의 최고서비스온도를 더하여 전기기기의 온도 등급을 결정 한다. 15.4.4 내부 점화에 의한 인화시험(Test for non-transmission of an internal ignition) 15.4.4.1 일반사항(General) 이 시험은 15.3 에 따라 다음과 같은 추가 및 수정을 통해 이루어져야 한다. 15.4.4.2 시험 절차(Test procedure) 점화원은 먼저 통기 및 배수 장치의 내부 표면 가까이에 배치한 후 장치의 표면에서 높은 피크 폭발 압력 및 압력 상승률이 발생할 가능성이 있다면 하나 이상의 위치에 배치하여야 한다. 용기에 2 개 이상의 동일한 장치가 설치된 경우, 시험할 장치는 가장 불리한 결과 를 주는 장치어어야 한다. 용기 내부의 시험 혼합물을 점화시킨다. 시험은 점화원의 각 위치에 대해 5 회 실시하여야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. 43 | {}
bef20a08-9313-4fde-a304-7a95b0255e4e | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 15.4.4.3 통기 및 배수 장치의 인화시험(Non-transmission test for breathing and draining devices) 15.4.4.3.1 일반사항(General) 그룹 1, 그룹 IIA 및 그룹 IIB 의 통기 및 배수 장치의 경우, 15.3.2 에 따른 인화시험을 적용해야 한다. 경로를 측정할 수 있는 그룹 IIC 의 통기 및 배수 장치의 경우, 15.3.3 에 따른 인화시험을 적용해야 한 다. 경로를 측정할 수 없는 그룹 IIC 의 통기 및 배수 장치의 경우, 15.4.4.3.2 또는 15.4.4.3.3 에 따른 인화시험을 적용해야 한다. 15.4.4.3.2 방법 A - 증가된 압력에 의한 시험(Method A - Testing by increased pressure) 시험은 각 시험 혼합물로 5 회 실시한다. 시험은 15.3.3.3 과 15.4.4.2 에 따라 수행한다. 수소에서만 사용하기 위한 장치의 경우, 수소/공기 혼합물을 사용한 시험만 실시한다. 15.4.4.3.3 방법 B- 시험 가스의 산소 농축에 의한 시험(Method B - Testing by oxygen enrichment of test gases) 체적이 100 cm3 이상인 용기의 경우, 이황화탄소는 제외된다. 사용되는 시험 혼합물의 대기압에서 체 적비는 다음과 같이 구성한다. a) (40 土 1) % 수소, (20± 1) % 산소 및 나머지는 질소; 및 b) (10 ± 1) % 아세틸렌, (24± 1) % 산소 및 나머지는 질소. 시험은 15.4.4.2 에 따라 각 시험 혼합물로 5 회 실시하여야 한다. 수소에서만 사용하기 위한 장치의 경우, 시험 혼합물 a)로만 실시한다. 15.4.4.4 적합 기준(Acceptance criterion) 화염이 시험 챔버로 전파되지 않을 경우, 시험 결과 가 만족스러운 것으로 간주한다. 15.5 "dc" 장치에 대한 시험(Tests for "dc" devices) 15.5.1 일반사항(General) 15.5 의 시험은 15.2 부터 15.4.4.4 까지의 시험을 대체한다. 15.5.2 "dc" 시료의 준비(Preparation of "dc" samples) 사용 중에 개방될 수 있거나 기계적 또는 환경적 손상으로부터 보호받지 못하는 덮개의 밀봉용 탄성 체(elastomeric) 또는 열가소성 물질은 제거된 상태에서 더 악조건의 시험이 될 경우, 장치 또는 부품 의 형식시험을 실시하기 전에 전체적으로 또는 부분적으로 제거되어야 한다. 비고 용기의 나머지 금속이 아닌 부분은 내열시험을 거쳐야 한다. 44 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
fe17bef1-6e98-4efe-ab05-4fc6af2cec1c | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 15.5.3 "dc" 장치의 시험 조건(Test conditions for "dc" devices) 15.5.3.1 일반사항(General) 제작 도면에서 허용되는 가장 불리한 치수를 갖도록 하여 장치 또는 부품을 아래의 폭발성 혼합물로 내부 및 외부를 채운다. 그룹 IIA: 대기압에서 (55±0.5) % 수소/공기 - 그룹 IIB: 대기압에서 (37 ±0.5) % 수소/공기 - 그룹 IIC: 대기압에서 (40 ± 1) % 수소, (20 ± 1) % 산소 및 나머지는 질소 또는 대안으로 대기압의 1.5 배로 가압된 (27.5± 1.5) % 수소/공기 15.5.3.2 시험 절차(Test procedure) "dc"의 경우, 장치 내부의 폭발성 혼합물은 전압, 전류, 주파수 및 역률의 면에서 최대 정격 에너지 원 및 최대 부하에 연결된 경우 폐쇄 접점의 작동에 의해 점화되어야 한다. 접점의 개로 및 폐로 시 험을 각 시험마다 신선한 폭발성 혼합물을 사용하여 10 회 실시하여야 하며 그 주위의 폭발성 혼합물 을 점화시키지 않아야 한다. 16 일상시험(Routine test) 16.1 일반사항(General) 16.1.1 다음의 일상시험은 용기가 압력을 견딜 수 있고 또한 외부로 연결되는 구멍이나 균열이 없는 지 확인하기 위한 시험이다. 일상시험은 15.2.3 의 형식 시험에 기술된 방법 중 하나에 따라 수행되는 내압시험을 포함한다. -20 °C 이하의 주위온도에서 사용하기 위한 기기의 경우, 정상 주위온도(normal ambient temperature)에서의 압력 시험으로 충분하다. 16.1.2 두 번째 방법으로 내압형식시험을 한 경우에도 첫 번째 방법으로 일상내압시험을 할 수 있다. 기준압력을 측정하기 불가능하거나 동적 시험 중에 기기에 포함된 부품(권선 등)이 손상될 우려가 있 을 경우, 적용될 정적 압력은 표 13 에 주어진다. 표 13 - 정적 압력 ¦ 체적 3 cm ¦ 그룹 ¦ 압력 b kPa ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ ≤10a ¦ 1, IIA, IIB, IIC ¦ 1 000 ¦ ¦ >10 ¦ I ¦ 1 000 ¦ ¦ >10 ¦ IIA, IIB ¦ 1 500 ¦ ¦ >10 ¦ IIC ¦ 2 000 ¦ ¦ a 용접 구조에만 적용 가능 ¦ a 용접 구조에만 적용 가능 ¦ a 용접 구조에만 적용 가능 ¦ b -20 °C 이하의 주위온도에 사용하기 위한 기기의 경우, 상기 압력은 표 7 에 명시된 적절한 시험 계수에 의해 증가되어야 한다. 45 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
e2978352-c9d2-4e20-9f63-ed9cd75ff997 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 16.1.3 두 번째 방법이 선택되는 경우, 일상시험은 다음과 같이 구성된다. 용기의 내부 및 외부에 대기압의 1.5 배에서 15.2.2 에 명시된 해당 폭발성 혼합물(폭발 압력의 결 정을 위한)로 폭발시험, 또는 용기의 내부에 대기압의 1.5 배에서 15.2.2 에 명시된 해당 폭발성 혼합물(폭발 압력의 결정을 위한) 로 폭발시험을 실시한 다음, 용기의 내부 및 외부에 대기압으로 15.3.2.2 또는 15.3.3.2(확대된 틈 새로 인화시험)에 명시된 폭발성 혼합물로 인화시험, 또는 대기압의 1.5 배에서 15.2.2 에 명시된 해당 폭발성 혼합물(폭발 압력의 결정을 위한)로 폭발시험을 실시한 다음, 최소 200 kPa 의 압력에서 정적 시험 실시. 16.1.4 일상시험의 경우, 비어 있는 용기로 시험해도 충분하다. 그러나 일상시험이 동적 방법이고 내 부에 설치된 기기가 내부 폭발과 정에서 압력 상승에 영향을 미치는 경우, 시험조건에 이러한 영향을 반영하여야 한다. 내압방폭용기의 개별 부품(예: 덮개 및 베이스)은 별도로 시험할 수 있다. 시험 조건은 응력이 이들 부품이 전체 용기에서 노출되는 응력과 동등한 수준이어야 한다. 비고 이러한 시험을 위해 일반적으로 비압축성 매체가 사용된다. 공기 또는 불활성 가스와 같은 압 축성 매체를 사용하는 경우, 용기의 파괴는 신체적 상해나 재산 피해를 야기할 수 있다. 16.2 용접 구조가 없는 용기(Enclosures not incorporating a welded construction) 용접 구조가 없는 용기의 경우, 다음 조건 중 하나에 해당하는 경우 일상내압시험을 실시하지 않을 수 있다. 체적이 10 cm3 이하인 경우; 또는 체적이 10 cm3 를 초과 하는 경우에 대해 규정된 형식 시험이 기준압력의 4 배에 해당하는 정적 압 력으로 실시한 경우. 16.3 용접 구조가 있는 용기(Enclosures incorporating a welded construction) 용접 구조를 포함하는 용기 또는 용기의 일부에 대한 용접 구조의 무결성(integrity)은 일상내압시험을 통해 검증되어야 한다. 대안으로, 용접 구조에 대한 일상내압시험이 현실적이지 못하고(용기의 구조적 이유와 같은) 용기가 4 배의 내압시험을 만족하는 경우, 용접의 무결성은 다음의 검사 방법 중 하나를 통해 검증될 수 있다. - 방사선투과 용접 검사 - 초음파탐상 용접 검사 - 자분탐상 용접 검사 침투탐상 용접 검사 비고 위의 각 용접 검사 방법에 대해 ISO 표준이 있다. 16.4 특정 내압방폭용기에만 적용되지 않는 부싱(Bushings not specific to one flameproof enclosure) 조립 절차가 충분히 문서화된 경우(C.2.1.4 참조), 하나의 내압방폭용기에만 사용되지 않는 부싱에 대 해서는 일상시험을 요구하지 않는다. 46 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
7a67e3a9-07dc-45ed-80b7-6ffbb7c21d41 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 16.5 적합 기준(Acceptance criteria) 일상시험은 다음과 같은 경우, 만족스러운 것으로 간주한다. a) 용기는 접합부의 영구 변형이나 용기의 손상 없이 압력을 견뎌야 하며 b) 일상시험이 동적 시험에 이어서 16.1.3 에 따른 정적 시험을 실시한 경우 용기의 벽을 통한 누설 이 없거나, 동적 시험을 실시한 경우 내부 점화에 의한 화염전파가 없어야 한다. 16.6 배치시험(Batch testing) 일상내압시험이 KS Q ISO 2859-1[5]에 기초한 다음 기준에 따라 배치시험으로 대체하는 경우: 최대 100 개의 생산 배치의 경우, 기준압력의 1.5 배에서 8 개의 샘플을 시험하고 부적합이 없어야 한다. 101 개에서 1 000 개의 생산 배치의 경우, 기준압력의 1.5 배에서 32 개의 샘플을 시험하고 부적합이 없어야 한다. 1 001 개에서 10 000 개의 생산 배치의 경우, 기준압력의 1.5 배에서 80 개의 샘플을 시험하고 부적 합이 없어야 한다. 10 000 개 이상의 배치는 작은 배치로 세분해야 한다. 시험결과 부적합이 발생할 경우, 배치에 남아 있는 모든 샘플의 100 %를 기준압력의 1.5 배에서 시험 해야 한다. 이후 배치는 배치시험의 신뢰성이 확보될 때까지 기준압력의 1.5 배에서 일상시험을 실시 하여야 한다. 비고 부적합 시험 결과 에 따라, 이 배치시험의 재실시 여부는 관련 인증서를 발행한 인증기관의 재 량에 맡긴다. 17 그룹 I 용 개폐장치(Switchgear for Group I) 17.1 일반사항(General) 예를 들어 조정 목적이나 보호 계전기 재설정과 같이 현장에서 때때로 개방되며 별도의 영향(예: 기 계적, 전기적, 전기 광학적, 공압, 음향, 자기적 또는 열적인)으로 회로가 개폐될 수 있는 원격으로 동 작되는 스위칭 장치를 포함하는(이때, 이러한 영향은 기기 자체에 수동으로 가하지 않음), 그리고 폭 발성 혼합물을 점화시킬 수 있는 작동 중 아크 또는 스파크(in-service arcs or sparks)가 발생하는 그 룹 I 내압방폭용기는 다음 사항을 준수해야 한다. 17.2 분리 수단(means of isolation) 17.2.1 일반사항(General) KS C IEC 60079-11 에 부합하는 본질안전회로 및 본딩(bonding) 또는 접지용 도체를 제외하고 접근 가능 한 모든 도체는 내압방폭용기를 개방하기 전에 공급 전원으로부터 분리(isolated)될 수 있어야 한다. 이러한 내압방폭용기의 분리 수단은 17.2.2, 17.2.3 또는 17.2.4 에 부합해야 한다. 17.2.2 분리 수단은 내압방폭용기의 내부에 설치되어야 하며, 분리 수단이 개방된 후에도 통전 상태 로 유지되는 부분은 다음 중 하나와 같아야 한다. 47 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
16ba4e50-8994-453f-a7e4-bbbd5d7c3bb7 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 KS C IEC 60079-0 에 열거된 EPL Mb 의 표준 방폭구조 중 하나에 의해 보호 KS C IEC 60079-7 의 요구사항에 따라 상(phases)과 접지(earth) 사이에 공간거리와 연면거리를 가 져야 하며, 적어도 IP20 의 보호 등급을 가진 용기로 보호되어 공구가 개구부를 통하여 통전부와 접촉할 수 없어야 한다. 이 요구사항은 KS C IEC 60079-11 에 적합한 통전 상태를 유지하는 부품 에는 적용하지 않는다. 두 경우 모두, 통전 상태를 유지하고 있는 부품을 보호하는 덮개에 표 14 의 c)에 따른 표시를 하여야 한다. 17.2.3 분리 수단은 KS C IEC 60079-0 에 열거된 EPL Mb 의 표준 방폭구조 중 하나를 준수하는 다른 용기 내부에 설치되어야 한다. 17.2.4 분리 수단은 13.3 의 요구사항을 준수하는 플러그 및 소켓 또는 케이블 커플러로 구성되어야 한다. 17.3 문 또는 덮개(Doors or covers) 17.3.1 단순조작 문 또는 덮개(Quick-acting doors or covers) 이러한 문 또는 덮개는 분리기(isolator)와 기계적으로 인터록(interlock)되어 다음과 같아야 한다. a) 분리기가 닫혀 있는 동안 용기는 내압방폭용기의 특성(방폭구조 "d")을 유지한다. b) 분리기는 이러한 문 또는 덮개가 내압방폭용기 특성(방폭구조 "d")을 보장할 때만 닫힐 수 있다. 17.3.2 나사로 고정된 문 또는 덮개(Doors or covers fixed by screws) 이러한 문 또는 덮개에는 표 14, c)에 따른 표시를 하여야 한다. 17.3.3 나사형 문 또는 덮개(Threaded doors or covers) 이러한 문 또는 덮개에는 표 14, c)에 따른 표시를 하여야 한다. 18 램프홀더 및 램프 캡(Lampholders and lamp caps) 18.1 일반사항(General) 다음 요구사항은 방폭구조 "d"의 내압방폭용기를 형성해야 하는 램프홀더와 램프 캡에 적용하며 안전 증방폭구조 "e"의 등기구에도 사용할 수 있다. 18.2 램프 이완 방지장치(Device preventing lamps working loose) KS C IEC 60079-7, 안전증방폭구조 "e"에서 요구되는 램프의 헐거워짐을 방지하는 장치는 접점의 분 리 이전에 램프 회로의 모든 극을 차단하는 방폭구조 "d"의 내압방폭용기에 신속반응스위치(quick- acting switch)가 있는 나사식 램프홀더의 경우 생략될 수 있다. 18.3 원통형 캡이 있는 램프의 홀더 및 캡(Holders and caps for lamps with cylindrical caps) 18.3.1 관형 형광 램프용 홀더 및 캡은 KS C IEC 60061 의 데이터 시트 Fa6 의 치수 요구사항을 준수 해야 한다. 48 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
ea95dd21-12f5-4a39-8b42-de8da6d50bce | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 18.3.2 다른 홀더의 경우, 5 절의 요구사항을 적용하되 홀더와 캡 사이의 내압방폭 접합부의 길이는 접점이 분리되는 순간에 최소 10mm 이상이어야 한다. 18.4 나사형 캡이 있는 램프용 홀더(Holders for lamps with threaded caps) 18.4.1 홀더의 나사 부분은 사용 가능 조건에서 부식에 강한 재질어아야 한다. 18.4.2 램프를 풀어 접점이 분리되는 순간에 최소 2 개의 완전 나사산이 맞물려 있어야 한다. 18.4.3 나사형 램프홀더 E26/E27 및 E39/E40 의 경우, 전기 접점은 스프링장착 접촉소자(spring- loaded contact elements)에 의해 이뤄져야 한다. 또한 그룹 IIB 또는 그룹 IIC 의 전기기기의 경우, 램 프의 삽입 및 제거 중 접점의 접촉 및 분리는 그룹 IIB 또는 그룹 IIC 각각의 방폭구조 "d"의 내압방 폭용기 내부에서 이루어져야 한다. 나사형 램프홀더 E10 및 E14 의 경우, 18.4.3 의 요구사항은 필요하지 않다. 19 비금속 용기 및 용기의 비금속 부(Non-metallic enclosures and non-metallic parts of enclosures) 19.1 일반사항(General) 다음 요구사항은 비금속 용기 및 용기의 비금속 부에 적용하되 아래의 경우는 예외로 한다. a) C.3 이 적용되는 케이블 글랜드 또는 전선관 밀봉장치(conduit sealing devices)의 밀봉 링, b) 6 절이 적용되는 고착 접합부, 및 c) 방폭구조에 영향을 주지 않는 비금속 부품. 19.2 용기 내부 표면의 내트래킹성 및 연면거리(Resistance to tracking and creepage distances on internal surfaces of the enclosure walls) 비금속 용기 또는 용기의 비금속 부가 노출된 통전부를 직접 지지하는 경우, 용기 내부 표면의 내 트래킹성 및 연면거리는 KS C IEC 60079-7 또는 KS C IEC 60079-15 의 해당 요구사항을 준수해야 한다. 그러나 16 A 이상의 정격 전류에 기인하여 공기 중 아크를 발생시킬 수 있어 전기적 응력을 받을 수 있는 그룹 I 전기기기의 용기의 경우, 12.6 에 명시된 요구사항을 준수해야 한다. 19.3 형식 시험 요구사항(Requirements for type tests) 비금속 용기 및 용기의 비금속 부에 대해서 이 표준에 따른 형식 시험은 다음 순서에 따라 수정된 다. a) KS C IEC 60079-0 에 따른 용기 시험을 실시했거나 또는 실시하지 않은 1 개의 시료에 대하여 15.2.2 에 따라 폭발 압력(기준압력)을 결정 b) KS C IEC 60079-0 에 따라 용기 시험을 실시한 모든 시료에 대하여 15.2.3 에 따라 내압시험 c) 상기 b)에 제시된 시험을 실시한 하나의 시료에 대하여 15.3 에 따라 내부 점화에 의한 인화시험 d) 상기 c)에 제시된 시험을 실시한 시료에 대하여 19.4 에 따라 화염침식시험 e) 상기 d)에 명시된 시험을 실시한 시료에 대하여 15.3 에 따라 내부 점화에 의한 인화시험 49 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
7da29ccd-4fbc-42dc-b4bb-a0419c6917a6 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 19.4 화염침식시험(Test of erosion by flame) 이 시험은 체적이 50 cm3 이상이고 내압방폭 접합부의 적어도 한면이 플라스틱 재질인 용기에 적용 한다. 시료는 15.3 에 설명된 대로 준비하되, 플랜지 접합부 및 마개 접합부의 평면부 틈새가 0.1 mm 에서 0.15 mm 사이의 값으로 설정하여야 한다. 인접한 두 개의 내압방폭용기에 공통적인 부싱의 경우, 시험은 최악의 조건을 제공하는 용기에서 실 시되어야 한다. 이 시험은 해당 그룹에 대해 15.2.2.2 에 명시된 폭발성 혼합물을 50 회 점화하여 실시한다. 그룹 IIC 의 전기기기의 경우, 15.2.2.2 에 명시된 두 개의 폭발성 혼합물 각각에 대해 25 회씩 점화하여 시험한다. 시험은 15.3 의 인화시험이 만족스럽다면 만족스러운 것으로 판정한다. 20 표시(Marking) 20.1 일반사항(General) 내압방폭용기 "d"에는 방폭구조 "d"에 대한 다음의 추가 표시를 하여 KS C IEC 60079-0 에 따라 표시 하여야 한다. 보호등급 "da"에 대하여는 4.2 의 요구사항에 따라 "da"를 표시하여야 한다. 보호등급 "db"에 대하여는 4.3 의 요구사항에 따라 "db"를 표시하여야 한다. 보호등급 "dc"에 대하여는 4.4 의 요구사항에 따라 "dc"를 표시하여야 한다. 20.2 주의 및 경고 표시(Caution and warning markings) 다음의 표시가 필요한 경우, 표 14 에 기술된 바와 같이 "주의" 또는 "경고"라는 단어 뒤에 나오는 문 구는 기술적으로 동등한 문구 또는 기호로 대체될 수 있다. 여러 개의 경고는 하나의 동등한 경고 문구로 통합할 수 있다. 표 14- 주의 또는 경고 표시 문구 ¦ 항 ¦ 관련 ¦ 주의 또는 경고 표시 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ a) ¦ 11.3 ¦ "주의 - 항복강도 ≥(특정 값)인 패스너를 사용하십시오." 여기에서 (특정 값)은 해당 시험시험에 의해 결정된다. ¦ ¦ b) ¦ 13.6.5 ¦ "경고 - 통전 상태에서 분리하지 마십시오." ¦ ¦ c) ¦ 17.2.2 17.3.2 17.3.3 ¦ "경고 - 통전 상태에서 개방하지 마십시오." ¦ ¦ d) ¦ E.3.2 ¦ "경고 - 폭발성 가스 분위기가 존재하는 경우 열지 마십시오." ¦ 20.3 정보 표시(Informative markings) 다음의 표시가 필요한 경우, 표 15 에 기술된 문구는 기술적으로 동등한 문구 또는 기호로 대체될 수 있다. 여러 개의 경고는 하나의 동등한 경고 문구로 통합할 수 있다. 50 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
edf707e8-bd90-4b3f-a918-036fdc71f32e | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 표 15 - 정보 표시 문구 ¦ 항 ¦ 관련 ¦ 정보 표시 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ a) ¦ 13.2 ¦ 나사산 크기 및 종류의 식별. 예: "1/2 NPT", "M25" ¦ ¦ b) ¦ 13.2 ¦ "설치 시 사용설명서 참조" ¦ ¦ c) ¦ 15.3.1 ¦ "이 기기의 플랜지 접합부는 고형 물체(SOLID OBJECT)로부터 (값) 이상 이격하여 설치할 것." 여기에서 (값)에 해당하는 수치가 표 11 에 명시된 값보다 작은 경우, 인화시험 중 고형 물체의 근접거리로 결정한다. ¦ 21 사용설명서(Instructions) 모든 내압방폭 "d" 기기는 5.1 에 따라 필요한 경우 적어도 화염경로(flamepath)의 치수 또는 화염경로 의 수리의 금지 등에 대한 상세사항을 포함하여 KS C IEC 60079-0 에서 요구하는 사용설명서를 제공 하여야 한다. 51 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
cc7eb276-068e-4c09-8a27-45ed216476f0 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 부속서 A (규정) 통기 및 배수장치의 주름 리본 엘리먼트와 멀티 스크린 엘리먼트에 대한 추가 요구사항 (Additional requirements for ribbon elements and multiple screen elements of breathing and draining devices) A.1 주름 리본 엘리먼트와 멀티 스크린 엘리먼트는 구리-니켈, 스테인레스 스틸 또는 기타 적합한 금속으로 만들어야 한다. 알루미늄, 티타늄, 마그네슘 및 그 합금은 사용하지 않아야 한다. 구리 함량에 대한 제한은 10.3 을 참조한다. A.2 장치를 통과 하는 경로가 도면에서 명시되고 완성된 장치에서 측정될 수 있는 경우, 경로의 치 수 에 대한 상한 및 하한 공차 한도를 지정하고 생산 중 모니터링하여야 한다. A.3 A.2 가 적용되지 않는 경우, 부속서 B 의 요구사항을 적용하여야 한다. A.4 15.4.4 의 형식 시험은 최대 허용 틈새값의 90 % 이상으로 제조된 시료로 수행되어야 한다. 52 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
bc5e879e-cbeb-47d2-98ba-f9fe1013e853 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 부속서 B (규정) 경로를 측정할 수 없는 통기 및 배수장치 엘리먼트에 대한 추가 요구사항 (Additional requirements for elements, with non-measurable paths of breathing and draining devices) B.1 소결금속 엘리먼트(Sintered metal elements) B.1.1 소결금속 엘리먼트는 다음 중 하나로 구성되어야 한다. 스테인리스 스틸 - 90/10 구리-주석 청동 용도에 적합한 특정 금속 또는 특정 합금. 알루미늄, 티타늄, 마그네슘 및 그 합금은 사용해서는 안 된다. 구리 함량에 대한 제한은 10.3 을 참조한다. B.1.2 최대기포시험기공크기(maximum bubble test pore size)는 ISO 4003 에 명시된 방법에 따라 결정 되어야 한다. B.1.3 소결금속 엘리먼트의 밀도는 ISO 2738 에 따라 결정되어야 한다. B.1.4 장치의 기능적 측면과 관련하여 엘리먼트의 다공성(open porosity) 및/또는 유체 투과 성(fluid permeability)을 결정해야 하는 경우, ISO 2738 및 ISO 4022 에 따라 측정해야 한다. B.1.5 소결금속 엘리먼트는 다음 사항이 문서에 명확히 명시되어야 한다. a) 10.3 및 B.1.1 에 따른 재질 b) B.1.2 에 따른 최대기포시험기공크기(마이크로 미터 단위) c) B.1.3 에 따른 최소 밀도 d) 최소 두께 e) 해당되는 경우, B.1.4 에 따른 유체 투과 성 및 다공성 B.2 압축 금속와 이어 엘리먼트(Pressed metal wire elements) B.2.1 압축 금속와 이어 엘리먼트는 스테인리스 스틸 와이어 브레이드(stainless steel wire braid) 또는 적용에 적합한 다른 특정 금속으로 구성되어야 한다. 구리 함량에 대한 제한은 10.3 을 참조한다. 알루미늄, 티타늄, 마그네슘 및 그 합금은 사용해서는 안 된다. 제조는 균일한 매트릭스 (homogeneous matrix)를 형성하기 위해 금형(die)에서 압축된 와이어 브레이드로 시작한다. B.2.2 밀도를 평가하기 위해, 와이어 지름이 명시되어야 한다. 질량, 와이어 브레이드 길이, 엘리먼트 53 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
7baa8bb3-3889-4df4-aaf8-fdb04813b407 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 의 두께 및 메시 크기(mesh size)에 대한 정보도 제공되어야 한다. 엘리먼트 질량과 동일 금속의 동 일 부피의 질량 사이의 비율은 0.4 에서 0.6 사이여야 한다. B.2.3 최대기포시험기공크기는 ISO 4003 에 명시된 방법에 따라 결정되어야 한다. B.2.4 엘리먼트의 밀도는 ISO 2738 에 따라 결정되어야 한다. B.2.5 엘리먼트의 기능적 측면과 관련하여 엘리먼트의 다공성 및/또는 유체 투과 성을 결정해야 하는 경우, ISO 2738 및 ISO 4022 에 따라 측정해야 한다. B.2.6 금속와 이어 엘리먼트는 다음 사항이 문서에 명확히 명시되어야 한다. a) 10.3 및 B.2.1 에 따른 재질 b) B.2.3 에 따른 최대기포시험 기공크기(마이크로 미터 단위) c) B.2.4 에 따른 최소 밀도 d) 공차를 포함한 치수 e) 원래 와이어 지름 f) 해당되는 경우, B.2.5 에 따른 유체 투과 성 및 다공성 B.3 발포금속 엘리먼트(Metal foam elements) B.3.1 발포금속 엘리먼트는 망상조직의 발포 폴리우레탄을 니켈로 코팅하고 열분해에 의해 폴리우레 탄을 제거한 다음, 니켈을 니켈-크롬 합금으로 변환(예: 기체 확산에 의해)시킨 후 필요시 재료를 압 축함으로써 생산하여야 한다. B.3.2 발포금속 엘리먼트는 최소 질량 15 % 이상의 크롬을 함유하여야 한다. B.3.3 최대기포시험기공크기는 ISO 4003 에 명시된 방법으로 결정하여야 한다. B.3.4 엘리먼트의 밀도는 ISO 2738 에 따라 결정되어야 한다. B.3.5 엘리먼트의 기능적 측면과 관련하여 엘리먼트의 다공성 및/또는 유체 투과 성을 결정해야 하는 경우, ISO 2738 및 ISO 4022 에 따라 측정해야 한다. B.3.6 발포금속 엘리먼트는 다음 사항이 문서에 명확히 명시되어야 한다. a) 10.3, B.3.1 및 B.3.2 에 따른 재질 b) B.3.3 에 따른 최대기포시험 기공크기(마이크로미터 단위) c) 최소 두께 d) 최소 밀도 e) 해당되는 경우, B.3.5 에 따른 유체 투과 성 및 다공성 54 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
0562bdb4-0689-49f4-8052-289cd4ea9987 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 부속서 c (규정) 내압방폭 인입 장치에 대한 추가 요구사항 (Additional requirements for flameproof entry devices) C.1 일반사항(General) 이 부속서는 내압방폭형 인입 장치의 구조 및 시험에 대한 KS C IEC 60079-0 의 요구사항에 추가하여 적용되는 특정 요구사항을 포함한다. 인입 장치에는 케이블 글랜드, 전선관 밀봉장치, 방폭 블랭킹 엘리먼트, 방폭 나사어댑터 및 부싱이 포함된다. C.2 구조 요구사항(Constructional requirements) C.2.1 밀봉 방법(Sealing methods) C.2.1.1 탄성 실링링이 있는 케이블 글랜드 및 전선관 밀봉장치(Cable glands and conduit sealing de vices with elastomeric sealing rings) C.2.1.1.1 케이블 글랜드 또는 전선관 밀봉장치가 바깥지름은 동일하지만 안지름이 상이한 실링링을 수용할 수 있는 경우, 실링링은 글랜드 몸체와 실링링 사이 및 실링링과 케이블 사이의 비압축 상태 에서 축방향 밀봉 높이(즉, 틈새 길이)는 다음과 같아야 한다. 지름이 20 mm 이하의 원형 케이블 및 둘레길이(perimeter) 60 mm 이하의 비원형 케이블에 대해서 는 20 mm 지름이 20 mm 를 초과 하는 원형 케이블 및 둘레길이가 60 mm 를 초과 하는 비원형 케이블에 대해 서는 25 mm C.2.1.1.2 케이블 글랜드 또는 전선관 밀봉장치가 하나의 특정 탄성 실링링만 수용할 수 있는 경우, 실링링은 글랜드 몸체와 실링링 사이 및 실링링과 케이블 사이의 비압축 상태에서 축방향 밀봉 높이 는 최소 5 mm 이상이어야 한다. C.2.1.2 경화 컴파운드로 밀봉하는 케이블 글랜드(Cable glands sealed with setting compound) 설치되었을 때 컴파운드의 최소 길이는 20 mm 이상이어야 한다. 제조자는 아래 사항을 명시하여야 한다. a) 글랜드가 수용할 수 있는 케이블 코어의 최대 지름(maximum diameter over cores of the cable) b) 컴파운드를 관통할 수 있는 코어의 최대 개수 이 명시한 값은 요구되는 컴파운드 길이 20 mm 에 걸쳐 단면적의 최소 20 % 이상이 컴파운드로 채 워지도록 보장해야 한다. 케이블 글랜드는 컴파운드의 지정된 경화 시간 후 컴파운드 밀봉부분을 방해하지 않고 전기기기에 탈착할 수 있어야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 55 | {}
4ab73b6a-117f-475e-ac39-0f3449c54abb | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 충진 컴파운드(filling compound) 및 적합한 사용설명서를 케이블 글랜드와 함께 제공하여야 한다. C.2.1.3 경화 컴파운드로 밀봉하는 전선관 밀봉장치(Conduit sealing devices with setting compound) 설치되었을 때 컴파운드의 최소 길이는 20mm 이상이어야 한다. 제조자는 컴파운드를 관통할 수 있는 코어의 최대 개수를 명시해야 한다. 이 명시한 값은 요구되는 컴파운드 길이 20 mm 에 걸쳐 단면적의 최소 20 % 이상이 컴파운드로 채 워지도록 보장해야 한다. 충진 컴파운드 및 적합한 사용설명서를 전선관 밀봉장치와 함께 제공하여야 한다. C.2.1.4 부싱(Bushings) 부싱은 한 개 이상의 도체를 포함할 수 있다. 부싱이 올바르게 조립되어 용기 벽에 설치될 때, 모든 접합부 길이, 틈새 또는 고착 접합부는 5 절, 6 절 및 C.2.2 의 관련 요구사항에 부합해야 한다. 문서는 컴파운드를 통과 할 수 있는 코어의 최대 개수를 명시해야 한다. 비고 적절한 강도를 제공하기 위해, 부싱 설계는 일반적으로 요구되는 고착 접합부 길이에 걸쳐 컴 파운드로 채워지는 단면적이 최소 20 % 이상 되도록 한다. 부싱이 금속부(metallic parts)에 절연재 몰딩으로 성형될 때는 5.2, 5.3 및 5.4 의 요구사항은 적용되지 않지만, 6 절은 문서에 명시된 최소 도체 길이를 사용해 의도한 최대 응용 체적의 대표 용기에 부싱을 장착하여 실시하는 인화시험에 적용할 수 있다. 절연 물질 자체는 용기의 기계적 강도에 기여할 수 있다. 부싱이 접착제로 조립된 부품을 포함하는 경우, 접착제는 문서에 명시된 최소 도체 길이를 사용해 의도한 최대 응용 체적의 대표 용기에 부싱을 장착하여 실시하는 인화시험으로 6 절의 요구사항을 만 족한다면 고착제(cement)로 간주된다. 그렇지 않은 경우, 5.2.1, 5.3 및 5.4 의 요구사항을 적용할 수 있 다. 내압방폭용기 외부의 부싱 부분은 KS C IEC 60079-0 에 따라 보호되어야 한다. 내압방폭용기에 특정된 부싱은 해당 용기에 대한 형식 시험 및 일상시험을 만족시켜야 한다. 방폭부품 부싱(Ex component bushings)은 15.2.3.2 에 명시된 정압시험을 아래의 값을 적용하여 내압 시험을 실시하여야 한다. - 그룹 I 의 전기기기의 경우, 2 000 kPa - 그룹 II 의 전기기기의 경우, 3 000 kPa 이러한 부싱은 조립 절차가 제조자의 문서에 명시되어 있고 제조된 제품의 일관성을 보장하는 경우 를 제외하고는 16.1 에 명시된 일상압력시험을 실시하여야 한다. 시멘트 접합부가 누설 유무와 관계없이 만족스럽다고 판단되면, 방폭 부품 인증서 상의 사용제한표 (schedule of limitations)에 사용 가능한 최대 용기 체적 및 최소 지정 도체 길이를 명시해야 한다. 56 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
3bebd4e1-e8d7-402b-a56b-959bd679ba55 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 C.2.2 내압방폭 접합부(Flameproof joints) C.2.2.1 나사 접합부(Threaded joints) 내압방폭 접합부의 나사부는 5.3 의 관련 요구사항에 적합해야 하며 다음 중 하나이어야 한다. ISO 965-1 및 ISO 965-3 에 따른 공차 등급 6g/6H 이상의 미터 나사, 그리고 암나사의 모따기 또 는 언더컷은 외부 표면에서 최대 깊이 2 mm 로 제한된다. 테이퍼 나사는 ANSI/ASME B1.20.1 의 NPT 요구사항을 준수해야 한다. 단붙이(shoulder) 또는 마감(interruption)이 있는 수나사 NPT 피팅은 아래 요건을 충촉하여야 한다. a) 유효 나사 길이는 "L2"(유효 나사산까지 길이) 값 이상이어야 하며 b) 단붙이 면부터 나사산 끝까지 길이는 "L4"(나사산이 가공된 총 길이) 값 이상이어야 한다. NPT 암나사는 L1 플러그 게이지를 사용해 "플러시(flush)"에서 "2 산 여유(2 turns large)"로 측정되 어야 한다(L1 플러그 게이지를 암나사에 넣어 손으로 체결할 때 게이지에 2 산의 여유가 남아야 한다). 이전 KS C IEC 60079-1 표준에서 허용된 다른 수나사 형식. 장치가 이전 KS C IEC 60079-1 의 판 을 적용한 수나사 형식을 포함할 경우, 해당 장치에는 나사 형식이 표시되어야 한다. 인증서에는 또한 나사 형식 요구사항이 적용된 KS C IEC 60079-1 의 이전 판과 함께 나사 형식을 명시하여야 한다. 비고 1 "다른 수나사 형식"을 허용하는 것은 현행 KS C IEC 60079-1 에서 더 이상 허용하지 않는 암나사 형식을 포함하고 있는 기존 설치된 기기를 위한 대체 인입 장치의 제조를 위한 것이다. 내압방폭기기의 나사 인입부에 설치하기 위한 미터 수나사의 경우, 나사산 부분의 길이는 최소 8 mm 이상이어야 하고 최소 8 개의 완전 나사산으로 구성되어야 한다. 나사부에 언더컷이 있는 경우, 언더컷의 크기와 상관없이 분리되지 않는 비압축성 와셔나 이와 동등한 장치를 설치하여 요구되는 나사 체결 길이(length of thread engagement)가 보증될 수 있도록 하여야 한다. 비고 2 적어도 8 개의 완전 나사산을 요구하는 것은 모따기 또는 언더컷(13 절 참조)을 고려하여 케이 블 글랜드가 나사 인입부에 설치될 때 적어도 5 개의 완전 나사산이 맞물리는 것을 보장하기 위해서이다. C.2.2.2 비나사 접합부(그룹 I 만 해당) (Non-threaded joints (Group I only)) 비나사 접합부는 그룹 I 에만 적용되며 5.2 의 관련 요구사항을 준수해야 한다. 고정 방법(들)은 15 절의 형식 시험의 일부로서 평가되어야 한다. 고정 수단으로 사용되는 패스너는 KS C IEC 60079-0 의 특수 패스너의 요건을 준수해야 한다. 비고 내압방폭용기와 함께 원래 평가되지 않은 비나사 접합부형 케이블 어댑터 및/또는 케이블 글랜 드는 설치 시 고정 방법이 적합하고 내압방폭용기의 요구사항을 만족하는지를 보장하기 위해 검토 및/또는 평가된다. C.2.3 방폭 블랭킹 엘리먼트의 구조 요구사항(Constructional requirements for Ex blanking elements) C.2.3.1 일반 요구사항(General requirements) 기계적으로 또는 마찰로 고정된 블랭킹 엘리먼트는 다음 요구사항 중 하나 이상을 준수해야 한다. 57 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
3b0ce186-d415-4eb5-b9c8-f57906c37df0 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 블랭킹 엘리먼트가 외부에서 제거 가능한 경우, 용기 내부의 고정장치가 분리된 후에만 가능해야 한다(그림 C.1a 참조). 블랭킹 엘리먼트가 공구의 사용에 의해서만 장착 또는 제거될 수 있도록 설계될 수 있다(그림 C.1b 참조). 블랭킹 엘리먼트의 삽입이 제거를 위해 사용되는 방법 이외의 방법으로 수행되도록 하는 특별한 구조로 할 수 있다[그림 C.1 c) 참조]. ![image](/image/placeholder) 내부 외부 a) 예시 1 내부 외부 b) 예시 2 공구 홈 전단 목(삽입 후 전단) c) 예시 3 내부 외부 그림 C.1 - 사용되지 않는 인입부를 위한 블랭킹 엘리먼트의 예시 C.2.3.2 미터법 방폭 블랭킹 엘리먼트(Metric Ex blanking elements) 추가적으로 미터법 방폭 블랭킹 엘리먼트는 다음을 준수해야 한다. a) 방폭 블랭킹 엘리먼트가 용기 벽을 통과 하여 나사가 완전히 체결되는 것을 방지하기 위해 단붙이 (shoulder) 또는 마감(interruption)이 있도록 한다. 단붙이가 제공될 때, 그 지름과 두께는 표준에서 허용하는 방법으로만 제거될 수 있도록 하여야 한다. b) 나사산은 C.2.2 의 관련 요구사항을 준수해야 한다. 비고 이 요구사항은 블랭킹 엘리먼트의 외부 표면을 가능한 한 용기에 가깝게 유지함으로써 용기로 들어가는 것에 대한 우려를 해소하기 위한 것이다. C.2.3.3 NPT 방폭 블랭킹 엘리먼트(NPT Ex blanking elements) NPT 방폭 블랭킹 엘리먼트는 다음과 같은 특징을 가져야 한다. 58 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
ca228758-29f0-4a96-b83d-e27549279682 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 a) 단붙이가 없어야 한다. b) 나사 형태는 ANSI/ASME B1.20.1 의 NPT 요구사항에 적합해야 한다. c) 공구를 위한 자리가 있어야 한다. 그리고 d) 유효 나사 길이는 "L2" 치수 이상이어야 한다. 비고 이 요구사항은 블랭킹 엘리먼트의 외부 표면을 가능한 한 용기에 가깝게 유지함으로써 용기로 들어가는 것에 대한 우려를 해소하기 위한 것이다. C.2.3.4 비나사 방폭 블랭킹 엘리먼트(그룹 1 만 해당)(Non-threaded Ex blanking elements (Group I only)) 그룹 I 의 경우만, 평면(비나사) 블랭킹 엘리먼트는 C.2.2.2 및 C.2.3.1 의 요구사항을 준수해야 한다. C.2.4 방폭 나사 어댑터의 구조 요구사항(Constructional requirements for Ex thread adapters) C.2.4.1 모든 나사는 C.2.2 의 관련 요구사항을 준수해야 한다. C.2.4.2 방폭 나사 어댑터의 나사는 동축(co-axial)이어야 한다. C.2.4.3 방폭 나사 어댑터의 길이 및 내부 체적은 최소화되어야 한다. C.3 형식 시험(Type tests) C.3.1 밀봉 시험(Sealing test) C.3.1.1 일반사항(General) KS C IEC 60079-0 에 규정된 고온 및 저온 내열성에 대한 요구사항은 제조자의 사용설명서에 따라 맨 드릴(mandrel) 또는 케이블을 사용하여 조립된 시료에 적용하여야 한다. 고온 및 저온에 대한 내열성시험을 수행한 후, 외부 부품은 제조자의 유지보수 지침에 따라 다시 조 일 수 있다. 어떠 조건에서도 케이블 글랜드를 부분적으로 또는 완전히 분해(예: 검사 목적으로)하여 느슨하게 해서는 안 된다. C.3.1.2 실링링이 있는 케이블 글랜드 및 전선관 밀봉장치(Cable glands and conduit sealing devices with sealing ring) 이 시험은 케이블 글랜드 또는 전선관 밀봉장치의 각 형식에 대하여 서로 다른 크기의 하나의 실링 링을 사용하여 수행하여야 한다. 탄성 실링링의 경우, 각 링은 깨끗하며 건조한 광택 연마된 내 부식 성 금속(예: 316 스테인리스 스틸) 원통형 멘드릴에 장착하되, 멘드릴의 바깥지름은 케이블 글랜드 또 는 전선관 밀봉장치 제조자가 지정한 링에 삽입 가능한 가장 작은 케이블의 지름과 같아야 한다. 금속 또는 합성소재(composite) 실링링의 경우, 각 링은 깨끗하며 건조한 케이블 시료의 금속 외장 (metal sheath)에 장착하되, 그 바깥지름은 케이블 글랜드 또는 전선관 밀봉장치 제조자가 지정한 링 에 삽입 가능한 가장 작은 케이블의 지름과 같아야 한다. 비원형 케이블용 실링링의 경우, 각 링은 깨끗하며 건조한 케이블 시료에 장착하되, 케이블의 둘레 길이는 케이블 글랜드 또는 전선관 밀봉장치 제조자가 지정한 링에 삽입 가능한 것과 가장 같아야 한다. 59 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
2a47bff6-3259-42c3-b2da-87f84753f420 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 그런 다음, 조립품을 인입부에 끼우고 나사(플랜지식 압착 장치의 경우) 또는 너트(나사식 압착 장치 의 경우)에 토크를 가하여 그룹 I 의 경우 2 000 kPa, 그룹 II 의 경우 3 000 kPa 의 유압 하에 밀봉이 유지되도록 한다. 비고 1 위에서 언급된 토크 수치는 시험 전에 실험적으로 결정되거나, 케이블 글랜드 또는 전선관 밀봉장치 제조자가 제공한 것이다. 이어서 조립품은 유색 수 또는 오일을 유체로 사용하는 유압시험장치에 장착하며 그 원리는 그림 C.2 에 설명되어 있다. 유압 회로를 퍼지시킨다. 그 다음 유압을 점진적으로 증가시킨다. 밀봉은 압력이 그룹 I 의 경우 2 000 kPa 또는 그룹 II 의 경우 3 000 kPa 에서 최소 10 초 이상 유지했 을 때 흡착지(blotting paper)에 누출 흔적이 없는 경우 만족스러운 것으로 간주한다. 비고 2 시험 압력을 유지하기 위해, 시험 중인 실링링과 관련된 것을 제외하고 시험 장치에 장착된 케이블 글랜드 또는 전선관 밀봉장치의 모든 접합부를 밀봉할 필요가 있다. 금속 외장 케이 블의 시료를 사용하는 경우, 도체의 끝부분 또는 케이블의 내부에 압력이 가해지지 않도록 할 필요가 있다. ![image](/image/placeholder) 6 7 1 2 3 5 4 9 8 식별부호 1 유압 펌프 2 압력 게이지 3 호스 4 흡습지 5 어댑터 6 실링링 7 맨드릴/금속외장 케이블 8 압착 부품 9 고정 클램프 그림 C.2 - 케이블 글랜드 밀봉시험 장치 C.3.1.3 경화 컴파운드로 밀봉하는 케이블 글랜드(Cable glands sealed with setting compound) 케이블 글랜드의 각 크기에 대하여, 시험은 금속 맨드릴을 사용하여 수행하여야 하며, 그 수와 지름 은 C.2.1.2 의 요구사항에 따라 제조자가 명시한 최대 코어 수를 갖는 경우의 코어의 최대 지름과 동 일해야 한다. 경화 컴파운드를 제조자의 사용 방법에 따라 준비하여 적절한 분량을 주입하고 적당한 시간 동안 경 화시킨다. 그 다음 조립체를 C.3.1.2 에 정의 된 유압시험장치에 장착하고 동일한 절차를 적용한다. 적합 기준도 동일하다. 60 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c5e5c328-36be-402c-8dbb-49e386f40108 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 C.3.1.4 경화 컴파운드로 밀봉하는 전선관 밀봉장치(Conduit sealing devices sealed with setting compoun d) 전선관 밀봉장치의 각 크기에 대하여, 시험은 금속 맨드릴을 사용하여 수행하여야 하며, 그 수와 지 름은 C.2.1.3 의 요구사항에 따라 제조자가 명시한 최대 코어 수와 동일해야 한다. 경화 컴파운드를 제조자의 사용 방법에 따라 준비하여 적절한 분량을 주입하고 적당한 시간 동안 경 화시킨다. 그 다음 조립체를 C.3.1.2 에 정의 된 유압시험장치에 장착하고 동일한 절차를 적용한다. 적합 기준도 동일하다. C.3.2 기계적 강도시험(Test of mechanical strength) C.3.2.1 나사형 압착 부품이 있는 케이블 글랜드(Cable glands with a threaded compression element) 밀봉시험에서 요구되는 값 2 배의 토크를 압착 부품에 적용한다. 하지만 이 토크 값(Nm 단위)은 항상 케이블 글랜드가 원형 케이블용으로 설계된 경우 최대 허용 케이블 지름의 밀리미터(mm) 값의 최소 3 배 이상이 되어야 하며, 케이블 글랜드가 비원형 케이블용으로 설계된 경우에는 최대 허용 케이블 둘레의 밀리미터(mm) 값과 동일해야 한다. 그런 다음, 케이블 글랜드를 해체하여 부품을 검사한다. C.3.2.2 나사 고정형 압착 부품이 있는 케이블 글랜드(Cable glands with a compression element fixed by screws) 밀봉시험에서 요구되는 값 2 배의 토크를 압착 부품 나사(compression element screws)에 적용한다. 하 지만 이 토크 값은 항상 최소한 다음 값과 같아야 한다. ¦ M6: ¦ 10 Nm ¦ M12: ¦ 60 Nm ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ M8: ¦ 20 Nm ¦ M14: ¦ 100 Nm ¦ ¦ M10: ¦ 40 Nm ¦ M16: ¦ 150 Nm ¦ 그런 다음, 케이블 글랜드를 해체하여 부품을 검사한다. C.3.2.3 경화 컴파운드로 밀봉하는 케이블 글랜드(Cable glands sealed with setting compound) 나사산이 있는 글랜드의 경우, C.3.2.1 에 명시된 최소값과 동일한 토크(Nm 단위)를 적절한 나사 구멍 이 있는 철재 시험 블록에 체결할 때 글랜드에 적용하여야 한다. 그런 다음, 케이블 글랜드를 해체하여 부품을 검사한다. C.3.2.4 적합 기준(Acceptance criteria) C.3.2.1 부터 C.3.2.3 까지의 시험은 케이블 글랜드의 어떤 부분에도 손상이 없다면 만족스러운 것으로 간주한다. 61 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
ad245133-ee64-4219-8454-6845fb54ee6d | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 비고 이 시험은 케이블 글랜드의 기계적 강도가 사용 조건을 견디기에 충분하다는 것을 보여주는 시험이기 때문에 실링링의 손상은 무시된다. C.3.3 방폭 블랭킹 엘리먼트의 형식 시험(Type tests for Ex blanking elements) C.3.3.1 토크시험(Torque test) 각 크기별 방폭 블랭킹 엘리먼트 시료를 시험하는 장치에 적합한 크기 및 형태의 나사 구멍을 가진 철재 시험 블록에 체결하여야 한다. 시료를 적절한 공구를 사용하여 표 C.1 또는 표 C.2 의 2 열에 주 어진 해당 토크와 최소 동일한 토크로 조여야 한다. 시험은 올바른 나사 결합(thread engagement)이 달성되고 해체되었을 때 그림 C.1c - 예 3 의 전단 목이 파손된 경우를 제외하고는 방폭구조를 무효 로하는 손상이 발견되지 않으면 만족스러운 것으로 간주한다. 그림 C.1b - 예 2 의 플러그는 적절한 공구로만 제거될 수 있어야 한다. 그림 C.1b - 예 2 의 미터식 방폭 블랭킹 엘리먼트는 표 C.1 의 3 열에 주어진 해당 토크와 적어도 동 등 한 토크로 추가 시험을 실시해야 하며, 단붙이가 나사 안쪽으로 완전히 들어가지 않은 경우 만족 스러운 것으로 간주한다. C.3.3.2 내압시험(Over-pressure test) 방폭 블랭킹 엘리먼트는 다음 값으로 15.2.3.2 에 규정된 정압으로 수행하는 내압시험을 실시해야 한다. - 그룹 I 의 전기기기에 대해 2 000 kPa - 그룹 II 의 전기기기에 대해 3 000 kPa C.3.4 방폭 나사 어댑터의 형식 시험(Type tests for Ex thread adapters) C.3.4.1 토크시험(Torque test) 각 크기별 방폭 나사 어댑터 시료를 시험하는 장치에 적합한 크기와 형태의 나사 구멍을 가진 철재 시험 블록에 체결하여야 한다. 적합한 형태 및 크기의 철강 또는 황동 나사 플러그를 방폭 나사 어 댑터 인입부에 체결하여야 한다. 어댑터의 두 나사 중 큰 값에 해당하는 표 C.1 또는 표 C.2 의 2 열에 표시된 토크와 동등한 토크로 플러그를 조인다. 조립체를 해체했을 때 방폭구조를 무효로 하는 손상이 방폭 나사 어댑터에 발견되 지 않으면 만족스러운 것으로 간주한다. C.3.4.2 충격시험(Impact test) 각 크기별 방폭 나사 어댑터 시료를 시험하는 장치에 적합한 크기와 형태의 나사 구멍을 가진 철재 시험 블록에 체결하여야 한다. 어댑터의 인입부에 적합하게 한쪽 끝에 나산산이 나있고, 그 길이는 인입부 지름 또는 최소 50 mm 이상이 돌출하도록 하는 적당한 지름의 견고한 강철 또는 황동 봉을 어댑터의 인입부에 적어도 표 C.1 또는 표 C.2 의 2 열에 명시된 해당 토크와 동등한 토크로 체결하여 야 한다. 그런 다음 조립체를 KS C IEC 60079-0 에 주어진 해당 요구사항에 따라 충격시험을 실시한 다. 충격은 봉의 축에 직각으로 그리고 봉의 가능한 한 끝 부분에 가해져야 한다. C.3.4.3 내압시험(Over-pressure test) 방폭 나사 어댑터는 다음 값으로 15.2.3.2 에 규정된 정압으로 수행하는 내압시험을 실시해야 한다. 62 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
71abf261-54dd-4fe7-9c9e-2665beb90b12 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 그룹 I 의 전기기기의 경우, 2 000 kPa 그룹 II 의 전기기기의 경우, 3 000 kPa 표 C.1 - 조임 토크 값(미터법) ¦ 나사 크기 mm ¦ 토크 및 충격시험에 대한 조임 토크 Nm ¦ 그림 C.1b 에 대한 조임 토크 - 예시 2 플러그 Nm ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ < 16 ¦ 2 da ¦ 3.5 da ¦ ¦ 16 ¦ 40 ¦ 65 ¦ ¦ 20 ¦ 40 ¦ 65 ¦ ¦ 25 ¦ 55 ¦ 95 ¦ ¦ 32 ¦ 65 ¦ 110 ¦ ¦ 40 ¦ 80 ¦ 130 ¦ ¦ 50 ¦ 100 ¦ 165 ¦ ¦ 63 ¦ 115 ¦ 195 ¦ ¦ 75 ¦ 140 ¦ 230 ¦ ¦ > 75 ¦ 2 da ¦ 3.5 da ¦ ¦ a 변수 d 는 나사산의 바깥지름(mm) ¦ a 변수 d 는 나사산의 바깥지름(mm) ¦ a 변수 d 는 나사산의 바깥지름(mm) ¦ 표 C.2 - 조임 토크 값, NPT ¦ 나사 크기 ¦ 조임 토크 Nm ¦ ¦ --- ¦ --- ¦ ¦ 1/2 ~ 3/4 ¦ 90 ¦ ¦ 1 ~ 1 1/2 ¦ 113 ¦ ¦ 2 및 그 이상 ¦ 181 ¦ ![image](/image/placeholder) 그림 C.3 - 방폭 나사 어댑터의 예 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 63 | {}
7dc775af-ffd7-491d-b704-aed0d5e50dc1 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 부속서 D (규정) 방폭부품용 빈 내압방폭용기 (Empty flameproof enclosures as Ex components) D.1 일반사항(General) 빈 용기에 대한 방폭부품 용기 인증서의 목적은 내부 장치가 정의 되지 않은 상태에서 내압방폭용기 의 제조자가 인증서를 취득할 수 있게 하고, 빈 용기가 제 3 자에게 제공되었을 때 KS C IEC 60079-1 및 KS C IEC 60079-0 에서 요구하는 내압방폭용기 "d"에 대한 모든 형식 시험을 반복하지 않고 완전한 기기의 인증을 취득할 수 있도록 하기 위함이다. 전체 기기와 관련된 인증서가 요구될 경우, 빈 용기 에 대한 방폭부품 인증서는 필요하지 않다. D.2 서언(Introductory remarks) 이 부속서에는 빈 용기에 대한 방폭부품 용기 인증서의 요구사항이 담겨 있다. 이것은 후속되는 기 기인증서에 대한 필요성을 배제하는 것이 아니라 그러한 인증서를 용이하게 하기 위한 것이다. 방폭부품 용기 제조자는 각 모든 부품이 다음과 같이 공급되도록 보장할 책임이 있다. a) 방폭부품 용기 인증서와 관련된 문서에 명시된 본래의 설계와 동일하며 b) 요구되는 경우, 일상내압시험을 거쳤으며 c) 방폭부품 용기 인증서 상에서 부과 된 사용제한표(schedule of limitations)의 요구사항을 만족해야 한다. D.3 방폭부품 용기 요구사항(Ex component enclosure requirements) D.3.1 방폭부품 용기는 해당하는 경우 KS C IEC 60079-0 및 이 표준의 요구사항을 준수해야 한다. D.3.2 방폭부품 용기는 테이퍼가 10 %를 초과 하지 않는 정사각형, 직사각형 또는 원통형 단면의 기 본적으로 단순한 형상으로 구성되어야 한다. 비고 단순한 형상은 그룹 1, 그룹 IIA 및 그룹 IIB 의 경우 주요 치수가 다른 치수를 4:1 로 넘지 않거 나 그룹 IIC 의 경우 다른 치수를 2:1 로 넘지 않는 구조를 포함하는 것으로 간주된다. D.3.3 회전기기(rotating machines)용 용기는 방폭부품 용기로 평가되어서는 안 된다. 비고 "기기(machines)"는 실질적으로 용기를 채우는 전기 모터를 의미한다. D.3.4 방폭부품 용기에는 내부 부품의 장착 및 위치에 적절한 수단을 제공해야 한다. D.3.5 기계적 목적이건 전기적 목적이건 또는 막혀 있건 뚫려 있건, 방폭부품 용기 인증서에서 허용 하는 것 이외에 방폭부품 용기에 구멍을 뚫어서는 안 된다. D.3.6 그룹 1, 그룹 IIA 및 그룹 IIB 방폭부품 용기의 경우, 기준압력은 다음과 같이 시험 시료를 수정 64 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
4589b3b1-0a1b-4173-9ee3-2e25e38ca14f | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 하여 15.2.2 에 따라 결정한다. - 주요 치수가 다른 주요 치수를 2:1 보다 크게 초과 하지 않는 경우, 수정은 필요하지 않다. - 그 밖의 모든 허용되는 구조의 경우, 단면적의 약 80 %에 해당하는 견고한 장애물[배플 판(baffle plate)]이 짧은 축의 중심에 위치하고, 긴 축을 따라 약 2/3 지점에 위치해야 한다. 이 장애물은 용 기의 단면과 형태가 같아야 한다. 그룹 IIC 방폭부품 용기의 경우, 기준압력은 단면적의 약 60 %에 해당하는 견고한 장애물이 짧은 축 의 중심에 위치하고, 긴 축을 따라 약 2/3 지점에 위치시킨 상태에서 15.2.2 에 따라 결정된다. 이 장 애물은 용기의 단면과 형태가 같아야 한다. 견고한 장애물을 넣어 시료를 수정해야 하는 경우, 점화원과 압력측정장치는 장애물의 양쪽에 배치 하여 결과 압력을 동시에 측정한다. D.3.7 방폭부품 용기는 빈 상태에서 인입부를 적절한 방법으로 밀폐하고 15.2.2 에 따라 측정된 피크 폭발압력(기준압력)의 1.5 배에 해당하는 압력에서 최대 크기의 구멍을 최대 개수로 하여 실시한 내압 형식 시험을 견뎌야 한다. 규정된 형식 시험이 기준압력의 4 배에 해당하는 정압으로 실시한 경우, 방폭부품 용기에는 일상시험 이 필요하지 않다. 하지만 용접 구조로 된 방폭부품 용기는 모든 경우에 대하여 일상시험을 실시해 야 한다. 일상시험은 용기 내부와 외부에 15.2.2(폭발압력의 결정)에 규정된 해당 폭발성 혼합물을 대기압의 1.5 배로 하여 동적 시험을 실시하거나 또는 최소 350 kPa 및 기준압력의 1.5 배 이상의 압력으로 정 적 시험을 실시하여야 한다. D.3.8 용기는 KS C IEC 60079-0 에 주어진 방폭부품의 표시 요구사항에 따라 표시되어야 하지만 표시 는 용기 내부에 해야 하며 영구적일 필요는 없다. Ex 표시 문자열은 외부에 표시되어서는 안 된다. 용기 외부에는 제조자의 이름 및 용기의 식별 정보(형식 또는 일련번호 등)만을 표시할 수 있다. 이 러한 표시는 영구적일 필요는 없다. 이러한 표시는 방폭부품 용기의 제조자가 기기 인증서의 소지자이기도 하고 방폭부품 인증서에 이러 한 사항이 사용제한표에 표시되었는 경우 생략할 수 있다. D.3.9 KS C IEC 60079-0 에 따라 기기의 외부에 표시를 부착하기 위한 조치가 마련되어야 한다. D.3.10 다음과 같은 정보가 사용제한표의 일부로 방폭부품 용기 인증서에 제공되어야 한다. a) 구멍의 최대 개수, 최대 크기 및 위치를 직접 표기하거나 관련 도면 번호를 명시하여야 한다. b) 오일로 채워진 차단기 및 접촉기를 사용할 수 없다. c) (주위온도 범위가 -20 °C 에서 +40 °C 가 아닌 경우) 주위온도 범위 d) (D.3.8 에 따라 해당하는 경우) 방폭부품 용기 제조자가 관련 기기 인증서의 유일한 소지자로 예정 되어 있음을 표시 e) (그룹 1, 그룹 IIA 및 그룹 IIB 방폭 부품 용기의 경우) 방폭부품 용기의 내용물은 각 단면적의 최 소 20 %의 단면적이 비어 있어 가스의 흐름을 방해하지 않아 폭발이 제한을 받지 않고 형성될 수 있다면 어떠한 방식으로든 배치할 수 있다. 각 구역이 어떠한 방향으로든 12.5mm 의 최소 치 수를 갖는 경우 별도의 완화 구역을 모을 수 있다. f) (그룹 IIC 방폭부품 용기의 경우) 방폭부품 용기의 내용물은 각 단면적의 최소 40 %의 단면적이 비어 있어 가스의 흐름을 방해하지 않아 폭발이 제한을 받지 않고 형성될 수 있다면 어떠한 방식 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 65 | {}
45e8dec6-3e3e-4b29-accf-0ecb256ca7a0 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 으로든 배치할 수 있다. 각 구역이 어떠한 방향으로든 12.5 mm 의 최소 치수를 갖는 경우 별도의 완화 구역을 모을 수 있다. 특정 구조에 요구되는 추가적인 제한사항(예: 투시창의 최고 작동온도) g) D.4 방폭기기 인증서 준비를 위한 방폭부품 용기 인증서의 활용(Utilization of an Ex component enclosure certificate to prepare an equipment certificate) D.4.1 절차(Procedure) 방폭부품 용기 인증서가 있는 용기는 일반적으로 방폭부품 용기에 이미 D.3.10 에 설명된 사용제한표 를 반영하여 적용된 요구사항을 반복적으로 적용하지 않고 KS C IEC 60079-0 및 이 표준을 적용한 기기 인증서에 통합될 수 있다. 방폭부품 용기 내부에 설치 조건과 함께 특정 부품, 허용되는 대체품 또는 생략 가능품 등을 설명하 는 기기 인증서에 대한 문서가 마련되어야 하며, 그럼으로써 방폭부품 용기 인증서의 사용제한표를 반영한 준수(compliance)가 검증될 수 있다. 방폭부품 용기 인증서에 따라 허용되는 모든 구멍은 방폭부품 용기 제조자 또는 기기 제조자와 방폭 부품 용기 제조자 사이의 합의 를 통해 기기 제조자가 뚫을 수 있다. 기준압력의 증가를 초래하는 심각한 난류를 발생시킬 수 있는 회전장치와 같은 장치의 지속적인 영 향을 고려하여야 한다. D.4.2 사용제한표의 적용(Application of the schedule of limitations) 사용제한표를 준수하는 것 외에도, 적용상의 모든 문제는 KS C IEC 60079-0 및 이 표준의 해당 요구 사항을 준수하기 위하여 고려되고 결정되어야 한다. 66 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f5efa3ce-70c1-4ac8-9e1f-ee0ccb0d970e | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 부속서 E (규정) 내압방폭 "d" 용기에 사용되는 전지 및 배터리 (Cells and batteries used in flameproof "d" enclosures) E.1 서언(Introductory remarks) 이 부속서에는 회로에 전력을 공급하기 위한 배터리로 사용되는 한 개 이상의 전지를 포함하는 방폭 구조 "d" 내압방폭용기에 의해 보호되는 전기기기에 대한 요구사항을 포함하고 있다. 사용되는 전기화학 전지 형식에 관계 없이, 주요 목적은 내압방폭용기 내부에서 가연성 전해 가스(일 반적으로 수소와 산소)의 혼합물이 발생하는 것을 방지하는 것이다. 이러한 관점에서 정상적인 사용 상태에서 전해 가스를 방출할 가능성이 있는(자연 배기 또는 압력배출밸브에 의해) 전지와 배터리는 내압방폭용기 내부에 사용해서는 안 된다. 비고 이러한 요구사항은 측정 장치로 사용되는 전기화학 전지(예: 산소 농도 측정에 사용되는 KS C IEC 60086-1 에 따른 형식 A 아연/산소 전지)에 적용되는 것은 아니다. E.2 허용되는 전기화학 시스템(Acceptable electrochemical systems) KS C IEC 전지 표준이 존재하는 아래의 표 E.1 및 표 E.2 에 열거된 전지만을 사용하여야 한다. 표 E.1 - 허용되는 1 차 전지 ¦ KS C IEC 60086-1 형식 ¦ 양극 ¦ 전해질 ¦ 음극 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ - ¦ 이산화 망간(MnO2) ¦ 염화 암모늄, 염화 아연 ¦ 아연(Zn) ¦ ¦ A ¦ 산소(O2) ¦ 염화 암모늄, 염화 아연 ¦ 아연(Zn) ¦ ¦ B ¦ 일산화탄소 화합물(CF)x ¦ 유기 전해질 ¦ 리튬(Li) ¦ ¦ C ¦ 이산화 망간(MnO2) ¦ 유기 전해질 ¦ 리튬(Li) ¦ ¦ E ¦ 염화 티오닐 (SOCl2) ¦ 비수성 유기염 ¦ 리튬(Li) ¦ ¦ L ¦ 이산화 망간(MnO2) ¦ 알칼리금속 수산화물 ¦ 아연(Zn) ¦ ¦ S ¦ 산화 은(AG2O) ¦ 알칼리금속 수산화물 ¦ 아연(Zn) ¦ ¦ a ¦ 이산화 황(SO2) ¦ 비수성 유기염 ¦ 리튬(Li) ¦ ¦ a ¦ 수은(Hg) ¦ 알칼리금속 수산화물 ¦ 아연(Zn) ¦ ¦ 비고 아연/이산화망간 전지는 KSCIEC 60086-1 에 열거되어 있지만 형식 문자로 분류되지는 않는다. ¦ 비고 아연/이산화망간 전지는 KSCIEC 60086-1 에 열거되어 있지만 형식 문자로 분류되지는 않는다. ¦ 비고 아연/이산화망간 전지는 KSCIEC 60086-1 에 열거되어 있지만 형식 문자로 분류되지는 않는다. ¦ 비고 아연/이산화망간 전지는 KSCIEC 60086-1 에 열거되어 있지만 형식 문자로 분류되지는 않는다. ¦ ¦ a KS C IEC 전지 표준이 있는 경우에만 사용될 수 있음. ¦ a KS C IEC 전지 표준이 있는 경우에만 사용될 수 있음. ¦ a KS C IEC 전지 표준이 있는 경우에만 사용될 수 있음. ¦ a KS C IEC 전지 표준이 있는 경우에만 사용될 수 있음. ¦ 67 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c5054788-c2f6-44ef-bead-adab85f3c316 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 표 E.2 - 허용되는 2 차 전지 ¦ 관련 KS C IEC 표준/형식 ¦ 형식 ¦ 전해질 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 형식 K KS C IEC 61951-1 KS C IEC 60623 KS C IEC 60622 ¦ 니켈-카드뮴(Ni-Cd) ¦ 수산화칼륨(KOH) ¦ ¦ KS C IEC 61960 ¦ 리튬(Li) ¦ 비수성 유기염 ¦ ¦ KS C IEC 61951-2 ¦ 수산화니켈금속 ¦ 수산화칼륨(KOH) ¦ E.3 내압방폭용기 내부 전지(또는 배터리)에 대한 일반 요구사항 (General requirements for cells (or batteries) inside flameproof enclosures) E.3.1 다음과 같은 사용의 제한을 특정 형식의 전지에 적용하여야 한다. 통기 또는 개방형 2 차 전지(vented or open secondary cells)는 내압방폭용기 내부에서 배터리를 구 성하기 위하여 사용할 수 없다. 밀봉된 밸브 조절형 전지(sealed valve regulated cells)는 내압방폭용기 내부에서 사용할 수 있지만, 방출 목적으로만 사용한다. E.5 의 요구사항에 따라, 가스 밀폐형 2 차 전지(sealed gas tight secondary cells)는 내압방폭용기 내 부에서 재충전될 수 있다. E.3.2 배터리를 포함한 내압방폭용기는 20.2 의 표 14, d)에 따라 표시되어야 한다. 이 요구사항은 배터리 및 배터리에 연결된 회로가 KS C IEC 60079-11 을 준수하고 배터리가 사용 중 재충전되지 않을 경우에는 적용할 필요가 없다. E.3.3 배터리 및 관련 안전 장치는 견고하게 고정되어야 한다(예: 설계된 전용 클립 또는 브래킷으로 제자리에 고정). E.3.4 관련 방폭구조의 요구사항에 대한 적합성을 손상시킬 수 있는 배터리와 관련 안전 장치 또는 장치 사이의 상대적인 움직임은 없어야 한다. E.3.5 E.3.3 및 E.3.4 에 대한 적합성은 KS C IEC 60079-0 에서 요구하는 용기에 대한 시험 전후에 검 증하여야 한다. E.4 안전 장치의 배치(Arrangement of safety devices) E.4.1 과도한 온도 상승 및 전지 손상 방지(Prevention of excessive temperature and cell damage) E.4.1.1 단락 방전 상태에서 배터리는 아래의 두 조건을 모두 만족하거나 E.4.1.2 에 설명된 안전 장 치를 설치하여야 한다. a) 전지 또는 배터리의 외부 표면 온도는 용기내 국부적인 주위온도를 고려하여 전지 또는 배터리 제조자가 지정한 연속사용온도를 초과 하지 않아야 하며 b) 최대 방전 전류는 전지 또는 배터리 제조자가 명시한 범위를 초과 하지 않아야 한다. 68 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
ce7d380b-b1b7-456d-920c-28a11a88f04e | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 E.4.1.2 상기 E.4.1.1 의 두 가지 조건을 달성할 수 없는 경우, KS C IEC 60079-11 에 정의 된 "ib" 보호 수준의 무고장 부품에 대한 요구사항을 충족시키는 안전장치가 필요하며 가능한 한 전지 또는 배터 리 단자 가까이에 위치해야 하며 다음 중 하나와 같아야 한다. 전류를 배터리 제조자가 명시한 최대연속인출전류(maximum continuous withdrawal current)로 제한 하는 저항기나 전류 제한 장치 퓨징 특성(fusing characteristic)이 배터리 제조자가 명시한 최대인출전류 및 허용 지속시간을 초과 하지 않도록 선택된, IEC 60127 시리즈에 적합한 퓨즈. 퓨즈가 교체형인 경우, 퓨즈 홀더 옆에 라 벨을 부착하여 사용하는 퓨즈의 형식을 명시하여야 한다. 저항기나 전류 제한 장치의 정격은 전지나 배터리의 전압을 기준으로 해야 한다. E.4.2 역극성 및 동일 배터리 내의 다른 전지로 인한 역충전의 방지(Prevention of cell polarity reversal or reverse charging by another cell in the same battery) E.4.2.1 배터리가 다음과 같을 경우, 극성 반전에 의한 전해 가스의 방출을 방지하거나 동일한 배터 리의 다른 전지에 의한 전지의 역충전을 방지하기 위해 추가적인 보호장치를 설치할 필요가 없다. a) 1.5 Ah 이하의 용량(1 h 방전율에서), 및 b) 용기의 빈 체적의 1 % 미만의 체적 E.4.2.2 배터리의 용량 및/또는 체적이 위의 값을 초과 하는 경우, 전지 역극성이나 동일 배터리 내의 다른 전지로 인한 역충전을 방지하기 위한 조치를 취해야 한다. 이것이 어떻게 달성될 수 있는지에 대한 두 가지 예가 아래에 나와 있다. 하나의 전지(또는 몇 개의 전지)에서 전지 전압을 모니터링하고 전압이 전지 제조자가 지정한 최 소 전압 미만으로 떨어지면 전원을 차단한다. 비고 1 이러한 보호는 주로 전지가 "과방전(deep discharge)" 상태가 되는 것을 방지하기 위해 사용 된다. 직렬로 연결된 전지를 너무 많이 모니터링하려고 시도하면 개별 전지 전압 및 보호회 로의 허용오차로 인해 보호 기능이 안정적으로 작동하지 않을 경우가 있다. 일반적으로 하 나의 보호 장치로 전지 6 개 이상의 전지(직렬)를 모니터링하는 것은 효과 적이지 않다. - 각 전지의 역극성 전압을 제한하기 위해 연결된 분로 다이오드(shunt diode)를 사용한다. 예를 들 어 직렬로 연결된 3 개의 전지로 구성된 배터리의 보호 장치는 그림 E.1 과 같다. ![image](/image/placeholder) +Ve -Ve 그림 E.1 - 직렬로 연결된 전지 3 개를 위한 다이오드의 배열 이 방호 장치가 효과 적이기 위해서는, 전지의 역충전을 방지하는 데 사용되는 각 다이오드의 순방향 전압 강하가 해당 전지의 안전 역충전 전압(safe reverse charge voltage)을 초과 해서는 안 된다. 비고 2 실리콘 다이오드는 이 요구사항을 충족시키기에 적합한 것으로 간주된다. 69 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f4faac5d-f085-47e2-86a4-afb5fd44cfa9 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 E.4.3 용기 내의 다른 전압원에 의한 배터리의 의도치 않은 충전 방지(Prevention of inadvertent chargin g of a battery by other voltage sources in the enclosure) 배터리가 다음과 같을 경우, 재충전 전류에 의한 전해 가스의 방출을 방지하기 위해 추가적인 보호 장치를 설치할 필요가 없다. a) 1.5 Ah 이하의 용량(1 h 방전율에서), 및 b) 용기의 빈 체적의 1 % 미만의 체적 동일한 용기 내에 다른 전압원(다른 배터리를 포함)이 있는 경우, 배터리 및 관련 회로는 충전용으로 특별히 설계된 회로 이외의 회로에 의한 충전으로부터 보호되어야 한다. 그 예는 다음과 같다. 오염(contamination)을 일으킬 수 있는 최고 전압에 대한 KS C IEC 60079-7 에 명시된 공간거리 및 연면거리를 사용하여 배터리 및 관련 회로를 용기 내부의 다른 모든 전압원과 분리 전원의 최대 고장 전류를, 존재할 가능성이 있는 시간 동안(퓨즈나 접지고장보호와 같이 제공되는 모든 회로 보호를 고려한), 전달할 수 있는 접지된 금속 배리어/스크린(barrier/screen)을 사용하여 배터리 및 관련 회로를 용기 내부의 다른 모든 전압원과 분리 KS C IEC 60079-7 에 규정된 공간거리와 연면거리를 사용하여 배터리만을 다른 전압원과 분리하되, 그림 E.2 와 같이 차단 다이오드(blocking diodes)를 설치 배열하여 두 다이오드 모두 단락을 유발하 는 단일 고장(single fault)의 위험을 감소시킨다. ![image](/image/placeholder) +Ve H -Ve 그림 E.2 - E.4.3 을 충족하기 위한 차단 다이오드의 설치(세 번째 예) E.4.3 의 예시 요구사항은 전압 기준점(voltage reference point)을 생성하기 위해 배터리에 연결된 회로 또는 E.5 에 따라 2 차 배터리를 충전하기 위한 충전 전원에 연결된 회로에는 적용하지 않는다. E.5 내압방폭용기 내부 2 차 전지의 재충전(Recharging of secondary cells inside flameproof enclosures) E.5.1 표 E.2 에 열거된 전지만 내압방폭용기 내부에서 충전할 수 있다. E.5.2 전지나 배터리를 내압방폭용기 내부에서 충전하는 경우, 충전 조건은 제조자의 문서에 모두 명 시되어야 하며 안전 장치는 이러한 조건이 초과 되지 않도록 보장하기 위해 설치되어야 한다. E.5.3 충전 장치는 역충전을 방지할 수 있는 것이어야 한다. E.5.4 배터리가 다음과 같을 경우, 재충전 전류에 의한 전해 가스의 방출을 방지하기 위해 추가적인 보호장치를 배터리에 설치할 필요가 없다. a) 1.5 Ah 이하의 용량, 및 b) 용기의 빈 체적의 1 % 미만의 체적 비고 위의 내용은 안전 장치가 설치되지 않은 전지(또는 배터리)의 사용을, 예를 들어 프로그램 가 능한 전자 회로의 메모리를 유지하기 위해 사용되는 "버튼형 전지(button type cells)"와 같은 유 70 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
1ed9a093-d92a-420c-899f-1735e144fbbb | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 형으로 효과 적으로 제한한다. E.5.5 용량 및/또는 체적이 상기 값을 초과 하는 배터리를 사용하는 경우, 배터리 내부 전지의 전압이 제조자가 지정한 최대 전압을 초과 하는 경우 충전 전류를 차단하고 전해 가스의 생성 및 방출을 방 지하도록 구성된 안전장치가 전지에 장착된 경우에만 내압방폭용기 내부에서 재충전이 허용된다. E.6 보호 다이오드의 정격 및 보호 장치의 신뢰성(Rating ofprotection diodes and reliability of protection devices) E.6.1 E.4.2 에 적합하도록 설치된 보호 다이오드의 정격 전압은 배터리의 최대 개방 회로 전압 이상 이어야 한다. E.6.2 E.4.3(세 번째 예)에 적합하도록 설치된 직렬 차단 다이오드의 정격 전압은 내압방폭용기 내부 의 최대 피크 전압 이상이어야 한다. E.6.3 보호 다이오드의 정격 전류는 E.4.1 에 따라 제한되는 최대 방전 전류 이상이어야 한다. E.6.4 이 표준에서 요구하는 안전 장치는 제어 시스템의 안전 관련 부분을 형성한다. 제어 시스템의 안전 무결성(safety integrity)이 이 표준에서 요구하는 안전 수준과 일치하는지 평가하는 것은 제조자 의 책임이다. 71 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
69f7b4fb-ab37-42c1-96fb-12375b1ff9b4 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 부속서 F (참고) 나사 및 너트의 기계적 특성 (Mechanical properties for screws and nuts) 11.3 의 요구사항을 적용할 때, 다음 정보가 유용할 수 있다. 표 F.1 - 나사 및 너트의 기계적 특성 ¦ 패스너 재료 ¦ 특성 등급 ¦ 공칭 인장 강도 MPa ¦ 최소 인장 강도 MPa ¦ 공칭 항복 응력 MPa ¦ 최소 항복 응력 MPa ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 탄소강 ¦ 3.6 ¦ 300 ¦ 330 ¦ 180 ¦ 190 ¦ ¦ 탄소강 ¦ 4.6 ¦ 400 ¦ 400 ¦ 240 ¦ 240 ¦ ¦ 탄소강 ¦ 4.8 ¦ 400 ¦ 420 ¦ 320 ¦ 340 ¦ ¦ 탄소강 ¦ 5.6 ¦ 500 ¦ 500 ¦ 300 ¦ 300 ¦ ¦ 탄소강 ¦ 5.8 ¦ 500 ¦ 520 ¦ 400 ¦ 420 ¦ ¦ 탄소강 ¦ 6.8 ¦ 600 ¦ 600 ¦ 480 ¦ 480 ¦ ¦ 탄소강 ¦ 8.8 ≤ M16 ¦ 800 ¦ 800 ¦ 640 ¦ 640 ¦ ¦ 탄소강 ¦ 8.8 > M16 ¦ 800 ¦ 830 ¦ 640 ¦ 660 ¦ ¦ 탄소강 ¦ 9.8 ¦ 900 ¦ 900 ¦ 720 ¦ 720 ¦ ¦ 탄소강 ¦ 10.9 ¦ 1 000 ¦ 1 040 ¦ 900 ¦ 940 ¦ ¦ 탄소강 ¦ 12.9 ¦ 1 200 ¦ 1 220 ¦ 1 080 ¦ 1 100 ¦ ¦ 스테인리스강 (오스테나이틱) ¦ A*-50 ¦ ¦ 500 ¦ ¦ 210 ¦ ¦ 스테인리스강 (오스테나이틱) ¦ A*-70 ¦ ¦ 700 ¦ ¦ 450 ¦ ¦ 스테인리스강 (오스테나이틱) ¦ A*-80 ¦ ¦ 800 ¦ ¦ 600 ¦ ¦ 스테인리스강 (마텐자이틱) ¦ C*-50 ¦ ¦ 500 ¦ ¦ 250 ¦ ¦ 스테인리스강 (마텐자이틱) ¦ C*-70 ¦ ¦ 700 ¦ ¦ 410 ¦ ¦ 스테인리스강 (마텐자이틱) ¦ C*-80 ¦ ¦ 800 ¦ ¦ 640 ¦ ¦ 스테인리스강 (마텐자이틱) ¦ C*-110 ¦ ¦ 1 100 ¦ ¦ 820 ¦ ¦ 스테인리스강 (페라이틱) ¦ F1-45 ¦ ¦ 450 ¦ ¦ 250 ¦ ¦ 스테인리스강 (세라이틱) ¦ F1-60 ¦ ¦ 600 ¦ ¦ 410 ¦ ¦ 비고 위의 스테인리스강 A 급 및 C 급의 경우, "*" 표시는 속성 등급 숫자로 대체된다. ¦ 비고 위의 스테인리스강 A 급 및 C 급의 경우, "*" 표시는 속성 등급 숫자로 대체된다. ¦ 비고 위의 스테인리스강 A 급 및 C 급의 경우, "*" 표시는 속성 등급 숫자로 대체된다. ¦ 비고 위의 스테인리스강 A 급 및 C 급의 경우, "*" 표시는 속성 등급 숫자로 대체된다. ¦ 비고 위의 스테인리스강 A 급 및 C 급의 경우, "*" 표시는 속성 등급 숫자로 대체된다. ¦ 비고 위의 스테인리스강 A 급 및 C 급의 경우, "*" 표시는 속성 등급 숫자로 대체된다. ¦ 72 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
82982f2e-293a-4c8a-8fbd-27a84036a61e | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 부속서 G (규정) 내부 누출원(컨테인먼트 시스템)이 있는 내압방폭용기의 추가 요구사항 (Additional requirements for flameproof enclosures with an internal source of release (containment system)) G.1 일반사항(General) 컨테인먼트 시스템은 내압방폭용기를 통과 하여 용기에 내부 누출 또는 배선 시스템으로의 내부 누출 을 초래할 수 있는 공정 유체를 담고 있는 기구의 일부분이다. G.1 참조 정상적인 공기에서 발견되는 것보다 큰 농도의 산소 또는 기타 산화제의 내부 누출원이 있는 기기는 이 표준의 범위를 벗어난다. 비고 정상 또는 비정상 상태에서의 누출로 인하여 공기를 포함 가연성 또는 비가연성의 공정 유체 가 컨테인먼트 시스템에서 내압방폭용기로 누출될 때, 때때로 인입 흐름 제한장치(inlet flow restrictors) 및 통기/배수 장치의 사용을 내압방폭용기의 내부 압력이 KS C IEC 60079-0 의 적용 범위에 나타난 90 kPa ~ 110 kPa(절대압력) 사이의 대기압으로 유지되도록 필요로 할 수 있다. 잠재적 누출원에는 O-링, 개스킷, 나사 접합부, 플랜지 접합부, 공정 연결부 및 기타 부품이 포 함된다. ![image](/image/placeholder) 컨테인먼트 시스템 내압방폭용기 통기 배수 장치 유량 제한장치 통기/배수 장치 또는 화염방지기 그림 G.1 - 컨테인먼트 시스템이 있는 내압방폭용기 G.2 누출 조건(Release conditions) G.2.1 누출 없음(No release) 73 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
76178e23-50ec-41af-b918-a9984e716362 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 컨테인먼트 시스템이 무고장(infallible) 구조인 경우, 내부 누출은 없다. 무고장 컨테인먼트 시스템에 대한 설계 요구사항을 참조 G.2.2 가스 또는 증기의 제한적 누출(Limited release of a gas or vapour) 공정 유체가 내압방폭용기로 누출되는 속도는 컨테인먼트 시스템의 모든 고장 조건에서 예측 가능해 야 한다. 제한적 누출이 있는 컨테인먼트 시스템에 대한 설계 요구사항 참조 비고 이 표준의 목적상, 액화가스의 누출은 가스 누출로 간주한다. G.2.3 액체의 제한적 누출(Limited release of a liquid) 공정 유체가 내압방폭용기로 누출되는 속도는 가스 또는 증기에 대해서는 제한되지만, 액체의 증기 로의 변환은 예측할 수 없다. 내압방폭용기 내부에 액체가 축적될 가능성과 그 결과 에 대해 고려해 야 한다. 제한적 누출이 있는 컨테인먼트 시스템에 대한 설계 요구사항 참조 G.3 컨테인먼트 시스템의 설계 요구사항(Design requirements for the containment system) G.3.1 일반 설계 요구사항(General design requirements) 누출이 발생할지 여부를 결정하는 컨테인먼트 시스템의 설계 및 구조는 제조자가 지정한 최악의 사 용 조건을 기반으로 해야 한다. 컨테인먼트 시스템은 무고장이거나 제한적 누출이어야 한다. 제조자는 컨테인먼트 시스템 인입부(inlet)의 최대 압력을 명시해야 한다. 컨테인먼트 시스템의 설계 및 구조에 대한 세부 사항(공정 유체의 종류, 작동 조건 및 해당 위치에서 의 예상 누출 속도 등)은 컨테인먼트 시스템이 무고장 컨테인먼트 시스템 또는 제한적 누출이 있는 컨테인먼트 시스템으로 평가될 수 있도록 제조가가 제공해야 한다. 컨테인먼트 시스템이 이 표준의 무고장 컨테인먼트 시스템에 대한 요구사항을 충족하지 못한다면, 컨테인먼트 시스템의 모든 입구와 출구는 내압방폭용기의 벽에 통기/배수 장치 또는 화염방지 장치 를 갖추고 있어야 하며, 이는 용기와 분리되거나 통합되어 있을 수 있으며 15 절의 형식 시험을 수행 하는 동안 고려되어야 한다. 컨테인먼트 시스템 내부의 점화원은 별도로 고려되어야 하며 통기/배수 장치 또는 화염방지 장치가 필요할 수도 있다. G.3.2 무고장 컨테인먼트 시스템(Infallible containment system) 컨테인먼트 시스템은 움직이는 접합부(moving joints)를 포함하지 않는 금속, 세라믹 또는 유리 재료의 파이프, 튜브 또는 용기로 구성되어야 한다. 접합부는 용접, 브레이징, 유리와 금속 간의 밀봉 또는 공정 방법(eutectic methods)으로 이루어져야 한다. 비고 1 공정 방법은 일반적으로 금속성의 두 개 이상의 구성 부품을 결합하는 것으로, 결합되는 어 느 부품의 응고 시작보다 낮은 일정 온도에서 응고하는 2 원 또는 3 원 합금 시스템을 사용하 는 결합 방법이다. 74 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
fe88b04b-f91c-47d7-a8d2-34f4f51d726c | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 납/주석 복합 재료와 같은 저온 땜납 합금(solder alloys)은 허용되지 않는다. 비고 2 불리한 작동 조건(내압방폭용기의 문 또는 덮개가 열렸을 때의 진동, 열충격 및 유지보수 작 업 포함)은 잠재적으로 깨지기 쉬운 컨테인먼트 시스템에 손상을 줄 수 있다. 컨테인먼트 시스템의 외부 표면은 내압방폭용기를 완성하는 역할을 한다. 따라서 컨테인먼트 시스템 과 내압방폭용기의 전체 조립품은 동일한 합격/불합격 기준이 적용되는 독립적 내압방폭용기로서 동 일한 형식 시험을 모두 거쳐야 한다. 비고 3 이 부속서에서는 컨테인먼트 시스템이 내압방폭용기인 것처럼 내부 체적을 평가하는 것을 의도하지 않는다. G.3.3 제한적 누출이 있는 컨테인먼트 시스템(Containment system with a limited release) 컨테인먼트 시스템의 고장 우려 때문에, 컨테인먼트 시스템으로 유입되는 공정 유체의 흐름은 내압 방폭용기 외부에 설치된 유량 제한장치(flow limiting devices)를 통해 예측 가능한 속도로 제한되어야 한다. 유량 제한장치는 컨테인먼트 시스템이 내압방폭용기로 들어가는 인입부부터 유량 제한장치의 입구를 포함한 유량 제한장치까지 무고장 컨테인먼트 시스템에 대한 설계 요구사항을 충족하는 경우 내압방 폭용기 내부에 설치될 수 있다. 이러한 유량 제한장치는 영구적으로 고정되어야 하며 움직이는 부품 이 없어야 한다. 유량 제한장치는 중합체 또는 탄성 중합체 물질(polymeric or elastomeric materials)을 포함하지 않아야 하지만 세라믹 또는 유리 물질은 포함할 수 있다. 또한 컨테인먼트 시스템의 고장 문제로 인하여 내압방폭용기 주위 대기압의 1.1 배 이상의 내압 상승 은 없어야 한다. 비고 내부 압력의 잠재적인 상승을 제한하기 위해, 내압방폭용기의 벽에 설치된 통기/배수 장치 및 이들 장치와 유량 제한장치 간의 조정(coordination)이 때때로 사용된다. 정상 동작 조건에서, 제한된 누출이 있는 컨테인먼트 시스템은 차압이 0.1 MPa(1 bar)에서 10-2Pa x l/s (10-4mbar x I/s) 미만의 헬륨 누설률과 동등한 최대 누설률을 달성하도록 밀봉되어야 한다. 탄성 중합체 실(elastomeric seals), 창 및 기타 컨테인먼트 시스템의 비금속 부품은 허용된다. 관용 나사, 압착 접합부(예: 금속 압착 피팅) 및 플랜지 접합 등도 허용된다. G.4 컨테인먼트 시스템에 대한 형식 시험(Type tests for the containment system) G.4.1 내압시험(Overpressure test) 무고장 컨테인먼트 시스템 또는 제한적 누출이 있는 컨테인먼트 시스템의 경우, 적어도 2 분 동안 최대 정격 압력의 4 배 이상, 적어도 1 000 Pa 이상의 시험 압력을 컨테인먼트 시스템에 가해야 한다. 컨테인 먼트 시스템은 최저 및 최고 서비스 온도 모두에서 시험되어야 한다. 일상시험은 필요하지 않다. 제한된 누출이 있는 컨테인먼트 시스템의 경우, 정상 사용을 위해 명시된 최대 내부 압력의 적어도 1.5 배, 최소 200 Pa 시험 압력을 컨테인먼트 시스템에 가하고 적어도 2 분 이상 유지해야 한다. 동일 75 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
4d8a3fe1-74a8-494d-aec5-569d67a491c4 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 한 조건하에서 일상 내압시험이 요구된다. 시험압력은 5 초 이내에 최대 압력에 도달해야 한다. 영구적인 변형이 발생하지 않고 무고장 컨테인먼트 시스템 또는 제한된 누출이 있는 컨테인먼트 시 스템에 대한 해당 누설 시험에 대한 적합성이 검증된다면 이 시험은 만족스러운 것으로 간주한다. G.4.2 무고장 컨테인먼트 시스템에 대한 누설 시험(Leakage test for an infallible containment system) 컨테인먼트 시스템은 다음과 같아야 한다. 최대 정격 압력과 같은 압력으로 헬륨으로 주위를 채운다. 컨테인먼트 시스템을 절대압력 0.1 Pa 이하로 감압시킨다. 진공 챔버에 넣고 최대 정격 압력으로 헬륨 공급 장치에 연결한다. 진공 챔버를 절대압력 0.1 Pa 이하로 감압시킨다. 시험은 진공 시스템이 동작하는 상태에서 절대압력 0.1 Pa 을 유지할 수 있다면 만족스러운 것으로 간주한다. G.4.3 제한된 누출이 있는 컨테인먼트 시스템에 대한 누설 시험(Leakage test for a containment system with a limited release) 컨테인먼트 시스템은 다음과 같아야 한다. 최대 정격 압력과 같은 시험 압력으로 하되 최소 1 000 Pa 이상의 헬륨으로 주위를 채운다. 최대 정격 압력으로 헬륨 공급 장치에 연결하되 최소 1 000 Pa 이상으로 한다. 최대 헬륨 누설률은 10-2Pa x l/s (10-4mbar x I/s) 미만이어야 한다. 76 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
f52d91cd-2d62-469a-b770-eee45044aa03 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 부속서 H (규정) 컨버터 공급 내압방폭 "d"형 회전기기에 대한 요구사항 (Requirements for machines with flameproof "d" enclosures fed from converters) H.1 일반사항(General) 이 부속서에는 컨버터와 함께 사용하는 회전전기기기에 대한 요구사항을 포함하고 있다. H.2 베어링 설치 요구사항(Construction requirements for bearings) 내압방폭용기 내부에 위치한 베어링의 경우에도 KS C IEC 60079-0 의 베어링 요구사항을 적용한다. 비고 샤프트 및 베어링 표류 전류(stray current)는 조기에 베어링의 고장을 발생시켜 기계적 고장을 초래하고, 이로 인해 외부 분위기에 열적 점화(thermal ignition)를 발생시킬 수 있다. 또한 이러 한 샤프트 및 베어링의 표류 전류로 인해 샤프트와 하우징 또는 구동 장치(driven equipment) 사이에 불꽃을 일으켜 점화가 발생할 수 있다. H.3 온도 요구사항(Temperature requirements) 해당 온도등급의 결정은 다음을 통해 이루어질 수 있다. KS C IEC 60079-0 에 기술된 바와 같이 지정된 듀티(specified duty)에 대해 모터와 특정 컨버터를 함께 평가 로터 베어링, 베어링 캡 및 샤프트 익스텐션(shaft extensions)에서 과도한 온도를 감지할 수 있는 충분한 여유(margin)를 가지고 보통 고정자 권선에 설치되는 적절한 직접 과열 보호 장치의 설치 (provision of appropriate direct thermal protection). 이러한 여유는 시험이나 계산을 통해 결정할 수 있다. 과열 보호 장치의 사용은 인증서의 특정사용조건에 이를 명시함으로써 의무 사항으로 할 수 있다. 비고 전형적인 설치의 경우, 고정자 권선에 내장(팬의 반대쪽 권선의 한 상에 하나씩)된 PTC 160 서 미스터(thermistors) 또는 160 °C 서모스텟(thermostats)을 사용하면 온도 등급 T3 할당이 정당 하다는 것이 판명되었다. 77 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
4feed9b1-8059-4903-991b-b5260a3732bd | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 참고문헌 [1] IEC 60050-426, International Electrotechnical Vocabulary - Part 426: Equipment for explosive atmospheres [2] ISO/IEC 60079-20-1, Explosive atmospheres - Part 20-1: Material characteristics for gas and vapour classification - Test methods and data [3] KS A ISO 80000-1, 양 및 단위 - 제 1 부: 일반사항 [4] ANSI/UL 1203, Explosion-proof electrical equipment for use in hazardous (classified) locations [5] KS Q ISO 2859-1, 계수형 샘플링검사 절차 - 제 1 부: 로트별 합격품질한계(AQL) 지표형 샘플링 검사 방식 KS C IEC 60034-1, 회전기기 - 제 1 부: 정격 및 성능 IEC 60079(all parts), Explosive atmospheres KS C IEC 60079-14, 방폭 기기 - 제 14 부: 폭발 위험 장소에서의 전기 설비 KS C IEC 60086-1, 일차전지 - 일반사항 KS C IEC 60112, 고체 절연 재료의 내트래킹 및 비교 트래킹 지수 측정 방법 KS C IEC 60622, 각형 밀폐형 니켈 · 카드뮴 축전지 KS C IEC 60623, 알칼리 또는 기타 비-산성 전해질을 포함하는 2 차 단전지와 전지 - 각형 배기식 니켈-카드뮴 축전지 IEC 61508(all parts), Functional safety of electrical/electronic/programmable electronic safety-related systems KS C IEC 61951-1, 알칼리 또는 기타 비산성 전해질을 포함하는 이차 단전지 및 전지 - 휴대기기용 이차 밀폐 단전지 및 전지 - 제 1 부: 니켈-카드뮴 KS C IEC 61951-2, 알칼리 또는 기타 비산성 전해질을 포함하는 이차 단전지 및 전지 - 휴대기기용 이차 밀폐 단전지 및 전지 - 제 2 부: 니켈-수소 KS C IEC 61960, 휴대 기기용 리튬 2 차 전지 ISO 185, Grey cast irons - Classification ISO 468, Surface roughness - Parameters, their values and general rules for specifying requirements (withdrawn in 1998) 78 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
35a226ff-6c3b-44f5-ae39-947833d74ce8 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 KS C IEC 60079-1:2014 해 설 이 해설은 본체 및 부속서에 규정 · 기재한 사항과 이것들과 관련된 사항을 설명하는 것으로 표준의 일부는 아니다. 1 개정 취지 이 표준은 기존 2007 년 제 6 판 IEC 60079-1 을 기초로 하여 발행된 KS C IEC 60079-1 표준을 최신 국 제표준인 2014 년 제 7 판 IEC 60079-1, Exprosive atmospheres Part 1: Equipment protection by flameproof enclosures "d" 및 Corrigendum 1(2018)을 기초로 해당 표준의 기술적 내용 및 대응국제표 준의 구성을 변경하지 않고 작성한 한국산업표준이다. 2 개정 내용 기존 KS C IEC 60079-1:2012 에서 현 KS C IEC 60079-1:2014 로의 변경사항은 다음과 같다. ¦ ¦ ¦ 타입 ¦ 타입 ¦ 타입 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 변경사항에 대한 설명 ¦ 조항 ¦ 경미한 변경 및 편집상 변경 ¦ 확장 ¦ 주요 기술적 변경 ¦ ¦ 인용표준 (KS C IEC 60079-0 발행 일자 삭제) ¦ 2 절 ¦ X ¦ ¦ ¦ ¦ 보호등급 "da"의 요구사항 (휴대용 가연성 가스 감지기의 촉매 센서) ¦ 4.2 ¦ ¦ X ¦ ¦ ¦ 보호등급 "dc"의 요구사항 [KS C IEC 60079-15 상의 차단기(Enclosed break devices)] ¦ 4.4, 15.5 ¦ X ¦ ¦ ¦ ¦ 접합부의 일반 요구사항 (부식억제용 그리스 사용 관련 문서화) ¦ 5.1 ¦ X ¦ ¦ ¦ ¦ 접합부의 일반 요구사항 (보수작업을 하면 안 되는 접합부 표시) ¦ 5.1 ¦ ¦ X ¦ ¦ ¦ 접합부의 일반 요구사항 (0.008 mm 두께 이상의 전기도금) ¦ 5.1 ¦ ¦ X ¦ ¦ ¦ 비나사접합, 틈새(1) (플랜지 접합부 표면 틈새) ¦ 5.2.2 ¦ X ¦ ¦ ¦ ¦ 톱니접합 (사용 및 시험 시 요구사항) ¦ 5.2.8 ¦ X ¦ ¦ ¦ ¦ 다단 접합 (3 단 이하로 인접하고 2 회 경로 변경) ¦ 5.2.9 ¦ ¦ X ¦ ¦ ¦ 그룹 IIA 및 IIB 용기의 접합부 최소 길이와 최대 틈새 (플랜지의 최대 틈새, 최소 9.5 mm 길이 및 체적 2 000 cm3 이상에서의 원통 또는 마개 접합) ¦ 표 2 ¦ ¦ X ¦ ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 79 | {}
4f88d217-7025-4ae8-a343-24f4bfa317cf | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 ¦ ¦ ¦ 타입 ¦ 타입 ¦ 타입 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 변경사항에 대한 설명 ¦ 조항 ¦ 경미한 변경 및 편집상 변경 ¦ 확장 ¦ 주요 기술적 변경 ¦ ¦ 그룹 1, 그룹 IIA, 그룹 IIB 및 그룹 IIC 용기 의 접합부 최소 길이와 최대 틈새 (KS A ISO 80000-1 에서 구조 관련 수치) ¦ 표 2, 표 3 ¦ X ¦ ¦ ¦ ¦ 원통 나사 접합 (ISO 965-1 나사산의 형상 또는 체결) ¦ 표 4 ¦ X ¦ ¦ ¦ ¦ 테이퍼 나사 접합 (외부, 내부 나사의 구조) ¦ 표 5 ¦ X ¦ ¦ ¦ ¦ 고착 접합 (기계강도 보증에 대한 추가사항) ¦ 6.1.2 ¦ ¦ ¦ C1 ¦ ¦ 고착 접합 (누설 발생 시 평가에 관한 사항) ¦ 6.1.2 ¦ ¦ X ¦ ¦ ¦ 유리 접합부 (유리-금속 접합부) ¦ 6.2 ¦ ¦ X ¦ ¦ ¦ 통기 및 배수 장치의 온도시험 (10 분간 시험 후 외부 표면온도에 따른 온도 등급) ¦ 10.9.3.2 ¦ X ¦ ¦ ¦ ¦ 통기 및 배수 장치의 내압시험 (온도시험 전부터 인화시험 이후까지 위치 변경) ¦ 10.9.3.4 ¦ X ¦ ¦ ¦ ¦ 방폭 부품의 인증서 (KS C IEC 60079-0 에 따른 비금속 용기의 서 비스 온도 범위) ¦ 10.9.4 ¦ X ¦ ¦ ¦ ¦ 패스너 (fastener) 및 개구부 (블랭킹엘리먼트 13.8 및 C.2.3 의 관련 사항 위치 변경) ¦ 11 절 ¦ X ¦ ¦ ¦ ¦ 패스너 및 개구부, 특성 등급 또는 항복응력 (인증서의 특정사용조건) ¦ 11.3 ¦ X ¦ ¦ ¦ ¦ 패스너 및 개구부 (용기의 벽면 구멍) ¦ 11.8 ¦ X ¦ ¦ ¦ ¦ 재질 (아세틸렌 가스 분위기에서 재질 사용제한) ¦ 12.8 ¦ ¦ ¦ C2 ¦ ¦ 내압방폭용기의 인입부, 일반사항 (미터 나사 및 NPT 나사 인입부) ¦ 13.1 ¦ X ¦ ¦ ¦ ¦ 내압방폭용기의 인입부, 일반사항 (그룹 I 비나사접합) ¦ 13.1 ¦ ¦ X ¦ ¦ ¦ 내압방폭용기의 인입부, 나사산이 없는 구멍 (그룹 I 적용사항) ¦ 13.3 ¦ ¦ X ¦ ¦ ¦ 내압방폭용기의 인입부, 케이블 글랜드 (그룹 I 적용사항) ¦ 13.4 ¦ ¦ X ¦ ¦ ¦ 케이블 글랜드, 전선관 밀봉장치 (체결작업에 관한 문서화) ¦ 13.4, 13.5 ¦ X ¦ ¦ ¦ ¦ 플러그, 소켓 및 케이블 커플러 (아크소멸시험에서 전기부하의 요건) ¦ 13.6.4 ¦ ¦ ¦ C3 ¦ 80 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
831da54b-5619-4a22-a670-05c5edc7aa12 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 ¦ ¦ ¦ 타입 ¦ 타입 ¦ 타입 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 변경사항에 대한 설명 ¦ 조항 ¦ 경미한 변경 및 편집상 변경 ¦ 확장 ¦ 주요 기술적 변경 ¦ ¦ 부싱 (체결작업에 관한 문서화) ¦ 13.7 ¦ X ¦ ¦ ¦ ¦ 블랭킹엘리먼트 (11 절에서 이동) ¦ 13.8 ¦ X ¦ ¦ ¦ ¦ 검증 및 시험 (최고표면온도 조건) ¦ 표 6 ¦ X ¦ ¦ ¦ ¦ 형식 시험 (시료의 수량 및 시험절차) ¦ 15 절 ¦ X ¦ ¦ ¦ ¦ 폭발압력의 결정, 일반사항 (난기류를 야기할 수 있는 기구) ¦ 15.2.2.2 ¦ X ¦ ¦ ¦ ¦ 폭발압력의 결정, 일반사항 (그룹 IIC 에서 시험의 횟수) ¦ 15.2.2.2 ¦ X ¦ ¦ ¦ ¦ 폭발압력의 결정, 일반사항 (그룹 IIB 에서 시험의 횟수) ¦ 15.2.2.4 ¦ X ¦ ¦ ¦ ¦ 폭발압력의 결정, 일반사항 (단일 가스용 기기의 표기) ¦ 15.2.2.5 ¦ X ¦ ¦ ¦ ¦ 내압시험, 일반사항 (주위온도 하한에서 내압시험이 필요하지 않은 경우) ¦ 15.2.3 ¦ X ¦ ¦ ¦ ¦ 내압시험 - 제 1 시험법(정압시험) (배치 단위로 일상시험 시 3 배 선택에 관한 사항) ¦ 15.2.3.2 ¦ ¦ X ¦ ¦ ¦ 내압시험 - 제 1 시험법(정압시험) (소형기기에서 주위온도 하한치에 대한 조정) ¦ 15.2.3.2 ¦ ¦ X ¦ ¦ ¦ 내압시험 - 제 2 시험법(동압시험) (시험의 횟수) ¦ 15.2.3.3 ¦ X ¦ ¦ ¦ ¦ 내부 점화에 의한 인화시험 (그리스 여부의 명확화) ¦ 15.3 ¦ X ¦ ¦ ¦ ¦ 인화시험에서 나사접합의 길이 감소 (ISO 965-1 및 ISO 965-3 표준에 따른 나사 산의 형상 또는 체결) ¦ 표 9 ¦ X ¦ ¦ ¦ ¦ 압력 또는 시험 틈새 증가를 위한 시험계수 (그룹 IIC 기기 주위온도 증가에 따른 조정) ¦ 표 10 ¦ X ¦ ¦ ¦ ¦ 내부 점화에 의한 인화시험, 그룹 1, 그룹 IIA 및 그룹 IIB(시험의 횟수) ¦ 15.3.2.3 ¦ X ¦ ¦ ¦ ¦ 내부 점화에 의한 인화시험 틈새를 증가하 여 그룹 IIC 시험(시험의 횟수) ¦ 15.3.3.2 ¦ X ¦ ¦ ¦ ¦ 내부 점화에 의한 인화시험, 그룹 IIC (시험가스의 산소농도) ¦ 15.3.3.4 ¦ ¦ X ¦ ¦ ¦ 통기 및 배수장치가 장착된 용기의 온도시험 (10 분간 시험 실시 후 외부 표면온도에 따 른 온도등급) ¦ 15.4.3.1 ¦ X ¦ ¦ ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 81 | {}
2ee511b5-5913-4d23-9eea-8119cb71042b | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 ¦ ¦ ¦ 타입 ¦ 타입 ¦ 타입 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 변경사항에 대한 설명 ¦ 조항 ¦ 경미한 변경 및 편집상 변경 ¦ 확장 ¦ 주요 기술적 변경 ¦ ¦ "dc" 구조의 시험 (KS C IEC 60079-15 표준에 따른 밀봉형 차 단기) ¦ 15.5 ¦ ¦ X ¦ ¦ ¦ 일상시험(routine test), 일반사항 (소형 기기의 주위온도 하한 값의 조정) ¦ 16.1.2 ¦ ¦ X ¦ ¦ ¦ 일상시험, 일반사항 (제 2 시험법을 선택했을 때 선택사항) ¦ 16.1.3 ¦ X ¦ ¦ ¦ ¦ 일상시험, 일반사항 (용접부 검사 선택사항) ¦ 16.3 ¦ ¦ X ¦ ¦ ¦ 일상시험, 일반사항 (배치 단위 시험의 수용) ¦ 16.6 ¦ ¦ X ¦ ¦ ¦ 그룹 I 개폐기(switchgear) (EPL Mb 부합하는 요구사항) ¦ 17.2.2, 17.2.3 ¦ X ¦ ¦ ¦ ¦ 비금속 용기와 비금속 용기 부품, 일반사항 (고착 접합에 대하여는 예외) ¦ 19.1 ¦ X ¦ ¦ ¦ ¦ 비금속재 용기와 비금속재 용기 부품, 트래 킹 및 연면거리 저항치 (KS CIEC 60079-7 및 또는 KS C IEC 60079- 15 관련) ¦ 19.2 ¦ ¦ X ¦ ¦ ¦ 비금속 용기와 비금속 용기 부품, 형식 시험 요구사항 (시험절차의 분류) ¦ 19.3 ¦ X ¦ ¦ ¦ ¦ 사용설명서 (보수하면 안 되는 방폭 접합부의 검사) ¦ 21 절 ¦ ¦ X ¦ ¦ ¦ 부싱 (코어의 개수에 대한 문서화) ¦ C.2.1.4 ¦ X ¦ ¦ ¦ ¦ 부싱 (인화시험에서 요구사항) ¦ C.2.1.4 ¦ X ¦ ¦ ¦ ¦ 부싱 (누설이 있을 경우, 평가에 관한 사항) ¦ C.2.1.4 ¦ ¦ X ¦ ¦ ¦ 방폭 접합부, 나사접합 (요구사항) ¦ C.2.2.1 ¦ X ¦ ¦ ¦ ¦ 방폭 접합부, 비나사 접합 (그룹 I 적용) ¦ C.2.2.2 ¦ ¦ X ¦ ¦ ¦ 방폭 블랭킹 엘리먼트의 구조 요구사항 (11 절에서 이동) ¦ C.2.3.1 ¦ X ¦ ¦ ¦ ¦ 방폭 블랭킹 엘리먼트의 구조 요구사항 (미터 및 NPT 방폭 블랭킹 엘리먼트) ¦ C.2.3.2, C.2.3.3 ¦ X ¦ ¦ ¦ ¦ 방폭 블랭킹 엘리먼트의 구조 요구사항 (그룹 I 비나사식 구조) ¦ C.2.3.4 ¦ ¦ X ¦ ¦ ¦ 밀봉 시험, 일반사항 (열안정성 시험 후 다시 조임하는 것을 허 용) ¦ C.3.1.1 ¦ X ¦ ¦ ¦ 82 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
37063843-71c9-4d0a-80cf-9167c22ca5ba | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 ¦ ¦ ¦ 타입 ¦ 타입 ¦ 타입 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 변경사항에 대한 설명 ¦ 조항 ¦ 경미한 변경 및 편집상 변경 ¦ 확장 ¦ 주요 기술적 변경 ¦ ¦ 실링 링을 이용하는 케이블 글랜드와 전선 관 밀봉 장치 (내식강 맨드릴) ¦ C.3.1.2 ¦ X ¦ ¦ ¦ ¦ 방폭 블랭킹 엘리먼트 형식 시험, 토크 시험 (강재 시험블록) ¦ C.3.3.1 ¦ X ¦ ¦ ¦ ¦ 조임 토크값 (<16 mm 이하 나사산 사이즈 추가) ¦ 표 C.1 ¦ ¦ X ¦ ¦ ¦ 조임 토크값 (NPT 나사산 사이즈 추가) ¦ 표 C.2 ¦ ¦ X ¦ ¦ ¦ 방폭 부품용기의 요구사항 (표기내용에 관한 사항) ¦ D.3.8 ¦ ¦ ¦ C4 ¦ ¦ 방폭 부품용기의 요구사항 (인증서 내용에 관한 사항) ¦ D.3.10 ¦ ¦ X ¦ ¦ ¦ 기기 인증서 발행 시 방폭 부품용기의 사용 시 준비사항, 절차 (기기 내부에서 발생 가능한 난기류) ¦ D.4.1 ¦ ¦ X ¦ ¦ ¦ 허용 가능한 1 차 전지 (타입 B 전지 추가) ¦ 표 E.1 ¦ ¦ X ¦ ¦ ¦ 허용 가능한 1 차 전지 (타입 T 전지 제거) ¦ 표 E.1 ¦ ¦ ¦ C5 ¦ ¦ 허용 가능한 2 차 전지 (리튬 타입 전지 추가) ¦ 표 E.2 ¦ ¦ X ¦ ¦ ¦ 온도 초과 방지 및 전지 손상 (KS C IEC 60079-11 요구사항 적용) ¦ E.4.1.2 ¦ X ¦ ¦ ¦ ¦ 기기내부 기타 전압에 의한 예기치 않은 배 터리 충전방지 (구조상의 추가보호는 요구되지 않음.) ¦ E.4.3 ¦ ¦ X ¦ ¦ ¦ 내압방폭용기 내부에서 2 차 전지의 충전 (추가 배터리 선택사항) ¦ E.5.1 ¦ ¦ X ¦ ¦ ¦ 방폭기기의 보호등급을 포괄한 대체 위험성 평가 방법 (기존 부속서 삭제) ¦ 부속서 G ¦ X ¦ ¦ ¦ ¦ 내부 누출원을 가진 내압방폭용기의 추가 요구사항 (새로운 부속서 추가) ¦ 부속서 G ¦ ¦ X ¦ ¦ ¦ 컨버터를 사용하는 내압방폭용기 "d"의 요구 사항 (새로운 부속서 추가) ¦ 부속서 H ¦ ¦ X ¦ ¦ 비고 언급된 기술적 변경 사항에는 개정된 KS 표준의 기술적 주요 변경 변경 사항을 포함하지만, 이전 판의 모든 수정 사항을 세세히 나열하지는 않았다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 83 | {}
4cc72ec8-d38c-4b14-83eb-eeda10de2d52 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 설명: A) 정의 경미한 변경 및 편집상 변경 명확화 기술적 요구사항 축소 경미한 기술적 변경 편집 수정 이러한 변경은 편집상 또는 미미한 기술적 적인 요구사항을 수정하는 변경이다. 여기에는 기술 적 변경 없이 기술적 요건을 명확하게 하기 위한 표현의 변경 또는 기존 요구 수준의 감소가 포함된다. 확장 기술적 선택 사항 추가 이는 새로운 선택 사항을 제시하는 방식으로 새로운 기술적 요구사항을 추가하거나 수정하지만 기존의 표준을 완전히 준수하는 기기에 대한 요건을 강화시키는 변경은 아니다. 따라서 이는 이 전 판에 따른 제품에 대해 영향을 미치지 않는다. 주요 기술적 변경 기술적 요구사항의 추가 기술적 요구사항의 증가 이는 이전 판에 따른 제품이 최신 판에 주어진 요구사항을 충족할 수 없는 방식으로 기술적 변경 (추가, 수준 강화 또는 제거)이 발생한 경우이다. 이러한 변경 사항은 이전 판에 부합하는 제품에 대해 고려되어야 한다. 이러한 변경 사항에 대해서 추가적인 정보는 아래 B)항에서 다룬다. 비고 이러한 변경은 현재의 기술적 지식을 담고 있으나, 이미 시장에 출시된 기기에는 일반적으로 영향을 미쳐서는 안 된다. B) '주요 기술적 변경' 의 배경 정보 C1 - 고착 접합부를 고정하기 위한 추가적인 기계적 수단은 설치 또는 유지보수 중에 열리는 문 이나 덮개의 개방으로 인해 기능이 상실되어서는 안 된다. 예를 들어, 아래 그림에서 렌즈와 커버 사이에 고착 접합부가 있는 등기구의 경우, 두 번째 그림에 표시된 구성은 이 요구사 항과 일치하지만 첫 번째 그림에 표시된 구성은 그렇지 않다. 84 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
f95f51bf-b190-4f79-b018-15e2e3c1d514 | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 ![image](/image/placeholder) 2 렌즈 렌즈 개방형 커버 개방형 커버 고착접합 고착접합 방쪽접합면 서클립 또는 기타 기계적 고정기구 방쪽접합면 용기 용기 C2 - 아세틸렌을 함유하는 폭발성 가스 분위기에서 사용되는 경우(12.8), 구리 또는 구리 합금으 로 제조된 용기 및 외부에 장착되는 방폭 부품의 용기에 대한 재료 제한 사항의 추가 C3 - 시험회로를 개방하는 중 아크 소염(arc-quenching) 기간 동안 플러그 및 소켓의 내압방폭 성 능을 평가하기 위한 역률(power factor) 요구사항 추가 C4 - KS C IEC 60079-0(D.3.8)에 주어진 방폭 부품의 표시 요구사항에 추가하여 방폭 부품 용기의 표시에 대한 요구사항의 추가 C5 - 1 차 전지로 허용했던 T 형 전지의 제거(표 E.1) 3 기타 이 표준은 KS A 0001:2015(표준의 서식과 작성방법)에 따라 작성하였다. 85 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
a4c2b7cb-ed91-437c-821b-c904e068957c | KSCIEC60079-1_2024확인_KR | KS C IEC 60079-1:2014 KSKSKS KSKSK KSKS KSK KS KSK KSKS KSKSK KSKSKS Explosive atmospheres Part 1: Equipment protection by flameproof enclosures "d" ICS 29.260.20 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
88d6d741-9497-4937-8c63-eecc7ef88e7b | KSCIEC60364-5-54_2024확인_KR | KSKSKSKS KS C IEC 60364-5-54 KSKSKSK KSKSKS KSKSK KSKS KSK K KS 저압전기설비 - 제 5-54 부: 전기기기의 선정 및 설치 - 접지설비 및 보호도체 KS C IEC 60364-5-54:2011 산 업 표 준 심 의 회 2014 년 5 월 9 일 개정 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
1a47479a-a723-428e-a86a-17ae98ab6b92 | KSCIEC60364-5-54_2024확인_KR | KS CIEC 60364-5-54:2011 심 의 : 전력기기 기술심의 회 성 명 (회 장) 홍 순 찬 (위 원) 김 재 철 서 호 선 심 대 섭 이 주 철 전 기 중 박 현 주 안 상 필 채 경 수 (간 사) 이 승 훈 근 무 처 직 위 단국대학교 교 수 숭실대학교 교 수 KR 국제특허법률사무소 대 표 (주)정인시스템 연 구 소 장 (주)건일이엔지 연 구 소 장 (주)피디엔에스 전 무 한국전력공사 전력연구원 책임연구원 한국전기연구원 본 부 장 한국시험인증산업협회 전 문 위 원 국가기술표준원 표준정책국 전기전자정보표준과 공업사무관 표준열람 : e 나라표준인증(http://www.srandiand.go.kr) 제 정 자 : 산업통상자원부 국가기술표준원장 제 정 : 2002 년 10 월 29 일 개 정 : 2014 년 5 월 9 일 심 의 : 산업표준심의 회 전력기기 기술심의 회 원안작성협력 : 이 표준에 대한 의견 또는 질문은 e 나라표준인증 웹사이트를 이용하여 주십시오. 이 표준은 산업표준화법 제 10 조의 규정에 따라 매 5 년마다 산업표준심의 회에서 심의 되어 확인, 개정 또는 폐지됩니다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
e0613e11-ea20-4536-8de7-07c4b9c39f5f | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 목 차 머 리 말 .................................... ii 개 요 ...................................... iii 541 일반 .................................... 1 541.1 적용범위 ................... 1 541.2 인용표준 .................... 1 541.3 용어와 P....................... 542 접지설비 .........................^ 542.1 일반 연월.......................) 542.2 접지극 ......................... 542.3 접지도체 ...................... 542.4 주접지단자 ................ 7 543 보호도체 ................ 7 543.1 최소 단면적 -------------- 7 543.2 보호도체의 종류 ------ 9 543.3 보호도체의 전기적 연속성 ............. 10 543.4 PEN, PEL 또는 PEM 도체 .............. 10 543.5 보호 및 기능접지도체의 □종□□□□□□□□□□ 13 543.6 보호접지도체의 전류 ......................................... 13 543.7 10 mA 를 초과 하는 보호접지도체 전류에 대한 보강 보호접지도체 ........................................ 13 543.8 보호도체의 부설 ............................. .......................... 13 544 보호본딩도체 ....................................... 14 544.1 주접지단자에 접속하기 위한 보호본딩도체 ......................................... 14 544.2 보조본딩을 위한 보호본딩도체 ....................................... 14 부속서 A(규정) 543.1.2 에 제시된 계수 k 의 유도방법 ...................................... 15 부속서 B(참고) 접지설비 및 보호도체의 예 .......................... 19 부속서 C(참고) 콘크리트매입 기초접지극의 설치 ................................ 21 C.1 일반사항 ........................................ 21 C.2 콘크리트매입 접지극의 사용에 따른 그 밖의 고려사항 ..........................................21 C.3 콘크리트매입 기초접지극의 구조 ......................................... 21 C.4 콘크리트매입 기초접지극 외부의 다른 접지 설비에 가능한 부식 문제 ................................... 22 C.5 콘크리트매입 기초접지극의 완성 ·················· 23 부속서 D(참고) 토양매설 접지극의 ⌀= = = = = 24 D.1 일반사항 ......... 24 D.2 토양 저항률 ---------- D.3 토양에 매설된 Partications 25 D.4 접지극으로서의 ============= 참고문헌 ....................................... KSCIEC 60364-5-54:2011 ⌀1000000 I - 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및무단배포를 금합니다. | {}
bf687c3c-d3f9-46a6-813f-fccbde454d81 | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 머 리 말 이 표준의 내용 일부 또는 전부는 저작권법에 따른 보호대상이 되는 저작물이 될 수 있다. 이 표준의 내용 일부 또는 전부가 ISO · IEC 등에서 제정한 표준을 참고하여 제정 또는 개정된 경우, 해당 표준의 저작권을 보유하고 있는 ISO · IEC 등의 저작권 보호 규정 등에 따라 보호되어야 한다. 이 표준의 일부가 기술적 성질을 가진 특허권, 출원공개 이후의 특허출원, 실용신안권 또는 출원공개 후의 실용신안등록출원에 저촉될 가능성이 있다는 것에 주의 를 환기한다. 국가기술표준원장 및 산업 표준심의 회는 이러한 기술적 성질을 가진 특허권, 출원공개 이후의 특허출원, 실용신안권 또는 출원 공개 후의 실용신안등록출원에 관계되는 확인에 대하여 책임을 지지 않는다. -ii- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
6af28f34-f71c-430e-8aaf-29758b709d3e | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 개 요 이 표준은 2011 년에 제 3.0 판으로 발행된 IEC 60364-5-54,Low-voltage electrical installations - Part 5- 54: Selection and erection of electrical equipment - Earthing arrangements and protective conductors 를 기초로, 기술적인 내용 및 대응국제표준의 구성을 변경하지 않고 작성한 한국산업표준이다. -iii- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
d41c2510-7564-409d-911d-5ff77b0eb443 | KSCIEC60364-5-54_2024확인_KR | 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
9e29255d-3631-4222-a7cc-d812bd454149 | KSCIEC60364-5-54_2024확인_KR | 한국산업표준 KS C IEC 60364-5-54:2011 저압전기설비 - 제 5-54 부: 전기기기의 선정 및 설치 - 접지설비 및 보호도체 Low-voltage electrical installations - Part 5-54: Selection and erection of electrical equipment - Earthing arrangements and protective conductors 541 일반 541.1 적용범위 이 표준은 전기설비의 안전성을 충족하기 위해 보호본딩도체를 포함하여 접지설비 및 보호도체에 대 하여 규정한다. 541.2 인용표준 다음의 인용표준은 이 표준의 적용을 위해 필수적이다. 발행연도가 표기된 인용표준은 인용된 판만 을 적용한다. 발행연도가 표기되지 않은 인용표준은 최신판(모든 추록을 포함)을 적용한다. KS C IEC 60364-4-41:2013, 저압전기설비 - 제 4-41 부: 안전을 위한 보호 - 감전에 대한 보호 KS C IEC 60364 -4-44:2013, 저압전기설비 - 제 4-44 부: 안전을 위한 보호 - 전압 및 전기자기 방 해에 대한 보호 KS C IEC 60364 -5-51:2013, 건축전기설비 - 제 5-51 부 : 전기기기의 선정 및 시공 - 공통 규칙 KS C IEC 60439-2, 저전압 개폐장치 및 제어장치 부속품 - 제 2 부: 부스바 트렁킹 시스템의 개별 요구사항 KS C IEC 60724, 정격 전압 1 kV 및 3 kV 전기케이블의 단락 온도 한계 KS C IEC 60853 -2, 케이블의 비상 전류 정격 및 주기 계산 - 제 2 부: 18/30 kV 초과 케이블의 주기 정격 및 케이블의 비상 정격 KS C IEC 60949, 비단열 가열 효과 를 고려한 열적 허용 단락 전류의 산출 KS C IEC 61140, 감전 보호 - 설비 및 기기의 공통 사항 KS C IEC 62305 (모든 부), 피뢰시스템 KS C IEC 62305-3:2012, 피뢰시스템 - 제 3 부: 구조물의 물리적 손상 및 인명위험 IEC 60909-0, Short-circuit currents in three-phase a.c. systems - Part 0: Calculation of currents IEC 61024-1, Protection of structures against lightning - Part 1 : General principles IEC 61439-1, Low-voltage switchgear and controlgear assemblies - Part 1: General rules IEC 61439-2, Low-voltage switchgear and controlgear assemblies - Part 2: Power switchgear and controlgear assemblies IEC 61534- 1, Powertrack systems - Part 1: General requirements 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 1 | {}
8f13b65e-af39-4a75-a8fc-4f2eca4fdafc | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 541.3 용어와 정의 이 표준의 목적을 위하여 KS C IEC 61140 의 용어와 정의 및 다음을 적용한다. 접지설비, 보호도체 및 보호본딩도체의 사용에 대한 정의 는 다음과 같으며, 부속서 B 에 예시되어 있다. 541.3.1 노출도전부 (exposed-conductive-part) 접촉할 수 있으며, 보통 충전되어 있지 않지만 기초절연 고장 시에는 충전이 될 수 있는 기기의 도전부 [IEC 60050- 826:2004, 826-12-10] 541.3.2 계통외도전부 (extraneous-conductive-part) 전기설비의 일부를 구성하지 않고 일반적으로 국부 대지전위가 전도될 수 있는 도전부 [IEC 60050- 826:2004, IEV 826-12-11] 541.3.3 접지극 (earth electrode) 대지와 전기적으로 접촉하고 있는 토양 또는 특정 도전성 매체(예: 콘크리트)에 매설된 도전부 [IEC 60050 - 826:2004, 826-13-05, 수정됨] 541.3.4 콘크리트매입 기초접지극 (concrete-embedded foundation earth electrode) 건축물 기초 콘크리트에 매입된 접지극으로 일반적으로 페루프를 형성한다. [IEC 60050 - 826:2004, 826-13-08, 수정됨] 541.3.5 토양매설 기초접지극 (soil-embedded foundation earth electrode) 건축물 기초 아래의 토양에 매설된 접지극으로 일반적으로 페루프를 형성한다. [IEC 60050 - 826:2004, 826-13-08, 수정됨] 541.3.6 보호도체 (protective conductor) 감전에 대한 보호 등 안전을 목적으로 제공되는 도체 [IEC 60050- 826:2004, 826-13-22] 비고 보호본딩도체를 포함한 보호도체의 예는 감전에 대한 보호를 위해 사용되는 보호접지도체와 접지도체이다. 541.3.7 보호본딩도체 (protective bonding conductor) 보호등전위본딩을 제공하는 보호도체 [IEC 60050- 826:2004, 826-13-24] 2 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
172f9f5a-64e6-429a-8d01-56aa7bb83a06 | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 541.3.8 접지도체 (earthing conductor) 계통, 설비 또는 기기 안의 한 점과 접지극 사이의 전도 경로 또는 그 경로의 일부를 제공하는 도체 [IEC 60050 - 826:2004, 826-13-12] 비고 이 표준의 목적에 따라 접지도체는 접지극을 등전위본딩시스템의 한 점, 주로 주접지단자에 연 결하는 도체이다. 541.3.9 주접지단자(주접지 부스바) [main earthing terminal(main earthing busbar)] 설비의 접지설비의 일부이며 접지를 목적으로 여러 개의 도체가 전기적으로 결합할 수 있는 단자 또 는 부스바 [IEC 60050 - 826:2004, 826-13-15] 541.3.10 보호접지도체 [protective earthing conductor] 보호접지를 위해 제공되는 보호도체 [IEC 60050- 826:2004, 826-13-23] 541.3.11 기능접지 [functional earthing] 전기안전 이외의 목적으로 계통, 설비 또는 기기의 한 점 또는 여러 점을 접지 [IEC 60050 - 826:2004, IEV 826-13-10] 541.3.12 접지설비 [earthing arrangement] 계통, 설비 또는 기기의 접지에 관한 모든 전기적 접속 및 장치 [IEC 60050 - 195:2004, 195-02-20] 542 접지설비 542.1 일반 요구사항 542.1.1 접지설비는 전기설비의 요건에 따라 보호 및 기능의 목적을 병용 또는 분리하여 사용될 수 있다. 보호목적에 관한 요건은 항상 우선적으로 고려해야 한다. 542.1.2 설비 안에 여러 접지극을 설치할 때는 접지도체를 사용하여 주접지단자에 접속해야 한다. 542.1.3 전력공급이 고압일 때 고압전력공급의 접지설비와 저압 설비의 접지설비에 관한 요건은 KS C IEC 60364 -4-44:2013 의 442.에 따른다. 542.1.4 접지설비에 대한 요건은 다음과 같은 대지로의 접속을 위해 고안되었다. 설비의 보호 요건에 있어 믿을 수 있고 적합한 것. - 열적, 열-기계적, 전기기계적 응력 및 이러한 전류로 인한 감전의 위험 없이 지락전류와 보호도체 전류를 대지로 흘려 보내는 것. 3 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
1f180123-8b58-4f02-8953-7e74cb8e8677 | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 - 관련이 있는 경우, 기능적 요구사항을 충족하는 것. - 예를 들어, 기계적 응력 및 부식에 의해 예상되는 외적 영향(KS C IEC 60364 - 5-51 참조)에 대 해 적절할 것. 542.1.5 고주파를 포함한 전류가 흐를 것이 예상될 때는 접지설비를 고려해야 한다(IEC 60364-4- 44:2013 의 444. 참조). 542.1.6 KS C IEC 60364 - 4-41 에 규정된 감전에 대한 보호가 어떠한 예측 가능한 접지저항의 변화 (예: 부식, 건조 또는 동결로 인한)에 의해 영향을 받지 않아야 한다. 542.2 접지극 542.2.1 접지극의 종류, 재질 및 크기는 의도하는 수명기간 동안 부식에 견디고 충분한 기계적 강도 를 갖는 것으로 선정해야 한다. 비고 1 부식에 관해서 다음의 요소를 고려할 수 있다. 부지의 토양 pH, 토양의 저항률, 토양의 수분, 표유 전류와 교류 및 직류의 누설전류, 화학 오염, 그리고 다른 물질의 접근 토양 또는 콘크리트에 매입되는 접지극으로 부식 및 기계적 강도의 관점에서 일반적으로 사용되는 재질의 최소 굵기는 표 54.1 에 명시되어 있다. 비고 2 보호코팅의 최소 두께가 수평 접지극이 수직 접지극보다 더 큰 것은 매입된 동안의 기계적 스트레스가 더 크기 때문이다. 피뢰시스템이 있다면 KS C IEC 62305-3 의 5.4 요건을 적용한다. 4 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
269fe9b3-b423-4511-a150-ffc31d24302a | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 표 54.1 - 토양 또는 콘크리트에 매설되는 접지극으로 부식방지 및 기계적 강도를 대비하여 일반적으로 사용되는 재질의 최소 굵기 ¦ 재질 및 표면 ¦ 모양 ¦ 최소 크기 ¦ 최소 크기 ¦ 최소 크기 ¦ 최소 크기 ¦ 최소 크기 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 재질 및 표면 ¦ 모양 ¦ 지름 mm ¦ 단면적 mm2 ¦ 두께 mm ¦ 코팅 무게 g/m2 ¦ 코팅/외장 두께 �m ¦ ¦ 콘크리트매입 강철 (나강, 아연도금 또는 스테인리스) ¦ 원형 강선 ¦ 10 ¦ ¦ ¦ ¦ ¦ ¦ 콘크리트매입 강철 (나강, 아연도금 또는 스테인리스) ¦ 강테이프 또는 강대 ¦ ¦ 75 ¦ 3 ¦ ¦ ¦ ¦ 용융 아연도금 강철° ¦ 강대 b 또는 성형 강대/ 강판-경질 강판/ 격자형 강판 ¦ ¦ 90 ¦ 3 ¦ 500 ¦ 63 ¦ ¦ 용융 아연도금 강철° ¦ 수직부설 원형 강봉 ¦ 16 ¦ ¦ ¦ 350 ¦ 45 ¦ ¦ 용융 아연도금 강철° ¦ 수평부설 원형 강선 ¦ 10 ¦ ¦ ¦ 350 ¦ 45 ¦ ¦ 용융 아연도금 강철° ¦ 강관 ¦ 25 ¦ ¦ 2 ¦ 350 ¦ 45 ¦ ¦ 용융 아연도금 강철° ¦ 강연선(콘크리트매입) ¦ ¦ 70 ¦ ¦ ¦ ¦ ¦ 용융 아연도금 강철° ¦ 수직부설 십자형 강철 ¦ ¦ (290) ¦ 3 ¦ ¦ ¦ ¦ 구리외장 강철 ¦ 수직부설 원형 강봉 ¦ (15) ¦ ¦ ¦ ¦ 2000 ¦ ¦ 전착된 구리도금 강철 ¦ 수직부설 원형 강봉 ¦ 14 ¦ ¦ ¦ ¦ 250e ¦ ¦ 전착된 구리도금 강철 ¦ 수평부설 원형 강선 ¦ (8) ¦ ¦ ¦ ¦ 70 ¦ ¦ 전착된 구리도금 강철 ¦ 수평부설 강대 ¦ ¦ 90 ¦ 3 ¦ ¦ 70 ¦ ¦ 스테인리스 강철 a ¦ 강대 b 또는 성형 강대/ 강판 ¦ ¦ 90 ¦ 3 ¦ ¦ ¦ ¦ 스테인리스 강철 a ¦ 수직부설 원형 강봉 ¦ 16 ¦ ¦ ¦ ¦ ¦ ¦ 스테인리스 강철 a ¦ 수평부설 원형 강선 ¦ 10 ¦ ¦ ¦ ¦ ¦ ¦ 스테인리스 강철 a ¦ 관 ¦ 25 ¦ ¦ 2 ¦ ¦ ¦ ¦ 구리 ¦ 구리대 ¦ ¦ 50 ¦ 2 ¦ ¦ ¦ ¦ 구리 ¦ 수평부설 원형 강선 ¦ ¦ (25)d 50 ¦ ¦ ¦ ¦ ¦ 구리 ¦ 수직부설 원형 강봉 ¦ (12) 15 ¦ ¦ ¦ ¦ ¦ ¦ 구리 ¦ 연선 ¦ 1.7 연선의 소선 ¦ (25)d 50 ¦ ¦ ¦ ¦ ¦ 구리 ¦ 관 ¦ 20 ¦ ¦ 2 ¦ ¦ ¦ ¦ 구리 ¦ 강판 ¦ ¦ ¦ (1.5) 2 ¦ ¦ ¦ ¦ 구리 ¦ 격자형 강판 ¦ ¦ ¦ 2 ¦ ¦ ¦ 비고 괄호 안의 값은 감전에 대한 보호를 위해서만 적용하고, 괄호가 없는 값은 피뢰 및 감전에 대한 보호를 위해 적용한다. a 크롬≥16%, 니켈≥5%, 몰리브덴≥2%, 카본≤0.08 % b 압연강대 또는 둥근 모서리 슬릿(slit) 강대 C 도금(코팅)은 매끄럽고 연속적이며 얼룩이 없는 것이어야 한다. d 경험적으로 부식 및 기계적 위험이 매우 낮을 것으로 판단될 때 16 mm2 인 것을 사용할 수 있다. e 이 두께는 설치과 정 중에 구리도금의 기계적 손상에 견딜 수 있다. 설치과 정 중에 제조업체의 지침에 따라 구리에 대한 기계적 손상[예를 들면, 절삭기의 구멍 또는 특수 보호 팁(tips)]을 피하기 위해 특별히 주의 하는 경우 적어도 100 �m 까지 감소될 수 있다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 5 | {}
87754e99-c9e6-4e61-9ece-7f60575263f6 | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 542.2.2 접지극의 유효성은 접지극 자체의 형상과 그 부지의 토양 조건에 따라 다르다. 토양 조건 과 필요한 접지 저항 값에 적절한 하나 또는 그 이상의 접지극을 선정한다. 접지극 저항의 개산법을 부속서 D 에 나타낸다. 542.2.3 다음은 사용 가능한 접지극의 예이다. 콘크리트매입 기초접지극 비고 좀 더 상세한 사항은 부속서 C 참조 토양 매설 기초접지극 - 토양에 수직 또는 수평으로 직접 매설된 금속전극(예: 봉, 선, 테이프, 관 또는 판) - 부지 조건 또는 요건에 적합한 케이블 금속외장 및 그 밖의 금속피복 - 부지 조건 또는 요건에 적합한 그 밖의 적절한 지중 금속 구조물(예: 관) - 대지에 매설된 콘크리트(PS 콘크리트 제외)의 용접된 철근 542.2.4 접지의 종류 및 매설 깊이를 선정할 때 일어날 수 있는 기계적 손상과 토양의 건조 및 동 결이 부지 조건에 영향을 최소화하도록 고려하여야 한다. 542.2.5 접지설비에서 다른 재질을 사용할 때 전해부식을 고려해야 한다. 콘크리트에 매입된 기초 접지극에 접속하는 외부도체(예: 접지도체)의 경우 용융 아연도금 강철로 만든 접속부는 토양에 매설 해서는 안 된다. 542.2.6 가연성 액체 또는 가스용 금속관은 접지설비로 사용해서는 안 되며, 그 관이 묻힌 부분을 접지극의 치수 산정에 고려해서도 안 된다. 비고 이 요건은 KS C IEC 60364 -4-41 을 준수하기 위해 이러한 관의 주접지단자(541.3.9)를 경유하 는 보호등전위본딩을 배제하는 것은 아니다. 음극방식 설비가 시설된 경우와 TT 계통에서 전력이 공급되는 전기기기 부품의 노출도전부가 직접 관에 접속되어 있는 경우, 가연성 액체 또는 가스용 금속관은 이 특정 기기의 유일한 접지극의 역할 을 할 수 있다. 542.2.7 접지극은 개울, 강, 못, 호수 또는 이와 유사한 곳(542.1.6 참조)의 물속에 직접 잠겨서는 안 된다. 542.2.8 접지극이 함께 접속되어야 하는 부분으로 구성되어 있는 경우 발열성 용접, 압착 접속기, 클 램프 또는 그 밖의 적절한 기계적 접속장치에 의해 접속되어야 한다. 비고 철선만으로 감아 싼 접속은 보호목적에 적합하지 않다. 542.3 접지도체 542.3.1 접지도체는 543.1.1 또는 543.1.2 의 규정을 준수해야 한다. 그 단면적은 구리 6 mm2 이상, 철 50 mm2 이상이어야 한다. 토양에 매설된 나 접지도체의 치수 및 특성은 표 54.1 에 따라야 한다. 큰 고장전류가 접지도체를 통해 흐르는 것이 예상되지 않는 경우(예: TN 계통 또는 IT 계통) 접지도 체는 544.1 의 굵기에 따를 수 있다. 알루미늄 도체는 접지도체로 사용해서는 안 된다. 6 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
d7f8f1e3-7903-41fc-90be-d4bac0978e35 | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 비고 피뢰시스템이 접지도체에 접속된 때 접지도체의 단면적은 구리(Cu) 16mm2 이상 또는 철(Fe) 50 mm2 이상이어야 한다(KS C IEC 62305 시리즈 참조). 542.3.2 접지극에 접지도체의 접속은 견고하고 전기적으로 충족하여야 한다. 접속은 발열성 용접, 압착 접속기, 클램프 또는 그 밖의 적절한 기계적 접속장치에 의해 이루어져야 한다. 기계적 접속장 치는 제조자의 지침에 따라 설치되어야 한다. 클램프를 사용할 때 전극 또는 접지도체가 손상되어서 는 안 된다. 납땜만이 유일한 접속기구나 금구는 충분한 기계적 강도 측면에서 신뢰할 수 없기 때문에 독립적으 로 사용해서는 안 된다. 비고 수직 접지극을 설치할 때 접속의 점검과 수직봉의 교환 대책을 구비할 수 있다. 542.4 주접지단자 542.4.1 보호등전위본딩이 사용되는 모든 설비에는 주접지단자를 설치하고 다음과 같은 것에 접속 하여야 한다. - 보호본딩도체 - 접지도체 - 보호도체 - 관련이 있는 경우, 기능성 접지도체 비고 1 다른 보호도체를 주접지단자에 접속할 때, 모든 개별 보호도체가 주접지단자에 직접 접속되 어야 하는 것은 아니다. 비고 2 건축물의 주접지단자는 일반적으로 기능접지 목적으로 사용될 수 있다. 정보기술 목적을 위 해 주접지단자는 대지에 접속점으로 간주된다. 하나 이상의 접지단자가 있을 때는 그들을 상호 접속하여야 한다. 542.4.2 주접지단자에 접속된 각 도체는 개별적으로 분리할 수 있어야 한다. 이 접속은 믿을 수 있 어야 하며, 도구를 이용해서만 분리할 수 있어야 한다. 비고 분리대책은 접지극의 저항측정이 가능하도록 주접지단자에 결합하는 것이 편리하다. 543 보호도체 비고 KS C IEC 60364-5-51:2013 의 516.의 요건을 고려한다. 543.1 최소 단면적 543.1.1 모든 보호도체의 단면적은 KS C IEC 60364 -4-41:2013 의 411.3.2 에서 요구하는 자동 전원 차단 조건을 충족하여야 하며, 보호장치의 차단시간 동안 예상 고장전류로 인해 발생되는 기계적 및 열적 응력을 견딜 수 있어야 한다. 보호도체의 단면적은 543.1.2 에 따라 계산하거나 표 54.2 에 따라 선정할 수 있다. 어느 쪽이든 543.1.3 의 요건을 고려하여야 한다. 7 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
c01b8a7f-a59a-41a4-8e1e-5f085acbc4dc | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 보호도체용 단자는 이 항에서 요구하는 도체의 크기를 수용할 수 있어야 한다. TT 계통에서 전력공급계통의 접지극과 노출도전부의 접지극이 독립한 경우(312.2.2 참조) 보호도체의 단면적은 다음의 값을 초과 할 필요는 없다. - 구리 25 mm2 - 알루미늄 35 mm2 표 54.2 - 보호도체의 최소 단면적 (543.1.2 에 따라 계산하지 않는 경우) ¦ 선 도체의 단면적, S mm2 구리 ¦ 대응하는 보호도체의 최소 단면적 mm2 구리 ¦ 대응하는 보호도체의 최소 단면적 mm2 구리 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 선 도체의 단면적, S mm2 구리 ¦ 보호도체의 재질이 선 도체와 같은 경우 ¦ 보호도체의 재질이 선 도체와 다른 경우 ¦ ¦ S≤16 ¦ S ¦ K1 xS K2 ¦ ¦ 16< S≤35 ¦ 16a ¦ K1 x16 K2 ¦ ¦ S>35 ¦ S a 2 ¦ K1 x S K2 2 ¦ ¦ 여기에서 k1 : 도체 및 절연의 재질에 따라 KS C IEC 60364-4-43 의 표에서 선정되거나 부속서 A 의 식으로부터 유도된 선 도체에 대한 k 값 ¦ 여기에서 k1 : 도체 및 절연의 재질에 따라 KS C IEC 60364-4-43 의 표에서 선정되거나 부속서 A 의 식으로부터 유도된 선 도체에 대한 k 값 ¦ 여기에서 k1 : 도체 및 절연의 재질에 따라 KS C IEC 60364-4-43 의 표에서 선정되거나 부속서 A 의 식으로부터 유도된 선 도체에 대한 k 값 ¦ K2 : 표 A.54.2~A.54.6 을 적용하여 선정된 보호도체에 대한 k 값 a PEN 도체의 경우, 그 단면적의 감소는 중성선의 굵기 결정에 대한 규칙에 따라서 만 허용된다(KS C IEC 60364-5-52 참조). 543.1.2 보호도체의 단면적은 다음에서 결정된 값 이상이어야 한다. - KS C IEC 60949 에 따른 단면적, 또는 - 차단 시간이 5 초를 넘지 않는 경우에만 적용 가능한 다음 식으로 계산된 단면적 V12t S= k 여기에서 S : 단면적(mm2) / : 무시 가능한 임피던스 고장으로 보호장치를 통해 흐를 수 있는 예상 고장전류를 암페어 로 나타낸 실효 값(IEC 60909-0 참조) t : 자동 차단을 위한 보호장치의 초 단위 동작 시간 k : 보호도체, 절연물, 그 밖의 부분의 재질 및 초기온도와 최종온도에 따라 정해지는 계수 (k 의 계산은 부속서 A 참조) 위 식으로 표준에 일치하지 않는 굵기가 산출된 경우, 가장 가까운 상위 표준 단면적을 가진 도체를 사 용해야 한다. 비고 1 계산은 회로 임피던스에 의한 전류 제한효과 및 보호장치의 Pt 의 제한을 고려한다. 8 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
8bed14f1-db89-4940-8ef7-86e60d74f9a1 | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 비고 2 잠재적으로 폭발 가능한 환경에 설치된 설비의 온도 한계는 KS C IEC 60079-0 참조 비고 3 IEC 60702-1 에 의한 무기절연케이블(MI 케이블)의 금속외장은 선 도체보다 큰 지락 고장용량 을 가지고 있으므로 그것을 보호도체로 사용할 때 금속외장 관의 단면적을 계산할 필요는 없다. 543.1.3 보호도체가 케이블의 일부를 구성하지 않거나 또는 선 도체와 공통으로 외함에 수납되어 있지 않는 경우 모든 보호도체의 단면적은 다음 값 이상이어야 한다. - 기계적 손상에 대한 보호가 된 것은 구리 2.5 mm2, 알루미늄 16 mm2 - 기계적 손상에 대한 보호가 되지 않은 것은 구리 4 mm2, 알루미늄 16 mm2 비고 보호도체로서 강철의 사용을 배제하는 것은 아니다(543.1.2 참조). 전선관, 트렁킹 안에 설치되거나 이와 유사한 배선방식으로 보호된 경우 케이블의 일부를 구성하지 않는 보호도체는 기계적으로 보호된 것으로 간주한다. 543.1.4 보호도체가 2 개 또는 그 이상의 회로에 공통이라면 그 단면적은 다음 중 하나에 따라 결정 하여야 한다. - 이들 회로에서 발생할 수 있는 가장 가혹한 예상 고장전류와 동작 시간을 543.1.2 에 따라 계산한다. - 이들 회로 중 가장 큰 선 도체의 단면적에 상응하도록 표 54.2 에 따라 선정한다. 543.2 보호도체의 종류 543.2.1 보호도체는 다음 중 하나 또는 그 이상으로 구성된다. - 다심 케이블의 도체 - 충전도체와 공통의 외함 안에 수납된 절연도체 또는 나도체 - 고정하여 시설한 나도체 또는 절연도체 - 543.2.2 의 a), b)에 규정된 조건에 따르는 금속 케이블 외장, 케이블 차폐, 케이블 강대외장, 편조 전선, 동심 도체, 금속관 비고 보호도체의 배치에 관해서는 543.8 을 참조 543.2.2 설비가 저압 개폐기, 제어장치 조립품(IEC 61439- 1 및 IEC 61439-2 참조), 부스바트렁킹 시스템(KS C IEC 60439-2 참조)과 같은 금속외함을 가진 기기를 포함하는 경우, 다음의 3 가지 요건 을 동시에 충족한다면, 그 금속외함 또는 프레임을 보호도체로 사용할 수 있다. a) 기계적, 화학적 또는 전기화학적 열화에 대한 보호를 확실하게 하도록 구조 또는 적절한 연결로 전기적 연속성을 보장할 것. b) 543.1 의 요건에 적합할 것. c) 미리 결정한 모든 분기 접속점에서 다른 보호도체의 연결을 허용할 것. 543.2.3 다음과 같은 금속부분은 보호도체 또는 보호본딩도체로 사용할 수 없다. - 금속 수도관. 다만, 수도설비관리자가 승인한 경우는 예외로 한다. - 가스, 액체, 분말과 같은 잠재적 가연성 물질이 들어 있는 금속관 비고 1 음극부식방지에 관해서는 542.2.6 참조 9 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
cceb4b4f-779b-40fb-a1c2-be44ef22076b | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 - 통상 사용 중에 기계적 응력을 받는 구조물 일부 - 유연성 또는 휘기 쉬운 금속관, 다만 그 목적으로 설계되지 않았을 경우에 한함 - 유연성 금속제 부품 - 지지용 선; 케이블 트레이 및 케이블 래더 비고 2 감전에 대한 보호에 사용할 때 보호도체의 예로써 보호본딩도체, 보호접지도체 및 접지도체 를 포함한다. 543.3 보호도체의 전기적 연속성 543.3.1 기계적 손상, 화학적 또는 전기화학적 열화, 전기역학적 힘 및 열역학적 힘에 대해 보호도 체를 적절히 보호하여야 한다. 보호도체 사이 또는 보호도체와 다른 기기 사이의 모든 접속(예: 나사접속, 클램프 접속)은 영구적인 전기적 연속성과 충분한 기계적 강도 및 보호를 제공하여야 한다. 보호도체를 접속하는 나사는 다른 목적으로 사용해서는 안 된다. 접속부는 납땜으로 접속해서는 안 된다. 비고 모든 전기적 접속은 가장 큰 단면적의 도체 또는 케이블/외함에 발생할 수 있는 전류/시간의 모든 조합에 견딜 수 있는 충분한 열용량 및 기계적 강도를 가져야 한다. 543.3.2 보호도체의 접속부는 다음을 제외하고 검사와 시험을 위해 접근이 가능하여야 한다. - 화합물로 충전된 접속부 - 캡슐로 싸인 접속부 - 금속관, 덕팅 및 부스바트렁킹에서의 접속부 - 기기 표준에 부합하는 기기의 일부를 구성하는 접속부 - 용접 또는 경납땜에 의한 접속부 - 압축공구에 의한 접속부 543.3.3 개폐장치를 보호도체에 삽입할 수 없지만, 시험을 위한 공구를 사용하여 차단할 수 있는 접속부에는 설치할 수 있다. 543.3.4 접지의 전기적 감시를 수행할 때의 전용장치(예: 동작 센서, 코일, 전류변성기)는 보호도체 에 직렬로 접속하면 안 된다. 543.3.5 전기기기의 노출도전부는 543.2.2 에 허용된 것을 제외하고 다른 기기의 보호도체의 일부로 구성하는 데 사용해서는 안 된다. 543.4 PEN, PEL 또는 PEM 도체 비고 이러한 도체는 보호도체(PE)로서의 기능과 중성선(N), 선 도체(L), 중간선(M) 중의 어느 하나와 2 가지 기능을 수행하므로 해당 기능에 대한 모든 적용 가능한 요건을 고려한다. 543.4.1 PEN, PEL 또는 PEM 도체는 고정 전기설비에서만 사용할 수 있고, 기계적인 이유로 그 단 면적은 구리 10 mm2 또는 알루미늄 16mm2 이상이어야 한다. 비고 1 EMC 에 관한 이유로 PEN 도체는 설비 원점의 부하측에 시설해서는 안 된다(KS C IEC 60364 10 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
933a21c1-e0a5-411b-80ad-9db48e03f6c7 | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 - 4-44:2013 의 444.4.3.2 참조). 비고 2 KS C IEC 60079 - 14 에서 폭발성 분위기에서의 PEN, PEL 또는 PEM 도체는 사용을 금지하고 있다. 543.4.2 PEN, PEL 또는 PEM 도체는 선 도체의 정격전압에 대해 절연하여야 한다. 배선설비의 금속 외함은 KS C IEC 60439-2 에 적합한 부스바트렁킹시스템에 관한 것과 IEC 61534- 1 에 적합한 파워트랙시스템에 관한 것 이외에는 PEN, PEL 또는 PEM 도체로 사용될 수 없다. 비고 기기위원회는 PEN, PEL 또는 PEM 도체로부터 기기 안으로 유도되는 EMI 의 전위 영향을 고려 한다. 543.4.3 설비의 어느 지점에서 중성선/중간점/선 도체 및 보호 기능이 별도의 도체에 의해 배선된다 면, 중성선/중간점/선 도체를 설비의 모든 다른 접지 부분에 접속하는 것은 허용되지 않는다. 그러나 PEN, PEL 또는 PEM 도체에서 각각 하나 이상의 중성선/중간점/선 도체와 하나 이상의 보호도체를 구성하는 것은 허용한다. PEN, PEL 또는 PEM 도체는 PEN, PEL 또는 PEM 도체의 접속을 의도한 특정 단자 또는 바(그림 54.1b 및 54.1c 의 예)의 경우를 제외하고, 보호도체용 단자 또는 바에 접속되어야 한다(그림 54.1a 참조). 11 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
4c40864f-ca90-42ac-b7dc-24c5bd621491 | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 ![image](/image/placeholder) MDB L1 ○ ○ ○ L1 bar L2 ○ ○ L2 bar L3 ○ ○ ○ L3 bar ○ ○ ○ N bar PEN ○ ○ ○ ○ ○ ○ PEN (PE) bar I PE 도체 N 도체 그림 54.1a - 예 1 MDB L1 ○ L1 bar L2 ○ ○ ○ ○ L2 bar L3 ○ ○ ○ ○ L3 bar PEN ○ ○ ○ ○ ○ Q ○ PEN (N) bar ① ○ ○ ○ ○ ○ ○ ○ ○ PE bar PE 도체 N 도체 그림 54.1b - 예 2 MDB L1 ○ L1 bar ![image](/image/placeholder) L2 ○ ○ L2 bar L3 ○ ○ L3 bar ○ ○ Q ○ N bar PEN bar PEN ○ ○ ○ ○ ○ PE bar · I PE 도체 N 도체 그림 54.1c - 예 3 MDB 주배전반 그림 54.1 - PEN 도체 접속의 예 12 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
9c253f9b-ce55-42bf-a2ca-90bfb2d10708 | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 비고 직류 SELV 회로(예: 통신설비)에서 공급되는 계통에서는 PEL 또는 PEM 도체가 없다. 543.4.4 계통외도전부는 PEN, PEL 또는 PEM 도체로 사용해서는 안 된다. 543.5 보호 및 기능접지도체의 겸용 보호 및 기능접지도체를 겸하여 사용할 경우 보호도체에 대한 요건을 충족해야 한다. 또한 관련 기 능 요건(KS C IEC 60364 - 4-44:2013, 444. 참조)에도 적합하여야 한다. 정보기술 전원공급을 위한 직류귀환도체 PEL 또는 PEM 은 기능접지도체와 보호도체로서의 역할을 겸용할 수 있다. 비고 추가 정보에 관해서는 KS C IEC 61140 의 7.5.3.1 을 참조 543.6 보호접지도체의 전류 보호접지도체는 정상 작동상태에서 전류의 전도성 경로(예: EMC 에 관한 이유로 필터의 접속)로 사용 되지 않아야 한다. 또한 KS C IEC 61140 참조. 정상적인 운전상태에서 전류가 10 mA 를 초과 하면 증 강된 보호도체를 사용한다(543.7 참조). 비고 용량성 누설전류(예: 케이블 또는 전동기에 의한)는 설비 및 기기의 설계에 의해 감소된다. 543.7 10mA 를 초과 하는 보호접지도체 전류에 대한 보강 보호접지도체 전류사용기기에 영구적인 접속을 위한 보호접지도체의 전류가 10 mA 를 초과 하는 경우에 대해서 다 음의 것을 적용한다. 보호접지도체가 하나뿐인 전류사용기기인 경우 보호도체의 단면적은 그 전체 길이에 걸쳐 구리 10 mm2 이상 또는 알루미늄 16mm2 이상이어야 한다. 비고 1 543.4 에 의한 PEN, PEL 또는 PEM 도체는 이 요건에 적합하다. 전류사용기기가 두 번째 보호접지도체용 별도의 단자가 있는 경우 고장보호를 위해 요구되는 것 과 같은 단면적 이상의 두 번째 보호접지도체는 최소한 보호접지도체의 단면적이 구리 10 mm2 이상 또는 알루미늄 16mm2 이상인 지점에서부터 배선되어야 한다. 비고 2 중성선 및 보호도체가 기기단자까지 단일도체에서 하나의 도체(PEN 도체)로 겸용하는 TN-C 계통에서는 보호도체 전류를 부하 전류로 취급할 수 있다. 비고 3 보통 사용 상태에서 보호도체 전류가 큰 전류사용기기에 누전차단기를 장착한 설비는 사용하 지 못할 수 있다. 543.8 보호도체의 부설 과전류보호장치가 감전에 대한 보호용으로 사용될 때의 보호도체는 충전도체와 같은 배선설비에 병 합시키거나 그들과 근접한 곳에 부설한다. 13 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
0c75c595-fb5a-4e7e-a422-9ced9a62e0ec | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 544 보호본딩도체 544.1 주접지단자에 접속하기 위한 보호본딩도체 주접지단자에 접속하기 위한 보호본딩도체는 설비 안에 있는 가장 큰 보호접지도체 단면적의 1/2 이 상의 단면적을 가져야 하고 다음의 단면적 이상이어야 한다. - 구리 6 mm2 또는 - 알루미늄 16 mm2 또는 - 강철 50 mm2 주접지단자에 접속하기 위한 보호본딩도체의 단면적은 구리 25 mm2 또는 다른 재질의 동등한 단면 적을 초과 할 필요는 없다. 544.2 보조본딩을 위한 보호본딩도체 544.2.1 두 개의 노출도전부에 접속하는 보호본딩도체의 컨덕턴스는 노출도전부에 접속된 더 작은 보호도체의 컨덕턴스보다 커야 한다. 544.2.2 계통외도전부에 노출도전부를 접속하는 보호본딩도체의 컨덕턴스는 상응하는 단면적을 갖 는 보호도체 컨덕턴스의 1/2 이상이어야 한다. 544.2.3 보조 본딩을 위한 보호본딩도체 및 두 계통외도전부 사이의 본딩도체의 최소 단면적은 543.1.3 에 따라야 한다. 14 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
726348e8-4ad3-4c8d-9f46-756ed7075ecc | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 부속서 A (규정) 543.1.2 에 제시된 계수 k 의 유도방법 (KS c IEC 60724 및 KS C IEC 60949 참조) 계수 k 값은 다음 식에 의해 결정된다. Q(B+20 °C) B+0f k = In P20 �+� 여기에서 ¦ Qc ¦ : 20 °C 에서 도체 재료의 용적 열용량(J/°C mm3) ¦ ¦ --- ¦ --- ¦ ¦ B ¦ : 해당 도체에 대한 0 °C 에서 저항률의 온도계수의 역수(°C) ¦ ¦ P20 ¦ : 20 °C 에서 도체 재료의 전기적 저항률(�mm) ¦ ¦ 0 ¦ : 도체의 초기 온도(°C) ¦ ¦ 0 ¦ : 도체의 최종 온도(°C) ¦ 표 A.54.1 - 여러 가지 재료의 변수 값 ¦ 재료 ¦ B a °C ¦ Qa J/°C mm 3 ¦ a P20 � mm ¦ Q(B + 20 °C) P20 AVs /mm2 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 구리 알루미늄 강철 ¦ 234.5 228 202 ¦ 3.45x10-3 2.5x10-3 3.8X10-3 ¦ 17.241 x10-6 28.264x10-6 138x10-6 ¦ 226 148 78 ¦ ¦ a KS C IEC 60949 에 의한 값 ¦ a KS C IEC 60949 에 의한 값 ¦ a KS C IEC 60949 에 의한 값 ¦ a KS C IEC 60949 에 의한 값 ¦ a KS C IEC 60949 에 의한 값 ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 15 | {}
a327460e-ab64-4dc3-a08c-d79de137c597 | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 표 A.54.2 - 케이블에 병합되지 않고 다른 케이블과 묶여 있지 않은 절연 보호도체의 k 값 ¦ 도체 절연 ¦ 온도 °C b ¦ 온도 °C b ¦ 도체의 재질 ¦ 도체의 재질 ¦ 도체의 재질 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도체 절연 ¦ 온도 °C b ¦ 온도 °C b ¦ 구리 ¦ 알루미늄 ¦ 강철 ¦ ¦ 도체 절연 ¦ 초기 ¦ 최종 ¦ k 값 c ¦ k 값 c ¦ k 값 c ¦ ¦ 70 °C 열가소성 물질 (PVC) ¦ 30 ¦ 160/140 a ¦ 143/133 a ¦ 95/88 a ¦ 52/49 a ¦ ¦ 90 °C 열가소성 물질 (PVC) ¦ 30 ¦ 160/140 a ¦ 143/133 a ¦ 95/88 a ¦ 52/49 a ¦ ¦ 90 °C 열경화성 물질 (예: XLPE, EPR) ¦ 30 ¦ 250 ¦ 176 ¦ 116 ¦ 64 ¦ ¦ 60 °C 열경화성 물질 (EPR 고무) ¦ 30 ¦ 200 ¦ 159 ¦ 105 ¦ 58 ¦ ¦ 85 °C 열경화성 물질 (EPR 고무) ¦ 30 ¦ 220 ¦ 166 ¦ 110 ¦ 60 ¦ ¦ 185 °C 열경화성 물질 (실리콘 고무) ¦ 30 ¦ 350 ¦ 201 ¦ 133 ¦ 73 ¦ ¦ a 낮은 값은 b ¦ 단면적이 300 mm2 이상인 열가소성 물질(예: 염화비닐)의 절연도체에 적용한다. ¦ ¦ --- ¦ --- ¦ ¦ 여러 종류의 C k 의 계산방법은 이 부속서의 ¦ 절연물의 최고허용온도는 KS C IEC 60724 에 나타낸다. 처음에 나오는 식을 참조 ¦ 표 A.54.3 - 케이블 피복에 접촉되지만 다른 케이블과 묶여 있지 않은 나보호도체의 k 값 ¦ 케이블 피복 ¦ 온도 °Ca ¦ 온도 °Ca ¦ 도체의 재질 ¦ 도체의 재질 ¦ 도체의 재질 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 케이블 피복 ¦ 온도 °Ca ¦ 온도 °Ca ¦ 구리 ¦ 알루미늄 ¦ 철 ¦ ¦ 케이블 피복 ¦ 초기 ¦ 최종 ¦ k 값 b ¦ k 값 b ¦ k 값 b ¦ ¦ 열가소성 물질 (PVC) ¦ 30 ¦ 200 ¦ 159 ¦ 105 ¦ 58 ¦ ¦ 폴리에틸렌 ¦ 30 ¦ 150 ¦ 138 ¦ 91 ¦ 50 ¦ ¦ CSPC a ¦ 30 ¦ 220 ¦ 166 ¦ 110 ¦ 60 ¦ 여러 종류의 절연물의 최고허용온도는 KS C IEC 60724 에 나타낸다. b 계수 k 의 계산방법은 이 부속서의 처음에 나오는 식을 참조 C CSP = 클로르설문화폴리에틸렌(Chloro-Sulphonated Polyethylene) 16 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
d139beca-c3b3-43f9-b4c3-fac78376240e | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 표 A.54.4 - 케이블에 병합되었거나 다른 케이블과 묶여 있는 선심 또는 절연도체로서 보호도체의 k 값 ¦ 도체 절연 ¦ 온도 °C b ¦ 온도 °C b ¦ 도체의 재질 ¦ 도체의 재질 ¦ 도체의 재질 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도체 절연 ¦ 온도 °C b ¦ 온도 °C b ¦ 구리 ¦ 알루미늄 ¦ 강철 ¦ ¦ 도체 절연 ¦ 초기 ¦ 최종 ¦ k 값 c ¦ k 값 c ¦ k 값 c ¦ ¦ 70 °C 열가소성 물질 (PVC) ¦ 70 ¦ 160/140 a ¦ 115/103 a ¦ 76/68 a ¦ 42/37 a ¦ ¦ 90 C 열가소성 물질 (PVC) ¦ 90 ¦ 160/140 a ¦ 100/86 a ¦ 66/57 a ¦ 36/31 a ¦ ¦ 90 °C 열경화성 물질 (예: XLPE, EPR) ¦ 90 ¦ 250 ¦ 143 ¦ 94 ¦ 52 ¦ ¦ 60 °C 열경화성 물질 (고무) ¦ 60 ¦ 200 ¦ 141 ¦ 93 ¦ 51 ¦ ¦ 85 °C 열경화성 물질 (고무) ¦ 85 ¦ 220 ¦ 134 ¦ 89 ¦ 48 ¦ ¦ 185 °C 열경화성 물질 (실리콘 고무) ¦ 180 ¦ 350 ¦ 132 ¦ 87 ¦ 47 ¦ a 낮은 값은 단면적이 300 mm2 이상인 열가소성 물질(예: 염화비 닐)의 절연도체에 적용한다. b 여러 종류의 절연물의 최고허용온도는 KS C IEC 60724 에 나타낸다. C k 의 계산방법은 이 부속서의 처음에 나오는 식을 참조 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 17 | {}
d846f897-4975-44dd-b2d9-19993f0c4189 | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 표 A.54.5 - 금속외장, 금속 시스, 동축케이블의 외부도체 등과 같은 케이블 금속층의 보호도체에 대한 k 값 ¦ 도체 절연 ¦ 온도 °Ca ¦ 온도 °Ca ¦ 도체의 재질 ¦ 도체의 재질 ¦ 도체의 재질 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 도체 절연 ¦ 온도 °Ca ¦ 온도 °Ca ¦ 구리 ¦ 알루미늄 ¦ 강철 ¦ ¦ 도체 절연 ¦ 초기 ¦ 최종 ¦ k 값 c ¦ k 값 c ¦ k 값 c ¦ ¦ 70 °C 열가소성 물질 (PVC) ¦ 60 ¦ 200 ¦ 141 ¦ 93 ¦ 51 ¦ ¦ 90 °C 열가소성 물질 (PVC) ¦ 80 ¦ 200 ¦ 128 ¦ 85 ¦ 46 ¦ ¦ 90 °C 열경화성 물질 (예: XLPE, EPR) ¦ 80 ¦ 200 ¦ 128 ¦ 85 ¦ 46 ¦ ¦ 60 °C 열경화성 물질 (고무) ¦ 55 ¦ 200 ¦ 144 ¦ 95 ¦ 52 ¦ ¦ 85 °C 열경화성 물질 (고무) ¦ 75 ¦ 220 ¦ 140 ¦ 93 ¦ 51 ¦ ¦ 무기물 열가소성 물질 (PVC) 외장 b ¦ 70 ¦ 200 ¦ 135 ¦ - ¦ - ¦ ¦ 나 무기물 시스 ¦ 105 ¦ 250 ¦ 135 ¦ ¦ ¦ ¦ a 여러 종류의 절연물의 최고허용온도는 KS C IEC 60724 에 나타낸다. ¦ ¦ --- ¦ ¦ b 이 값은 닿거나 가연성 물질이 접촉할 수 있는 노출된 나도체에 관해 사용되어야 한다. C k 의 계산방법은 이 부속서의 처음에 나오는 식을 참조 ¦ 표 A.54.6 - 제시된 온도에서 모든 인접 물질에 손상 위험성이 없는 경우 나도체의 k 값 ¦ 조건 ¦ 초기 온도 °C ¦ 도체 재료 ¦ 도체 재료 ¦ 도체 재료 ¦ 도체 재료 ¦ 도체 재료 ¦ 도체 재료 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 조건 ¦ 초기 온도 °C ¦ 구리 ¦ 구리 ¦ 알루미늄 ¦ 알루미늄 ¦ 철 ¦ 철 ¦ ¦ 조건 ¦ 초기 온도 °C ¦ k 값 ¦ 최대온도 °C ¦ k 값 ¦ 최대온도 °C ¦ k 값 ¦ 최대온도 °C ¦ ¦ 눈에 보이면서 제한된 구역 ¦ 30 ¦ 228 ¦ 500 ¦ 125 ¦ 300 ¦ 82 ¦ 500 ¦ ¦ 통상 조건 ¦ 30 ¦ 159 ¦ 200 ¦ 105 ¦ 200 ¦ 58 ¦ 200 ¦ ¦ 화재 위험성 ¦ 30 ¦ 138 ¦ 150 ¦ 91 ¦ 150 ¦ 50 ¦ 150 ¦ 18 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
2e868b37-c19d-47f6-9207-d00ad78e3301 | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 부속서 B (참고) 접지설비 및 보호도체의 예 ![image](/image/placeholder) LPS LPS Bathroom C6 M M 3 3 SEBT C7 4 1 1 4 DB PE C4 1 MDB C5 PE/PEN 1a C1 C2 C3 2 1 2 MET 5 5 5 지표면 !T2 T2! T1 그림 B.54.1 - 기초접지극, 보호도체 및 보호본딩도체에 관한 접지설비의 예 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 19 | {}
7ff8beb9-fe08-4ea9-af73-5cfb7df83e8e | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 식별 부호 ¦ 기호 ¦ 명칭 ¦ 비고 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ C ¦ 계통외도전부 ¦ ¦ ¦ C1 ¦ 수도관, 외부로부터의 금속부 ¦ 또는 지역난방용 배관 ¦ ¦ C2 ¦ 배수관, 외부로부터의 금속부 ¦ ¦ ¦ C3 ¦ 절연이음새를 삽입한 가스관, 외부로부터의 금속부 ¦ ¦ ¦ C4 ¦ 공조설비 ¦ ¦ ¦ C5 ¦ 난방설비 ¦ ¦ ¦ C6 ¦ 수도관, 예를 들어 욕실 안의 금속부 ¦ KS C IEC 60364-7-701:2008 의 701.415.2 참조 ¦ ¦ C7 ¦ 배수관, 예를 들어 욕실 안의 금속부 ¦ KS C IEC 60364-7-701:2008 의 701.415.2 참조 ¦ ¦ D ¦ 절연이음새 ¦ ¦ ¦ MDB ¦ 주배전반 ¦ ¦ ¦ DB ¦ 분전반 ¦ 주배전반으로부터 전력공급 ¦ ¦ MET ¦ 주접지단자 ¦ 542.4 참조 ¦ ¦ SEBT ¦ 보조등전위본딩단자 ¦ ¦ ¦ T1 ¦ 콘크리트매입 기초접지극 또는 토양매설 기초접지극 ¦ 542.2 참조 ¦ ¦ T2 ¦ 필요한 경우 피뢰시스템(LPS)용 접지극 ¦ 542.2 참조 ¦ ¦ LPS ¦ 피뢰시스템(있는 경우) ¦ ¦ ¦ PE ¦ 분전반 안의 PE 단자 ¦ ¦ ¦ PE/PEN ¦ 주배전반 안의 PE/PEN 단자 ¦ ¦ ¦ M ¦ 노출도전부 ¦ ¦ ¦ 1 ¦ 보호도체(PE) ¦ 543. 참조 단면적은 543.1 참조 보호도체의 종류는 543.2 참조 전기적 연속성은 543.3 참조 ¦ ¦ 1a ¦ 필요하다면 전력공급망으로부터의 보호도체 또는 PEN 도체 ¦ ¦ ¦ 2 ¦ 주접지단자 접속용 보호본딩도체 ¦ 544.1 참조 ¦ ¦ 3 ¦ 보조본딩용 보호본딩도체 ¦ 544.2 참조 ¦ ¦ 4 ¦ 있는 경우 피뢰시스템의 인하도선 ¦ ¦ ¦ 5 ¦ 접지도체 ¦ 542.3 참조 ¦ 피뢰시스템이 설치된 경우 추가요건은 KS C IEC 62305-3:2012 의 6.에, 특히 6.1 과 6.2 에 나타낸다. 비고 기능접지도체는 그림 B.54.1 에 표시되지 않았다. 그림 B.54.1 - 기초접지극, 보호도체 및 보호본딩도체에 관한 접지설비의 예(계속) 20 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
ccfcef75-01c7-49bd-9429-7b14a8e2722b | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 부속서 c (참고) 콘크리트매입 기초접지극의 설치 C.1 일반사항 건축물의 기초에 사용되는 콘크리트는 확실한 전도성을 띠며, 일반적으로 토양과 넓은 접촉 면적을 이룬다. 그러므로, 특수한 열절연 또는 다른 대책을 통하여 토양으로부터 격리된 경우를 제외하고 콘 크리트에 완전히 매입된 나 금속 전극은 접지 목적에 사용될 수 있다. 화학적 및 물리적 효과 로 5 cm 이상의 깊이로 콘크리트에 묻은 나 강철 또는 용융 아연도금 강판 및 다른 금속은 일반적으로 건축물의 전체 수명기간 동안 부식에 대해 고도로 보호된다. 가능한 경우, 건축물 철근의 전도 효과 도 또한 이용된다. 건축물의 건설기간 동안 콘크리트매입 기초접지극의 제작은 다음과 같은 이유로 오랫동안 양호한 접 지를 얻기 위한 경제적인 해결책일 수 있다. - 추가 시추 작업을 필요로 하지 않는다. - 일반적으로 계절의 기상 조건으로 인한 바람직하지 않은 영향을 받지 않는 깊이에 설치된다. - 토양과 양호한 접촉을 제공한다. - 건축물의 기초표면을 실질적으로 모두 이용하며, 그 결과 최소접지극의 임피던스를 이 표면에서 얻을 수 있다. - 피뢰시스템의 목적에 따른 최적의 접지설비가 제공된다. - 건축물의 건설 초기부터 건설 현장의 전기설비의 접지극으로 사용할 수 있다. 그러한 접지 효과 외에도 콘크리트매입 기초접지극은 주보호본딩을 위한 양호한 기준이 된다. 콘크리트매입 기초접지극의 설치에 관한 다음의 요건과 조언을 적용한다. C.2 콘크리트매입 접지극의 사용에 따른 그 밖의 고려사항 비전도성 물질을 사용하여 그것을 절연함으로써 열에너지 손실에 대해 건축물의 기초를 완벽하게 보 호하거나, 기초의 물에 대한 격리 대책, 예를 들어 두께 0.5 mm 이상 플라스틱 판을 사용하여 격리 할 때는 기초 콘크리트를 이용하는 접지는 실현될 수 없다. 이러한 경우에는 보호본딩을 위한 철근 의 긍정적인 효과 를 사용할 수 있고, 접지 목적을 위해 다른 접지설비, 예를 들면, 격리된 기초 아래 에 추가된 콘크리트매입 기초접지극이나, 건축물 주변의 접지설비 또는 토양매설 기초접지극을 사용 할 수 있다. C.3 콘크리트매입 기초접지극의 구조 C.3.1 무근콘크리트 기초에 관해서는 콘크리트매입 기초접지극은 기초의 종류와 크기에 대해 협조 가 이루어져야 한다. 1 이상의 폐쇄 링 또는 20 m 이하의 크기로 상호 접속한 사각형이 바람직하다. C.3.2 콘크리트에 접지가 5 cm 미만의 깊이에 매설되는 것을 피하기 위해 지상 전극배선의 거리에 관한 적절한 방법을 이용해야 한다. 강대를 접지극으로 사용할 때, 강대 아래에 콘크리트가 없는 공 간이 있는 것을 피하기 위해 강대 모서리를 세우고 고정해야 한다. 철근이 있는 경우, 그 배선은 2m 21 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
bb4115ec-a655-48b2-875d-de40435a44ff | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 이하의 간격으로 고정한다. 접속은 542.3.2 에 따른다. 체결 접속의 사용은 피한다. C.3.3 콘크리트매입 기초접지극의 배선은 건축물의 전기계통에 접속하기 위해 건축물의 콘크리트 안에서 인출할 적절한 접속점(예: 주접지단자)이나, 벽 표면의 콘크리트에 매설된 특수접속 클램프의 단말 중 하나에서 1 개 이상의 단자 인출구가 있어야 한다. 접속점의 단자 인출구는 보수 및 측정 목 적으로 접근할 수 있어야 한다. 피뢰시스템과 정보기술에 관한 특별 요건이 있는 건축물은 예를 들어, 피뢰시스템의 인하도선을 위 해 기초접지극의 단자 인출구가 1 개 이상 필요할 수 있다. 토양을 통해서 기초콘크리트의 외부에 접속할 필요가 있을 때, 강선의 부식 문제를 고려해야 한다(C.4 참조). 이러한 접속을 위해, 그 단자 인출구가 건축물의 내부에서 또는 지표 위 적절한 높이의 외부 에서 콘크리트에 들어가는 것을 권장한다. C.3.4 단자 인출구를 포함한 전극의 최소 단면적은 표 54.1 의 규정 값을 적용한다. 접속은 전기적으 로 충족하고 확실하여야 한다(542.3.2 참조). C.3.5 건축물 기초의 철근은 그것이 542.3.2 에 의해 확실하게 접속되어 있다는 조건에서 전극으로 사용할 수 있다. 철근과 철근의 용접 접속은 건축물의 구조 설계 및 구조 해석 책임자의 허가를 필 요로 한다. 철사로만 감은 접속은 보호 목적에 적합하지 않지만, 정보기술에 대한 EMC 목적으로는 충분할 수 있다. PS 콘크리트의 철근은 전극으로 사용해서는 안 된다. 보강을 위해 좀 더 작은 직경의 선으로 만들어진 용접된 격자가 사용된다면 그들이 단자 인출구에서 또는 최소한 표 54.1 에서 요구하는 것과 동일한 단면적을 제공하는 전극의 다른 부분에서 1 개 이상 의 다른 점에 확실히 접속될 때 그들을 전극으로 사용할 수 있다. 이러한 격자의 단선의 최소 직경 은 단자 인출구와 각 격자의 여러 점에서 그 격자와 의 사이에 최소 4 개 접속한 5 mm 이어야 한다. C.3.6 전극의 배선은 더 큰 기초의 다른 부분 사이를 연결 없이 배선하지 말아야 한다. 이러한 장소 에는 필요한 전기적 접속을 제공하기 위해 적절한 적응성이 있는 접속기를 콘크리트의 외부에 설치 한다. C.3.7 단일 기초(예: 대규모 홀 구조를 위한) 콘크리트매입 기초접지극은 적절한 접지도체를 이용하 여 콘크리트매입 기초접지극의 다른 부분에 접속한다. 토양에 묻혀 있는 이러한 접속은 C.4 를 참조 C.4 콘크리트매입 기초접지극 외부의 다른 접지 설비에 가능한 부식 문제 콘크리트에 매설한 일반 강철(나 강철 또는 용융 아연도금 강)은 토양에 매설된 구리의 전기화학적 전위와 동일하게 전기화학적 전위를 갖게 되는 것에 특히 주의 해야 한다. 따라서 기초 근처의 토양 에 매설되어 있고, 콘크리트매입 기초접지극과 접속된 강재로 만든 다른 접지설비에 전기화학적 부 식이 발생할 위험이 있다. 이 영향은 대규모 건축물의 기초에 들어가는 철근에서도 볼 수 있다. 그러므로 스테인리스강이나, 습도에 대해 적절히 사전 제작된 보호에 의해 잘 보호된 접지를 제외하 고, 어떠한 강철 전극도 기초콘크리트에서 직접 토양 속으로 설치해서는 안 된다. 용융 아연도금 피 복이나, 도장에 의한 보호 또는 추후에 다른 유사한 재료에 의한 보호는 이 목적을 위해 충분하지 않다. 이러한 건축물의 부근 및 주변의 추가 접지설비는 그 접지설비의 그 부분에 대해 충분한 수명 을 제공하기 위해 용융 아연도금 강판으로 제작되어야 한다. 22 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
dedfc6bd-0f84-40c5-b5b6-826b605a4ed9 | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 C.5 콘크리트매입 기초접지극의 완성 C.5.1 전극의 접속 및/또는 철근의 부설 작업이 완료된 후, 다만, 콘크리트 충진 전에 해당 설비의 검사와 기록이 숙련자에 의해 실시되어야 한다. 이 기록은 작성, 도면 및 사진이 포함되어야 하며, 그리고 전기설비에 관한 모든 기록의 일부분이어야 한다(KS C IEC 60364 -6 참조). C.5.2 기초에 사용되는 콘크리트는 m3 당 240 kg 이상의 시멘트로 만들어야 한다. 그 콘크리트는 전 극 아래의 모든 공간을 충전하기 위해 적절한 준 액체의 점성을 가져야 한다. 23 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
8371b13e-d9fe-4436-80bc-1ca4dc8278f7 | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 부속서 D (참고) 토양매설 접지극의 설치 D.1 일반사항 접지극의 저항은 그 크기, 그 형상 및 그것이 매설된 토양의 저항률에 달려 있다. 이 저항률은 한 장 소에서 다른 장소로 자주 변화하고 또한 깊이에 따라서도 변화한다. 토양의 저항률은 �m 로 표시한다. 수치적으로는 단면적 1 m2, 길이 1 m 의 원통형 토양의 저항을 용으 로 표시한 것이다. 지표면과 식물의 성장 상황은 접지극의 수행에 대해 토양의 대체로 양호한 특성을 나타낸다. 유사한 토양에 시공된 접지극에 대한 측정 가능한 결과 는 더 나은 지표를 제공한다. 토양 저항률은 그 습도와 온도에 따라 양쪽은 1 년 내내 변화한다. 습도 자체는 토양의 알갱이 모양 및 다공성에 의해 영향을 받는다. 실제로 토양 저항률은 습도가 감소할 때 증가한다. 물이 흐를 수 있는 지층은 그것이 강에 접근하는 경우 접지극의 수행에 적합한 것은 좀처럼 없다. 실제로 이러한 계층은 돌이 많은 토양으로 구성되어 침투성이 좋고 자연적인 필터로 정화된 물에 쉽 게 잠겨 높은 저항률을 나타낸다. 심타봉은 더 나은 전도성을 가질 수 있는 토양 깊숙이 도달하도록 시공한다. 결빙은 상당히 토양 저항률을 증가시켜 동결층에서는 수천 �m 에 도달할 수 있다. 이 동결층의 두께 는 어느 지역에서는 1 m 이상이 될 수 있다. 건조 또한 토양 저항률을 증가시킨다. 가뭄은 어느 지역에서는 깊이 2 m 까지 영향을 줄 수 있다. 이 같은 상황에서 저항률 값은 결빙 기간에 나타나는 저항률과 같은 자릿수이다. D.2 토양 저항률 표 D.54.1 은 어떤 종류의 토양에 대한 저항률 값을 정보로 제공한다. 표 D.54.2 는 같은 종류의 토양에 대해 상당한 비율로 저항률이 변화할 수 있음을 보여준다. 24 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
199982b3-612f-49a2-80c4-1edb5c8606af | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 표 D.54.1 - 토양의 종류에 관한 저항률 ¦ 대지의 성질 ¦ 저항률 �m ¦ ¦ --- ¦ --- ¦ ¦ 습지 ¦ ~30 ¦ ¦ 충적층 ¦ 20~100 ¦ ¦ 부식토 ¦ 10~150 ¦ ¦ 습한 이탄 ¦ 5~100 ¦ ¦ 무른 점토 ¦ 50 ¦ ¦ 이회토 및 조밀점토 ¦ 100~200 ¦ ¦ 쥐라기 이회토 ¦ 30~40 ¦ ¦ 점토질 모래 ¦ 50~500 ¦ ¦ 실리카를 함유한 모래 ¦ 200~3000 ¦ ¦ 나석이 많은 토양 ¦ 1 500~3 000 ¦ ¦ 잔디로 덮인 돌이 많은 토양 ¦ 300~500 ¦ ¦ 부드러운 석회암 ¦ 100~300 ¦ ¦ 조밀한 석회암 ¦ 1 000~5000 ¦ ¦ 균열된 석회암 ¦ 500~1 000 ¦ ¦ 편암 ¦ 50~300 ¦ ¦ 운모 편암 ¦ 800 ¦ ¦ 풍화 작용을 받은 화강암과 사암 ¦ 1 500~10 000 ¦ ¦ 화강암과 특히 열화된 사암 ¦ 100~600 ¦ 접지극 저항의 최초 추정을 가능하게 하기 위해 표 D.54.2 에 표시된 평균값을 사용하여 계산할 수 있다. 이들 값에서 계산된 접지극 저항의 결과 는 단순한 추정에 불과 한 것은 분명하다. D.3 에 주어진 공식 을 사용한 후 이 저항을 측정하여 그 대지의 평균 저항률 값을 평가할 수 있다. 이러한 연구 결과 는 유사한 조건에서 수행하는 향후 작업에 유용하다. 표 D.54.2 - 토양의 종류에 관한 저항률 ¦ 토양의 성질 ¦ 저항률의 평균값 �m ¦ ¦ --- ¦ --- ¦ ¦ 진흙 경작지 토양, 습기가 조밀한 성토 ¦ 50 ¦ ¦ 마른 경작지의 흙, 자갈, 거친 성토 ¦ 500 ¦ ¦ 나석이 많은 토양, 건조한 모래, 불침투성의 암반 ¦ 3000 ¦ D.3 토양에 매설된 접지극 D.3.1 구성 부품 접지극은 다음의 토양에 매설된 소재로 구성될 수 있다. - 용융 아연도금 강 25 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
e6656601-7c99-43cf-b919-dcac8d6c790f | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 - 동피복 강 - 전착동도금 강 - 스테인리스 강 - 나동 다른 특성의 금속 사이의 연결은 토양과 접촉해서는 안 된다. 일반적으로 다른 금속과 합금은 사용 하지 않는다. 다음 품목의 최소 두께와 직경은 일반적으로 화학 및 기계적 열화의 위험을 고려한다. 그러나 이러 한 치수는 부식의 중대한 위험이 존재하는 상황에서는 충분하지 않을 수 있다. 실례로서 전기철도의 귀환 직류 전류 또는 음극방식설비 근처에서 누설되는 전류가 순환하는 토양에서 이 같은 위험이 발 생할 수 있다. 이러한 경우에는 특별한 주의 를 기울여야 한다. 접지극은 유효한 토양의 가장 다습한 부분에 매설한다. 침투로 부식을 일으킬 수 있는 폐기물(거름, 액체 비료, 화학 제품, 석탄 등) 집적장과 번화한 장소에서 가능한 한 멀리 설치해야 한다. D.3.2 접지극 저항의 평가 a) 수평매설도체 수평매설도체(542.2.3 과 표 54.1 참조)에서 실현하는 접지극의 저항(R)은 다음 식에 의해 추정할 수 있다. R=2 은 여기에서 P: 토양의 저항률(�m) L : 도체에 의해 점유되는 트렌치(trench) 길이(m) 트렌치에서 구불구불한 통로를 갖는 도체의 포설은 접지극의 저항을 두드러지게 개선하지 않는다는 사실에 주목해야 한다. 사실 이러한 도체는 다음 두 가지의 다른 방법으로 포설된다. 건축물의 기초접지극: 이러한 접지극은 건축물의 모든 경계부를 둘러싼 기초 루프에서 만들어지고 있다. 고려해야 할 길이는 건축물 주위의 길이이다. - 수평 트렌치: 도체는 이 목적으로 굴착한 트렌치에 약 1 m 깊이로 매설된다. 트렌치는 바위, 석탄재 또는 이와 유사한 재료로 되메우기를 하지 말아야 한다. 그러나 습도를 유지 하기 쉬운 대지로 한다. b) 매설 판(plates) 두 표면이 토양과 양호한 접촉을 유지하기 위해 판 전체를 되도록이면 수직으로 배치하는 것이 바람 직하다. 판은 그 윗면 끝부분이 약 1 m 깊이에 위치하도록 매설한다. 충분한 깊이에 매설된 판 접지극의 저항(R)은 대략 다음 식과 같다. 26 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
675d164d-c37b-420a-90e9-69ade6e60351 | KSCIEC60364-5-54_2024확인_KR | KS CIEC 60364-5-54:2011 R=0.8 은 여기에서 p: 토양의 저항률(�m) L: 판 주위의 길이(m) c) 수직 매설 접지극 수직으로 매설된 접지극(542.2.3 과 표 54.1 참조)의 저항(R)은 다음 식으로 추정할 수 있다. R=은 여기에서 p: 토양의 저항률(�m) L: 봉 또는 관의 길이(m) 결빙 또는 건조의 위험이 있는 경우에는 봉의 길이를 1 m 또는 2m 증가시킨다. 봉이 2 개인 경우에는 봉 1 개의 길이만큼 서로 이격하고, 봉이 3 개 이상인 경우에는 봉 1 개의 길이보 다 더 이격하여 병렬로 접속하여 설치하면 접지극의 저항 값을 줄일 수 있다. 특별히 긴 봉을 사용할 경우, 토양이 드물게 균질성을 가지므로 봉이 저항률이 낮거나 무시할 수 있 는 토양층에 도달할 수도 있다는 사실에 유의 한다. D.4 접지극으로서의 금속주 금속 구조물로 상호 접속되어 있고 땅속의 어느 깊이에 매설된 금속주는 접지극으로 사용할 수 있다. 매설 금속주의 저항(R)은 다음 식에 의해 추정할 수 있다. R = 0.366 은 10g100 여기에서 L : 금속주 매설 길이(m) d: 금속주를 둘러싼 원통의 직경(m) P : 토양의 저항률(�m) 건축물의 주위에 위치한 상호 접속되어 고정된 금속주는 기초접지극과 같은 저항을 가지고 있다. 콘크리트에 매설된 경우 접지극으로 금속주의 사용을 막는 것은 아니며, 접지극 저항을 상당량 수정 하는 것은 아니다. 27 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
2a906b28-c5b6-4190-86c3-10bd102be092 | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 참고문헌 KS C IEC 60050- 195:2003, 국제 전기 기술 용어 - 제 195 부: 감전 보호용 접지 IEC 60050- 826:2004, International Electrotechnical Vocabulary - Part 826: Electrical installations KS C IEC 60079-0, 방폭 전기기계 기구 - 일반 요구사항 KS C IEC 60079- 14, 방폭 전기기계 기구 - 제 14 부: 위험 지역의 전기 설비 KS C IEC 60364-4-43, 저압전기설비 - 제 4-43 부: 안전을 위한 보호 - 과전류에 대한 보호 KS C IEC 60364-5-52, 저압전기설비 - 제 5-52 부: 전기기기의 선정 및 설치 - 배선설비 KS C IEC 60364 - 6, 저압전기설비 - 제 6 부: 검증 KS C IEC 60364- 7-701:2008, 저압전기설비 - 제 7-701 부: 특수설비 또는 특수장소의 요건 욕조 또는 샤워가 있는 장소 IEC 60702 - 1, Mineral insulated cables and their terminations with a rated voltage not exceeding 750 V - Part 1: Cables KS C IEC 61643 - 12, 저압 서지 보호 장치 - 제 12 부: 저전압 배전 계통에 접속한 서지 보호 장치 선정 및 적용 지침 National Standard DIN 18014:1994, Fundamenterder ("Foundation earth electrode" in English) 28 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
2c5cbca1-46d0-4b95-81ee-d8a29727e069 | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364-5-54:2011 KS C IEC 60364-5-54:2011 해 설 이 해설은 본체 및 부속서에 규정 · 기재한 사항 및 이와 관련된 사항을 설명하는 것으로 표준의 일부는 아니다. 1 개요 1.1 개정의 취지 이 표준은 2011 년에 제 3.0 판으로 발행된 IEC 60364-5-54, Low-voltage electrical installations - Part 5- 54: Selection and erection of electrical equipment - Earthing arrangements and protective conductors 를 번역하여 부합화한 것이다. 1.2 개정의 경위 이 표준은 2002 년 제 2 판으로 발행된 IEC 60364-5-54, Electrical installations of buildings - Part 5-54: Selection and erection of electrical equipment -Earthingarrangements and protective conductors 가 2011 년 제 3 판으로 개정됨에 따라 IEC 표준과 일치(IDT)시켜 개정한 것이다. 2 주요 개정 내용 2.1 용어와 정의 KS C IEC 60050 의 용어로 통일시키고 표준 사용자가 이해하기 쉽도록 다음의 용어를 정비하였다. ¦ KS C IEC 60364-5-54(2002) ¦ KS C IEC 60364-5-54(2014) ¦ ¦ --- ¦ --- ¦ ¦ 건축전기설비 - 제 5-54 부: 전기기기의 선정 및 시공 - 접지배치, 보호도체 및 결합도체 ¦ 저압전기설비 - 제 5-54 부: 전기기기의 선정 및 설치 - 접지설비 및 보호도체 ¦ ¦ 접지전극 ¦ 접지극 ¦ ¦ 보호결합도체 ¦ 보호본딩도체 ¦ ¦ 접지배치 ¦ 접지설비 ¦ ¦ 보호도체의 전기적 지속성 ¦ 보호도체의 전기적 연속성 ¦ 2.2 접지설비 a) 접지극의 종류, 재질 및 크기는 수명기간 동안 부식에 견디고 충분한 기계적 강도를 갖는 것을 선 정하도록 하였다. b) 기초접지극을 토양매설 기초접지극과 콘크리트매입 기초접지극으로 분류하고 접지극 저항의 개산 법 등 상세사항을 부속서 C 와 D 에 참고로 신설하였다. 2.2 보호도체 보호도체의 정의 를 명확히 함과 동시에 PEN 도체 외에 PEL 또는 PEM 도체에 관한 요건을 신설하 였다. 29 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
49c3bc34-2de3-4394-9b3e-8bbc982d633b | KSCIEC60364-5-54_2024확인_KR | 3 원안작성 협력자 대한전기협회 KEPIC 처 COSD 그룹(표준개발협력기관 지원사업) 30 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
d87550ee-8527-4d2e-b876-f88e1c8d89d3 | KSCIEC60364-5-54_2024확인_KR | 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
b7f5a058-a3ad-49a0-b8d7-5793a95dbdc2 | KSCIEC60364-5-54_2024확인_KR | KS C IEC 60364 - 5-54:2011 KSKSKS SKSKS KSKS SKS KS SKS KSKS SKSKS KSKSKS Low-voltage electrical installations Part 5-54: Selection and erection of electrical equipment - Earthing arrangements and protective conductors ICS 29.020; 91.140.50 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
9c0efa03-7df5-4a34-89f1-3aad3515724d | 21036D-IC-M16G00-HV-A00-00192 M16_Ph-2 시방서-- APPENDIX-II(PROCESS EXHAUST DUCT ACCESSORY).pdf | SK ecoplant SPECIFICATION FOR HVAC & PLUMBING SYSTEM - APPENDIX-II (PROCESS EXHAUST DUCT ACCESSORY) ¦ DOC No. ¦ : 21036D-IC-M16G00-HV-A00-00192 ¦ ¦ --- ¦ --- ¦ ¦ DISCIPLINE ¦ : HVAC ¦ ¦ PROJECT No. ¦ : 21036D ¦ ¦ PROJECT TITLE ¦ : M16 Ph2 Project ¦ ¦ CLIENT ¦ : SK hynix ¦ ¦ LOCATION ¦ : Icheon city, Gyeonggi-do, Korea ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 2022.01.25 ¦ APPROVED FOR CONSTRUCTION ¦ T.G.YU ¦ J.H. YANG ¦ Y.T.OH ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ REV. ¦ DATE ¦ DESCRIPTION ¦ PRPD ¦ CHKD ¦ APPD ¦ 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. | {}
3881e07c-3ca4-4855-b911-03f1fb9e7297 | 21036D-IC-M16G00-HV-A00-00192 M16_Ph-2 시방서-- APPENDIX-II(PROCESS EXHAUST DUCT ACCESSORY).pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00192 Rev. 0 Page 1 of 5 ¦ ¦ --- ¦ --- ¦ --- ¦ 1. PROCESS EXHAUST DUCT ACCESSORY (STS COATING DUCT) 1.1 PROCESS EXHAUST DUCT ACCESSORY 기준 1.1.1 PROCESS 공정에 따른 순위 분류 ¦ 분 류 ¦ 공 정 ¦ 세부공정 ¦ 비 고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1 순위 ¦ T/F ¦ T/F [TCW (CODE NAME), SIH4, CVD W, PVD W (EQ NAME)] ¦ ¦ ¦ 2 순위 ¦ DIFF, T/F, Cu ¦ ¦ ¦ ¦ 3 순위 ¦ 1 순위, 2 순위 外 ¦ ¦ ¦ 1.1.2 PROCESS 공정 순위에 따른 ACCESSORY 적용 기준 ¦ ACCESSORY ¦ SYSBOL ¦ 1 순위 ¦ 2 순위 ¦ 3 순위 ¦ 비 고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ CHECK WINDOW (W/TEST HOLE) ¦ W ¦ ○ ¦ ○ ¦ ○ ¦ ¦ ¦ CLEAN PORT ¦ CP ¦ ○ ¦ ○ ¦ X ¦ ¦ ¦ ENDOSCOPE PORT ¦ E ¦ ○ ¦ ○ ¦ ○ ¦ ¦ ¦ POWDER CHAMBER ¦ ¦ ○ ¦ ○ ¦ X ¦ ¦ ¦ SUB DUCT 중앙부 POWDER CHAMBER ¦ ¦ T/F Zone [TCW (CODE NAME), SIH4, CVD W, PVD W (EQ NAME)]에 설치 ¦ DIFF Zone [5DAS5901[LTO TEL, NT333]에 설치 ¦ X ¦ ¦ ¦ PRESSURE TRANSMITTER PORT ¦ P ¦ ○ ¦ ○ ¦ ○ ¦ ¦ ¦ TEMPERATURE TRANSMITTER PORT ¦ T ¦ ○ ¦ ○ ¦ ○ ¦ ¦ ¦ DRAIN PORT ¦ D ¦ ○ ¦ ○ ¦ ○ ¦ ¦ ¦ VIBRATOR ¦ ¦ 필요 시 ¦ 필요 시 ¦ 필요 시 ¦ ¦ ¦ N2 Cleaning ¦ ¦ ○ ¦ ○ ¦ X ¦ ¦ - PJT 별 발주처 협의 에 따른 변경 적용 될 수 있음 1.1.3 ACCESSORY 별 설치 기준 (1) CHECK WINDOW + TEST HOLE 공정 순위 구분없이 SUB Duct 말단에 1 개소 설치 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. engineering & construction ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00192 Rev. 0 Page 2 of 5 ¦ ¦ --- ¦ --- ¦ --- ¦ (2) CLEAN PORT 1 순위 : SUB Duct 3m 마다 1 개소씩 Duct 상부 45 도로 설치 (N2 Cleaning Port 2 개당 1 개씩 반영) 2 순위 : SUB Duct 3m 마다 1 개소씩 Duct 상부 45 도로 설치 (N2 Cleaning Port 2 개당 1 개씩 반영) 3 순위 : 미설치 (3) ENDOSCOPE PORT ① 1 순위 : SUB Duct 3m 마다 1 개소씩 Damper 전단 1 개 Duct 상부 45 도로 설치 2 순위 : SUB Duct 6m 마다 1 개소씩 Damper 전단 1 개 Duct 상부 45 도로 설치 ③ 3 순위 : Main Duct 분기점 댐퍼 전단 1 개 Duct 상부 45 도로 설치 (4) POWDER CHAMBER (Duct 밑면에 설치) ① 1 순위 : Main Duct 분기 시작점 1 개 설치 (댐퍼 + POWDER CHAMBER) 2 순위 : Main Duct 분기 시작점 1 개 설치 (댐퍼 + POWDER CHAMBER) ③ 3 순위 : 미설치 (5) SUB DUCT 중앙부 POWDER CHAMBER (Duct 밑면에 설치) 1 순위 : T/F Zone [TCW (CODE NAME), SIH4, CVD W, PVD W (EQ NAME)] 에 설치 2 순위 : DIFF Zone [5DAS5901[LTO TEL, NT333]에 설치 3 순위 : 미설치 (6) PRESSURE TRANSMITTER PORT (Duct 윗면에 설치) ① 1 순위 : SUB Duct 말단에 2 개소 설치 (Monitoring X 1 개소 / Local Guage X 1 개소) 2 순위 : SUB Duct 말단에 2 개소 설치 (Monitoring X 1 개소 / Local Guage X 1 개소) 3 순위 : SUB Duct 말단에 2 개소 설치 (Monitoring X 1 개소 / Local Guage X 1 개소) (7) TEMPERATURE TRANSMITTER PORT (Duct 윗면에 설치) ① 1 순위 : SUB Duct 균등 분할 3 개소 (시작 1 개소, 중간 1 개소, 말단 1 개소) 2 순위 : SUB Duct 균등 분할 3 개소 (시작 1 개소, 중간 1 개소, 말단 1 개소) 3 순위 : Main Duct 분기 시작점 댐퍼 전단 1 개소 설치 (8) DRAIN PORT (Duct 아랫면에 설치) ① 1 순위 : Duct 의 시작점에 100A 1 개 설치 2 순위 : Duct 의 시작점에 100A 1 개 설치 3 순위 : Duct 의 시작점에 100A 1 개 설치 * Duct Up/Down 구간 DRAIN PORT 추가 설치. * 향후 Auto Check Drain 설치 가능토록 구성. (9) N2 Cleaning 1 순위 : 1.5m 당 1 개씩 구성 (80A) / Damper 전단 1 개 구성 2 순위 : 1.5m 당 1 개씩 구성 (80A) / Damper 전단 1 개 구성 3 순위 : 미설치 PJT 별 발주처 협의 에 따른 변경 적용 될 수 있음 hynix SK SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. engineering & construction ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00192 Rev. 0 Page 3 of 5 ¦ ¦ --- ¦ --- ¦ --- ¦ 1.1.4 ACCESSORY DETAIL (REFERENCE) (1) CHECK WINDOW ![image](/image/placeholder) 150 CHECK WINDOW 中 ◇ ◇ ⑪ 0 6 0 , 0 0 0 0 0 0 。 0 。 0 O 0 。 ○ � TEST HOLE(25A) TEST HOLE(25A) (2) CLEAN PORT ![image](/image/placeholder) 70~100 � CLEAN PORT 0 O 0 0 ⑪ 0 0 / 0 。 (⑪) 0 to 0 간 6 中 CLEAN PORT (3) POWDER CHAMBER ![image](/image/placeholder) CLEAN PORT 200 TYP. DAMPER TYP CHECK WINDOW 1,300 F.L ![image](/image/placeholder) CLEAN PORT 200,200,200 DAMPER TYP 1,300 F.L SK hynix SK engineering & construction 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00192 Rev. 0 Page 4 of 5 ¦ ¦ --- ¦ --- ¦ --- ¦ (4) DRAIN PORT ![image](/image/placeholder) 0 0 0 0 200 200 DRAIN PORT 8" DRAIN PORT 8" 1.2 PROCESS EXHAUST DUCT 설치 개념도 1.2.1 1 순위 공정 PROCESS EXHAUST DUCT 설치 개념도 ![image](/image/placeholder) N2 CP N2 N2 N2 E V.D E T N2 T N2 T P 압력계 X 2EA Check F Window CP CP CP E E E Powder Chamber 1.2.2 2 순위 공정 PROCESS EXHAUST DUCT 설치 개념도 ![image](/image/placeholder) CP N2 N2 N2 E 압력계 x 2EA V.D E T N2 T N2 T P Check Window V Powder Chamber SK hynix SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. engineering & construction | {}
a1498b00-019d-4ade-a1be-c3126c4d68d4 | 21036D-IC-M16G00-HV-A00-00192 M16_Ph-2 시방서-- APPENDIX-II(PROCESS EXHAUST DUCT ACCESSORY).pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00192 Rev. 0 Page 5 of 5 ¦ ¦ --- ¦ --- ¦ --- ¦ 1.2.3 3 순위 공정 PROCESS EXHAUST DUCT 설치 개념도 ![image](/image/placeholder) E 압력계 X 2EA V.D Check Window - End of Document - SK hynix SK engineering & construction 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. | {}
712b554b-06a2-4c57-85ce-29a0b8109244 | 21036D-IC-M16G00-HV-A00-00191 M16_Ph-2 시방서-APPENDIX-I (눈관리 STICKER).pdf | ecoplant SK SPECIFICATION FOR HVAC & PLUMBING SYSTEM - APPENDIX-I - (눈 관리 STICKER) ¦ DOC No. ¦ : 21036D-IC-M16G00-HV-A00-00191 ¦ ¦ --- ¦ --- ¦ ¦ DISCIPLINE ¦ : HVAC ¦ ¦ PROJECT No. ¦ : 21036D ¦ ¦ PROJECT TITLE ¦ : M16 Ph2 Project ¦ ¦ CLIENT ¦ : SK hynix ¦ ¦ LOCATION ¦ : Icheon city, Gyeonggi-do, Korea ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 0 ¦ 2022.01.25 ¦ APPROVED FOR CONSTRUCTION ¦ T.G.YU ¦ J.H. YANG ¦ Y.T.OH ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ REV. ¦ DATE ¦ DESCRIPTION ¦ PRPD ¦ CHKD ¦ APPD ¦ 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. | {}
cd9803ff-fc27-49c3-9c20-5a53557d721c | 21036D-IC-M16G00-HV-A00-00191 M16_Ph-2 시방서-APPENDIX-I (눈관리 STICKER).pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00191 Rev. 0 Page 1 of 9 ¦ ¦ --- ¦ --- ¦ --- ¦ 1. 눈 관리 STICKER 1.1 규격 및 재질 1.1.1 배관 및 덕트의 눈 관리 STICKER 의 규격 및 재질은 다음 표에 따른다. ¦ 배관경 ¦ 덕트 SIZE (장변기준) ¦ STICKE SIZE (mm) ¦ 재 질 ¦ 비 고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 15A ~ 125A ¦ 150mm 미만 ¦ 200 X 100 ¦ PVC 시트지 ¦ [그림 A-1 / A-2] ¦ ¦ 150A ~ 300A ¦ 150mm ~ 349mm ¦ 300 X 150 ¦ PVC 시트지 ¦ [그림 B-1 / B-2] ¦ ¦ 350A ~ 750A ¦ 350mm ~ 799mm ¦ 400 X 200 ¦ PVC 시트지 ¦ [그림 C-1 / C-2] ¦ ¦ 800A 이상 ¦ 800mm 이상 ¦ 500 X 250 ¦ PVC 시트지 ¦ [그림 D-1 / D-2] ¦ [그림 A-1] 200 ![image](/image/placeholder) 25 150 25 10 바탕 색상은 LINE 별 색상 참조 ※ 30 FLUID 10 100 SIZE 배관 실명제 시공사 40 FROM 책임자 부착일자 년 월 일 TO 부착자 확인 10 25 70 10 70 25 [그림 A-2] Chart Type: bar 바탄 색상은 LINE 별 색상 참조 ᄊ 바탄 색상은 LINE 별 색상 참조 item_01 70 130 hynix SK SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00191 Rev. 0 Page 2 of 9 ¦ ¦ --- ¦ --- ¦ --- ¦ [그림 B-1] ![image](/image/placeholder) 300 60 180 60 15 ※ 바탕 색상은 LINE 별 색상 참조 45 FLUID 15 150 SIZE 배관 실명제 시공사 09 FROM 책임자 부착일자 년 월 일 TO 부착자 확인 15 60 85 10 85 60 [그림 B-2] Chart Type: pie Red Blue Green Yellow item_01 7% 38% 38% 7% hynix SK SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00191 Rev. 0 Page 3 of 9 ¦ ¦ --- ¦ --- ¦ --- ¦ [그림 C-1] Chart Title: FLUID Chart Type: bar SIZE FROM TO item_01 250Not explicitly stated 250Not explicitly stated 75Not explicitly stated [그림 C-2] Chart Type: bar Red Orange Yellow Green Cyan item_01 140 260 40 20 10 SK hynix SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00191 Rev. 0 Page 4 of 9 ¦ ¦ --- ¦ --- ¦ --- ¦ [그림 D-1] Chart Title: FLUID Chart Type: bar SIZE FROM TO 봅자 95 310 95 벽임자 25 50 90 부회사 20 10 30 뷴 90 70 10 [그림 D-2] Chart Title: 500 Chart Type: line 125 폿 바팅 색상은 LINE 별 색상 참조 175kg 굣 바팅 색상은 LINE 별 색상 참조 325kg -12 630kg -23 -12kg 1.1.2 배관 및 덕트의 눈 관리 STICKER 색상기준 (1) 배관의 눈 관리 STICKER 의 색상은 아래표의 기준에 따른다. ¦ 배관 유체명 ¦ STICKER 색상 ¦ 비 고 ¦ ¦ --- ¦ --- ¦ --- ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
fc98f2bb-5af6-4bfd-afa7-8f7d8a9c25f3 | 21036D-IC-M16G00-HV-A00-00191 M16_Ph-2 시방서-APPENDIX-I (눈관리 STICKER).pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00191 Rev. 0 Page 5 of 9 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 증기(SS) ¦ 적색 PANTONE 199 C ¦ SS SIZE 배관 실명제 식품과 FROM 책임자 부탁물과 TO ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 증기응축수(SR) ¦ 분홍색 PANTONE 213C ¦ SR SIZE 배관 실명제 시골과 FROM 확립자 부터빌라 년 TO 부작자 ¦ ¦ ¦ 냉수(CHS/R) 공정냉각수(PCWS/R) DCC 냉수 (DCWS/DCWR) ¦ 파랑색 PANTONE 072C ¦ LT CHS SIZE 배관 실명제 사람과 FROM 복업자 부착없이 TO ¦ ¦ ¦ 온수(HWS/R) ¦ 노랑색 PANTONE YELLOW C ¦ HWS SIZE 배관 실명제 시공사 FROM 책임자 투자일자 TO 부적자 ¦ ¦ ¦ 시수(CTW) ¦ 초록색 PANTONE 361 C ¦ CTW SIZE 배관 실명제 세종자 FROM 책임자 부착률 TO 시정자 ¦ ¦ ¦ 폐열회수(RHWS/R) ¦ 아이보리 PANTONE 607 C ¦ RHWS SIZE 배관 실명제 사용자 FROM 먹임자 부과 일자 TO 부마다 ¦ ¦ ¦ DRAIN ¦ 회색 PANTONE 173-8 C ¦ DRAIN SIZE 배관 실명제 시원자 FROM 적절차 부착되지 TO 부터의 ¦ ¦ ¦ 중수(NPW) ¦ 보라색 PANTONE 253 C ¦ NPW SIZE 배관 실명제 비교과 FROM 책임자 부착일자 TO 부탁자 확인 ¦ ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00191 Rev. 0 Page 6 of 9 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 공업용수(IW) ¦ 흰색 ¦ IW SIZE 배관 실명제 사전자 FROM 핵심자 부자갈마 년 TO 부터가 확인 ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 우수(SD) ¦ 회색 PANTONE 173-8C ¦ SD SIZE 배관 실명제 시공자 FROM 적동자 부작업자 TO 부탁자 ¦ ¦ ¦ VENT(V) ¦ 회색 PANTONE 173-8C ¦ SIZE 배관 실명제 시공자 FROM 자 부작업자 TO 부작자 ¦ ¦ ¦ H-VAC ¦ 회색 PANTONE 173-8C ¦ H-VAC ¦ 별첨.1 참조 (시방서 끝부분) ¦ * 상기표에 없는 배관 LINE 의 눈 관리 STICKER 색상은 발주 담당자와 협의 하여 결정한다. (2) 덕트의 눈 관리 STICKER 의 색상은 아래표의 기준에 따른다. ¦ 덕트 유체명 ¦ STICKER 색상 ¦ STICKER 색상 ¦ 비 고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ACID EXHAUST ¦ 파랑색 PANTONE 072C ¦ ACID SIZE 배관 실명제 시공자 FROM 해줬다 부작물자 TO ¦ ¦ ¦ HEAT/GEN. EXHAUST ¦ 초록색 PANTONE 361C ¦ H/G SIZE 배관 실명제 시공자 FROM 비용자 부착실자 TO 부탁자 ¦ ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00191 Rev. 0 Page 7 of 9 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ ORGANIC EXHAUST ¦ 분홍색 PANTONE 199 C ¦ ORG SIZE 배관 실명제 사용적 FROM 11 TO ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ EMERGENCY EXHAUST ¦ 회색 PANTONE 173-8 C ¦ EMER' SIZE 배관 실명제 시공자 FROM 책임시 부족십자 TO 부과 다 ¦ ¦ ¦ CABINET EXHAUST ¦ 빨강색 PANTONE 1795 C ¦ CABINET SIZE 배관 실명제 시공자 FROM TO ¦ ¦ ¦ ALKALI EXHAUST ¦ 연적색 PANTONE 7417 C ¦ ALK SIZE 배관 실명제 시공자 FROM 해물자 제일자 TO 부탁자 ¦ ¦ ¦ DRY EXHAUST ¦ 노랑색 PANTONE YELLOW C ¦ DRY SIZE 배관 실명제 비공자 FROM 0 TO ¦ ¦ ¦ PFC EXHAUST ¦ 파랑색 PANTONE 072C ¦ PFC SIZE 배관 실명제 제공제 FROM 18 차 TO ¦ ¦ ¦ HVAC FA, SA, RA, OA, EA ¦ 흰색 ¦ SA SIZE 배관 실명제 사용과 FROM TO 총 본 ¦ ¦ * 상기표에 없는 덕트 LINE 의 눈 관리 STICKER 색상은 발주 담당자와 협의 하여 결정한다. 1.2 눈 관리 STICKER 부착 기준 1.2.1 배관(덕트)의 표식 (1) 배관(덕트)이 머리 상부에 있을 때는 배관 하부에 부착하며, 배관이 머리 하부에 있을 때는 배관(덕트) 상부에 부착하여야 한다. SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00191 Rev. 0 Page 8 of 9 ¦ ¦ --- ¦ --- ¦ --- ¦ (2) 배관(덕트)이 교차로 인하여 표식이 알아보기 힘들 때에는 상황에 맞게 추가 부착하도록 한다. (3) PIPE RACK 에 고정, 설치 되는 배관(덕트)에 부착하는 눈 관리 STIKER 의 위치는 PIPE RACK 과 RACK 사이의 센터에 견고하게 부착하도록 한다. ¦ 구 분 ¦ 구 분 ¦ 간 격 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 장비 연결부 ¦ 1m EQUIPMENT ¦ 1m 이내 ¦ ¦ 수평 & 수직 ¦ 5m (수평 & 수직) ¦ 수평, 수직거리 5m 간격 ¦ ¦ 곡관부 ¦ 1m 트 ¦ 굴곡지점 1m 이내 ¦ ¦ 관말부 ¦ 1m m ¦ 관말에서 1m 이내 ¦ ¦ 밸브 및 플랜지 ¦ 1m 1m ¦ 1m 이내 ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
5c20c5a4-43eb-46b9-b473-54f3205edbf6 | 21036D-IC-M16G00-HV-A00-00191 M16_Ph-2 시방서-APPENDIX-I (눈관리 STICKER).pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00191 Rev. 0 Page 9 of 9 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 벽체 관통부 ¦ 1m 1m 관통부 전·후 1m 이내 ¦ ¦ --- ¦ --- ¦ ¦ 눈 관리 STICKER 방향 ¦ ¦ 1.2.2 기타의 표식 배관(덕트)표식 이외의 안전표식 및 수송표식 등에 대한 표식은 발주 담당자의 지시에 의한다. 별첨.1 H-VAC 배관 SIZE 별 Sticker 분류 표준 Table ¦ No ¦ 배관 Size ¦ Sticker Size (가로 x 세로) ¦ 장비명 기입란 Size (가로 x 세로) ¦ 화살표 Size (가로 X 세로) ¦ 글씨 Size ¦ 글씨체 ¦ 비고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ 1/4" ~ 1/2" ¦ 60mm X 10mm ¦ 18mm X 6mm ¦ 14mm X 6mm ¦ 24 Point ¦ Arial Bold ¦ 테두리 1pt ¦ ¦ 2 ¦ 3/4" ~ 1" ¦ 76mm X 20mm ¦ 20.5mm X 11.5mm ¦ 14mm X 12mm ¦ 32 Point ¦ Arial Bold ¦ 테두리 1pt ¦ ¦ 3 ¦ 1 1/4" ~ 2" ¦ 127mm X 25mm ¦ 39.5mm X 16.5mm ¦ 18mm X 11mm ¦ 34 Point ¦ Arial Bold ¦ 테두리 1pt ¦ ¦ 4 ¦ 40A, 25A ¦ 127mm X 25mm ¦ 39.5mm X 16.5mm ¦ 18mm X 11mm ¦ 34 Point ¦ Arial Bold ¦ 테두리 1pt ¦ ¦ 5 ¦ 2 1/2" ~ 4" ¦ 203mm X 38mm ¦ 59.5mm X 29.5mm ¦ 38mm X 23mm ¦ 54 Point ¦ Arial Bold ¦ 테두리 1pt ¦ ¦ 6 ¦ 5" ~ 8" ¦ 254mm X 51mm ¦ 62.5mm X 36.5mm ¦ 47mm X 31mm ¦ 78 Point ¦ Arial Bold ¦ 테두리 1pt ¦ ¦ 7 ¦ 8" 초과 ¦ 305mm X 76mm ¦ 75 mm X 57mm ¦ 57mm X 46mm ¦ 100 Point ¦ Arial Bold ¦ 테두리 1pt ¦ - End of Document - SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
af8bdc74-34cc-4087-a63a-f5ab825118ba | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1 KSKSKSKS KSKSKSK KSKSKS KSKSK KSKS KSK K KS 저전압 개폐 장치 및 제어 장치 부속품 - 제 1 부: 형식 시험 및 부분 형식 시험 부속품 KS C IEC 60439-1 : 1999 산 업 표 준 심 의 회 2003 년 11 월 3 일 제정 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
dd881ebe-8eea-4db9-a4de-ba336e78ad1f | KSCIEC60439-1_2024확인_KR | KS CIEC 60439-1:1999 심 의 : 전력기기 기술심의 회 성 명 근 무 처 직 위 (회 장) 홍 순 찬 단국대학교 교 수 (위 원) 김 재 철 숭실대학교 교 수 박 현 주 한전전력연구원 책 임 서 호 선 케이알지식재산법률사무소 대 표 심 대 섭 J&I 시스템기술연구소 대 표 안 상 필 한국전기연구원 본 부 장 이 주 철 (주)건일이엔지 소 장 전 기 중 (주)피디엔에스 전 무 채 경 수 한국스마트의 료기기산업진흥재단 연 구 위 원 (간 사) 진 상 언 국가기술표준원 표준정책국 전기전자정보표준과 연 구 관 원안작성협력 : 저압개폐장치류 전문위원회 성 명 근 무 처 직 위 (대표전문위원) 최 상 열 인덕대학교 교 수 (위 원) 김 명 식 한국전기에너지산업협동조합 전 무 이 사 김 민 영 (주)에이치디전력기술단 이 사 김 복 용 (주)삼성파워텍 이 사 김 태 경 (주)비츠로이엠 치 장 박 노 천 (주)비츠로이엠 부 장 박 태 식 (주)베스텍 연 구 소 장 송 민 국 HD 현대일렉트릭 책 임 연 구 원 송 인 권 슈나이더 일렉트릭 코리아 팀 장 신 성 수 대한전기협회 팀 장 오 준 식 LS 일렉트릭(주) 매 니 저 (간 사) 정 흥 수 한국전기연구원 책 임 기 술 원 표준열람 : e 나라표준인증(http://www.sranniand.go.kr) 제 담당부처 : 산업통상자원부 국가기술표준원 제 심 정 자 : 산업표준심의 회 위원장 정 : 2003 년 11 월 3 일 의 : 산업표준심의 회 전력기기 기술심의 회 원안작성협력 : 저압개폐장치류 전문위원회 이 표준에 대한 의견 또는 질문은 e 나라표준인증 웹사이트를 이용하여 주십시오. 이 표준은 산업표준화법 제 10 조의 규정에 따라 매 5 년마다 산업표준심의 회에서 심의 되어 확인, 개정 또는 폐지됩니다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
5ea8f654-800d-483d-93d5-333c74873072 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 목 차 서 문 ........................ 1 1. 일반 사항 ................ 1 1.1 적용 범위 및 목적 - 1 1.2 인용 규격 .............. 1 2. 정 의 .................... 3 2.1 일반 사항 .............. 3 2.2 부속품의 구조적 장치 ------ 4 2.3 부속품의 외부 설계 .......................... ......................... 5 2.4 부속품의 구조적 부분 ---- 5 2.5 부속품의 설치 조건 - 6 2.6 전기 감전에 관한 보호 측정 ............. 6 2.7 부속품 내의 통로 --- 7 2.8 전기적 기능 ........... 7 2.9 절연 협조 .............. 7 2.10 단락 회로 전류 .... 8 3. 부속품의 분류 ........ 9 4. 부속품의 전기적 특징 ⌀10mmx⌀10mm 9 4.1 정격 전압 ⌀10mmx⌀10mm:1mm 9 4.2 정격 전류(h) (부속품 회로의) ................. 10 4.3 정격 단기 전류(/cw) (부속품 회로의) ......................... 10 4.4 정격 첨두 내전류(pk) (부속품 회로의) ··························· 10 4.5 정격 조건부 단락 전류(cc)(부속품 회로의) ...................................... 10 4.6 정격 퓨즈 단락 회로 전류(kf) (부속품 회로의) ......................................... 10 4.7 정격 변화율 --------- 10 4.8 정격 주파수 ......... 10 5. 부속품에 관한 정보 - 11 5.1 명 판 ................ 11 5.2 표 시 ---------------- 11 5.3 설치, 작동 및 유지 보수 방법 ................. 11 6. 공급 조건 ·········_ 12 6.1 정상 공급 조건 ----- 12 6.2 특별 공급 조건 ...... 12 -i- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 하며 불법 복사및 무단 배포를 금 니다. | {}
7fc297fb-0454-4192-a978-b66a9b13292b | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 6.3 운송, 저장, 조립시 조건 ········· 13 7. 설계와 구조 ··········· 13 7.1 기계적 설계 ・・・・・・・ 13 7.2 외함과 보호 등급 - 16 7.3 온도 상승 ................................... ・・・・・・・・・・・・・・・ 17 7.4 전기 감전에 대한 보호 ・・・・・・・・・・・・ ・・・・・・・・ .............. 18 7.5 단락 회로 보호와 단락 회로 저항 강도 ······················· ................ 24 7.6 부속품에 설치된 개폐 장치와 구성 22.................... 26 7.7 장벽이나 분할에 의한 부속품의 내부 분리 ................................................... .................... 30 7.8 부속품 내의 전기적 연결 : 장애물과 절연 도체 ・・・・・・・・・・・・・・・・ ・・・・・・・・・・・・・・・・・ 30 7.9 전자 장치 공급 회로의 요구 사항 .......... 31 7.10 전자기 호환성(EMC) ······················· 32 7.11 전기적 연결 기능 장치 유형 설명 ························ 33 8. 시험 설명 ······················· ························· 33 8.1 시험 분류 ・・・・・・・・・・・・ 33 8.2 형식 시험 ・・・・・・・・・・・・・ 34 8.3 정규 시험 ············ 46 부속서 A(규정) 연결에 적합한 구리 도체의 최소 및 최대 단면 ······················ 50 부속서 B(규정) 단시간의 전류로 인한 열 압력에 관련된 보호 도체의 단면적 계산법 ..........................51 부속서 C(참고) 부속품의 전형적인 예 ・・・・・・・・・・・・ ..........................52 부속서 D(참고) 내부 분할의 형태 ・・・・・・・・ ------------------------- 62 부속서 E(참고) 제조업자와 사용자 사이의 협의 에 따른 항목 --------------------------------------------------- 65 부속서 F(규정) 연면 거리와 공간 거리의 측정 ························ 66 부속서 G(규정) 공급 시스템의 미소 전압과 설비의 정격 충격 저항 전압 사이의 상관성 ・・・・・・・・・・・・・・・・・・・・・・・・ 71 참고 문헌 ・・・・・・・・・・・・・・ ··················································· 72 0+Au 그림 1 시간 함수로 의 비율 ························· 31 0 그림 2 공칭 시스템 전압의 최대 허용 고조파 성분 ........................................... 32 그림 C.1 개방형 부속품(2.3.1 참조) .............................. ・・・・・・・・・・・・・・ 52 그림 C.2 앞이 막힌 부속품(2.3.2 참조) ····························· ................ 53 그림 C.3 큐비클형 부속품(2.3.3.1 참조) ··························· 54 그림 C.4 다중 큐비클형 부속품(2.3.3.2 참조) ・・・・・・・・・・・・・・・・・・・・・ ..................55 그림 C.5 책상형 부속품(2.3.3.3 참조) ・・・・・・・・・・・・・・・・・ .................. 56 그림 C.6 다중 상자형 부속품(2.3.3.5 참조) --------------------------------------------------- ····················· 57 그림 C.7 부스바 트렁킹 시스템(2.3.4 참조) ................................................... 58 그림 C.8 설치 구조(2.4.2 참조) ................ 59 -ii- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 하며 불법 복사및 무단 배포를 금합 니다. | {}
005e9d74-e2ed-4a4a-ad4b-32cfe0cf6266 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 그림 C.9 고정 부분(2.2.5, 2.4.3, 2.4.4 참조) ............................() 그림 C.10 회수 가능한 부분(2.2.7 참조) ............................ 61 그림 D.1 그림 D.2 에 사용된 기호 ·················· 62 그림 D.2 형태 1 과 2 ⌀1mm:1mm 63 그림 D.2 형태 3 과 4 ······ 64 그림 F.1 리브의 측정 - 66 표 1 정격 변화율 값 ⌀10000000000000000000000000 10 표 2 온도 상승 범위 ·················· ··················· 17 표 3 보호 도체의 단면적(PE, PEN) - ···················· 21 표 3A 구리 결합 도체의 단면적 .............................. ················· 22 표 4 인수 n 의 표준 값 ....................................... ·············· 25 표 5 도체 선택과 설치 요구 사항 ··················································· ...................... 26 표 6 회수 가능한 부분의 다른 위치에서의 전기 조건 ............................. ...................29 표 7 TTA 와 PTTA 에 수행된 검증과 시험 목록 ················· ·············· 35 표 8 400 A 이상의 시험 전류에 대한 시험 구리 도체 ・・・・・・・・・・・・・・・・・ ················· 37 표 9 시험 전류에 따른 구리 도체의 기준 단면적 ······························ ·················· 38 표 10 ···················· ··················································· ························· 39 표 11 ······ ······················· ··············· 40 표 12 예상 장애 전류와 구리 전선의 지름 사이의 관계 ························· ················· 42 표 13 임펄스, 전력 주파수와 직류 시험에 대한 절연 저항 전압 ・・・・・・・・・・・・・・・・ ················· 47 표 14 공기 중의 최소 공간 거리 --------------------------------------------------- 48 표 15 절연에 적합한 설비의 개방 접촉부에 걸린 시험 전압 - 48 표 16 최소 연면 거리 - 49 표 A.1 ....... 50 표 B.1 케이블에 연결하지 않은 절연 보호 도체 또는 케이블 외피와 접촉하는 노출된 보호 도체의 k 값 ・・・・・・・・・ 51 표 G.1 IEC 60099-1 에 따른 서지 피뢰기에 의한 과전압 보호의 경우, 공급 시스템의 미소 전압과 설비 정격 충격 저항 사이의 상관성 ········ 71 -iii- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
bd4dc19a-20bb-4ead-9cee-aeaecad7fb7f | KSCIEC60439-1_2024확인_KR | 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
d001e137-49ef-4079-b20d-8d3bae2cc000 | KSCIEC60439-1_2024확인_KR | 한국산업표준 KS C IEC 60439-1:1999 저전압 개폐 장치 및 제어 장치 부속품 - 제 1 부: 형식 시험 및 부분 형식 시험 부속품 Low-voltage switchgear and controlgear assemblies Part 1: Type-tested and partially type-tested assemblies 1. 일반 사항 1.1 적용 범위 및 목적 이 규격은 1000Hz, 또는 1500V 직류를 넘지 않는 주파수에서, 1000V 를 초과 하 지 않는 정격 전압의 저전압 개폐 장치 및 제어 장치 부속품[(형식 시험 부속품(TTA)과 부분 형식 시험 부속품(PTTA)]에 적용된다. 이 규격은 또한 주파수가 더 높은 제어와(또는) 전원 장치에 연결되는 부속품에도 적용된다. 이러한 경우, 적절한 추가 요구 사항이 적용된다. 이 규격은 외함을 갖거나 또는 갖지 않는 고정형 또는 이동형 부속품에 적용된다. 비 고 부속품의 특정 형식의 추가 요구 사항이 IEC 규격 보충판에 주어진다. 이 규격은 전기 에너지의 발생기, 전송, 배전과 변환 연결 그리고 전기 에너지 소비 장치의 제어에 사용 되기 위해 적용된다. 예를 들어 선박, 철도 운송 수단, 기계 장치, 승강기 또는 폭발성 대기와 같은 특별 공급 조건 하에서 사용될 목적으로 설계된 부속품에도 적용되고, 관련 규격 요구 사항에 제공되는 국내(비전문가가 작동하 는) 응용물도 이에 따른다. 이 규격은 모터 시동기, 퓨즈 스위치, 전기 장치 등의 개별 장치들과 자체- 포장 성분에는 적용되지 않고 그들의 관련 규격에 따른다. 이 규격의 목적은 정의 와 공급 조건, 구조적 요구 사항, 기술적 특징 및 저전압 개폐 장치 및 제어 장치 부속품의 시험을 규정한다. 1.2 인용 규격 다음 인용 문서는 본문의 인용을 통해, 이 규격 규정을 구성하는 규정을 포함한다. 기한이 지난 규격, 일련의 수정안 또는 발행판의 개정들은 적용되지 않는다. 그러나, 이러한 국제 규격에 기초하여 동의 한 참가원들은 아래 표시되는 인용 문서의 가장 최신판이 적용될 가능성을 조사해보는 것이 권장된다. 기한이 정해지지 않은 규격, 언급된 인용 문서의 최신 판이 적용된다. IEC 와 ISO 의 구성원들은 일반적으로 유효한 국제 규격의 등록을 유지한다. IEC 60038 : 1983, IEC 규격 전압 IEC 60050(441) : 1984, 국제 전기 기술 용어(IEV)-441 장 : 개폐 장치, 제어 장치 그리고 퓨즈 IEC 60050(471) : 1984, 국제 전기 기술 용어(IEV) -471 장 : 절연체 IEC 60050(604) : 1987, 국제 전기 기술 용어(IEV) - 604 장 : 전기의 발전, 변환과 분배 - 작동 IEC 60050(826) : 1982, 국제 전기 기술 용어(IEV) -826 장 : 건물의 전기 설치 IEC 60060, 고전압 시험 기술 IEC 60071-1 : 1976, 절연 협조- 제 1 부 : 용어, 정의, 원리 및 법칙 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 1 | {}
97662a7d-9507-4607-9437-028e2e34c9a2 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 IEC 60073 : 1996, 맨머신 인터페이스의 기본적이고 안전적 원리, 표시 및 확인-표시 장치와 작동기 원리의 부호화 IEC 60099-1 : 1991, 서지 피뢰기-제 1 부 : 교류 시스템에 대해, 서지 피뢰기와 떨어진 비선형 저항기 유형 IEC 60112 : 1979, 습한 조건 하에서 고체 절연 물질의 비교와 교정 - 추적 목록의 측정 방법 IEC 60146-2 : 1974, 반도체 변환기 - 제 2 부 : 반도체 자기 전환 변환기 IEC 60158-2 : 1982, 저전압 제어 장치 - 제 2 부 : 반도체 접촉기(고체 상태 접촉기) IEC 60227- 3 : 1993, 450/750V 이상 정격 전압의 폴리비닐 염화물 절연 케이블- 제 3 부 : 고정 배선용 비 외장 케이블 IEC 60227-4 : 1992, 450/750V 이상의 정격 전압 폴리비닐 염화물 절연 케이블- 제 4 부 : 고정 배선용 외장 케이블 IEC 60245-3 : 1994, 450/750 v 이상의 정격 전압 고무 절연 케이블- 제 3 부 : 열저항 실리콘 절연 케이블 IEC 60245-4 : 1994, 450/750 v 이상의 정격 전압 고무 절연 케이블- 제 4 부 : 코드와 유연한 케이블 IEC 60269, 저전압 퓨즈 IEC 60364-3 : 1993, 건물의 전기 설치- 제 3 부 : 일반 특성 평가 IEC 60364-4-41 : 1992, 건물의 전기 설치 - 제 4 부 : 안전 보호-41 장 : 전기 감전에 대한 보호 IEC 60364-4-443 : 1995, 건물의 전기 설치 ¦ 제 4 부 : 안전 보호-44 장 : 과전압에 대한 보호 - 443 절 : 방전 또는 스위칭에 의한 과전압에 대한 보호 IEC 60364-4-46 : 1981, 건물의 전기 설치 - 제 4 부 : 안전 보호-46 장 : 절연과 스위치 IEC 60364-5-54 : 1980, 건물의 전기 설치- 제 5 부 : 전기 장치의 선택과 조립-54 장 : 접지 배치와 보호 도체 IEC 60417(모든 부분), 장치에 쓰이는 도표의 기호. 표시, 단일 문서의 조사와 편집 IEC 60445 : 1988, 단자와 정확하게 설계된 도체의 말단과 문자와 숫자를 조합한 시스템의 일반적 규 칙을 포함한 장치 확인 IEC 60446 : 1989, 색깔과 숫자에 의한 도체 확인 IEC 60447 : 1993, 맨머신 인터페이스(MMI)- 작동 원리 IEC 60502 : 1994, 1kV 에서 30kV 까지의 정격 전압을 위해 돌출된 고체 유전체 절연 전력 케이블 IEC 60529 : 1989, 외함(IPCode)에 의해 제공되는 보호 등급 IEC 60664-1 : 1992, 저전압 시스템 내의 장치를 위한 절연 조정 - 제 1 부 : 원리, 요구 사항 및 시험 IEC 60750 : 1983, 전기 공학의 항목 지정 IEC 60865(모든 부분), 단락 회로 전류- 효과 계산 IEC 60890 : 1987, 저전압 개폐 장치 및 제어 장치의 부분적 형식 시험을 거친 부속품(PTTA)의 추정 에 의한 온도 상승 평가 방법 IEC 60947- 1 : 1988, 저전압 개폐 장치 및 제어 장치 - 제 1 부 : 일반 규칙 IEC 60947- 3 : 1999, 저전압 개폐 장치 및 제어 장치 - 제 3 부 : 스위치, 연결 해제 장치, 스위치 연결 해 제 장치 및 퓨즈 조합 단위 IEC 60947-4-1 : 1990, 저전압 개폐 장치 및 제어 장치-제 4 부 : 접촉기와 모터 시동기- 1 절 : 전기 공 학적 접촉기와 모터 시동기 IEC 61000-4-2 : 1995, 전자기 호환성 (EMC)- 제 4 부 : 시험과 측정 기술-2 절 : 정전기 방전 보호 시험 - 기본 EMC 출판 2 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
9a503f29-06c5-4e31-938b-3d5d757d2d54 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 IEC 61000-4-3 : 1995, 전자기 호환성(EMC)- 제 4 부 : 시험과 측정 기술-3 절 : 복사, 무선 주파수, 전자 기장 보호 시험 IEC 61000-4-4 : 1995, 전자기 호환성(EMC)- 제 4 부 : 시험과 측정 기술-4 절 : 전기적 과도 전류 폭발 보호 시험 - 기본 EMC 출판 IEC 61000-4-5 : 1995, 전자기 호환성(EMC)- 제 4 부 : 시험과 측정 기술-5 절 : 서지 피뢰기 시험 IEC 61117 : 1992, 부분적 형식 시험된 부속품(PTTA)의 단락 회로 저항력 평가 방법 CISPR 11 : 1990, 산업, 과학, 의료(ISM) 무선 주파수 장비의 전자기적 교란 특징의 제한과 측정 방법 2. 정 의 이 규격의 목적을 위해 다음의 정의 들이 적용된다. 비 고 이 절의 어떤 정의 들은 바뀌지 않았거나 IEC 60050(IEV) 또는 다른 IEC 발행물로부터 수정되 었다. 2.1 일반 사항 2.1.1 저전압 개폐 장치 및 제어 장치 부속품(부속품) 제조자의 책임 하에 모든 내부 전기와 기계적 상호 연결, 구조상의 부분으로 완전하게 조립된 제어, 측정, 신호, 보호, 조정 장치 등으로 함께 연결된 한 개 또는 그 이상의 저전압 개폐 장치 결합(2.4 참조) 비 고 1. 이 규격의 전반에 걸쳐, 부속품이라는 약어는 저전압 개폐 장치 및 제어 장치 부속품에 대해 사용된다. 비 고 2. 부속품의 성분은 전기 기계적 또는 전기적일 수 있다. 비 고 3. 여러 가지 이유로 인해, 예를 들어 운송 또는 생산의 특정 조립 단계는 제조사의 공장 외 부에서 이루어질 수 있다. 2.1.1.1 형식 시험된 저전압 개폐 장치 및 제어 장치 부속품(TTA) 이 규격에 부합하여 검증된 전형적인 부속품으로부터, 성능에 중요한 영향을 미치는 것과 같이 편차가 없도록 확증된 유형 또는 시스템에 일 치하는 저전압 개폐 장치 및 제어 장치 부속품 비 고 1. 이 규격의 전반에 걸쳐, TTA 라는 약어는 형식 시험된 저전압 개폐 장치 및 제어 장치 의 부속품에 사용된다. 비 고 2. 여러 가지 이유로 인해, 예를 들어 운송 또는 생산의 특정 조립 단계는 TTA 제조사의 공장 외부에서 이루어질 수 있다. 그러한 부속품은 TTA 로 제공된 부속품으로 생각될 수 있는데 정규 시험이 적용 가능한 제안을 포함하면서 규격이 확실한 입증된 유형이 나 시스템에 따르는 방식으로 제조사의 지시에 일치하도록 행해진다. 2.1.1.2 부분적으로 형식 시험된 저전압 개폐 장치 및 제어 장치 부속품(PTTA) 형식 시험된 배치와 형식 시험되지 않은 배치 둘 다를 포함하는 저전압 개폐 장치 및 제어 장치 부속품[관련 시험(표 7 참조)에 부 합하는 형식 시험된 배치로부터 후자가 도출(예, 계산에 의해) 된다면] 비 고 이 규격의 전반에 걸쳐, PTTA 의 약어는 부분적으로 형식 시험 개폐 장치 및 제어 장치 부 속품에 쓰인다. 2.1.2 주 회 로(부속품) 전기 에너지를 운반할 수 있는 회로를 포함하는 부속품의 모든 도체 부분[IEV 441 - 13-02] 2.1.3 보조 회로(부속품) 제어, 측정, 신호, 조정, 자료 처리 등을 할 수 있는 회로(주회로와 는 다른)를 포 함하는 부속품의 모든 도체 부분[수정된 IEV 441-13-03] 비 고 부속품의 보조 회로는 개폐 장치의 제어 및 보조 회로를 포함한다. 2.1.4 부 스 바 몇 개의 전기 회로가 개별적으로 연결될 수 있도록 하는 낮은 임피던스 도체 3 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
64a7f5bf-7645-48d5-b0fb-96a3d03d9bde | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 비 고 부스바라는 용어는 기하학적 모양, 크기, 또는 도체의 넓이를 전제로 하지는 않는다. 2.1.4.1 주부스바 한 개 또는 여러 개의 배전 부스바와(또는) 입력 장치와 출력 장치가 연결될 수 있는 부스바 2.1.4.2 배전 부스바 주부스바와 연결되고 출력 장치에서 공급되는 한 구획 내의 부스바 2.1.5 기능 장치 같은 기능의 수행에 도움이 되는 모든 전기적이고 기계적인 요소들을 구성하는 부속품 부분 비 고 기능 장치와 연결되었으나 구획 또는 폐쇄되고 보호된 영역(예로 공통 구획과 연결된 보조 케이블)의 외부에 있는 도체들은 기능 장치 부분을 형성한다고 보지 않는다. 2.1.6 입력 장치 전기 에너지가 부속품 안으로 정상적으로 공급되는 기능 장치 2.1.7 출력 장치 전기 에너지가 하나 또는 그 이상의 출력 회로에 정상적으로 공급되는 기능 장치 2.1.8 기능적 그룹 조작 기능의 이행을 위해 전기적으로 내부 연결된 여러 개의 기능 장치의 집합 2.1.9 시험 상태 협력 장치의 작동 시험이 허용되므로, 관련 주회로는 개방되어 있으나, 결합 보조 장 치가 연결되는 동안 반드시 분리(절연)되지는 않는 부속품 또는 그 일부의 상태 2.1.10 분리 상태 주회로와 관련되고, 보조 회로와 연결된 부속품 또는 그 일부가 분리된 (절연된) 상태 2.1.11 연결된 상태 주회로와 관련되고, 보조 회로와 연결된 부속품 또는 그 일부가 그것의 정상적으로 계획된 기능에 연결된 상태 2.2 부속품의 구조적 장치 2.2.1 구 획(그림 C.4 참조) 두 개의 연속하는 수직 도형 사이에 있는 부속품의 구조적 장치 2.2.2 일부 구획(sub-section) 구획 내의 두 개 연속하는 수평 도형 사이에 있는 부속품의 구조적 장치 2.2.3 칸 막 이 상호 연결, 제어 또는 통풍 상태에 필요한 통로를 제외하고 폐쇄된 구획 또는 일부 구획 2.2.4 전송 장치 기계의 분해 없이 운반하기에 알맞은 부속품의 일부 또는 완전 부속품 2.2.5 고정된 부품(그림 C.9 참조) 공통 지속과 고정된 설치로 설계된 조립과 이루어진 성분과 고정된 설치를 위해 설계된 부품 2.2.6 제거 가능한 부품 부속품로부터 완전히 제거될 수 있고 회로에 전기가 통하고 있을 때에도 교체 되는 부품 2.2.7 회수 가능한 부품(그림 C.10 참조) 만약 부속품에 기계적으로 접합되어 있을 때 연결된 위치에서 단절된 위치와 시험 위치로 옮길 수 있는 제거 가능한 부품 비 고 절연 거리는 주회로만 관련되거나 또는 주회로와 보조 회로에 관련된다(2.2.10 참조). 표 6 역시 참조 2.2.8 연결된 위치 정상적인 기능대로 완전히 연결된 상태에서 제거 또는 회수 가능한 부품의 위치 2.2.9 시험 위치 관련 주회로가 공급쪽에 열려있으나 필수적으로 분리(절연된) 되어 있지 않고, 보조 회 로가 연결되어 있어서 부속품에 기계적으로 접해있는 회수 가능한 부품의 작동 시험을 허가하는 위치 비 고 통로는 적당한 장치의 작동에 의해 회수 가능한 부품의 기계적 움직임 없이 이루어 질 수 있다. 2.2.10 분리된 위치(절연된 위치) 기계적으로 부속품에 밀착한 회수 가능한 부분인 주회로와 보조 회로 에 설치된 절연 거리에서 회수 가능한 부품의 상태 비 고 절연된 거리는 적절한 장치의 작동에 의해 회수 가능한 부품의 어떠한 기계적 움직임 없이 도 입증될 수 있다. 2.2.11 제거된 위치 제거 또는 회수 가능한 부품이 부속품 외부에 있을 때 부속품으로부터 기계적이고 전기적으로 떨어져 있는 위치 4 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
3f08b108-f6a0-4d51-a690-f8e6233dbe45 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 2.2.12 기능 장치의 전기적 연결 2.2.12.1 고정된 연결 도구에 의해 연결되거나 분리되는 연결 2.2.12.2 단절된 연결 도구 없이 수동 작동으로 연결되거나 분리되는 연결 2.2.12.3 회수 가능한 연결 기능적 장치를 연결하거나 분리되는 상태로 만들어내는 연결되거나 분리되는 연결 2.3 부속품의 외부 설계 2.3.1 개방형 부속품(그림 C.1 참조) 전기 장비와 접근하기 쉬운 활성부를 지원하는 지원 구조로 이루 어져 있는 부속품 2.3.2 앞이 막힌 부속품(그림 C.2 참조) 정면에서 적어도 IP2X 의 보호 등급을 제공하는 앞 덮개의 개방형 부속품, 활성부는 다른 방향에서 접근 가능하다. 2.3.3 폐쇄된 부속품 적어도 IP2X 의 보호 등급을 제공하는 가능한 설치 표면을 제외한 모든 방면에서 폐쇄된 부속품 2.3.3.1 큐비클형 부속품(cubicle-type ASSEMBLY)(그림 C.3 참조) 여러 개의 구획, 일부 구획 또는 칸막 이로 구성되는 바닥 지속형 원리에 의한 폐쇄형 부속품 2.3.3.2 다중 큐비클형 부속품(그림 C.4 참조) 다수의 기계적으로 결합된 칸막이의 조합 2.3.3.3 데스크형 부속품(그림 C.5 참조) 제어, 측정, 신호 등의 장치를 통합하는 수평적 또는 기울어진 제어 기판 또는 그 둘의 조합을 갖는 폐쇄형 부속품 2.3.3.4 박스형 부속품(그림 C.6 참조) 수직 평면에 설치되는 원리로 폐쇄형 부속품 2.3.3.5 다중 박스형 부속품(그림 C.6 참조) 공통 지지 구조를 갖거나 또는 갖지 못하는, 인접면에서 통로 를 통한 두 개의 인접 박스 사이를 통과 하는 전기적 결합과 함께 기계적으로 연결된 박스의 조합 2.3.4 부스바 트렁킹 시스템(버스웨이)(그림 C.7 참조) 각광기 또는 그와 비슷한 외함의 도관에 있는 절연체에 의해 간격이 유지되고 지원되는 부스바로 구성되어 있는 도체 시스템 형태의 형식 시험 부속품 [수정된 IEV 441-12-07] 부속품은 다음과 같은 장치들로 구성될 수 있다: -부스바 트렁킹 장치를 갖고 있거나, 도선의 분기 장치를 가지지 않는다. - 단계의 전치, 확장, 신축성, 공급기 그리고 어댑터 장치 - 도선의 분기 장치 비 고 "부스바"라는 용어는 기하학적인 모양, 크기, 그리고 도체의 넓이를 전제 조건으로 하지는 않는다. 2.4 부속품의 구조적 부분 2.4.1 지원 구조(그림 C.1 참조) 부속품과 외함의 다양한 구성 요소들을 지원하도록 설계된 부속품의 구조를 이루는 부분 2.4.2 설치 구조(그림 C.8 참조) 폐쇄형 부속품을 지원하도록 설계된 부속품의 부분을 형성하지 않는 구조 2.4.3 설 치 판*(그림 C.9 참조) 다양한 구성 요소들을 지원하고 부속품 내의 설치에 적합하도록 설계된 판 주* 장치와 연결된 이러한 구조적 부분들은 자체-포장 부속품으로 구성될 것이다. 2.4.4 설치 구조*(그림 C.9 참조) 다양한 구성 요소들을 지원하고 부속품 내의 설치에 적합하도록 설계된 틀 구조 2.4.5 외 함 어떠한 방향에서 어떤 외부 영향에 대해 보호 장치를 제공하고 최소한 IP2X 의 보호 강도에 직접 접하게 되는 것을 보호하는 부분 5 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
2c9043eb-3142-43eb-8b2b-eacd6d623890 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 2.4.6 덮 개 부속품의 외부 외함 부분 2.4.7 도 어 경첩식으로 움직이거나 미끄러지는 덮개 2.4.8 제거 덮개 외부 외함의 통로를 닫고 그러한 작동과 유지 보수 작업 수행으로 제거될 수 있도록 설계된 덮개 2.4.9 덮 개 판 일반적인 상자에서(2.3.3.4 참조), 외부 외함 개방을 닫는데 쓰이고 나사 또는 그와 비슷한 방법으로 고정될 수 있도록 설계된 부속품의 부분. 장치가 사용된 후에는 보통 제거되지 않는다. 비 고 덮개판은 케이블 입구에 제공될 수 있다. 2.4.10 칸 막 이 다른 구획으로부터 칸막이가 분리되는 외함 부분 2.4.11 경 계 선 접근의 일반적 방향(최소 IP2X) 개폐 소자와 그 유사한 것들로부터의 직접 접촉에서 보 호하기 위해 제공되는 부분 2.4.12 장 애 물 고의 적인 시행은 막지 않지만, 의도하지 않은 직접 접촉은 막는 부분 2.4.13 셔 터 움직일 수 있는 부분 - 제거 가능하거나 회수 가능한 고정된 접촉 부분의 맞물림을 허용하는 위치의 사이 - 고정된 접촉을 차폐하는 구획 또는 포함하는 부분이 되는 위치 [변경된 IEV 441-13-07] 2.4.14 케이블 입구 케이블의 부속품 내의 통과 를 허용하는 통로 부분 비 고 케이블 입구는 동시에 케이블 봉함 끝으로 디자인되어야 한다. 2.4.15 여분의 공간 2.4.15.1 비어있는 공간 구획의 빈 공간 2.4.15.2 장비가 갖춰지지 않은 공간 부스바로만 결합되는 구획의 부분 2.4.15.3 부분적으로 장비가 갖춰진 공간 기능 장치들을 제외하고 완전히 갖추어진 구획의 부분. 설치될 수 있는 기능 장치들은 모듈과 크기의 개수에 의해 정의 된다. 2.4.15.4 완전히 장비가 갖춰진 공간 특정한 사용으로 할당되지 않은 기능 장치들로 완전히 갖추어진 구 획의 부분 2.4.16 폐쇄된 보호 공간 외부 영향과 활성부 접촉에 대한 규정된 보호를 제공하는 전기 성분을 밀폐하 기 위한 부속품 부분 2.4.17 삽입 연동 장치 제거 가능하거나 회수 가능하도록 고정된 부분 안쪽으로 제거 가능하거나 회수 가능한 부분이 삽입되는 것을 막는 장치 2.5 부속품의 설치 조건 2.5.1 실내 설치용 부속품 규격 6.1 에 명시되어 있는 실내 사용을 위한 일반 공급 조건으로 이행된 위치 에서 사용하도록 설계된 부속품 2.5.2 실외 설치용 부속품 규격의 6.1 에 명시되어 있는 실외 사용을 위한 일반 공급 조건 하에서 사용하 도록 설계된 부속품 2.5.3 고정 부속품 예를 들어 바닥이나 벽과 같은 장소에 사용될 수 있도록 설치 장소에 고정되어 설 계된 부속품 2.5.4 이동 가능한 부속품 하나의 사용 장소에서 다른 장소로 손쉽게 이동될 수 있도록 설계된 부속품 2.6 전기 감전에 관한 보호 측정 2.6.1 활 성 부 협약에 의하지만 PEN 도체가 아닌 중성 도체를 포함하는 일반 사용에 전류를 통하도록 도체 또는 전도성 부분[IEV 826-03-01] 비 고 이 문장은 전기 감전의 위험을 반드시 내포하는 것은 아니다. 6 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b60440ca-dab5-46fa-a18d-5575458e70d6 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 2.6.2 노출된 전도성 부분 만질 수 있고 일반적으로 활성화되지 않지만, 결함 조건 하에 사용될 수 있는 전기 장치의 전도성 부분[수정된 IEV 826- 03-02] 2.6.3 보호 도체 (PE) 다음의 부분들의 전기적 연결을 위해 전기 감전에 대한 보호의 몇 가지 측정이 요 구되는 도체 -노출된 전도성 부분 -외부에 발생한 전도성 부분 -주 접지 단자 - 접지 전극 -근원 또는 인공적 중성의 접지 지점[IEV 826-04-05] 2.6.4 중성 도체(N) 시스템의 중성 지점과 연결되고 전기 에너지의 변환에 기여 가능한 도체[IEV 826 -01-03] 2.6.5 PEN 도체 보호 도체와 중성 도체의 기능을 합한 접지된 도체[변경된 IEV 826- 04-06] 2.6.6 누전 전류 절연 실패 또는 절연의 교락으로부터 발생된 전류 2.6.7 접지 누전 전류 지상으로 흐르게 되는 누전 전류 2.6.8 직접 접촉에 대한 보호 활성부와 사람들의 위험한 접촉의 예방 2.6.9 간접 접촉에 대한 보호 노출된 전도성 부분과 사람들의 위험한 접촉의 예방 2.7 부속품 내의 통로 2.7.1 부속품 내 작동 통로 적합한 작동과 부속품 관리를 위해 작동자에 의해 사용되어야 하는 공간 2.7.2 부속품 내 통로 유지 권한이 있는 자에 의해서만 접근 가능하고 설치된 장비의 사용이 첫째 목적인 장소 2.8 전기적 기능 2.8.1 차 폐 물 다른 도체 또는 장비로부터 나오는 특유의 전자기적 방사에 의해 야기된 혼선에 대한 도 체 또는 장비의 보호 2.9 절연 협조 2.9.1 공간 거리 전도성 부분들 사이에서 섬유가 가장 짧은 방법으로 늘어진 두 개의 전도성 부분 사이 의 거리[IEC60947-1 의 2.5.46] [수정된 IEV 441-17-31] 2.9.2 절연 거리(기계적 개폐 장치의 극판) 단절을 위해 명시된 안전을 갖는 개방된 접촉 사이의 틈 [IEC60947-1 의 2.5.50][수정된 IEV 441-17-35] 2.9.3 연면 거리 두 개의 전도성 부분 사이의 절연 물질의 표면을 따라 가장 짧은 거리(IEC 60947-1 의 2.5.51)[수정된 IEV 471-01-08] 비 고 절연 물질 두 조각 사이의 접속 부분은 표면의 일부로 생각한다. 2.9.4 작용 전압 개방 회로 조건이나 정상 작동 조건 하에 경미한 과도 전류인, 정격 공급 전압에서 어떠 한 절연을 따라 발생하는(지역적으로) 교류(r.m.s.) 또는 직류 전압의 최고값[IEC60947-1 의 2.5.52] 2.9.5 일시적 과전압 주어진 장소와 비교적 긴 지속 (몇 초)의 상-접지, 상-중성, 또는 상-상 과전압 [IEC 60947-1 의 2.5.53][수정된 IEV 604-03-12] 2.9.6 과도 전류 과전압 이 규격의 의도로 과도 전류 과전압은 다음과 같다[IEC60947-1 의 2.5.54]. 2.9.6.1 개폐 과전압 특정한 개폐 작동 또는 누전에 의한 시스템 위치에서의 과도 전류 과전압[IEC 60947 -1 의 2.5.54.1][수정된 IEV 604-03-29] 2.9.6.2 전광 과전압 특정한 전광 방전에 의한 시스템 위치에서의 과도 전류 과전압 (IEC 60060 및 IEC 60071-1 참조) [IEC60947-1 의 2.5.54.2] 7 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
89d528a4-cbeb-43b1-a4f9-d15d66bc80d4 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 2.9.7 임펄스 내전압 특정한 시험 조건 하에 절연 파괴를 일으키지 않는 지정 형태와 극성의 임펄스 전압의 최고 첨두값[IEC60947-1 의 2.5.55] 2.9.8 상용 주파수 내전압 특정한 시험 조건 하에 절연 파괴를 일으키지 않는 상용 주파수 사인 곡선 전 압의 r.m.s. 값(IEC60947-1 의 2.5.56)[수정된 IEV 604-03-40] 2.9.9 오 염 유전력 또는 표면 저항에 영향을 미치는 이질적인 물질, 고체, 액체 또는 기체(이온화된 기 체)의 상태[IEC60947-1 의 2.5.57] 2.9.10 오염도(환경적 상태의) 전도성이나 검습기 먼지, 이온화된 기체나 소금 및 상대 습도와 검습기의 흡수 또는 유전력과 표면 저항의 감소를 일의 키는 습기 응축을 발생하는 주파수 양에 기초한 보편적인 수 비 고 1. 장치와 구성 요소의 절연 물질 오염 등급은 장치 또는 성분이 위치한 대형 환경과 는 다 르게 드러나는데 그 이유는 흡수 또는 습기 응축을 방지하기 위한 외함 또는 내부 가 열과 같은 수단으로 방지하기 때문이다. 비 고 2. 이 규격의 목적을 위해 오염 등급은 극소 환경의 등급이다[IEC60947-1 의 2.5.59]. 2.9.11 극소 환경(공간 거리 또는 연면 거리의) 고려 중에 있는 공간 거리 또는 연면 거리를 둘러싸고 있는 대기 상태 비 고 연면 거리 또는 공간 거리와 부속품 또는 구성 요소의 환경이 아닌 극소 환경은 절연상의 영향을 결정한다. 극소 환경은 부속품 또는 성분의 환경보다 나을 수도 더 안 좋을 수도 있다. 극소 환경은 기후와 전자기적인 상태, 오염의 발생 등과 같은 절연에 영향을 미치는 요소들을 모두 포함한다[수정된 IEC60947-1 의 2.5.59]. 2.9.12 과전압 범주 (회로나 전기체계 내의) 회로(또는 명목상의 전압과 는 다른 전기 체계 내) 안에서 발 생하는 과도 전류 과전압의 값들을 제한하고(또는 제어하는) 과전압에 영향을 미치는 수단에 의존함을 기 초한 보편적인 수 비 고 전기 체계 내에서, 하나의 과전압 범주로부터 보다 낮은 다른 범주로의 변환은, 과전압 보 호 장치 또는 발산될 수 있는 시리즈-션트 임피던스 배열, 또는 더 낮은 과전압 범주가 요구되는 더 낮은 과도 전류 과전압값인 서지 전류와 연결된 전환 에너지와 같은 계면 요 구 사항에 부합하는 적절한 수단을 통하여 얻어진다[IEC60947-1 의 2.5.60]. 2.9.13 서지 피뢰기 높은 과도 전류 과전압으로부터 전기 기계를 보호하고 지속과 후속 전류의 진폭을 제한하도록 설계된 장치[IEC60947-1 의 2.2.22] [IEV 604-03-51] 2.9.14 절연 협조 예상 과전압과 다른 방면으로는 과전압 방지 장치의 특징을 갖고 예상 극소 환경과 다 른 방면으로는 오염 방지 수단을 갖는 전기 장비 절연 특징의 상호 관계[IEC 60947-1 의 2.5.61] [수정된 IEV 604-03-08] 2.9.15 균등(동일) 자기장 구 간의 간격보다 구의 반지름이 더 큰 두 개의 구와 같은 전극 사이에서 본질적으로 일정한 전압값을 갖는 전기장[IEC60947-1 의 2.5.62] 2.9.16 불균등 (비동일) 자기장 전극 간에 본질적으로 일정한 전압값을 갖지 않는 전기장[IEC 60947-1 의 2.5.63] 2.9.17 추 적 전기 압박과 표면의 전해질 오염의 결합으로 인한 고체 절연 물질의 표면에 생성된 전도 통로의 점진적 형성[IEC60947-1 의 2.5.64] 2.9.18 상대적 추적 목록(CTI) 추적 없이 정의 된 50 방울의 시험액을 견뎌내는 물질의 볼트(volt)로 표현 되는 최대 전압의 수치 비 고 각 시험 전압과 CTI 값은 25 로 나누어 질 수 있어야 한다[IEC60947-1 의 2.5.65]. 2.10 단락 회로 전류 8 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
e8f3104d-8ee7-4da1-8d40-233e8b83deee | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 2.10.1 단락 회로 전류(k)(부속품 회로의) 전기 회로에서 잘못 또는 부정확한 연결에 의한 단락으로부터 생기는 과전류[IEC60947-1 의 2.1.6][변경된 IEV 441-11-07] 2.10.2 예상 단락 회로 전류(cp)(부속품 회로의) 회로의 공급 도체가 부속품의 공급 단자에 가능한 한 가까운 곳에 위치한 대수롭지 않은 임피던스의 도체에 의하여 단락될 때 흐르는 전류 2.10.3 차단 전류 ; 넘치는 전류 개폐 장치 또는 퓨즈의 단선 작업 중에 도달하는 전류의 최대 순간값 [IEV 441-17- 12] 비 고 이 개념은 회로의 예견된 첨두 전압에 다다르지 않은 경우처럼 개폐 장치와 퓨즈가 작동할 특별히 중요한 개념이다. 3. 부속품의 분류 부속품은 다음에 의해 분류된다. - 외부 디자인(2.3 참조) -설치 장소(2.5.1 과 2.5.2 참조) -이동성과 관련된 설치 조건(2.5.3 과 2.5.4 참조) - 보호 등급(7.2.1 참조) - 외함의 유형 -설치의 방법, 예로 고정되거나 제거 가능한 부분(7.6.3 과 7.6.4) -사람의 보호를 위한 측정(7.4 참조) -내부적 분리의 형태(7.7 참조) - 기능 장치의 전기적 연결 유형(7.11 참조) 4. 부속품의 전기적 특징 부속품은 다음과 같은 전기적 특성들에 의해 정의 된다. 4.1 정격 전압 부속품은 다음과 같은 여러 가지 회로의 정격 전압으로 정의 된다. 4.1.1 정격 작동 전압 (부속품 회로의) 부속품 회로의 정격 작동 전압(Us)은 작용을 결정하는 회로의 정격 전류와 결합된 전압값이다. 다상 회로의 경우에는, 상 간의 전압으로 설명된다. 비 고 정격 제어 회로의 표준값은 통합된 장치에 관련된 규격에서 찾을 수 있다. 부속품 제조사는 주회로와 보조 회로의 올바른 기능에 필요한 전압의 제한을 명시해야 한다. 어떤 경우 라도, 관련 IEC 규격에 명시되어 있는 제한대로 일반 부하 조건 하에서 통합 성분의 제어 회로 단자의 전 압이 유지될 수 있는 제한이어야 한다. 4.1.2 정격 절연 전압(U) (부속품 회로의) 부속품 회로의 정격 절연 전압(U)은 유전체의 시험 전압과 연 면 거리를 참조한 전압값이다. 부속품의 모든 회로의 정격 최대 작동 전압은 정격 절연 전압을 초과 해서는 안 된다. 부속품의 모든 회 로의 정격 작동 전압은 일시적으로라도 정격 절연 전압의 110 %를 초과 하지 않을 것이라고 추정된다. 비 고 IT 시스템(IEC 60364-3 참조)으로부터 유도된 단상 회로일 경우에는, 정격 절연 전압이 공 급상 사이의 전압과 최소한 같아야 한다. 4.1.3 정격 임펄스 내전압(Ump)(부속품 회로의) 부속품 회로의 규정된 형태와 극성의 충격 전압의 첨두 값은 명시된 시험 조건 하에 실패 없이 견딜 수 있으며 공간 거리 값과 관련된다. 부속품 회로의 전압을 견디는 정격 충격은 부속품이 삽입된 시스템 내에서 발생하는 과도 전류 과전압 으로 명시된 값과 같거나 커야 한다. 비 고 정격 임펄스 내전압의 우선값은 표 13 에 주어졌다. 9 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c03db6e4-5947-43d0-88f4-300c2c8c4eb8 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 4.2 정격 전류(h)(부속품 회로의) 부속품 회로의 정격 전류는 제조자에 의해 명시되는데, 배열되고 적용 된 부속품 안의 전기 장비 성분의 등급을 고려해야 한다. 이 전류 8.2.1 에 의해 검증 될 때는 7.3(표 2)에 명시되어 있는 제한을 초과 하는 부속품의 여러 가지 부분의 온도 상승 없이 전해져야 한다. 비 고 정격 전류를 결정하는 복잡한 요인들로 인해 기준값이 주어질 수 없다. 4.3 정격 단기 전류(/cw)(부속품 회로의) 부속품 회로의 정격 단기 전류는 8.2.3 에 명시되어 있는 시험 조 건 하에 회로가 파손 없이 수행할 수 있도록 제조된 회로에 해당하는 단기 전류의 r.m.s. 값이다. 제조자에 의해 다르게 명시되지 않는 한 시간은 1 초이다[수정된 IEV 441-17-17]. 교류의 경우, 전류값은 교류 성분의 r.m.s. 값이고 7.5.3 에서 인수 n 이 주어진 r.m.s. 값의 n 배를 초과 하 지 않는 최고 첨두값이 발생한다고 가정한다. 비 고 1. 만약 시간이 1 초 미만이면, 정격 단축 전류와 시간이 명시되어야 한다. 예로 20kA, 0.2 초 비 고 2. 정격 단축 전류는 시험이 정격 작동 전압에서 진행되었을 때 예견된 전류 또는 시험이 저 전압에서 진행되었을 때 실제 전류 중 하나가 될 수 있다. 등급은 만약에 최대 정격 작동 전압에서 시험이 진행되었다면, 규격의 제 2 판에 정의 되어 있는 정격 예견된 단락 회로 전 류와 유사하다. 4.4 정격 첨두 내전류(pk)(부속품 회로의) 부속품 회로의 정격 첨두 내전류는 8.2.3(7.5.3 참조)에 명 시되어 있는 시험 조건 하에 회로가 충분히 견딜 수 있도록 제조한 회로에 해당하는 첨두 전류의 값이다[수정된 IEV 441-17-18]. 4.5 정격 조건부 단락 회로 전류(kc)(부속품 회로의) 부속품 회로의 정격 조건부 단락 전류는 제조자에 의해 명시된 예기된 단락 회로 값이며, 제조자에 의해 명시된 단락 회로 방지 장치에 의해 방지되고, 8.2.3(7.5.2 참조)에 명시된 시험 조건 하에 장치의 작동 시간을 충분히 견딜 수 있다. 명시된 단락 회로 방지 장치의 세부 항목은 제조자에 의해 명시된다. 비 고 1. 교류의 경우, 정격 조건부의 단락 회로 전류는 교류 성분의 r.m.s. 값에 의해 표현된다. 비 고 2. 단락 회로 방지 장치는 부속품의 완전한 부분을 형성하거나 분리된 장치가 된다. 4.6 정격 퓨즈 단락 회로 전류(�)(부속품 회로의) 부속품 회로의 정격 퓨즈 단락 회로 전류는 단락 회로 방지 장치가 IEC60269 에 따른 퓨즈일 때 정격 조건부의 단락 회로 전류가 된다[수정된 IEV 441-17-21] 4.7 정격 변화율 부속품의 정격 변화율 또는 여러 개의 주회로를 갖는 부속품의 부분은 부속품의 모든 주회로 또는 부속품의 선택된 부분의 정격 전류합을 포함하는 모든 주회로의 추정된 전류의 최대합의 비 율이다. 제조자가 정격 변화율을 명시할 때 인수는 8.2.1 과 부합하는 온도 상승 시험에 쓰일 수 있다. 비 고 실제 전류를 고려하는 정보가 없을 시에는, 다음의 보편적인 값들이 사용된다. 표 1 정격 변화율 값 ¦ 주회로의 개수 ¦ 정격 변화율 ¦ ¦ --- ¦ --- ¦ ¦ 2 와 3 ¦ 0.9 ¦ ¦ 4 와 5 ¦ 0.8 ¦ ¦ 6~9 ¦ 0.7 ¦ ¦ 10(그 이상) ¦ 0.6 ¦ 4.8 정격 주파수 부속품의 정격 주파수는 작동 조건과 관련 있는 주파수의 값이다. 만약에 부속품 회로가 다른 주파수 값으로 설계되었다면, 각 회로의 정격 주파수가 주어져야 한다. 10 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
97f1461a-7079-4cd0-ae04-6d407de6215c | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 비 고 주파수는 결합된 성분을 위해 관련된 IEC 규격에 명시된 제한 내여야 한다. 부속품 제조자에 의해 다르게 명시되지 않는한 제한은 정격 주파수의 98 %와 102 %로 가정한다. 5. 부속품에 관한 정보 다음의 정보는 제조자에 의해 주어진다. 5.1 명 판 각 부속품은 하나 또는 그 이상의 튼튼하고 부속품이 설치될 때 보이고 읽기 쉬운 판이 제 공된다. a)와 b) 항목 아래 명시된 정보는 명판 위에 주어진다. 항목 c)~t)의 정보는, 적용 가능할 때 명판이나 제조자의 기술 문서에 주어진다. a) 제조자의 이름 또는 상표 비 고 제조자는 완전한 부속품의 책임을 지는 조직으로 간주한다. b) 유형 지정 또는 식별 번호, 또는 제조자로부터 관련된 정보를 얻을 수 있는 다른 가능한 증명 수단 c) IEC60439-1 d) 전류의 유형(그리고 주파수, 교류의 경우) e) 정격 작동 전압(4.1.1 참조) f) 정격 절연 전압(4.1.2 참조) - 정격 임펄스 내전압, 제조자에 의해 선언된 경우(4.1.3 참조) g) 보조 회로의 정격 전압(적용 가능하다면) h) 작동의 제한(조항 4. 참조) j) 각 회로의 정격 전류(적용 가능하다면 4.2 참조) k) 단락 저항력(7.5.2 참조) I) 보호 등급(7.2.1 참조) m) 사람의 보호를 위한 측정(7.4 참조) n) 내부 사용을 위한 공급 조건, 외부 사용 또는 특별한 사용, 만약 평상시의 공급 조건과 다르다면 6.1 에 주어진다. -오염도, 제조자에 의해 선언된 경우(6.1.2.3 참조) o) 부속품이 설계된 접지 체계의 유형 p) 가급적 높이, 폭(또는 길이), 깊이 순서대로 주어진 치수(그림 C.3 과 C.4 참조) q) 무게 r) 내부 분리 형태(7.7 참조) s) 기능 장치의 전기적 연결 유형(7.11 참조) t) 환경 1 또는 2(7.10.1 참조) 5.2 표 시 부속품 안에는, 개별 회로와 보호 장치를 확인할 수 있어야 한다. 부속품 장비의 항목들이 지정되면, 부속품과 함께 제공되고 IEC 60750 과 일치하는 케이블 도식과 유사 해야 한다. 5.3 설치, 작동 및 유지 보수 방법 제조자는 문서나 목록에 조건을 명시해야 하고, 부속품의 설치, 작동, 보수와 장비가 그 중에 포함되어야 한다. 필요하다면, 부속품의 이송, 설치, 작동에 대한 지침서는 부속품의 적정하고 올바른 설치, 권한, 작동에 대한 특별한 중요성에 대한 측정을 나타내야 한다. 위 언급한 문서가 필요한 곳에서 권장된 크기와 보수의 주파수를 나타내야 한다. 회로 소자가 설치된 기계의 물리적 배열로부터 명확하지 않으면, 적당한 정보가 제공되어야 한다. 예를 11 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
e1039bf5-70c2-4d28-8cfa-16ce06b5eb3b | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 들어 케이블 도식이나 표 6. 공급 조건 6.1 정상 공급 조건 이 규격을 따르는 부속품은 다음의 공급 조건 하에 사용될 것이다. 비 고 만약 이 조건을 위해 설계되지 않은 릴레이와 같은 전기 장비는 적합한 작동을 하기 위해 적 당한 단계를 거쳐야 한다(둘째 문단의 7.6.2.4 참조). 6.1.1 주위 대기 온도 6.1.1.1 내부 설치의 주위 대기 온도 주위 대기 온도는 +40°C 를 넘지 않고 24 시간 동안의 평균은 +35°C 를 넘지 않는다. 주위 대기 온도의 보다 낮은 제한은 -5°C 이다. 6.1.1.2 외부 설치를 위한 주위 대기 온도 주위 대기 온도는 +40°C 를 넘지 않고 24 시간 동안의 평균은 +35°C 를 넘지 않는다. 주위 대기 온도의 보다 낮은 제한은 · 온대 기후에서 -25°C 와 · 북극 지방의 기후에서 -50°C 비 고 북극 지방의 기후에서 부속품 사용은 제조자와 사용자 간의 특별한 합의 를 요구한다. 6.1.2 대기의 조건 6.1.2.1 내부 설치의 대기 조건 공기는 맑고 상대 습도는 최대 온도인 +40°C 의 50%를 넘지 않아야 한다. 보다 높은 상대 습도는 보다 낮은 온도에서 허용되는데 예로, +20°C 의 90% 온도가 변화에 의해 때때로 발생할 수 있는 알맞은 응축에 주의 한다. 6.1.2.2 외부 설치의 대기 조건 상대 습도는 일시적으로 최대 온도 +25°C 의 100 %만큼 높을 수 있다. 6.1.2.3 오 염 도 오염도(2.9.10 참조)는 계획된 부속품의 환경적 조건을 참조한다. 외함 내부의 개폐 장치와 구성 요소에는, 외함의 환경적 조건의 오염 등급이 적용된다. 공간 거리와 연면 거리를 평가하는 목적에는, 다음 극소 환경의 네 가지 오염 등급이 정해진다(다른 오 염 등급에 의하면 공간 거리와 연면 거리는 표 14 와 표 16 에 주어진다.). 오염도 1 : 오염이 없거나 또는 건조하기만 하는 비전도성 오염이 발생한다. 오염도 2 : 일반적으로, 비전도성 오염만 발생한다. 그러나, 때때로 응축에 의한 일시적인 전도가 일어 날 수도 있다. 오염도 3 : 전도성 오염이 발생하거나, 또는 응축에 의해 전도체가 되는 건조하고, 비전도성 오염이 발생 한다. 오염도 4 : 오염은 예를 들면, 전도성 먼지 또는 비나 눈에 의해 발생하는 영속적인 전도체를 생성한다. 산업 적용의 기준 오염 등급 다르게 명시되지 않는 한, 산업 적용을 위한 부속품은 오염도 3 의 환경에 쓰인다. 그러나, 다른 오염 등급을 적용시키는 것은 특별한 적용이나 극소 환경에 달려 있다. 비 고 장비를 위한 극소 환경의 오염도는 외함 내의 설치에 의해 영향을 받는다. 6.1.3 고 도 설치 대지의 고도는 2000m 를 넘지 않는다(6600ft). 비 고 1000 m 이상의 고도에서 전기 장비를 쓰기 위해서는, 유전력과 대기의 냉각 영향을 고려해 야 한다. 이러한 조건 하에 작동시킬 전기 장비는 제조자와 사용자 간의 협의 에 의해 설계되 거나 사용되어야 한다. 6.2 특별 공급 조건 다음의 특별한 공급 조건이 있을 때는, 적용 가능한 특별한 요구 조건을 따르거나 12 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
9b31334e-f3e8-43b7-9a1e-357fc551e979 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 사용자와 제조자 간에 특별한 협의 가 있어야 한다. 만약 예외적인 공급 조건이 있다면, 사용자는 제조자 에게 알려야 한다. 특별 공급 조건은, 예를 들어 6.2.1 온도값, 상대 습도 또는 6.1 에 명시된 내용과 다른 고도 6.2.2 온도 대기압 변화가 있는 곳의 적용은 부속품 내에 예외적인 응축이 급속하게 생기길 것이다. 6.2.3 먼지, 연기, 부식되거나 방사성이 있는 입자, 증기 또는 염류에 의한 심각한 공기 오염 6.2.4 강한 전기장 또는 자기장에 노출 6.2.5 최종 온도, 예를 들어 태양이나 몹시 더운 상태로부터의 방사에 노출 6.2.6 진균류 또는 작은 생물들에 의한 공격 6.2.7 불 또는 폭발 위험이 있는 장소에서의 설치 6.2.8 심각한 진동과 충격에 노출 6.2.9 전류가 전해지는 용량 또는 단선 용량이 영향을 받는 경우, 예를 들어 기계나 벽의 움푹 패인 곳에 장비가 설치되었을 때의 설치 6.2.10 적합한 교정의 고려 사항 - EMC 와는 다른 전도되고 방사된 장애에 대한, 그리고 -7.10.1 에 기술된 내용들과 는 다른 환경에서의 EMC 장애 6.3 운송, 저장, 조립시 조건 6.3.1 만약 운송, 저장, 조립시의 조건이, 예를 들어 6.1 에 정의 된 것과 는 다른 온도와 습기 상태일 때에는 사용자와 제조자 간에 특별한 협의 가 만들어져야 한다. 다르게 명시되어 있지 않는 한, 다음의 온도 범위가 적용된다: 운송과 저장 시에는 -25°C 와 +55°C 사이, 그리고 24 시간을 넘지 않는 짧은 기간과 +70°C 를 넘지 않아야 한다. 작동되지 않고 이러한 최종 온도를 조건으로 요하는 장비는 변경할 수 없는 파손을 당하지 않으며 특별한 조건 하에 정상적으로 작동되어야 한다. 7. 설계와 구조 7.1 기계적 설계 7.1.1 일반 사항 부속품은 기계적, 전기적, 열의 압박과 정상 공급 하에 받을 수 있는 습기의 영향을 견 딜 수 있는 물질로만 설비되어야 한다. 부식에 대한 보호는 알맞은 물질의 사용이나 사용과 유지 보수 조건을 고려하여, 노출된 표면에 상응하 는 보호 코팅 적용으로 안전하게 한다. 도어, 회수 가능한 부분 등의 잠금 장치 도구들을 포함하는 모든 외함 또는 분할 구획은 정상 조건에서 받기 쉬운 압박을 견디기에 충분한 기계적 힘으로 이루어져야 한다. 부속품의 기계 장치와 회로는 작동과 유지를 쉽게 하고 동시에 필요한 안정 등급을 지킬 수 있도록 배열한다. 7.1.2 공간 거리, 연면 거리와 절연 거리 7.1.2.1 공간 거리와 연면 거리 부속품의 일부를 구성하는 기계 장치는 관련 사항의 요구 조건을 따르는 간격을 두고 이 간격은 정상 공급 조건 하에 유지되어야 한다. 부속품과 함께 기계 장치를 배열할 때는, 명시된 연면 거리와 공간 거리 또는 임펄스 내전압이 고려된 관련 공급 조건을 따라야 한다. 노출된 사용 도체와 단자(예를 들면, 부스바와, 기계 장치와 케이블 러그 사이의 연결), 연면 거리와 공 13 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
9fcf39d7-47a3-4c5d-8dbb-67d5b45419c7 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 간 거리 또는 임펄스 내전압은 적어도 직접적으로 관련된 기계 장치를 위해 명시된 내용들을 따라야 한다. 게다가, 단락 회로와 같은 비정상적인 상태는 부스바와 케이블을 제외한 직접적으로 관련된 기계 장치 를 위해 아래에 명시된 것의 연결 사이에 있는 공간 거리 또는 유전력을 영구적으로 줄여서는 안 된다. 8.2.2 참조 이 규격의 8.2.2.6 에 의해 시험된 부속품의 경우에는, 표 14 와 표 16 에 최소값이 주어지며, 7.1.2.3 에는 시험 전압이 주어진다. 7.1.2.2 회수 가능한 부분의 절연 회수 가능한 부분에 기능 장치들이 배치된 경우에 제공된 절연은 최 소한 제조시 허용 오차와 마모에 의한 크기 변화를 고려하여 새로운 조건에서 장비를 갖춘 단서기에 대한 관련 규격 요구 사항에 부합하여야 한다. 7.1.2.3 유전체 특성 회로 또는 부속품의 회로에 대해 정격 임펄스 내전압이 제조자에 의해 선언되었을 때, 7.1.2.3.1~7.1.2.3.7 의 요구 사항을 적용하고 8.2.2.6 과 8.2.2.7 에 명시된 유전체의 검증과 시험을 만 족해야 한다. 다른 경우에 부속품의 회로는 8.2.2.2, 8.2.2.3, 8.2.2.4 와 8.2.2.5 에 명시된 유전체의 시험을 만족해야 한다. 비 고 그러나, 이러한 경우에 절연 협조의 요구 조건은 검증될 수 없음을 생각해야 한다. 충격 전압 등급을 기초로 한 절연 조정 검증 개념이 선호된다. 7.1.2.3.1 일반 사항 다음의 요구 조건들은 IEC 60664-1 의 원리를 바탕으로 하며 설치 내의 조건과 함께 장비의 절연 조정 검증 가능성을 제공한다. 부속품의 회로는 부속서 G 또는 표 13 에 나와 있듯이 대응되는 교류 또는 직류 전압이 적용 가능한 과 전압 범주에 일치하는 정격 임펄스 내전압을 견딜 수 있어야 한다. 절연 또는 회수 가능한 부분에 적합 한 장치의 절연 간격에 걸친 저항 전압은 표 15 에 나와 있다. 비 고 공급 체계의 근소한 전압과 부속품 회로의 정격 임펄스 내전압 사이의 상호 관계는 부 속서 G 에 나와 있다. 주어진 정격 작동 전압의 정격 임펄스 내전압은 부속품이 사용되고 과전압 범주에 적합할 때, 회로 공 급 체계의 근소한 전압과 상호 관련 부속서 G 의 내용보다 낮아서는 안 된다. 7.1.2.3.2 주회로의 임펄스 내전압 a) 접지되려는 활성부로부터의 공간 거리와 극 사이의 공간 거리는 정격 임펄스 내전압에 알맞은 표 13 의 시험 전압을 견뎌야 한다. b) 절연 위치의 회수 가능한 부분의 개방 접촉에 걸친 공간 거리는 정격 임펄스 내전압에 알맞은 표 15 의 시험 전압을 견뎌야 한다. c) a)와 b)의 공간 거리와 관련된 부속품의 고체 절연은 적용 가능한 a)와 b)에 명시된 충격 전압을 견뎌야 한다. 7.1.2.3.3 보조 회로의 임펄스 내전압 a) 과전압 감소의 어떠한 수단 없이 정격 작동 전압의 주회로로부터 직접적으로 작동하는 보조 회로는 7.1.2.3.2 의 a)와 c) 항목의 요구 조건을 따라야 한다. b) 주회로로부터 직접적으로 작동하지 않는 보조 회로는 주회로와 는 다른 과전압 저항 용량을 가질 수 있 다. 공간 거리와 교류 또는 직류 회로와 같은 관련 있는 고체 절연은 부속서 G 와 일치하는 알맞은 전압을 견뎌야 한다. 7.1.2.3.4 공간 거리 7.1.2.3.2 와 7.1.2.3.3 에 의하면, 회로가 시험 전압에 저항할 수 있도록 공간 거리 는 충분해야 한다. 14 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
82c83eb1-e996-4810-b4e9-02b1a9710ac6 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 공간 거리는 적어도 균등의 자기장을 나타내는 B 의 경우에 대해 표 14 에 명시된 값만큼 높아야 한다. 시험은 만약 정격 임펄스 내전압과 오염도와 관련된 공간 거리가 비균등 자기장을 설명하는 A 의 경우, 표 14 에 명시된 값보다 높아야 한다. 공간 거리 측정 방법은 부속서 F 에 주어진다. 7.1.2.3.5 연면 거리 a) 치 수 오염도 1 과 2 의 경우에 연면 거리는 7.1.2.3.4 에 의해 선택된 관련 공간 거리보다 작아서는 안된다. 오염도 3 과 4 의 경우에 연면 거리는 A 의 경우, 7.1.2.3.4 에 허락된 A 경우의 값보다 공간 거리 가 작을 지라도 과전압으로 인한 방전 분열의 위험을 줄이는 공간 거리보다 작아서는 안 된다. 연면 거리 측정 방법은 부속서 F 에 나와 있다. 연면 거리는 6.1.2.3 의 오염도와 일치해야 하며 표 16 에 주어진 정격 절연 (또는 작용) 전압에서 일치 하는 재료군과 도 일치해야 한다. 재료군은 상대적 능력별 지표 (CTI)의 수치 범위에 의해 다음과 같이 분류된다(2.9.18 참조). - 재료군 I 600≤CTI - 재료군 II 400≤CTI<600 - 재료군 IIIa 175≤CTI<400 - 재료군 IIIb 100≤CTI<175 비 고 1. CTI 값은 절연 물질에 쓰이는 IEC 60112 의 A 방법과 일치하여 얻어진 값을 참조한다. 2. 무기성의 절연 물질의 경우에는, 예를 들어 유리 또는 세라믹의 경우 연면 거리가 관련 공간 거리보다 클 필요가 없다. 그러나, 방전 분열의 위험은 고려해야 한다. b) 리브의 사용 리브의 개수와 는 상관없이, 최소 2mm 높이의 리브를 사용함으로써 표 16 의 값의 0.8 까지 연면 거리가 줄어들 수 있다. 리브의 최소 기반은 기계적 요구 사항에 의해 결정된다(F.2 참조). c) 특별 적용 절연 누전의 심각한 결말을 고려할 때, 특정한 적용을 위한 회로는 표 16 의 회로의 측정된 절연 전압보다 높은 절연 전압을 얻기 위해 이용된 표 16 의 영향 요인(거리, 절연 물질, 극소 환경 내 의 오염)을 하나 또는 그 이상 가져야 한다. 7.1.2.3.6 분리 회로 간의 간격 공간 거리, 연면 거리와 분리 회로 간의 고체 절연의 치수에는 가장 높은 전압 등급이 사용되어야 한다(공간 거리와 관련 고체 절연, 연면 거리를 위한 정격 절연 전압). 7.1.3 외부 도체의 단자 7.1.3.1 제조자는 단자가 구리 도체 또는 알루미늄 도체의 연결에 적합한지 또는 두 경우 모두에 적합한 지를 명시해야 한다. 단자는 정격 전류와 기계와 회로가 유지되는 단락력에 상응하는 필요 접촉 압력을 안전하게 하는 도구(나사, 접촉기 등)에 의해 연결된 외부 도체여야 한다. 7.1.3.2 제조자와 사용자 간에 특별 동의 가 없을 시에는, 단자가 도체를 조절할 수 있어야 하고 적합한 정 격 전류에 상응하는 가장 작은 단면적에서 가장 큰 단면적까지의 구리 케이블을 조절할 수 있어야 한다. 알루미늄 도체가 사용될 때에는, 표 A.1 의 C 란에 명시되어 있는 도체의 최대 크기를 제공하는 단자가 일반적 차원으로 적합하다. 최대 크기의 알루미늄 도체 사용이 회로의 정격 전류의 모든 사용을 방지하는 경우에는, 제조자와 사용자 간의 승인된 동의 로 인해, 다음으로 큰 크기의 알루미늄 도체의 연결 도구를 제공할 필요가 있을 것이다. 저전류와 전압(1A 와 50V 교류, 120V 직류보다 작은)을 갖는 전기 회로의 외부 도체 경우 부속품에 연 결되어야 하고 표 A.1 은 적용되지 않는다[표 A.1 의 주(주) 참조]. 7.1.3.3 이용 가능한 전선 간격은 표시된 물질의 외부 도체의 알맞은 연결을 허용해야 하고 다중 자기 코어의 경우에는 자기 코어를 펼치는 것을 허용한다. 15 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
b82dcaab-507d-45c2-b419-b77bd47a2076 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 도체는 표준 수명을 줄이는 압박을 받아서는 안 된다. 7.1.3.4 제조업자와 사용자 사이에 3 상과 중성 회로에 대해 따로 합의 되지 않는다면 중성 도체를 위한 단말기는 구리 도체의 연결이 전류 전달 용량을 갖는 것을 허용한다. - 만약 상 도체의 크기가 10mm2 을 초과 하면 최소 10mm2 의 값으로 상 도체의 전류 전달 용량의 반과 같다. - 만약 후자의 크기가 10mm2 보다 작거나 같으면, 상 도체의 모든 전류 전달 용량과 같다. 비 고 1. 구리 도체를 제외한 도체의 경우에, 위의 단면은 보다 큰 단자를 요하는 같은 전도성의 단면으로 대체되어야 한다. 비 고 2. 중성 도체 내의 전류가 높은 값에 이르게 되는 특정 응용에는, 예를 들어 중성 도체가 상 도체와 같은 전류 전달 용량을 갖는 큰 형광 설치가 필요할 수 있고, 제조자와 사 용자 간에 특별한 협의 가 필요하다. 7.1.3.5 들어오고 나가는 중성, 보호, PEN 도체를 위한 연결 설비가 제공되면, 결합된 상 도체 단자의 근 처에 배열된다. 7.1.3.6 케이블, 덮개판 등의 개방은 케이블이 올바르게 설치되었을 때, 접촉과 보호 등급에 대해 명시된 보호 수치를 얻을 수 있도록 설계되어야 한다. 이것은 제조자에 의해 명시된 대로 적용에 적합한 수단의 선택을 의미한다. 7.1.3.7 단자의 확인 단자의 확인은 IEC 60445 를 따르도록 권장된다. 7.2 외함과 보호 등급 7.2.1 보호 등급 7.2.1.1 사용 부분, 고체 이질적 본체의 진입과 액체와 의 접촉에 대한 모든 부속품에 의해 제공된 보호 등급은 IEC60529 에 의한 IP 지정에 의해 표시된다. 물의 진입에 대한 보호 조건이 없는 실내 부속품의 경우, 다음의 IP 참조가 선호된다: IP00, IP2X, IP3X, IP4X, IP5X. 7.2.1.2 폐쇄된 부속품의 보호 등급은 제조자의 지시 사항에 일치하는 설치를 한 다음 적어도 IP2X 가 되 어야 한다. 7.2.1.3 추가 보호가 없는 실외 부속품의 경우, 두 번째의 특징수는 최소한 3 이 되어야 한다. 비 고 실외 설치의 경우, 추가 보호는 보호 지붕 또는 그와 비슷한 것이 된다. 7.2.1.4 다르게 명시되지 않는 한, 제조자에 의해 표시된 보호 등급은 제조자의 지시와 일치하게 설치될 때(7.1.3.6 역시 참조) 완전한 부속품에 적용되며, 예로 부속품의 개방 설치 표면을 덮는 것이 있다. 제조자는 권한을 가진 사람에 의해 부속품 내부 부분에 접근 가능성을 필요로 하는 조건 하에 있는 직접 접촉, 고체 이질적 본체의 진입과 액체에 대한 보호 등급 역시 명시해야 한다(7.4.6 참조). 이동 가능 하고 회수 가능한 부속품의 경우에는 7.6.4.3 을 참조 7.2.1.5 예를 들어 작동 면에서 부속품 부품의 보호 등급이 주요 부품과 다른 경우에, 제조자는 그 부품의 보호 등급을 분리하여 명시해야 한다. 예 : IP00, 작동 면 IP20 7.2.1.6 PTTA 의 경우, IEC 60529 에 의해 적절한 검증이 이루어지거나, 시험된 조립식 외함이 사용되지 않 는다면 IP 코드는 주어지지 않는다. 7.2.2 대기 습기를 고려한 측정 폭넓은 제한, 적합한 배열(통풍과 내부 가열, 배수 구멍 등)에서 높은 습도와 온도를 변화시키는 장소에 쓰일 목적으로 외부 설치를 위한 부속품과 내부 설치를 위해 폐쇄된 부속품의 경우, 부속품 내에서 유해한 응축을 방지하도록 만들어진다. 그러나, 그와 동시에 명시된 보호 등급은 유지된다(설치된 기계의 경우, 7.6.2.4 참조). 16 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
f71ba999-0415-49e9-9f7b-ba3902355cee | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 7.3 온도 상승 표 2 에 주어진 온도 상승 제한은 35°C 보다 작거나 같은 평균 대기 온도의 경우에 적용 되고 8.2.1 과 일치하도록 검증된 부속품의 경우는 제한을 초과 할 수 없다. 비 고 요소 또는 부품의 온도 상승은 8.2.1.5 와 일치하는 요소 또는 부품의 온도와 부속품 외부의 대기 온도 사이의 차이이다. 표 2 온도 상승 범위 ¦ 부속품의 부품 ¦ 온도 상승 ¦ ¦ --- ¦ --- ¦ ¦ 설치 요소(1) ¦ 각각 성분의 관련된 요구 사항을 따르거나, 제조자 의 지시를 따르면서 부속품 내의 온도를 고려한다. ¦ ¦ 외부 절연 도체의 단자 ¦ 70(2) ¦ ¦ 부스바, 도체, 부스바에 연결된 이동 가능 또는 회 수 가능한 부품의 플러그인 접촉 ¦ 제한된다. - 전도 물질의 기계적 힘으로 - 가능한 인접 장비의 영향으로 - 도체와 접촉하는 절연 물질의 가능한 온도 제한 에 의해 - 기계위에 연결된 도체 온도 영향으로 - 접촉 물질의 플러그 접속식의 특성과 표면 처리에 의해 ¦ ¦ 수동 작동 방법 - 금속 - 절연 물질 ¦ 15() 25() ¦ ¦ 접근 가능한 외부 외함과 덮개: - 금속 표면 - 절연 표면 ¦ 30(4) 40(4) ¦ ¦ 플러그와 소켓 유형 연결의 불연속 배치 ¦ 부품을 형성하는 관련 장비 성분의 제한으로 결정 된다(?). ¦ 주(1) "설치 요소" 용어의 의미는 -보편적인 개폐 장치 및 제어 장치 - 전기적 부분 부속품(예 : 정류기 전교, 인쇄된 회로) - 장비의 부품(예 : 조정기, 안정된 전력 공급 장치, 조작상의 증폭기). (2) 70K 의 온도 상승 제한은 8.2.1 의 보편적 시험을 바탕으로 한 값이다. 설치 조건 하에 사 용되고 시험된 부속품은 시험용으로 채택된 것과 는 다른 연결, 유형, 특성, 성질을 갖고, 단자의 다른 온도 상승이 초래되며 요구되거나 채택된다. 설치된 성분의 단자가 외부 절 연된 도체의 단자이기도 할 때에는, 보다 낮은 온도 상승 제한이 적용된다. (3) 조립이 개방된 후에만 접근 가능한 수동 작동 방법은, 예를 들어 드물게 작동되는 비상 손잡이, 당기는 손잡이는 더 높은 온도 상승을 취하도록 허용된다. (4) 다르게 명시되지 않는 한, 접근 가능하지만 평상시 작동에서는 건드리지 않는 덮개와 외함의 경우에는, 10K 의 온도 상승 제한의 증가가 허용된다. () 일반적으로 관련된 개폐 장치 및 제어 장치와 는 다른 온도 상승 제한을 따르는 장비의 경우에는 굴곡성을 허용한다. 7.4 전기 감전에 대한 보호 다음 요구 사항은 관련된 설명서를 따르는 시스템에 설치된 부속품의 경우에 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 17 | {}
6ea129fe-ed21-4086-b25f-0e5d35015383 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 필요한 보호 기준를 지키기 위함이다. 일반적으로 받아들여진 보호 기준은 IEC 60364-4-41 을 따른다. 부속품에 특별히 중요한 보호 기준은 부속품의 특정한 필요 사항을 고려한 아래의 사항들에 다시 만들 어져 있다. 7.4.1 직접 및 간접 접촉에 대한 보호 7.4.1.1 안전 특별 저전압에 의한 보호 (IEC 60364-4-41 의 411.1 참조) 7.4.2 직접 접촉에 대한 보호(2.6.8 참조) 직접 접촉에 대한 보호는 부속품 자체의 적합한 구조 기준이나 설치 중에 쓰이는 부가 기준에 의해 얻어진다. 이것은 제조자에 의해 제공된 정보를 필요로 한다. 부가 기준이 사용되는 예는, 권한자에게만 접근이 허용된 장소에서 더 이상의 설비가 없는 개방형 부속 품의 설치이다. 아래에 정의 된 하나 또는 그 이상의 보호 기준은 다음의 부속항에 있는 설비된 요구 사항을 고려하여 선택될 수 있다. 보호 기준의 선택은 제조자와 사용자 간의 동의 에 따라 이루어질 수 있다. 비 고 제조자의 목록에 나와 있는 정보는 그러한 동의 를 대신할 수 있다. 7.4.2.1 활성부 절연에 의한 보호 사용 부분은 파괴에 의해서만 제거될 수 있는 절연으로 완전히 감쌀 수 있다. 이 절연은 절연이 사용 가능한 기계적, 전기적, 온도적 압박을 오래 견딜 수 있는 적합한 물질로 이루 어진다. 비 고 예들은 절연과 케이블에 끼워진 전기 성분들이다. 페인트, 광택, 래커와 유사한 제품들은 평상 사용시의 전기 감전에 대한 보호에 알맞은 절연을 제한다고 고려되지 않는다. 7.4.2.2 장벽 또는 외함에 의한 보호 다음의 요구 사항을 따른다. 7.4.2.2.1 모든 외부 표면은 적어도 IP2X 또는 IPXXB 의 직접 접촉에 대한 보호 등급을 따라야 한다. 보 호를 위해 제공되는 기계 장치와 보호되는 사용 부분 사이의 간격은 기계 장치가 절연 물질이 아닌 한, 7.1.2 의 공간 거리와 연면 거리의 명시된 값보다 작아서는 안 된다. 7.4.2.2.2 모든 장벽과 외함은 장소에 단단히 고정되어야 한다. 특성, 크기, 배열을 고려할 때, 충분한 안 전성과 7.4.2.2.1 에 의한 공간 거리를 줄이지 않은 상태에서 생기는 변형, 압박을 견딜 수 있는 내구성을 가져야 한다. 7.4.2.2.3 장벽의 제거, 외함 개방 또는 외함 회수(문, 포장, 뚜껑, 덮개와 그와 유사한 것.) 준비가 필요한 경우에는, 다음 요구 사항 중 하나와 일치해야 한다. a) 제거, 개방 또는 회수는 전건 또는 도구의 사용을 필요로 한다. b) 문이 개방된 후에 비고의 적으로 만져질 수 있는 모든 사용 부분은 문이 열리기 전에 단절되어야 한다. TN-C 시스템 내에, PEN 도체는 절연되거나 개폐되지 않아야 한다. TN-S 시스템에서 중성 도체는 절연되거나 개폐되지 않아야 한다(IEC60364-4-46 참조). 보 기 문과 단절기를 연결시킴으로써 단절기가 개방되어 있을 때만 개방되며 가장 중요한 연결 또는 도구 사용을 제외하고는 단절기를 문이 열린 상태에서 닫을 수는 없다. 만약, 작동의 이유로 부속품이 장비가 사용되고 있는 동안 장비가 접근을 허용하는 장치가 설비되면 연 결은 자동적으로 접속된 문에 복구된다. c) 부속품은 내부 장애물 또는 도어가 개방되었을 때 무심코 만져지지 않도록 셔터 차폐되는 모든 활성 부를 포함하여야 한다. 이 장애물 또는 셔터는 7.4.2.2.1[예외 사항으로는, d)항목 참조]의 요구 사항 과 7.4.2.2.2 를 따른다. 한 위치에 고정되거나 문이 개방된 순간에 끼어 들어가야 한다. 장애물 또는 18 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
932dccb8-647a-434e-b044-0e8f6244b61a | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 셔 터는 전건 또는 도구의 사용 없이는 제거될 수 없다. 경고 라벨을 제공하는 것이 필요할 수 있다. d) 임시 운용 (램프 또는 퓨즈 연결의 대체와 같은), 제거, 전건과 도구의 사용 없이 그리고 스위치를 내린 상태에서의 개방 또는 회수가 필요로 하는 장벽 또는 외함 내부의 모든 부분은 다음의 조건이 만족될 때만 가능하다(7.4.6 참조). - 장애물은 장벽 또는 외함 내부의 뒤에 제공됨으로써, 다른 보호 기준으로 보호하지 않는 사용 부분 과의 비고의 적 접촉을 일으키는 사람으로부터 보호될 수 있다. 그러나 이 장애물은 고의 적으로 장 애물을 손으로 접촉하는 사람으로부터 보호되기 어렵다. 전건 또는 도구의 사용을 제외한 장애물 을 제거하기는 불가능하다. - 안전 특별 저전압의 조건을 만족하는 사용 부분과 전압은 덮개로 씌어질 필요가 없다. 7.4.2.3 장애물에 의한 보호 이 방법은 개방형 부속품에 적용된다(IEC 60364-4-41 의 412.3 참조). 7.4.3 간접 접촉에 대한 보호(2.6.9 참조) 사용자는 부속품의 설치 목적으로 적용되는 보호 기준을 명시 해야 한다. 특히, 간접 접촉에 대한 보호 요구 사항이 완전한 설치를 위해 명시된 경우, 예로 보호 도체의 사용 경우에는 IEC 60364-4-41 을 주의 해야 한다. 7.4.3.1 보호 회로 사용에 의한 보호 부속품 내의 보호 회로는 분리 보호 도체 또는 전도성 구조물로 구 성되거나 둘 모두에 의해 구성된다. 다음의 내용을 제공한다. -부속품 내의 누전 결과 로부터의 보호 -부속품을 통해 공급되는 외부 회로 내의 누전 결과 로부터의 보호 요구 사항은 다음 부속항에 따른다. 7.4.3.1.1 부속품의 노출된 전도 부분(7.4.3.1.5 참조) 사이와 이 부분들과 장치의 보호 회로(7.4.3.1.6 참조) 사이의 전기적 연속성을 지키기 위해 구조상의 예방 조치가 취해진다. PTTA 의 경우, 형식 시험된 배치가 사용되지 않거나, 짧은 회로의 저항력 검증이 8.2.3.1.1 과 8.2.3.1.3 의 일치를 위해 필요하지 않는 한, 별개의 보호 도체가 보호 회로를 위해 사용되며 부스바에 관해서 전자 기력의 효과 가 무시해도 되도록 배치된다. 7.4.3.1.2 위험을 초래하지 않는 부속품의 특정 노출 전도 부분은 - 넓은 표면 위를 건드리거나 손으로 쥐어서 안되기 때문에, - 또는 크기가 작거나(대략 50x50mm) 활동 부분과 의 접촉을 차단하도록 위치해 있기 때문에, 보호 회로에 연결될 필요가 없다. 이는 나사와 리벳과 명판에 해당된다. 또한 크기에는 상관없이 접촉 기의 전자석과 변압기의 자기 코어(보호 도체의 연결을 위한 단말기가 제공되지 않으면)와 배출 장치의 특정 부분 등에도 해당된다. 7.4.3.1.3 수동 작동 방법(손잡이, 바퀴 등)은 - 안전하고 영구적인 방법으로 보호 회로에 연결된 부분들과 전기적으로 연결되거나, -부속품의 다른 전도 부분으로부터 절연시키는 추가적인 절연이 공급된다. 이 절연은 적어도 관련된 장치의 최대 정격 절연 전압에 정격된다. 작동 중 보통 손으로 쥐게되는 수동 작동 방법의 부분은 장치의 최대 정격 절연 전압에 정격된 절연 재 료로 만들어졌거나 감싸지는 것이 바람직하다. 7.4.3.1.4 니스나 에나멜 층으로 감싸진 금속 부분은 일반적으로 이 요구 조건에 따르도록 적절히 절연되 었다고 여겨질 수 없다. 7.4.3.1.5 보호 회로의 연속성은 직접적이든 보호 도체 방법이든 효과 적인 상호 연결로 보증한다. a) 부속품의 부분이 예를 들어 루틴 유지를 위해 외함에서 제거되면, 부속품의 나머지를 위한 보호 회로가 일시적으로 중단되지 않는다. 19 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
43872fe4-8985-4fdd-8cbf-3ae3a4862bb4 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 부속품의 다양한 금속 부분을 조립하기 위해 사용하는 방법은 만약 사전에 이루어진 예방 조치가 영구 적으로 좋은 전도성과 부속품 내에 흐르는 접지 장애 전류를 저항하기에 충분한 전류가 흐르는 용량을 보증할 수 있다면, 보호 회로의 연속성을 확실하게 하기 위해서는 충분하다고 여겨진다. 비 고 유동성의 금속 도관은 보호형 도체로 사용되어서는 안 된다. b) 제거 가능하거나 회수 가능한 부분이 표면들에 표면을 받치는 금속으로 설치되면 이 표면들에 미치는 압력이 충분히 높다는 전제 하에 보호 회로의 연속성을 보증하기에 충분하다고 여겨진다. 영구적으로 좋은 전도성을 보장하기 위해 예방 조치가 취해져야 한다. 회수 가능한 부분의 보호 회로의 연속성은 연결된 위치에서 단절된 위치(절연된 위치)를 포함하는 것까지 전부 유효하게 남아있다. c) 뚜껑, 문, 덮개판 그리고 그와 유사한 제품의 경우 보통의 금속 나사로 쥔 연결과 금속 경첩은 어떠한 전기 기구도 붙어있지 않다는 전제 하에 연속성을 보증하기에 충분하다고 여겨진다. 특별 저전압의 한계를 넘는 전압을 가진 기구가 뚜껑, 문, 덮개판 등에 붙여지면 보호성 회로의 연 속성 을 보증하기 위한 조치가 취해진다. 이 부분들이 기구가 붙은 공급 도선의 최대 단면도에 따르는 단면 적을 가지고 표 3A 와 같은 보호 도체(PE, PEN)에 맞춰질 것을 권한다. 이 목적(미끄러지는 접촉, 부식으로부터 보호된 경첩)을 위해 특별히 디자인된 같은 값의 전기 연결 역시 만족하다고 여겨진다. d) 부속품 내의 보호 회로의 모든 부분들은 부속품의 설치 위치에서 일어날 수 있는 최고 온도와 동적인 압력을 견뎌낼 수 있도록 디자인된다. e) 부속품의 외함이 보호 회로의 부분으로 사용될 때 이 외함의 단면적은 적어도 7.4.3.1.7 에 명시된 최소 단면적과 전기적으로 같은 값이다. f) 연속성이 연결기나 플러그-소켓 장치의 방법으로 중단될 수 있는 곳에 보호 회로는 활동 도체가 일시 중단된 후에만 중단되며 연속성은 활동 도체가 재연결되기 전에 이루어진다. g) 원칙적으로 항목 f) 아래에 언급된 경우를 제외하고 부속품 안의 보호 회로는 연결이 끊긴 장치(스 위치, 연결 끊는 기구 등)를 포함하지 않는다. 보호 도체가 흐르는 방법으로 허용된 유일한 것은 도구 로써 제거할 수 있고 권한자 만이 접근 가능한 링크이다(이 링크는 특정 시험을 위해 필요할 수도 있다.). 7.4.3.1.6 외부 보호 도체를 위한 단말기와 외장은 요구되는 곳에 따로 명시되어 있지 않는 한 드러낸 상 태이고 구리 도체의 연결에 적합하다. 적절한 크기의 개별적인 단말기는 각 회로의 외향성의 보호 도체 (들)를 위해 제공된다. 외함과 알루미늄이나 알루미늄합금의 도체의 경우 전해질 부식의 위험을 특별히 고려한다. 전도성의 구조와 외함 등을 가진 부속품의 경우, 부속품의 노출 전도 부분(보호 회로)과 연결 케이블의 금속 덮개(강철 콘딧, 도선 외장 등) 사이의 전기 연속성을 보증하기 위해 수단이 제공된다. 노 출된 전도 부분과 외부 보호 도체의 연속성을 보증하기 위한 연결 수단은 다른 어떠한 기능도 갖고 있지 않다. 비 고 마멸 저항이 끝나는 부속품의 금속 부분, 특히 선극판에는 가루를 입히는 등의 방법으로 특별 예방 조치가 취해진다. 7.4.3.1.7 외부 도체가 연결될 부속품의 보호 도체(PE, PEN)의 단면적은 다음 방법 중 하나로 결정된다. a) 보호 도체(PE, PEN)의 단면적은 표 3 에 보여진 적당값보다 작지 않다. 만약 표 3 이 PEN- 도체에 해당 된다면 중성 전류가 상 전류의 30 %를 넘지 않는 것으로 본다. 이 표에의 적용이 비표준 크기를 제공한다면 가장 가까운 더 큰 표준 단면적을 갖는 보호성 도체(PE, PEN)가 사용된다. 표 3 보호 도체의 단면적(PE, PEN) 20 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
1f44d360-0557-4c68-8912-3f4c60cd155a | KSCIEC60439-1_2024확인_KR | KS CIEC 60439-1:1999 ¦ 상 도체의 단면적 s mm2 ¦ 상응하는 보호 도체 (PE, PEN)의 최소 단면적 Sp mm2 ¦ ¦ --- ¦ --- ¦ ¦ s ≤ 16 ¦ S ¦ ¦ 16< s ≤ 35 ¦ 16 ¦ ¦ 35< s ≤ 400 ¦ S/2 ¦ ¦ 400 ¦ 200 ¦ ¦ S> 800 ¦ S/4 ¦ 표 3 의 값은 보호 도체(PE, PEN)가 상 도체와 똑같은 금속으로 만들어졌을 때만 유효하다. 그렇지 않 으면 보호 회로(PE, PEN)의 단면적이 표 3 에 적용한 결과 와 똑같은 전도성을 산출하는 방법으로 결정 한다. PEN 도체의 경우, 다음 추가적인 요구 사항이 적용된다. - 최소 단면적은 10mm2Cu 또는 16mm2 Al 이다. - PEN 도체는 부속품 내에서 절연될 필요가 없다. -구조 부분은 PEN 도체와 같이 사용되지 않는다. 단, 구리나 알루미늄으로 만든 설치 레일은 PEN 도체 와 같이 사용된다. - PEN 도체 내의 전류가 높은 값에 도달할 수 있는, 예를 들어 커다란 형광 설치와 같은 특정한 적용의 경우, 제조자와 사용자 간의 특별 동의 의 조건 하에 상 도체와 같거나 더 높은 전류가 흐르는 용량을 갖는 PEN 도체가 필요할 수도 있다. b) 보호 도체(PE, PEN)의 단면적은 부속서 B 에 명시된 방법으로 계산되거나 검사와 같은 다른 방법으로 얻어질 수 있다. 보호 도체(PE, PEN)의 단면을 결정지을 경우, 다음 조건이 동시에 만족되어야 한다. 1) 8.2.4.2 에 따른 검사가 이루어질 때, 장애 루프 임피던스의 값이 보호 장치의 작동에 요구된 조건을 만족한다. 2) 전기 보호 장치의 작동 조건은 이 도체나 그것의 전기 연속성을 해치려는 경향으로 온도 상승을 야 기하는 보호 도체(PE, PEN) 안의 장애 전류의 가능성을 없앨 수 있도록 선택된다. 7.4.3.1.8 전도성 재료로 만들어진 구조 부분, 하부 구조, 외함 등을 포함하는 부속품의 경우, 보호 도체가 주어졌다면 이 부분들로부터 절연될 필요는 없다(예외의 경우 7.4.3.1.9 참조). 7.4.3.1.9 별개의 접지 전극에 연결하는 도체를 포함하는 특정 보호 장치의 도체는 조심스럽게 절연된다. 예를 들어 이는 전압 작동 장애 간파 장치에 해당되며 변압기 중성의 접지 연결에도 해당될 수 있다. 비 고 그러한 장치와 관련된 요구 사항에 따를 때 이뤄져야하는 특별 예방 조치에 주의 를 요 한다. 7.4.3.1.10 장치를 고정시키는 수단으로 보호 회로에 연결을 할 수 없는 장치의 접근하기 쉬운 전도 부 분은 단면적이 표 3A 에 따라 선택된 도체에 의한 보호 결합을 위한 부속품의 보호 회로에 연결된다. 21 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
58648b01-8552-42b1-89df-3b3c2ca7a289 | KSCIEC60439-1_2024확인_KR | KS CIEC 60439-1:1999 표 3A 구리 결합 도체의 단면적 ¦ 정격 작동 전류 Ie A ¦ 결합 도체의 최소 단면적 mm2 ¦ ¦ --- ¦ --- ¦ ¦ Ie ≤ 20 ¦ s* ¦ ¦ 20 < Ie ≤ 25 ¦ 2.5 ¦ ¦ 25< Ie ≤ 32 ¦ 4 ¦ ¦ 32< Ie ≤ 63 ¦ 6 ¦ ¦ 63 < Ie ¦ 10 ¦ 주* S= 상 도체의 단면적(mm2) 7.4.3.2 보호 회로 이외의 측정법에 의한 보호 부속품은 보호 회로를 요구하지 않는 다음 측정법에 의한 간접 연결로부터의 보호를 규정할 수 있다. - 회로의 전기 분리 - 전체 절연 7.4.3.2.1 회로의 전기 분리 (IEC 60364-4-41 의 413.5 참조) 7.4.3.2.2 전체 절연에 의한 보호* 전체 절연으로 간접 연결로부터 보호하기 위해 다음 요구 사항에 따른 다. a) 장치는 절연 물질 안에 완전하게 폐쇄시켜야 한다. 외함은 밖에서 볼 수 있는 기호 �를 운반해야 한다. b) 외함은 일반 또는 특별 작동 조건(6.1 과 6.2 참조)에 따르는 기계적, 전기적, 온도적 압력을 견딜 능력 이 있는 절연 재료로 만들어지며 노화와 화염을 방지한다. c) 외함은 장애 전압이 외함으로부터 나올 가능성이 있는 방법으로 전도 부분에 의해 뚫릴 가능성은 없다. 이는 구조적인 이유로 외함을 통해 전달되어야 하는 작동기 통로와 같은 금속 부분이 최대 정격 절 연 전압의 활동 부분으로부터 외함의 안과 밖에 절연되고 최대 정격 충격이 적용된다면 부속품 내의 모 든 회로의 전압을 견뎌낸다는 뜻이다. 주* IEC 60364-4-41 의 413.2.1.1 에 따라, 이는 클래스 II 장비에 상당한다. 작동기가 금속으로 만들어졌다면(절연 재료로 덮여있든 아니든) 최대 정격 절연 전압으로 정격 된 절연이 주어지며 최대 충격이 적용된다면 부속품 내의 모든 회로의 전압을 견뎌낸다. 작동기가 주로 절연 재료로 만들어졌다면 절연 실패할 만한 금속 부분의 어떤 부분 역시 최대 정격 절연 전압으로 활동 부분에서 절연되며 최대 정격 충격이 적용된다면 부속품 내의 모든 회 로의 전압을 견뎌낸다. d) 조립이 작동할 준비가 되고 공급에 연결되었을 때, 모든 활성부와 노출된 전도 부분 그리고 보호 회 로에 속한 부분들을 건드리지 않는 방법으로 둘러싼다. 외함은 적어도 보호 등급 IP3XD*를 준다. 부속품의 부하면에 연결된 전기 장치로 확장된 보호 도체가 노출된 전도성 부분이 절연된 부속품을 통해 지나갈 것이라면, 외부 보호 도체를 연결하기 위해 필요한 단말기는 제공되며 알맞은 표시로 명 시될 것이다. 외함 안에는 보호 도체와 단말기가 활동 부분과 노출된 전도 부분으로부터 활동 부분이 절연된 방 법과 같은 방법으로 절연된다. e) 부속품 내의 노출된 전도성 부품은 보호 회로에 연결되지 않아야 한다. 다시 말하면 보호 회로의 사용 에 관련된 보호 기준에 포함되지 않아야 한다. 이것은 보호 도체의 연결 단자를 가질 때에도 설비된 22 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
dd7f5cf5-b224-40ae-b902-1ab67349c25d | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 기계 장치에 적용된다. f) 만약 외함의 문과 덮개가 전건 또는 도구의 사용 없이 개방되면, 절연 물질의 장애물은 접근 가능한 사용 부분에 비고의 적 접촉을 방지할 뿐만 아니라, 덮개가 개방된 후에만 접근 가능한 노출된 전도성 부분에도 제공된다. 그러나 이 장애물은 도구의 사용 없이는 제거될 수 없다. 7.4.4 전기 충전의 방전 만약 부속품이 스위치가 꺼진(커패시터 등) 후에도 위험한 전기적 충전을 유지 하는 장비의 항목을 포함한다면, 경고판이 요구된다. 아크 흡광에 쓰이는 것과 같은 작은 커패시터는 릴레이의 늦은 응답으로 위험하다고 간주되지 않는다. 비 고 의도하지 않은 접촉은, 만약 공전으로부터 얻어진 전압이 전력 공급으로부터 5 초 내에 단절 된 후에 직류 120V 이하로 떨어지면 위험하다고 간주되지 않는다. 7.4.5 부속품 내의 작동과 유지 통로(2.7.1 과 2.7.2 참조) 부속품 내의 작동과 유지 통로는 IEC 60364-4 -481 의 요구 조건을 따라야 한다. 비 고 1m 의 제한된 깊이의 부속품 내의 오목한 부분은 통로로 생각하지 않는다. 7.4.6 권한자에 의해 작동에 접근 가능한 요구 사항 권한 있는 사람에 의한 작동이 가능한 경우, 제조 자와 사용자 간 동의 처럼 하나 또는 그 이상의 다음 요구 사항은 제조자와 사용자 사이의 협의 에 따라 수 행되어야 한다. 이 요구 사항들은 7.4 에 명시된 보호 기준과 상호 보완적이어야 한다. 비 고 예를 들어 부속품 또는 그 부품이 전압에 가해진 상태에서 도구의 사용 또는 우선시되는 연동 장치(7.4.2.2.3 참조)에 의해, 권한 있는 사람이 부속품에 대한 접근이 가능할 때, 협 의된 요구 사항은 유효함을 의미한다. 7.4.6.1 점검과 유사 작동 접근에 관련된 요구 사항 부속품은 제조자와 사용자 간의 협의 되고 부속품이 사용되거나 전압이 가해진 상태에서 특정한 실행 방법으로 설계되고 배열된다. 그러한 시행은 - 시각적 점검 · 개폐 장치와 다른 기계 장치 · 릴레이와 릴리스의 조절과 지표 · 도체 연결과 표시 - 릴레이, 릴리스, 전기 장치의 조정과 재조정 - 퓨즈 연결의 대체 - 지시 램프의 대체 - 특정 잘못된 장소에서의 작동, 예를 들어 적합하게 설계되고 절연된 장치로 측정된 전압과 전류 7.4.6.2 유지를 위한 접근과 관련된 요구 사항 인접 기능 장치나 전압이 가해진 그룹과 함께 단절된 기능 장치나 조립의 그룹에 제조자와 사용자 간에 협의 된 것을 유지하기 위해서는 필요한 등급이 정해져야 한다. 제조자와 사용자 간의 협의 를 따르는 선택은 제공 조건, 관리의 빈도, 권한자의 능력, 로컬 설치 규 정, 등과 같은 요인들에 의존한다. 그러한 측정은 분류(7.7 참조)의 적합한 형태의 선택과 다음의 내용을 포함한다. - 실제 기능 장치 또는 근접한 기능 장치 또는 그룹 사이의 충분한 간격. 관리를 위해 제거되는 부품은 가능한 계속 유지되는 잠금 도구를 갖도록 권장된다. - 이웃한 기능 장치 또는 그룹에 의한 직접 접촉을 방지하기 위해 설계되고 배열된 장애물의 사용 - 각 기능 단위 또는 그룹의 칸막이 사용 - 제조자에 의해 규정되거나 명시되는 추가 보호 장비의 삽입 7.4.6.3 전압 하에서 확장하는 동안 접근 용이성에 관한 요구 사항 여전히 전압이 걸려 있는 부속품의 23 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b8656961-4a2a-44a2-8d03-5e4d6a8d6638 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 여분에 추가 기능 단위 또는 그룹으로 부속품의 확장이 허용될 때 제조자와 사용자가 협의 하여 7.4.6.2 에 명시된 조건을 적용한다. 이 조건은 기존 케이블이 전압이 걸려있을 때 추가 외부 케이블의 주입과 연결 에 역시 적용된다. 인입 공급원에 부스바의 확장과 추가 단일체의 연결은 부속품의 설계가 그와 같은 연결을 허용하지 않 는다면 전압 하에서 이루어질 수 없다. 7.5 단락 회로 보호와 단락 회로 저항 강도 비 고 이 시간 동안 이 부속항은 교류 장치에 우선 적용한다. 직류 장치에 관련된 조건은 고려 중이다. 7.5.1 일반 사항 단락 회로 전류가 정격값까지 상승하여 유발되는 열 압력과 동적 압력을 견딜 수 있게 하기 위해서 부속품은 구성된다. 비 고 단락 회로 압력은 전류 제한 장치(유도, 전류 제한 퓨즈 또는 그 밖의 전류 제한 개폐 장 치)를 사용하면 줄일 수도 있다. 부속품은 부속품에 연결되거나 외부에 배치되는 회로 차단기, 퓨즈 또는 조합품과 같은 수단을 이용 하여 단락 회로 전류로부터 보호된다. 비 고 IT 시스템*에서 사용하고자 하는 부속품의 경우 단락 회로 보호 장치는 이중 접지 장애를 해결하기 위해 선간 전압에서 각각의 단극 위에 충분한 차단 능력을 가지고 있어야 한다. 주* IEC 60364-3 참조 부속품을 주문할 때 사용자는 설치할 지정에 단락 회로 조건을 명시한다. 비 고 주요한 물체가 적당한 설계에 의해 아크를 피하거나 지속 시간을 제한한다 하더라도 부속품 내의 아크로 인한 고장의 경우 사람에게 최고로 가능한 보호 등급이 준비되어야만 하는 것이 바람직하다. PTTA 의 경우 8.2.3.1.1~8.2.3.1.3 에 주어진 면제가 적용되지 않는다면 부스바와 같은 형식 시험 배치 를 사용하도록 권한다. 예외적으로 형식 시험 배치의 사용이 불가능한 곳에서는 그와 같은 부분의 단락 회로 저항 강도(8.2.3.2.6 참조)는 유사한 형식 시험 배치로부터 추정하여 검증된다(IEC 60865 와 IEC 61117 참조). 7.5.2 단락 회로 저항 강도에 관한 정보 7.5.2.1 오직 하나의 입력 장치를 갖는 부속품의 경우, 제조자는 다음과 같이 단락 회로 저항 강도를 설명 한다. 7.5.2.1.1 입력 장치에 연결된 단락 회로 보호 장치(SCPD)를 갖는 부속품의 경우, 제조자는 입력 장치의 단자에 예상되는 단락 회로 전류의 최대 허용값을 나타낸다. 이 값은 적당한 정격을 초과 하지 않는다(4.3, 4.4, 4.5, 4.6 참조) 관련되는 역률과 최대 7.5.3 에서 보인 것과 같다. 단락 회로 보호 장치가 퓨즈나 전류 제한 회로 차단기라면, 제조자는 SCPD 의 특성(전류 정격, 차단 능 력, 차단 전류,Pt 등등)을 설명한다. 시간 지연 릴레이를 갖는 회로 차단기가 사용된다면, 제조자는 지시된 예상 단락 회로 전류에 따라 최 대 시간 지연과 전류 세팅을 설명한다. 7.5.2.1.2 단락 회로 보호 장치가 입력 장치에 연결되지 않는 부속품의 경우 제조자는 하나 또는 그 이 상의 다음 방법으로 단락 회로 저항 강도를 나타낸다. a) 연관 시간이 1 초가 아닌 정격 단시간 전류(4.3 참조)와 정격 첨두 내전류(4.4 참조) 비 고 최대 3 초 동안 정격 단시간 전류와 관련 시간 사이의 관계는 첨두값이 정격 첨두 내전류를 초 과하지 않는다면 Pt= 상수라는 수식으로 주어진다. b) 정격 조건부 단락 회로 전류(4.5 참조) 24 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
b4ba7b5c-427c-4ded-a9b1-4ac8141553f0 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 c) 정격 퓨즈 단락 회로 전류(4.6 참조) 항목 b)와 c)의 경우, 제조자는 부속품 보호에 필요한 단락 회로 보호 장치의 특성(전류 정격, 차단 용량, 차단 전류,I2t 등등) 을 나타낸다. 비 고 퓨즈 고리의 교체가 필요할 때 같은 특성을 갖는 퓨즈 고리를 사용하는 것으로 가정한다. 7.5.2.2 동시에 작동하기 어려운 여러 개의 입력 장치를 갖는 부속품의 경우, 단락 회로 저항 강도는 7.5.2.1 에 따라 각각의 입력 장치에 표시할 수 있다. 7.5.2.3 동시에 작동하기 쉬운 여러 개의 입력 장치를 갖는 부속품과, 하나의 입력 장치와 단락 회로 전 류를 유발하기 쉬운 대전력 전동기의 하나 이상의 외부 장치를 갖는 부속품의 경우 각각의 내부 장치, 외 부 장치 그리고 부스바에서의 예상 단락 회로 전류의 값을 결정하기 위한 특별한 협의 가 이루어진다. 7.5.3 첨두 내전류와 단시간 내전류 사이의 관계 전기력 압력을 결정할 때 첨두 내전류의 값은 단시간 전류에 인수 n 을 곱하여 얻는다. 인수 n 과 관련 역률의 표준 값은 표 4 에 주어진다. 표 4 인수 n 의 표준 값 ¦ 단락 회로 전류의 RMS 값 kA ¦ cos ⌀ ¦ n ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ I ≤ 5 ¦ 0.7 ¦ 1.5 ¦ ¦ 15< I ≤ 10 ¦ 0.5 ¦ 1.7 ¦ ¦ 10< I ≤ 20 ¦ 0.3 ¦ 2 ¦ ¦ 20< I ≤ 50 ¦ 0.25 ¦ 2.1 ¦ ¦ 50< I ¦ 0.2 ¦ 2.2 ¦ 비 고 이 표의 값은 대부분 적용한다. 예를 들어 변압기나 발전기의 근접 부분과 같은 특 별한 위치에서 더 낮은 역률이 얻어지고 이에 따라 최대 예상 첨두 전류는 단락 회 로 전류의 r.m.s. 값 대신에 한계값이 된다. 7.5.4 단락 회로 보호 장치의 조정 7.5.4.1 보호 장치의 조정은 제조자와 사용자 사이의 협의 를 필요로 한다. 제조자의 목록에 주어진 정보는 그 협의 를 대신한다. 7.5.4.2 작동 조건이 공급의 최대 연속성을 요구한다면 부속품 내의 단락 회로 보호 장치의 설치나 선택 은 가능한 한 등급을 매겨 외부로 나가는 지선 회로에서 발생한 단락 회로가 다른 외부 지선 회로에 영 향을 주지 않고 보호 시스템의 선택도를 보증하면서 누전된 지선 회로에 설치된 개폐 장치로 제거되도록 한다. 7.5.5 부속품 내의 회로 7.5.5.1 주 회 로 7.5.5.1.1 부스바(노출 또는 절연된)는 내부 단락 회로가 정상 작동 조건 하에서 예상되지 않은 방식으로 배치된다. 다르게 설명되지 않는다면, 이들은 단락 회로 저항 강도(7.5.2 참조)에 관한 정보에 따라 평가되 고 부스바의 공급측 위의 보호 장치(들)에 의해 제한되는 최소의 단락 회로 압력을 견디도록 설계되어 있다. 7.5.5.1.2 도체들이 정상 작동 상태 하에서 상 사이 그리고/또는 상과 접지 사이에 내부 단락 회로가 생길 가능성이 희박하도록 배열된다면(7.5.5.3 참조) 구획 내에 이 장치들에 포함된 구성 요소뿐만이 아니라 주부스바와 기능 장치의 공급측 사이의 도체(배전 부스바를 포함)는 각 장치 내에 단락 회로 보호 장치의 25 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
9dd254e1-8bb5-4ff6-9465-317a849efd75 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 부하쪽에 발생한 감소된 단락 회로 압력을 기초로 하여 평가된다. 이와 같은 도체들은 고체형의 딱딱한 제조에 바람직하다. 7.5.5.2 보조 회로 보조 회로의 설계는 공급 접지 시스템을 고려하고 접지 장애나 사용 부분과 노출된 전도 부분 사이의 장애가 우연한 위험 작동을 유발하지 않도록 보증한다. 일반적으로 보조 회로는 단락 회로의 영향을 받지 않는다. 그러나 만일 작동이 위험을 유발한다면 단락 회로 보호 기기는 주어지지 않는다. 이런 경우에는 단락 회로가 정상 작동 조건(7.5.5.3 참조) 하에서 기 대하지 않은 방식으로 보조 회로의 도체가 배열된다. 7.5.5.3 단락 회로 가능성을 감소시키기 위한 비보호 능동 도체의 선택과 설치 단락 회로 보호 장치에 의해 보호하지 않는 부속품 안의 능동 도체들(7.5.5.1.2 와 7.5.5.2 참조)은 전체 부속품의 전부가 선택되 고 설치되어서 정상 작동 조건 하에서 상 사이 또는 상과 접지 사이에 완전한 단락 회로가 생길 가능성은 희박하다. 도체 유형의 예와 설치 조건은 표 5 에 주어진다. 표 5 도체 선택과 설치 요구 사항 ¦ 도체 유형 ¦ 요구 사항 ¦ ¦ --- ¦ --- ¦ ¦ 기본 절연이 되어 있는 노출 도체와 단일 코어 도체 예를 들면, IEC 60227-3 을 따르는 케이블 ¦ 예를 들어 역전류기를 사용하여 공통 접촉이나 도체 부분의 접촉은 피한다. ¦ ¦ 기본 절연과 도체 작동 온도가 최대 90°C 이상 허 용되는 단일 코어 도체 예를 들면,IEC 60245-3 을 따르는 케이블 또는 IEC 60227-3 에 따르는 내열 PVC 절연 케이블 ¦ 공통 접촉이나 도체 부분의 접촉은 외부에서 인가한 압력이 없는 곳에서 허용된다. 날카로운 모서리의 접촉은 피해야 한다. 기계적 손상의 위험은 없다. 이 도체들은 작동 온도가 70°C 를 초과 하지 않도 록 부하가 걸려야 한다. ¦ ¦ 기본 절연된 도체 예를 들면, IEC 60227-3 을 따르는 케이블 추가 보충 절연된 도체 예를 들면, 주름잡힌 슬리브관으로덮여있거나 플라 스틱 도관 안에서 움직이는 케이블 ¦ 기계적 손상의 위험이 없다면 추가 조건은 없다. ¦ ¦ 매우 높은 기계 강도 물질로 절연된 도체 예를 들면, 3 kV 까지 사용하도록 강화된 외부 덮개가 있는 FTFE 절연물 또는 이중 절연된 도체 IEC 60502 에 따르는 케이블 ¦ 기계적 손상의 위험이 없다면 추가 조건은 없다. ¦ ¦ 하나 이상의 다중 코어로 둘러싸인 케이블 예를 들면, IEC 60245-4 나 IEC 60227-4 에 따르는 케이블 ¦ 기계적 손상의 위험이 없다면 추가 조건은 없다. ¦ 비 고 위의 표와 같이 설치된 노출 또는 절연된 도체는 부하 쪽 위로 3m 이하 길이로 연 결된 단락 회로 보호 장치를 가지고 있다. 7.6 부속품에 설치된 개폐 장치와 구성 요소 7.6.1 개폐 장치와 구성 요소의 선택 부속품 내에 연결된 개폐 장치와 부품을 적절한 IEC 규격을 따른다. 개폐 장치와 부품은 부속품의 외부 구조(개방형 또는 폐쇄형), 정격 전압(정격 절연 전압, 정격 임펄스 저항 전압 등), 정격 전류, 작동 수명, 생성 및 차단 능력, 단락 회로 저항 강도 등에 대해 특별히 적용할 때 적당하다. 단락 회로 저항 강도 그리고/또는 설치 위치에서 발생하기 쉬운 압력을 견디기에 불충분한 차단 능력을 26 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
300a10cd-d81b-4657-acaa-717c8bf22153 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 갖는 개폐 장치와 구성 요소는 예를 들어 퓨즈나 회로 차단기와 같은 전류 제한 보호 장치를 이용하여 보 호된다. 내부의 개폐 장치의 전류 제한 보호 장치를 선택할 때 조정시 적당히 주의 하여 기기의 제조자가 명시한 최대 허용값을 고려한다(7.5.4 참조). 개폐 장치와 구성 요소의 조정, 예를 들면 단락 회로 보호 장치를 가진 전동기 시동 장치의 조정은 적절한 IEC 규격을 따른다. 정격 임펄스 저항 전압이 제조자에 의해 알려진 회로 안의 개폐 장치와 구성 요소는 회로의 정격 임펄 스 저항 전압보다 더 큰 개폐 과전압을 생성하지 않고 회로의 정격 임펄스 저항 전압보다 더 큰 개폐 과 전압을 필요로 하지 않는다. 주어진 회로에서 사용하기 위해 개폐 장치와 구성 요소를 선택할 때 후자의 주안점을 고려해야 한다. 보 기 정격 임펄스 전압 Uimp= 4000 V, 정격 절연 전압 Ui=250V 그리고 1200 V 의 최대 개폐 과전 압(230V 의 정격 작동 전압에서)을 갖는 개폐 장치와 구성 요소는 적당한 과전압 보호 수단 이 사용되는 과전압 범위 I,II, III 심지어 IV 의 회로에 사용된다. 비 고 과전압 범위에 관해서는 2.9.12 와 부속서 G 를 참조하라. 7.6.2 설 치 개폐 장치와 구성 요소는 제조업자의 지시(전기 아크 또는 아크 슈트를 제거하는 동안 관 찰되는 공간 거리, 사용 위치)에 따라 설치된다. 7.6.2.1 접근 용이성 기구, 같은 받침대(설치 판, 설치 틀) 위에 설치된 기능 장치와 외부 도체용 단자는 설치, 배선, 관리 그리고 교체동안 접근을 가능하게 하기 위해 배열된다. 특히, 단자는 바닥에 설치된 부속 품의 밑면 위로 최소 0.2m 에 설치되고 더욱이 케이블이 그것들과 쉽게 연결될 수 있도록 위치한다. 부속품 내에서 작동되어야만 하는 조정 기기와 리셋 기기는 쉽게 접근할 수 있다. 일반적으로 바닥에 설치된 부속품의 경우, 작동자가 읽을 필요가 있는 지시 기기는 부속품의 밑면 위로 2m 이상에 위치해서는 안 된다. 핸들, 누름 버튼 등과 같은 작동 기기는 쉽게 작동되는 높이에 위치해야 한다. 이는 일반적으로 중심선이 부속품의 밑면 위로 2m 이상에 오지 않아야 함을 의미한다. 비 고 1. 비상용 개폐 장치의 작동기는 작동 단계 위의 0.8 m 와 1.6 m 사이의 지대 내에서 접근 이 가능해야 한다. 2. 벽과 바닥에 설치되는 부속품은 위의 접근 용이성 조건과 작동 높이가 만나는 지점의 높이에 설치되도록 권한다. 7.6.2.2 상호 작용 개폐 장치와 구성 요소는 정상 작동시 나타나는 열, 아크, 진동, 에너지장과 같은 상호 작용에 의해 적절한 기능이 손상을 입지 않는 방법으로 부속품 내에 설치되고 배선되어야 한다. 전자 부 속품의 경우, 전력 회로로부터 감시 회로의 분리 또는 칸막이가 필요하다. 퓨즈를 조정하도록 설계되어 있는 외함의 경우, 열 영향에 관해 특별한 관심이 필요하다(7.3 참조). 제 조자는 사용된 퓨즈 고리의 유형과 정격을 설명한다. 7.6.2.3 장 벽 수동 개폐 장치용 장벽은 개폐 아크가 작동자에게 위험을 나타내지 않도록 설계된다. 퓨즈 고리를 교체할 때 위험을 최소화하기 위해 퓨즈의 구조와 위치가 이를 불필요하게 만들지 않는다 면 내부상 장벽은 적용된다. 7.6.2.4 설치 위치에서 존재하는 조건 부속품의 개폐 장치와 구성 요소는 6.1 에서 설명한 부속품의 정상 작동 조건을 기초로 하여 선택된다(7.6.2.2 참조). 적절한 설명에 따라 예를 들어 릴레이, 계량기, 전자 요소 등의 올바른 작동을 위한 최저 온도와 같이 적당한 작동에 필요한 조건은 유지된다는 것을 보증하는 적절한 경고문(가열, 통풍)이 필요한 곳에 주어 진다. 7.6.2.5 냉 각 부속품의 경우 자연 냉각과 강제 냉각이 주어진다. 적당한 냉각을 하기 위해 설치 위치에 27 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 OK 무단 배포를 금합니다. | {}
a64b2ad1-d94b-4fbc-94cf-b525eb442ecf | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 특별한 경고문이 필요하다면 제조자는 필요한 정보를 주도록 한다(예를 들어 열의 낭비를 막거나 스스로 열을 생산하기 쉬운 부분에 관한 공간 거리 표시 필요). 7.6.3 고정 부분 고정 부분(2.2.5 참조)의 경우, 부속품이 움직이지 않을 때 주회로(2.1.2 참조)의 연결은 이루어질 수도 끊어질 수도 있다. 일반적으로 고정 부분의 제거와 설치는 도구 사용을 요한다. 고정 부분의 분리는 완전한 부속품이나 그 부분의 절연을 필요로 한다. 허용되지 않은 작동을 막기 위해 개폐 장치는 하나 이상의 위치에서 안전 수단을 제공받는다. 비 고 어떤 조건 하에서 사용 회로의 작동이 허용된다면 적절한 안전 경고문에 주의 하여야 한다. 7.6.4 제거 가능한 부분과 회수 가능한 부분 7.6.4.1 설 계 제거 가능한 부분과 회수 가능한 부분은 그들의 전기적 설비가 안전하게 분리되거나 이 회로가 작동되는 동안에는 주회로에 연결될 수 있도록 설계된다. 제거와 회수가 가능한 부분에 삽입 연동 장치가 주어진다(2.4.17 참조). 공간 거리와 연면 거리의 최소값(7.1.2.1 참조)은 한 위치에서 다른 위치로 전달되는 동안만이 아니라 다른 위치에서도 따른다. 비 고 1. 이에는 적당한 기구의 사용이 요구된다. 2. 이 작동들이 부하가 걸린 상태에서는 수행되지 않음을 확인하는 것이 필요하다. 제거 가능한 부분은 연결 위치(2.2.8 참조)와 제거 위치(2.2.11 참조)를 가지고 있다. 회수 가능한 부분은 추가적으로 분리 위치(2.2.10 참조)를 가지고 있고 시험 위치(2.2.9 참조) 또는 시 험 상태(2.1.9 참조)를 갖는다. 이 부분은 이 위치에 정확하게 놓인다. 이 위치들은 명확히 인식 가능하다. 회수 가능한 부분의 다른 위치에 대한 전기적 조건에 관해서는 표 6 을 참조하라. 7.6.4.2 회수 가능한 부분의 연동과 잠금 다르게 설명되지 않는다면 회수 가능한 부분은 주회로가 중 단된 후에 기구가 확실히 회수 그리고/또는 재삽입될 수 있는 장치에 고정된다. 허용되지 않은 작동을 막기 위해 회수 가능한 부분에 하나 이상의 위치에서 이들을 보호하는 맹꽁이 자 물쇠나 자물쇠가 주어진다. 7.6.4.3 보호 등급 부속품에 나타난 보호 등급(7.2.1 참조)은 제거 그리고/또는 회수 가능한 부분의 연결 위치(2.2.8 참조)에 정상적으로 적용한다. 제조자는 다른 위치에서와 위치 사이로 이동하는 동안 얻어지는 보호 등급을 나타낸다. 회수 가능한 부분이 있는 부속품은 연결 위치에 적용하는 보호 등급이 시험 위치와 분리 위치 그리고 한 위치에서 다른 위치로 이동하는 동안에 유지된다. 제거 그리고/또는 회수 가능한 부분을 없앤 후에 최초 보호 등급이 유지되지 않는다면, 적당한 보호도를 확인하기 위한 측정을 협의 하에 실시한다. 제조자의 목록에 주어진 정보는 그 협의 를 대신한다. 7.6.4.4 보조 회로의 연결 방법 보조 회로는 도구를 사용하는 것과 상관없이 열릴 수 있도록 설계된다. 회수 가능한 부분의 경우, 보조 회로는 도구를 사용하지 않고 바람직한 연결이 가능하다. 7.6.5 확 인 7.6.5.1 주회로와 보조 회로의 도체 확인 7.6.5.2 에 언급한 경우를 제외하고 연결된 단자 위나 도체 끝 위에 배치, 색깔 또는 기호로 도체를 구별하는 방법과 정도는 제조자에게 책임이 있고 전선 도표와 그림 위의 표시로 협의 한다. 적절한 부분에서는 IEC 60445 와 IEC 60446 에 따르는 확인 방법을 적용한다. 28 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 OK 무단 배포를 금합니다. | {}
07ce6731-5672-4bd0-9ba5-192f1b586dea | KSCIEC60439-1_2024확인_KR | KS CIEC 60439-1:1999 표 6 회수 가능한 부분의 다른 위치에서의 전기 조건 ¦ 회 로 ¦ 연결 방법 ¦ 위 치 ¦ 위 치 ¦ 위 치 ¦ 위 치 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 회 로 ¦ 연결 방법 ¦ 연결된 위치 (2.2.8 참조) ¦ 실험 상태/위치 (2.1.9/2.2.9 참조) ¦ 분리된 위치 (2.2.10 참조) ¦ 제거된 위치 (2.2.11 참조) ¦ ¦ 입력 주회로 ¦ 입력 선 플러그와 소켓 또는 다른 연 결 설비 ¦ ¦ ¦ ¦ ¦ ¦ 출력 주회로 ¦ 출력 선 플러그와 소켓 또는 다른 연 결 설비 ¦ ¦ 또는 () ¦ ○ 1) 또는 ¦ ○ ¦ ¦ 보조 회로 ¦ 플러그와 소켓 또 는 유사 연결 설비 ¦ ¦ ¦ ○ ¦ ○ ¦ ¦ 회수 가능한 부분 안의 회로 조건 ¦ 회수 가능한 부분 안의 회로 조건 ¦ 움직인다. ¦ 움직인다. 작동 실험시 준비 된 보조 회로 ¦ 피드백이 없다면 움직 이지 않는다. ¦ ○ ¦ ¦ 주회로의 출력 조립 단자 의 조건 ¦ 주회로의 출력 조립 단자 의 조건 ¦ 움직인다. ¦ 움직이거나 연결되 지 않는다(주). ¦ 피드백이 없다면 움직 이지 않는다. ¦ 피드백이 없다면 움직 이지 않는다. ¦ ¦ 주회로의 출력 조립 단자 의 조건 ¦ 주회로의 출력 조립 단자 의 조건 ¦ 7.4.4 의 조건은 따른다. ¦ 7.4.4 의 조건은 따른다. ¦ 7.4.4 의 조건은 따른다. ¦ 7.4.4 의 조건은 따른다. ¦ 주(1) 설계에 따라 (2) 비상시 대기 공급원과 같은 다른 공급원으로부터 보급되는 단자에 따라 I = 연결된 ○ = 분리된(절연된) 1 = 열려 있으나 반드시 분리(절연)되지는 않은 비 고 접지 연속성은 7.4.3.1.5 의 항목 b)에 따르고 절연 거리가 이루어질 때까지 유지된다. 7.6.5.2 보호 도체(PE, PEN)와 주회로의 중성 도체(N)의 확인 보호 도체는 모양, 위치, 표시 또는 색으로 쉽게 확인할 수 있다. 색으로 확인하는 방법이 쓰인다면 녹색과 노란색이 틀림없다(쌍을 이루는 색). 보호 도체가 절연된 단일 심 케이블일 때 우선적으로 전 길이에 걸쳐 이 색 판정법이 사용된다. 비 고 녹색/노란색 판정법은 보호 도체에 정확히 보유된다. 주회로의 일부 중성 도체는 모양, 위치, 표시 또는 색으로 쉽게 구별할 수 있어야 한다. 색으로 구별하 는 방법이 쓰인다면 하늘색을 선택하도록 권한다. 외부 보호 도체의 단자는 IEC 60445 에 따라 표시된다. 예로 IEC 60417 의 5019 번 그림 기호 ① 를 참 조하라. 명확히 녹색/노란색으로 구별할 수 있는 내부 보호 도체에 연결될 외부 보호 도체는 이 기호가 필요하지 않다. 7.6.5.3 작동의 방향과 개폐 위치의 표시 작동기의 작동 방향이 요소나 기기의 설치 배열에 의해 지시 되지 않거나 그렇지 않으면 표시로 명확히 구별할 수 없는 곳에서 IEC 60447 에 주어진 작동의 방향이 추 천된다. 7.6.5.4 지시등과 누름 버튼 지시등과 누름 버튼의 색은 IEC 60073 에 주어져 있다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 29 | {}
6750cb44-5545-4e08-82ba-2338ec20b98b | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 7.7 장벽이나 분할에 의한 부속품의 내부 분리 하나 이상의 다음 조건은 분리된 구획이나 둘러싸인 보호 공간에 분할이나 장벽(금속 또는 비금속)을 이용하여 부속품을 나눌 때 얻을 수 있다. -이웃한 기능 장치에 속하는 위험 부분과 의 접촉 예방 보호 등급은 최소 IPXXB 이다. - 이질적인 고체 본체의 부속품의 한 장치부터 이웃 장치까지의 이동에 대한 보호 보호 등급은 최소 IP2X 이다. 제조자가 다르게 설명하지 않는다면 이 두 조건은 적용한다. 비 고 보호 등급 IP2X 는 보호 등급 IPXXB 를 포함한다. 다음의 내용은 장벽이나 분할에 의한 분리의 전형적인 형태이다(예를 들어, 부속서 D 참조). ¦ 주요 표준 ¦ 하위 표준 ¦ 형태 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 분리가 없다. ¦ ¦ 형태 1 ¦ ¦ 기능 장치로부터 부스바의 분리 ¦ 부스바로부터 분리되지 않는 외부 도체용 단자 ¦ 형태 2a ¦ ¦ 기능 장치로부터 부스바의 분리 ¦ 부스바와 분리되는 외부 도체용 단자 ¦ 형태 2b ¦ ¦ 기능 장치로부터 부스바의 분리와 각자로부 터 모든 기능 장치의 분리 각자로부터가 아닌 기능 장치로부터 외부 도 체용 단자의 분리 ¦ 부스바로부터 분리되지 않는 외부 도체용 단자 ¦ 형태 3a ¦ ¦ 기능 장치로부터 부스바의 분리와 각자로부 터 모든 기능 장치의 분리 각자로부터가 아닌 기능 장치로부터 외부 도 체용 단자의 분리 ¦ 부스바와 분리되는 외부 도체용 단자 ¦ 형태 3b ¦ ¦ 기능 장치를 구성하는 부분인 외부 도체용 단 자를 포함하여 기능 장치로부터 모선의 분리 와 서로로부터 모든 기능 장치 분리 ¦ 관련 기능 장치와 동일한 구획을 갖는 외부 도체용 단자 ¦ 형태 4a ¦ ¦ 기능 장치를 구성하는 부분인 외부 도체용 단 자를 포함하여 기능 장치로부터 모선의 분리 와 서로로부터 모든 기능 장치 분리 ¦ 관련 기능 장치와 동일한 구획을 갖지 않고 개별적으로 분리, 봉합 보호된 공간 또는 구획을 갖는 외부 도체용 단자 ¦ 형태 4b ¦ 분리 형태와 더 높은 보호 등급은 제조자와 사용자 사이의 협의 에 따른다. 장벽과 분할의 안정성과 내구성에 관해서는 7.4.2.2.2 를 참조하라. 연결되지 않은 기능 장치 관리를 위한 접근 용이성에 관해서는 7.4.6.2 를 참조하라. 전압이 걸린 상태에서 확장을 할 때의 접근 용이성에 관해서는 7.4.6.3 을 참조하라. 7.8 부속품 내의 전기적 연결 : 장애물과 절연 도체 7.8.1 일반 사항 전류를 전달하는 부분의 연결은 정상적인 온도 상승, 절연 물질의 수명 그리고 정상 작 동시 발생하는 진동의 결과 로 부적절하게 교체하지 않는다. 특히 금속과 유사하지 않은 경우 열 팽창과 전해질 작용의 영향 그리고 도달한 온도에 대한 물질의 내구성의 영향은 고려한다. 전류 전달 부분 사이의 연결은 충분하고 연속적인 접촉 압력을 유지하는 수단으로 성립된다. 7.8.2 부스바와 절연 도체의 크기와 정격 부속품 내에 도체 단면의 선택은 제조자의 책임이다. 전달되어 야 하는 전류에 추가하여 부속품이 받는 기계적 압력, 이 도체가 놓여 있는 방식, 절연 유형 그리고 가능 하다면 연결된 요소의 종류(즉, 전자 요소)에 의해 선택된다. 7.8.3 배 선(7.8.2 참조) 7.8.3.1 절연된 도체는 관련된 회로의 최소 정격 절연 전압(4.1.2 참조)동안 평가된다. 7.8.3.2 두 개의 연결 장치 사이의 케이블은 중간에 접착 또는 납땜 접합이 없다. 가능한 한, 연결은 고정 된 단자에 이루어진다. 7.8.3.3 절연 도체는 다른 전위에서 노출된 움직이는 부분이나 날카로운 모서리에 두지 않고 적당히 지 탱한다. 30 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
a7355c0c-6235-4b60-b208-61c1fb712278 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 7.8.3.4 덮개나 도어 안의 기구와 측정 설비를 작동시키는 공급원은 덮개나 문이 이동하여 도체에 기계적 손상이 발생하지 않도록 설치된다. 7.8.3.5 기구의 용접 연결은 기구 위에 이런 유형의 연결을 규정한 경우만 부속품 내에서 허용된다. 설비가 정상 작동 동안 심한 진동을 받기 쉬운 경우, 용접 케이블이나 전선 연결은 용접된 접합 부위로 부터 단거리 내에 보충 수단을 이용하면 기계적으로 안전하다. 7.8.3.6 예를 들어 준설기와 기중기 작동, 배 갑판 위에서의 작동, 물건을 들어올리는 설비와 기관차의 경 우처럼 정상 작동 동안 심한 진동이 생기는 위치에서는 도체를 지탱시킬 때 주의 해야 한다. 7.8.3.5 에 언 급한 것 이외의 기구에서 용접된 케이블 손잡이 또는 꼬아져 있는 도체의 용접 끝은 심한 진동을 견디지 못한다. 7.8.3.7 일반적으로 단 하나의 도체가 단자에 연결되어야 한다. 한 단자에 두 개 이상의 도체 연결은 단 자가 이 목적으로 설계된 경우에만 허용된다. 7.9 전자 장치 공급 회로의 요구 사항 전자 설비의 적절한 IEC 설명서가 다르게 설명하지 않는다면 다 음 조건은 적용한다. 7.9.1 입력 전압 변화* a) 배터리 전원의 공급 전압 범위는 정격 공급 전압 ±15 %와 같다. 비 고 이 범위는 충전 배터리에 필요한 추가 전압 범위를 포함하지 않는다. b) 입력 직류 전압의 범위는 교류 공급 전압을 정류하여 얻어진다(항목 3. 참조). c) 교류 전원의 공급 전압 범위는 정격 입력 전압 士10 %와 같다. d) 넓은 오차 범위가 필요하다면, 이는 제조자와 사용자 사이의 협의 를 따른다. 주* IEC60146-2 에 따라서 7.9.2 과 전 압* 그림 1 에 공급 과전압이 명시되어 있다. 이 그림은 단 시간 범위 내에 정격 첨두값으로 부터 편차로서 비주기적 과전압에 적용한다. 부속품은 곡선 1 에 나타난 값 미만의 과전압의 경우에 작동 능력이 유지되도록 설계된다. Chart Type: line 10^-3 2 4 6 10^-2 10^-1 2-4 8 item_01 2.0 1.5 1.5 1.5 1.5 1.0 1.5 1.5 U : 정격 절연 전압의 정형파 첨두값 Au : 첨가된 비주기 첨두 전압 t: 시간 0+Au 그림 1 시간 함수로 의 비율 0 과전압이 곡선 1 과 2 사이의 범위 내에 발생한다면 부속품을 안전하게 보호하는 보호 장치의 반응으로 31 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
1fde3c22-6ef0-4d9d-bf5c-dad08855235a | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 작동은 중단되고 첨두값 전압 2U + 1 000 V 까지 작동이 허용된 부속품에 손상을 가하지 않는다. 비 고 1. 1 ms 미만의 일시적인 지속은 검토 중이다. 2. 위에 주어진 것보다 더 높은 과전압은 적당히 측정하여 제한되는 것으로 가정한다. 7.9.3 파 형* 전자 설비를 연결한 부속품에 공급하는 입력 교류 전압의 고조파는 다음 범위로 제한된다. a) 관련 고조파 성분은 10 %를 넘지 않는다. 즉, 관련 기본파 성분이 99.5 %와 같거나 더 크다. b) 고조파 성분은 그림 2 에 주어진 값을 초과 하지 않는다. 비 고 1. 부속품은 연결되지 않는 것으로 가정하고 공급원의 내부 임피던스는 이 임피던스가 상당 한 값이라면 제조자와 사용자 사이의 협의 에 명시되어야 한다. 2. 전자 제어와 감시에도 같은 값이 표시된다. c) 교류 공급 전압의 최고 주기 순간값은 기본파의 첨두값 위로 20% 이상이 되지 않는다. 주* IEC 60146-2 에 따라 Chart Type: line 3 5 7 9 11 13 25 100 item_01 0.05 0.05 0.05 0.05 0.045 0.04 0.03 0.01 n : 고조파 성분의 순서 Un : 고조파 순서 n 의 실효값 Un : 공칭 시스템 전압의 실효값 그림 2 공칭 시스템 전압의 최대 허용 고조파 성분 7.9.4 전압과 주파수의 일시적 변화 다음 조건에서 일시적인 변화가 있을 때 설비는 손상 없이 작동 한다. a) 0.5 초 이하의 주기 동안 정격 전압의 15 %를 초과 하지 않는 전압 강하 b) 정격 주파수의 士1 % 이하의 공급 주파수 편차. 넓은 오차가 필요하다면 제조자와 사용자 사이의 협의 에 따른다. c) 설비에 공급 전압을 중단하는 데 최대로 허용될 수 있는 시간은 제조자가 나타낸다. 7.10 전자기 호환성(EMC) 7.10.1 EMC 환경 특별한 협의 에 따르지 않는다면(6.2.10 참조), 이 규격의 범위에서 벗어난 부속품의 경 우 두 환경 조건은 고려되고 다음과 같이 언급된다. a) 환경 1 b) 환경 2 32 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
e53d86f4-0d8c-4e34-bc49-e2770c3b1446 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 환경 1 은 주거, 상업, 경공업 지역/설치 같은 저전압 공동 회로망과 관련된다. 아크 용접기 같은 상당히 방해가 높은 발생원은 이러한 환경에 포함되지 않는다. 환경 2 는 대중에게 공개되지 않은 저전압 또는 높은 방해 발생원을 포함하는 산업 네트워크/위치/설치와 관련된다. 7.10.2 시험 조건 부속품은 대부분의 경우에 몇 개의 장치와 요소에 임의 적으로 결합하여 연결되고 한 차례만 제조 또는 조립된다. 다음 조건이 만족된다면 EMC 면제나 방출 시험은 최종 부속품에 필요하지 않다. a) 연결된 장치와 요소가 관련 제품이나 일반 EMC 규격에 일치하는 7.10.1 에 명시된 환경으로 설계된다. b) 내부 설치와 배선은 기기와 요소 제조자의 지시에 따라 이루어진다(상호 영향, 케이블 칸막이, 접지 등 에 관한 배열). 다른 모든 경우에 EMC 조건은 8.2.8 에 따라 시험으로 검증되어야 한다. 7.10.3 내 성 7.10.3.1 전자 회로와 연결하지 않는 부속품 전자 회로와 연결하지 않는 부속품은 정상 전자기 교란에 민감하지 않고 내성 시험도 필요하지 않다. 7.10.3.2 전자 회로와 연결한 부속품 부속품에 연결된 전자 회로는 관련 제품이나 일반 EMC 규격의 면 제 조건을 따르고 명시된 EMC 환경에 알맞다. 비 고 간단한 정류 회로는 정상 전자기 교란에 민감하지 않고 따라서 면제 시험이 필요하지 않다. 7.10.4 방 사 7.10.4.1 전자 회로와 연결하지 않은 부속품 전자 회로와 연결하지 않은 부속품은 임의 의 개폐 작동 동 안만 전자기 교란을 발생시킬 수 있다. 그러나 이는 ms 로 측정된 지속 시간과 관련 회로(들)의 정격 임 펄스 저항 전압을 초과 하지 않는 크기의 개폐 과전압으로 제한된다. 주파수, 이 방출의 정도와 결과 는 저전압 설치의 정상 전자기 환경의 부분으로써 검토된다. 그러므로 전자기 방출의 조건은 만족되는 것으로 생각하고 검증은 불필요하다. 7.10.4.2 전자 회로와 연결한 부속품 전자 회로와 연결한 부속품(즉, 개조된 공급원, 고조파 클럭과 마이 크로 프로세서를 연결하는 회로는 연속적인 전자기 교란을 발생시킨다. 전자 회로를 포함하고 있는 개별 장치와 요소들은 관련 제품이나 일반 EMC 규격의 조건 그리고 명시된 EMC 환경을 따른다. 7.11 전기적 연결 기능 장치 유형 설명 부속품이나 부속품 부품 내의 전기적 연결 기능 장치의 유형은 세 개의 문자 암호로 표시할 수 있다. -첫 번째 문자는 주 입력 회로의 전기적 연결 유형을 의미한다. -두 번째 문자는 주 출력 회로의 전기적 연결 유형을 의미한다. -세 번째 문자는 보조 회로의 전기적 연결 유형을 의미한다. 다음 문자들이 사용된다. - 고정 연결은 F(2.2.12.1 참조) - 떼어 낼 수 있는 연결은 D(2.2.12.2 참조) - 회수 가능한 연결은 W(2.2.12.3 참조) 8. 시험 설명 8.1 시험 분류 부속품의 특성을 검증하기 위한 시험은 다음을 포함한다. - 형식 시험(8.1.1 과 8.2 참조) 33 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
30e58bfe-910a-470b-9f8c-0a1f54d7f353 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 - 정규 시험(8.1.2 와 8.3 참조) 요구하는 대로 제조자는 검증을 위한 원칙을 설명한다. 비 고 TTA 와 PTTA 에 수행된 검증과 시험은 표 7 에 목록화되어 있다. 8.1.1 형식 시험(8.2 참조) 형식 시험은 부속품의 주어진 유형에 대해 이 규격에 놓여 있는 조건을 따르 는지 검증하려는 것이다. 형식 시험은 동일하거나 유사한 구조로 제조된 부속품이나 조립 부품의 표본에 수행된다. 이는 제조자의 주도로 수행된다. 형식 시험은 다음을 포함한다. a) 온도 상승 범위의 검증(8.2.1) b) 유전체 특성의 검증(8.2.2) c) 단락 회로 저항 강도의 검증(8.2.3) d) 보호 회로의 효율성 검증(8.2.4) e) 공간 거리와 연면 거리 검증(8.2.5) f) 기계적 작동 검증(8.2.6) g) 보호 등급 검증(8.2.7) 이 시험들은 일부 순서 그리고/또는 같은 유형의 다른 표본 위에서 수행된다. 부속품의 구성 요소를 변경하려면 이러한 변경이 반대로 시험 결과 에 영향을 미칠것 같은 한 새 형식 시험은 수행되어야만 한다. 8.1.2 정규 시험(8.3 참조) 정규 시험은 물질과 기능 장애를 검출하려는 것이다. 이 시험은 조립된 후의 모든 새 부속품과 각각의 전송 장치에 수행된다. 설치 위치에서 다른 정규 시험은 필요하지 않다. 이 구성 요소의 제조자의 제품 외부에 표준화된 요소로 조립되어 있는 부속품은 이 용도로 제조자에 의 해 명시되거나 공급되는 부품과 부속품을 전문적으로 사용하여 부속품을 조립한 회사에 의해 정규 시험 된다. 정규 시험은 다음을 포함한다. a) 배선 검사를 포함한 부속품 검사, 필요하다면 전기적 작동 시험(8.3.1) b) 유전체 시험(8.3.2) c) 보호 측정 기구의 조사와 보호 회로의 전기적 연속성의 조사(8.3.3). 이 시험은 임의 의 순서로 수행된다. 비 고 제조자의 제품에 정규 시험을 수행했다 하더라도 부속품을 설치한 회사는 운송과 설치 후에 그 제품을 검사하여야 한다. 8.1.3 기기의 시험과 부속품에 연결된 자기 포함 요소 형식 시험이나 정규 시험은 7.6.1 에 따라 선택 되고 제조업자의 설명서에 따라 설치되었을 때 부속품에 연결된 기기와 자기 포함 요소에 수행될 필요가 없다. 8.2 형식 시험 8.2.1 온도 상승 한계의 검증 8.2.1.1 일반 사항 온도 상승 시험은 부속품의 다른 부분에 대해 7.3 에 명시한 온도 상승 한계를 초과 하지 않는지 검증하기 위한 것이다. 시험은 설치된 부속품의 기구와 8.2.1.3 에 따라 정격 전류의 값에서 정상적으로 수행된다. 시험은 8.2.1.4 에 따라 동일한 전력이 손실되는 열 저항기를 사용하여 수행한다. 시험 표본에 적당한 경고문이 주어진다면 부속품(8.2.1.2 참조)의 각각의 부분(판, 박스, 외함 등)을 시 34 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
77759213-2682-48a2-b21d-3bbc64c2dbf2 | KSCIEC60439-1_2024확인_KR | KS CIEC 60439-1:1999 험하는 것을 허용한다. 각 회로의 온도 상승 시험은 의도하는 전류 유형과 설계 주파수에서 이루어진다. 사용된 시험 전압은 8.2.1.3 에 따라 결정되는 전류와 동일한 전류가 회로를 통과 하도록 한다. 릴레이, 접촉기, 해제 장치 등의 코일은 정격 전압으로 공급된다. 표 7 TTA 와 PTTA 에 수행된 검증과 시험 목록 ¦ 번호 ¦ 검사할 특성 ¦ 부속항 ¦ TTA ¦ PTTA ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ 온도 상승 한계 ¦ 8.2.1 ¦ 시험에 의한 온도 상승 한계의 검 증(형식 시험) ¦ 시험이나 추측을 통한 온도 상승 한계 의 검증 ¦ ¦ 2 ¦ 유전체 특성 ¦ 8.2.2 ¦ 시험에 의한 유전체 특성의 검증 (형식 시험) ¦ 8.2.2 나 8.3.2 에 따른 시험에 의한 유 전체 특성 검증 또는 8.3.4 에 따른 절연 저항 검증 (9 번과 11 번 참조) ¦ ¦ 3 ¦ 단락 회로 저항 강도 ¦ 8.2.3 ¦ 시험에 의한 단락 회로 저항 강도 의 검증(형식 시험) ¦ 시험이나 유사 형식 시험 배치로부터 추측한 단락 회로 저항 강도의 검증 ¦ ¦ 4 ¦ 보호 회로의 효율성 부속품의 노출된 전도 부 분과 보호 회로 사이의 효율적인 연결 보호 회로의 단락 회로 저항 강도 ¦ 8.2.4 8.2.4.1 8.2.4.2 ¦ 조사나 저항 측정을 통해 부속품 의 노출된 전도 부분과 보호 회로 사이의 효율적인 연결의 검증(형 식 시험) 시험에 의한 보호 회로의 단락 회 로 저항 강도의 검증 ¦ 조사나 저항 측정을 통해 부속품의 노출된 전도 부분과 보호 회로 사이의 효율적인 연결의 검증 시험, 적당한 설계, 보호 도체의 배열에 의한 보호 회로의 단락 회로 저항 강도의 검증(7.4.3.1.1 마지막 단락 참조) ¦ ¦ 5 ¦ 공간 거리와 연면 거리 ¦ 8.2.5 ¦ 공간 거리와 연면 거리의 검증 (형식 시험) ¦ 공간 거리와 연면 거리의 검증 ¦ ¦ 6 ¦ 기계적 작동 ¦ 8.2.6 ¦ 기계적 작동의 검증 (형식 시험) ¦ 기계적 작동의 검증 ¦ ¦ 7 ¦ 보호 등급 ¦ 8.2.7 ¦ 보호 등급의 검증(형식 시험) ¦ 보호 등급의 검증 ¦ ¦ 8 ¦ 배선, 전기적 작동 ¦ 8.3.1 ¦ 배선 검사를 포함한 부속품 검사, 필요하다면 전기 작동 시험(정규 시험) ¦ 배선 검사를 포함한 부속품 검사, 필요 하다면 전기 작동 시험 ¦ ¦ 9 ¦ 절연 ¦ 8.3.2 ¦ 유전체 시험(정규 시험) ¦ 유전체 시험 또는 8.3.4 에 따른 절연 저항 검증(2 번과 11 번 참조) ¦ ¦ 10 ¦ 보호 측정 ¦ 8.3.3 ¦ 보호 측정 기구와 보호 회로의 전 기적 연속성의 검사(정규 시험) ¦ 보호 측정 기구의 검사 ¦ ¦ 11 ¦ 절연 저항 ¦ 8.3.4 ¦ ¦ 8.2.2 또는 8.3.2 에 따른 시험이 이루 어지지 않는다면 절연 저항의 검증 (2 번과 9 번 참조) ¦ 개방형 부속품은 각각의 부품에 실행한 형식 시험 또는 도체의 크기 그리고 기구의 배치가 분명하다면 온도 상승 시험을 따를 필요가 없다. 과도한 온도 상승은 없고, 부속품과 절연 물질의 이웃 부분에 연결된 설비에 손상을 가하지 않는다. PTTA 에 대한 온도 상승 범위의 검증은 어느 쪽이든 이루어진다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. 35 | {}
99706190-21f8-40dc-afa1-7cbc54a0b804 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 -8.2.1 에 따른 시험에 의해, 또는 - 추론에 의해, 예를 들어 IEC60890 에 따라 8.2.1.2 부속품의 배치 부속품은 정상적으로 사용될 때와 같이 제자리에서 모든 덮개를 가지고 배열된다. 각각의 부품이나 구성 장치를 시험할 때 인접한 부품이나 구성 장치는 정상적으로 사용될 때와 같은 온 도 조건을 제시한다. 열 저항은 사용된다. 8.2.1.3 모든 장치에 전류를 사용한 온도 상승 시험 합리적으로 정확한 가능한 최고 온도 상승을 얻기 위해 선택하도록 설계된 부속품의 경우 이 시험은 하나 이상의 각 회로 조합품 위에서 이루어진다. 이 시험 동안 입력 회로는 정격 전류로 부하가 걸려 있고(4.2 참조) 각 출력 회로는 정격 변화 인자를 곱한 정격 전류로 부하가 걸려 있다. 부속품이 퓨즈를 포함하고 있다면 제조자에 의해 명시한 대로 이는 퓨즈 고리를 가진 시험에 적합하다. 이 시험에 사용된 퓨즈 고리의 전력 손실은 시험 보고서에 설명된다. 시험에 사용된 외부 도체의 크기와 배열은 시험 보고서에 설명된다. 시험은 온도 상승이 일정한 값에 도달하는 데 충분한 시간 동안 이루어진다(보통 8 시간을 초과 하지 않 는다.). 실제로 이 조건은 변화가 1K/h 을 초과 하지 않을 때 이루어진다. 비 고 1. 시험을 단축하기 위해 기기가 허락한다면 전류는 이 시험의 첫 부분 동안 증가되고 후 에 명시된 시험 전류로 감소된다. 2. 시험 동안 제어 전자석에 전압이 가해져서 주회로와 제어 전자석 모두 열 평형 상태 에 도달할 때 온도는 측정된다. 3. 모든 경우에 다상 부속품을 시험할 때 단상 교류의 사용은 무시할 만큼 자기장의 영 향이 작다면 허용된다. 이는 400A 초과 전류에 대해 특별히 주의 깊은 검토가 필요하다. 외부 도체와 작동 조건에 관한 세부 정보가 없는 경우 외부 시험 도체의 단면은 다음과 같다. 8.2.1.3.1 400 A 이하의 시험 전류값에 대해 a) 도체는 표 8 에 주어진 것과 같은 단면적을 가진 단심 구리 케이블 또는 절연 전선이다. b) 실행할 수 있는 한, 도체는 자유 공기 안에 있다. c) 단자에서 단자까지의 각각의 일시적 연결의 최소 길이는 - 단면적이 35mm2 이하의 경우 1m - 단면적이 35 mm2 초과 의 경우 2m 이다. 8.2.1.3.2 400 A 초과 800A 미만의 시험 전류 값에 대해 a) 도체는 표 9 에 주어진 단면적을 갖는 단심 PVC 절연 구리 케이블 또는 제조자의 권유에 따라 표 9 에 주어진 동일한 구리 막대이다. b) 케이블 또는 구리 막대는 단자 사이에 적당한 거리 간격을 유지한다. 구리 막대는 검은 매트로 끝손 질한다. 단자당 다수 병렬 케이블은 함께 다발로 묶이고 상호 간에 대략 10mm 공중 간격으로 배열 된다. 단자당 다수 구리 막대는 대략 막대 두께와 같은 거리에 간격을 유지한다. 막대에 지시된 크기가 단자에 알맞지 않거나 이용할 수 없다면 단면적이 거의 동일하고 냉각 표면이 같거나 작은 다 른 막대를 사용해도 좋다. 케이블 또는 구리 막대는 끼워 넣지 않는다. c) 단상 또는 다상 시험의 경우, 시험 공급원에 임시적인 연결의 최소 길이는 2m 이다. 별 점에 연결하는 최소 길이는 1.2m 로 줄어든다. 8.2.1.3.3 800 A 초과 3 150 A 미만의 시험 전류 값에 대해 a) 부속품이 케이블 연결용으로만 설계되지 않는다면 도체는 표 9 에 제시한 크기의 구리 막대이다. 이런 경우에 케이블의 크기와 배열은 제조업자에 의해 명시된다. 36 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
bc6d0667-b015-4caf-9bd0-5dc75bbf28ee | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 표 8 400 A 이하의 시험 전류에 대한 시험 구리 도체 ¦ 시험 전류의 범위(1) ¦ 시험 전류의 범위(1) ¦ 도체 크기(1),() ¦ 도체 크기(1),() ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ A ¦ A ¦ mm2 ¦ AWG/MCM ¦ ¦ 0 ¦ 8 ¦ 1.0 ¦ 18 ¦ ¦ 8 ¦ 12 ¦ 1.5 ¦ 16 ¦ ¦ 12 ¦ 15 ¦ 2.5 ¦ 14 ¦ ¦ 15 ¦ 20 ¦ 2.5 ¦ 12 ¦ ¦ 20 ¦ 25 ¦ 4.0 ¦ 10 ¦ ¦ 25 ¦ 32 ¦ 6.0 ¦ 10 ¦ ¦ 32 ¦ 50 ¦ 10 ¦ 8 ¦ ¦ 50 ¦ 65 ¦ 16 ¦ 6 ¦ ¦ 65 ¦ 85 ¦ 25 ¦ 4 ¦ ¦ 85 ¦ 100 ¦ 35 ¦ 3 ¦ ¦ 100 ¦ 115 ¦ 35 ¦ 2 ¦ ¦ 115 ¦ 130 ¦ 50 ¦ 1 ¦ ¦ 130 ¦ 150 ¦ 50 ¦ 0 ¦ ¦ 150 ¦ 175 ¦ 70 ¦ 00 ¦ ¦ 175 ¦ 200 ¦ 95 ¦ 000 ¦ ¦ 200 ¦ 225 ¦ 95 ¦ 0000 ¦ ¦ 225 ¦ 250 ¦ 120 ¦ 250 ¦ ¦ 250 ¦ 275 ¦ 150 ¦ 300 ¦ ¦ 275 ¦ 300 ¦ 185 ¦ 350 ¦ ¦ 300 ¦ 350 ¦ 185 ¦ 400 ¦ ¦ 350 ¦ 400 ¦ 240 ¦ 500 ¦ 주() 시험 전류값은 첫 행의 첫 번째 값보다 크고 두 번째 값보다 작거나 같다. (2) 시험 편의 상 제조업자의 목록에 따라 설명된 시험 전류에 주어진 것보다 더 작은 도체가 사용된다. (3) 주어진 시험 전류 범위에 명시된 두 도체 중 하나는 사용된다. b) 구리 막대는 대략 단자 사이의 거리에 간격을 유지한다. 구리 막대는 검은 매트로 끝손질한다. 단자 당 다수의 구리 막대는 대략 막대 두께와 같은 거리에 간격을 유지한다. 막대에 지시된 크기 가 단자에 알맞지 않거나 이용할 수 없다면 단면적이 거의 동일하고 냉각 표면이 같거나 작은 다른 막 대를 사용해도 좋다. 구리 막대는 끼워 넣지 않는다. c) 단상 또는 다상 시험의 경우, 시험 공급원에 임시적인 연결의 최소 길이는 3 m 이다. 그러나 연결의 공 급원 끝에 온도 상승은 연결 길이의 중간에서의 온도 상승 아래로 5 K 이하로 규정되고 2 m 로 감소할 수 있다. 별 점에 연결하는 최소 길이는 2m 이다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 37 | {}
4a63d320-c0e3-4f6a-a835-ba663af25c26 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 표 9 시험 전류에 따른 구리 도체의 기준 단면적 ¦ 정격 전류의 값 A ¦ 시험 전류의 값(1) A ¦ 시험 도체 ¦ 시험 도체 ¦ 시험 도체 ¦ 시험 도체 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 정격 전류의 값 A ¦ 시험 전류의 값(1) A ¦ 케이블 ¦ 케이블 ¦ 구리 막대(주) ¦ 구리 막대(주) ¦ ¦ 정격 전류의 값 A ¦ 시험 전류의 값(1) A ¦ 수 량 ¦ 단 면(3) mm2 ¦ 수 량 ¦ 크 기() mm ¦ ¦ 500 ¦ 400~500 ¦ 2 ¦ 150 (16) ¦ 2 ¦ 30x5(15) ¦ ¦ 630 ¦ 500~630 ¦ 2 ¦ 185 (18) ¦ 2 ¦ 40x5(15) ¦ ¦ 800 ¦ 630~800 ¦ 2 ¦ 240 (21) ¦ 2 ¦ 50x5(17) ¦ ¦ 1 000 ¦ 800~1 000 ¦ ¦ ¦ 2 ¦ 60x5(19) ¦ ¦ 1 250 ¦ 1 000~1 250 ¦ ¦ ¦ 2 ¦ 80x5(20) ¦ ¦ 1 600 ¦ 1 250~1 600 ¦ ¦ ¦ 2 ¦ 100x5(23) ¦ ¦ 2000 ¦ 1 600~2000 ¦ ¦ ¦ 3 ¦ 100x5(20) ¦ ¦ 2500 ¦ 2 000~2500 ¦ ¦ ¦ 4 ¦ 100x5(21) ¦ ¦ 3150 ¦ 2500~3150 ¦ ¦ ¦ 3 ¦ 100x10(23) ¦ 주() 전류의 값은 첫 번째 값보다 크고 두 번째 값보다 작거나 같다. (2) 막대는 긴 표면에 수직으로 배열된다. 긴 표면에 수평 배열은 제조자가 명시한다면 사용된다. (3) 괄호 안의 값은 기준으로 주어진 시험 도체의 평가된 온도 상승(켈빈으로)이다. 8.2.1.3.4 3 150 A 초과 시험 전류의 값에 대해 공급원의 유형, 상과 주파수의 수(적용 가능할 경우), 시 험 도체의 단면적 등과 같은 시험의 모든 관련 항목에 대해 제조자와 사용자 사이에 협의 가 이루어진다. 이 정보는 시험 보고서의 부분을 형성한다. 8.2.1.4 동일한 전력을 손실하는 열 저항기를 이용한 온도 상승 시험 비교적 저정격 전류를 갖는 주회 로와 보조 회로를 포함한 폐쇄형 부속품의 일부 유형의 경우, 전력 손실은 같은 양의 열을 생산하고 외함 내의 적당한 위치에 설치된 열 저항기를 이용하여 모의 시험된다. 이 저항기의 리드의 단면은 상당한 열의 양이 외함으로부터 유도되지 않도록 한다. 열 저항기에 관한 이 시험은, 비록 다른 기구에 설치된다하더라도 변화 인자를 고려한 내부 기구의 전 력 손실의 합이 이 시험에 적용된 값을 초과 하지 않는다면 같은 외함을 이용하여 모든 부속품의 적당한 표본에 고려된다. 내부 기구의 온도 상승은 표 2 에 주어진 값을 초과 하지 않는다(7.3 참조). 이 온도 상승은 개방된 공간 에서 측정되고 외함 내부의 온도와 외함 주변의 대기 온도의 차에 의해 증가하는 기구의 온도 상승으로 계산될 수 있다. 8.2.1.5 온도 측정 열전지 또는 온도계는 온도 측정에 사용된다. 권선의 경우, 저항 변화에 의한 온도 측 정 방법이 일반적으로 사용된다. 부속품 내의 공기 온도를 측정하는 경우 여러 측정 장치가 편리한 곳에 배치된다. 열전지 또는 온도계는 공기 전류와 열 방사에 대해 보호된다. 8.2.1.6 주위 온도 부속품으로부터 약 1m 의 거리와 부속품 높이의 약 1/2 지점에서 부속품 주위에 똑같 이 배치되어 있는 최소 두 개의 온도계 또는 열전지를 이용하여 시험 시간의 마지막 15 분 동안 대기 온도 를 측정한다. 온도계 또는 열전지는 대기 전류와 열 방사에 대해 보호된다. 시험 동안 대기 온도가 +10°C 와 +40°C 사이라면 표 2 의 값은 온도 상승의 한계값이다. 시험 동안 대기 온도가 +40°C 를 초과 하거나 +10°C 보다 낮다면 이 규격은 적용하지 않고 제조자와 사 용자 사이에 특별한 협의 가 이루어진다. 38 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
ffc7abb5-3ca0-4419-a412-c3cabb9d39f8 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 8.2.1.7 결 과 시험이 끝나갈 때의 온도 상승은 표 2 에 명시된 값을 초과 하지 않는다. 기구는 부속품 내 의 온도에서 기구에 명시된 전압 범위 내에서 충분히 작동한다. 8.2.2 유전체 특성의 검증 8.2.2.1 일반 사항 이 형식 시험은 절연 강도가 설치에 의해 손상되지 않는다면 관련 설명에 따라 이미 형식 시험된 부속품의 부품 위에 수행될 필요가 없다. 더욱이 이 시험은 PTTA 에서 수행될 필요는 없다(표 7 참조). 부속품이 7.4.3.2.2 의 항목 d)에 따라 노출된 전도 부분으로부터 절연된 보호 도체를 포함하고 있을 때 도체는 분리된 회로로 간주한다. 즉 속해 있는 주회로와 같은 전압으로 시험된다. 시험은 이루어진다. - 제조자가 정격 임펄스 저항 전압 Uimp 의 값을 지시한다면 8.2.2.6.1~8.2.2.6.4 에 따라(4.1.3 참조) -ユ 밖의 경우에 8.2.2.2~8.2.2.5 에 따라 8.2.2.2 절연 물질로 이루어진 외함의 시험 절연 물질로 이루어진 외함의 경우, 개방부와 접합부 위의 외 함 외부에 놓인 금속 박막과 개방부와 접합부 옆에 위치한 외함 내의 상호 연결된 이동, 노출된 전도 부 분 사이에 시험 전압을 인가하여 추가 유전체 시험이 수행된다. 이 추가적인 시험 동안 시험 전압은 표 10 에 나타난 값의 1.5 배와 같다. 비 고 전체 절연에 의해 보호되는 부속품의 외함에 대한 시험 전압은 검토 중이다. 8.2.2.3 절연 물질로 이루어진 외부 작동 핸들 7.4.3.1.3 에 따라 절연 물질로 이루어져 있거나 덮여 있 는 핸들의 경우, 움직이는 부분과 핸들의 전체 표면 주위에 감싼 금속 박막 사이에 표 10 에 나타난 시험 전압의 1.5 배와 같은 시험 전압을 인가하여 유전체 시험은 수행된다. 이 시험 동안 틀은 접지되거나 다른 회로에 연결되어서는 안 된다. 8.2.2.4 시험 전압의 값과 적용 시험 전압은 적용되어야 한다. a) 모든 활성부와 부속품의 상호 연결된 노출 전도 부분 사이에 b) 각 극과 이 시험 동안 부속품의 상호 연결된 노출 전도 부분에 연결된 모든 다른 극 사이에 적용하는 순간에 시험 전압은 이 부속항에 주어진 값의 50%를 초과 하지 않는다. 몇 초 내에 이 부속항 에 명시된 전체 값까지 점차적으로 증가하고 이는 5 초 동안 유지된다. 교류 전력 전원은 누설 전류와 관 계없이 시험 전압을 유지하기 위해 충분한 전력을 가지고 있다. 시험 전압은 실제적으로 정형파이고 45 Hz 와 62 Hz 사이의 주파수를 가진다. 시험 전압의 값은 다음과 같다. 8.2.2.4.1 아래의 8.2.2.4.2 에 포함되지 않은 주회로와 보조 회로의 경우 값은 표 10 에 따른다. 표 10 ¦ 정격 절연 전압 Ui (선간 전압) V ¦ 유전체 시험 전압 교류 실효값 V ¦ ¦ --- ¦ --- ¦ ¦ Ui ≤1560 ¦ 1 000 ¦ ¦ 60< Ui ≤1 300 ¦ 2 000 ¦ ¦ 300< Ui ≤1 690 ¦ 2 500 ¦ ¦ 690 < Ui ≤1 800 ¦ 3 000 ¦ ¦ 800 < Ui ≤1000 ¦ 3 500 ¦ ¦ 1000 < Ui ≤1500* ¦ 3 500 ¦ 주 직류의 경우만 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 39 | {}
591b9361-25ce-4059-aee1-48c8f3dd33ed | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 8.2.2.4.2 주회로로부터 직접 공급이 부적절하여 제조자에 의해 지시되는 보조 회로의 경우, 값은 표 11 에 따른다. 표 11 ¦ 정격 절연 전압 Ui (선간 전압) v ¦ 유전체 시험 전압 교류 실효값 v ¦ ¦ --- ¦ --- ¦ ¦ Ui ≤ 12 ¦ 250 ¦ ¦ 12 ¦ 500 ¦ ¦ Ui ≤ 60 ¦ 최소값이 1500 인 2Ui+1000 ¦ 8.2.2.5 결 과 펑크나 섬락이 없다면 시험은 통과 되는 것으로 간주한다. 8.2.2.6 임펄스 전압 저항 시험 8.2.2.6.1 일반 조건 시험된 부속품은 제조자의 지시 사항과 6.1 에 명시된 대기 조건에 따라 정상 작동 처럼 자신의 받침대 또는 동등한 받침대 위에 완전하게 설치된다. 절연 물질로 된 작동기와 추가 외함 없이 사용된 설비의 전체 비금속 외함은 틀 또는 설치판에 연결된 금속막에 의해 덮여 있다. 포일은 기준 시험 지시물에 닿을 수 있는 모든 표면에 적용된다(IEC 60529 의 시 험 시도 B). 8.2.2.6.2 시험 전압 시험 전압은 7.1.2.3.2 와 7.1.2.3.3 에 명시되어 있다. 제조자의 동의 로 시험은 표 13 에 주어진 전력 주파수 또는 직류 전압을 이용하여 행해진다. 시험 동안 서지 피뢰기의 분리는 서지 피뢰기의 특성을 알고 있다면 허용된다. 그러나, 과전압 방지 장치와 연결된 수단은 임펄스 전압으로 우선 시험된다. 시험 전류의 에너지 용량은 과전압 방지 장치의 에너지 정격을 초과 하지 않는다. 비 고 방지 장치의 정격은 적용할 때 적합해야 한다. 그와 같은 정격은 검토 중이다. a) 1.2/50 us 임펄스 전압은 최소 1 초간 각 극성에 대해 세 번 적용한다. b) 전력 주파수와 직류 전압은 교류의 경우는 세 번의 주기 동안 인가되고 직류의 경우는 각 극성에 10 ms 씩 인가된다. 표 14 의 경우 A 의 값보다 크거나 같은 공간 거리는 부속서 F 에 설명된 방법에 따라 측정하여 검증 된다. 8.2.2.6.3 시험 전압의 적용 시험 전압은 다음과 같이 적용된다. a) 각각의 활성부(주회로에 연결된 제어 및 보조 회로를 포함)와 부속품의 상호 연결된 노출 전도 부분 사이 b) 주회로의 각각의 극점과 다른 극점 사이 c) 정상적으로 주회로에 연결되지 않은 각각의 제어 및 보조 회로와 -주회로 사이 - 다른 회로 사이 - 노출된 전도 부분 사이 - 외함 또는 설치 받침 사이 d) 분리된 위치에서 회수 가능한 부분의 경우 : 절연 틈에 걸쳐 적절하게 공급측과 회수 가능한 부분 사 이, 그리고 공급 단자와 부하 단자의 사이 40 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
e26b8400-0f84-4263-90cb-b3616978a0ae | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 8.2.2.6.4 결 과 시험 동안 우연한 분열 방전은 없다. 비 고 1. 순간 과전압 방지 장치와 같은 목적으로 설계된 의도적인 분열 방전은 예외이다. 2. "분열 방전"이란 용어는 전기적 압력 하에서 절연의 장애에 관련된 현상을 말한다. 이는 전극 사이의 전압을 0 또는 거의 0 으로 줄이면서 시험 중인 절연체는 완전히 방전된다. 3. "섬광"이란 용어는 가스나 액체 유전체 내에 분열 방전이 발생할 때 사용된다. 4. "섬락"이란 용어는 가스나 액체 매질로 된 절연물의 표면 위로 분열 방전이 발생할 때 사용된다. 5. "펑크"란 용어는 분열 방전이 고체 절연체를 통과 하여 발생할 때 사용된다. 6. 고체 유전체 안의 분열 방전은 유전체 강도의 영구적 손실을 만든다. 액체나 가스로 된 절연체에서의 손실은 단지 순간적일 뿐이다. 8.2.2.7 연면 거리의 검증 상 사이, 다른 전압에서의 회로 도체 사이, 그리고 움직이고 노출 전도 부분 사이에서 최단 연면 거리는 측정된다. 물질의 종류와 오염 정도에 관해 측정된 연면 거리는 7.1.2.3.5 의 조건을 따른다. 8.2.3 단락 회로 저항 강도의 검증 8.2.3.1 단락 회로 저항 강도의 검증을 면제받은 부속품의 회로 단락 회로 저항 강도의 검증은 다음의 경우에 필요하지 않다. 8.2.3.1.1 10kA 를 넘지 않는 정격 단시간 전류 또는 정격 조건부 단락 회로 전류를 가진 부속품 8.2.3.1.2 부속품의 입력 회로 단자에서 최대 허용 예상 단락 회로 전류로 17 kA 를 초과 하지 않는 단락 전류를 가진 전류 제한 장치에 의해 보호되는 부속품 8.2.3.1.3 110V 이상의 정격 2 차 전압에서는 10kVA 이하의 정격 전력을 갖고 110V 미만의 정격 2 차 전 압에서는 1.6 kVA 이하의 정격 전력을 갖으며 단락 회로 임피던스가 4% 이상인 변압기에 연결될 부속품 의 보조 회로 8.2.3.1.4 부속품의 조건에 유효한 형식 시험을 이미 끝낸 부속품의 모든 부품(부스바, 부스바 받침대, 부 스바의 연결, 입력과 출력 장치, 개폐 장치 등) 비 고 개폐 장치의 예로 IEC 60947-3 에 따라 정격 조건부 단락 회로 전류를 갖는 장치이거나 IEC 60947-4-1 에 따라 단락 보호 장치로 조정된 전동기 시동 장치를 들 수 있다. 8.2.3.2 단락 회로 저항 강도가 검증된 부속품의 회로 이 부속항 8.2.3.1 에 언급하지 않은 모든 회로에 적용한다. 8.2.3.2.1 시험 배치 부속품 또는 부품은 정상적으로 사용할 때처럼 설치된다. 부스바에 대한 시험을 제 외하고 부속품의 구조 유형에 따라, 나머지 기능 장치가 같은 식으로 구성되고 시험 결과 에 영향을 미칠 수 없다면 단일 기능 장치를 시험하는데 충분하다. 8.2.3.2.2 시험 수행-일반 사항 시험 회로가 최대 전류 정격(정격 전류에 따른)의 퓨즈, 퓨즈 고리에 연 결되어 있거나 필요한 경우 수락할 수 있는 것으로 제조자가 지시한 유형의 퓨즈, 퓨즈 고리에 연결되어 있다면 사용된다. 부속품을 시험할 때 필요한 공급 도체와 단락 회로 연결은 단락 회로를 견디는 데 충분한 강도를 가지 고 있고 추가 압력이 들어오지 않도록 배치된다. 다르게 협의 되지 않는다면, 시험 회로는 부속품의 입력 단자에 연결된다. 3 상 부속품은 3 상 받침에 연결 된다. 모든 단락 회로 저항 정격의 검증시(4.3, 4.4, 4.5, 4.6 참조) 정격 작동 전압의 1.05 배의 공급 전압에서 41 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
7ad8c5cb-b946-4943-ab24-83dff713fe3d | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 예상 단락 회로 전류의 값은 부속품의 입력 공급원에 가능한 가깝게 설치된 무시할 만큼의 임피던스를 가 진 연결에 의해 단락된 부속품에 공급 도체를 사용하는 눈금 측정 오실로그램으로부터 결정된다. 오실로 그램은 부속품 안에 연결된 보호 장치의 작동 순간에 측정할 수 있고 특정 시간 동안 8.2.3.2.4 에 명시된 값에 근사한 전류가 일정하게 흐르는 것을 보여준다. 교류 시험의 경우, 단락 회로 시험 동안 시험 회로의 주파수는 25%의 오차를 조건으로 한 정격 주파수 와 같다. 외함을 포함하여 작동 중인 보호 도체에 연결될 설비의 모든 부분은 다음과 같이 연결된다. a) 접지된 별점이 있고 그에 따라 공급원의 중성점이나 최소 1500 A 의 예상 장애 전류를 허용하는 유도 인공 중성점에 충분히 표시된 3 상 4 선 시스템(IEC60038)에 사용하기 적합한 부속품 b) 3 상 4 선 시스템뿐만 아니라 3 상 3 선 시스템에 사용하기 적합하고 접지에 아크와 같은 아주 작은 상 도체에 표시되는 부속품 비 고 표시와 지시 방법은 검토 중이다. 7.4.3.2.2 에 따르는 부속품을 제외하고 시험 회로는 장애 전류를 검출하는 확실한 장치(즉, 0.8 mm 의 지 름, 50 mm 이상의 길이의 구리 전선의 퓨즈)를 포함하고 있다. 가용성 요소 회로에서 예상 장애 전류는 주 2 와 3 에 설명한 것을 제외하고 1 500 A±10%이다. 필요하다면 그 값으로 전류를 제한하는 저항이 사용 된다. 비 고 1. 지름이 0.8mm 인 구리 전선은 약 반주기 동안 45 Hz 와 67 Hz 사이의 주파수와 1500 A 에서 녹는다(직류의 경우 0.01 초간). 2. 예상 장애 전류는 비고 1.과 같은 용해 시간에 따라 더 작은 지름을 가진 구리 선으로(비 고 4. 참조) 적절한 제품 규격의 요건을 따르는 소형 설비의 경우에 1500A 미만이다. 3. 인공 중성점을 가진 공급원의 경우, 더 낮은 예상 장애 전류는 비고 1.과 같은 용해 시간에 따라 더 작은 지름을 가진 구리선(비고 4. 참조)으로 제조자의 동의 하에 받아들여진다. 4. 가용성 요소 회로에서 예상 장애 전류와 구리 전선의 지름의 관계는 표 12 에 따라야 한다. 표 12 예상 장애 전류와 구리 전선의 지름 사이의 관계 ¦ 구리 전선의 지름 ¦ 가용성 요소 회로에서의 예상 장애 전류 ¦ ¦ --- ¦ --- ¦ ¦ mm ¦ A ¦ ¦ 0.1 ¦ 50 ¦ ¦ 0.2 ¦ 150 ¦ ¦ 0.3 ¦ 300 ¦ ¦ 0.4 ¦ 500 ¦ ¦ 0.5 ¦ 800 ¦ ¦ 0.8 ¦ 1 500 ¦ 8.2.3.2.3 주회로의 시험 부스바가 있는 부속품의 경우, 아래의 항목 a), b) 그리고 d)에 따른 시험을 적 용한다. 부스바가 없는 부속품의 경우, 항목 a)에 따른 시험을 적용한다. 7.5.5.1.2 의 조건이 만족되지 않는 부속품의 경우, 항목 c)에 따른 시험을 추가적으로 적용한다. a) 출력 회로가 적당한 시험을 미리 따르지 않는 요소를 포함하는 경우 다음 시험이 적용될 것이다. 출력 회로를 시험할 때 관련 출력 단자는 잠겨 있는 단락 회로 연결을 제공받는다. 출력 회로의 보 42 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
bbf0f807-8438-47f8-997a-d0181b6ec76c | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 호 장치가 회로 차단기일 때 시험 회로는 IEC 60947-1 의 8.3.4.1.2 b)에 따라 단락 회로 전류를 조정 하기 위해 사용된 반응 장치와 병렬로 연결된 분로 저항을 포함한다. 630A 이하의 정격 전류를 갖는 회로 차단기의 경우, 기존의 열 전류(IEC 60947-1, 표 9 와 10)에 따 르는 단면적을 갖는 0.75m 길이의 케이블은 시험 회로에 포함된다. 개폐 장치는 정상적으로 작동할 때 사용되는 방식으로 닫히고 닫힘을 유지한다. 시험 전압은 한번만 적용하고 충분히 긴 시간 동안, 어떤 경우에는 10 주기(시험 전압 지속 시간) 이상 출력 장치에서 단락 회로 보호 장치가 장애를 없애도록 작동한다. b) 주요 부스바를 포함하는 부속품은 주요 부스바와 접합 부분을 포함한 입력 회로의 단락 회로 저항 강 도를 증명하기 위한 추가 시험을 따른다. 단락 회로가 만들어지는 점은 공급원에 가장 가까운 점으로 부터 2±0.40 m 이다. 정격 단시간 전류(4.3 참조)와 정격 첨두값 내전류(4.4 참조)의 검증할 때 시험 전 류가 정격값[8.2.3.2.4 의 항목 b) 참조]을 제공하는 낮은 전압에서 시험이 수행된다면 이 거리는 증가 된다. 시험된 부스바의 길이가 1.6 m 미만이고 부속품이 확장되지 않게 부속품이 설계되는 경우 부스바 의 전체 길이는 부스바의 끝에 단락 회로를 만들어서 시험된다. 부스바의 한 세트가 다른 구획(단면, 인접한 부스바 사이의 거리, 미터당 받침대의 종류와 개수에 관한)으로 구성되어 있다면 위의 조건이 충족되는 한 각 구획은 개별적으로 또는 일괄적으로 시험된다. c) 단락 회로는 출력 장치의 부스바 측 단자에 가능한 실제적으로 가깝게 하나의 출력 장치에 부스바를 연결하는 도체 위를 잠궈 얻는다. 단락 회로 전류의 값은 주요 선의 전류값과 같다. d) 중성 선이 있다면 접합 부분을 포함하여 가장 가까운 상 부스바에 관한 단락 회로 저항 강도를 검증 하기 위한 시험을 따른다. 이러한 상 부스바에 중성 선을 연결하는 경우 8.2.3.2.3 의 항목 b)의 조건 을 적용한다. 제조자와 사용자 사이에 협의 되지 않는다면 중성 선에 흐르는 시험 전류값은 3 상 시험 동안 상 전류의 60 %이다. 8.2.3.2.4 단락 회로 전류의 값과 지속 시간 a) 단락 회로 보호 장치에 의해 보호되는 부속품의 경우, 이 장치가 입력 회로에 있던지 없던지 시험 전압 은 충분히 긴 시간 동안, 어떤 경우에는 10 주기 이상 단락 회로 보호 장치가 장애를 없애도록 작동 한다. b) 입력 장치에 단락 회로 보호 장치와 연결되지 않은 부속품(7.5.2.1.2 참조) 모든 단락 회로 저항 정격에 대해 동적 및 열적 압력은 명시된 보호 장치의 공급 측에서 정격 단시간 전류와 같은 예상 전류, 정격 첨두값 내전류, 정격 조건부 단락 회로 전류 또는 제조자에 의해 지시된 정격 퓨즈 단락 회로 전류로 검증된다. 최대 작동 전압에서 단시간 또는 첨두값 저항 시험을 하기 어려운 시험 장소에서는 8.2.3.2.3 의 항목 b),c) 그리고 d)에 따른 시험은 더 낮은 전압에서 이루어지고 이런 경우 실제 시험 전류는 정격 단시간 또는 정격 첨두값 내전류와 같다. 이는 시험 보고서에 명시되어 있다. 그러나 순간의 접촉 분리가 시험 동안 보호 장치 내에서 발생한다면 시험은 최대 작동 전압에서 반복된다. 단시간 및 첨두값 전류 저항 시험의 경우, 시험 동안 작동하기 쉬운 과부하 해제 장치는 작용하지 않게 된다. 모든 시험은 오차 범위 ±25%를 갖는 설비의 정격 주파수와 표 4 에 따르는 단락 회로 전류에 적절한 역률로 시험된다. 눈금을 측정하는 동안의 전류값은 모든 상의 교류 성분의 실효값의 평균값이다. 최대 작동 전압에서 시험할 때 측정된 전류는 실제 시험 전류이다. 각 상에서 전류의 오차 범위는 +5 %와 0 % 사이이고 역률의 오차 범위는 +0.0~-0.05 까지이다. 전류는 교류 성분의 실효값이 일정하게 되는 명시 시간 동 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. 43 | {}
f02894de-42ea-4ed3-abcb-5b3cd713b1da | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 안 인가 된다. 비 고 1. 그러나 필요하다면 시험 제한 요건 때문에 다른 시험 시간이 허용된다. 그런 경우에 첨두값 이 제조자의 동의 없이 정격 첨두값 내전류를 초과 하지 않고 단 시간 전류의 실효값이 전 류가 들어온 후로 최소 0.1 초 동안 적어도 하나의 상에서의 정격 값보다 작지 않다면 시험 전류는 "I2t= 일정"의 수식에 따라 수정되어야 한다. 2. 첨두값 전류 저항 시험과 단시간 전류 시험은 분리된다. 이런 경우에 첨두값 전류 저항 시험에 단락 회로가 인가되는 시간은 12t 의 값이 단시간 전류 시험에 상응하는 값보다 크지 않고 3 주기 이상이 될 수 있도록 해야 한다. 조건부 및 퓨즈로 연결된 단락 회로 전류 시험 동안, 시험은 명시된 보호 장치의 공급 측에서 정격 조건부 및 퓨즈로 연결된 단락 회로 전류의 값과 같은 예상 전류의 정격 작동 전압(8.2.3.2.2 참조)의 1.05 배로 수행된다. 더 낮은 전압에서의 시험은 허용되지 않는다. 8.2.3.2.5 결 과 시험 후에 도체는 심한 변형을 보이지 않는다. 부스바의 미세한 변형은 7.1.2 에 주어진 공간 거리와 연면 거리를 계속 따른다면 받아들여진다. 또한 도체의 절연과 지탱하는 절연 부분은 악화된 기미를 보이지 않는다. 말하자면, 절연의 본질적인 특성은 설비의 기계적 특성과 유전체 특성이 이 기준의 조건을 만족하도록 유지된다. 검출 기기는 가능한 장애 전류를 나타내지 않아야 한다. 도체 연결에 사용된 부분은 느슨하지 않고 도체는 출력 단자로부터 분리되지 않는다. 외함의 변형은 보호 등급이 손상되지 않고 공간 거리가 명시된 값 미만의 값으로 감소되지 않는 범위 까지 허용된다. 부스바 회로의 뒤틀림 또는 회수 가능하거나 제거 가능한 장치의 정상적인 삽입을 손상시키는 부속품의 틀은 고장으로 간주한다. 의심이 드는 경우 부속품에 연결된 기구가 적절한 설명서에 규정되어 있는 상태인지 확인한다. 추가적으로 8.2.3.2.3 a)의 시험과 단락 회로 보호 장치에 관련된 시험 후에 시험된 설비는 적당한 단락 회로 시험에 대한 관련 규격에 규정된 이후의 시험 조건에 대한 전압 값에서 다음과 같이 8.2.2 의 유전체 시험을 견딜 수 있다. a) 모든 사용 부분과 부속품의 틀 사이 그리고 b) 각 극과 부속품의 틀에 연결된 모든 다른 극 사이 위의 시험 a)와 b)가 수행된다면, 개폐 장치가 닫히고 일부 퓨즈는 교체한 뒤 수행한다. 8.2.3.2.6 PTTA 의 경우, 단락 회로 저항 강도의 검증은 다음에 의해 이루어진다. -8.2.3.2.1~8.2.3.2.5 에 따른 시험 - 또는 유사 형식 시험 배치로부터의 추론 비 고 1. 형식 시험된 배치로부터 추론하는 방법의 예는 IEC61117 에 주어져 있다. 2. 도체 강도, 사용 부분과 노출된 전도 부분 사이의 거리, 받침대 사이의 거리, 받침 대의 높이와 강도 그리고 받침 위치 구조의 강도와 유형을 비교할 때 주의 를 기울 여야 한다. 8.2.4 보호 회로의 효율성 검증 8.2.4.1 부속품의 노출된 전도 부분과 보호 회로 사이의 효율적인 연결의 검증 부속품의 다른 노출 전도 부분이 보호 회로에 효과 적으로 연결되고 입력 보호 도체와 적절한 노출 전도 부분 사이의 저항이 0.1 �을 초과 하지 않음이 검증된다. 저항 측정점 사이의 0.1�의 임피던스로 최소 교류 또는 직류 10A 의 전류를 이끌어 낼 수 있는 기기나 44 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
62411ce2-c792-4cb0-b5c8-dc4647bf9d1b | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 배치를 측정하는 저항을 제공하여 검증한다. 비 고 저전류 설비가 시험에 의해 역으로 영향을 받는 경우 시험 시간을 5 초로 제한하는 것이 필요하다. 8.2.4.2 시험에 의한 보호 회로의 단락 회로 강도의 검증(8.2.3.1 에 따르는 회로에는 적용하지 않는다.) 단상 시험 공급원은 단상 입력 단자와 입력 보호 도체의 단자에 연결된다. 부속품이 각각의 보호 도체 를 공급받는다면 가장 가까운 상 도체가 사용된다. 각 표본 출력 장치의 경우, 개별적인 시험은 장치의 관련 출력 상 단자와 적절한 출력 보호 도체 단자 사이에 볼트로 연결된 단락 회로에 이루어진다. 시험할 각 출력 장치는 첨두값 전류의 최대값과 I2t 를 통과 하는 장치 사이에 보호 장치로 공급된다. 시 험은 부속품 외부에 위치한 보호 장치로 이루어진다. 시험 동안 부속품의 틀은 접지로부터 절연된다. 시험 전압은 정격 작동 전압의 단상 값과 같다. 사용된 예상 단락 전류의 값은 부속품의 3 상 단락 회로 저항 시험의 예상 단락 회로 전류값의 60%이다. 이 시험의 모든 다른 조건은 8.2.3.2 와 유사하다. 8.2.4.3 결 과 분리된 도체 또는 틀로 구성되어 있던지 없던지 간에 보호 회로의 연속성과 단락 회로 저항 강도는 크게 손상되지 않는다. 시각적 검사와 더불어 관련 출력 장치의 정격 전류 순으로 전류를 측정하여 검증한다. 비 고 1. 틀이 보호 도체로 사용되는 경우, 접합 부분에서의 섬광과 국부적인 열은 전기적 연속 성을 손상시키지 않고 인접한 가연성 부분을 연소시키지 않는다면 허용된다. 2. 입력 보호 도체의 단자와 관련 출력 보호 도체의 단자 사이에 시험 전후로 측정된 저 항의 비교는 이 조건에 부합하는지 보여준다. 8.2.5 공간 거리와 연면 거리의 검증 공간 거리와 연면 거리가 7.1.2 에 명시된 값에 따르는지 검증된다. 필요하다면 이 공간 거리와 연면 거리는 단락 회로의 경우 가능한 변화를 포함하여 외함의 부분이나 칸 막이의 가능한 변형을 고려한 측정으로 검증된다. 부속품이 회수 가능한 부분을 포함하고 있다면 시험 위치(2.2.9 참조)와 분리된 위치(2.2.10 참조)에서 공간 거리와 연면 거리가 따르는지 검증할 필요가 있다. 8.2.6 기계적 작동의 검증 이 기계적 작동이 설치에 의해 손상되지 않는다면 적절한 설명에 따라 미리 형식 시험된 부속품의 기기에 이 형식 시험은 수행되지 않는다. 형식 시험이 필요한 부분의 경우, 만족할 만한 기계적 작동은 부속품 내에 설치를 하고 나서 검증된다. 작동 주기의 수는 50 이다. 비 고 회수 가능한 기능 장치의 경우, 주기는 연결 위치에서 분리 위치까지 그리고 다시 연결 위 치까지이다. 동시에 이 움직임에 관련된 기계적 연동 장치의 작동이 검사된다. 기구, 연동 장치 등의 작동 조건이 손상되지 않고 작동에 요구되는 작동력이 실제로 시험 전과 같다면 이 시험은 통과 하는 것으로 간주한다. 8.2.7 보호 등급의 검증 7.2.1 과 7.7 에 따라 주어지는 보호 등급은 IEC 60529 에 따라 검증되고 필요하 다면 부속품의 특별 유형에 맞추기 위한 적응성과 제작 과정에 따라 검증된다. 시험 후에 물의 유입으로 즉시 외함 내에 물이 쉽게 보인다면 유전체 특성은 8.2.2 에 따른 시험으로 검증된다. IP4X 시험 중의 외함의 받침대 유형 뿐만이 아니라 IP3X 와 IP4X 의 시험 기기는 시험 보고서에 설명된다. IP5X 의 보호 등급을 갖는 부속품은 IEC60529 의 13.4 의 범위 2 에 따라 시험된다. IP6X 의 보호 등급을 갖는 부속품은 IEC60529 의 13.4 의 범위 1 에 따라 시험된다. 8.2.8 EMC 시험 7.10.2 a)와 b)의 조건을 만족하지 않은 부속품이나 부속품은 적용할 수 있다면 다음 45 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b3858656-c471-4a16-9c2c-51a69d6268ec | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 시험을 따른다. 8.2.8.1 내성 시험 내성은 다음 시험에 의해 검증되어야 한다. ¦ 시험 형식 ¦ 요구되는 시험 수치(1) ¦ ¦ --- ¦ --- ¦ ¦ 1.2/50 �s~8/20 ,us 서지 ¦ 2kV(선에서 접지까지) ¦ ¦ IEC 61000-4-5 ¦ 1kV(선에서 선까지) ¦ ¦ 빠른 순간 파열 ¦ 2kV ¦ ¦ IEC 61000-4-4 ¦ ¦ ¦ 전자기장 ¦ 10 V/m ¦ ¦ IEC 61000-4-3 ¦ ¦ ¦ 정전기 방전 ¦ 8 kV/공기 방전 ¦ IEC 61000-4-2 주(1) 이는 IEC 61000-4 에서 레벨 3 과 관련이 있다. 8.2.8.2 방사 시험 방사 한계는 다음 규격에 따라 검증된다. - 환경 1 의 경우 CISPR 11 B 종 - 환경 2 의 경우 CISPR 11 A 종 8.3 정규 시험 8.3.1 전선의 검사를 포함한 부속품의 검사 그리고 필요하다면 전기 작동 시험 기계적 작동 요소, 연동 장치, 잠금 장치 등의 효율성은 검사된다. 도체와 케이블은 적당하게 놓였는지 기기는 적당하게 설치되었 는지 확인한다. 규정된 보호 등급, 연면 거리와 공간 거리가 유지되는지 눈으로 확인하는 과정 역시 필요 하다. 연결, 특히 꼬여 있고 잠겨 있는 연결은 가능한 임의 의 시험으로 적당한 접촉을 확인한다. 더욱이 5.1 과 5.2 에 명시된 정보와 표시가 완전하고 부속품이 이에 관련되는지 검증된다. 추가하여 제 조자에 의해 주어지는 회로와 전선 그림, 기술적 자료에 부속품이 부합하는지 확인한다. 부속품의 복잡성에 따라 전선을 검사하고 전기적 기능 시험을 수행하는 것이 필요하다. 시험 과정과 시 험의 수는 부속품이 복잡한 연동 장치, 연속 제어 시설 등을 포함하는지 그렇지 않은가에 달려 있다. 어떤 경우에는 부속품이 작동하려 하는 위치에 설치될 때 이 시험을 수행 또는 반복할 필요가 있다. 이 런 경우 특별한 협의 가 제조자와 사용자 사이에 이루어진다. 8.3.2 유전체 시험 시험은 이루어진다. - 제조자가 정격 임펄스 저항 전압 Uimp(4.1.3 참조)의 값을 제시한다면 8.3.2.1 과 8.3.2.2 의 항목 b)에 따라 - 다른 경우에 8.3.2.1 과 8.3.2.2 의 항목 a)에 따라 이 시험들은 절연 저항이 8.2.2.1 또는 8.3.4 에 따라 검증되는 PTTA 위에 수행될 필요가 없다. 이 시험은 미리 전기적 기능 시험(8.3.1 참조)이 보조 회로에 설계된 정격 전압에서 이루어진다면 16A 를 초과 하지 않는 정격을 가진 단락 회로 보호 장치에 의해 보호되는 TTA 와 PTTA 의 보조 회로에 수행될 필요가 없다. 8.3.2.1 일반 사항 부속품의 모든 전기 설비는 관련 설명에 따라 더 낮은 시험 전압으로 설계된 기구를 제외하고 시험 동안 연결된다. 시험 전압의 적용이 전류의 흐름을 유발하는 전류 소비 기구(즉, 권선, 측정 설비)는 분리된다. 모든 단자가 분리되어 있는 경우에 전체 시험 전압을 견디도록 설계되어 있지 않다면 이 기구들은 이 단자들 중의 하나에서 분리된다. 사용 부분과 노출된 전도 부분 사이에 설치된 간섭 방해 콘덴서는 분리되지 않고 시험 전압을 견딜 수 있다. 46 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
525d327b-d428-47e7-b629-0c073abaa8f2 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 8.3.2.2 시험 전압의 적용과 시간과 값 a) 8.2.2.4 에 따르는 시험 전압은 1 초간 인가된다. 교류 전원은 모든 누설 전류에 상관없이 시험 전압을 유지하기 위해 충분한 전력을 가지고 있다. 시험 전압은 실제로 정형파이고 45 Hz 와 62Hz 사이이다. 시험된 주회로 또는 보조 회로에 포함된 설비가 이미 유전체 시험을 받았다면 시험 전압은 8.2.2.4 에 제시한 값의 85 %로 감소한다. 시험 동안 - 모든 개폐 장치가 닫혀 있거나 - 시험 전압이 회로 전 부분에 연속적으로 공급된다. 시험 전압은 사용 부분과 부속품의 전도 구조 부분 사이에 인가된다. b) 시험은 8.2.2.6.2 와 8.2.2.6.3 에 따라 수행된다. 만약 IEC 규격에 따라 더 낮은 시험 전압으로 정규 시험된 회로에서 요소가 연결되어 있다면 더 낮은 전압이 시험 동안 사용된다. 그러나 시험 절연은 정 격 저항 임펄스 전압(크기 보정 인자 없이)의 30% 이상 또는 정격 전압 절연의 두 배 중 더 큰 값이다. 8.3.2.3 결 과 시험은 펑크나 섬락이 없다면 통과 하는 것으로 간주한다. 8.3.3 보호 측정과 보호 회로의 전기적 연속성의 검사 직접 및 간접 접촉에 대한 보호에 관한 보호 측정(7.4.2 와 7.4.3 참조)은 확인된다. 보호 회로는 7.4.3.1.5 에 규정된 측정을 따르는지 조사하여 확인한다. 특히 꼬여 있고 잠겨 있는 연결은 가능한 임의 의 시험에 의해 적당한 접촉을 확인한다. 8.3.4 절연 저항의 검증 8.2.2 또는 8.3.2 에 따라 유전체 시험을 수행하지 않은 PTTA 의 경우, 최소 500V 의 전압에서 절연 측정 기기를 사용한 절연 측정이 수행된다. 이런 경우 회로와 노출된 전도 부분 사이의 절연 저항은 이 회로의 접지에서 공칭 전압으로 언급된 회 로당 최소 1 000�/V 이다. 예외적으로 특정 조건에 따라 시험 전압을 인가하거나 완전 시험 전압으로 설계되지 않은 전류 소비 기 구(예, 권선, 측정 도구)는 적당하게 분리된다는 항목이 있다. 표 13 임펄스, 전력 주파수와 직류 시험에 대한 절연 저항 전압 ¦ 정격 임펄스 저항 전압 Uimp kV ¦ 시험 전압과 관련 고도 ¦ 시험 전압과 관련 고도 ¦ 시험 전압과 관련 고도 ¦ 시험 전압과 관련 고도 ¦ 시험 전압과 관련 고도 ¦ 시험 전압과 관련 고도 ¦ 시험 전압과 관련 고도 ¦ 시험 전압과 관련 고도 ¦ 시험 전압과 관련 고도 ¦ 시험 전압과 관련 고도 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 정격 임펄스 저항 전압 Uimp kV ¦ U1.2/50, 교류 첨두값과 직류 kV ¦ U1.2/50, 교류 첨두값과 직류 kV ¦ U1.2/50, 교류 첨두값과 직류 kV ¦ U1.2/50, 교류 첨두값과 직류 kV ¦ U1.2/50, 교류 첨두값과 직류 kV ¦ AC 실효값 kV ¦ AC 실효값 kV ¦ AC 실효값 kV ¦ AC 실효값 kV ¦ AC 실효값 kV ¦ ¦ 정격 임펄스 저항 전압 Uimp kV ¦ 해 발 ¦ 200 m ¦ 500 m ¦ 1 000 m ¦ 2 000 m ¦ 해 발 ¦ 200 m ¦ 500 m ¦ 1 000 m ¦ 2 000 m ¦ ¦ 0.33 ¦ 0.36 ¦ 0.36 ¦ 0.35 ¦ 0.34 ¦ 0.33 ¦ 0.25 ¦ 0.25 ¦ 0.25 ¦ 0.25 ¦ 0.23 ¦ ¦ 0.5 ¦ 0.54 ¦ 0.54 ¦ 0.53 ¦ 0.52 ¦ 0.5 ¦ 0.38 ¦ 0.38 ¦ 0.38 ¦ 0.37 ¦ 0.36 ¦ ¦ 0.8 ¦ 0.95 ¦ 0.9 ¦ 0.9 ¦ 0.85 ¦ 0.8 ¦ 0.67 ¦ 0.64 ¦ 0.64 ¦ 0.60 ¦ 0.57 ¦ ¦ 1.5 ¦ 1.8 ¦ 1.7 ¦ 1.7 ¦ 1.6 ¦ 1.5 ¦ 1.3 ¦ 1.2 ¦ 1.2 ¦ 1.1 ¦ 1.06 ¦ ¦ 2.5 ¦ 2.9 ¦ 2.8 ¦ 2.8 ¦ 2.7 ¦ 2.5 ¦ 2.1 ¦ 2.0 ¦ 2.0 ¦ 1.9 ¦ 1.77 ¦ ¦ 4 ¦ 4.9 ¦ 4.8 ¦ 4.7 ¦ 4.4 ¦ 4 ¦ 3.5 ¦ 3.4 ¦ 3.3 ¦ 3.1 ¦ 2.83 ¦ ¦ 6 ¦ 7.4 ¦ 7.2 ¦ 7 ¦ 6.7 ¦ 6 ¦ 5.3 ¦ 5.1 ¦ 5.0 ¦ 4.75 ¦ 4.24 ¦ ¦ 8 ¦ 9.8 ¦ 9.6 ¦ 9.3 ¦ 9 ¦ 8 ¦ 7.0 ¦ 6.8 ¦ 6.6 ¦ 6.4 ¦ 5.66 ¦ ¦ 12 ¦ 14.8 ¦ 14.5 ¦ 14 ¦ 13.3 ¦ 12 ¦ 10.5 ¦ 10.3 ¦ 10.0 ¦ 9.5 ¦ 8.48 ¦ 비 고 1. 이 표는 임펄스, 직류 그리고 첨두값 교류 저항 전압값이 같은 경우 동종 분야, 경우 B 의 특성을 사용한다. 2. 공간 거리가 경우 A 와 경우 B 의 상태 사이에 있는 경우, 이 표의 교류 및 직류값은 임 47 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
4ff779dc-aa75-49cc-bbff-ac58e6d57c4d | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 펄스 전압보다 더 엄밀하다. 3. 전력 주파수 전압 시험은 제조자의 동의 를 따른다(8.2.2.6.2 참조). 표 14 공기 중의 최소 공간 거리 ¦ 정격 임펄스 저항 전압 Uimp kV ¦ 최소 공간 거리 mm ¦ 최소 공간 거리 mm ¦ 최소 공간 거리 mm ¦ 최소 공간 거리 mm ¦ 최소 공간 거리 mm ¦ 최소 공간 거리 mm ¦ 최소 공간 거리 mm ¦ 최소 공간 거리 mm ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 정격 임펄스 저항 전압 Uimp kV ¦ 경우 A 이종 분야 (2.9.16 참조) ¦ 경우 A 이종 분야 (2.9.16 참조) ¦ 경우 A 이종 분야 (2.9.16 참조) ¦ 경우 A 이종 분야 (2.9.16 참조) ¦ 경우 B 동종 분야, 이상적인 상태 (2.9.15 참조) ¦ 경우 B 동종 분야, 이상적인 상태 (2.9.15 참조) ¦ 경우 B 동종 분야, 이상적인 상태 (2.9.15 참조) ¦ 경우 B 동종 분야, 이상적인 상태 (2.9.15 참조) ¦ ¦ 정격 임펄스 저항 전압 Uimp kV ¦ 오염도 ¦ 오염도 ¦ 오염도 ¦ 오염도 ¦ 오염도 ¦ 오염도 ¦ 오염도 ¦ 오염도 ¦ ¦ 정격 임펄스 저항 전압 Uimp kV ¦ 1 ¦ 2 ¦ 3 ¦ 4 ¦ 1 ¦ 2 ¦ 3 ¦ 4 ¦ ¦ 0.33 ¦ 0.01 ¦ ¦ ¦ ¦ 0.01 ¦ ¦ ¦ ¦ ¦ 0.5 ¦ 0.04 ¦ 0.2 ¦ ¦ ¦ 0.04 ¦ 0.2 ¦ ¦ ¦ ¦ 0.8 ¦ 0.1 ¦ ¦ 0.8 ¦ ¦ 0.1 ¦ ¦ 0.8 ¦ 1.6 ¦ ¦ 1.5 ¦ 0.5 ¦ 0.5 ¦ ¦ 1.6 ¦ 0.3 ¦ 0.3 ¦ ¦ ¦ ¦ 2.5 ¦ 1.5 ¦ 1.5 ¦ 1.5 ¦ ¦ 0.6 ¦ 0.6 ¦ ¦ ¦ ¦ 4 ¦ 3 ¦ 3 ¦ 3 ¦ 3 ¦ 1.2 ¦ 1.2 ¦ 1.2 ¦ ¦ ¦ 6 ¦ 5.5 ¦ 5.5 ¦ 5.5 ¦ 5.5 ¦ 2 ¦ 2 ¦ 2 ¦ 2 ¦ ¦ 8 ¦ 8 ¦ 8 ¦ 8 ¦ 8 ¦ 3 ¦ 3 ¦ 3 ¦ 3 ¦ ¦ 12 ¦ 14 ¦ 14 ¦ 14 ¦ 14 ¦ 4.5 ¦ 4.5 ¦ 4.5 ¦ 4.5 ¦ 비 고 해발 2000 m 위에서의 정상 대기압과 기압계의 압력 80 kPa 이 같다면 공기중의 최소 공간 거 리의 값은 1.2/50 us 임펄스 전압을 기본으로 한다. 표 15 절연에 적합한 설비의 개방 접촉부에 걸린 시험 전압 ¦ 정격 임펄스 저항 전압 Uimp kV ¦ 시험 전압과 관련 고도 ¦ 시험 전압과 관련 고도 ¦ 시험 전압과 관련 고도 ¦ 시험 전압과 관련 고도 ¦ 시험 전압과 관련 고도 ¦ 시험 전압과 관련 고도 ¦ 시험 전압과 관련 고도 ¦ 시험 전압과 관련 고도 ¦ 시험 전압과 관련 고도 ¦ 시험 전압과 관련 고도 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 정격 임펄스 저항 전압 Uimp kV ¦ U1.2/50, 교류 첨두값과 직류 kV ¦ U1.2/50, 교류 첨두값과 직류 kV ¦ U1.2/50, 교류 첨두값과 직류 kV ¦ U1.2/50, 교류 첨두값과 직류 kV ¦ U1.2/50, 교류 첨두값과 직류 kV ¦ AC 실효값 kV ¦ AC 실효값 kV ¦ AC 실효값 kV ¦ AC 실효값 kV ¦ AC 실효값 kV ¦ ¦ 정격 임펄스 저항 전압 Uimp kV ¦ 해 발 ¦ 200 m ¦ 500m ¦ 1 000 m ¦ 2000 m ¦ 해 발 ¦ 200 m ¦ 500 m ¦ 1 000 m ¦ 2000 m ¦ ¦ 0.33 ¦ 1.8 ¦ 1.7 ¦ 1.7 ¦ 1.6 ¦ 1.5 ¦ 1.3 ¦ 1.2 ¦ 1.2 ¦ 1.1 ¦ 1.06 ¦ ¦ 0.5 ¦ 1.8 ¦ 1.7 ¦ 1.7 ¦ 1.6 ¦ 1.5 ¦ 1.3 ¦ 1.2 ¦ 1.2 ¦ 1.1 ¦ 1.06 ¦ ¦ 0.8 ¦ 1.8 ¦ 1.7 ¦ 1.7 ¦ 1.6 ¦ 1.5 ¦ 1.3 ¦ 1.2 ¦ 1.2 ¦ 1.1 ¦ 1.06 ¦ ¦ 1.5 ¦ 2.3 ¦ 2.3 ¦ 2.2 ¦ 2.2 ¦ 2 ¦ 1.6 ¦ 1.6 ¦ 1.55 ¦ 1.55 ¦ 1.42 ¦ ¦ 2.5 ¦ 3.5 ¦ 3.5 ¦ 3.4 ¦ 3.2 ¦ 3 ¦ 2.47 ¦ 2.47 ¦ 2.4 ¦ 2.26 ¦ 2.12 ¦ ¦ 4 ¦ 6.2 ¦ 6 ¦ 5.8 ¦ 5.6 ¦ 5 ¦ 4.38 ¦ 4.24 ¦ 4.10 ¦ 3.96 ¦ 3.54 ¦ ¦ 6 ¦ 9.8 ¦ 9.6 ¦ 9.3 ¦ 9 ¦ 8 ¦ 7.0 ¦ 6.8 ¦ 6.60 ¦ 6.40 ¦ 5.66 ¦ ¦ 8 ¦ 12.3 ¦ 12.1 ¦ 11.7 ¦ 11.1 ¦ 10 ¦ 8.7 ¦ 8.55 ¦ 8.27 ¦ 7.85 ¦ 7.07 ¦ ¦ 12 ¦ 18.5 ¦ 18.1 ¦ 17.5 ¦ 16.7 ¦ 15 ¦ 13.1 ¦ 12.80 ¦ 12.37 ¦ 11.80 ¦ 10.6 ¦ 비 고 1. 공간 거리가 경우 A 와 경우 B 의 상태 사이에 있는 경우(표 14 참조), 이 표의 교류 및 직류 값은 임펄스 전압보다 더 엄밀하다. 2. 전력 주파수 전압 시험은 제조자의 동의 를 따른다(8.2.2.6.2 참조). 48 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f39e01ec-26fa-4fa9-90db-4f2dd71c2313 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 표 16 최소 연면 거리 ¦ 설비의 정격 절연 전압 또는 작동 전압 교류 실효값 또는 직류 V(5) ¦ 장시간의 압력을 받은 설비의 연면 거리 mm ¦ 장시간의 압력을 받은 설비의 연면 거리 mm ¦ 장시간의 압력을 받은 설비의 연면 거리 mm ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 설비의 정격 절연 전압 또는 작동 전압 교류 실효값 또는 직류 V(5) ¦ 오염도 ¦ 오염도 ¦ 오염도 ¦ 오염도 2 ¦ 오염도 2 ¦ 오염도 2 ¦ 오염도 2 ¦ 오염도 ¦ 오염도 ¦ 오염도 ¦ 오염도 ¦ 오염도 ¦ 오염도 ¦ 오염도 ¦ ¦ 설비의 정격 절연 전압 또는 작동 전압 교류 실효값 또는 직류 V(5) ¦ 1(6) 50 ¦ 2(6) ¦ 1 ¦ 오염도 2 ¦ 오염도 2 ¦ 오염도 2 ¦ 오염도 2 ¦ 3 ¦ 3 ¦ 3 ¦ 4 ¦ 4 ¦ 4 ¦ 4 ¦ ¦ 설비의 정격 절연 전압 또는 작동 전압 교류 실효값 또는 직류 V(5) ¦ 물 질 군 ¦ 물 질 군 ¦ 물 질 군 ¦ 물 질 군 ¦ 물 질 군 ¦ 물 질 군 ¦ 물 질 군 ¦ 물 질 군 ¦ 물 질 군 ¦ 물 질 군 ¦ 물 질 군 ¦ 물 질 군 ¦ 물 질 군 ¦ 물 질 군 ¦ ¦ 설비의 정격 절연 전압 또는 작동 전압 교류 실효값 또는 직류 V(5) ¦ (3) ¦ ⌀ ¦ (3) ¦ I(1) ¦ II ¦ IIIa ¦ IIIb ¦ I ¦ II 90 ¦ IIIa IIIb ¦ I ¦ II ¦ IIIa ¦ IIIb ¦ ¦ 10 ¦ 0.025 ¦ 0.04 ¦ 0.08 ¦ 0.4 ¦ 0.4 ¦ 0.4 ¦ 1 ¦ ¦ 1 ¦ 1 ¦ 1.6 ¦ 1.6 ¦ 1.6 ¦ ¦ ¦ 12.5 ¦ 0.025 ¦ 0.04 ¦ 0.09 ¦ 0.42 ¦ 0.42 ¦ 0.42 ¦ ¦ 1.05 100 ¦ 1.05 ¦ 1.05 ¦ 1.6 ¦ 1.6 ¦ 1.6 ¦ ¦ ¦ 16 ¦ 0.025 ¦ 0.04 ¦ 0.1 ¦ 0.45 ¦ 0.45 ¦ 0.45 ¦ ¦ 1.1 ¦ 1.1 ¦ 1.1 ¦ 1.6 ¦ 1.6 ¦ 1.6 ¦ ¦ ¦ 20 ¦ 0.025 ¦ 0.04 ¦ 0.11 ¦ 0.48 ¦ 0.48 ¦ 0.48 ¦ ¦ 1.2 ¦ 1.2 ¦ 1.2 ¦ 1.6 ¦ 1.6 ¦ 1.6 ¦ ¦ ¦ 25 ¦ 0.025 ¦ 0.04 ¦ 0.125 ¦ 0.5 ¦ 0.5 ¦ 0.5 ¦ ¦ 1.25 ¦ 1.25 ¦ 1.25 ¦ 1.7 ¦ 1.7 ¦ 1.7 ¦ ¦ ¦ 32 ¦ 0.025 ¦ 0.04 ¦ 0.14 ¦ 0.53 ¦ 0.53 ¦ 0.53 ¦ 1.3 ¦ 1.3 ¦ ¦ 1.3 ¦ 1.8 ¦ 1.8 ¦ 1.8 ¦ ¦ ¦ 40 ¦ 0.025 ¦ 0.04 ¦ 0.16 ¦ 0.56 ¦ 0.8 ¦ 1.1 ¦ 1.4 ¦ ¦ 1.6 ¦ 1.8 ¦ 1.9 ¦ 2.4 ¦ 3 ¦ ¦ ¦ 50 ¦ 0.025 ¦ 0.04 ¦ 0.18 ¦ 0.6 ¦ 0.85 ¦ 1.2 ¦ 1.5 ¦ 1.7 ¦ ¦ 1.9 ¦ 2 ¦ 2.5 ¦ 3.2 ¦ ¦ ¦ 63 ¦ 0.04 ¦ 0.063 ¦ 0.2 ¦ 0.63 ¦ 0.9 ¦ 1.25 ¦ 1.6 ¦ ¦ 1.8 ¦ 2 ¦ 2.1 ¦ 2.6 ¦ 3.4 ¦ ¦ ¦ 80 ¦ 0.063 ¦ 0.1 ¦ 0.22 ¦ 0.67 ¦ 0.95 ¦ 1.3 ¦ ¦ 1.7 ¦ 1.9 ¦ 2.1 80 ¦ 2.2 ¦ 2.8 ¦ 3.6 ¦ ¦ ¦ 100 ¦ 0.1 ¦ 0.16 ¦ 0.25 ¦ 0.71 ¦ 1 160 ¦ 1.4 ¦ 1.8 ¦ ¦ 2 ¦ 2.2 ¦ 2.4 ¦ 3.0 ¦ 3.8 ¦ ¦ ¦ 125 ¦ 0.16 ¦ 0.25 ¦ 0.28 ¦ 0.75 ¦ 1.05 ¦ 1.5 ¦ 1.9 ¦ ¦ 2.1 ¦ 2.4 ¦ 2.5 ¦ 3.2 ¦ 4 ¦ ¦ ¦ 160 ¦ 0.25 ¦ 0.4 ¦ 0.32 ¦ 0.8 ¦ 1.1 ¦ 1.6 110 ¦ 2 ¦ ¦ 2.2 ¦ 2.5 ¦ 3.2 ¦ 4 ¦ 5 ¦ ¦ ¦ 200 ¦ 0.4 ¦ 0.63 ¦ 0.42 ¦ 1 ¦ 1.4 ¦ 2 ¦ 2.5 ¦ 2.8 ¦ 25 32 ¦ 3.2 100 ¦ 4 ¦ 5 125 160 ¦ 6.3 160 ¦ ¦ ¦ 250 ¦ 0.56 ¦ 1 ¦ 0.56 ¦ 1.25 ¦ 1.8 ¦ 2.5 ¦ 63 ¦ 3.2 ¦ 3.6 100 ¦ 4 125 ¦ 5 ¦ 6.3 ¦ 8 200 ¦ ¦ ¦ 320 ¦ 0.75 ¦ 1.6 ¦ 0.75 ¦ 1.6 ¦ 2.2 45 ¦ 3.2 ¦ 4 ¦ 4.5 ¦ ¦ 5 ¦ 6.3 ¦ 8 ¦ 10 ¦ (4) ¦ ¦ 400 ¦ 1 ¦ 2 ¦ 1 ¦ 2 ¦ 2.8 56 ¦ 4 ¦ 5 ¦ 5.6 ¦ 125 ¦ 6.3 ¦ 8 160 ¦ 10 200 ¦ 12.5 250 ¦ ¦ ¦ 500 8000 ¦ 1.3 ¦ 2.5 ¦ 1.3 32 ¦ 2.5 40 ¦ 3.6 ¦ 5 80 ¦ 6.3 ¦ 7.1 10000 ¦ ¦ 8.0 ¦ 10 ¦ 12.5 6300 ¦ 16 ¦ ¦ ¦ 630 ¦ 1.8 ¦ 3.2 ¦ 1.8 ¦ 3.2 ¦ 4.5 ¦ 6.3 ¦ 8 125 ¦ 9 ¦ ¦ 10 ¦ 12.5 ¦ 16 ¦ 20 ¦ ¦ ¦ 800 ¦ 2.4 ¦ 4 ¦ 2.4 ¦ 4 ¦ 5.6 ¦ 8 100 ¦ 10 ¦ 11 140 ¦ 12.5 ¦ ¦ 16 ¦ 20 ¦ 25 ¦ ¦ ¦ 1000 ¦ 3.2 ¦ 5 ¦ 3.2 ¦ 5 ¦ 7.1 71 200 ¦ 10 ¦ 12.5 ¦ 14 ¦ 16 ¦ ¦ 20 ¦ 25 ¦ 32 ¦ ¦ ¦ 1250 ¦ ¦ ¦ 4.2 ¦ 6.3 ¦ 9 ¦ 12.5 ¦ 16 ¦ 18 ¦ 20 ¦ ¦ 25 ¦ 32 ¦ 40 ¦ ¦ ¦ 1600 ¦ ¦ ¦ 5.6 ¦ 8 ¦ 11 ¦ 16 ¦ 20 ¦ 22 ¦ 25 ¦ ¦ 32 ¦ 40 ¦ 50 ¦ ¦ ¦ 2000 ¦ ¦ ¦ 7.5 ¦ 10 ¦ 14 ¦ 20 ¦ 25 ¦ 28 ¦ 32 ¦ ¦ 40 ¦ 50 250 ¦ 63 ¦ ¦ ¦ 2500 ¦ ¦ ¦ 10 ¦ 12.5 ¦ 18 ¦ 25 ¦ 32 ¦ 36 ¦ 40 ¦ ¦ 50 ¦ 63 ¦ 80 ¦ ¦ ¦ 3200 ¦ ¦ ¦ 12.5 40 ¦ 16 ¦ 22 ¦ 32 ¦ 40 ¦ 45 ¦ 50 ¦ (4) ¦ 63 80 ¦ 80 100 ¦ 100 125 320 ¦ ¦ ¦ 4000 5000 ¦ ¦ ¦ 16 20 ¦ 20 25 ¦ 28 36 ¦ 40 50 ¦ 50 63 ¦ 56 71 ¦ 63 80 ¦ ¦ ¦ ¦ ¦ ¦ 주() IEC 60664-1 의 2.4 에 기인하여 흠이 생길 가능성이 줄어드는 물질 군 I 또는 II, IIIa, IIIb (2) 물질 군 I,II, IIIa 그리고 IIIb () 물질 군 I,II, IIIa (4) 이 영역에서 연면 거리의 값은 성립되지 않는다. 물질 군 IIIb 는 일반적으로 630V 이상의 오염도 3 과 오염도 4 에서 사용되지 않도록 권한다. () 예외로 정격 절연 전압 127, 208, 415, 440, 660/690 그리고 830V 의 경우 더 낮은 값 125, 200, 400, 630 그리고 800 V 에 관한 연면 거리가 사용된다. (9 이 두 행에 주어진 값은 인쇄된 전선 물질의 연면 거리에 적용한다. 비 고 1. 흠이나 부식은 32 V 와 그 이하의 작동 전압에 걸린 절연체에서 발생하지 않는 것으로 인정된다. 그러나 전해질 침식의 가능성은 고려되어야만 하고 이런 이유로 최소 연면 거리가 명시된다. 2. 전압값은 R10 시리즈에 따라 선택된다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. 49 | {}
2d3e61fe-1eeb-4071-8a78-7d20fcb20091 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 부속서 A(규정) 연결에 적합한 구리 도체의 최소 및 최대 단면(7.1.3.2 참조) 다음 표는 단자당 하나의 구리 케이블을 연결할 때 적용한다. 표 A.1 ¦ 정격 전류 ¦ 고체 또는 꼬아놓은 도체 ¦ 고체 또는 꼬아놓은 도체 ¦ 유동적인 도체 ¦ 유동적인 도체 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 정격 전류 ¦ 단 면 ¦ 단 면 ¦ 단 면 ¦ 단 면 ¦ ¦ 정격 전류 ¦ 최 소 ¦ 최 대 ¦ 최 소 ¦ 최 대 ¦ ¦ A ¦ mm2 ¦ mm2 ¦ mm2 ¦ mm2 ¦ ¦ 6 ¦ 0.75 ¦ 1.5 ¦ 0.5 ¦ 1.5 ¦ ¦ 8 ¦ 1 ¦ 2.5 ¦ 0.75 ¦ 2.5 ¦ ¦ 10 ¦ 1 ¦ 2.5 ¦ 0.75 ¦ 2.5 ¦ ¦ 12 ¦ 1 ¦ 2.5 ¦ 0.75 ¦ 2.5 ¦ ¦ 16 ¦ 1.5 ¦ 4 ¦ 1 ¦ 4 ¦ ¦ 20 ¦ 1.5 ¦ 6 ¦ 1 ¦ 4 ¦ ¦ 25 ¦ 2.5 ¦ 6 ¦ 1.5 ¦ 4 ¦ ¦ 32 ¦ 2.5 ¦ 10 ¦ 1.5 ¦ 6 ¦ ¦ 40 ¦ 4 ¦ 16 ¦ 2.5 ¦ 10 ¦ ¦ 63 ¦ 6 ¦ 25 ¦ 6 ¦ 16 ¦ ¦ 80 ¦ 10 ¦ 35 ¦ 10 ¦ 25 ¦ ¦ 100 ¦ 16 ¦ 50 ¦ 16 ¦ 35 ¦ ¦ 125 ¦ 25 ¦ 70 ¦ 25 ¦ 50 ¦ ¦ 160 ¦ 35 ¦ 95 ¦ 35 ¦ 70 ¦ ¦ 200 ¦ 50 ¦ 120 ¦ 50 ¦ 95 ¦ ¦ 250 ¦ 70 ¦ 150 ¦ 70 ¦ 120 ¦ ¦ 315 ¦ 95 ¦ 240 ¦ 95 ¦ 185 ¦ 비 고 1. 외부 도체가 내부 기구에 직접적으로 연결된다면 관련 설명에 지시된 단면은 유효하다. 2. 표에 설명된 것 이외에 도체에 제공될 필요가 있는 경우, 특별한 협의 가 제조자와 사용자 사이에 이루어진다. 50 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
391966d0-3759-4100-8f5f-21442b956864 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 부속서 B(규정) 단시간의 전류로 인한 열 압력에 관련된 보호 도체의 단면적 계산법 (더 자세한 정보는 IEC 60364-5-54 에서 찾을 수 있다.) 다음의 수식은 0.2 초에서 5 초까지의 차례대로 흐르는 전류로 인한 열 압력을 견디기 위해 필요한 보호 도체의 단면을 계산하는 데 사용된다. I2t Sp= k 여기에서 Sp : mm2 로 표시되는 단면적이다. I: 보호 장치를 통과 할 수 있는 무시할 만큼의 임피던스의 장애 동 안 교류 장애 전류의 값(실효값)이며 A 로 표시된다. t: 분리 장치의 작동 시간이고 초로 표시된다. k : 보호 도체의 물질, 절연체와 다른 부분 그리고 처음과 끝의 온 도에 의존하는 인수이다. 비 고 회로 임피던스의 전류 제한 영향과 보호 장치의 제한 능력(줄 적분)을 고려한다. 표 B.1 케이블에 연결하지 않은 절연 보호 도체 또는 케이블 외피와 접촉하는 노출된 보호 도체의 k 값 ¦ ¦ 보호 도체 또는 케이블 외피의 절연 ¦ 보호 도체 또는 케이블 외피의 절연 ¦ 보호 도체 또는 케이블 외피의 절연 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ PVC ¦ XLPE EPR 노출된 도체 ¦ 부틸 고무 ¦ ¦ ¦ 최종 온도 ¦ 160°C ¦ 250°C ¦ 220°C ¦ ¦ ¦ 인수 k ¦ 인수 k ¦ 인수 k ¦ ¦ 도체 물질 ¦ ¦ ¦ ¦ ¦ 구리 ¦ 143 ¦ 176 ¦ 166 ¦ ¦ 알루미늄 ¦ 195 ¦ 116 ¦ 110 ¦ ¦ 철 ¦ 152 ¦ 164 ¦ 160 ¦ 비 고 도체의 처음 온도는 30°C 로 가정한다. 51 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
0359cb2f-af05-4f45-a04c-0fedeae5647c | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 부속서 C(참고) 부속품의 전형적인 예 ![image](/image/placeholder) 받침 구조 그림 C.1 개방형 부속품(2.3.1 참조) 52 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f09619fa-bfb2-43c7-a8b8-3b4cc366b660 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 ![image](/image/placeholder) □ □ � □□ � □ � V 받침 구조 그림 C.2 앞이 막힌 부속품(2.3.2 참조) 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 53 | {}
f4db3ba2-e27d-4120-beb7-86e7dc8b3780 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 ![image](/image/placeholder) [o 푹 폭 깊이 그림 C.3 큐비클형 부속품(2.3.3.1 참조) 54 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
29d24d5d-ae87-4d15-a699-5580b81a3ceb | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 ![image](/image/placeholder) 전송 개체 구획 - 높이 □ □ □ 깊이 폭 길이 그림 C.4 다중 큐비클형 부속품(2.3.3.2 참조) 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 55 | {}
d13061b9-aa88-40df-8e7e-f94dfa910f37 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 ![image](/image/placeholder) O ○ - 그림 C.5 책상형 부속품(2.3.3.3 참조) 56 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
bd817b6d-0f8a-4a36-8022-e5e2b7d221aa | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 박스형 조립품 ![image](/image/placeholder) (2.3.3.4 참조) + + + ++ + + ++++ 케이블 입구 그림 C.6 다중 상자형 부속품(2.3.3.5 참조) 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 57 | {}
825b2943-448a-4653-b38d-146b0bbc8cfb | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 ![image](/image/placeholder) 탭 오프 능력이 없는 모선 본선 시스템 탭 오프 능력을 가진 모선 본선 시스템 그림 C.7 부스바 트렁킹 시스템(2.3.4 참조) 58 2025-07-16, 에스케이에코플랜트( 주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f24835a4-dead-4813-80b9-cfdc2e753d01 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 ![image](/image/placeholder) 그림 C.8 설치 구조(2.4.2 참조) 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 59 | {}
873ef77b-f29f-41f1-b3dc-2160f41a0d57 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 ![image](/image/placeholder) 설치 틀 설치 판 그림 C.9 고정 부분(2.2.5, 2.4.3, 2.4.4 참조) 60 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
6a59d386-ddca-4393-ab94-fc418c9bd63f | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1 :1999 ![image](/image/placeholder) 그림 C.10 회수 가능한 부분(2.2.7 참조) 2025-07-16, 에스케이에코플랜트( 주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 61 | {}
cdbc8f91-7061-4c92-95b9-1367269c56ea | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 부속서 D(참고) 내부 분할의 형태(7.7 참조) 기 호 분배 부스바를 포함한 부스바 ![image](/image/placeholder) 외함 내부 분할 관련 외부 도체용 단자를 포함하는 기능 개체 그림 D.1 그림 D.2 에 사용되는 기호 62 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
95c76015-38a3-4dcc-b1c2-9149b621bf7e | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 형태 1 내부 분할이 없다. ![image](/image/placeholder) 형태 2 기능 장치로부터의 부스바 분리 ![image](/image/placeholder) ![image](/image/placeholder) 형태 2a : 형태 2b : 부스바로부터 분리되지 않은 단자 부스바로부터 분리된 단자 그림 D.2 형태 1 과 2 형태 3 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 63 | {}
3a81f954-aebf-45f4-9949-d4c5c9fa07a6 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 기능적인 장치로부터의 부스바의 분리 + 각자로부터의 기능 장치의 분리 + 기능적인 장치로부터의 단자의 분리 ![image](/image/placeholder) 형태 3a : 부스바로부터 분리되지 않은 단자 ![image](/image/placeholder) 형태 3b : 부스바로부터 분리된 단자 형태 4 기능적인 장치로부터의 부스바의 분리 + 각자로부터의 기능 장치의 분리 + 기능적인 장치로부터의 단자의 분리 ![image](/image/placeholder) 형태 4a 관련 기능 장치로써 같은 부분안의 단자 ![image](/image/placeholder) 형태 4b 관련 기능 장치로써 같은 부분안에 있지 않은 단자 그림 D.2 형태 3 과 4 64 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
23d0955a-4220-49ad-9a64-837a1397a900 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 부속서 E(참고) 제조업자와 사용자 사이의 협의 에 따른 항목 이 규격의 부속항 ¦ 4.7 ¦ 정격 변화 인자 ¦ ¦ --- ¦ --- ¦ ¦ 6.1.1.2 ¦ (비고) 북극 기후에서의 조립품 사용 ¦ ¦ 6.1.3 ¦ (비고) 해발 1 000 m 에서의 전자 설비의 사용 ¦ ¦ 6.2 ¦ 특별 동작 조건 ¦ ¦ 6.2.10 ¦ 전기적 그리고 방사된 간섭 ¦ ¦ 6.3.1 ¦ 전송, 보관 그리고 조립 동안의 조건 ¦ ¦ 7.1.3 ¦ 외부 도체용 단자 ¦ ¦ 7.2.1.1 ¦ 의도적인 설치시 필요한 보호 등급, 바닥에 설치하는 조립품의 경우 바닥의 보호 등급 또한 나타냄 ¦ ¦ 7.4.2 ¦ 직접 접촉에 대한 보호 측정의 선택 ¦ ¦ 7.4.3 ¦ 간접 접촉에 대한 보호 측정의 선택 ¦ ¦ 7.4.6 ¦ 권한자에 의한 동작 접근성 ¦ ¦ 7.4.6.1 ¦ 검사와 유사 동작에 대한 접근성 ¦ ¦ 7.4.6.2 ¦ 유지에 대한 접근성 ¦ ¦ 7.4.6.3 ¦ 전압 하에서의 확장에 대한 접근성 ¦ ¦ 7.5.2.3 ¦ 고전력 회전 기계에 대한 여러 입력 또는 출력 장치의 경우 예상 단락 회로 전류의 값 ¦ ¦ 7.5.4 ¦ 단락 회로 보호 장치의 조정 ¦ ¦ 7.6.4.1 ¦ 내부 연동 장치 ¦ ¦ 7.6.4.3 ¦ 제거 가능하거나 회수 가능한 부분 제거 후 보호 등급 ¦ ¦ 7.7 ¦ 분할 형태 ¦ ¦ 7.9.1 ¦ 전자 설비 공급에 대한 입력 전압 변화 ¦ ¦ 7.9.4 항목 b) ¦ 공급 주파수 편차 ¦ ¦ 8.2.1.3.4 ¦ 3150 A 보다 더 큰 실험 전류에 대한 온도 상승 실험 ¦ ¦ 8.2.1.6 ¦ 온도 상승 실험에 대한 대기 온도 ¦ ¦ 8.2.3.2.3 항목 d) ¦ 단락 회로 실험에 대한 중성 모선 전류 값 ¦ ¦ 8.3.1 ¦ 부지 위의 전기적 동작의 반복 ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 65 | {}
5318fab4-eb49-4cc1-9477-c9c50c564582 | KSCIEC60439-1_2024확인_KR | KS CIEC 60439-1:1999 부속서 F(규정) 연면 거리와 공간 거리의 측정* F.1 기본 원리 다음 예 1~11 까지에 명시된 홈의 폭 X 는 기본적으로 다음과 같이 오염의 함수로 모든 예 에 적용한다. ¦ 오염도 ¦ 홈의 폭 X 의 최소값 mm ¦ ¦ --- ¦ --- ¦ ¦ 1 ¦ 0.25 ¦ ¦ 2 ¦ 1.0 ¦ ¦ 3 ¦ 1.5 ¦ ¦ 4 ¦ 2.5 ¦ 관련 공간 거리가 3 mm 미만이라면 최소 홈의 폭은 이 공간 거리의 1/3 으로 줄어든다. 연면 거리와 공간 거리를 측정하는 방법은 예 1~11 까지 나타난다. 이 예는 갭과 홈 사이 또는 절연의 유형 사이를 구별하지 못한다. 더욱이 - 가장 바람직하지 못한 위치로 이동되는 X mm 의 절연 고리로 연결되는 구석(예 3 참조) - 홈의 꼭대기를 가로지르는 거리가 x mm 이상인 경우, 연면 거리는 홈의 경로를 따라 측정된다(예 2 참조). - 이 부분들이 가장 바람직하지 못한 위치에 있을 때 연면 거리와 공간 거리는 각각에 대해 이동하는 부분 사이에 측정된다. F.2 리브의 사용 오염과 더 나은 건조 영향 때문에 리브는 누설 전류의 형성을 감소시킨다. 그러므로 불룩한 부분의 최소 높이가 2mm 라면 연면 거리는 필요한 값의 0.8 배로 줄어든다. ![image](/image/placeholder) 최소 높이 2mm - EXPROS 기계적 조건에 따른 바닥의 최소 폭 그림 F.1 리브의 측정 주* 이 부속서 F 는 IEC 60947- 1 의 부속서 G 와 동일하다. 66 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
ae0a69f2-c29d-4e59-9c2c-59283b44d820 | KSCIEC60439-1_2024확인_KR | KS CIEC 60439-1:1999 ![image](/image/placeholder) 예 1 <Xmm 조건 : 연면 거리 경로는 Xmm 미만의 폭과 일정 깊이의 병렬 또는 수렴 홈을 포함한다. 규칙 : 연면 거리와 공간 거리는 보이는 대로 홈을 직접 가로질러 측정된다. ![image](/image/placeholder) 예 2 ≥Xmm 20,0 조건 : 연면 거리 경로는 Xmm 이상의 폭과 일정 깊이의 병렬 또는 수렴 홈을 포함한다. 규칙 : 공간 거리는 "조준선" 거리이다. 연면 거리 경로는 홈의 윤곽을 따른다. ![image](/image/placeholder) 예 3 > X mm 조건 : 이 연면 거리 경로는 Xmm 이상의 폭을 가진 V 자 모형의 홈을 포함한다. 규칙 : 공간 거리는 "조준선" 거리이다. 연면 거리 경로는 홈의 윤곽을 따르지만 Xmm 연결로 홈의 바닥 위에 "단선"이 있다. 공간 거리 AMARWERS 연면 거리 67 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
0820bf20-3f02-4a77-93d3-23fe0b1f51d4 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 ![image](/image/placeholder) 예 4 - 조건 : 이 연면 거리는 리브를 포함한다. 규칙 : 공간 거리는 리브의 꼭대기 위로 최단 공기 경로이다. 연면 경로는 리브의 윤곽을 따른다. 예 5 ![image](/image/placeholder) <X mm <X mm 조건 : 이 연면 거리는 각 쪽에 Xmm 미만의 홈으로 연속적으로 연결되는 있는 것을 포함한다. 규칙 : 연면 거리와 공간 거리 경로는 보이는 대로 "조준선" 거리이다. ![image](/image/placeholder) 예 6 ≥X mm ≥X mm 조건 : 이 연면 거리는 각 쪽에 Xmm 이상의 홈이 연속적으로 연결되는 있는 것을 포함한다. 규칙 : 공간 거리는 "조준선" 거리이다. 연면 거리는 홈의 윤곽을 따른다. 공간 거리 AMERSIONS 연면 거리 68 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
13a91e27-a9c1-4ac9-8bf3-0d41ea381e0b | KSCIEC60439-1_2024확인_KR | KS CIEC 60439-1:1999 예 7 ![image](/image/placeholder) ≥X mm <X mm - - 조건 : 이 연면 거리 경로는 한 쪽은 폭이 x mm 미만이고 나머지 한 쪽은 x mm 이상인 홈이 연속적으로 연결되어 있는 것을 포함한다. 규칙 : 공간 거리와 연면 거리는 보는 것과 같다. ![image](/image/placeholder) 예 8 ソウル YOURSHOUS 조건 : 연결된 부분을 통과 한 연면 거리는 장벽을 넘은 연면 거리보다 작다. 규칙 : 공간 거리는 장벽의 꼭대기 위의 최단 직접 공기 경로이다. 예 9 ![image](/image/placeholder) ≥X mm ≥X mm 강보험심사진단가 조건 : 나사의 머리와 홈의 벽 사이에 거리는 고려해야 할 정도로 충분히 크다. 규칙 : 공간 거리와 연면 거리 경로는 보는 대로이다. 공간 거리 ������������� 연면 거리 69 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
2f2da5c6-cf51-4301-990a-832bb9fec5d4 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 예 10 ![image](/image/placeholder) = X mm = X mm PART 조건 : 나사의 머리와 홈의 벽 사이의 거리는 고려하지 않아도 될 만큼 좁다. 규칙 : 연면 거리의 측정은 거리가 X mm 와 같을 때 나사에서 벽까지이다. 예 11 ![image](/image/placeholder) C' 표류 부분 I d D C' · ≥X ≥X 공간 거리는 거리 d+D 이다. 연면 거리 또한 d+D 이다. 공간 거리 PARKWARKS 연면 거리 70 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
dfb9f3be-eaa3-4d61-9415-6554540ace4b | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 부속서 G(규정) 공급 시스템의 미소 전압과 설비의 정격 충격 저항 전압 사이의 상관성 머 리 말 이 부속서는 전기적 시스템이나 부품내 회로에서 사용되는 설비의 선택에 관해 필요한 정보를 제공한다. 표 G.1 은 미소 공급 시스템 전압과 설비의 관련 정격 충격 저항 전압 사이의 상관성의 예를 보여준다. 표 G.1 에 주어진 정격 충격 저항 전압의 값은 서지 피뢰기의 수행 특성에 근거한다. IEC 60099-1 에 따 른 특성에 기초한다. 표 G.1 의 값에 관한 과전압의 제어는 적당한 임피던스나 케이블 피드의 존재와 같이 공급 시스템 조건 에 의해 성립된다. 과전압의 제어가 서지 피뢰기 이외의 수단에 의해 성립되는 경우, 미소 공급 전압과 설비 정격 충격 저항 전압 사이의 상관성에 대한 내용은 IEC 60364-4-443 에 주어져 있다. 표 G.1 IEC 60099-1 에 따른 서지 피뢰기에 의한 과전압 보호의 경우, 공급 시스템의 미소 전압과 설비 정격 충격 저항 전압 사이의 상관성 ¦ 접지에 대한 정격 동작 전압의 최대값 ¦ 공급 시스템의 미소 전압 (≤ 설비의 정격 절연 전압) v ¦ 공급 시스템의 미소 전압 (≤ 설비의 정격 절연 전압) v ¦ 공급 시스템의 미소 전압 (≤ 설비의 정격 절연 전압) v ¦ 공급 시스템의 미소 전압 (≤ 설비의 정격 절연 전압) v ¦ 2000m 에서 정격 충격 저항 전압 (1.2/50��s)의 우선값 kV ¦ 2000m 에서 정격 충격 저항 전압 (1.2/50��s)의 우선값 kV ¦ 2000m 에서 정격 충격 저항 전압 (1.2/50��s)의 우선값 kV ¦ 2000m 에서 정격 충격 저항 전압 (1.2/50��s)의 우선값 kV ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 접지에 대한 정격 동작 전압의 최대값 ¦ ¦ ¦ ¦ ¦ 과전압 범위 ¦ 과전압 범위 ¦ 과전압 범위 ¦ 과전압 범위 ¦ ¦ 접지에 대한 정격 동작 전압의 최대값 ¦ IV ¦ III ¦ II ¦ I ¦ ¦ ¦ ¦ ¦ ¦ 교류 실효값 또는 직류 v ¦ AC. r.m.s ¦ AC. r.m.s ¦ AC. r.m.s 또는 d.c ¦ AC.r.m.s 또는 d.c ¦ 설치 원인 (동작 진행 단계) ¦ 분리 회로 단계 ¦ 부하 (기구, 설비 단계) ¦ 특별 보호 된 단계 ¦ ¦ 50 ¦ - ¦ - ¦ 12.5,24,25 30,42,48 ¦ ¦ 1.5 ¦ 0.8 ¦ 0.5 ¦ 0.33 ¦ ¦ 100 ¦ 66/115 ¦ 66 ¦ 60 ¦ - ¦ 2.5 ¦ 1.5 ¦ 0.8 ¦ 0.5 ¦ ¦ 150 ¦ 120/208 127/220 ¦ 115, 120 127 ¦ 110, 120 ¦ 220- 110 240 - 120 ¦ 4 ¦ 2.5 ¦ 1.5 ¦ 0.8 ¦ ¦ 300 ¦ 220/380, 230/400 240/415, 260/440 227/480 ¦ 220,230 240,260 277 ¦ 220 ¦ 440-220 ¦ 6 ¦ 4 ¦ 2.5 ¦ 1.5 ¦ ¦ 600 ¦ 347/600, 380/660 400/690, 415/720 480/830 ¦ 347,380,400 415, 440,480 500,577,600 ¦ 480 ¦ 960-480 ¦ 8 ¦ 6 ¦ 4 ¦ 2.5 ¦ ¦ 1 000 ¦ - ¦ 660 690,720 830,1000 ¦ 1000 ¦ - ¦ 12 ¦ 8 ¦ 6 ¦ 4 ¦ 71 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
91f181c4-2eb1-49f3-b2f6-2bc7b8c21a1a | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 참고 문헌 IEC 60364-5- 537 : 1981, 빌딩의 전기적 설치 - 제 5 부 : 전기적 설비의 선택과 설치 - 53 장 : 개폐 장치와 제어 장치 - 537 절 : 절연 및 개폐 장치 72 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
a7f9983f-577e-431f-a4ff-55af60657d40 | KSCIEC60439-1_2024확인_KR | 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
d83f7591-e337-4766-8fc2-da6eebcc0068 | KSCIEC60439-1_2024확인_KR | KS C IEC 60439-1:1999 KSKSKS KSKSK KSKS KSK KS KSK KSKS KSKSK KSKSKS Low-voltage switchgear and controlgear assemblies - Part 1: Type-tested and partially type-tested assemblies ICS 29.120.60 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
5b92319f-0379-4e36-8fd0-867b8309e1c0 | KSCIEC60364-5-53_KR | KSKSKSKS KS C IEC 60364 -5- 53 KSKSKSK KSKSKS KSKSK KSKS KSK K KS 저압 전기설비-제 5-53 부 : 전기기기의 선정 및 설치- 안전, 절연, 개폐, 제어 및 감시를 위한 보호장치 KS C IEC 60364 - 5 - 53:2019 산 업 표 준 심 의 회 2020 년 12 월 29 일 개정 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
3a69fa50-dab1-45e5-abae-fa846f57bb59 | KSCIEC60364-5-53_KR | KS CIEC 60364-5-53:2019 심 의 : 전기응용 기술심의 회 성 명 근 무 처 직 위 (회 장) 신 판 석 홍익대학교 교 수 (위 원) 권 오 화 KIC TECH 대 표 김 갑 일 명지대학교 교 수 김 재 희 한국산업기술시험원 수 석 박 효 성 한국화학융합시험연구원 연 구 위 원 박 현 주 한전 전력연구원 책 임 서 호 선 케이알 지식재산법률사무소 대 표 이 주 철 대한전기협회 처 장 임 영 민 전자부품연구원 수 석 장 우 진 서울과 학기술대학교 교 수 조 두 희 한국전자통신연구원 책 임 (간 사) 김 원 석 국가기술표준원 표준정책국 전기전자정보표준과 연 구 관 원안작성 협력기관 : 저압전기설비 전문위원회 성 명 근 무 처 직 위 (대표전문위원) 김 재 철 숭실대학교 교 수 (위 원) 이 주 철 대한전기협회 처 장 김 세 동 두원공과 대학교 교 수 이 창 열 한국전력공사 처 장 신 석 하 (주)엘엠솔루텍 부 사 장 정 우 성 (주)동서엔지니어링 상 무 송 인 권 슈나이더일렉트릭코리아 부 장 김 영 석 한국전기안전공사 전기안전연구원 책 임 연 구 원 이 기 홍 한국토지주택공사토지주택연구원 수 석 연 구 원 박 원 석 ABB 코리아 부 장 신 효 섭 (주)더힐코리아 회 장 이 강 수 (주)옴니엘피에스 상 무 주 문 노 한국전기연구원 책 임 연 구 원 안 준 호 한국전기산업연구원 실 장 신 성 수 대한전기협회 팀 장 류 기 환 대한전기협회 과 장 표준열람: e 나라 표준인증(http://www.standard.go.kr) ¦ 제 정 자 : 제 ¦ 산업표준심의 회 위원장 담당부처 : 산업통상자원부 국가기술표준원 ¦ ¦ --- ¦ --- ¦ ¦ 정 : 2002 년 7 월 26 일 심 의 : 산업표준심의 회 전기응용 원안작성협력 : 저압전기설비 전문위원회 ¦ 개 정 : 2020 년 12 월 29 일 기술심의 회(C) ¦ 이 표준에 대한 의견 또는 질문은 e 나라 표준인증 웹사이트를 이용하여 주십시오. 이 표준은 산업표준화법 제 10 조의 규정에 따라 매 5 년마다 산업표준심의 회에서 심의 되어 확인, 개정 또는 폐지됩니다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
43c09cfe-186c-431a-92ec-1c7631d3fdf0 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 목 차 머 리 말 ................................. 개 요 ............................... IV 530.1 적용범위 .............. 1 530.2 인용표준 ................ 1 530.3 용어와 정의 ___________ 530.4. 일반 및 공통 (서분 ~ ~ ~ ~ ~ ~ 7 530.5 기기의 설치 7 - 531 전원의 자동차단에 의한 고장보호장치 ...................) 531.1 과전류 보호장치 - 8 531.2 누전 차단기(RCD, Residual Cumen_porediaDevice)___________________________C 8 531.3 절연 감시 장치 ... ........................ 9 532 열 영향에 대한 보호장치 및 예방 조치 ........................... 10 532.1 일반사항 .......... 10 10 532.2 화재 위험이 있는 - - 532.3 아크 고장 검출장치(AFDD,Arc Fault Detection Devices)의 선정. ......................................... 11 533 과전류 보호장치 ......... 11 533.1 일반 요구사항 ····_ 11 533.2 과부하 전류 보호장치의 선정 ...................... 13 533.3 단락 전류에 대한 보호장치의 선정 ............................. 14 533.4 과전류 보호장치의 위치 ······················· 15 533.5 과부하 및 단락 보호 기능들의 협조______________________ 16 534 과도 과전압에 대한 보호장치 ........... 17 534.1 일반사항 ·············· 17 534.2 공백 ····················· 17 534.3 공백 .................... 17 534.4 SPD 의 선정과 설치 17 535 보호장치들의 협조 .... 31 535.1 과전류 보호장치 사이의 선택성 ...................... 31 535.2 누전차단기와 OCPD 간의 ............... 33 535.3 누전차단기 사이의 선택성 ................ 33 535.4 RCD 와 OCPD 의 선택성 ------------- 33 535.5 OCPD 의 결합된 단락 ⌀20-000 - 33 -i- 2 07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및무단배포를 금합니다. | {}
163d6df8-ae71-4cfd-815c-7f9c9c58dda5 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 536 절연 및 개폐 ................. 34 536.2 절연 ··················· ----- 34 536.3 기계의 유지 보수를 위한 전원 차단(privingoil)............... 36 536.4 비상 개폐 ....... 37 536.5 기능적 - 38 537 감시 ...................... 39 537.1 일반사항 .............. 39 537.2 연속 전원을 위한 IT -------- 39 537.3 공공 배전 IT 계통 ················ 40 537.4 TN, TT 및 IT 계통의 오프라인 시스템 .................................. 40 부속서 A(참고) 과부하 보호 장치의 설치위치 .............................. 42 A.1 일반사항. ························· - 42 A.2 과부하 보호가 분기 회로의 기점에 위치하지 않아도 되는 사례 ................................................... 42 부속서 B(참고) 단락 보호 장치의 설치위치. ················ www.conationao.com/shotosmationalized 44 B.1 일반사항. ・・・・・・・・・・・・・ ··················· 44 B.2 단락 보호가 분기 회로의 기점에 위치하지 않아도 되는 사례 ------------------------ 44 부속서 C(참고)SPD 설치 - 계통 구성에 따른 설치도의 예 100011100011000000111100000001001001001110000000000 46 C.1TT 계통 - 3 상 전원과 중성 ················· 46 50 C.2 TN-C 및 TN-C-S 계통 - 3 상 전_________________ C.3 TN-S 계통 - 3 상 전원과 중성 ................... 54 C.4IT 계통 - 중성이 있거나 없는 3 상 전원 ................................... 56 부속서 D(참고) 가공선로에 의해 공급되는 설비 ................................. 59 부속서 E(인용) 절연 및 개폐 장치의 참조 표준 .................................. 60 부속서 F (참고) 특정 국가들에 관한 비고 등록...................... 62 참고문헌 ............................... 70 -ii- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
5c7fbd33-1ded-447b-a75e-4e6b300948f4 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 머 리 말 이 표준은 저작권법에서 보호 대상이 되는 저작물이다. 이 표준의 일부가 기술적 성질을 가진 특허권, 출원공개 이후의 특허출원, 실용신안권 또는 출원공개 후의 실용신안등록출원에 저촉될 가능성이 있다는 것에 주의 를 환기한다. 기술표준원장 및 산업표준 심의 회는 이러한 기술적 성질을 가진 특허권, 출원공개 이후의 특허출원, 실용신안권 또는 출원공개 후의 실용신안등록출원에 관계되는 확인에 대하여 책임을 지지 않는다. -iii- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f9005d8a-9120-403a-a1d5-a0e6c275a660 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 개 요 이 표준은 2019 년에 제 4 판으로 발행된 IEC 60364 - 5- 53, Low-voltage electrical installations- Part 5 - 53 : Selection and erection of electrical equipment - Devices for protection for safety, isolation, switching, control and monitoring 을 기초로, 기술적인 내용 및 대응국제표준의 구성을 변경하지 않고 작성한 한국산업표준이다. - iv- 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
95caeba9-822b-4376-b518-0431cb7aead5 | KSCIEC60364-5-53_KR | 한국산업표준 KS C IEC 60364-5-53:2019 저압 전기설비-제 5-53 부 : 전기기기의 선 정 및 설치-안전, 절연, 개폐, 제어 및 감시를 위한 보호장치 Low-voltage electrical installations - Part 5-53 : Selection and erection of electrical equipment - Devices for protection for safety, isolation, switching, control and monitoring 530.1 적용범위 이 표준은 다음 사항에 대한 요구사항을 제공한다. a) 절연, 개폐, 제어 및 감시 b) 다음의 선정 및 설치 1) 절연, 개폐, 제어 및 감시를 위한 장치 2) 안전보호조치를 준수하기 위한 장치 530.2 인용표준 다음의 인용표준은 이 표준의 적용을 위해 필수적이다. 발행연도가 표기된 인용표준은 인용된 판만 을 적용한다. 발행연도가 표기되지 않은 인용표준은 최신판(모든 추록을 포함)을 적용한다. KS C IEC 60204-1, 기계류의 안전성-기계의 전기 장비-제 1 부 : 일반 요구사항 KS C IEC 60269-2, 저전압 퓨즈-제 2 부: 전문가용 퓨즈의 추가 요구사항(산업용) KS C IEC 60269-3, 저전압 퓨즈-제 3 부: 비전문가용 퓨즈의 추가 요구사항(가정용 및 유사용도의) KS C IEC 60269-4, 저전압 퓨즈-제 4 부: 반도체 소자의 보호용 퓨즈 링크의 추가 요구사항 KS C IEC 60309 (모든 부), 산업용 플러그, 콘센트 및 커플러 KS C IEC 60364 (모든 부), 저압 전기설비 KS C IEC 60364-4-41:2005, 저압 전기설비-제 4-41 부 : 안전을 위한 보호-감전에 대한 보호 KS C IEC 60364-4-42:2010, 저압 전기 설비-제 4-42 부: 안전을 위한 보호-열 영향에 대한 보호 KS C IEC 60364-4-43:2008, 저압 전기설비-제 4-43 부: 안전을 위한 보호-과전류에 대한 보호 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 1 | {}
e99f7262-c8df-4455-8382-d28f229ba10a | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 KS C IEC 60364-4-44:2007, 저압 전기설비-제 4-44 부: 안전을 위한 보호- 전압 및 전기자기 방해에 대한 보호 KS C IEC 60364-5-55, 저압 전기설비-제 5-55 부: 전기기기의 선정 및 설치-기타 기기 KS C IEC 60364-6:2016, 저압 전기설비-제 6 부: 검증 KS C IEC 60664-1:2007, 저압기기의 절연협조-제 1 부 : 원칙, 요구사항, 시험 KS C IEC 60669-1, 가정용 및 이와 유사한 용도의 고정 전기 설비용 스위치-제 1 부: 일반 요구사항 KS C IEC 60669-2-1, 가정용 및 이와 유사한 용도의 고정 전기설비용 스위치-제 2-1 부: 전자스위치 개별 요구사항 KS C IEC 60669-2-2, 가정용 및 이와 유사한 용도의 고정 전기설비용 스위치 -제 2-2 부: 개별요구사 항-원격 제어 스위치(RCS) KS C IEC 60669-2-3, 가정용 및 이와 유사한 용도의 고정 전기설비용 스위치 -제 2-3 부: 개별 요구사 항-시간 지연 스위치(TDS) KS C IEC 60884 (모든 부), 가정용 및 이와 유사한 용도의 플러그와 콘센트 KS C IEC 60898 (모든 부), 가정용 및 이와 유사한 용도의 과전류 보호용 차단기 KS C IEC 60906 (모든 부), 가정용 및 이와 유사한 용도의 IEC 표준 플러그와 콘센트 KS C IEC 60947-2:2016, 저전압 개폐장치 및 제어장치-제 2 부: 차단기 KS C IEC 60947-4-1, 저전압 개폐장치 및 제어장치-제 4-1 부: 접촉기 및 모터기동기-전자식 접촉기 및 모터기동기 KS C IEC 60947-4-3, 저압개폐장치 및 제어장치-제 4-3 부: 접촉기 및 모터기동기-비 모터부하용 AC 반도체 제어기와 접촉기 KS C IEC 60947-5-1, 저압개폐장치 및 제어장치-제 5-1 부: 제어회로 소자 및 개폐소자-전기기계적 제어 회로 소자 KS C IEC 60947-6-1, 저전압 개폐장치 및 제어장치-제 6-1 부: 다기능 기기-절체개폐기 KS C IEC 60947-6-2, 저전압 개폐장치 및 제어장치-제 6-2 부: 다기능 기기-제어 및 보호 개폐 장치 (또는 설비) KS C IEC 61008 (모든 부), 주택용 및 이와 유사한 용도의 과전류 보호장치가 없는 누전차단기 (RCCB) KS C IEC 61009 (모든 부), 주택용 및 이와 유사한 용도의 과전류 보호장치를 가진 누전차단기 (RCBO) KS C IEC 61095, 가정용 및 이와 유사 용도의 전자식 접촉기 2 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
4af718c0-506e-415f-aa39-c08f0f293048 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 KS C IEC 61439-2, 저압 배전반 및 제어반 어셈블리-제 2 부: 전력배전반과 제어반 KS C IEC 61534 (모든 부), 전원 트랙 KS C IEC 61557-8, 교류 1000 V 및 직류 1500 V 이하 저압 배전계통의 전기적 안전성-보호 수단의 시험, 측정 또는 감시용 장치-제 8 부: IT 계통의 절연 감시장치 KS C IEC 61557-9, 교류 1000 V 및 직류 1500 V 이하 저압 배전계통의 전기적 안정성-보호 수단의 시험, 측정 또는 감시용 장치-제 9 부: IT 계통에서 절연고장 위치에 대한 장치 KS C IEC 61643-11, 저 전압 서지 보호장치-제 11 부: 저 전압 전력계통의 저 전압 서지 보호장치-요 구사항 및 시험방법 KS C IEC 61643-12, 저 전압 서지 보호장치-제 12 부: 저압 배전계통 보호용-선정 및 지침 KS C IEC 62305 (모든 부), 피뢰 시스템 KS C IEC 62423, 가정용 및 이와 유사한 용도의 과전류보호 겸용/비겸용 B 형 누전차단기 KS C IEC 62606, 사고아크 검출장치에 대한 일반조건 IEC 60364-4-41:2005/AMD1:2017 IEC 60364-4-44:2007/AMD1:2015 IEC 60417 (all parts), Graphical symbols for use on equipment IEC 60669-2-4, Switches for household and similar fixed electrical installations - Part 2-4: Particular requirements - Isolating switches IEC 60669-2-5, Switches for household and similar fixed electrical installations - Part 2-5: Particular requirements - Switches and related accessories for use in home and building electronic systems (HBES) IEC 60669-2-6, Switches for household and similar fixed electrical installations - Part 2-6: Particular requirements - Fireman's switches for exterior and interior signs and luminaires IEC 60670-24, Boxes and enclosures for electrical accessories for household and similar fixed electrical installations - Part 24: Particular requirements for enclosures for housing protective devices and other power dissipating electrical equipment IEC 60947-3, Low-voltage switchgear and control gear - Part 3: Switches, disconnectors, switch- disconnectors and fuse-combination units IEC 60947-4-2, Low-voltage switchgear and controlgear - Part 4-2: Contactors and motorstarters - AC semiconductor motor controllers and starters IEC 60947-4-3, Low-voltage switchgear and controlgear - Part 4-3: Contactors and motorstarters - AC semiconductor controllers and contactors for non-motor loads IEC 61439-6, Low-voltage switchgear and controlgear assemblies - Part 6: Busbar trunking systems (busways) IEC 61984:2008, Connectors - Safety requirements and tests 3 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
48574dc2-2ff8-444c-9c81-35592f55e3ff | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 IEC 61995 (all parts), Devices for the connection of luminaires for household and similar purposes IEC 62020, Electrical accessories - Residual current monitors for household and similar uses(RCMs) IEC 62208, Empty enclosures for low-voltage switchgear and controlgear assemblies - General requirements IEC 62626-1, Low-voltage switchgear and controlgear enclosed equipment - Part 1: Enclosed switch- disconnectors outside the scope of IEC 60947-3 to provide isolation during repair and maintenance work 530.3 용어와 정의 이 표준에는 다음과 같은 용어와 정의 가 적용된다. ISO 와 IEC 는 다음의 주소에서 표준화를 위해 용어 데이터 베이스를 유지한다. · IEC Electropedia: http://www.electropedia.org/ · ISO Online browsing platform: http://www.iso.org/obp 530.3.1 단로기 개방 상태일 때 절연 기능에 지정된 요구사항을 준수하는 기계적 개폐 장치 비고 단로기는 무시할만한 전류를 끊거나 연결할 때, 혹은 단로기의 각 극의 단자 양단 전압의 상당한 변화가 발생하지 않을 때 회로를 열고 닫을 수 있다. 또한, 정상 회로 조건 하에서 전류를 흘릴 수 있고 단락 회로와 같은 비정상 조건 하에서 지정된 시간 동안 전류를 흘릴 수 있다. [출처: IEC 60050-441 1984 / AMD1:2000, 441-14-05] 530.3.2 개폐 단로기 개방 상태에서 단로기에 규정된 분리 요구 사항을 충족시키는 개폐기 [출처: IEC 60050-441:1984, 441-14-12] 530.3.3 기계적 개폐기 규정된 운전 과부하 조건을 포함할 수 있는 정상 회로 조건에서 기계적 동작에 의해 제어되는 접점 을 통해 전류를 투입, 운반 및 차단할 수 있으며, 또한 단락과 같은 특정 비정상 회로 조건에서 지정 된 시간 동안 전류를 전달할 수 있는 장치 비고 개폐기는 전류를 투입할 수는 있으나 단락전류를 차단할 수는 없다. [출처: IEC 60050-441:2000, 441-14-10] 4 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b4652ec9-fc43-43c4-b250-6398a576ef46 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 530.3.4 기계적 유지보수를 위한 전원 차단 기기가 전기로 동작하지 않을 때 감전이나 아크로 인한 위험 이외의 위험 방지를 위해 전기기기의 품목 혹은 품목들을 비활성화하기 위한 개폐기 장치의 개방 동작 [출처: IEC 60050-826:2004, 826-17-02] 530.3.5 비상 전원 차단 위험한 상황을 피하거나 완화하기 위해 전기 설비에서 전력을 제거하기 위한 개폐장치의 개방 동작 [출처: IEC 60050-826:2004, 826-17-03] 530.3.6 비상 정지 동작이 위험하게 되면 가능한 한 빨리 정지시키는 동작 [출처: IEC 60050-826:2004, 826-17-04] 530.3.7 기능적 개폐 정상적인 운영 목적을 위해 전기 설비 또는 그 일부에 대한 전기 에너지 공급을 켜거나 끄고 혹은 변화시키는 동작 530.3.8 SPD 조합체 계통접지 형태에 대해 필요한 과전압 보호 기능을 제공하며, SPD 제조자가 요구하는 모든 SPD 분리 기를 포함하는 하나의 SPD 또는 여러 SPD 세트 530.3.9 SPD 분리기 전력 계통에서 SPD 혹은 SPD 의 일부를 분리하는 장치 비고 이 장치에는 안전을 위한 분리 기능이 요구되지 않는다. 계통의 지속적인 고장을 방지하고 SPD 의 고장을 나타내는데 사용된다. 분리기는 내장형 또는 외장형(제조자에 의해 요구됨)일 수 있다. 분리기에 하나 이상의 기능이 있을 수 있다, 예를 들어 과전류 보호와 열 보호 기능 이 함께 있을 수 있다. 이 기능들은 각기 다른 장치에 존재할 수도 있다. [출처: IEC 61643-11:2011, 3.1.28] 530.3.10 SPD 의 보호 모드 보호 부품이 포함된 단자 간에 의도된 전류 경로. 예를 들어 선간, 상-대지, 상-중성점, 중성점-대지 5 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
646281e0-cc1f-43c2-b764-6277a493ee39 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 [출처: IEC 61643-11:2011, 3.1.8] 530.3.11 속류 차단 정격 Ifi 분리기가 동작하지 않고 SPD 가 차단할 수 있는 예상 단락 전류 [출처: IEC 61643-11:2011, 3.1.39] 530.3.12 정격 단락 전류 ISCCR 규정된 분리기와 함께 SPD 의 정격이 결정된 전력계통에서의 최대 예상 단락전류 [출처: IEC 61643-11:2011, 3.1.27] 530.3.13 전압 보호 수준 Up 정의 된 전압 기울기의 임펄스 스트레스와 주어진 진폭 및 파형을 갖고 있는 방전전류의 임펄스 스트 레스로 인한 SPD 단자에서의 최대 기대 전압 비고 전압 보호 수준은 제조자에 의해 주어지며 다음을 초과 하지 않을 수도 있다. · 시험 등급 I 및/또는 II 에 대해 각각, In 및/또는 Iimp 에 대응하는 진폭에서 잔류 전압 측정으로 결 정된 측정 제한 전압 과 파두섬락전압을 위해(적용 가능하다면)정해진 측정 제한 전압. · 시험 등급 III 에 대해 조합 파형을 위해 측정된 조합파 발생기의 개방 회로 전압(U�)에서 측정된 제한 전압 [출처: IEC 61643-11:2011, 3.1.14] 530.3.14 정격 임펄스 전압 Uw 제조자가 기기 또는 기기의 일부에 부여한 임펄스 내전압 값으로, 과도 과전압에 대한 절연체의 규 정된 내력특성을 나타낸다. [출처: IEC 60664-1:2007, 3.9.2] 530.3.15 최대 연속 운전 전압 Uc 최대 RMS 전압, SPD 의 보호 모드에 연속적으로 적용될 수 있다. 6 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f1c25309-4323-4814-af7e-0a7aff239665 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 비고 1 참고: 이 표준이 다루는 Uc 값은 1,000 V 를 초과 할 수도 있다. [출처: IEC 61643-11:2011, 3.1.11] 530.3.16 등급 II 시험을 위한 공칭 방전 전류 In 8/20 �s 의 전류 파형을 갖는 SPD 를 통과 한 전류의 파고 값 [출처: IEC 61643-11:2011, 3.1.9] 530.3.17 등급 I 시험을 위한 임펄스 방전 전류 Iimp 규정된 전하 전달 Q 및 특정 시간동안 규정된 에너지 W/R 로 SPD 를 통과 한 방전 전류의 파고 값 [출처: IEC 61643-11:2011, 3.1.10] 530.3.18 2-포트 SPD 별도의 입력 및 출력 연결부 사이에 특정 직렬 임피던스가 연결된 SPD [출처: IEC 61643-11:2011, 3.1.3] 530.4. 일반 및 공통 요구사항 530.4.1 보호, 절연, 개폐, 제어 및 감시를 위한 기기는 설비의 의도된 사용을 위한 안전과 기능을 제공하기 위해 선정 및 설치되어야 한다. 이러한 기기는 이 표준에 명시된 요구사항과 KS C IEC 60364 의 다른 부에 있는 관련 요구사항의 준 수가 가능하도록 선정 및 설치 되어야 한다. 530.4.2 536.2.2.7 및 536.5.1.2 에 규정된 경우를 제외하고 독립적으로 동작하는 단극 보호 또는 개폐장치를 중성선에 삽입해서는 안 된다. 530.4.3 두 개 이상의 기능을 제공하는 장치는 각각의 개별 기능에 적절한 이 표준의 모든 요구 사항을 준수 해야 한다. 530.5 기기의 설치 7 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사및 무단 배포를 금합니다. | {}
69d384c4-3867-44b8-9a92-72d64cb6df73 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 530.5.1 배선과 기기 사이의 접속은 기기의 예정된 사용으로 발생하는 과도한 인장이나 압력을 받지 않는 방 법으로 설치되어야 한다. 530.5.2 밀폐되지 않은 유형의 기기는 적절한 설치함 또는 관련 표준에 부합하는 외함에 설치되어야 한다. 비고 관련 표준의 예시는 KS C IEC 60670 (모든 부), KS C IEC 62208, KS C IEC 61439 (모든 부), 및 KS C IEC 61084 (모든 부) 이다. 531 전원의 자동차단에 의한 고장보호장치 531.1 과전류 보호장치 531.1.1 TN 계통 TN 계통에서 과전류 보호장치는 KS C IEC 60364-4-41:2005, 434.2 및 431 에 따라 선정 및 설치하고 단락 보호장치의 경우 533.3 에 규정된 조건에 따라 선정 및 설치하면서 KS C IEC 60364-4-41:2005, 413.1.3.3 의 요구 사항을 충족해야 한다. 531.1.2 TT 계통 검토 중 531.1.3 IT 계통 노출 도전부가 상호 접속하고 있는 경우, 제 2 고장 발생 시 과전류 보호장치는 KS C IEC 60364-4- 41:2005, 413.1.5.5 의 요구 사항을 고려하여 531.1.1 에 부합해야 한다. 531.2 누전 차단기(RCD, Residual Current protective Devices) 531.2.1 일반 설치 조건 직류 계통에서 누전 차단기는 직류 잔류 전류를 검출하고 정상 상태 및 고장 조건에서도 회로 전류 를 차단할 수 있도록 특별히 설계해야 한다. 531.2.1.1 누전 차단기는 피보호 회로의 모든 충전선을 차단해야 한다. TN-S 계통에서, 전원 조건이 만약 중성선이 대지 전위에 있는 것으로 간주할 수 있는 경우에는 중성선을 분리할 필요가 없다. 비고 중성선이 대지 전위에 있다는 것을 검증하는 조건은 현재 검토 중 531.2.1.2 보호도체는 누전 차단기의 자기 회로를 통과 해서는 안 된다. 531.2.1.3 접속된 부하의 통상 동작 시 예상되는 누설 전류가 장치에서 불필요한 트립을 야기하지 않 도록 누전 차단기를 선정하고 회로를 소분할 해야 한다. 비고 누전 차단기는 잔류 전류가 정격 동작 전류의 50 %를 초과 하는 경우에 동작할 수 있다. 8 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
38bed1ef-2560-491b-a799-7672e9bdfa26 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 531.2.1.4 직류 성분의 영향 검토 중 531.2.1.5 보호도체가 없는 회로에 연관된 누전 차단기를 사용할 경우, 정격 동작 잔류 전류가 30 mA 이하라 하더라도 간접 접촉에 대한 충분한 보호가 이루어진 것으로 간주하지 않는다. 531.2.2 적용 방법에 따른 보호장치의 선정 531.2.2.1 531.2.2.2 의 요구 사항을 고려했을 때, 누전 차단기는 보조 전원이 있을 수도 없을 수도 있 다. 비고 보조 전원은 전원 계통 이어도 무방하다. 531.2.2.2 보조 전원 고장 시 자동 동작하지 않는 보조 전원을 갖춘 누전 차단기는 다음의 두 가지 조건 중 어느 하나가 충족하는 경우에만 사용 가능하다. - 보조 전원 고장 시에도 KS C IEC 60364-4-41:2005 의 413.1 에 따른 간접 접촉 보호 조치가 보장 된다. - 장치를 기능자(BA4) 또는 숙련자(BA5)가 조작, 시험 및 검사하는 설비에 설치된다. 531.2.3 TN 계통 특정 기기 또는 특정 기기의 일부분이 KS C IEC 60364-4-41:2005, 413.1.3 에서 명시하는 조건 중 하 나 이상에 적합하지 않는 경우에는, 해당 부분을 누전 차단기로 보호할 수 있다. 이 경우 노출 도전 부가 누전 차단기의 동작 전류에 맞는 저항을 갖는 접지 전극에 접속되어 있다면 노출 도전부는 TN 접지 계통 보호도체에 접속할 필요가 없다. 따라서 피보호 회로는 TT 계통으로 취급하고 KS C IEC 60364-4-41:2005, 413.1.4 를 적용한다. 다만, 노출 도전부에 대한 개별 접지 전극이 없는 경우에는 누전 차단기의 전원 측에 노출 도전부와 보호도체를 접속해야 한다. 531.2.4 TT 계통 하나의 누전 차단기로 설비를 보호하는 경우, 누전 차단기는 설비의 전력 공급점에 설치해야 한다. 다만, 전력 공급점과 누전 차단기 사이의 설비부가 2 종 기기 또는 이와 동등한 절연을 사용함으로써 보호 요구 사항(KS C IEC 60364-4-41:2005, 413.2)에 부합하는 경우는 제외한다. 비고 복수의 공급점이 있는 경우에는 이 요구 사항을 각각의 공급점에 적용한다. 531.2.5 IT 계통 누전 차단기로 보호되고 초기 고장 시 전류가 차단되지 않는 경우, 누전 차단기의 잔류 비 동작 전 류는 초기 고장 시 상전선에 영향을 미치는 무시 가능한 임피던스의 대지로 순환하는 전류 이상이어 야 한다. 531.3 절연 감시 장치 비고 절연 감시 장치는 적절한 응답 시간으로 동작할 수 있다. 9 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
e5de5ca0-bb4a-438f-b16b-cbb366013141 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 413.1.5.4 에 따라 설치된 절연 감시 장치는 전기 설비의 절연을 지속적으로 감시하는 장치이다. 이 장치는 설비의 절연 수준의 급격한 감소를 측정하기 위한 것으로 제 2 고장 발생 전에 이 감소의 원인 을 발견하여 전원 차단을 피하기 위해 의도된 것이다. 따라서 관련 설비에 적합하도록 KS C IEC 60364-6-6:2016 의 6.4.3.3 에 명시된 값 이하로 설정한다. 절연 감시 장치는 열쇠나 공구를 사용하지 않으면 설정 값을 변경할 수 없도록 설계 또는 설치해야 한다. 532 열 영향에 대한 보호장치 및 예방 조치 532.1 일반사항 설치 지점에서 예상되는 모든 동작 조건에서 유해한 열 영향을 야기할 수 있는 열 또는 아크/불꽃의 안전한 방출을 허용하도록 장치를 장착해야 한다. 보호장치는 보호를 위해 회로의 공급점에 실용적을 가능한 선에서 최대한 가깝게 설치한다. 532.2 화재 위험이 있는 장소 532.2.1 일반사항 비고 화재 위험이 있는 장소는 KS C IEC 60364-4-42 에 정의 되 있다 고정 설비의 장치 또는 고정 설비에 통합되어 열 효과 에 대한 보호를 위해 사용되는 장치에는 자동 재설정이 제공되지 않아야 한다. 532.2.2 BD2, BD3 또는 BD4 외부영향을 받는 장소 대피용 장치를 제외하고 BD2, BD3 또는 BD4 외부 영향을 받는 장소의 배전반 및 제어반 장치는 인 가된 사람만 접근할 수 있어야 한다. 통로에 설치될 때, 배전반 및 제어반 장치는 IEC 60670-24, KS C IEC 61439-2, IEC 61439-3 또는 KS C IEC 62208 에 부합하며 외함에 설치되어야 한다. 532.2.3 BE2 외부영향을 받는 장소 532.2.3.1. 일반사항 다음과 같은 장소에 해당하는 등급의 보호를 제공하는 외함이 아닌 경우에는 보호, 제어 혹은 절연 을 위한 스위치기어는 외부 조건 BE2 가 보이도록 장소 밖에 설치되어야 한다. · IP4X · 먼지가 있는 IP5X · 전도성 먼지가 있는 IP6X 본질적으로 과열을 제한하도록 특별히 설계되지 않았을 경우, 모든 동작 모드에서 모터는 수동 초기 화가 있는 모터 보호장치를 통해 과도한 열로부터 보호받아야 한다. 532.2.3.2 누전차단기(RCD, Residual Current protective Devices)의 선정 10 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
dc78a925-f50a-482c-8f24-cb6d0da96d0e | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 과열 영향 보호를 위한 누전차단기가 필요한 경우 정격 잔류 전류는 KS C IEC 60364-4-42:2010 및 IEC 60364-42:2010/AMD1:2014, 422.3.9 에 부합해야 한다. 누전차단기들은 KS C IEC 61008(모든 부), KS C IEC 61009(모든 부), KS C IEC 62423 혹은 KS C IEC 60947-2 와 531.2.2 에 부합하여야 한다. 누전 차단기는 보호하는 회로에서 모든 충전선의 분리를 보장해야 한다. 532.2.3.3 IT 계통에서 잔류 전류 감시 장치(RCM, Residual Current Monitoring device)의 선정 화재 위험을 방지하기 위해 KS C IEC 60364-4-42:2010 및 IEC 60364-4-42:2010/AMD1:2014, 422.3.9 b)에 부합하여 RCM 이 선정될 때 정격 잔류 경고 수준은 300 mA 를 초과 하지 않고 예상 최초 고장 전류 보다 작거나 같아야 한다. 응답 전류 값을 합리적으로 낮게 설정해서 고장 시에 고장이 최대한 빨리 표시되는 것이 권장된다. RCM 은 IEC 62020 에 부합해야 한다. 532.2.3.4 IT 계통에서 절연 감시 장치(IMDs, Insulation Monitoring Devices)의 선정 화재 위험을 방지하기 위해 KS C IEC 60364-4-42:2010 및 IEC 60364-4-42:2010/AMD1:2014, 422.3.9 b)에 부합하여 IMD 가 선정될 때 응답 값은 100 �/V 이상이어야 하며, 전기 공급 장치가 있는 공영 배전 계통에서는 40 �/V 이상 혹은, 절연 실패 및 전부하가 없는 절연 저항의 50 % 이상이어야 한다. 응답 값을 합리적으로 높게 설정해서 고장 시에 고장이 최대한 빨리 표시되는 것이 권장된다. IMD 는 KS C IEC 61557-8 에 부합해야 한다. 532.3 아크 고장 검출장치(AFDD, Arc Fault Detection Devices)의 선정. 아크 방전에 대비하여 AFDD 가 KS C IEC 60364-4-42:2010 및 IEC 60364-4 42:2010/AMD1:2014, 421.7 을 준수하여 지정될 때 다음이 적용된다. · AFDD 는 KS C IEC 62606 에 부합한다. · AFDD 는 보호받기 위해 최종 회로의 기점에 설치된다. · AFDD 는 제조자의 안내에 따라 설치 및 조정된다. 비고 KS C IEC 62606 에 따른 AFDD 는 다른 보호 능력을 가지고 있을 수 있다. 예를 들어 과전류 보 호 및/또는 잔류 전류 보호. 533 과전류 보호장치 533.1 일반 요구사항 533.1.1 일반사항 533 절에 KS C IEC 60364-4-43 이 요구하는 과전류 보호장치의 선정 및 설치에 대한 요구사항이 규 정 되 있다. 기능자(BA4) 및 숙련자(BA5)외에 사람이 동작 할 수 있는 보호장치가 과전류 특성 설정에 접근할 수 11 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
ea378da1-f71b-4305-93da-d4a8f4d4274c | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 있는 보호장치일 경우에 이는 열쇠, 자물쇠, 도구, 비밀번호 사용 등 의도적인 행동으로만 접근이 되 고 그 설정의 결과 가 눈에 띄게 선정 혹은 설치되어야 한다. 533.1.2 규정 준수 533.1.2.1 일반사항 과전류에 대한 보호장치는 다음 규정 중 하나 이상과 부합해야 한다 · KS C IEC 60269-2 · KS C IEC 60269-3 · KS C IEC 60269-4 · KS C IEC 60898 (모든 부) · KS C IEC 60947-2 · IEC 60947-3 · KS C IEC 60947-6-2 · KS C IEC 61009 (모든 부) · KS C IEC 62423. 533.1.2.2 장치의 적용 가능성 전압 값이 식별된 IEC 60947-2 을 따른 회로 차단기가 기호 (IEC 60417-6363:2016-07-16) 혹은 기호 ⑭ 가 있으면 식별된 전압 값이나 그 이상일 때 IT 계통에서 사용하면 안 된다. 관련된 전압 값이 없는 IEC 60947-2 을 따른 회로 차단기가 기호 (IEC 60417-6363:2016-07-16) ⑭ IT 계통에서 사용하면 안 된다. 혹은 기호 가 식별되면 IEC 62423 은 과전류 보호가 있는 잔류 전류 동작 회로 차단기(RCBOs, Residual Current Operated circuit-Breakers)에만 적용된다. IEC 60947-3 은 퓨즈와 결합한 장치에만 적용된다. 예를 들어 개폐기-퓨즈, 퓨즈 개폐기, 단로기-퓨즈, 퓨즈-단로기, 개폐기-단로기-퓨즈 및 퓨즈-개폐기-단로기. 다음과 같은 장치들은 단락 전류에 대한 보호만 제공하므로 과부하 보호에 사용해서는 안 된다. · KS C IEC 60947-2:2014, 부속서 O 에 따른 순시 트립 차단기(ICB, Instantaneous trip Circuit- Breakers) · KS C IEC 60269-2 혹은 KS C IEC 60269-3 에 따른 aM 및 aR 타입 퓨즈 533.1.3 퓨즈 533.1.3.1 스크류형 베이스 퓨즈는 그 중심 접촉이 전원 측의 도체에, 외곽 접촉이 부하 측의 도체에 접촉하도록 연결해야 한다. 퓨즈 베이스는 퓨즈 캐리어로 인해 인접한 퓨즈 베이스에 속하는 전도성 부품들이 접촉하는 가능성 을 배제하도록 배치되어야 한다. KS C IEC 60269-3 에 따른 퓨즈 베이스는 더 높은 정격 전류의 퓨즈 링크 사용을 방지하는 게이지 피스와 함께 사용해야 한다. 게이지 피스는 보호 목적으로 퓨즈 계통 내에서 최대 정격 전류인 퓨즈 12 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
a1c3564c-24a4-4276-a977-7914102b4c45 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 -링크가 허용될 때 불필요하다. 직류 회로 또는 직류 응용 희로의 보호를 위해 직류 적합성이 표시된 퓨즈 계통(퓨즈-홀더, 퓨즈 베 이스)만 사용해야 한다. 533.1.3.2 기능자(BA4) 또는 숙련자(BA5) 이외의 사람이 제거하거나 설치할 수 있는 퓨즈 링크를 갖 춘 퓨즈는 KS C IEC 60269-3 을 따라야 한다. 기능자(BA4) 또는 숙련자(BA5)만이 제거하거나 교체할 수 있는 퓨즈 링크를 갖춘 퓨즈나 조합 유닛 은 충전부에 우연히 접촉되지 않고 퓨즈 링크를 확실히 제거하거나 교체할 수 있도록 설치해야 한다. 이 장치들은 일반 사람들이 접근할 수 없도록 설치되어야 한다. 533.2 과부하 전류 보호장치의 선정 533.2.1 일반사항 다음 요구사항을 충족하도록 보호장치를 선택해야 한다. a) 보호장치의 정격 전류 또는 전류 설정인 In 이 회로의 설계 전류 IB 보다 크거나 같음 b) 정격 전류 또는 전류 설정인 In 이 케이블의 전류 운반 용량보다 작거나 같음 c) 보호장치가 통상적인 시간내에 효과 적인 동작을 하기위한 전류 I2 가 케이블의 전류 운반 용 량에 계수 1.45 를 곱한 값 Iz 보다 작거나 같음 a), b) 및 c)의 준수가 특정 경우에는 보호를 보장하지 못한다. 예를 들어 I2 미만의 지속 과전류가 발 생하였을 때 단면적이 더 넓은 케이블을 고려하거나 Iz 보다 작거나 같은 I2 값을 가진 장치를 선정 한다. 비고 1 KS C IEC 60898(모든 부), KS C IEC 60947-2, KS C IEC 61009(모든 부)을 준수하는 보호장치 또는 KS C IEC 62423 을 준수하는 RCBO 는 b)를 적용하면 c)의 요구사항이 자동으로 충족된다. 보호기기의 효과 적인 동작을 보장하는 전류 I2 는 제조자가 제공한다. 보호장치의 통상적인 시간 내에 효과 적인 동작을 보장하는 전류는 제품 표준에 따라 Ir, It 또는 If 로 명명될 수 있다.I, 와 Is 는 둘 다 In 의 배수이며 올바른 값과 색인에 주의 하여야 한다. 중성선의 등가 구리 단면적이 상전선보다 작을 경우 KS C IEC60364-4-43 을 준수하여 중성선 과부 하 보호를 제공해야 한다. 이 요구사항을 위하여 중성선의 전류 운반용량을 알아야 한다. 일반적으로 제조자로부터 얻을 수 있다. 비고 2 중성선의 전류 운반 용량은 KS C IEC 60364-5-52:2009, 523 절에 따라서 같은 도체 단면적을 갖고, 설치와 건축 조건이 같은 회로의 중성선의 잔류 전류 운반 용량과 같은 것으로 볼 수 있다. 533.2.2 고조파 전류의 존재 고조파 전류가 존재하는 상태에서 올바르게 동작하기 위해 과부하 보호장치를 선택해야 한다. 533.2.3 병렬 도체들 사이의 불균등한 전류 분배 병렬 도체들 사이의 전류가 불균등할 때 각 도체는 533.2.1 에 따른 과부하 보호장치로 개별적으로 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 13 | {}
839f752f-0698-45ca-8674-f29ca429d278 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 보호받아야 한다. 533.3 단락 전류에 대한 보호장치의 선정 533.3.1 열 스트레스 533.3.1.1 케이블 및 절연된 도체 KS C IEC 60364-43:2008, 434.5 의 요구사항을 준수하기 위해서는 회로의 임의 의 지점에서 발생하는 단락으로 인해 발생하는 모든 전류에 대해 보호장치의 동작 시간은 도체의 절연으로 허용 가능한 최 고 온도가 되는 시간보다 같거나 낮아야 한다. 다음 식으로 계산된다. t≤(k · S/I)2 여기에서 t 보호장치의 동작 시간, s I RMS 로 나타낸 효력이 있는 단락 전류, A S 도체의 단면적, mm2 k 도체 재료의 저항성, 온도 계수 및 열 용량과 적절한 초기 및 최종 온도를 고려한 계수이다. 비고 1 위의 공식에 사용된 계수 k 의 설명과 값은 KS C IEC 60364-43 을 참조한다. 보호장치의 동작 시간이 <0.1 s(예: 전류 제한 장치)인 경우 보호기기의 이탈 에너지(rt)가 도체의 최 대 내에너지(K2S2)보다 작거나 같은 경우에 위의 요구사항을 적용해야 한다. Pt<kS2 비고 2 보호장치의 이탈 에너지는 제조자가 제공한다 533.3.1.2 모선 트렁킹 계통 및 파워 트랙 IEC 61439-6 을 준수하는 모선 트렁킹 계통 또는 KS C IEC 61534(모든 부)를 준수하는 파워트랙을 사용하는 경우 KS C IEC 60364-4-43:2008, 434.5.3 의 요구사항을 준수하기 위해 다음 조건 중 하나 를 따른 단락 보호장치를 선정해야 한다. · 보호장치의 최대 동작 시간은 모선 트렁킹 또는 파워트랙 계통에 대해 Icw(정격 단시간 내 전류)가 정의 된 최대 시간을 초과 하지 않아야 한다. · 모선 트렁킹 혹은 파워트랙 계통의 제조자에 따라 선정된 보호장치와 관련된 모선 트렁킹 또는 파 워트랙 계통의 정격 조건부 단락 전류, Icc 는 설치 지점에서의 예상 단락 전류보다 높거나 같아야 한다. 533.3.2 차단 용량 보호장치의 단락 차단 용량(Icu 또는 Icn)은 설치된 지점의 예상 최대 단락 전류와 같거나 그 이상이 어야 한다. 단, KS C IEC 60364-4-43:2008, 434.5.1 에 의해 허용된 경우 더 낮은 단락 용량을 선택할 수 있다. 특정 상황(예: 단락 전류를 차단한 후에 보호장치 사용이 적합하도록 의도된 경우)에서는 사용 단락 14 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
51d16f10-097f-48db-a351-7807f7d3fe27 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 차단 용량(Ics)에서 보호장치를 선택하는 것이 바람직할 수 있다. 비고 차단 용량은 다음과 같이 정의 된다. KS C IEC 60947-2 에서 - 사용 단락 차단 용량(Ics, service short-circuit breaking capacity): 지정된 시험 순서에 따른 조건들 이 정격 전류를 연속적으로 전달할 수 있는 차단기의 능력을 포함하는 차단 용량 - 최대 단락 차단용량(IcU, ultimate short-circuit breaking capacity) 지정된 시험 순서에 따른 조건들이 정격 전류를 연속적으로 전달할 수 있는 차단기의 능력을 포함하지 않는 차단 용량 KS C IEC 60898-1 및 KS C IEC 61009-1 에서 - 사용 단락 차단 용량(Ics, service short-circuit breaking capacity): 지정된 시험 순서에 따른 조건들 이 통상적인 시간 동안 차단기의 비-트립 전류를 0.85 배만큼 전달할 수 있는 능력을 포함한 차단 용량 - 정격 단락 용량(Icn, rated short-circuit capacity): 지정된 시험 순서에 따른 조건들이 통상적인 시간 동안 차단기의 비-트립 전류를 0.85 배만큼 전달할 수 있는 능력을 포함하지 않은 차단 용량 533.4 과전류 보호장치의 위치 533.4.1 일반사항 533.4.2 및/또는 533.4.3 의 예외를 적용하지 않는 한, 과부하 및/또는 단락 보호를 위해 KS C IEC 60364-4-3 에서 요구하는 장치는 각 회로의 공급점에 설치되어야 한다(부속서 A 참조). 533.4.2 과부하 방지를 위한 장치의 위치 533.4.2.1 KS C IEC 60364-43:2008, 533.4.2.2, 533.4.2.3, 533.4.2.4 또는 433.3 이 적용되는 경우를 제 외하고는 도체의 전류 전달 용량 값이 감소하는 각 지점에 과부하 방지를 위한 장치를 배치해야 한 다. 533.4.2.2 부터 533.4.2.4 의 요구사항은 화재 위험 또는 폭발 위험이 나타나는 장소에 위치한 설비에 적용되지 않는다. 비고 도체의 전류 운반 능력이 감소하는 것은 다음과 같은 예시 때문 일 수도 있다. · 도체 물질 · 도체 절연 물질 · 설치 방법 · 외부 영향 · 도체의 그룹화 533.4.2.2 다음과 같은 경우 도체를 과부하로부터 보호하는 장치를 도체 내에 연결할 수 있다. a) 전류 운반 용량 값의 감소가 발생하는 지점(533.4.2.1 참고)과 보호장치의 위치 사이에 분기 회로 나 콘센트가 없는 부분 b) 다음 두 가지 조건 중 적어도 하나를 충족한다. 1) KS C IEC 60364-4-43:2008, 434 절에 명시된 요구사항에 따라 단락 전류로부터 보호된다. 15 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
e975a75f-86ba-4770-be40-50ff96e4588f | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 2) 길이는 3 m 를 초과 하지 않고, 합선의 위험을 최소로 줄이는 방법으로 수행하며, 사람에게 화 재나 어떠한 위협의 위험을 최소로 감소하는 방식으로 설치된다(533.4.3.2 항 참조) 비고 1)에 따른 설치를 위해서는 그림 A.1 을, 2)에 따른 설치를 위해서는 그림 A.2 를 참고하라 533.4.2.3 다음의 경우 과부하에 대한 보호를 위한 장치가 필요 없다 a) 전원 측에 위치한 보호장치로 도체의 전류 운반 용량 값이 감소하는 부하지점에 위치한 도체가 효과 적으로 과부하에 대해 보호될 때 b) 혹은, 제조자가 과부하 장치를 제공하고 추가 과부하 보호가 제공되는 설비의 공급점과 주 배전 지점 사이의 설비 부분에 대한 보호를 제공하는 것에 동의 하는 경우 533.4.2.4 중성선이 없는 IT 계통에서 각 회로에 잔류 전류 보호장치가 설치된 경우 상전선 중 하나 에 과부하 보호장치를 생략할 수 있다. 533.4.3 단락 보호를 위한 장치의 위치 533.4.3.1 단락 보호를 위한 장치는 KS C IEC 60364-4 43:2008, 533.4.3.2, 533.4.3 또는 434.3 이 적 용되는 경우를 제외하고는 도체의 통과 에너지 허용량(K-S2)이 감소하는 지점에 배치해야 한다. 비고 도체의 통과 에너지 허용량(KS2)은 KS C IEC 60364-4-43:2008, 434.5 에 따라 결정된다. 533.4.3.2 및 533.4.3.3 의 요구사항은 화재 위험 또는 폭발 위험이 있는 위치에 위치한 설비에 적용 되지 않는다. 533.4.3.2 KS C IEC 60364-43:2008, 434.2.1 에 의해 허용된 경우, 단락에 대한 보호를 위한 장치는 다 음을 준수할 경우 533.4.3 에 명시된 곳 외에도 배치할 수 있다. a) 통과 에너지 허용량(K2S2) 감소가 있는 위치와 보호장치의 위치 사이에 분기나 콘센트가 없는 회로 의 일부 b) 도체의 부분이 1) 길이가 3m 를 넘지 않고 2) 단락의 위험을 최소한으로 줄이도록 설치되고 비고 1 이 조건은 예를 들어 배선의 외부 영향에 대한 보호를 강화함으로써 얻는다. 비고 2 그림 B.1 참조 3) 가연성 물질 근처에 배치되지 않는다. 533.4.3.3 KS C IEC 60364-4-43:2008, 434.5.2 에 따라 부하 측에 위치한 배선을 단락으로부터 보호하 는 동작 특성이 있는 경우 통과 에너지 허용량(K-2)이 감소된 지점의 전원 측에 보호장치를 배치할 수 있다. 비고 533.4.3.3 의 요구사항은 부속서 B 에 제시된 방법으로 충족시킬 수 있다. 533.4.3.4 배급사가 단락에 대한 보호를 제공하는 하나 이상의 장치를 설치하고 추가적인 단락 보호 가 제공될 때 그 장치가 공급점과 설비의 주 분배 지점 사이에 보호를 제공하는 것으로 합의 하면 단 락에 대한 보호를 설비의 공급점에서 제공할 필요는 없다 533.5 과부하 및 단락 보호 기능들의 협조 16 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f93ebbbb-06e8-4b2f-a8eb-bc315a5834ff | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 533.5.1 하나의 장치가 제공하는 보호 기능들 과부하 및 단락 전류에 대한 보호를 제공하는 보호장치는 533.1 부터 533.4 의 해당 요구사항을 충족 해야 한다. 533.5.2 개별 장치들이 제공하는 보호 기능들 과부하 보호장치와 단락 보호장치에 각각 533.1 부터 533.4 의 요구 사항이 적용된다. 또한 이러한 기기는 서로 조합하여 사용할 경우 기기의 적합성에 관련해서는 제조자의 지침이 있는 경우 제조자 의 지침에 따라 조정해야 한다. 534 과도 과전압에 대한 보호장치 534.1 일반사항 이 절은 KS C IEC 60364-4-44, KS C IEC 60664-1, KS C IEC 62305-1, KS C IEC 62305-4 및 KS C IEC 61643-12 에 명시된 사례들과 관련한 절연을 얻기 위하여 전압 제한 적용에 대한 규정을 담고 있다. 부속서 C 또한 참고한다. 이 절은 KS C IEC 60364-4-44:2007 의 443 절, KS C IEC 62305 시리즈 또는 달리 명시된 순간 과전압 에 대한 보호를 위한 SPD 의 선택 및 설치의 요구사항에 대해 주로 초점을 맞추고 있다. 이 절은 다음을 고려하지 않는다 - 설비에 연결된 장치에 통합될 수 있는 서지 보호 구성 요소 - 휴대용 SPD 비고 추가적인 정보는 KS C IEC 61643-12 에서 찾을 수 있다. 이 절은 AC 전원 회로에 적용된다. 적용 가능하다면 DC 전원 회로에도 이 절의 요구 사항을 적용할 수 있다. 534.2 공백 534.3 공백 534.4 SPD 의 선정과 설치 534.4.1 SPD 위치 및 SPD 시험 등급 SPD 는 최소한 설비의 공급점에 최대한 가깝게 설치해야 한다. 번개의 영향 및 개폐 과전압으로부터 보호를 위해서는 시험 등급 II SPD 를 사용해야 한다. 구조물에 외부 피뢰 시스템이 장착되어 있거나 직접 번개의 영향에 대한 보호장치가 달리 지정되어 있는 경우 시험 등급 I SPD 를 사용해야 한다. 구조물에 외부 피뢰 시스템이 장착되지 않은 경우와 마지막 극과 설비 입구 사이의 오버헤드 라인에 직접적인 낙뢰가 발생하는 경우를 고려할 때는 전기 설비의 시작점 또는 근처에는 부속서 D 를 참고 한 시험 등급 I SPD 를 사용해야 한다 비고 1 설비의 공급점은 건물에 전원이 들어오는 지점이나 주 배전반이 될 수 있다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 17 | {}
65c3932c-21f1-405d-bed6-133821c6ed48 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 비고 2 제품의 표준에 따르면 제품의 마킹은 다음과 같다. - 시험 등급 I : "test class I " 및/또는 U (사각형 안 T1) - 시험 등급 II : "test class II" 및/또는 ⑫ (사각형 안 T2) - 시험 등급 III : "test class III" 및/또는 T3" (사각형 안 T3) 534.4.4.2 에 따라 설비를 충분히 보호하려면 추가 II 등급 또는 시험 등급 III SPD 가 필요할 수 있으 며 고정 전기 설비의 후단에 위치해야 한다. 예를 들어, 보조 배전반 또는 콘센트가 있다. 이러한 SPD 는 설비의 공급점에 SPD 를 설치하지 않고 사용할 수 없으며, 전단에 위치한 SPD 와 조정되어야 한다. (534.3.3.5 참조) 시험 등급 I SPD 가 534.4.4.2 에 따른 보호를 제공하지 못하는 경우에는 조정을 한 시험 등급 II 또 는 시험 등급 III SPD 를 함께하여 요구되는 전압 보호 수준을 보장해야 한다. 추가 II 등급 또는 시험 등급 III SPD 는 표 1 에 따라 기기를 충분히 보호할 수 있도록 민감한 기기 근처에 필요할 수 있으며, 전단 쪽에 위치한 SPD 와 조정되어야 한다. 비고 3 이러한 추가 SPD 는 고정된 전기 설비 혹은 휴대용 SPD 의 일부 일 수 있다. 추가 SPD 는 다음과 같은 요소로 인한 위협에 대한 순간 과전압 보호용으로 중요할 수 있다. - 설비 내에 위치한 기기를 사용하여 전류에 의해 생성되는 개폐 과전압 - 전화선, 인터넷 연결과 같은 기타 수신 서비스에 대한 과전압 2 차 건물, 외부 설치/조명, 외부 센서 전원 공급 등 다른 구조물에 공급되는 기타 서비스에 대한 과전압 이러한 위협의 원점에 가능한 한 가까운 곳에 SPD 를 설치하는 것을 고려해야 하는 경우 관련 추가 정보는 KS C IEC 61643-12 에서 찾을 수 있다. ![image](/image/placeholder) At or near the origin Distribution circuits Close to sensitive equipment of the installation e.g. sub-distribution board e.g. main distribution board S S SP P P D D D Class I tested SPD Class II tested SPD Class II tested SPD and/or or or Class II tested SPD Class III tested SPD Class III tested SPD 그림 1 - 시험 등급 I II, III SPD 설비의 예 배전반의 후단에 설치된 SPD(예를 들어 콘센트)는 영구히 표시(예들 들어 라벨)되어야 한다. 18 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
16232ae2-f5be-421e-ac3b-e07c154be388 | KSCIEC60364-5-53_KR | KS CIEC 60364-5-53:2019 534.4.2 순간 과전압 보호 요구 사항 순간 과전압에 대한 보호는 다음에 해당된다. - 충전선과 PE 사이에(공통 모드 보호) - 충전선 사이에(차동 모드 보호) 비고 1 연결 형태 CT1 은 주로 공통 모드 보호를 제공한다. 만약 차동 모드 보호 또한 중요하면 이는 거의 모든 경우에서 충전선 사이에 추가적인 SPD 를 요구한다. 비고 2 연결 형태 CT2 는 공통 모드 보호와 차동 모드 보호의 조합을 제공한다. 충전선과 PE(중성선 있는 경우 중성 PE 까지 포함해서)사이의 보호는 필수적이다. 기기 보호를 보장하기 위해 상전선과 중성선(중성선 있는 경우) 사이의 보호가 권장된다. 상전선 사이의 보호는(여러 상이 있을 때) 선택 사항이다. 몇몇 기기는 공통 모드 보호(임펄스 내구성)와 차동 모드 보호(임펄스 내성)를 둘 다 요구할 수 있다. 비고 3 예를 들어, FE 연결 전자 등급 I 또는 II 기기는 개폐 또는 대기 기원으로 인한 순간 과전압 으로부터 전체적인 보호를 보장하기 위해 공통 모드와 차동 모드 보호가 필요하다. 534.4.3 연결 형태 연결 형태 CT1(예를 들어 3+0 또는 4+0 구성): 각각 충전선(가능하면, 상전선 및 중성선)과 PE 사이 혹은 각각 상전선과 PEN 사이에 보호 모드를 제공하는 SPD 조립 3 상 시스템에 적용하기 위한 연결 형태 CT1 의 두 가지 예는 그림 2 와 그림 3 과 같다. 연결 형태 CT2(예를 들어 3+1 구성): 각각 상전선과 중성선 그리고 중성선과 PE 사이에 보호 모드를 제공하는 SPD 조립 연결 형태 CT2 의 3 상 계통 적용 예시는 그림 4 와 같다. ![image](/image/placeholder) L1 L2 L3 N SPD SP SP SPD D D PE 그림 2- 중성선이 있는 3 상 계통 용 연결 형태 CT1(4+0 구성) 19 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
d3cf9c2e-82f5-4ee3-8b12-dc60b67b4533 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 ![image](/image/placeholder) L1 L2 L3 SP SP SPD D D PEN 그림 3 - 3 상 계통용 연결 형태 CT1(3+0 구성) ![image](/image/placeholder) L1 L2 L3 N SPD SP SP D D SPD PE 그림 4- 중성선이 있는 3 상 계통 용 연결 형태 CT2(예를 들어 3+1 구성) SPD 를 조립할 때 연결 형태에 따라 N 과 PE 사이에 연결된 SPD 에 대한 매개변수 선택에 주의 해야 한다. TN-S 또는 TN-C-S 계통인 경우, PE 에서 N 까지의 분리 지점과 설치된 SPD 위치 사이의 거리가 0.5 m 미만이거나 분리 지점과 SPD 가 동일한 배전반에 위치한 경우 중성극과 PE 사이의 SPD 가 생 략될 수 있다. 이 부속 절에 적용되기 위해, 상전선이 접지된 경우 기술적으로 중성선과 동등한 것으로 간주한다. 그러나 SPD 매개변수의 올바른 선택은 해당 경우에 특별한 고려사항이 필요하다. 534.4.4 SPD 의 선정 534.4.4.1 일반사항 SPD 의 선정은 다음과 같은 매개변수에 의한다. - 보호할 기기의 전압 보호 수준(Up)과 정격 임펄스 전압(Uw) (534.4.4.2 참조) - 연속 동작 전압(Uc). 예를 들어 전원 계통(TT, TN, IT)(534.4.4.3 참조) 20 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
79ba3b53-4009-4931-8c21-655cbf746cc1 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 - 방전 전류 (In) 와 임펄스 방전 전류 (Iimp) (534.4.4.4 참조) - SPD 조정(534.4.4.5 참조) - 예상 단락 전류(534.4.4.6 참조) - 속류 방해 정격(534.4.4.7 참조) SPD 들은 IEC 61643-11 에 부합해야 한다. 비고 선정과 응용에 관한 추가 정보들은 KS C IEC 61643-12 에서 주어진다. 534.4.4.2 기기 정격 임펄스 전압(Uw)의 기능으로서 전압 보호 수준(Up)의 선정 SPD 의 전압 보호 수준은 표 1 의 과전압 범주 II 의 정격 임펄스 전압에 따라 선정한다. 기기의 적절 한 보호를 제공하기 위해 충전선과 PE 사이의 전압 보호 수준은 표 1 에 따라 기기의 필요한 정격 임펄스 전압을 초과 해서는 안 된다. 비고 1 과전압 범주 III 또는 IV 기기만 보호할 경우 표 443.2 의 필요한 정격 임펄스 전압을 참조한 다. 직렬 연결 SPD(예를 들어 단일 모드 SPD, 선-중성 + 중성-PE, CT2 에 따른)에 의해 상전선과 PE 사 이에 보호가 제공되는 경우 이 직렬 연결은 위의 전압 보호 수준 요구사항을 충족해야 한다. 상도체와 PE 사이의 이러한 결합된 전압 보호 수준이 제조자의 데이터 시트에 제공되지 않는 경우 직렬로 연결된 개별 SPD 보호 모드에 대해 주어진 전압 보호 수준을 추가하여 계산해야 한다. SPD 가 제공하는 전압 보호 수준은 표 1 과 과전압 범주 II 에 따라 기기에 필요한 정격 임펄스 전압 의 80 %를 초과 하지 않는 것이 좋다. 그러나 어떤 경우에도 기기의 필요한 정격 임펄스 전압을 초과 해서는 안 된다. 이러한 보호 여분은 다음과 같은 사례에서는 중요하지 않다. - 기기가 SPD 에 직접 연결되었을 때 - 그림 9 에 따른 보호 계획이 이미 적용된 경우 - 전압 보호 수준 Up 를 위해 SPD 분기 회로의 과전류 보호에서 전압 강하가 이미 고려된 경우 - 과전압 범주 II 에 따른 보호가 제공되지만 이 위치에는 과전압 범주 III 또는 IV 기기만 설치된 경우 비고 2 KS C IEC 61643-12 는 기기의 정격 임펄스 전압 및 SPD 에 주어진 Up 대한 추가 정보를 제공 한다. 21 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
a09c03d3-f705-4457-888e-600c67bea731 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 표 1 - 기기의 요구 정격 임펄스 전압 ¦ 전원 계통 a 의 공칭 전압 3 상 계통 ¦ 전원 계통 a 의 공칭 전압 단상 계통 ¦ 아래 전압을 포함하는 전압 값이나 공칭 AC 에서 중성 으로 가는 선 전압 ¦ 기기의 요구 정격 임펄스 전압°(Uw) ¦ 기기의 요구 정격 임펄스 전압°(Uw) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 전원 계통 a 의 공칭 전압 3 상 계통 ¦ 전원 계통 a 의 공칭 전압 단상 계통 ¦ 아래 전압을 포함하는 전압 값이나 공칭 AC 에서 중성 으로 가는 선 전압 ¦ 과전압 범주 II 일때 (정상 정격 임펄스 전압인 기기) ¦ 과전압 범주 I 일때 (감소된 정격 임펄스 전압인 기기) ¦ ¦ V ¦ V ¦ V ¦ kV ¦ kV ¦ ¦ ¦ ¦ 50 ¦ 0.5 ¦ 0.33 ¦ ¦ ¦ ¦ 100 ¦ 0.8 ¦ 0.5 ¦ ¦ ¦ 120/240 ¦ 150 ¦ 1.5 ¦ 0.8 ¦ ¦ 230/400 277/480 ¦ ¦ 300 ¦ 2.5 ¦ 1.5 ¦ ¦ 400/690 ¦ ¦ 600 ¦ 4 ¦ 2.5 ¦ ¦ 1,000 ¦ ¦ 1,000 ¦ 6 ¦ 4 ¦ ¦ ¦ ¦ 1,500 DC ¦ 8b ¦ 6° ¦ ¦ a KS CIEC 60038 에 따라 ¦ a KS CIEC 60038 에 따라 ¦ a KS CIEC 60038 에 따라 ¦ a KS CIEC 60038 에 따라 ¦ a KS CIEC 60038 에 따라 ¦ ¦ b ¦ 60664-2-1:2011 의 부속서 D 에 따른 권장 값 KS CIEC ¦ ¦ --- ¦ --- ¦ ¦ C ¦ 정격 임펄스 전압은 충전선과 PE 사이에 적용된다 ¦ 오동작을 방지하긴 위해서 충전선 사이에 추가적인 SPD 가 필요할 수 있다. 기기 내성 및 가용성 요 구 사항에 따라 적절한 전압 보호 수준을 평가해야 한다. (KS C IEC 61643-12 참조) 하나의 SPD 조립으로 요구되는 전압 보호 수준을 도달할 수 없는 경우, 추가적인 SPD 를 요구되는 전압 보호 수준의 도달을 보장하기 위해 설치해야 한다. 534.4.4.3 연속 동작 전압(U。)에 관한 SPD 의 선정 교류에서는 SPD 의 최대 연속 동작 전압 Uc 가 표 2 의 요구보다 높거나 같아야 한다. 표 2- 전원 계통 조정에 따른 SPD 의 Uc ¦ 다음 사이에 설치된 SPD (적용 가능하면) ¦ 배전 네트워크의 계통 조정 ¦ 배전 네트워크의 계통 조정 ¦ 배전 네트워크의 계통 조정 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 다음 사이에 설치된 SPD (적용 가능하면) ¦ TN 계통 ¦ TT 계통 ¦ IT 계통 ¦ ¦ 상전선 과 중성선 ¦ 1,1U 또는 (0.64 x U) ¦ 1,1U 또는 (0.64 x U) ¦ 1,1 U V3 또는 (0.64 x U) ¦ ¦ 상전선 과 PE 선 ¦ 1,1U 또는 (0.64 x U) ¦ 1,1U 또는 (0.64 x U) ¦ 1.1 x U ¦ 22 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b93e4b80-461e-4906-b5d5-6a5d7f2b0568 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 ¦ 상전선 과 PEN 선 ¦ 1,1U 또는 (0.64 x U) ¦ N/A ¦ N/A ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 중성선과 PE 선 ¦ U a ¦ U V3 a ¦ 1,1 U V3 또는 (0.64 x U) ¦ ¦ 상전선 ¦ 1.1 x U ¦ 1.1 x U ¦ 1.1 x U ¦ 비고 1 N/A: 적용 불가 비고 2 U 는 저 전압 계통에서 선간 전압이다 a 이러한 값들은 최악의 경우의 고장 조건과 관련이 있다. 그러므로 10 %의 오차는 고려하지 않 았다. 534.4.4.4 공칭 방전 전류(I") 및 임펄스 방전 전류(Iimp)에 대한 SPD 의 선정 설비의 공급점이나 그 근처의 SPD 는 다음 중 하나의 경우와 부합해야 한다. - 건물이 직접 낙뢰에 대해 보호되는 경우, 설비 공급점의 SPD 는 534.4.4.2 및 표 4 에 따라 선정되 어야 한다. - 다른 경우일 때는 SPD 는 534.4.4.4.1 에 따라 선정되어야 한다. 설비 공급점이나 그 근처 SPD 의 후단에 설치된 추가 SPD 는 534.4.4.5 의 조정 요구사항에 부합해야 한다. 개폐로 인한 과전압은 지속 시간이 길어질 수 있으며 대기 근원의 순간 과전압보다 더 많은 에너지 를 포함할 수 있다. 이는 공칭 방전 전류와 임펄스 방전 전류에 대한 SPD 를 선정할 때 고려해야 한 다. 534.4.4.4.1 시험 등급 II SPD 설비 공급점이나 그 근처 SPD 에 시험 등급 II SPD 가 필요한 경우 그 공칭 방전 전류가 표 3 에 제 시된 값 이상이어야 한다. 표 3- 전원 계통과 연결 형태에 따른 공칭 방전 전류(I",KA) ¦ 연결 ¦ 전원 계통 ¦ 전원 계통 ¦ 전원 계통 ¦ 전원 계통 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 연결 ¦ 단상 ¦ 단상 ¦ 3 상 ¦ 3 상 ¦ ¦ 연결 ¦ CT1 ¦ CT2 ¦ CT1 ¦ CT2 ¦ ¦ L-N ¦ ¦ 5 ¦ ¦ 5 ¦ ¦ L-PE ¦ 5 ¦ ¦ 5 ¦ ¦ ¦ N-PE ¦ 5 ¦ 10 ¦ 5 ¦ 20 ¦ 534.4.4.4.2 시험 등급 I SPD 설비 공급점이나 그 근처 SPD 에 시험 등급 I SPD 가 필요한 경우 다음 경우 중 하나가 적용되어야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 23 | {}
2d285a54-3c94-4e1a-88cf-6e1413b5c29d | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 KS C IEC 62305-2 에 따른 위험 분석이 수행되지 않은 경우, 임펄스 방전 전류(Iimp)는 표 4 에 제시된 값 이상이어야 한다. 표 4- 건물이 직접 낙뢰에 대해 보호받을 때 임펄스 방전 전류(limp)의 선정 ¦ 연결 ¦ Iimp (kA) ¦ Iimp (kA) ¦ Iimp (kA) ¦ Iimp (kA) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 연결 ¦ 전원 계통 ¦ 전원 계통 ¦ 전원 계통 ¦ 전원 계통 ¦ ¦ 연결 ¦ 단상 ¦ 단상 ¦ 3 상 ¦ 3 상 ¦ ¦ 연결 ¦ CT1 ¦ CT2 ¦ CT1 ¦ CT2 ¦ ¦ L-N ¦ ¦ 12,5 ¦ ¦ 12,5 ¦ ¦ L-PE ¦ 12,5 ¦ ¦ 12,5 ¦ ¦ ¦ N-PE ¦ 12,5 ¦ 25 ¦ 12,5 ¦ 50 ¦ ¦ 비고 이 표는 낙뢰 보호 수준(LPL, lightning protection levels) III 및 IV 를 나타낸다 ¦ 비고 이 표는 낙뢰 보호 수준(LPL, lightning protection levels) III 및 IV 를 나타낸다 ¦ 비고 이 표는 낙뢰 보호 수준(LPL, lightning protection levels) III 및 IV 를 나타낸다 ¦ 비고 이 표는 낙뢰 보호 수준(LPL, lightning protection levels) III 및 IV 를 나타낸다 ¦ 비고 이 표는 낙뢰 보호 수준(LPL, lightning protection levels) III 및 IV 를 나타낸다 ¦ KS C IEC 62305-2 에 따른 위험 분석이 수행된 경우, 임펄스 방전 전류(Iimp)는 KS C IEC 62305 에 따 라 결정해야 한다. 534.4.4.5 두 개 혹은 그 이상의 SPD 간의 조정 설비의 SPD 조정을 확실히 해야 한다. SPD 간의 조정을 달성하는 방법에 대한 제조자의 지침은 KS C IEC 61643-12 를 참조해야 한다. 534.4.4.6 정격 단락 전류 ISCCR 에 관한 SPD 의 선정 일반적으로, 제조자가 명시한 대로 SPD 의 정격 단락 전류 ISCCR 은 SPD 조립의 연결 지점의 예상 최 대 단락 전류보다 낮지 않아야 한다. 그림 5 참조. 이 요구사항은 TN 또는 TT 계통의 중성선과 PE 사이에 연결된 SPD 에는 적용되지 않으며, 이 경우 에는 이미 제품 표준 KS C IEC 61643-11 에 의해 적용되었다. IT 계통에서 중성선과 PE 사이에 연결된 SPD 는 SPD 의 정격 단락 전류 ISCCR 이 이중 접지 고장이 발 생한 최악의 상항에서 SPD 연결지점상의 예상 최대 단락 전류 이상 이어야 한다. 534.4.4.7 속류 방해 정격에 대한 SPD 의 선정 일반적으로 SPD 의 속류 차단 정격 Ifi 를 제조자가 정한 경우 이는 SPD 조립의 연결 지점에서 최대 예상 단락 전류 이상이어야 한다. 그림 5 참조. 이 요구사항은 TN 또는 TT 계통에서 중성선과 PE 선 사이에 연결된 SPD 들에는 적용되지 않는다. 이 경우에는 이미 제품 표준 KS C IEC61643-11 에 의해 적용되었다. IT 계통에서 중성선과 PE 사이에 연결된 SPD 들은 제조자에 의한 SPD 속류 차단 정격 Ifi 가 최악의 상 황인 이중 접지 고장이 발생한 SPD 의 연결지점상의 예상 최대 단락 전류 이상이어야 한다. 24 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
100672e8-6626-41a5-bf5e-8ed746d32e16 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 ![image](/image/placeholder) A OCPD 1 E/I OCPD2 SPD SPDA B ¦ 여기에서 ¦ ¦ ¦ --- ¦ --- ¦ ¦ OCPD1 ¦ 설비의 과전류 보호장치 ¦ ¦ OCPD2 SPD ¦ SPD 제조자에 의해 요구되는 과전류 보호장치(SPD 분리기) ¦ ¦ SPD ¦ 서지보호장치 ¦ ¦ SPDA ¦ SPD 조합체 ¦ ¦ A & B ¦ SPD 조합체의 연결점 ¦ ¦ E/I ¦ 보호 대상 기기 혹은 설비 ¦ 그림 5 - SPD 조립의 연결 지점 534.4.5 과전류에 대한 SPD 의 보호 534.4.5.1 일 반 SPD 설비는 단락 전류를 고려하여 과전류로부터 보호되어야 한다. 이 보호장치는 제조자의 지침에 따라 SPD 의 내부 및/또는 외부일 수 있다. SPD 조합체를 보호하기 위한 외부 과전류 보호장치(OCPD, overcurrent protective device)의 정격 및 특성은 다음과 같이 선정되어야 한다. 434 절에 따르고 - 완전한 조합을 위한 높은 서지 전류 수용량을 보장하기 위해 가능한 높게 그러나 최대 과전류 보호를 위해 SPD 제조자의 설치 지침에서 요구되는 정격과 특성을 초과 하지 않 는다. 534.4.5.2 과전류 보호와 관련된 SPD 배치 SPD 를 보호하는 데 사용되는 과전류 보호장치의 위치는 설비 전원의 연속성과 설비내의 유효 전압 보호 수준에 영향을 미칠 수 있다. 비고 1 국가 위원회는 설비 유형에 따라 다음 중 어느 것을 선호할지 결정할 수 있다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 25 | {}
8ba06b3e-2178-4fa0-b186-7f3d63725bc8 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 a) SPD 용 과전류 보호장치가 SPD 분기 회로에 위치한 경우, SPD 고장 시 전원의 연속성은 영향을 받지 않지만 해당 보호장치 트립 후에는 설비와 기기 모두 발생 가능한 추가 과전압으로부터 보 호되지 않는다(그림 6 참조). 해당 배치에서는 SPD 와 직렬로 연결된 외부 과전류 보호장치의 전 압 강하에 의해 설비 내의 유효 전압 보호 수준이 증가한다. 비고 2 과전류에 대한 보호가 SPD 의 내부에 있다면 과전류 보호장치의 전압 강하가 이미 SPD 의 전 압 보호 수준 Up 에 포함되어 있다. ![image](/image/placeholder) A E/I OCPD SPD B ¦ 여기에서 ¦ ¦ ¦ --- ¦ --- ¦ ¦ OCPD ¦ SPD 제조자에 의해 요구되는 과전류 보호장치(SPD 분리기) ¦ ¦ SPD ¦ 서지보호장치 ¦ ¦ A 및 B ¦ SPD 조합체의 연결점 ¦ ¦ E/I ¦ 보호 대상 기기 혹은 설비 ¦ 그림 6- 전용 외부 과전류 보호장치를 사용한 SPD 분기의 과전류 보호 예시 b) SPD 용 과전류 보호장치가 SPD 분기 회로의 전단에 설치되어 있는 경우 SPD 고장 시 전원의 연 속성이 제공되지 않을 가능성이 있다(그림 7 참조). 그럼에도 불구하고 해당 배치에서 설비 내의 유효 전압 보호 수준은 최소로 유지된다. 단, 그림 6 에 따른 보호는 전단 과전류 보호장치(OCPD, overcurrent protective device)의 정격이 SPD 제조자가 권장하는 최대 과전류 보호장치보다 높을 때 적용되어야 한다. 26 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
50c34725-7e68-4a69-8de0-e893d156d284 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 ![image](/image/placeholder) A OCPD E/I SPD B ¦ 여기에서 ¦ ¦ ¦ --- ¦ --- ¦ ¦ OCPD ¦ SPD 보호에 사용되는 설비의 과전류 보호장치 ¦ ¦ SPD ¦ 서지보호장치 ¦ ¦ A 및 B ¦ SPD 조합체의 연결점 ¦ ¦ E/I ¦ 보호 대상 기기 혹은 설비 ¦ 그림 7 - SPD 보호에도 사용되는 설비의 일부인 보호장치들 534.4.5.3 과전류 보호장치 사이의 선택성 필요한 경우 SPD 설비의 설치 조건과 제조자가 제공한 정보에 따라 과전류 보호장치 사이의 선택성 을 고려해야 한다(KS C IEC 60364-53:2002 의 535 절 참조). 534.4.5.4 전단 장치의 서지 전류 내구성 SPD 설비의 전단에 설치된 대부분의 설비 장치(예: 계측기, 단자, 보호장치, 개폐기 등)에 대해서는 관련 제품 표준에서 요구하는 전용 서지 전류 내구성은 없다. 534.4.1 에 따라 공급점에 최대한 가까이 SPD 를 설치하면 후단 설치 장비를 통과 하는 서지 전류가 감소한다. 추가 정보를 위해서는 제조자의 정보뿐만이 아니라 KS C IEC 61643-12 도 참고한다. 534.4.6 고장 보호 KS C IEC 60364-41 에서 정의 한 고장 보호는 SPD 고장이 발생하더라도 보호받은 설비에서 유효하다. 전원의 자동 분리 시에는 - TN 계통의 경우 일반적으로 SPD 전원 측에 있는 과전류 장치에 의해 이 기능이 충족될 수 있다. TT 계통의 경우 다음에 의해 충족될 수 있다. a) RCD 의 후단에 SPD 설치 27 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c5bf352c-c7a2-4ec2-aec2-de0f0f75edef | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 b) 주 RCD 의 전단에 SPD 설치. 중성선과 PE 사이에 연결된 SPD 의 고장 가능성 때문에 KS C IEC 60364-41:2005 의 411.4.1 조건을 충족하며 연결 형태 CT2 에 따라 SPD 를 설치해야 한 다. - IT 계통에서는 추가적인 방법이 필요하지 않다. 설비의 공급점 혹은 그 근처의 서지 보호장치는 표 5 에 의해 연결되어야 한다. 표 5- 전원 계통에 따른 SPD 의 연결 ¦ SPD 조립의 연결 지점의 전원 계통 ¦ 연결 형태 ¦ 연결 형태 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ SPD 조립의 연결 지점의 전원 계통 ¦ CT1 ¦ CT2 ¦ ¦ TN 계통 ¦ X ¦ X ¦ ¦ TT 계통 ¦ 후단 RCD 에만 SPD ¦ X ¦ ¦ 중성이 있는 IT 계통 ¦ X ¦ X ¦ ¦ 중성이 없는 IT 계통 ¦ X ¦ N/A ¦ ¦ 비고 1X= 적용 가능 ¦ 비고 1X= 적용 가능 ¦ 비고 1X= 적용 가능 ¦ 비고 2 N/A = 적용 불가능 비고 철도 시스템, HV 전원 시스템, 모바일 장치 등이 적용되는 영향의 영역에 설치된 SPD 에는 추가 적인 요구사항이 적용될 수 있다. 534.4.7 RCD 와 연결된 SPD 설비 SPD 가 534.4.1 에 따라 설치되고 누전 차단기의 부하 측에 위치하는 RCD 는 시간 지연이 있거나 없 을 수 있지만 최소 3 kA 8/20 의 서지 전류에 내성이 있어야 한다. 비고 1 KS C IEC 61008-1 및 61009-1 에 따른 S-타입 RCD 는 이 요구사항을 만족한다. 비고 2 서지 전류가 3 kA 8/20 보다 높을 때는 RCD 가 전원 공급을 방해하며 트립 할 수 있다. 비고 3 민감한 기기를 보호하기 위해 추가 SPD 의 전단에 설치된 SPD 에는 적용하지 않을 수 있다. RCD 후단에 1 등급 시험이 된 SPD 의 설치는 권장하지 않는다. 534.4.8 SPD 의 연결 설비의 유효 전압 보호 수준은 SPD 의 연결과 배선 길이 및 SPD 자체의 배치와 필요한 SPD 단로기 에 따라 크게 달라진다. 보호해야할 SPD 와 외부 SPD 단로기 사이의 연결 만이 아니라 모든 도체와 관련선으로의 상호 연결 은 가능한 짧고 직선으로 유지해야 하며 불필요한 케이블 루프는 피해야 한다. 연결 도체의 길이는 그림 8 에서 정의 한 연결 지점 A 와 B 사이에있는 사용한 충전선으로부터 PE 까지 있는 도체들의 길이의 합으로 정의 된다. SPD 조립의 연결 지점들 사이에 있는 도체들의 총 배선 길이를 0.5 m 이하의 값으로 제한하는 것을 28 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
5306bb5a-e612-43da-9615-96024c151dcf | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 고려해야 한다(아래 그림 8 참조). ![image](/image/placeholder) A 충전선 길이 a OCPD 길이 b SPD 길이 C B PE ¦ 여기에서 ¦ ¦ ¦ --- ¦ --- ¦ ¦ OCPD ¦ 과전류 보호장치 ¦ ¦ SPD ¦ 서지 보호장치 ¦ ¦ PE conductor ¦ 보호적 접지 도체 ¦ ¦ A and B ¦ SPD 조립의 연결 지점 ¦ 비고 OCPD 가 없을 때 길이 b 는 0 이다 그림 8 - SPD 의 연결 이러한 요구사항을 충족하기 위해, 필요한 경우 중간 접지 단자를 추가하여 주 보호 도체를 SPD 에 가능한 가까운 곳에 위치한 접지 단자에 연결해야 한다(그림 9 의 도표 참조). 그림 9 에 따라서 연결되는 도체의 총 길이를 정하려면 다음 케이블의 길이는 고려하지 않는다. 주 접지 단자부터 중간 접지 단자까지 - 중간 접지 단자부터 PE 도체까지 SPD 와 주 접지 단자 사이의 케이블 길이(따라서 인덕턴스)는 최소로 유지해야 한다. SPD 는 PE 에 연 결되어 있고 IEC 60364-5-54 에 따른 보호 도체에 대한 요구사항을 충족하는 경우 금속 부품(예를 들어 금속 외함)을 통해 주 접지 단자 또는 보호 도체에 연결할 수 있다(543.4.2 참조). 관련 SPD 들 이 주 보호 도체와 의 연결에 더하여 주 접지 단자에 연결되면 전압 보호 수준이 올라갈 수 있다. 그림 8 처럼 정의 한 총 배선 길이(a+b+c)가 0.5 m 를 넘길 경우 다음 선택 지중 하나를 선택해야 한다. · 더 낮은 전압 보호 수준의 SPD 선택 (10 kA(8/20)의 방전 전류를 운반하는 1 m 길이의 직선 케이 29 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
7800b8eb-ccaa-4e9a-9643-8a490a91052c | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 블 약 1,000 V 의 전압 강하를 추가함) · 보호할 기기 근처에 조정된 두 번째 SPD 를 설치하여 전압 보호 수준을 보호할 기기의 정격 임펄 스 전압까지 조정 · 그림 9 에 묘사된 설비를 사용한다 ![image](/image/placeholder) OCPD E/I PE SPD 5 B 3 �� 2 1 ○ ○- 4 ¦ 여기에서 ¦ 여기에서 ¦ ¦ --- ¦ --- ¦ ¦ OCPD ¦ 과전류 보호장치 ¦ ¦ SPD ¦ 서지 보호장치 ¦ ¦ PE ¦ 보호 접지 ¦ ¦ E/I ¦ 기기/설비 ¦ ¦ 1 ¦ 주 접지 단자 ¦ ¦ 2 ¦ 중간 접지 단자 ¦ ¦ 3 ¦ 길이 C(고려될 예정) ¦ ¦ 4 ¦ 고려되지 않을 케이블 길이 ¦ ¦ 5 ¦ 고려되지 않을 케이블 길이 ¦ ¦ A 및 B ¦ SPD 조립의 연결 지점 ¦ 그림 9 - SPD 전원 도체의 길이를 줄이기 위한 SPD 의 설치 예시 534.4.9 SPD 의 유효 보호 거리 SPD 와 보호 대상 기기 사이의 거리가 10 m 이상인 경우 다음과 같은 추가 보호 조치를 제공해야 한다. - 보호 대상 기기에 최대한 가깝게 추가로 설치된 SPD 의 전압 보호 수준 Up 는 어떠한 경우에도 기 기의 필요한 정격 임펄스 전압 Uw 를 초과 해서는 안된다. 또는, 설비의 공급점이나 근처에 1 포트 SPD 를 사용하는 경우, 전압 보호 수준 Up 는 보호 대상 기기에서 요구되는 정격 임펄스 전압 Uw 의 50 %를 초과 해서는 안 된다. 이 방법은 전체 보호 회 로에 차폐 배선을 사용하는 등 다른 방법과 함께 실행해야 한다. 또는, 설비의 공급점이나 근처에 2 포트 SPD 를 사용하는 경우, 전압 보호 수준 Up 는 보호해야 할 기기의 필요한 정격 임펄스 전압 Uw 를 초과 해서는 안 된다. 이 방법은 전체 보호 회로에 차폐 배 30 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
9cc177d9-ee0f-4c45-80c9-d86c097260f9 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 선을 사용하는 등 다른 방법과 함께 실행해야 한다. 534.4.10 SPD 의 연결 도체들 주 접지 단자 혹은 보호 도체와 SPD 사이의 도체들은 다음 단면적 이상이어야 한다. 6 mm2 구리 혹은 공급점이나 그 근처에 설치된 동급의 II 등급 시험이 된 SPD - 16 mm2 구리 혹은 공급점이나 그 근처에 설치된 동급의 I 등급 시험이 된 SPD IEC 60364-4-43:2008 의 433.3.1 b)에 따라, SPD 및 과전류 보호장치를 충전선에 연결하는 도체는 예 측되는 예상 단락 전류를 견딜 수 있게 정격이어야 하며, 다음 단면적 이상이어야 한다. 2.5 mm2 구리 혹은 공급점이나 그 근처에 설치된 동급의 II 등급 시험이 된 SPD - 6 mm2 구리 혹은 공급점이나 그 근처에 설치된 동급의 I 등급 시험이 된 SPD 535 보호장치들의 협조 535.1 과전류 보호장치 사이의 선택성 535.1.1 일 반 과부하, 단락 또는 접지 고장의 경우라면 여러 개의 직렬 과전류 보호장치들(OCPD OverCurrent Protective Devices) 중에 선택성이 주어진다. 고장이나 과부하의 전원 측에 직접적으로 있는 OCPD(Q2)만 병렬로 있는 전원(Q3)에 영향을 안 끼치면서 동작한다. (그림 10 참조) 부하 측의 OCPD(Q2)는 전단의 OCPD(Q1)의 동작을 야기하지 않으면서 과전류 선택성 제한 Is 수준 까지 보호를 제공한다. 선택성 제한 전류 Is 를 결정하려면 전단 및 후단 OCPD 의 제조자 지침을 참조해야 한다. 이에 대한 제조자의 지침이 없을 경우 선택성 제한 전류 Is 는 OCPD 의 동작 시간-전류 곡선과 비교하여 정의 한 다. 선택성 제한 전류 Is 는 회로 차단기의 통과 에너지나 퓨즈가 녹는 에너지 같은 에너지 값들을 고려하 여 평가되어야 한다. 관련 제품 표준들도 참고한다. Chart Type: line Q Q2 IEC item_01 0 1 0 ¦ 여기에서 ¦ ¦ ¦ --- ¦ --- ¦ ¦ Q1, Q3 ¦ 비 트립 ¦ ¦ Q2 ¦ 트립 ¦ 31 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
e9d509ad-1dfc-4a68-8cd8-d3ea2bb05571 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 그림 10 - 선택성의 예시 535.1.2 부분 선택성 선택성 제한 전류 Is 는 OCPD 설치지점의 부하측 최대 예상 단락 전류 Isc_max (그림 11 참 보다 작다. 조) Is<Isc_max 535.1.3 완전 선택성 선택성 제한 전류 Is 는 OCPD 설치지점의 부하측 최대 예상 단락 전류 Isc_max 크거나 같고 IEC 보다 60947-2 에 따라 용량 Icu 또는 IEC 60898(모든 부)나 IEC 61009-1 에 따른 Icn 보다 작다. (그림 11 참조) Isc_max≤Is<Icu 또는 Icn 535.1.4 전체 선택성 선택성 제한 전류 Is 는 OCPD 설치지점의 부하측 최대 예상 단락 전류 Isc_max 크거나 같고 IEC 보다 60947-2 에 따른 차단 용량 Icu 또는 IEC 60898(모든 부)나 IEC 61009-1 에 따른 Icn 과 똑같다. (그림 11 참조) Isc_max ≤Is = Icu 또는 Icn 535.1.5 향상된 선택성 선택성 제한 전류 Is 는 OCPD 설치지점의 부하측(Q2) 최대 예상 단락 전류 보다 크거나 같고 이 조 합의 결합 전류 Icomb 보다 작거나 같다. 부하 측(Q2) OCPD 의 IEC 60947-2 에 따른 차단 용량 Icu 또는 IEC 60898(모든 부)나 IEC 61009-1 에 따른 Icn 은 설치지점의 최대 예상 단락전류보다 작다. Icu 또는 Icn<Isc_max≤Iz≤Icomb 장치의 제조자에서 각각의 정보가 있어야 향상된 선택성 디자인을 할 수 있다. ![image](/image/placeholder) Iz Isc_min Isc_max IB IquorIcn Icomb IEC ¦ 여기에서 ¦ ¦ ¦ --- ¦ --- ¦ ¦ Iz ¦ 케이블의 연속 전류운반 용량 ¦ ¦ Isc_min ¦ 최소 예상 단락 전류(회로의 부하측) ¦ ¦ ISC_max ¦ 최대 예상 단락 전류(회로의 부하측) ¦ ¦ IB ¦ 회로의 설계 전류 ¦ ¦ Is ¦ 선택성 제한 전류 ¦ ¦ Icu ¦ 최종 단락 차단 용량 ¦ 32 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
245b2a5a-0492-4634-93c0-710dc8e12e83 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 Icomb 조합의 결합 전류 그림 11 、 전류와 선택성과 의 상관 관계 예제 535.2 누전차단기와 OCPD 간의 협조 과부하 보호 기능이 없는 잔류 전류 보호장치는 과전류 보호가 필요하다. 이 과전류 보호는 잔류 전 류 보호장치 제조자의 지침에 따라 선정해야 한다. 535.3 누전차단기 사이의 선택성 직렬로 설치된 잔류 전류 보호장치 사이의 선택성은, 특히 안전성이 관련된 경우, 고장이 일어나지 않은 설비의 부분이 있다면 그 파트에 전원의 연속성을 위해 서비스상의 이유로 필요할 수 있다. 이러한 선택성은 고장이 발생할 경우 전원 측에서 고장과 가장 가까운 RCD 만 동작하도록 잔류 전류 보호장치를 선택하고 설치함으로써 달성할 수 있다. 직렬로 연결된 두개의 잔류 전류 보호장치의 선택성을 보장하기 위해서 이 장치들은 다음의 조건을 만족해야 한다. a) IEC 61008(모든 부), IEC 61009(모든 부) 또는 IEC 62423(모든 부) 유형 S 에 따라 또는 IEC 60947-2 시간 지연 유형에 따라 전원측(전단) 잔류 전류 보호장치를 선정해야 한다. b) 전원 측에 위치한 장치의 정격 잔류 동작 전류는 부하 측에 위치한 보호장치의 잔류 전류 보다 적어도 세 배 이상 커야 한다. 535.4 RCD 와 OCPD 의 선택성 고려중 535.5 OCPD 의 결합된 단락 보호 IEC 60947-2 또는 IEC 60898(모든 파트) 또는 IEC 61009-1 에 따라 OCPD(Q2)가 자체 차단 용량 Icu 보다 높은 예상 단락 전류를 차단해야 하는 경우 전단 OCPD(Q1)의 단락전류와 단락 에너지의 추가 제한을 통해 차단을 돕는다. (그림 12 참조) 전단 OCPD 도 트립되어 다른 회로(Q3)에 대한 전원이 방해될 수 있다. Chart Type: line Q Q2 Q3 item_01 0 2 3 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 33 | {}
c260e025-49a8-48bd-bae9-125c92e1ed7c | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 여기에서 Q1 및 Q2 트립: ICN 또는 Icu Q2≤Isc_max Q3 비 트립 그림 12 - OCPD 의 결합된 단락 보호 예시 결합된 단락 보호 OCPD 를 위해 두개의 OCPD 를 선정할 때 후단 OCPD 제조자의 지침을 참조해야 한다. 제조자로부터 정보를 얻을 수 없을 때 결합된 단락 보호를 사용하면 안되고 각각의 OCPD 는 설치 지점의 요구되는 단락 능력을 갖춰야 한다. 두 OCPD 의 제조자에서 명시했을 때, 직렬연결의 결합된 OCPD 의 단락 능력은 두 OCPD 의 각각의 차단 용량보다 높을 수 있다. 이러한 경우에서 두 OCPD 사이의 도체는 · 단락의 위험을 최소한으로 줄이는 방법으로 만들고(IEC 60364-4-43:2008, 434.2.1b) 참고) · 가연성 물질 근처에 두지 않는다. 두 OCPD 의 제조자에서 명시했을 때, 직렬연결의 결합된 OCPD 의 결합 단락 능력은 두 OCPD 의 각 각의 차단 용량보다 높을 수 있다. 이러한 경우에서 두 OCPD 사이의 도체는 · IEC 60364-4-43:2008, 434.5.2 에 따라 OCPD 의 결합으로 보호됨 · 길이가 3m 를 초과 하지 않고 · 단락의 위험을 최소한으로 줄이는 방법으로 만들고 비고 이 조건은 예를 들어 배선의 외부 영향에 대한 보호를 강화함으로써 얻는다. · 가연성 물질 근처에 두지 않는다. OCPD 의 단락 차단 용량을 증가시키기 위해 별도의 전류 제한기와 OCPD 의 조정은 제조자의 지침 에 따라 사용될 수 있다. 536 절연 및 개폐 536.2 절연 536.2.1 일 반 536.2.1.1 모든 회로는 모든 충전선으로부터 절연될 수 있어야 한다. 사용 조건에 따라 허용되는 경우, 공통 수단으로 회로 그룹의 절연에 대한 대책을 수립할 수 있다. 각각의 전원은 절연 수단이 있어야 한다. 536.2.1.2 기기가 의도하지 않게 충전이 되지 않도록 적절한 수단이 제공되어야 한다. 이러한 예방조치는 다음 조치 중 하나 이상을 포함할 수 있다. · OFF 위치에서 잠금 장치를 채우기 적합한 장치 선택 · 열쇠로 잠기는 통제 구역 또는 외함이 있는 적절한 방법의 장소에 설치 비고 보조 수단으로 접지가 사용될 수 있다. 34 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
73cac203-f439-47af-b4fb-053b9793dd44 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 536.2.1.3 기기의 품목 또는 외함이 한 개 이상의 전원에 접속된 충전부를 포함하는 경우 충전부에 접근하는 사람이 각각의 전원으로부터 충전부를 분리할 필요가 있음을 알 수 있도록 경보 표지를 부 착해야 한다. 다만, 모든 관련 회로를 모든 전원에서 확실히 절연시킬 수 있는 연동 장치를 설치한 경우에는 제외한다. 연동 장치의 메커니즘은 · 어떤 회로도 독립적으로 충전할 수 없도록 OFF 위치에서 안정적으로 고정할 수 있으면서 · 하나 이상의 회로가 다른 보호 회로보다 오래 충전되지 않도록 모든 회로에 동시에 격리를 제공한 다 536.2.1.4 필요한 경우 축적된 전기 에너지가 방전되도록 적절한 수단을 제공해야 한다(자세한 사항 은 IEC 60364-5-55 참조). 536.2.2 절연을 위한 장치 7 536.2.2.1 절연에 적합한 일부 장치는 기호 로 식별된다. (IEC 60417-6169-1:2012-08) 이 기호는 다른 기능을 위한 기호와 결합할 수 있다. 장치들은 설치지점에서 적용되는 과전압 범주 III 혹은 IV 에만 따라서 선정해야 한다. 격리에 사용되는 장치는 536.2.2.2 부터 536.2.2.7 에 따르고 표 E.1, 부속서 E 에서 선택해야 한다. 536.2.2.2 절연 장치는 접촉 위치가 명료하면서 신뢰성이 있도록 선정 및 설치되어야 한다. 예 "Off" "off" 또는 "OFF" 표식 혹은 기호 "O"는 개방 상태를 표시한다. "On", "on", 또는 "ON" 표식 혹은 기호"I"는 닫힘 상태를 표시한다. 536.2.2.3 반도체 장치를 절연 장치로 사용해서는 안 된다. 536.2.2.4 절연 장치는 의도되지 않은 폐로 동작을 방지하도록 설계 및 설치해야 한다. 이는 장치를 열쇠로 잠글 수 있는 공간이나 외함 혹은 자물쇠를 통한 곳에 위치해서 얻는다. 비고 폐로는 예를 들어 쇼크나 진동에 의해 발생할 수 있다. 536.2.2.5 절연을 위한 장치가 정상적인 조건에서 전류를 만들고 차단할 수 없는 경우를 제외하고 단 로기의 우발적 및/또는 허가되지 않은 개방을 방지하기 위한 대책을 수립해야 한다. 이는 절연 장치를 열쇠로 잠긴 통제 구역에 설치하거나 외함 내에 설치 또는 자물쇠를 사용하면 가 능하다. 이러한 방법 대신에 단로기를 개폐기 혹은 보호장치와 연동하는 방법이 있다. 536.2.2.6 중성선에 링크가 삽입된 경우 다음이 적용된다. · 숙련자만 접근이 가능하다. · 우발적 및/또는 허가되지 않은 제거를 방지하기 위해 디자인 된다. · 도구를 사용해야 제거가 된다 35 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
9b72e0bf-e553-4668-9dd6-5033314d56b3 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 536.2.2.7 절연 수단은 해당 전원의 모든 전극을 분리하는 다극식 개폐 장치를 사용하는 것이 바람직 하지만 단극식 장치를 다상 회로용으로 상호 인접해 사용하는 것도 배제하지 않는다. 단극식 보호장치(예를 들어 회로 차단기 혹은 퓨즈)가 중선선에서만 사용되면 안 된다. 536.2.2.8 절연에 이용되는 모든 장치는 표시 등을 이용해 절연 대상 회로를 표시하여 명확히 식별할 수 있게 해야 한다. 536.2.2.9 부속 절 536.2.2.1 부터 536.2.2.8 는 플러그와 콘센트, 접촉기와 등기구의 연결을 위한 장 치에 적용되지 않는다. 536.3 기계의 유지 보수를 위한 전원 차단(switching-off) 536.3.1 일 반 536.3.1.1 기계의 유지 보수가 감전 또는 방전 발생 이외의 인체에 상해를 줄 우려가 있는 경우에는 전원 차단 장치 수단이 제공되어야 한다. 전기 구동식 기계기기가 IEC 60204-1 의 범위 내에 있는 경우 IEC 60204-1 의 기계적 유지보수를 위한 전원차단 요구사항이 적용된다. 압축 공기, 물, 증기 등의 다른 수단으로 전원을 공급받는 계통에는 536.3.1 을 적용하지 않는다. 이러 한 경우, 연관된 모든 전기 공급을 차단하는 것이 충분한 조치가 아닐 수도 있다. 536.3.1.2 기계의 유지 보수가 이루어지는 동안에 전기 기기가 갑자기 재 동작하지 않도록 적절한 예 방 조치를 취해야 한다. 다만, 이러한 유지 보수를 행하는 작업자가 해당 전원 차단 장치를 계속해서 관리하고 있는 경우는 제외한다. 예시 · OFF 위치에서 자물쇠를 채우기 적합한 기기의 선정 · 열쇠로 잠기는 통제 구역 또는 외함에 설치 전원차단은 절연에 적합한 장치에 의해 모든 상전선을 분리해야 한다. 536.3.2 기계의 유지 보수를 위한 전원 차단 장치 536.3.2.1 기계의 유지 보수를 위한 전원 차단 장치는 536.2.2 에 부합하며 536.3.2 의 모든 다른 요구 사항들을 만족해야 한다. 기계의 유지 보수를 위한 전원 차단 장치는 유지할 기기를 사용하여 전류의 전원 회로에 삽입하는 것이 바람직하다. 이 목적으로 개폐기를 설치할 경우 이 개폐기는 설비의 해당 부분의 전체 부하 전류를 차단할 수 있 어야 한다. 개폐기가 모든 상전선을 반드시 다 차단할 필요는 없다. 유지할 기기를 사용하여 전류의 전원 회로에 장치를 삽입하지 않는 제어 회로의 중단은 다음과 같은 경우에만 사용해야 한다. · 기계적 구속 장치 등 보조 안전 대책이 제공됨 36 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
ec25545f-1dc9-48bc-a1f8-bb1b22399edb | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 · 사용된 제어장치에 대한 요구사항이 주 전원의 직접 중단과 똑같은 조건을 제공한다. 예시 기계의 유지 보수를 위한 전원 차단은 다음과 같은 방법으로 가능하다 · 다극 개폐기 · 회로 차단기 · 접촉기를 동작시키는 제어 개폐기 · 플러그와 콘센트 536.3.2.2 기계 유지 보수를 위한 전원 차단 장치는 쉽게 식별 가능하고 의도된 대로 사용하기 편하 도록 설치 및 표시되어 있어야 한다. 536.4 비상 개폐 536.4.1 일 반 536.4.1.1 IEC 60204-1 범위 내의 전기적으로 전원이 공급되는 기기는 IEC 60204-1 의 비상 개폐 요구 사항이 적용된다. 비상 개폐라 함은 비상 전원 개방 혹은 비상 전원 차단 둘 다에 해당된다. 536.4.1.2 예상치 못한 위험을 제거하기 위해 전원을 제어할 필요가 있는 경우에는 설비의 모든 부분 에 대해 비상 개폐 수단을 적용하여야 한다. 536.4.1.3 비상 개폐 수단은 해당하는 모든 전원 도체에 가능한 한 직접 동작해야 한다 536.4.1.4 비상 개폐는 그 동작이 재차 별도의 위험을 유발하거나 위험을 제거하는 데 필요한 조작을 방해하지 않도록 배치해야 한다. 536.4.2 비상 전원 차단 장치 536.4.2.1 비상 개폐에 사용되는 장치들은 표 E.1 에서 선택하며 536.4.2.1 부터 536.4.2.6 에 부합해야 한다. 비상 전원 차단 장치는 모든 충전선을 차단하여야 한다. 비상 개폐 장치는 해당하는 전동기 전류를 고려해 설비의 해당 부분의 전체 부하 전류를 차단할 수 있어야 한다. 536.4.2.2 비상 개폐 수단은 다음으로 구성될 수 있다. · 해당 전원을 직접 차단할 수 있는 절연에 적합한 단독 개폐 장치 1 개 · 해당 전원을 차단하기 위해 단일 동작으로 기동되는 기기의 조합 주회로의 직접 차단에는 실용적인 경우 수동형 개폐 장치를 적용해야 한다. 원격 제어를 통해 동작하는 절연에 적합한 장치는 코일 소자에 의해 개로하거나 기타 이와 동등한 고장 - 안전(failure-to-safety) 기술을 적용한 것이어야 한다. 예시 고장 - 안전(failure-to-safety) 기술은 공압 동작기 이거나 혹은 동작기 회로의 연속성이 명시되는 것 37 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c5fc0cf4-8fc2-40ec-9d9f-d783eb24a5bc | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 이 보장된 경우 분로 트립 지연이다.(예를 들어 램프에 의해) 536.4.2.3 비상 개폐 장치의 조작부(핸들, 누름 단추 등)는 명확하게 식별해야 하며, 가능하면 배경과 대조되는 적색으로 하는 것이 좋다. 이러한 장치의 유일한 식별이 문자로 이루어 지면 안 된다. 536.4.2.4 비상 개폐 장치의 조작부는 위험이 발생할 우려가 있는 장소와 그 위험을 제거할 수 있는 적당히 떨어진 장소에서 쉽게 접근할 수 있어야 한다. 536.4.2.5 비상 개폐 장치의 해제로 설비의 해당 부분 및/또는 전기 기기가 재충전되어서는 안 된다 536.4.2.6 비상 정지를 포함한 비상 개폐 장치는 쉽게 식별 가능하고 의도된 대로 사용하기 편하도록 설치 및 표시되어 있어야 한다. 536.4.3 비상 정지를 위한 장치 비고 IEC 60204-1 은 비상 정지를 위한 장치의 선정 및 설치에 대한 요구 사항을 제공한다. 비상 정지 시에는 예를 들어 구동부의 제동을 위해 전원 유지가 필요할 수도 있다. 536.5 기능적 개폐(제어) 536.5.1 일 반 536.5.1.1 회로를 설비의 기타 부분과 독립해서 제어할 필요가 있는 경우에는 회로의 각 부분에 기능 적 개폐 장치를 설치해야 한다. 536.5.1.2 기능적 개폐 장치가 회로의 모든 충전선을 제어할 필요는 없다. 상전선이 개폐되지 않는 제어 장치의 동작이 중요한 경우(예를 들어 센서, 등기구 제어 장치, 조광기, 원격 제어 개폐기(RCS, Remote Control Switch))를 제외하고는 단극 개폐 장치는 중성선에 설치해서 는 안 된다. 536.5.1.3 제어가 요구되는 전류를 사용하는 기기는 적절한 기능적 개폐 장치를 통해 제어되어야 한 다. 하나의 기능적 개폐 장치는 동시에 동작하도록 의도된 기기 여러 개를 제어할 수 있다. 536.5.2 기능적 개폐를 위한 장치 536.5.2.1 기능적 개폐에 사용되는 장치들은 표 E.1 에서 선택하며 536.5.2.2 부터 536.5.2.3 에 부합해 야 한다. 536.5.2.2 기능적 개폐 장치는 이것이 동작할 가능성이 있는 가장 까다로운 조건에서 적합해야 한다. 536.5.2.3 기능적 개폐 장치는 동위극을 꼭 개방하지 않더라도 전류를 제어할 수 있다. 비고 반도체 개폐 장치는 회로 전류를 차단할 수는 있으나 동위극을 개방할 수 없는 예이다. 38 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
43473265-2a61-4090-99ad-50d12caa1ac5 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 536.5.2.4 링크는 기능적 개폐용으로 사용하면 안 된다. 536.5.2.5 16 A 이하의 플러그와 콘센트는 기능적 개폐에 사용할 수 있다. 537 감시 537.1 일반사항 537.1.1 감시 장치 감시 장치는 전기 쇼크에 대비한 보호가 제공되도록 의도되지 않는다. 537.1.2 절연 감시 장치(IMD, Insulation Monitoring Device)의 선정 IMD 는 IEC 61557-8 에 부합해야 한다. IMD 는 가능한 한 감시할 설비 부분의 공급점 혹은 그 근처에 설치되어야 한다. 537.1.3 잔류 전류 감시 장치(RCM, Residual Current Monitoring devices)의 선정 RCM 은 IEC 62020 에 부합해야 한다. RCM 은 가능한 한 감시할 설비 부분의 공급점 혹은 그 근처에 설치되어야 한다. 잔류 전류 보호장치(RCD)가 RCM 의 전단에 설치된 경우, RCM 을 설정하여 잔류 발동 전류가 RCD 의 정격 잔류 동작 전류 IAn 의 3 분의 1 이하로 되는 것이 권장된다. 537.2 연속 전원을 위한 IT 계통 537.2.1 일 반 IMD 는 IT 계통의 절연저항을 영구적으로 감시하고 절연저항 RF 가 응답 값 Ra 보다 낮은 경우 경보 를 제공하도록 되어 있다. IMD 는 IEC 60364-441:2005 및 IEC 60364-4-41:2005/AMD1:2017, 411.6.3.1 에 부합하여 IT 계통에 설 치되어야 한다. IMD 가 접지 고장을 감지하면 가능한 가장 짧은 지연으로 정상 동작 조건으로 복구되기 위해 고장의 위치가 감지되고 제거되기 위한 지침이 제공되어야 한다. IT 계통이 서비스의 연속성을 위해 사용되는 경우 첫 번째 절연 고장을 감지하는 알람은 기능자 (BA4) 혹은 숙련자(BA5)가 청각 및/또는 시각적으로 찾을 수 있게 위치 하여야 한다. 시스템 도체 및 접지에 대한 측정 연결의 차단을 알리는 IMD 를 사용하는 것이 좋다. IT 계통이 서비스의 연속성을 위해 사용되는 경우 부하시 고장 위치를 알 수 있게 해주는 장치와 IMD 를 조합하는 것이 권장되고 절연 고장위치 탐지 기기는 IEC 61557-9 에 따라 선정해야 한다. 537.2.2 절연 감시 장치(IMD, Insulation Monitoring Devices) 39 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
a76ea086-ec21-4157-830e-a7beff8007a3 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 다상 계통에서 IMD 는 적어도 선간 전압을 견딜 수 있게 선정되어야 한다. 감시 될 계통이 직류 소자를 포함하는 경우(예를 들어 정류기와 컨버터) 이에 따라 IMD 를 선정해야 한다. 537.2.3 IMD 의 설치 IMD 가 중성선에 연결 되 있을 경우 OCPD 가 IMD 와 중성선 사이에 삽입되면 안 된다. IMD 의 설정은 오직 기능자(BA4)와 숙련자(BA5)만 조정해야 한다. 설정수단의 접근은 열쇠, 도구 혹 은 비밀번호를 사용하여 이루어 질 수 있다. 비고 정격 계통의 100 �/V(사전 경고용은 300 �/V)전압 값은 통상적인 설정 값이다. 설비가 하나이상의 전원에서 공급받을 때 공급 마다 하나의 IMD 가 사용되어야 한다. 일시적으로 병렬 연결된 전원 공급들의 경우 하나의 IMD 만 IT 계통에 연결되도록 할당된 IMD 가 연동 되어야 한다. IMD 가 설비의 분리된 부분 또한 감시해야 한다면 IMD 는 보조 전원에 의해 공급되어야 한다. 537.3 공공 배전 IT 계통 공공 배전 네트워크 IT 에 연결된 설비와 하나이상의 설비가 같은 배전 네트워크에 연결되도록 의도 되는 경우 다음이 적용된다. 최초 접지 절연 고장시에 전원의 차단이 요구되지 않거나 허가 받지 않은 경우, IEC 60364-4- 41:2005/AMD1:2017 에 따라 충전선부터 노출된 도체 파트(혹은 접지)사이에 발생하는 최초 접지 고 장을 알리기 위해 감시 장치가 선정 및 설치되어야 한다. 이러한 감시 장치는 다음과 같을 수 있다. · IMD · 잔류 고장 전류가 충분히 높은 경우 잔류 전류 감시 장치(RCM) 높은 누설 커패시턴스가 RCM 설비의 후단 지점에서 존재할 수 있을 때 누설전류의 원하지 않는 신 호를 피하기 위해 RCM 의 차별화되는 사용이 권장된다. 비고 IT 계통에서 RCM 의 측정 원칙으로는 RCM 후단에 있는 다른 충전선의 이중 또는 대칭 절연 고장을 감지할 수 없다. 537.4 TN, TT 및 IT 계통의 오프라인 시스템 오프라인 시스템의 절연 감시가 필요한 경우 절연 감시 장치(IMD)를 사용하여 달성할 수 있다. 오프라인 시스템 감시에 사용되는 IMD 는 계통이 켜질 때마다 자동으로 비활성화되어야 한다. 비고 예를 들어, 이는 소방 펌프나 화재 환기와 같이 보통 전원이 차단되는 계통에 적용할 수 있다. 절연 수준의 감소는 원격 표시 옵션이 있는 시각 신호 또는 청각 신호로 국소적으로 표시해야 한다. 40 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
19f37ec4-2c1f-4509-8379-1faa99c993d4 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 첫 번째 절연 고장을 감지하는 알람은 기능자(BA4) 혹은 숙련자(BA5)가 청각 및/또는 시각적으로 찾 을 수 있게 위치 하여야 한다 일반적으로 측정된 절연 수준이 매우 높기 때문에 알람의 임계 값은 300 k� 이상이어야 한다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 41 | {}
fdef9c49-39f9-4089-ace6-a6bc539330ab | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 부속서 A (참고) 과부하 보호장치의 설치위치 A.1 일반사항 과부하 보호용 장치 및 단락 보호용 장치는 각각의 회로에 설치하여야 된다. 이 장치들은 일반적으 로 각각의 회로의 기점에 위치하여야 된다. 일부 적용에서 과부하 보호 혹은 단락 보호용 장치 중 하나가 아직 다른 보호의 제공이 유지된다면 이 일반적인 요구사항을 따르지 않을 수 있다. A.2 과부하 보호가 분기 회로의 기점에 위치하지 않아도 되는 사례 533.4.2.2 a) 및 그림 A.1 의 요구사항에 따라, P2(이 분기 회로의 보호장치)의 전원 측에 어떠한 다른 연결 또는 콘센트가 없다면 과부하 보호장치 P2 는 분기 회로(B)의 기점(O)에서 이동할 수 있고 533.4.2.2b) 1)의 요구사항에 따라 분기 회로의 이쪽 파트는 단락 보호가 제공된다. ![image](/image/placeholder) A S1 0 P1 S2 S2≤S1 B P2 IEC 여기에서 S 도체의 단면적 그림 A.1 - 분기 회로의 기점(B)에 없는 과부하 보호장치(P2) 과부하 보호장치는 배선 계통을 보호한다. 전류 사용 기기만 과부하를 발생시킬 수 있으므로, 분기 회로의 단락 보호 기능이 계속 동작한다면, 과부하 보호장치를 분기 회로의 동작에 따라 임의 의 장 소로 이동할 수 있다. 533.4.2.2 a) 및 그림 A.2 의 요구사항에 따라, 이 P2(이 분기 회로의 보호장치)의 분기 회로의 길이에 서 어떠한 다른 연결 또는 콘센트가 없다면 과부하 보호장치 P2 는 분기 회로(B)의 기점(○)에서 이동 할 수 있고 533.4.2.2 b) 2)의 요구사항에 따라 이 길이는 3 m 를 넘지 않고 이 길이에서 단락, 화재의 발생 및 사람에 대한 위험이 최소한으로 감소된다. 42 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
d82595a1-93a0-4c38-b90b-717072781e6d | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 ![image](/image/placeholder) A S1 0 P1 ≤3m S2 B P 2 IEC 여기에서 S 도체의 단면적 그림 A.2 - 분기 회로의 기점(B)의 3m 이내에 설치된 과부하 보호장치(P2) 3 m 길이 안에서는 분기 회로가 단락으로부터 보호되지 않는 것으로 인정되지만, 안전을 보장하기 위해 몇 가지 주의 사항을 따라야 한다. 533.4.2.2 b) 참조. 또한, 공급 회로의 단락 보호가 P2 가 설치 된 지점까지의 분기 회로에 단락 보호를 제공한다. (부속서 B 참조) 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 43 | {}
66949b42-1ecd-458a-9136-50cd109cb8cf | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 부속서 B (참고) 단락 보호장치의 설치위치 B.1 일반사항 과부하 보호용 장치 및 단락 보호용 장치는 각각의 회로에 설치하여야 된다. 이 장치들은 일반적으 로 각각의 회로의 기점에 위치하여야 된다. 일부 적용에서 과부하 보호 혹은 단락 보호용 장치 중 하나가 아직 다른 보호의 제공이 유지된다면 이 일반적인 요구사항을 따르지 않을 수 있다. B.2 단락 보호가 분기 회로의 기점에 위치하지 않아도 되는 사례 533.4.2.2 및 그림 B.1 의 요구사항에 따라, 이 길이의 분기회로에 어떠한 다른 연결 또는 콘센트가 없다면 과부하 보호장치 P2 는 분기 회로(B)의 기점(O)에서 3 m 까지 이동할 수 있고 533.4.3.2 사례 의 경우 단락의, 화재의 발생 및 사람에 대한 위험이 이 길이에서 최소한으로 감소한다. ![image](/image/placeholder) A S1 0 P1 53m S2 B P2 IEC 여기에서 S 도체의 단면적 그림 B.1 - 분기 회로 위 단락 보호장치(P2)의 제한적인 위치 변경 분기 회로의 도체 길이 3 m 는 단락으로부터 보호되지 않지만 공급 회로에 제공되는 단락 보호는 P2 가 설치된 지점까지 분기 회로에 단락 보호를 제공할 수 있다. 533.4.3.3 및 그림 B.2 의 요구사항에 따라 단락 보호장치 P2 는 533.4.3.3 을 준수하는 경우 분기 회로 (B)의 기점(O)의 전원측 지점에 설치할 수 있다. 533.4.3.3 에 따라, 분기 회로의 기점과 이 분기 회로 의 단락 보호장치 사이의 최대 길이는 "삼각형 규칙"이 제안한 규격에 따른다. 44 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
6c24b631-735c-428e-a106-e7751afd6183 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 ![image](/image/placeholder) A ○ B P1 S1 S2 P 2 N S2 P M 2 S2 P 2 L 1 B S1 N IEC ¦ 여기에서 ¦ ¦ ¦ --- ¦ --- ¦ ¦ AB ¦ A 에 배치된 보호장치 P1 에 의해 단락으로부터 보호되는 단면적 S1 도체의 최대 길이 L1 ¦ ¦ AM ¦ A 에 배치된 보호장치 P1 에 의해 단락으로부터 보호되는 단면적 S2 도체의 최대 길이 L2 ¦ 그림 B.2- 분기 회로의 전원측 기점에 설치된 단락 보호장치 P2 A 에 배치된 단락 보호장치 P1 에 의해 보호받고 단면적 S2 안에서 ○에서 갈라지는 도체의 최대 길이 는 삼각형 BON 에서 길이 ON 으로 주어진다. 단락에 대한 보호만 제공되는 경우 B.2 절을 사용할 수 있다. 이 예시 에서는 과부하 방지를 고려하 지 않는다. 이 최대 길이는 보호장치 P1 을 동작할 수 있는 최소 단락에 해당한다. 분기 회로 SI 을 AB 까지 보호 하는 이 보호장치도 분기 회로 S2 를 보호한다. P1 에 의해 보호되는 분기 회로 S2 의 최대 길이는 분기 회로 S2 가 S」에 연결되는 위치에 따라 달라진다. 분기 회로 S2 의 길이는 삼각형 도표에 의해 결정된 값을 초과 할 수 없다. 이 경우 보호장치 P2 는 분 기 회로 S2 를 따라 N 지점까지 이동할 수 있다. 비고 1 이 방법은 서로 다른 단면적의 3 개의 이어진 도체의 경우에도 적용할 수 있다. 비고 2 만약 S2 에서 단열 특성에 따라 배선의 길이가 다른 경우, 다음과 같은 길이를 통해 방법을 적 용할 수 있다. AB= L2S1/S2 만약 S2 에서 단열 특성에 관계없이 배선의 길이가 같은 경우, 다음과 같은 길이를 통해 방법을 적용 할 수 있다. AB=L1 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 45 | {}
e1b05287-e532-4cff-99d7-9fd7bc0119ed | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 부속서 C (참고) SPD 설치 - 계통 구성에 따른 설치도의 예 비고 1 국가 위원회는 국가에 맞는 도표를 선정할 수 있다. 비고 2 IEC 60364 에 따라 OCPD 는 단극 혹은 다극 일수 있다. ![image](/image/placeholder) C.1 TT 계통 - 3 상 전원과 중성 2 1 L1 L2 R C 3 L3 c P D D N 1 6 OCPD2 s P SPD D PE conductor 11110151015 PE 선 4 여기에서 1 LV 스위치 보드 2 HV/LV 변압기 3 기기/설비 4 주 접지 단자 5 중간 접지 단자 6 SPDA OCPD1 설비의 공급점의 과전류 보호장치 SPD 서지 보호장치 OCPD2 과전류 보호장치 (필요한 경우) RCD 잔류 전류 장치 그림 C.1 - TT 계통에서 주 RCD 의 전단 전원측 연결 형태 CT2 와 SPDA 설비의 연결 예시 46 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
e2a93bbc-42e1-4570-ba73-eb77b2e716ee | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 ![image](/image/placeholder) L1 L1 R L2 L2 0CPD1 L3 C L3 D N N PE 0CPD2 SPD 5a SPD H 5b I 0 4 ¦ 여기에서 ¦ 여기에서 ¦ ¦ --- ¦ --- ¦ ¦ OCPD1 ¦ 설비 공급점의 과전류 보호장치 ¦ ¦ SPD ¦ 서지 보호장치 ¦ ¦ OCPD2 ¦ 과전류 보호장치 (필요한 경우) ¦ 4 주 접지 단자 5a, 5b 서지 보호장치의 접지 연결, 5a 및/또는 5b 둘 다 (요구될 경우) RCD 잔류 전류 장치 그림 C.2 - TT 계통에서 주 RCD 의 전단 전원측 연결 형태 CT2 와 SPD 설비의 연결 예시 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 47 | {}
d4b00f97-1c67-4f46-b3e7-583ee25574d6 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 ![image](/image/placeholder) 2 1 L 1 L2 0 c R L3 3 P c N D D 1 6 OCPD2 SPD PE 선 PE conductor , [*] 5 4 ¦ 여기에서 ¦ 여기에서 ¦ ¦ --- ¦ --- ¦ ¦ 1 ¦ LV 스위치 보드 ¦ ¦ 2 ¦ HV/LV 변압기 ¦ ¦ 3 ¦ 기기/설비 ¦ ¦ 4 ¦ 주 접지 단자 ¦ ¦ 5 ¦ 중간 접지 단자 ¦ ¦ 6 ¦ SPDA ¦ ¦ OCPD1 ¦ 설비 공급점의 과전류 보호장치 ¦ ¦ SPD ¦ 서지 보호장치 ¦ OCPD2 과전류 보호장치 (필요한 경우) RCD 잔류 전류 장치 그림 C.3 - TT 계통에서 주 RCD 의 후단에서 부하측 SPDA 설비의 예시 48 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
56578e19-de30-4f9a-a185-7b76b07ef5e6 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 ![image](/image/placeholder) L1 L1 R L2 L2 0CPD1 C L3 L3 D N N PE 0CPD2 SPD 5a H 5b I ○ 4 여기에서 OCPD1 설비 공급점의 과전류 보호장치 SPD 서지 보호장치 OCPD2 과전류 보호장치 (필요한 경우) 4 주 접지 단자 5a, 5b 서지 보호장치의 접지 연결, 5a 및/또는 5b 둘 다 (요구될 경우) RCD 잔류 전류 장치 그림 C.4 - TT 계통에서 주 RCD 의 후단에서 부하측 SPD 설비의 예시 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 49 | {}
527cebe7-5c33-467d-b5bc-fb2f08390299 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 C.2 TN-C 및 TN-C-S 계통 - 3 상 전원 ![image](/image/placeholder) 2 1 1 o L2 C c P P L3 D 3 D 1 PEN 6 OCPD2 SPD PEN THE 5 4 여기에서 ¦ 1 ¦ LV 스위치 보드 ¦ ¦ --- ¦ --- ¦ ¦ 2 ¦ HV/LV 변압기 ¦ ¦ 3 ¦ 기기/설비 ¦ ¦ 4 ¦ 주 접지 단자 ¦ ¦ 5 ¦ 중간 접지 단자 ¦ ¦ 6 ¦ SPDA ¦ ¦ OCPD1 ¦ 설비 공급점의 과전류 보호장치 ¦ ¦ SPD ¦ 서지 보호장치 ¦ ¦ OCPD2 ¦ 과전류 보호장치 (필요한 경우) ¦ 그림 C.5 - TN-C 계통에서 SPDA 설비의 예시 50 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
3f4fe34e-b445-45c1-b9fd-fec0fc723d2e | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 ![image](/image/placeholder) L 1 L1 L2 L2 0CPD1 L3 L3 PEN PEN 0CPD2 SPD 5a 45b 。 4 여기에서 OCPD1 설비 공급점의 과전류 보호장치 SPD 서지 보호장치 OCPD2 과전류 보호장치 (필요한 경우) 4 주 접지 단자 5a, 5b 서지 보호장치의 접지 연결, 5a 및/또는 5b 둘 다 (요구될 경우) 그림 C.6 - TN-C 계통에서 연결 형태 CT1 의 SPD 설비 예시 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 51 | {}
dc5a20ca-bbaf-4550-85dc-f584467a06dd | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 ![image](/image/placeholder) L1 L1 L2 L2 0CPD1 L3 L3 N PEN PE 0CPD2 SPD SPD*) 5a 5b 4 ¦ 여기에서 ¦ 여기에서 ¦ ¦ --- ¦ --- ¦ ¦ OCPD1 ¦ 설비 공급점의 과전류 보호장치 ¦ ¦ SPD ¦ 서지 보호장치 ¦ ¦ *) ¦ 534.4.3 참조 ¦ ¦ OCPD2 ¦ 과전류 보호장치 (필요한 경우) ¦ ¦ 4 ¦ 주 접지 단자 ¦ 5a, 5b 서지 보호장치의 접지 연결, 5a 및/또는 5b 둘 다(요구될 경우) 그림 C.7 - 전단의 SPD 의 설비 공급점에서 PEN 이 PE 와 N 으로 분리되는 지점의 TN-C-S 계통에서 SPD 설비의 예시 52 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f6ece7a0-0ef7-4f5e-b8e6-6e150f60e1a4 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 ![image](/image/placeholder) L1 。 L2 0CPD1 。 。 L3 。 o N 。 PE ○ 。 PEN 0CPD2 0CPD2 OCPD2 SPD cas SPD 5a 5b 4 ¦ 여기에서 ¦ 여기에서 ¦ ¦ --- ¦ --- ¦ ¦ OCPD1 ¦ 설비 공급점의 과전류 보호장치 ¦ ¦ SPD ¦ 서지 보호장치 ¦ ¦ *) ¦ 534.4.3 참조 ¦ ¦ OCPD2 ¦ 과전류 보호장치 (필요한 경우) ¦ 4 주 접지 단자 5a, 5b 서지 보호장치의 접지 연결, 5a 및/또는 5b 둘 다(요구될 경우) 그림 C.8 - 서로 다른 배전반의 TN-C-S 내의 SPD 설비 예시 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 53 | {}
26714a78-1954-4197-bbb5-fb95090a7af6 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 C.3 TN-S 계통 - 3 상 전원과 중성 ![image](/image/placeholder) 2 1 1 L2 0 o C c L3 3 P P N D D 1 PE 6 OCPD2 SPD PE [*][*] 5 4 여기에서 1 LV 스위치 보드 2 HV/LV 변압기 3 기기/설비 4 주 접지 단자 5 중간 접지 단자 6 SPDA OCPD1 설비 공급점의 과전류 보호장치 SPD 서지 보호장치 OCPD2 과전류 보호장치 (필요한 경우) 그림 C.9 - TN-S 계통에서 SPDA 설비의 예시 54 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
b22bb124-3ac0-4ba3-b4a5-340eae08ab5d | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 ![image](/image/placeholder) L1 L1 L2 L2 0CPD1 L3 L3 N N PE PE OCPD2 SPD 5a 5b 수 4 여기에서 OCPD1 설비 공급점의 과전류 보호장치 SPD 서지 보호장치 *) 534.4.3 참조 OCPD2 과전류 보호장치 (필요한 경우) 4 주 접지 단자 5a, 5b 서지 보호장치의 접지 연결, 5a 및/또는 5b 둘 다 (요구될 경우) 그림 C. 10 - TN-S 에서 SPD 설비의 예시 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 55 | {}
71aa0ecc-a82e-4835-bc18-2e416c813710 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 C.4 IT 계통 - 중성이 있거나 없는 3 상 전원 ![image](/image/placeholder) 1 2 1 0 L2 C o L3 P c 3 D P N 1 D PE 6 OCPD2 SPD PE outhe] 5 4 여기에서 1 LV 스위치 보드 2 HV/LV 변압기 3 기기/설비 4 주 접지 단자 5 중간 접지 단자 6 SPDA 7 임피던스 OCPD1 설비 공급점의 과전류 보호장치 SPD 서지 보호장치 OCPD2 과전류 보호장치 (필요한 경우) 그림 C.11 - 중성이 있는 IT 계통에서 SPDA 설비의 예시 56 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
1bc774b8-a605-44cf-a629-986c8704e687 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 ![image](/image/placeholder) L1 L1 L2 L2 0CPD1 L3 L3 PE 0CPD2 개방 임피던스 또는 높은 임피던스 Z SPD 5a 5b + 4 여기에서 OCPD1 설비 공급점의 과전류 보호장치 SPD 서지 보호장치 OCPD2 과전류 보호장치 (필요한 경우) 4 주 접지 단자 5a, 5b 서지 보호장치의 접지 연결, 5a 및/또는 5b 둘 다(요구될 경우) 그림 C.12 - 중성이 없는 IT 계통에서 SPDA 설비의 예시 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 57 | {}
87ae6e90-57ff-4a6f-8165-f7c0a2f2da54 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 ![image](/image/placeholder) L1 L1 L2 L2 0CPD1 L3 L3 N N PE 0CPD2 *) 개방 임피던스 Z 또는 높은 임피던스 SPD 5b 5a *) ¦ 4 여기에서 OCPD1 설비 공급점의 과전류 보호장치 SPD 서지 보호장치 OCPD2 과전류 보호장치 (필요한 경우) 4 주 접지 단자 5a, 5b 서지 보호장치의 접지 연결, 5a 및/또는 5b 둘 다 (요구될 경우) 그림 C.13 - 중성이 있는 IT 계통에서 SPD 설비의 예시 58 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
f2af44da-7708-432b-8f5c-13d4c7353fdf | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 부속서 D (참고) 가공선로에 의해 공급되는 설비 IEC 60364-44:2007/AMD1:2015 의 443 절에 따라 과전압 보호가 필요할 때 건물에 들어가는 선이 가 공 전력선이고 건물에 가까운 가공전력선의 마지막 극에 낙뢰가 치는 것을 고려한 경우 설비의 공급 점에 있는 SPD 는 표 D.1 에 따라 선정해야 한다. 추가 정보는 IEC 62305(모든 파트)에서 찾을 수 있다. 표 D.1 - 임펄스 방전 전류(Iimp)의 선정 ¦ 연결 ¦ Iimp (kA) ¦ Iimp (kA) ¦ Iimp (kA) ¦ Iimp (kA) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 연결 ¦ 전원 계통 ¦ 전원 계통 ¦ 전원 계통 ¦ 전원 계통 ¦ ¦ 연결 ¦ 단상 ¦ 단상 ¦ 3 상 ¦ 3 상 ¦ ¦ 연결 ¦ CT1 ¦ CT2 ¦ CT1 ¦ CT2 ¦ ¦ L-N ¦ ¦ 5 ¦ ¦ 5 ¦ ¦ L- PE ¦ 5 ¦ ¦ 5 ¦ ¦ ¦ N- PE ¦ 5 ¦ 10 ¦ 5 ¦ 20 ¦ 비고 이 표는 낙뢰 보호 수준 III 및 IV 를 나타낸다. 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 59 | {}
56700a4d-1938-4781-ba56-500de05d922a | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 부속서 E (인용) 절연 및 개폐용 장치의 참조 표준 표 E.1 - 절연 및 개폐를 위한 장치 ¦ 장치 ¦ 표준 ¦ 다음에 적합함 ¦ 다음에 적합함 ¦ 다음에 적합함 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 장치 ¦ 표준 ¦ 절연 ¦ 기능적 개폐 및 제어 ¦ 비상 전원 차단 ¦ ¦ 개폐 단로기 ¦ IEC 60947-3 a ¦ Yes ¦ Yes ¦ Yes ¦ ¦ 개폐 단로기 ¦ IEC 62626-1 a ¦ Yes ¦ Yes ¦ Yes ¦ ¦ 개폐 단로기 ¦ IEC 60669-2-4 ¦ Yes ¦ Yes ¦ Yes ¦ ¦ 개폐 단로기 ¦ IEC 60669-2-6 ¦ Yes ¦ No ¦ Yes ¦ ¦ 단로기 ¦ IEC 60669-2-4 b ¦ Yes ¦ No ¦ No ¦ ¦ 단로기 ¦ IEC 60947-3 b ¦ Yes ¦ No ¦ No ¦ ¦ 개폐기 ¦ IEC 60669-1 ¦ No ¦ Yes ¦ No ¦ ¦ 개폐기 ¦ IEC 60669-2-1 ¦ No ¦ Yes ¦ No ¦ ¦ 개폐기 ¦ IEC 60669-2-2 ¦ No ¦ Yes ¦ No ¦ ¦ 개폐기 ¦ IEC 60669-2-3 ¦ No ¦ Yes ¦ No ¦ ¦ 개폐기 ¦ IEC 60669-2-5 ¦ No ¦ Yes ¦ No ¦ ¦ 개폐기 ¦ IEC 60947-3 c ¦ No ¦ Yes ¦ No ¦ ¦ 개폐기 ¦ IEC 60947-5-1 ¦ No ¦ Yes ¦ No ¦ ¦ 접촉기 ¦ IEC 60947-4-1 ¦ No ¦ Yes ¦ No ¦ ¦ 접촉기 ¦ IEC 61095 ¦ No ¦ Yes ¦ No ¦ ¦ 스타터 ¦ IEC 60947-4-1 ¦ Yes b ¦ Yes ¦ Yes b ¦ ¦ 스타터 ¦ IEC 60947-4-2 ¦ No ¦ Yes ¦ No ¦ ¦ 스타터 ¦ IEC 60947-4-3 ¦ No ¦ Yes ¦ No ¦ ¦ 회로 차단기 ¦ IEC 60898-1 ¦ Yes ¦ No ¦ Yes ¦ ¦ 회로 차단기 ¦ IEC 60898-2 ¦ Yes ¦ No ¦ Yes ¦ ¦ 회로 차단기 ¦ IEC 60947-2 ¦ b Yes ¦ No ¦ b Yes ¦ ¦ 누전차단기(RCD) ¦ IEC 60947-2 ¦ Yes b ¦ No ¦ Yes b ¦ ¦ 누전차단기(RCD) ¦ IEC 61008 (all parts) ¦ Yes ¦ No ¦ Yes ¦ ¦ 누전차단기(RCD) ¦ IEC 61009 (all parts) ¦ Yes ¦ No ¦ Yes ¦ ¦ 누전차단기(RCD) ¦ IEC 62423 ¦ Yes ¦ No ¦ Yes ¦ ¦ 아크고장 검출장치 ¦ IEC 62606 ¦ Yes ¦ No ¦ Yes ¦ ¦ 플러그 및 콘센트 ¦ IEC 60309 (all parts) ¦ Yes ¦ Yes d ¦ No ¦ ¦ 플러그 및 콘센트 ¦ IEC 60884 (all parts) ¦ Yes ¦ Yes d ¦ No ¦ ¦ 플러그 및 콘센트 ¦ IEC 60906 (all parts) ¦ Yes ¦ d Yes ¦ No ¦ 60 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
55dc696f-115f-41fd-a846-2661313c7f3c | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 ¦ 등기구의 연결을 위한 장 치 ¦ IEC 61995 (all parts) ¦ Yes e ¦ No ¦ No ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 전환 개폐 장치 ¦ IEC 60947-6-1 ¦ b Yes ¦ Yes ¦ b Yes ¦ ¦ 기기를 위한 제어 및 보 호 개폐 장치(CPS) ¦ IEC 60947-6-2 ¦ Yes b ¦ Yes ¦ Yes b ¦ ¦ 장치 ¦ 표준 ¦ 다음에 적합함 ¦ 다음에 적합함 ¦ 다음에 적합함 ¦ ¦ 장치 ¦ 표준 ¦ 절연 ¦ 기능적 개폐 및 제어 ¦ 비상 전원 차단 ¦ ¦ 퓨즈 ¦ IEC 60269-2 IEC 60269-3 IEC 60269-4 ¦ Yes f Yes Yes ↑ ¦ No No No ¦ No No No ¦ ¦ 퓨즈 조합 유닛 ¦ IEC 60947-3 ¦ b Yes ¦ a No ¦ a,b Yes ¦ ¦ 접촉기 g ¦ IEC 61984 ¦ Yes h ¦ No ¦ No ¦ ¦ 여기에서 Yes 기능이 제공됨 No 기능이 제공되지 않음 a 기호 또는 IEC 60947-3 혹은 IEC 62626-1 를 따른 기호들의 조합으로 표시돼 있는 경 우 b 장치가 절연에 적합하고 기호 -로 표식이 돼있는 경우만 기능이 제공됨 (IEC 60417-6169- 1:2012-08) C 기호 또는 IEC 60947-3 를 따른 기호들의 조합으로 표시돼 있는 경우. d 이하의 교류 플러그와 콘센트만 기능적 개폐를 위해 사용될 수 있다. 16A e 장치가 부하 시 절연에 적합하다. f 제조자에 의해 명시된 경우 g 연결 및 배선 단자는 제조자 혹은 디자이너의 문서에 따라 절연 기능을 제공할 수 있다. h 차단 용량(CBC, Connector with Breaking Capacity)이 있는 접촉기만 live 부하 혹은 under 부하에 서 결합 및 분리되도록 설계된다(IEC 61984:2008, 3.8 참조). ¦ 여기에서 Yes 기능이 제공됨 No 기능이 제공되지 않음 a 기호 또는 IEC 60947-3 혹은 IEC 62626-1 를 따른 기호들의 조합으로 표시돼 있는 경 우 b 장치가 절연에 적합하고 기호 -로 표식이 돼있는 경우만 기능이 제공됨 (IEC 60417-6169- 1:2012-08) C 기호 또는 IEC 60947-3 를 따른 기호들의 조합으로 표시돼 있는 경우. d 이하의 교류 플러그와 콘센트만 기능적 개폐를 위해 사용될 수 있다. 16A e 장치가 부하 시 절연에 적합하다. f 제조자에 의해 명시된 경우 g 연결 및 배선 단자는 제조자 혹은 디자이너의 문서에 따라 절연 기능을 제공할 수 있다. h 차단 용량(CBC, Connector with Breaking Capacity)이 있는 접촉기만 live 부하 혹은 under 부하에 서 결합 및 분리되도록 설계된다(IEC 61984:2008, 3.8 참조). ¦ 여기에서 Yes 기능이 제공됨 No 기능이 제공되지 않음 a 기호 또는 IEC 60947-3 혹은 IEC 62626-1 를 따른 기호들의 조합으로 표시돼 있는 경 우 b 장치가 절연에 적합하고 기호 -로 표식이 돼있는 경우만 기능이 제공됨 (IEC 60417-6169- 1:2012-08) C 기호 또는 IEC 60947-3 를 따른 기호들의 조합으로 표시돼 있는 경우. d 이하의 교류 플러그와 콘센트만 기능적 개폐를 위해 사용될 수 있다. 16A e 장치가 부하 시 절연에 적합하다. f 제조자에 의해 명시된 경우 g 연결 및 배선 단자는 제조자 혹은 디자이너의 문서에 따라 절연 기능을 제공할 수 있다. h 차단 용량(CBC, Connector with Breaking Capacity)이 있는 접촉기만 live 부하 혹은 under 부하에 서 결합 및 분리되도록 설계된다(IEC 61984:2008, 3.8 참조). ¦ 여기에서 Yes 기능이 제공됨 No 기능이 제공되지 않음 a 기호 또는 IEC 60947-3 혹은 IEC 62626-1 를 따른 기호들의 조합으로 표시돼 있는 경 우 b 장치가 절연에 적합하고 기호 -로 표식이 돼있는 경우만 기능이 제공됨 (IEC 60417-6169- 1:2012-08) C 기호 또는 IEC 60947-3 를 따른 기호들의 조합으로 표시돼 있는 경우. d 이하의 교류 플러그와 콘센트만 기능적 개폐를 위해 사용될 수 있다. 16A e 장치가 부하 시 절연에 적합하다. f 제조자에 의해 명시된 경우 g 연결 및 배선 단자는 제조자 혹은 디자이너의 문서에 따라 절연 기능을 제공할 수 있다. h 차단 용량(CBC, Connector with Breaking Capacity)이 있는 접촉기만 live 부하 혹은 under 부하에 서 결합 및 분리되도록 설계된다(IEC 61984:2008, 3.8 참조). ¦ 여기에서 Yes 기능이 제공됨 No 기능이 제공되지 않음 a 기호 또는 IEC 60947-3 혹은 IEC 62626-1 를 따른 기호들의 조합으로 표시돼 있는 경 우 b 장치가 절연에 적합하고 기호 -로 표식이 돼있는 경우만 기능이 제공됨 (IEC 60417-6169- 1:2012-08) C 기호 또는 IEC 60947-3 를 따른 기호들의 조합으로 표시돼 있는 경우. d 이하의 교류 플러그와 콘센트만 기능적 개폐를 위해 사용될 수 있다. 16A e 장치가 부하 시 절연에 적합하다. f 제조자에 의해 명시된 경우 g 연결 및 배선 단자는 제조자 혹은 디자이너의 문서에 따라 절연 기능을 제공할 수 있다. h 차단 용량(CBC, Connector with Breaking Capacity)이 있는 접촉기만 live 부하 혹은 under 부하에 서 결합 및 분리되도록 설계된다(IEC 61984:2008, 3.8 참조). ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 61 | {}
2307a661-18a5-4763-af16-6f1e2e02d4e6 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 부속서 F (참고) 특정 국가들에 관한 비고 목록 ¦ 국가 ¦ 부속절 ¦ 내용 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ IT ¦ 532.2 ¦ 이탈리아에서는 532.2 가 적용되지 않는다. 이탈리아에서는 국가 표 준 CEI 64-8 의 751 절 "Ambienti a Caso di incendio"에 화재 위험이 있는 지역에 대한 분류와 요구사항이 제시되어 있다. ¦ ¦ DE ¦ 532.2.2 ¦ 독일에서는 "Muster-Richtlinie �ber brandschutztechnische Anforderungen an Leitungsanlagen (MusterLeitungsanlagen-Richtlinie MLAR)" 가 적용된다. ¦ ¦ DE ¦ 532.2.3.2 ¦ 독일에서는 교류 형식 RCD 가 허용되지 않는다. ¦ ¦ ZA ¦ 532.2.3.2 ¦ 남아프리카에서는 IEC 61008 및 IEC 61009 를 준수하는 제품의 사 용이 금지된다. ¦ ¦ DE ¦ 532.2.3.3 ¦ 독일에서는 해당 문단이 다음으로 교체된다: 532.2.3.3 TN- 및 TT- 계통에서의 잔류 전류 감시 장치(RCM)의 선 정 잔류 전류 감시 장치(RCM)는 IEC 62020 에 부합해야 한다. 화재 위험을 방지하기 위해 잔류 전류 감시 장치(RCM)가 선정될 때 정격 잔류 경고 수준은 300 mA 를 초과 하면 안된다. 응답 값을 합리적으로 낮게 설정해서 고장 시에 고장이 최대한 빨 리 표시되는게 권장된다. ¦ ¦ DE ¦ 533.1.2.1 ¦ 독일에서는 IEC 61009-2-2 가 적용되지 않는다. ¦ ¦ GB ¦ 533.1.2.1 ¦ 영국에서 과전류 보호를 위한 장치는 다음 표준 중 하나 이상을 준 수해야 한다: BS 88 시리즈 BS 646 BS 1362 BS 3036 BS EN 60898-1 및 -2 BS EN 60947-2, -3 및 -6-2 BS EN 60947-4-1, -6-1 및 -6-2 BS EN 61009-1, -2-1 및 BS IEC 61009-2-2- BS EN 62423. 시간/전류 특성이 위에 나열된 장치가 제공하는 수준 이상의 보호 수준을 제공한다면 다른 기기의 사용을 배제하지 않는다. 다음 보호장치들은 단락 전류 및 접지 고장 전류에 대한 보호에서 만 사용될 수 있다: BS EN 609472:2017, 부속서 O 에 따른 순간 트립 회로 차단기(ICB). HD 60269-2 또는 HD 60269-3 에 따른 aM 및 aR 유형 퓨즈. ¦ ¦ DE ¦ 533.1.2.1, 첫 번째 문단 ¦ 독일에서는 DIN VDE 0641-21(VDE 0641-21)도 적용된다. ¦ 62 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
c0072cff-22d7-4749-8d02-715d1f4b55d9 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 ¦ 국가 ¦ 부속절 ¦ 내용 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ US ¦ 533.2.1 ¦ 미국에서는 과전류 및 과부하 보호에 대한 요구사항이 NFPA 70 NEC 에 명시되어 있다. ¦ ¦ NO ¦ 533.2.1, 첫번째 단락 ¦ 노르웨이에서는 a) - c)의 요구사항 외에도 다음과 같은 사항이 적 용된다: 보호장치가 PVC 로 절연되고 단면적이 4 mm2 를 초과 하지 않는 배 선 시스템을 보호할 때 정격 전류는 다음과 같아야 한다: IEC 604364-552:2009, 표 B.52.1 의 기준 설치 방법 A1 또는 A2 에 따르는 단면적이 1.5 mm2 인 배선 시스템의 경우 10A 이하 IEC 604364-5-52:2009, 표 B.52.1 의 A1 및 A2 와 다른 기준 설치 방 법이고 단면적이 1.5 mm2 인 배선 시스템의 경우 13A 혹은 그 이하 단면적이 2.5 mm2 인 배선 시스템의 경우 16A 혹은 그 이하 IEC 604364-552:2009, 표 B.52.1 의 기준 설치 방법 A1 또는 A2 에 따르는 단면적이 4 mm2 인 배선 시스템의 경우 20A 혹은 그 이하 IEC 604364-5-52:2009, 표 B.52.1 의 A1 및 A2 와 다른 기준 설치 방 법이고 단면적이 4 mm2 인 배선 시스템의 경우 25A 혹은 그 이하 ¦ ¦ DE ¦ 533.2.1, 비고 1 ¦ 독일에서는 DIN VDE 0641-21(VDE 0641-21)도 적용된다. ¦ ¦ DE ¦ 533.2.1 ¦ 독일에서는 다음과 같은 요구사항이 적용되지 않는다: 중성선의 등가 구리 단면적이 상전선보다 작을 경우 IEC60364-4- 43 을 준수하여 중성선 과부하 보호를 제공해야 한다. 이 요구사항 을 위하여 중성선의 전류 운반용량을 알아야한다. 일반적으로 제조 자로부터 얻을 수 있다. 비고 2 중성선의 전류 운반 용량은 같은 도체 단면적을 갖고, IEC 60364-5-52:2009, 523 절을 따른 중성선의 설치와 건축 조건이 같 은 회로와 같은 것으로 볼 수 있다 ¦ ¦ DE ¦ 533.3.1.1 ¦ 독일에서는 다음과 같은 비고가 부속절 끝에 추가된다: 비고 3 회로 차단기가 과전류 보호에 사용되는 경우, 이 조건은 회 로 차단기가 EN 60898-1 에 따른 에너지 제한 등급 3 의 요구사항을 만족하면 충족된다. ¦ ¦ DE ¦ 533.3.1.1 ¦ 독일에서는 다음과 같은 요구사항이 부속절 끝에 추가된다: 회로 차단기는 최소 6kA 의 생산 및 차단 용량을 가져야 한다. 적용 이 되는 경우, 이러한 회로 차단기는 EN 60898-1 에 따른 에너지 제 한 등급 3 의 요구사항을 충족해야 한다. ¦ ¦ DE ¦ 533.3.2 ¦ 독일에서 회로 차단기는 최소 6 kA 의 투입 및 차단 용량을 가져야 한다. 적용이 되는 경우, 이러한 회로 차단기는 EN 60898-1 에 따른 에너지 제한 등급 3 의 요구사항을 충족해야 한다. ¦ ¦ DE ¦ 533.4.2.2 ¦ 부속절 A 는 독일에서 적용되지 않는다. ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 63 | {}
4a5c47f5-bb3e-4269-a705-01c3340cd1e4 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 ¦ 국가 ¦ 부속절 ¦ 내용 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ DE ¦ 533.4.2.3 ¦ 독일에서는 다음과 같은 상황일 때도 과부하에 대한 보호장치가 제 공되지 않아도 된다: c) 회로의 과부하가 위험을 야기하지 않는 접지된 케이블 또는 오 버헤드 라인으로 구성된 배전 회로 ¦ ¦ DE ¦ 533.4.3.2 ¦ 독일에서는 비고 1 이 다음과 같다: 비고 1 이 조건은 예를 들어 배선의 외부 영향에 대한 보호를 강화 해서 본질적으로 단락 및 접지 고장 방지를 설치함으로써 얻는다. ¦ ¦ DE ¦ 533.4.3.2 ¦ 부속절 B 는 독일에서 적용되지 않는다. ¦ ¦ DE ¦ 533.4.3.4 ¦ 독일에서는 접지된 케이블 또는 오버헤드 라인으로 구성된 배전회 로에서 단락방지를 위한 장치의 누락이 추가적으로 허용된다. ¦ ¦ DE ¦ 534.4.1 ¦ 독일에서는 건물의 설비가 오버헤드 라인으로 전원을 받을 때 SPD 는 부속절 D 에따라 시험 등급 ISPD 이어야 한다. ¦ ¦ FR ¦ 534.4.1 ¦ 프랑스에서는 다음이 적용되지 않는다: 구조물에 외부 피뢰 시스템이 장착되지 않은 경우와 마지막 극과 설비 입구 사이의 오버헤드 라인에 직접적인 낙뢰가 발생하는 경우 를 고려할 때는 전기 설비의 시작점 또는 근처에는 부속서 D 를 참 고한 시험 등급 ISPD 를 사용해야 한다 ¦ ¦ GR ¦ 534.4.1 ¦ 그리스에서는 다음이 적용되지 않는다: 구조물에 외부 피뢰 시스템이 장착되지 않은 경우와 마지막 극과 설비 입구 사이의 오버헤드 라인에 직접적인 낙뢰가 발생하는 경우 를 고려할 때는 전기 설비의 시작점 또는 근처에는 부속서 D 를 참 고한 시험 등급 ISPD 를 사용해야 한다 ¦ ¦ HU ¦ 534.4.1 ¦ 헝가리에서는 다음이 적용되지 않는다: 구조물에 외부 피뢰 시스템이 장착되지 않은 경우와 마지막 극과 설비 입구 사이의 오버헤드 라인에 직접적인 낙뢰가 발생하는 경우 를 고려할 때는 전기 설비의 시작점 또는 근처에는 부속서 D 를 참 고한 시험 등급 ISPD 를 사용해야 한다 ¦ 64 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
568187f8-67f6-451d-a9e7-a0dc1626fed8 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 ¦ 국가 ¦ 부속절 ¦ 내용 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ ES ¦ 534.4.1 ¦ 스페인에서는 설비의 공급점이 전원이 건물에 들어오는 지점 및/또 는 전원이 주 배전반에 들어오는 지점이 될 수 있다. Local 。 vivienda de usuario 13 12 11 8 10 Wh CPM 9 2 IEC 소유); 주 회로 ¦ ¦ ES ¦ 534.4.1 ¦ 여기에서 1 공공 전원; 2 전원 케이블(공익사업의 8 민간 배전 회로; 9 퓨즈 (차단된);10 계량기; 11 차단기; 12 스위치 보드; 13 개인 설비 표 F.1 - 단독 사용자 Viviendas Locales de de usuarios usuarios 13 13 主 13 丰 13 丰 13 12 12� 12□ 12□ 12□ 11 호 110 11 호 11 호 8 8 7 10 10 10 10 10 Whi Whi Wh Wh¦ wh] ⌀9 ⌀9 ⌀9 ⌀9 09 5 IEC 여기에서 1 공공 전원; 2 전원 케이블(공익사업의 소유); 4 민간 설비의 전원 케이블; 5 주 개폐 장치; 7 계량 실 8 개별 배전 회로; 9 퓨즈 (차 단된);10 계량기; 11 주 회로 차단기; 12 스위치 보드; 13 민간 설비 표 F.2 - 여러 사용자 ¦ ¦ DE ¦ 534.4.3 ¦ 독일에서는 최대 거리 0.5 m 제한만이 고려해야할 유일한 요구사항 ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 65 | {}
639208fc-d94e-41dd-9705-5eaf42386750 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 ¦ ¦ ¦ 이다. ¦ 이다. ¦ 이다. ¦ 이다. ¦ 이다. ¦ 이다. ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 국가 ¦ 부속절 ¦ 내용 ¦ 내용 ¦ 내용 ¦ 내용 ¦ 내용 ¦ 내용 ¦ ¦ NO ¦ 534.4.4.3 ¦ 노르웨이에서 설비가 공공 IT 분배 네트워크에 전기적으로 연결된 곳은 설비의 공급점에 위치한 SPD 에 필요한 최소 Uc 는 350 V 이 상이다. ¦ 노르웨이에서 설비가 공공 IT 분배 네트워크에 전기적으로 연결된 곳은 설비의 공급점에 위치한 SPD 에 필요한 최소 Uc 는 350 V 이 상이다. ¦ 노르웨이에서 설비가 공공 IT 분배 네트워크에 전기적으로 연결된 곳은 설비의 공급점에 위치한 SPD 에 필요한 최소 Uc 는 350 V 이 상이다. ¦ 노르웨이에서 설비가 공공 IT 분배 네트워크에 전기적으로 연결된 곳은 설비의 공급점에 위치한 SPD 에 필요한 최소 Uc 는 350 V 이 상이다. ¦ 노르웨이에서 설비가 공공 IT 분배 네트워크에 전기적으로 연결된 곳은 설비의 공급점에 위치한 SPD 에 필요한 최소 Uc 는 350 V 이 상이다. ¦ 노르웨이에서 설비가 공공 IT 분배 네트워크에 전기적으로 연결된 곳은 설비의 공급점에 위치한 SPD 에 필요한 최소 Uc 는 350 V 이 상이다. ¦ ¦ DE ¦ 534.4.4.4.1 ¦ 수준이 증가된 시험 등 설비의 공급점 혹은 그 근처에 설치된 안전 급 II SPD 가 예를 들어 a) 인명 관리, b) 공공 서비스 및 문화 유산 에 영향을 끼치면 공칭 방전 전류 In 은 다음 표 3 에 주어진 값 이상 이어야 한다. Table 3 - 안전 수준이 증가된 설비의 전원 계통과 연결 형태에 따 른 In (kA) 연결 계통 단상 3 상 ¦ 수준이 증가된 시험 등 설비의 공급점 혹은 그 근처에 설치된 안전 급 II SPD 가 예를 들어 a) 인명 관리, b) 공공 서비스 및 문화 유산 에 영향을 끼치면 공칭 방전 전류 In 은 다음 표 3 에 주어진 값 이상 이어야 한다. Table 3 - 안전 수준이 증가된 설비의 전원 계통과 연결 형태에 따 른 In (kA) 연결 계통 단상 3 상 ¦ 수준이 증가된 시험 등 설비의 공급점 혹은 그 근처에 설치된 안전 급 II SPD 가 예를 들어 a) 인명 관리, b) 공공 서비스 및 문화 유산 에 영향을 끼치면 공칭 방전 전류 In 은 다음 표 3 에 주어진 값 이상 이어야 한다. Table 3 - 안전 수준이 증가된 설비의 전원 계통과 연결 형태에 따 른 In (kA) 연결 계통 단상 3 상 ¦ 수준이 증가된 시험 등 설비의 공급점 혹은 그 근처에 설치된 안전 급 II SPD 가 예를 들어 a) 인명 관리, b) 공공 서비스 및 문화 유산 에 영향을 끼치면 공칭 방전 전류 In 은 다음 표 3 에 주어진 값 이상 이어야 한다. Table 3 - 안전 수준이 증가된 설비의 전원 계통과 연결 형태에 따 른 In (kA) 연결 계통 단상 3 상 ¦ 수준이 증가된 시험 등 설비의 공급점 혹은 그 근처에 설치된 안전 급 II SPD 가 예를 들어 a) 인명 관리, b) 공공 서비스 및 문화 유산 에 영향을 끼치면 공칭 방전 전류 In 은 다음 표 3 에 주어진 값 이상 이어야 한다. Table 3 - 안전 수준이 증가된 설비의 전원 계통과 연결 형태에 따 른 In (kA) 연결 계통 단상 3 상 ¦ 수준이 증가된 시험 등 설비의 공급점 혹은 그 근처에 설치된 안전 급 II SPD 가 예를 들어 a) 인명 관리, b) 공공 서비스 및 문화 유산 에 영향을 끼치면 공칭 방전 전류 In 은 다음 표 3 에 주어진 값 이상 이어야 한다. Table 3 - 안전 수준이 증가된 설비의 전원 계통과 연결 형태에 따 른 In (kA) 연결 계통 단상 3 상 ¦ ¦ DE ¦ 534.4.4.4.1 ¦ 수준이 증가된 시험 등 설비의 공급점 혹은 그 근처에 설치된 안전 급 II SPD 가 예를 들어 a) 인명 관리, b) 공공 서비스 및 문화 유산 에 영향을 끼치면 공칭 방전 전류 In 은 다음 표 3 에 주어진 값 이상 이어야 한다. Table 3 - 안전 수준이 증가된 설비의 전원 계통과 연결 형태에 따 른 In (kA) 연결 계통 단상 3 상 ¦ 수준이 증가된 시험 등 설비의 공급점 혹은 그 근처에 설치된 안전 급 II SPD 가 예를 들어 a) 인명 관리, b) 공공 서비스 및 문화 유산 에 영향을 끼치면 공칭 방전 전류 In 은 다음 표 3 에 주어진 값 이상 이어야 한다. Table 3 - 안전 수준이 증가된 설비의 전원 계통과 연결 형태에 따 른 In (kA) 연결 계통 단상 3 상 ¦ 수준이 증가된 시험 등 설비의 공급점 혹은 그 근처에 설치된 안전 급 II SPD 가 예를 들어 a) 인명 관리, b) 공공 서비스 및 문화 유산 에 영향을 끼치면 공칭 방전 전류 In 은 다음 표 3 에 주어진 값 이상 이어야 한다. Table 3 - 안전 수준이 증가된 설비의 전원 계통과 연결 형태에 따 른 In (kA) 연결 계통 단상 3 상 ¦ 수준이 증가된 시험 등 설비의 공급점 혹은 그 근처에 설치된 안전 급 II SPD 가 예를 들어 a) 인명 관리, b) 공공 서비스 및 문화 유산 에 영향을 끼치면 공칭 방전 전류 In 은 다음 표 3 에 주어진 값 이상 이어야 한다. Table 3 - 안전 수준이 증가된 설비의 전원 계통과 연결 형태에 따 른 In (kA) 연결 계통 단상 3 상 ¦ 수준이 증가된 시험 등 설비의 공급점 혹은 그 근처에 설치된 안전 급 II SPD 가 예를 들어 a) 인명 관리, b) 공공 서비스 및 문화 유산 에 영향을 끼치면 공칭 방전 전류 In 은 다음 표 3 에 주어진 값 이상 이어야 한다. Table 3 - 안전 수준이 증가된 설비의 전원 계통과 연결 형태에 따 른 In (kA) 연결 계통 단상 3 상 ¦ 수준이 증가된 시험 등 설비의 공급점 혹은 그 근처에 설치된 안전 급 II SPD 가 예를 들어 a) 인명 관리, b) 공공 서비스 및 문화 유산 에 영향을 끼치면 공칭 방전 전류 In 은 다음 표 3 에 주어진 값 이상 이어야 한다. Table 3 - 안전 수준이 증가된 설비의 전원 계통과 연결 형태에 따 른 In (kA) 연결 계통 단상 3 상 ¦ ¦ DE ¦ 534.4.4.4.1 ¦ 수준이 증가된 시험 등 설비의 공급점 혹은 그 근처에 설치된 안전 급 II SPD 가 예를 들어 a) 인명 관리, b) 공공 서비스 및 문화 유산 에 영향을 끼치면 공칭 방전 전류 In 은 다음 표 3 에 주어진 값 이상 이어야 한다. Table 3 - 안전 수준이 증가된 설비의 전원 계통과 연결 형태에 따 른 In (kA) 연결 계통 단상 3 상 ¦ 수준이 증가된 시험 등 설비의 공급점 혹은 그 근처에 설치된 안전 급 II SPD 가 예를 들어 a) 인명 관리, b) 공공 서비스 및 문화 유산 에 영향을 끼치면 공칭 방전 전류 In 은 다음 표 3 에 주어진 값 이상 이어야 한다. Table 3 - 안전 수준이 증가된 설비의 전원 계통과 연결 형태에 따 른 In (kA) 연결 계통 단상 3 상 ¦ 수준이 증가된 시험 등 설비의 공급점 혹은 그 근처에 설치된 안전 급 II SPD 가 예를 들어 a) 인명 관리, b) 공공 서비스 및 문화 유산 에 영향을 끼치면 공칭 방전 전류 In 은 다음 표 3 에 주어진 값 이상 이어야 한다. Table 3 - 안전 수준이 증가된 설비의 전원 계통과 연결 형태에 따 른 In (kA) 연결 계통 단상 3 상 ¦ 수준이 증가된 시험 등 설비의 공급점 혹은 그 근처에 설치된 안전 급 II SPD 가 예를 들어 a) 인명 관리, b) 공공 서비스 및 문화 유산 에 영향을 끼치면 공칭 방전 전류 In 은 다음 표 3 에 주어진 값 이상 이어야 한다. Table 3 - 안전 수준이 증가된 설비의 전원 계통과 연결 형태에 따 른 In (kA) 연결 계통 단상 3 상 ¦ 수준이 증가된 시험 등 설비의 공급점 혹은 그 근처에 설치된 안전 급 II SPD 가 예를 들어 a) 인명 관리, b) 공공 서비스 및 문화 유산 에 영향을 끼치면 공칭 방전 전류 In 은 다음 표 3 에 주어진 값 이상 이어야 한다. Table 3 - 안전 수준이 증가된 설비의 전원 계통과 연결 형태에 따 른 In (kA) 연결 계통 단상 3 상 ¦ 수준이 증가된 시험 등 설비의 공급점 혹은 그 근처에 설치된 안전 급 II SPD 가 예를 들어 a) 인명 관리, b) 공공 서비스 및 문화 유산 에 영향을 끼치면 공칭 방전 전류 In 은 다음 표 3 에 주어진 값 이상 이어야 한다. Table 3 - 안전 수준이 증가된 설비의 전원 계통과 연결 형태에 따 른 In (kA) 연결 계통 단상 3 상 ¦ ¦ NO ¦ 534.4.4.5 ¦ 노르웨이에서는 설비가 공공 IT 분배 네트워크에 전기적으로 연결 되고 두번째 SPD 가 주 배전반에 위치한 SPD 의 후단에 설치된 경 우, 두번째 SPD 의 최대 연속 동작 전압 Uc 는 상전선과 PE 사이에서 최소 440 V 가 되야 하고 상전선들 사이에서는 최소 275 V 가 되야 한다. ¦ 노르웨이에서는 설비가 공공 IT 분배 네트워크에 전기적으로 연결 되고 두번째 SPD 가 주 배전반에 위치한 SPD 의 후단에 설치된 경 우, 두번째 SPD 의 최대 연속 동작 전압 Uc 는 상전선과 PE 사이에서 최소 440 V 가 되야 하고 상전선들 사이에서는 최소 275 V 가 되야 한다. ¦ 노르웨이에서는 설비가 공공 IT 분배 네트워크에 전기적으로 연결 되고 두번째 SPD 가 주 배전반에 위치한 SPD 의 후단에 설치된 경 우, 두번째 SPD 의 최대 연속 동작 전압 Uc 는 상전선과 PE 사이에서 최소 440 V 가 되야 하고 상전선들 사이에서는 최소 275 V 가 되야 한다. ¦ 노르웨이에서는 설비가 공공 IT 분배 네트워크에 전기적으로 연결 되고 두번째 SPD 가 주 배전반에 위치한 SPD 의 후단에 설치된 경 우, 두번째 SPD 의 최대 연속 동작 전압 Uc 는 상전선과 PE 사이에서 최소 440 V 가 되야 하고 상전선들 사이에서는 최소 275 V 가 되야 한다. ¦ 노르웨이에서는 설비가 공공 IT 분배 네트워크에 전기적으로 연결 되고 두번째 SPD 가 주 배전반에 위치한 SPD 의 후단에 설치된 경 우, 두번째 SPD 의 최대 연속 동작 전압 Uc 는 상전선과 PE 사이에서 최소 440 V 가 되야 하고 상전선들 사이에서는 최소 275 V 가 되야 한다. ¦ 노르웨이에서는 설비가 공공 IT 분배 네트워크에 전기적으로 연결 되고 두번째 SPD 가 주 배전반에 위치한 SPD 의 후단에 설치된 경 우, 두번째 SPD 의 최대 연속 동작 전압 Uc 는 상전선과 PE 사이에서 최소 440 V 가 되야 하고 상전선들 사이에서는 최소 275 V 가 되야 한다. ¦ ¦ AT ¦ 534.4.6 ¦ 오스트리아에서는 공급점 혹은 그 근처의 SPD 조립이 아무 RCD 의 후단에 설치되지 않아도 된다. ¦ 오스트리아에서는 공급점 혹은 그 근처의 SPD 조립이 아무 RCD 의 후단에 설치되지 않아도 된다. ¦ 오스트리아에서는 공급점 혹은 그 근처의 SPD 조립이 아무 RCD 의 후단에 설치되지 않아도 된다. ¦ 오스트리아에서는 공급점 혹은 그 근처의 SPD 조립이 아무 RCD 의 후단에 설치되지 않아도 된다. ¦ 오스트리아에서는 공급점 혹은 그 근처의 SPD 조립이 아무 RCD 의 후단에 설치되지 않아도 된다. ¦ 오스트리아에서는 공급점 혹은 그 근처의 SPD 조립이 아무 RCD 의 후단에 설치되지 않아도 된다. ¦ ¦ DE ¦ 534.4.6 ¦ RCD 접점에서 잘못된 트립 또는 용접이 방지되기 위해서는 높은 임펄스 전류 혹은 부분 낙뢰 전류가 흐르지 않도록 해야 한다. 따라 서 I 등급 시험 혹은 II 등급 시험된 SPD 가 RCD 의 라인 측에 설치 되어야 한다. 서지의 발생이 예를 들어 LPS 에 의해 보호되지 않는 외부 장착 기기로 인해 부하 측에서 예상될 경우, I 등급 시험 혹은 II 등급 시험된 SPD 가 RCD 의 라우드(loud) 측에 설치해야 한다. ¦ RCD 접점에서 잘못된 트립 또는 용접이 방지되기 위해서는 높은 임펄스 전류 혹은 부분 낙뢰 전류가 흐르지 않도록 해야 한다. 따라 서 I 등급 시험 혹은 II 등급 시험된 SPD 가 RCD 의 라인 측에 설치 되어야 한다. 서지의 발생이 예를 들어 LPS 에 의해 보호되지 않는 외부 장착 기기로 인해 부하 측에서 예상될 경우, I 등급 시험 혹은 II 등급 시험된 SPD 가 RCD 의 라우드(loud) 측에 설치해야 한다. ¦ RCD 접점에서 잘못된 트립 또는 용접이 방지되기 위해서는 높은 임펄스 전류 혹은 부분 낙뢰 전류가 흐르지 않도록 해야 한다. 따라 서 I 등급 시험 혹은 II 등급 시험된 SPD 가 RCD 의 라인 측에 설치 되어야 한다. 서지의 발생이 예를 들어 LPS 에 의해 보호되지 않는 외부 장착 기기로 인해 부하 측에서 예상될 경우, I 등급 시험 혹은 II 등급 시험된 SPD 가 RCD 의 라우드(loud) 측에 설치해야 한다. ¦ RCD 접점에서 잘못된 트립 또는 용접이 방지되기 위해서는 높은 임펄스 전류 혹은 부분 낙뢰 전류가 흐르지 않도록 해야 한다. 따라 서 I 등급 시험 혹은 II 등급 시험된 SPD 가 RCD 의 라인 측에 설치 되어야 한다. 서지의 발생이 예를 들어 LPS 에 의해 보호되지 않는 외부 장착 기기로 인해 부하 측에서 예상될 경우, I 등급 시험 혹은 II 등급 시험된 SPD 가 RCD 의 라우드(loud) 측에 설치해야 한다. ¦ RCD 접점에서 잘못된 트립 또는 용접이 방지되기 위해서는 높은 임펄스 전류 혹은 부분 낙뢰 전류가 흐르지 않도록 해야 한다. 따라 서 I 등급 시험 혹은 II 등급 시험된 SPD 가 RCD 의 라인 측에 설치 되어야 한다. 서지의 발생이 예를 들어 LPS 에 의해 보호되지 않는 외부 장착 기기로 인해 부하 측에서 예상될 경우, I 등급 시험 혹은 II 등급 시험된 SPD 가 RCD 의 라우드(loud) 측에 설치해야 한다. ¦ RCD 접점에서 잘못된 트립 또는 용접이 방지되기 위해서는 높은 임펄스 전류 혹은 부분 낙뢰 전류가 흐르지 않도록 해야 한다. 따라 서 I 등급 시험 혹은 II 등급 시험된 SPD 가 RCD 의 라인 측에 설치 되어야 한다. 서지의 발생이 예를 들어 LPS 에 의해 보호되지 않는 외부 장착 기기로 인해 부하 측에서 예상될 경우, I 등급 시험 혹은 II 등급 시험된 SPD 가 RCD 의 라우드(loud) 측에 설치해야 한다. ¦ ¦ NO ¦ 534.4.6 ¦ 노르웨이에서는 설비가 공공 IT 또는 TT 분배 네트워크에 분배된 PE 선의 제공 없이 전기적으로 연결되면(예를 들어 오버헤드 라인에 의해 공급받는 설비) 주 배전반에 위치한 SPD 의 고장으로 인한 화 재에 대한 보호는 다음과 같이 보장된다: SPD 를 별도의 비가연성 외함에 위치한다 또는, 정격 잔류 전류가 300 mA 를 초과 하지 않는 시간 지연 RCD(S-타입 혹은 비슷한)로 SPD 를 보호한다 또는, 고 전압 분배 네트워크에서 접지 실패로 인한 위협 및 화재발 생의 위험성이 최소한이 되도록 만들어진 SPD 의 사용 ¦ 노르웨이에서는 설비가 공공 IT 또는 TT 분배 네트워크에 분배된 PE 선의 제공 없이 전기적으로 연결되면(예를 들어 오버헤드 라인에 의해 공급받는 설비) 주 배전반에 위치한 SPD 의 고장으로 인한 화 재에 대한 보호는 다음과 같이 보장된다: SPD 를 별도의 비가연성 외함에 위치한다 또는, 정격 잔류 전류가 300 mA 를 초과 하지 않는 시간 지연 RCD(S-타입 혹은 비슷한)로 SPD 를 보호한다 또는, 고 전압 분배 네트워크에서 접지 실패로 인한 위협 및 화재발 생의 위험성이 최소한이 되도록 만들어진 SPD 의 사용 ¦ 노르웨이에서는 설비가 공공 IT 또는 TT 분배 네트워크에 분배된 PE 선의 제공 없이 전기적으로 연결되면(예를 들어 오버헤드 라인에 의해 공급받는 설비) 주 배전반에 위치한 SPD 의 고장으로 인한 화 재에 대한 보호는 다음과 같이 보장된다: SPD 를 별도의 비가연성 외함에 위치한다 또는, 정격 잔류 전류가 300 mA 를 초과 하지 않는 시간 지연 RCD(S-타입 혹은 비슷한)로 SPD 를 보호한다 또는, 고 전압 분배 네트워크에서 접지 실패로 인한 위협 및 화재발 생의 위험성이 최소한이 되도록 만들어진 SPD 의 사용 ¦ 노르웨이에서는 설비가 공공 IT 또는 TT 분배 네트워크에 분배된 PE 선의 제공 없이 전기적으로 연결되면(예를 들어 오버헤드 라인에 의해 공급받는 설비) 주 배전반에 위치한 SPD 의 고장으로 인한 화 재에 대한 보호는 다음과 같이 보장된다: SPD 를 별도의 비가연성 외함에 위치한다 또는, 정격 잔류 전류가 300 mA 를 초과 하지 않는 시간 지연 RCD(S-타입 혹은 비슷한)로 SPD 를 보호한다 또는, 고 전압 분배 네트워크에서 접지 실패로 인한 위협 및 화재발 생의 위험성이 최소한이 되도록 만들어진 SPD 의 사용 ¦ 노르웨이에서는 설비가 공공 IT 또는 TT 분배 네트워크에 분배된 PE 선의 제공 없이 전기적으로 연결되면(예를 들어 오버헤드 라인에 의해 공급받는 설비) 주 배전반에 위치한 SPD 의 고장으로 인한 화 재에 대한 보호는 다음과 같이 보장된다: SPD 를 별도의 비가연성 외함에 위치한다 또는, 정격 잔류 전류가 300 mA 를 초과 하지 않는 시간 지연 RCD(S-타입 혹은 비슷한)로 SPD 를 보호한다 또는, 고 전압 분배 네트워크에서 접지 실패로 인한 위협 및 화재발 생의 위험성이 최소한이 되도록 만들어진 SPD 의 사용 ¦ 노르웨이에서는 설비가 공공 IT 또는 TT 분배 네트워크에 분배된 PE 선의 제공 없이 전기적으로 연결되면(예를 들어 오버헤드 라인에 의해 공급받는 설비) 주 배전반에 위치한 SPD 의 고장으로 인한 화 재에 대한 보호는 다음과 같이 보장된다: SPD 를 별도의 비가연성 외함에 위치한다 또는, 정격 잔류 전류가 300 mA 를 초과 하지 않는 시간 지연 RCD(S-타입 혹은 비슷한)로 SPD 를 보호한다 또는, 고 전압 분배 네트워크에서 접지 실패로 인한 위협 및 화재발 생의 위험성이 최소한이 되도록 만들어진 SPD 의 사용 ¦ ¦ DE ¦ 534.4.7 ¦ 낙뢰 전류 혹은 높은 임펄스 전류가 RCD 로 흐르지 않는 것이 보장 되어야 한다. 따라서 후단에 시험 등급 I SPD 의 설치는 허용되지 ¦ 낙뢰 전류 혹은 높은 임펄스 전류가 RCD 로 흐르지 않는 것이 보장 되어야 한다. 따라서 후단에 시험 등급 I SPD 의 설치는 허용되지 ¦ 낙뢰 전류 혹은 높은 임펄스 전류가 RCD 로 흐르지 않는 것이 보장 되어야 한다. 따라서 후단에 시험 등급 I SPD 의 설치는 허용되지 ¦ 낙뢰 전류 혹은 높은 임펄스 전류가 RCD 로 흐르지 않는 것이 보장 되어야 한다. 따라서 후단에 시험 등급 I SPD 의 설치는 허용되지 ¦ 낙뢰 전류 혹은 높은 임펄스 전류가 RCD 로 흐르지 않는 것이 보장 되어야 한다. 따라서 후단에 시험 등급 I SPD 의 설치는 허용되지 ¦ 낙뢰 전류 혹은 높은 임펄스 전류가 RCD 로 흐르지 않는 것이 보장 되어야 한다. 따라서 후단에 시험 등급 I SPD 의 설치는 허용되지 ¦ 66 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
573ee072-1238-4394-ab4e-0ed5a14c388a | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 ¦ ¦ ¦ 않는다. 다만, RCD 의 부하 측에 부분적인 낙뢰 전류가 예상될 때는 허용된다. SPD 의 후단에 시험 등급 II SPD 의 설치는 II 등급 시험된 SPD 가 RCD 의 전단에 이미 설치 되 있거나 RCD 의 부하 측에 임펄스 전 류가 예상될 때만 허용된다. 서지 전류가 3 kA 8/20 보다 높을 때는 RCD 가 전원 공급을 방해하 며 트립 할 수 있다. ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 국가 ¦ 부속절 ¦ 내용 ¦ ¦ AT ¦ 534.4.7 ¦ 오스트리아에서는 공급점 혹은 그 근처의 SPD 조립이 어느 RCD 의 후단에도 설치되어서는 안 된다. ¦ ¦ DE ¦ 부속서 D ¦ 독일에서는 부속서 D 는 인용적이다 ¦ ¦ FR ¦ 부속서 D ¦ 부속서 D 가 적용되지 않는다. ¦ ¦ GR ¦ 부속서 D ¦ 부속서 D 가 적용되지 않는다. ¦ ¦ HU ¦ 부속서 D ¦ 부속서 D 가 적용되지 않는다. ¦ ¦ DE ¦ 536.2.1.1 ¦ 독일에서는 536.2.1.1 절의 문구가 다음으로 교체된다 각각의 전기 설비는 각각의 전원으로부터 절연될 수 있는 대비가 있어야 한다. 모든 회로는 다음 두 단락에서 묘사되는 상황을 제외하고 모든 충 전선으로부터 절연될 수 있어야 한다. TN-C 계통 및 TN-C-S 계통의 일부인 TN-C 에서 PEN 선이 절연 혹 은 개폐되어서는 안된다. 다음과 같다면 TN-S 계통 에서와, TN-C-S 혹은 TT 계통의 일부인 TN-S 에서 중성선이 절연 혹은 개폐될 필요가 없다 TN 계통에서 411.1 및 542.2 에 따라 보호용 등전위 본딩이 설치됨 TT 계통에서 N 과 PE 사이의 전압이 어떠한 경우에서도 통상적인 접 촉 전압을 초과 하지 않음 TT 계통 안에서 이 요구사항의 부합 여부를 검증은 것은 다음 식을 따른다: 50 V ≤ ILmax·0.5·Zi ILmax = 상전선안의 최대 전류 Zi = 상전선 및 N 의 임피던스와 전원의 임피던스를 포함한 그리 드의 임피던스 서비스 조건이 이같이 허용될 경우 공통적인 방법으로 회로 그룹에 대한 절연이 제공될 수 있다. ¦ ¦ SE ¦ 536.3 ¦ 스웨덴에서는 관련 기계 법률 때문에 536.4.3 절과 그 부속절이 전 기 설비에 적용될 수 없다. ¦ ¦ SE ¦ 536.4.3 ¦ 스웨덴에서는 관련 기계 법률 때문에 536.4.3 절과 그 부속절이 전 기 설비에 적용될 수 없다. ¦ ¦ CH ¦ 536.5.1.2 ¦ 스위스에서는 중성선의 단극 개폐 장치가 허용되지 않는다. ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 67 | {}
2f0233cb-3e9f-45a2-8dc4-630d70a86e4a | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 ¦ 국가 ¦ 부속절 ¦ 내용 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ DE ¦ 536.5.1.2 ¦ 독일에서는 다음이 추가된다: 그림 F.3 에 추가된 예시 L N 1 2 IEC 여기에서 1 조명 회로를 위한 제어 장치의 연결 2 램프의 전원을 공급하는 회로 3 제어 장치 그림 F.3- 중성선에서 개폐기가 있는 램프 제어 회로 ¦ ¦ NL ¦ 536.5.1.2 ¦ 네덜란드에서는 중성선의 단극 개폐장치로 장치를 제어하는 것이 허용되지 않는다. ¦ ¦ NO ¦ 536.5.1.2 ¦ 노르웨이에서는 중성선에 단극 기능 개폐기가 삽입되어서는 안된다. ¦ ¦ AT ¦ 537.1 ¦ 오스트리아에서는 감시 장치가 일반적으로 전기 쇼크에 대비한 보 호가 제공되도록 의도되지 않는다. 비고 이 일반적인 요구사항의 예외는 HD 60364(예를 들어 HD 60364-5-551)의 관련 파트에서 제공될 수 있다. ¦ ¦ GB ¦ 537.3 ¦ 영국에서는 공공 배전 IT 계통이 허용되지 않는다. ¦ 68 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
8364d85d-68f7-4250-8e4f-1a791b974061 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 ¦ 국가 ¦ 부속절 ¦ 내용 ¦ 내용 ¦ 내용 ¦ 내용 ¦ 내용 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ GB ¦ 표 E.1 ¦ 영국에서는 다음이 적용된다: ¦ 영국에서는 다음이 적용된다: ¦ 영국에서는 다음이 적용된다: ¦ 영국에서는 다음이 적용된다: ¦ 영국에서는 다음이 적용된다: ¦ ¦ GB ¦ 표 E.1 ¦ 장치 ¦ 표준 ¦ 절연(4) ¦ 비상 개폐(2) ¦ 기능 개폐(5) ¦ ¦ GB ¦ 표 E.1 ¦ 등기구 지지 커 플러 ¦ BS 6972 ¦ Yes(3) ¦ No ¦ No ¦ ¦ GB ¦ 표 E.1 ¦ 플러그 및 개폐 되지 않은 콘센 트 ¦ BS 1336-1 BS 1336-2 ¦ Yes(3) Yes(3) ¦ No No ¦ Yes Yes ¦ ¦ GB ¦ 표 E.1 ¦ 플러그 및 개폐 된 콘센트 ¦ BS 1336-1 BS 1336-2 ¦ Yes(3) Yes(3) ¦ No No ¦ Yes Yes ¦ ¦ GB ¦ 표 E.1 ¦ 플러그 및 콘센 트 ¦ BS 5733 ¦ Yes(3) ¦ No ¦ Yes ¦ ¦ GB ¦ 표 E.1 ¦ 개폐된 퓨즈 연 결 유닛 ¦ BS 1363-4 ¦ Yes(3) ¦ Yes ¦ Yes ¦ ¦ GB ¦ 표 E.1 ¦ 개폐되지 않은 퓨즈 연결 유닛 ¦ BS 1363-4 ¦ Yes(3) (퓨즈 링크 의 제거) ¦ No ¦ No ¦ ¦ GB ¦ 표 E.1 ¦ 퓨즈 ¦ BS 1362 ¦ Yes(3) ¦ No ¦ No ¦ ¦ GB ¦ 표 E.1 ¦ 쿠커 (coocker) 제어 유닛 ¦ BS 4177 ¦ Yes(3) ¦ Yes ¦ Yes ¦ ¦ GB ¦ 표 E.1 ¦ Yes = 기능이 제공됨 No = 기능이 제공되지 않음 (1) 장치가 절연에 적합하고 기호로 표시돼 있다면(BS EN 60617 Identification number S0028 참조)기능이 제공됨 (2) 규격 참조 BS 7671 (2018)의 537.3.3.6 (3) 부하시 절연에 적합함, 예를 들어 부하 전류를 움직이는 동안의 분리 ¦ Yes = 기능이 제공됨 No = 기능이 제공되지 않음 (1) 장치가 절연에 적합하고 기호로 표시돼 있다면(BS EN 60617 Identification number S0028 참조)기능이 제공됨 (2) 규격 참조 BS 7671 (2018)의 537.3.3.6 (3) 부하시 절연에 적합함, 예를 들어 부하 전류를 움직이는 동안의 분리 ¦ Yes = 기능이 제공됨 No = 기능이 제공되지 않음 (1) 장치가 절연에 적합하고 기호로 표시돼 있다면(BS EN 60617 Identification number S0028 참조)기능이 제공됨 (2) 규격 참조 BS 7671 (2018)의 537.3.3.6 (3) 부하시 절연에 적합함, 예를 들어 부하 전류를 움직이는 동안의 분리 ¦ Yes = 기능이 제공됨 No = 기능이 제공되지 않음 (1) 장치가 절연에 적합하고 기호로 표시돼 있다면(BS EN 60617 Identification number S0028 참조)기능이 제공됨 (2) 규격 참조 BS 7671 (2018)의 537.3.3.6 (3) 부하시 절연에 적합함, 예를 들어 부하 전류를 움직이는 동안의 분리 ¦ Yes = 기능이 제공됨 No = 기능이 제공되지 않음 (1) 장치가 절연에 적합하고 기호로 표시돼 있다면(BS EN 60617 Identification number S0028 참조)기능이 제공됨 (2) 규격 참조 BS 7671 (2018)의 537.3.3.6 (3) 부하시 절연에 적합함, 예를 들어 부하 전류를 움직이는 동안의 분리 ¦ ¦ DE ¦ 표 E.1 ¦ 독일에서는 다음이 적용됨: 행에 "회로 차단기"추가: DIN VDE 0641-21 Yes - Yesd - Yes 행에 "잔류 전류 보호장치(RCD)" 추가 DIN VDE 0664-400 Yes - Yesd - Yes DIN VDE 0664-401 Yes - Yesd - Yes DIN VDE 0664-101 Yes - Yes d Yes - 행에서 교체 "플러그 및 콘센트" DIN VDE 0620 (모든 부)과 IEC 60884 (모든 부) 및 IEC 60906 (모든 부) ¦ 독일에서는 다음이 적용됨: 행에 "회로 차단기"추가: DIN VDE 0641-21 Yes - Yesd - Yes 행에 "잔류 전류 보호장치(RCD)" 추가 DIN VDE 0664-400 Yes - Yesd - Yes DIN VDE 0664-401 Yes - Yesd - Yes DIN VDE 0664-101 Yes - Yes d Yes - 행에서 교체 "플러그 및 콘센트" DIN VDE 0620 (모든 부)과 IEC 60884 (모든 부) 및 IEC 60906 (모든 부) ¦ 독일에서는 다음이 적용됨: 행에 "회로 차단기"추가: DIN VDE 0641-21 Yes - Yesd - Yes 행에 "잔류 전류 보호장치(RCD)" 추가 DIN VDE 0664-400 Yes - Yesd - Yes DIN VDE 0664-401 Yes - Yesd - Yes DIN VDE 0664-101 Yes - Yes d Yes - 행에서 교체 "플러그 및 콘센트" DIN VDE 0620 (모든 부)과 IEC 60884 (모든 부) 및 IEC 60906 (모든 부) ¦ 독일에서는 다음이 적용됨: 행에 "회로 차단기"추가: DIN VDE 0641-21 Yes - Yesd - Yes 행에 "잔류 전류 보호장치(RCD)" 추가 DIN VDE 0664-400 Yes - Yesd - Yes DIN VDE 0664-401 Yes - Yesd - Yes DIN VDE 0664-101 Yes - Yes d Yes - 행에서 교체 "플러그 및 콘센트" DIN VDE 0620 (모든 부)과 IEC 60884 (모든 부) 및 IEC 60906 (모든 부) ¦ 독일에서는 다음이 적용됨: 행에 "회로 차단기"추가: DIN VDE 0641-21 Yes - Yesd - Yes 행에 "잔류 전류 보호장치(RCD)" 추가 DIN VDE 0664-400 Yes - Yesd - Yes DIN VDE 0664-401 Yes - Yesd - Yes DIN VDE 0664-101 Yes - Yes d Yes - 행에서 교체 "플러그 및 콘센트" DIN VDE 0620 (모든 부)과 IEC 60884 (모든 부) 및 IEC 60906 (모든 부) ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. 69 | {}
ee9bb86d-31a7-4043-8055-e335be422844 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 참고문헌 IEC 60050 (모든 부), International Electrotechnical Vocabulary IEC 60364-5-52:2009, Low-voltage electrical installations - Part 5-52: Selection and erection of electrical equipment - Wiring systems IEC 60670 (모든 부), Boxes and enclosures for electrical accessories for household and similar fixed electrical installations IEC 61084 (모든 부), Cable trunking systems and cable ducting systems for electrical installations IEC 61439 (모든 부), Low-voltage switchgear and controlgear assemblies 70 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
2513a7f2-86a5-4609-a4b7-abee494c1917 | KSCIEC60364-5-53_KR | KS C IEC 60364-5-53:2019 KSKSKS KSKSK KSKS KSK KS KSK KSKS KSKSK KSKSKS ¦ Low-voltage electrical installations ¦ ¦ --- ¦ ¦ Part 5-53: Selection and erection ¦ ¦ of electrical equipment-Devices for ¦ ¦ protection for safety, isolation, ¦ ¦ switching, control and monitoring ¦ ¦ ICS 29.130; 91.140.50 ¦ 2025-07-16, 에스케이에코플랜트(주)에 라이센스를 부여하며 불법 복사 및 무단 배포를 금합니다. | {}
0ad2376b-cb9c-40a0-89a4-77ebfc74bce0 | 21036D-IC-M16G00-HV-A00-00160 M16_Ph-2 시방서-도장·방청 및 부식 공사.pdf | SK ecoplant SPECIFICATION FOR HVAC & PLUMBING SYSTEM - 도장·방청 및 부식 공사 - ¦ DOC No. ¦ : 21036D-IC-M16G00-HV-A00-00160 ¦ ¦ --- ¦ --- ¦ ¦ DISCIPLINE ¦ : HVAC ¦ ¦ PROJECT No. ¦ : 21036D ¦ ¦ PROJECT TITLE ¦ : M16 Ph2 Project ¦ ¦ CLIENT ¦ : SK hynix ¦ ¦ LOCATION ¦ : Icheon city, Gyeonggi-do, Korea ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 0 ¦ 2022.01.25 ¦ APPROVED FOR CONSTRUCTION ¦ T.G.YU ¦ J.H. YANG ¦ Y.T.OH ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ REV. ¦ DATE ¦ DESCRIPTION ¦ PRPD ¦ CHKD ¦ APPD ¦ 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. | {}
47ceb7fb-b714-409f-9858-83f0f16bedf4 | 21036D-IC-M16G00-HV-A00-00160 M16_Ph-2 시방서-도장·방청 및 부식 공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00160 Rev. 0 Page 1 of 12 ¦ ¦ --- ¦ --- ¦ --- ¦ 1. 일반사항 1.1 적용범위 1.1.1 요약 (1) 이 절은 기기, 덕트, 배관, 지지철물, 보온용 피복 및 금속제 재료 등의 방청(��), 방식(��) 과 마감 도장에 적용한다. (2) 설계도서, 관계법규 또는 별도로 정한 규정에 의한 것을 제외하고는 모두 본 시방에 준한다. (3) 이 시방서에 기재되지 않은 사항은 국토교통부 제정 "기계설비공사 표준 시방서" 및, '1.3 항 참조표준'을 적용할 수 있다. 단 본 시방서와 상이한 내용은 본 시방서를 우선하여 적용한다. (4) 이 시방서에 특별한 명기가 없는 사항 중 건축, 전기에 관한 사항은 해당 시방서에 따른다. (5) 시방서, 설계도면 및 내역서 중 어느 한 도서에라도 표기되어 있는 사항은 시공하여야 한다. (6) 산업안전보건법에서 규정한 법규에 의해서 시공하여야 한다. 1.1.2 적용 및 우선 (1) 모든 공사는 설계도면 및 시방서에 준하여 시공하며, 설계도면과 시방이 상이한 경우에는 설 계도면을 우선하되 발주 담당자와 협의 하여 정한다. (2) 본 시방서, 설계도면 또는 표준 시방이 정한 공법, 자재 및 제품 등의 내용이 현실적으로 이 행하기 불가능할 경우에는 반드시 발주 담당자에게 서면으로 보고하고 대안에 대한 승인을 득한 후 시공한다. 1.1.3 주요내용 (1) 도장면의 정리작업 (2) 도장의 종별 (3) 방청(防�) 및 방식(防�) (4) 도장시공 1.2 관련 시방 1.2.1 일반공통사항 1.2.2 배관공사(공조, PCW, H-VAC, NG PIPING) 1.2.3 덕트공사(GALV, STS, STS COATING, FRP, FM PVC) 1.2.4 위생공사(급수급탕, 오배수통기, 위생기구) 1.3 참조 표준 1.3.1 한국산업표준 KS D 5101 구리 및 구리합금봉 SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. SK ecoplant | {}
b74b9350-bb17-4994-b763-387c28e47890 | 21036D-IC-M16G00-HV-A00-00160 M16_Ph-2 시방서-도장·방청 및 부식 공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00160 Rev. 0 Page 2 of 12 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ KS D 0201 ¦ 용융 아연 도금 시험방법 ¦ ¦ --- ¦ --- ¦ ¦ KS D 0229 ¦ 용융 알루미늄 도금 시험방법 ¦ ¦ KS D 8302 ¦ 니켈 및 니켈 크로뮴 도금 ¦ ¦ KS D 8304 ¦ 전기 아연 도금 ¦ ¦ KS D 8308 ¦ 용융 아연 도금 ¦ ¦ KS D 8309 ¦ 용융 알루미늄 도금 ¦ ¦ KS M 2611 ¦ 공업용 휘발유 ¦ ¦ KS M 5304 ¦ 염화비닐 수지 바니시 ¦ ¦ KS M 5305 ¦ 염화비닐 수지 에나멜 ¦ ¦ KS M 6010 ¦ 수성도료 ¦ ¦ KS M 6020 ¦ 유성도료 ¦ ¦ KS M 6030 ¦ 방청도료 ¦ ¦ KS M 6040 ¦ 래커도료 ¦ ¦ KS M 6050 ¦ 바니쉬 ¦ ¦ KS M 6060 ¦ 도료용 희석제 ¦ ¦ KS M ISO 150 ¦ 도료와 바니시용 천연 아마인유, 정제 아마인유, 아마 보일유 - 품질표준과 시험방법 ¦ 1.3.2 국토교통부 건축공사 표준시방서 KCS 41 47 00 도장공사 1.4 제출물 1.4.1 자재 공급 전 제출물 시공자는 다음의 사항을 자재공급 전에 발주 담당자에게 제출하여 승인을 받아야 한다. (1) 주요 기자재공급원 승인요청서 ① KS 규격 인증서 또는 ISO 품질인증서 ② 공급자의 사업자 등록증명원 (단, 외산자재인 경우 납품 회사 분) ③ 국세 및 지방세 완납증명서 (유효기관 확인) ④ 납품실적증명서 (유효기관 확인) ⑤ 품질검사 전문기관 및 국·공립검사기관의 시험성과 표 ⑥ 품질보증각서 : KS 비인증제품, 공인기관 시험 불가제품, 해외제품(시험성적서 제출)등 (2) 필요 시 재료에 대한 견본품을 제출하여야 한다. 1.4.2 자재 입고 검사 요청서 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
d01b03a3-07be-4d4e-a2f6-69b324f61608 | 21036D-IC-M16G00-HV-A00-00160 M16_Ph-2 시방서-도장·방청 및 부식 공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00160 Rev. 0 Page 3 of 12 ¦ ¦ --- ¦ --- ¦ --- ¦ 자재 반입 시 자재 입고 검사 요청서를 발주 담당자에게 제출하여 확인을 받는다. 1.4.3 검측 요청서 시공 담당자가 검측 요청서를 작성하여 건설사업관리기술인에게 확인을 받은 후 발주 담당자에게 제출 한다. 1.5 저장 및 취급 1.5.1 모든 재료는 옥내에 보관한다. 1.5.2 가연성 도료는 전용 창고에 보관하는 것을 원칙으로 한다. 반입한 도료 및 사용중인 도료는 현장 내에서 발주 담당자가 승인하는 창고에 보관하고 그 주변에서의 화기 사용을 금한다. 2. 재료 2.1 일반사항 2.1.1 도장은 원칙적으로 조합된 도료를 그대로 사용한다. 단, 바탕면의 상태, 흡수성, 온습도 조건 등에 따라서 도장에 알맞도록 조정할 수 있다. 2.1.2 도장 공정의 방치 시간은 도료의 종류, 기후조건에 따라서 적절하게 정하여 시공한다. 2.1.3 도장 재료는 한국산업표준의 제정이 있는 것에 대하여는 KS 표시품으로서 상표 등의 표시가 있는 것을 공사 현장에 반입한다. 2.1.4 마감의 색 배합은 견본 또는 도장 견본책을 제시하여 발주 담당자의 승인을 받는다. 2.1.5 상수(��)에 접하거나 접촉할 수 있는 기기, 탱크 및 관류 등에 사용하는 방청, 방식 및 도장 용 재료는 수질에 악영향을 미치지 않으며 보건위생상 무해한 것으로 한다. 2.1.6 도장부분은 오염되거나 손상되지 않도록 하고 필요에 따라 적절한 보호조치를 한다. 2.2 도장재료 2.2.1 도장재료는 다음 표에 따른다. ¦ 재료명 ¦ 규 격 ¦ 규 격 ¦ 규 격 ¦ 용 도 ¦ 비 ¦ 고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 재료명 ¦ 번 호 ¦ 명 칭 ¦ 종 별 ¦ 용 도 ¦ 비 ¦ 고 ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
9ebe7ac9-f220-4cdd-ba47-180de6d414ef | 21036D-IC-M16G00-HV-A00-00160 M16_Ph-2 시방서-도장·방청 및 부식 공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00160 Rev. 0 Page 4 of 12 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 방 청 도 료 ¦ KS M 6030 ¦ 방청 도료 ¦ 1 종 2 종 ¦ 철재부 ¦ 옥내·외 철제부의 연(�)계 방청 도료 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 방 청 도 료 ¦ KS M 6040 ¦ 래커 도료 ¦ ¦ 철재부 ¦ 래카 에나멜 도장의 초벌칠용 ¦ ¦ 방 청 도 료 ¦ - ¦ 아스팔트 도료 ¦ ¦ 특수장소 ¦ 방수성, 방식성이 있고, 매설관 등에 사용한다. ¦ ¦ 조 합 도 료 ¦ KS M 6020 ¦ 유성 도료 ¦ 1 급 ¦ 철재부 목재부 ¦ 내부, 옥외의 재벌칠, 정벌칠용 ¦ ¦ 합 성 수 지 에나멜 도 료 ¦ KS M 6010 ¦ 수성 도료 ¦ ¦ 콘크리트, 모르타르, 플라스터 ¦ 광택없는 마감, 초벌칠, 정벌칠용 ¦ ¦ 합 성 수 지 에나멜 도 료 ¦ KS M 6010 ¦ 수성 도료 ¦ ¦ 콘크리트, 모르타르, 플라스터 ¦ 광택있는 마감, 초벌칠, 정벌칠용 ¦ ¦ 래 카 도 료 ¦ KS M 6040 ¦ 래커 도료 ¦ ¦ 철재부 목재부 ¦ 건조성, 정벌칠, 분무, 마감용 ¦ ¦ 래 카 도 료 ¦ KS M 6040 ¦ 래커 도료 ¦ ¦ 철재부 목재부 ¦ 래카 에나멜 도장의 재벌칠용 ¦ ¦ 염화비닐 수지도료 ¦ KS M 5304 ¦ 염화비닐 수지 바니시 ¦ ¦ 철재부, 콘크리트, 모르타르, 플라스터 ¦ 내산, 내알칼리, 내약품 및 내수성이 있고, 투명하게 정벌칠 ¦ ¦ 염화비닐 수지도료 ¦ KS M 5305 ¦ 염화비닐 수지 에나멜 ¦ 1 종 ¦ 옥내철재부, 콘크리트, 모르타르, 플라스터 ¦ 내산, 내알칼리, 내약품 및 내수성이 있고, 재벌칠, 정벌칠 ¦ ¦ 염화비닐 수지도료 ¦ KS M 5305 ¦ 염화비닐 수지 에나멜 ¦ 2 종 ¦ 옥외철재부 ¦ 내산, 내알칼리, 내약품 및 내수성이 있고, 재벌칠, 정벌칠 ¦ ¦ 알루미늄 도 료 ¦ KS M 6020 ¦ 유성 도료 ¦ 3 종 ¦ 철재부 ¦ 옥내, 옥외의 일반도료, 내열성 있음 ¦ ¦ 금속 전처리 ¦ KS M 6030 ¦ 방청 도료 ¦ 1 총 ¦ 금속면 화학처리 ¦ 도장전의 전처리 도료 ¦ ¦ 수용성 도 료 ¦ - ¦ 아크릴 수지 ¦ - ¦ 철재부 ¦ 용제의 함유율은 10%이하로 한다. ¦ ¦ 수용성 도 료 ¦ - ¦ 메라민 수지 ¦ - ¦ 철재부 ¦ 용제의 함유율은 10%이하로 한다. ¦ ¦ 수용성 도 료 ¦ - ¦ 에폭시, 메라민 ¦ - ¦ 철재부 ¦ 용제의 함유율은 10%이하로 한다. ¦ ¦ 수용성 도 료 ¦ - ¦ 알키드 수지 ¦ - ¦ 철재부 ¦ 용제의 함유율은 10%이하로 한다. ¦ ¦ 분 체 도 료 ¦ - ¦ ¦ - ¦ 철재부 ¦ 일반용 ¦ ¦ 분 체 도 료 ¦ - ¦ ¦ - ¦ 철재부 ¦ 일반용 ¦ ¦ 분 체 도 료 ¦ - ¦ ¦ - ¦ 철재부 ¦ 일반용 ¦ SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
e697ad49-d9b7-4fb5-a92e-ff93b89c90af | 21036D-IC-M16G00-HV-A00-00160 M16_Ph-2 시방서-도장·방청 및 부식 공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00160 Rev. 0 Page 5 of 12 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 보일유 ¦ KS M ISO 150 ¦ 도료와 바니시용 천연 아마인유,정제아마인유, 아마보일유 품질규격과 시험방법 ¦ 도료와 바니시용 천연 아마인유,정제아마인유, 아마보일유 품질규격과 시험방법 ¦ 일반 페인트 엷게 하는 용도 ¦ 외부 엷게 하는 액 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 오일퍼티 ¦ - ¦ 오일 퍼티 ¦ ¦ ¦ 철재부의 구멍 메꿈 ¦ ¦ 합성수지 에멜션 퍼티 ¦ KS M 6010 ¦ 수성도료 ¦ 내수성 ¦ 콘크리트, 모르타르, 플라스터 ¦ 구멍 메꿈용으로 옥내에서 사용 ¦ * KS A 5101-1 시험용체-제 1 부 : 금속망체 * KS A 5101-2 시험용체-제 2 부 : 금속판체 * KS A 5101-3 시험용체-제 3 부 : 전기도금체 ¦ 재료명 ¦ 규 격 ¦ 규 격 ¦ 규 격 ¦ 용 도 ¦ 비 고 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 재료명 ¦ 번 호 ¦ 명 칭 ¦ 종 별 ¦ 용 도 ¦ 비 고 ¦ ¦ 미네랄 스프리트 ¦ KS M 2611 ¦ 공업용 휘발유 ¦ ¦ 일반도료를 엷게 하는 액 ¦ 유성 도료용을 조정 시키는 것 ¦ ¦ 내열도료 ¦ 상온 건조에 의한 300°C 온도에서 변질, 변색하지 않는 도료 ¦ 상온 건조에 의한 300°C 온도에서 변질, 변색하지 않는 도료 ¦ ¦ 특수장소, 내열성을 필요로하는 금속부 ¦ ¦ ¦ 규소수지 알루미늄 가루봉공제 ¦ - ¦ - ¦ ¦ 철재부 ¦ 알루미늄 용사를 바탕으로 하는 경우의 보호 피복용 ¦ 2.2.2 배관공사 및 SUPPORT 철골 도장 재료 규격 (1) 재료 규격 페인트는 다음 규정에 각각 합격한 것으로 한다. 조합 페인트 (강재용) -. 광 명 단 : KS M 6030 2 종 -. 페 인 트 : KS M 6030 1 급 -. 희 석 제 : KS M 6060 2 급 바니쉬 -. 바 니 쉬 : MS M 6050 -. 희 석 제 : KS M 6060 투명 락카 - 락 카 : MS M 6040 hynix SK SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
b3055f15-c378-4cf3-b723-70c81800058e | 21036D-IC-M16G00-HV-A00-00160 M16_Ph-2 시방서-도장·방청 및 부식 공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00160 Rev. 0 Page 6 of 12 ¦ ¦ --- ¦ --- ¦ --- ¦ -. 희 석 제 : KS M 6060 에폭시 페인트 에폭시 수지와 폴리 아마이드 수지 및 안료를 배합한 2 액형 자연 건조형 도료로서 완전 건 조 시 까지 출입을 제한하여야 한다. ⑤ 아크릴 우레탄 아크릴 수지와 아소시아네아트를 주성분으로 난황변형 2 액형 우레탄 수지계 도료로서 완전 건조 시 까지 출입을 제한하여야 한다. ⑥ 기타 재료 본 시방에 기술되지 않더라도 공사 수행에 필요한 모든 기타 재료는 미리 발주 담당자와 협의 하여 승인을 받아야 한다. 3. 시공 3.1 도장면 정리작업 3.1.1 철재면 (1) 철재면의 바탕준비는 다음 표에 따른다. ¦ 공 정 ¦ 종 별 ¦ 종 별 ¦ 종 별 ¦ 방 치 시 간 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 공 정 ¦ 1 종 A* (화학피막처리) ¦ 1 종 B* (블라스트) ¦ 2 종** (동력, 수작업) ¦ 방 치 시 간 ¦ ¦ 오염, 부착물제거 ¦ 오염, 부착물을 스크레이퍼, 와이어브러시 등으로 제거 ¦ 오염, 부착물을 스크레이퍼, 와이어브러시 등으로 제거 ¦ 오염, 부착물을 스크레이퍼, 와이어브러시 등으로 제거 ¦ ¦ ¦ 기름(�)제거 ¦ 녹제거가 블라스트의 경우에는 용제 분무, 녹제거가 산 세척의 경우에는 약알칼리성액가열 후 뜨거운물 또는 트리클로로에틸렌으로 세척 ¦ 녹제거가 블라스트의 경우에는 용제 분무, 녹제거가 산 세척의 경우에는 약알칼리성액가열 후 뜨거운물 또는 트리클로로에틸렌으로 세척 ¦ 용제분무 ¦ ¦ ¦ 녹 떨어내기 ¦ 산세척에 의해 검은 산성피막, 녹을 제거 ¦ 블라스트에 의해 검은산성 피막, 녹을 제거 ¦ 디스크샌더, 와이어호일 등의 동력공구를 사용하여 스크레이퍼, 와이어브러시 및 연마지 등의 수공구를 병행하여 녹을 제거. ¦ 즉시 다음 공정을 시작한다. ¦ ¦ 화학피막처리 ¦ 인산염화학 피막처리 후, 물세척한 다음 건조 ¦ - ¦ - ¦ 즉시 다음 공정을 시작한다. ¦ * 1 종 A*, 1 종 B* : 각종 반(�)류, 보일러 및 온풍난방기(외장강판), 냉동기(외장강판), 공기조화기, 송출구, 흡입구 및 팬튜브(Fan Tube) 방열기, 기타 이와 유사한 것 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
46c85866-7828-4d3f-ab1f-da3816b20cf8 | 21036D-IC-M16G00-HV-A00-00160 M16_Ph-2 시방서-도장·방청 및 부식 공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00160 Rev. 0 Page 7 of 12 ¦ ¦ --- ¦ --- ¦ --- ¦ * 2 종 ** 상기 이외의 것 : 3.1.2 비철 금속면 (1) 아연 도금면, 동 합금면, 및 경 금속면의 바탕준비는 다음 표에 따른다. ¦ 공 정 ¦ 종 별 ¦ 종 별 ¦ 종 별 ¦ 방 치 시 간 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 공 정 ¦ 1 종 A* (화학피막처리) ¦ 1 종 B* (에칭프라 ¦ 2 종** (탈지( ¦ 방 치 시 간 ¦ ¦ 오염, 부착물 제거 ¦ 오염, 부착물을 스크레이퍼, 와이어브러시 등으로 제거, 청소를 한다 ¦ 오염, 부착물을 스크레이퍼, 와이어브러시 등으로 제거, 청소를 한다 ¦ 오염, 부착물을 스크레이퍼, 와이어브러시 등으로 제거, 청소를 한다 ¦ ¦ ¦ 유지(��)제거 ¦ 약알칼리성액가열 후 더운 물세척 또는 트리클로로 에틸렌으로 세척 ¦ 용제분무 ¦ 용제분무 ¦ ¦ ¦ 화학피막처리 ¦ 인산염화학 피막처리 후, 물세척한 다음 건조 ¦ ¦ ¦ 즉시 다음 공정을 시작한다. ¦ * 표면처리 아연강판의 경우는 화학피막처리를 생략할 수 있다. 3.1.3 비철 금속면 (1) 플라스터면의 바탕준비는 다음 표에 따른다. ¦ 공 정 ¦ 재 료, 기 타 ¦ 처 리 내 용 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 건 조 ¦ - ¦ 바탕을 충분히 건조시킨다. ¦ ¦ 오염 및 부착물 제거 ¦ - ¦ 바탕이 상하지 않도록 제거 ¦ ¦ 요철부 메우기 ¦ 시멘트계 바탕조정도료 · 합성수지 에멀션퍼티 ¦ 균열부, 요철부를 메운다. ¦ ¦ 연 마 지 ¦ 연마지 #100 ~ 180 ¦ 요철부를 메운 자리 등이 건조된 후 표면을 매끈하게 연마한다. ¦ * 합성수지 에멀션퍼티는 외부 및 물기 있는 부분 등에 사용하여서는 안된다. 3.1.4 유리직물 및 면포면(보온표면) 바탕을 충분히 건조시키고 오물 및 부착물 등을 솔 및 걸레 등으로 제거한다. 3.1.5 재질별 도장 기준 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
a47144dd-a832-42fe-9aca-8db5e8fd88da | 21036D-IC-M16G00-HV-A00-00160 M16_Ph-2 시방서-도장·방청 및 부식 공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00160 Rev. 0 Page 8 of 12 ¦ ¦ --- ¦ --- ¦ --- ¦ (1) 재질에 따른 도장은 다음 표에 따른다. ¦ 재 질 ¦ AREA ¦ 도 장 ¦ 이 미 지 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 백강관 (SPP, KS D 3507, GALV.) ¦ 옥내 ¦ 광명단 도색 * FAB 내부 용접부 : 은색아연도금 보습제 ¦ ¦ ¦ 백강관 (SPP, KS D 3507, GALV.) ¦ 옥외 ¦ 1 차 : Wash Primer 2 차 : Enamel Paint ¦ ¦ ¦ 흑강관 (SPP, KS D 3507) ¦ 옥내 / 옥외 ¦ 광명단 도색 * FAB 내부 용접부 : 광명단 도색 ¦ ¦ ¦ STS304 (KS D 3576) ¦ 옥내 / 옥외 ¦ SUS COAT ¦ ¦ ¦ PIPE RACK ¦ 옥내(C/R 포함) ¦ 1 차 : Short Blast 2 차 : 상도 3 차 : 소부건조 ¦ ¦ hynix SK SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
b45f00e8-3c77-4391-b2fe-7de476f5f8d4 | 21036D-IC-M16G00-HV-A00-00160 M16_Ph-2 시방서-도장·방청 및 부식 공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00160 Rev. 0 Page 9 of 12 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ PIPE RACK ¦ 옥외 ¦ 1 차 : Short Blast 2 차 : 하도 3 차 : 자연건조 4 차 : 상도 ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ * 조합페인트의 색상은 발주 담당자와 협의 하여 정한다. (2) 건조막 두께는 다음 기준에 따른다 도막 두께는 건축 시방 "12_A14010 도장공사" 3.6 페인트 계획서 기준에 따른다. 단, 기타 장비 및 배관의 도막 두께는 Vendor Standard 기준 또는 발주처와 협의 하여 적용 할 수 있다. 3.2 방청(��) 및 방식(��) 3.2.1 전처리 방청 및 방식처리를 시행하는 금속표면은 산세척(���), 쇼트 블라스트 등에 의한 전처리를 한다. 전처리 후 즉시 다음 공정을 이행한다. 3.2.2 도금 (1) 용융아연도금 ① KS D 8308 에 따르며, 품질은 2 종 35 이상으로 한다. 시험 및 검사는 KS D 0201 에 따라 행한다. 3.2.3 라이닝 (1) 에폭시수지라이닝 시공은 바탕을 깨끗이 한 후 라이닝재를 도포하고 가열하여 완전히 경화시킨다. 가열이 어 려운 모양 및 크기의 것은 상온에서 경화한다. 시험 및 검사는 내열시험, 두께시험 및 핀홀검사 등으로 한다. 3.2.4 분체도장에 의한 방청 및 방식 (1) 방청 및 방식을 목적으로 특히 두꺼운 도막을 입혀야 하는 분체도장은 나일론 수지 염화비닐 수지 및 본절 '도장재료의 분체도료'에 의하며, 그 도장 방법 및 시험방법 등은 전문업자의 표 준에 의하여 행한다. 단, 화학처리는 탈산 후 적어도 인산철 또는 인산아연 처리로 한다. (2) 분체 도료는 인체에 유해한 성분이 섞여 있지 않아야 한다. SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
b3e94a6d-ad95-43ae-b263-823a89a16cf8 | 21036D-IC-M16G00-HV-A00-00160 M16_Ph-2 시방서-도장·방청 및 부식 공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00160 Rev. 0 Page 10 of 12 ¦ ¦ --- ¦ --- ¦ --- ¦ 3.3 도장 시공 3.3.1 도장 범위 각종 기기부재 중에서 다음 부분을 제외하고 전체 도장을 한다. (1) 매설되는 것(방식도장은 제외) (2) 아연도금 이외의 도장 마감면 (3) 아연도금 및 수지 코팅한 것으로서 은폐되는 부분 3.3.2 도장 방법 (1) 솔 도장은 도장에 적합한 솔을 사용하고, 솔의 방향은 올바르게 한쪽방향으로 칠한다. (2) 분무도장은 도장용 스프레이 건을 사용하고 캔의 종류, 구경 및 공기압은 사용한 도료의 성질 에 따라 적절한 것을 선택하고 얼룩이 없도록 정확한 방법으로 칠한다. (3) 롤러브러시 도장은 롤러브러시를 사용하고 모퉁이 및 구석 등은 솔 또는 전용롤러를 사용하 여 면이 균일하게 되도록 칠한다. 연마지는 면의 상태에 의해 생략할 수 있다. (4) 에어레스 분무도장은 압축기로부터 도료에 압력을 넣어 분무한다. (5) 열처리도장은 열처리 건조로, 분무용 압축기 및 분무용 부스 등의 설비가 갖춰진 공장에서 도 장하고 열처리한다. (6) 분체도장은 열처리로, 분체도장부스 및 정전도장기 회수장치 등의 설비가 갖춰진 분체도장 공 장에서 도장하고 열처리한다. (7) 옥외배관용 흑관(SPP. KS D 3507)은 반입 즉시(부식발생 전) 방청도장을 실시(초벌칠)하여야 하 며, 배관완료 후 용접부위 등 도장이 손상된 부분은 방청도장(정벌칠)을 실시하여야 한다. (8) 바닥 PLATE, SUPPORT 고정용 볼트는 부식방지를 위해 에폭시 방청도장 후 아크릴우레탄 도 장으로 마감한다. 도장색은 마감색과 동일한 색상으로 한다. (9) 볼트 절단면은 날카로운 부분을 정리한 후 징크프라이머 도장을 한다. (10) 공사현장 용접부의 도장 ① 공사현장 용접을 시행하는 부분 양측 약 100mm~200mm 범위는 수압시험이 완료될 때 까지는 도장을 해서는 안된다. 단, 용접 후 수압시험 시기까지 장시간이 소요되어 녹발생이 예상 되는 부위에 대해서는 발주자와 협의 후 즉시 방청 도장을 진행 한다. 수압시험을 진행하지 않는 용접 부위는 용접 후 즉시 방청 도장을 진행 한다. 배관 용접부위 도장 : 150A 이하 100mm, 200mm 이상 200mm 용접부 도장 진행 순서 : -. 용접부 브러싱 및 이물질 제거 → 좌,우측 테이핑 후 도장 진행 → 도장 완료 후 테이프 제거 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
7f8f1c2d-5beb-491e-bae8-ef5e06ea844b | 21036D-IC-M16G00-HV-A00-00160 M16_Ph-2 시방서-도장·방청 및 부식 공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00160 Rev. 0 Page 11 of 12 ¦ ¦ --- ¦ --- ¦ --- ¦ ![image](/image/placeholder) ![image](/image/placeholder) → → ② 공사현장 용접을 시행하는 부분에서 심한 녹이 발생할 우려가 있는 부분은 적절한 방청처리 를 한다. ③ 옥외배관(옥상 등)은 에폭시+아크릴우레탄으로 도장한다. (11)보온 등으로 가려져 있는 배관재, 구조물, 장비, 탱크 등의 볼트·너트는 부식방지를 위해 에폭 시 방청 페인팅을 한다. (12)부식발생 위험지역 및 기타지역을 점검하여 부식이 발생하는 모든 자재, 장비, 구조물에는 페 인팅 등 부식방지 조치를 취해야 한다. (13)가스폭발위험장소 또는 분진폭발위험장소에 자동소화설비가 없거나 장애물로 인해 소화가 곤란한 구역의 지지대(위험물 저장·취급용기의 지지대(30cm 이하 제외)는 지상으로부터 끝까 지, 배관·전선관 등의 지지대는 지상으로부터 1 단(1 단의 높이가 6m 를 초과 하는 경우 6m)까지 1 시간 이상 내화페인트로 마감하여야 한다. 3.3.3 도장 보수 (1) 도장 보수는 다음과 같은 경우에 시행한다. ① 도장막이 건조하기 전에 천우의 급변 등 기타에 의하여 도장면이 고르지 못하고 뜬 것. ② 심한 오물이 부착되었다고 인정될 때. ③ 도장 후 2~3 일 내에 도장막이 변색, 금간 것, 떨어진 것, 수축, 부풀음 등이 도장막에 이 상이 발생하였을 때. 3.3.4 도장 시공의 유의 사항 (1) 색의 얼룩, 칠의 떨어 짐, 몰림, 검품 및 솔자국 등의 결점이 없도록 전체 면을 균일하게 칠한 다. (2) 도장부분의 주변을 오염 및 손상되지 않도록 주의 하고 필요에 따라 적절한 보호조치를 한다. (3) 도장장소의 온습도 및 환기 등 도장의 건조조건에 주의 하고 도료의 종류와 건조조건에 따라 적합하게 정한다. (4) 도장을 하는 환경은 환기를 잘하여 용제에 의한 중독을 방지한다. (5) 도장 시에는 화기 및 전기스파크에 인한 인화에 주의 하고 화재 및 폭발 등의 발생을 방지 한 다. (6) 도장장소의 기온이 5°C 이하, 습도가 85% 이상 또는 환기가 충분하지 않고 결로가 있는 등 도료의 건조에 적당치 못한 장소에서는 원칙적으로 칠을 하지않아야 한다. 부득이 칠을 할 경 우는 가온(加温) 및 환기 등의 보양을 행한다. SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. SK ecoplant | {}
6de99164-f644-442c-91be-85f8a68edf8f | 21036D-IC-M16G00-HV-A00-00160 M16_Ph-2 시방서-도장·방청 및 부식 공사.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00160 Rev. 0 Page 12 of 12 ¦ ¦ --- ¦ --- ¦ --- ¦ (7) 외부 도장은 강우의 우려가 있는 장소 및 강풍 시에는 원칙적으로 작업을 하지 않아야 한다. 3.4 검사 3.4.1 검사 각 공종별 도장면의 상태, 도장재료 및 도장방법 등에 대한 검사를 실시한다. - End of Document - SK hynix SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
aa97f4d7-0dbb-4831-aaf9-71461bf15514 | 21036D-IC-M16G00-HV-A00-00100 M16_Ph-2_시방서-일반공통사항.pdf | SK ecoplant SPECIFICATION FOR HVAC & PLUMBING SYSTEM 일반공통사항 - ¦ DOC No. ¦ : 21036D-IC-M16G00-HV-A00-00100 ¦ ¦ --- ¦ --- ¦ ¦ DISCIPLINE ¦ : HVAC ¦ ¦ PROJECT No. ¦ : 21036D ¦ ¦ PROJECT TITLE ¦ : M16 Ph2 Project ¦ ¦ CLIENT ¦ : SK hynix ¦ ¦ LOCATION ¦ : Icheon city, Gyeonggi-do, Korea ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 0 ¦ 2022.01.25 ¦ APPROVED FOR CONSTRUCTION ¦ T.G.YU ¦ J.H. YANG ¦ Y.T.OH ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ REV. ¦ DATE ¦ DESCRIPTION ¦ PRPD ¦ CHKD ¦ APPD ¦ 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. | {}
0b55fb0c-51ea-44ab-b1db-cd966b83e4b0 | 21036D-IC-M16G00-HV-A00-00100 M16_Ph-2_시방서-일반공통사항.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00100 Rev. 0 Page 1 of 14 ¦ ¦ --- ¦ --- ¦ --- ¦ 1. 일반공통사항 1.1 적용범위 (1) 이 시방서는 급배수, 공기조화, 가스설비 및 기타 기계설비공사에 관한 표준을 규정하는 시방 서이다. (2) 이 시방서에 기재되지 않은 사항은 국토교통부 제정 "설비공사 표준 시방서(기계부문)"에 따른 다. (3) 이 시방에 기재된 이외의 건축 및 전기에 관한 사항은 국토교통부 제정 "건축공사 표준 시방서"와 "건축전기설비 표준 시방서"에 따른다. (4) 모든 시설물의 안전, 보건 및 환경관리관련 시설물의 기준은 산업안전보건법 및 안전보건기술 지침(KOSHA GUIDE)의 기준에 따른다. (5) 이 시방서의 내용 중 선택적 사항으로서 그 지정이 필요한 사항은 공사시방서에서 정하도록 한 다. (6) 시방서, 설계도면 및 내역서 중 어느 도서에서라도 표기되어 있는 사항은 시공하여야 한다. 1.2 용어의 정의 이 시방서에 사용되는 주된 용어는 다음과 같이 정의 한다. (1) 표준시방서 시설물의 안전 및 공사시행의 적정성과 품질확보 등을 위하여 시설별로 정한 표준적인 시공기준 으로서 발주처 또는 설계 등 용역업자가 공사시방서를 작성하는 경우에 활용하기 위한 시공기준 을 말한다. (2) 공사시방서 공사별로 건설공사 수행을 위한 기준으로서 계약문서의 일부가 되며, 설계도면에 표시하기 곤란 하거나 불편한 내용과 당해 공사의 수행을 위한 재료, 공법, 품질시험 및 검사 등 품질관리, 안전관리계획 등에 관한 사항을 기술하고, 당해 공사의 특수성, 지역여건, 공사방법 등을 고려하 여 공사별, 공종별로 정하여 시행하는 시공기준을 말한다. (3) 발주자 발주자라 함은 건설공사를 시공자에게 도급하고, 그 대가 또는 보수를 지불하기로 계약한 자를 말한다. (4) 시공자 시공자라 함은 발주자로부터 발주내용에 대해 모든 책임을 지고 완성시킬 것을 계약하고 그 대가 또는 보수를 받기로 한 자를 말한다. (5) 건설사업관리기술인 건설사업관리기술인이라 함은 건축법 및 건설기술진흥법, 주택법에서 정한 바에 따라 설계도서 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
df9b2849-89e5-46b2-89c6-247820307ea6 | 21036D-IC-M16G00-HV-A00-00100 M16_Ph-2_시방서-일반공통사항.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00100 Rev. 0 Page 2 of 14 ¦ ¦ --- ¦ --- ¦ --- ¦ 대로 시공되는 지의 여부를 확인하고 소관업무 등에 대한 기술지도를 하는 자를 말한다. (6) 발주 담당자 발주 담당자라 함은 도급공사 또는 직영공사에 있어서 건축주가 지정한 감독책임 기술자로서 현장감독(공사관리, 기술관리 등)을 하는 자를 말한다. (7) 현장대리인 현장대리인(현장기술관리인)이라 함은 공사계약 일반조건 및 건설기술관리법에 의거하여 시공자 가 지정하는 책임시공 기술자로서 그 현장의 공사관리 및 기술관리 기타 공사업무를 시행하는 현장책임자를 말한다. (8) 시공 담당자 시공 담당자라 함은 현장대리인 또는 그가 고용하는 현장시공을 담당하는 자를 말한다. 시공자, 현장대리인 또는 시공 담당자는 공사계약서 및 설계도서 등에 의거하여 공사시공을 충실히 수행하되 감리자의 검사 승인을 받고 그 지시에 따라 시행한다. (9) 설계도서 설계도서라 함은 표준시방서, 공사시방서, 설계도면, 설계계산서 및 현장설명서 등을 말한다. (10) 경미한 변경 현장에서의 마감상태, 작업상태 등으로 인하여 기기 및 재료의 설치위치 또는 공법을 다소 변경 하는 등을 말한다. (11)특기 특기라 함은 설계도면 또는 공사시방서에 기재된 사항을 말한다. (12)관계법령 관계법령이라 함은 법 · 시행령 · 시행규칙 · 고시 · 조례 · 세칙 · 유권해석 등을 말한다. 1.3 적용순서 (1) 설계도서 간에 상호 모순이 있을 경우 아래 순서에 따라 적용한다. 1) 설계도면 2) 공사시방서 3) 표준시방서 4) 공종별 물량내역서 5) 승인된 시공도면 6) 관계법령의 유권해석 (2) 표준시방서의 총칙과 총칙 이외의 시방 내용간에 상호 모순이 있을 경우에는 총칙 이외의 시방 에 명시된 내용을 우선 적용한다. (3) 본 시방과 특기시방서 사이에 내용이 서로 상이 할 때는 특기시방이 우선한다. (4) 본 시방서, 도면 또는 표준시방서가 정한 공법, 자재 및 제품 등의 내용이 현실적으로 이행하기 불가능할 경우(계약자가 도면 및 시방서상의 내용과 다르게 시공을 필요로 하는 경우 포함)에는 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
733f6ce2-2ddb-41b2-aea7-95a4872c92e7 | 21036D-IC-M16G00-HV-A00-00100 M16_Ph-2_시방서-일반공통사항.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00100 Rev. 0 Page 3 of 14 ¦ ¦ --- ¦ --- ¦ --- ¦ 반드시 발주 담당자에게 서면으로 보고하고 대안에 대한 승인을 얻은 뒤에 시공한다. (5) 참조 규격 1) 모든 공사는 관련 법규 및 조례, 관련 표준 등을 준수하여 시공한다. 2) 법령 또는 별도로 정한 규정 중 본 공사와 관련되는 법령은 다음과 같다. 관련법규 시행령, -. 건축법 및 동법 시행령, 시행규칙 -. 건축물의 설비비기준 등에 관한 규칙 - 소방기본법, 소방시설공사업법, 소방시설설치유지 및 안전관리에 관한 법, 시행규칙 -. 화재안전기준 - 위험물안전관리법, 시행령, 시행규칙 -. 산업안전보건법 및 동법 시행령, 시행규칙 -, 산업안전보건기준에 관한 규칙 -. 수도법 및 동법 시행령, 시행규칙 -. 오수·분뇨 및 축산폐수의 처리에 관한 법 및 동법 시행령, 시행규칙 -. 환경보전법 및 동법 시행령, 시행규칙 -. 고압가스안전관리법 및 동법 시행령, 시행규칙 -. 도시가스사업법 및 동법 시행령, 시행규칙 -. 열사용기자재 관리규칙 -. 건축물의 에너지 절약 설계기준 -. 에너지이용합리화법 및 동법 시행령, 시행규칙 -. 고효율에너지기자재 보급촉진에 관한 규정 -. 건축물의 에너지 절약 설계 기준 -. 대기환경보전법 -. 폐기물관리법 -. 하수도법 -. 건설산업기본법 -. 장애인, 노인, 임산부 등의 편의 증진보장에 관한 법률, 시행규칙 -. 기타 본 공사와 관련되 관계법규, 령, 규칙, 고시, 예규, 규정, 훈령, 조례 등 관련 표준, 지침, 기준 -. 한국산업표준(KS) -. 한국산업안전보건공단 기술지침(KOSHA GUIDE) -. 한국가스안전공사 업무처리지침(KGS CODE) 1.4 관공서 및 대외 기관과 의 수속 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
03f83283-1366-4bb4-b0bb-fb5271660ec8 | 21036D-IC-M16G00-HV-A00-00100 M16_Ph-2_시방서-일반공통사항.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00100 Rev. 0 Page 4 of 14 ¦ ¦ --- ¦ --- ¦ --- ¦ (1) 시공자는 공사착수 전에 관계법규에 의한 허가 및 신고를 필해야 할 모든 종류의 일정을 그 시기와 함께 작성하여 제출하여야 한다. (2) 시공자는 공사를 위한 허가수속 및 신고사항 일체를 지체없이 행 하여야 하며 그 진행사항을 수시로 발주 담당자에게 보고하여야 한다. (3) 허가수속 완료 후 관공서 및 기타기관에서 발행된 인, 허가서류 일체는 지체 없이 발주 담당자 에게 제출하여야 한다. 단, 허가수속 및 신고에 필요한 일체의 비용은 시공자 부담으로 한다. 1.5 이의(��) 설계도면과 시방서와 의 내용이 서로 다를 때, 설계도서에 명기하지 않은 사항이 있을 때, 관련 공사 와 부합되지 아니할 때 또는 이의 가 생겼을 때에는 감리자와 협의 하여 그 결과 를 발주 담당자에게 통보하여 승인을 받는다. 1.6 협의 설계도서만으로 판정이 곤란하거나 불가능할 경우 발주 담당자 및 감리자와 협의 한다. 1.7 경미한 변경 공사 도중 현장 사정 또는 기타 사유로 인하여 기기 및 재료의 설치위치, 설치공법 등을 변경하고자 할 때에는 그 사유를 발주 담당자에게 제출하고 발주 담당자의 승인을 득한 후 시공하여야 한다. 1.8 설계변경 (1) 설계변경은 원칙적으로 계약조건에 준하며, 반드시 발주 담당자의 승인을 받아 실시한다. (2) 시공자는 설계변경 시 발주 담당자가 요구하는 구비서류를 제출하여야 한다. 1.9 협의 결과 의 처리 발주 담당자의 협의 결과 에 따라 경미한 변경 외에는 설계변경을 한다. 2. 공사 현장관리 2.1 관계법규의 준수 모든 공사는 관련법규(근로기준법, 건설기술관리법, 산업안전보건법 등)를 준수하여 시공하고, 시공 에 필요한 관공서, 관계기관 등에 제출하여야 할 서류, 수속 등은 시공자 부담으로 시행하는 것을 원칙으로 하고, 이의 가 있을 경우에는 쌍방 합의 하에 이행한다. 다만, 공과 금은 건축주의 부담으로 한다. 2.2 정리, 정비, 청소 등 시공자는 공사현장에서 현장내의 제반 자재, 기계기구등의 정리정돈, 점검, 정비 및 청소를 하여 현 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
593c3a4b-d77a-4e65-8991-3ce2074ffcf5 | 21036D-IC-M16G00-HV-A00-00100 M16_Ph-2_시방서-일반공통사항.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00100 Rev. 0 Page 5 of 14 ¦ ¦ --- ¦ --- ¦ --- ¦ 장내를 청결하게 유지하여야 한다. 2.3 사고, 재해 및 공해방지 현장대리인은 공사시공에 수반하는 재해 및 공해방지를 위하여 관계법령 등에 따라 다음 사항을 준 수해야 한다. (1) 공사현장 주변의 건축물, 도로, 매설물 및 통행인 등 제 3 자에게 재해가 미치지 않도록 한다. (2) 공사현장 내의 사고, 화재 및 도난의 방지에 노력하고, 특히 위험한 장소의 점검은 주의 깊게 수행한다. (3) 공사 중의 소음, 진동, 먼지, 섬광 및 그 이외에 대해서도 적절한 조치를 하고, 공해가 발생하 지 않도록 한다. 2.4 응급조치 사고, 재해 또는 공해가 발생한 경우 또는 발생의 우려가 있고 긴급을 요하는 경우는 신속하게 조치를 하고 그 경위를 발주 담당자에게 보고한다. 2.5 보양 (1) 시공자는 인접한 건축물 및 공작물에 대해서는 사전에 점검하여 보양을 필요로 할 때는 지체없 이 행한다 (2) 기존부분, 시공완료부분, 미사용 기기 및 재료 등의 오염 또는 손상될 우려가 있는 것은 적절 한 방법으로 보양을 하여야 한다. 2.6 발생재의 처리 (1) 발생재 중 공사시방서에 의해 인도하도록 정해진 것은 지정된 장소에 정돈하고 서류를 첨부하 여 발주 담당자에게 제출한다. 불필요하다고 인정되는 것은 관계법규 등에 따라 적절히 처분한 다. (2) 공사시공상 지장이 되는 장해물의 처리에 대해서는 발주 담당자와 협의 한다. 2.7 뒷정리 공사완료시는 가설물 등을 신속하게 철거하고 청소 및 뒷정리를 원칙으로 하되 필요시 협의 된 가설 물은 존치할 수 있다. 2.8 기술자의 배치 건설기술관리법에 의한 기술자를 건축기계설비공사 현장대리인으로 지정하여 현장에 배치하고 시공 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
e721659f-5106-4db0-be9c-e61ad83a9cb5 | 21036D-IC-M16G00-HV-A00-00100 M16_Ph-2_시방서-일반공통사항.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00100 Rev. 0 Page 6 of 14 ¦ ¦ --- ¦ --- ¦ --- ¦ 의 정확성 및 공정관리를 책임지도록 한다. 3. 자재관리 및 품질관리 3.1 기기 및 자재 (1) 기계설비공사에 사용하는 기기 및 자재는 한국산업표준(KS) 인증제품으로 하되 KS 규격이 없는 경우는 중소기업청 등의 공공기관 제정에 의해 인증된 제품 또는 기능과 성능이 보장될 수 있 는 제품에 한하여 발주 담당자의 승인을 받아 사용할 수 있다. (2) 본 공사에 사용하는 모든 기자재는 시방서, 취급설명서, 견본(필요시 제출), 시험성적서, 카타 로그 등의 기술자료를 구비하여 제출하고 발주 담당자의 승인을 받아 사용한다. (3) 기기 또는 재료에는 제작회사, 제조번호, 제조 년/월/일, 형식 및 성능 등을 명시한 명판을 부 착하되 한국산업표준(KS) 또는 품질경영 및 공산품 품질관리법에 적합하며 발주처에서 요구한 양식에 맞는 것으로 한다. (4) 방폭설비의 안전인증 대상이 되는 모든 자재는 고용노동부 장관이 지정하는 안전인증기관에서 안전인증을 받은 제품을 사용하여야 한다. 다만, 해당 품목에 안전인증제품이 없는 경우에는 시 공전에 발주 담당자의 승인을 득한 후 시공하여야 한다 3.2 기기 및 자재의 관리 (1) 시험 및 검사에 합격한 기기 및 재료는 발주 담당자가 지정한 장소에 정리하여 보관하고, 불합 격품은 지체없이 공사장 밖으로 반출해야하며 그 처리 결과 를 발주 담당자에 보고하여야 한다. (2) 자재관리 시 자재의 특성을 감안하여 변형, 부식, 파손 등 보관에 주의 하여야 하며 인화성자재 는 방화안전대책(소화기설치 등)을 강구한다. (3) 관류 등 자재는 종류별, 규격별로 분리하여 오염, 훼손, 이종금속접촉 등이 되지 않도록 자재받 침 또는 자재관리대 위에 이물질이 들어가지 않도록 캡(마개) 등으로 보양하여 관리하고, 수지 류의 자재는 처짐에 의한 변형이 없도록 1.5m 간격으로 지지 받침을 설치 하도록 하며, 햇볕에 직접 노출 되지 않도록 관리에 유의 하여야 하고, 시공 시 모든 자재의 이상여부를 확인한다. (4) 클린룸과 관련된 기기 및 재료는 반입전 내, 외부를 깨끗이 청소를 하고 보양된 상태에서 반입 을 하고, 오염이 적은 장소에 보관한다. (5) 시공자는 시공도중 또는 공사가 완료된 부분의 각종 기구류 및 공작물의 오손, 파손, 변질, 분 실 등을 방지하기 위하여 철저한 보안대책을 수립하여야 한다. (6) 시공자가 발주 담당자로부터 인수 받은 각종 기자재는 오손, 파손, 변질, 분실 등의 방지를 위 하여 시공자 부담으로 철저히 보전하여야 한다. 3.3 기기 및 자재의 시험, 검사 (1) 시험과 검사방법은 관계법규, 한국산업표준(KS), 단체표준(SPS-KARSE, KRA) 및 기타 준용기준이 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
4eee43e4-e07c-4022-a595-8d68348e1fe6 | 21036D-IC-M16G00-HV-A00-00100 M16_Ph-2_시방서-일반공통사항.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00100 Rev. 0 Page 7 of 14 ¦ ¦ --- ¦ --- ¦ --- ¦ 있을 때에는 그것에 따른다. (2) 공정중 공사시방서에 명시되었거나 필요한 경우에는 반드시 기기, 자재 및 시공에 대한 시험 및 검사를 시행하고 이에 합격하여야 한다. 다만, 한국산업표준(KS), 단체표준(SPS-KARSE, KRA)에 의한 표준품과 제조업체 등의 시험성적서 및 검사증으로 발주 담당자가 인정하는 것이나 발주 담당자가 인정하는 경미한 사항에 대해서는 시험 및 검사를 생략할 수 있다. 시험, 검사를 위한 제반 경비는 시공자가 부담한다. 3.4 지급 자재 (1) 지급자재를 인도 할 때는 발주 담당자의 입회하에 검수하여 공사시공자의 책임하에 보관하고, 도난 및 훼손될 경우에는 시공자가 즉시 변상하여야 한다. (2) 발주 담당자가 지급하는 기자재의 인도 장소는 현장내로 하고 (가공이 필요한 자재에 한하여 한하여 협의 된 외부 지정 장소에서 인도 가능) 하역을 포함한 현장내에서의 운반은 시공자가 부담한다. (3) 시공자는 발주 담당자가 지급한 기자재의 보관 및 변질 등에 대하여 일체의 책임을 진다. (4) 시공자는 발주 담당자가 지급한 기자재의 수급대장을 작성하여 발주 담당자가 요청할때는 언제 든지 즉시 제출할 수 있도록 정리하여 두어야 한다. (5) 발주 담당자가 지급한 기자재의 보관 및 관리의 불찰로 인한 부속품이나 손상품은 시공자 부담 으로 원상 복구되어야 한다. (6) 발주 담당자가 지급한 기자재 중 사용 후의 잔여분은 즉시 반납하여야 한다. (7) 발주 담당자가 지급하는 기자재의 종류 및 공사범위는 별도로 정한 바에 따른다. 4. 시공 4.1 일반사항 (1) 공사는 설계도서에 표시된 제반설비가 그 기능을 충분히 발휘할 수 있도록 설계도서, 공정표, 시공계획서, 제작도 및 시공도 등에 따라서 철저히 시공한다. 다만, 명시되지 않은 사항은 발주 담당자와 협의 한다. (2) 시공자는 공사 투입과 동시에 설계도서의 적정성을 검토 하여 발주 담당자에게 서면으로 보고 토록 하여 완성 후 기능상의 문제가 없도록 하여야 한다. 4.2 공정표 (1) 공사 착공에 앞서 공정표를 작성하고 발주 담당자의 승인을 받는다. (2) 공정표에 변경이 생기는 경우는 변경공정표를 지체없이 작성하고 발주 담당자의 승인을 받는다. (3) 별도 계약공사와 의 협의 가 필요할 때는 발주 담당자의 지시를 받아 조정한다. 4.3 시공 계획서 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
71b3e0db-22b2-4e32-8104-cae85ee2f01f | 21036D-IC-M16G00-HV-A00-00100 M16_Ph-2_시방서-일반공통사항.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00100 Rev. 0 Page 8 of 14 ¦ ¦ --- ¦ --- ¦ --- ¦ (1) 시공자는 착공에 앞서 공사용 가설건물, 임시공급시설(전기, 상하수도, 냉난방, 통신 등), 가설도 로 등 종합가설을 정리한 시공계획서를 작성하고 발주 담당자에게 제출한다. (2) 공정별로 기기, 재료 및 공법 등을 구체적으로 정한 시공계획서를 작성하고 발주 담당자의 승인 을 받는다. (3) 시공자는 전문업체의 특기시방서를 제출토록 하며, 본 공사와 의 적정성 등을 검토 하여 시공계 획서에 적용토록 한다. 4.4 제작도, 시공도 및 견본제출 기기제작 및 시공상 필요한 도면을 작성하고 필요한 경우에는 견본 또는 기기 및 제품 카타로그를 제출하여 발주 담당자의 승인을 받아야 한다. 4.5 공사 보고서 공사에 관한 진척사항, 작업내용, 재료의 반입과 소비 및 기후조건 등 기타 발주 담당자가 필요하다 고 지시한 사항에 대해서는 정해진 기간내에 보고서를 제출한다. 4.6 시공에 대한 시험 및 검사 (1) 시험시공은 공사시방서에 명시되었거나 필요한 단계에서 반드시 행하고, 그 결과 를 발주 담당자 에게 보고한다. (2) 시공검사는 공사시방서에 명시되었거나 필요한 단계 또는 발주 담당자가 지정한 공정에 도달한 경우에는 발주 담당자의 검사를 받는다. (3) 시공 후에 검사가 불가능하거나 곤란한 공사부분은 발주 담당자의 승인 후 시공사 책임하에 입 회하여 시공 한다. 4.7 입회 검사 (1) 수중 또는 지하에 매설, 은폐되는 곳 또는 기능상 특수하게 사용되는 기자재의 조립, 설치, 기타 준공 후 외부로부터 검사 할 수 없는 공작물 등은 발주 담당자의 승인 후에 조립 시공하고 반드시 천연색 기록사진을 촬영하여 파일로 제출 한다. (2) 시공 후에 검사가 불가능하거나 곤란한 공사 또는 여러 개의 기자재를 조립 설치하는 경우에는 반드시 발주 담당자의 승인 후에 시공 한다. (3) 시운전은 발주 담당자의 입회하에 실시한다. 시공검사는 각 공정에 중간검사를 받아야 하며 검 사에 필요한 모든 준비 사항은 발주 담당자와 사전에 협의 하여 시공자 부담으로 행한다. (4) 검사방법과 검사기준은 각 공사의 해당사항에 따른다. 4.8 안전 · 보건 및 환경관리 (1) 모든 공사는 산업안전보건법에 준용하여 산업재해 예방을 위한 기준을 준수하여야 하며, 산업재 해 발생방지에 노력하여야 한다. SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
e374c49d-652c-4b55-8359-a57af361e06e | 21036D-IC-M16G00-HV-A00-00100 M16_Ph-2_시방서-일반공통사항.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00100 Rev. 0 Page 9 of 14 ¦ ¦ --- ¦ --- ¦ --- ¦ (2) 공사현장의 안전, 보건을 유지하기 위하여 안전보건관리체제를 구성하여야 하며, 안전·보건규정 을 작성한다. (3) 발주자 및 시공자는 공사계약을 체결할 때는 노동부장관이 정하는 바에 따라 산업재해 예방을 위한 표준안전관리비를 공사금액에 계상하여야 한다. (4) 통로면으로부터 높이 2m 이내에 설비 배관 및 Duct 지지대/연결부 등의 장애물을 설치할 수 밖에 없거나 제거하는 것이 곤란할 경우 근로자에게 발생할 수 있는 부상 등의 위험을 방지하기 위한 안전조치 (Protection 및 경고 표시문)를 실시한다. 4.9 타공사와 의 관계 (1) 본 공사 중 건축, 전기공사와 의 관련이 있는 부분의 공사는 해당 발주 담당자와 의 사전협의 후 에 시공하여야하며, 본 공사로 인하여 타공사 공정에 차질이 있거나 타공사에 하자가 발생하지 않도록 시공자는 모든 책임을 다하여야 한다. (2) 바닥, 벽, 기타 건축구조물에 구멍을 뚫거나 중량물을 현수하고자 할 때는 관계 발주 담당자와 협의 하여 건축구조물에 영향이 없음을 확인한 후 진행하여야 한다. (3) 기존 배관과 의 연결 작업은 발주 담당자와 협의 후 지정된 기일 내에 시공하여야 한다. 5. 완성 검사 5.1 관공서의 검사 공사가 완료되었을 때 관공서 또는 공공단체의 시험 및 검사를 필요로 하는 것은 그 시험 및 검사 에 합격하여야 한다. 5.2 완성 검사 시공자는 발주 담당자의 입회 하에 다음의 시험 및 검사를 필요로 하는 것은 그 시험 및 검사에 합 격하여야 한다. (1) 설비의 외관 및 정돈상태의 확인 (2) 설비기기의 작동시험 (도급기기에 한함) (3) 설비기기가 설계도서에 나타내는 용량 및 성능을 갖고, 정상적으로 작동하는 것을 확인하고 주 위환경에 장애를 주지 않는지 확인한다. (도급기기에 한함) 5.3 시운전 및 조정 (1) 시공자는 모든 공사완료 시 시운전 스케쥴을 수립하여 발주 담당자에게 보고하여야 한다. (2) 공사용 및 시험용 전력, 용수, 배수 등 기타 임시 가설공사는 공사진행에 차질이 없도록 시공자 가 시공하여야 한다. (3) 시운전은 부하특성에 따라 하절기, 동절기, 간절기의 계절별로 행한다. 단, 시운전기간은 여건에 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
7fdd04e3-1856-483d-85dc-f72b88a4195f | 21036D-IC-M16G00-HV-A00-00100 M16_Ph-2_시방서-일반공통사항.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00100 Rev. 0 Page 10 of 14 ¦ ¦ --- ¦ --- ¦ --- ¦ 따라 변경 할 수 있다. (4) 시공자는 모든 배관(덕트)공사를 완료한 후 시운전을 실시하기 이전에 관내의 이물질을 제거하 고, 원활한 기능을 보장하기 위하여 FLUSHING 을 실시하여야 한다. (5) 시공자는 시운전을 완료한 후 STRAINER, FILTER 등 배관(덕트)계통에 대한 청소를 기간 협의 하에 실시하여야 한다. (6) 시공자는 모든 공사 완료 후 기계설비에 대한 전반적인 설비 시운전을 실시하고, 종합시운전 결 과 보고서를 작성하여 발주 담당자에게 제출하여야 한다. 6. 기록 (1) 협의 및 지시사항에 대하여 경과 내용을 기록하고 정리한다. (2) 시험 및 검사에 대해서는 기록을 하고 정리한다. (3) 공사공정의 주요부분 등에서 매립 및 은폐 등으로 완성시에 확인이 불가능한 부분은 사진을 찍 어 정리한다. (4) 발주 담당자의 지시가 있을 때에는 그 기록 또는 사진을 제출한다. 7. 공사 인도 완성검사 후 운전지도를 수행하고, 다음에 표시한 관계 도서류를 발주자에게 제출하고 공사를 인계인수 한다. (1) 완성검사 필증 (2) 완성도면(준공도면) (3) 완공사진(특기에 의함) (4) 관공서 등의 허가서류 및 검사필증 (5) 성능시험성적서 및 검사증 (6) 취급설명서(기자재 매뉴얼 포함) (7) 유지관리 지침서 (8) 기기에 부속된 공구류 목록 (9) 예비품 목록 8. 가설공사 8.1 적용 범위 이 절은 건축물의 기계설비공사의 가설공사에 적용한다. SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
5357f78e-cecf-4f64-ab1c-464e45a801a4 | 21036D-IC-M16G00-HV-A00-00100 M16_Ph-2_시방서-일반공통사항.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00100 Rev. 0 Page 11 of 14 ¦ ¦ --- ¦ --- ¦ --- ¦ 8.2 참조 표준 본 시방서에 명시되지 않은 사항은 다음의 시방서를 적용한다. (1) KCS 21 20 05 현장가설공급설비 및 가설시설물 (2) 한국산업표준 KS F 8002 강관 비계용 부재 KS F 8003 강관틀 비계용 부재 및 부속 철물 8.3 재료 KCS 21 20 05 현장가설공급설비 및 가설시설물에 따른다. 8.4 가설 건물 (1) 공사현장의 안전관리, 공사의 시공관리상 필요한 울타리, 가설사무실 등을 설치한다. (2) 화기를 사용하는 장소에는 불연재료의 울타리를 설치하는 등 방화상 필요한 조치를 강구한다. (3) 재료창고는 그 품질 및 기능이 손상되지 않도록 배려한 구조로 한다. 또한 도료, 유류, 기타 인 화성 재료는 건축물 및 재료창고에서 격리된 장소에 보관하며 특히 방화상 안전한 조치를 강구 하고 각 출입문에는 시건장치를 하고 소화기구를 비치한다. (4) 가설건물은 공사가 완성될 때까지는 철거를 원칙으로 하되 필요 시 협의 된 가설물은 존치할 수 있다. 8.5 비계 (1) 공사용 비계는 공사의 종류, 규모, 장소 및 공기 등에 따라 적절한 재료 및 구조의 것으로 설치 하고 보수관리를 한다. (2) 비계는 KS F 8002(강관 비계용 부재) 및 KS F 8003(강관틀 비계용 부재 및 부속 철물) 사용을 원 칙으로 한다. 8.6 작업용 통로 건물내외에 설치한 작업용 통로는 기기의 반입 등에 용이하고, 동시에 안전하게 설치하며 필요에 따라 보수 및 보강을 한다. 8.7 안전시설 (1) 공사 중에는 추락, 낙하방지 등의 안전에 필요한 제반시설물을 공사의 진행에 지장이 없도록 설 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
fcc4b88e-5ffb-40cf-a48d-1c71168cdd6c | 21036D-IC-M16G00-HV-A00-00100 M16_Ph-2_시방서-일반공통사항.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00100 Rev. 0 Page 12 of 14 ¦ ¦ --- ¦ --- ¦ --- ¦ 치한다. (2) 주변의 통행인 등에 영향이 없도록 조치하고 고압선 등이 있을 경우 절연조치 등을 강구하여야 한다. 8.8 장애물 및 매설물 장애물의 철거, 매설물의 이설 및 철거, 가스관, 상수도관, 하수도관, 전기관등 매설물의 규모와 범위 는 설계도서에 따르며, 기타의 경우는 협의 하여 정한다. 8.9 공사용 전력, 용수 및 배수 공사용 및 실험용 전력, 용수, 배수, 기타 공사상 필요한 설비의 계획 및 시공은 공사진행에 지장이 없도록 이행한다. 8.10 인접물 보호 인접한 건물과 공작물에 대한 보호 조치가 필요할 때에는 공사 진행에 지장이 없도록 이를 시행한 다. 8.11 임시 난방 (1) 시공작업을 위해 명시된 조건을 유지하기 위해 난방장치와 열공급을 하고, 그 비용을 부담해야 한다. (2) 발주자가 난방비를 지불하는 경우에는 에너지보전 설비를 하고, 별도의 열량계를 설치하여 사용 된 열량에 대한 비용은 발주자로부터 정산 받아야 한다. (3) 개별 시방에 달리 명시된 것이 없으면 시공이 진행중인 구역에서 실내온도는 영상온도 이상으 로 유지해야 한다. 8.12 임시 냉방 (1) 시공작업을 위해 명시된 조건을 유지하기 위해 냉방장치를 갖추고 그 비용을 부담해야 한다. (2) 발주자가 냉방비를 지불하는 경우에는 에너지보전 설비를 하고, 별도의 열량계를 설치하여 사용 된 열량에 대한 비용은 발주자로부터 정산 받아야 한다. (3) 개별 시방에 달리 명시된 것이 없으면 시공이 진행중인 구역에서 실내온도는 28°C 이하으로 유 지해야 한다. 8.13 임시 환기 (1) 재료의 양생, 습기제거, 먼지, 연기, 수증기 또는 가스의 축척방지를 위해 폐쇄된 구역은 환기를 SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
e2acd0e2-3b20-4d53-96c5-40584581f3f7 | 21036D-IC-M16G00-HV-A00-00100 M16_Ph-2_시방서-일반공통사항.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00100 Rev. 0 Page 13 of 14 ¦ ¦ --- ¦ --- ¦ --- ¦ 해야 한다. (2) 기존 환기가 있는 경우 활용할 수 있고, 시공작업을 위해 청정공기를 유지하는 데 필요한 임시 환풍기로 시설용량을 확장, 보충해야 한다. 8.14 임시 상수도 (1) 시공작업을 위해 필요한 급수시설은 수질이 적합하여야 하고 공사착공 준비 시에 설치 한다. (2) 발주 담당자가 용수비를 지불하는 경우에는 수량보전시설을 하고, 발주처의 요구시 별도의 계량 기를 설치 한다. (3) 배관을 연장하고 급수전을 설치하고 나사로 연결되는 호스로 물을 사용할 수 있게 해야 하며, 동결방지를 위해서는 임시단열을 시공해야 한다. 8.15 임시 하수시설 (1) 기존시설물을 사용할 수 없는 경우에는 공사착공준비 시에 필요한 하수시설을 하고 유지관리해 야 하며, 현장은 항시 깨끗하고 위생적인 상태로 유지해야 한다. (2) 시공완료시에 시설물을 당초와 같거나 더 좋은 상태로 보수해서 반환해야 한다. 8.16 임시 현장배수 (1) 현장의 바닥면은 자연배수 되도록 비탈을 두고 땅파기 하는 구역에 물이 유입되지 않게 하고, 필요하면 펌프를 설치해서 운전, 유지관리해야 한다. (2) 현장에 물이 고이거나 흘러내리지 않게 하고, 물막이를 해서 세굴되지 않게 해야 한다. 8. 17 현장보안 (1) 공사착수 후 조속한 시일 내에 현장인원이 아닌자가 건물 내로 무단출입하거나 배회하지 못하 게 하고, 도난에 대비할 수 있도록 지상층과 출입이 가능한 곳에 보안시설을 한다. (2) 발주 담당자의 보안계획과 맞추어야 한다. 8. 18 공사 표지판 (1) 시공자는 건설산업기본법 제 43 조 제 1 항의 규정에 의하여 건설공사 현황의 표지를 설치하여야 한다. (2) 공사표지판은 발주 담당자가 지정하는 크기, 재료, 색상 및 방법으로 제작하여, 발주 담당자가 지정한 위치에 설치해야 한다. (3) 현장에는 법규로 요구된 경우를 제외하고, 발주 담당자의 허가 없이 다른 표지판을 설치해서는 아니 된다. SK SK hynix 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
aa00452e-178e-42a5-99f2-ddf379f147a6 | 21036D-IC-M16G00-HV-A00-00100 M16_Ph-2_시방서-일반공통사항.pdf | ¦ PJT : M16 Ph2 Project Client : SK hynix Date : 25.JAN. 2022 ¦ SPECIFICATION FOR HVAC & PLUMBING SYSTEM ¦ 21036D-IC-M16G00-HV-A00-00100 Rev. 0 Page 14 of 14 ¦ ¦ --- ¦ --- ¦ --- ¦ 8. 19 공사 중 현장청소 및 폐기물 제거 (1) 공사구역에는 폐자재, 부스러기 및 쓰레기 등이 없게 유지하고, 현장은 깨끗하고 정연한 상태 로 유지해야 한다. (2) 현장에 울타리를 치기전에 부스러기와 쓰레기는 제거해야 한다. (3) 표면마무리를 시작하기 전에 실내구역은 비빌하고, 진공청소를 해서 먼지가 일지 않게 청소를 계속해야 한다. (4) 매주 현장에서 폐자재, 부스러기, 쓰레기 등을 수거해서 제거하고, 현장 밖으로 처리해야 한다. (5) 덮개가 없는 슈트는 사용해서는 아니되며, 폐쇄된 슈트의 하단에는 뚜껑을 두고 용기 속에 묻 히게 해야 한다. (6) 위험하지 않고 비유독성 쓰레기를 처리할 수 있는 용기를 지정된 장소에 비치해야 한다. 8. 20 가설 시설물의 철거 (1) 임시시설물은 준공 전에 현장에서 철거하여야 한다. (철거가 원칙이며, 필요시 연장 가능) (2) 기초 구조체콘크리트 및 지중에 매설물은 30cm 이상 깊이까지 제거하여야 한다. (3) 임시공급시설의 설치 또는 사용으로 입은 손상을 청소하고 보수해야 하며, 영구시설물은 명시 된 상태로 복구해야 한다. - End of Document - SK hynix SK 경고: 본 문서는 SK hynix 의 기업비밀 자료로서, 어떠한 경우에도 목적 외 사용, 복제, 제 3 자에게 공개, 누설 및 유출할 수 없으며, 회사는 유포자의 불법 사용으로 피해가 발생할 경우 유포자에게 민/형사상 책임을 요구할 수 있음. ecoplant | {}
946b0bcb-24bd-4cc7-a8f3-eb873e5270d3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Automobiles 11.11 Expansion Devices. Virtually all modern automobiles use either a thermostatic expansion valve (TXV) or an orifice tube (or both, for dual-evaporator systems) as the expansion device (see Chapter 1 1 of the 2018 ASHRAE Handbook- -Refrigeration for more on these devices). Schematics of systems that use these devices are provided in the Controls section. Automotive TXVs operate in the same manner as those for com- mercial HVAC systems. Both liquid- and gas-charged power ele- ments are common. Internally and externally equalized valves are used as dictated by system design. Externally equalized valves are necessary where high evaporator pressure drops exist. A bulbless expansion valve, usually block-style, that senses evaporator outlet pressure without the need for an external equalizer is now widely used. TXV systems use a receiver-drier-filter assembly for refrigerant and desiccant storage. Because of their low cost and high reliability, orifice tubes have become increasingly popular with automotive manufacturers. Devel- oping an orifice tube system requires that components be matched to obtain proper performance. The orifice tube is designed to operate at 90 to 95% quality at the evaporator outlet, which requires a suction- line accumulator to protect the compressor from floodback and to maintain oil circulation. Because the orifice tube does not fully use the latent heat in the refrigerant systems, orifice-tube systems gener- ally require higher refrigerant flow than TXV systems to achieve the same performance. However, an orifice tube ensures that the com- pressor receives a continuous flow of cool refrigerant from the accu- mulator, offering benefits in compressor durability over a TXV system. Orifice-tube systems use an accumulator-drier-filter for refrigerant and desiccant storage. Receiver-Drier-Filter Assembly. A receiver-driver is installed in the A/C loop on the high-pressure side downstream of the con- denser. Several types of desiccant are used, the most common of which is spherical molecular sieves; silica gel is occasionally used. The unit typically has desiccant either in a bag or cartridge, or sandwiched between two plates. The receiver-drier (1) serves as a reservoir for refrigerant from part- to full-load operating conditions, (2) removes moisture from the system, (3) filters out debris headed for the TXV, and (4) only allows liquid refrigerant to enter the TXV (liquid is removed from the top of the unit, and comes from the bottom via a tube connected to the top fitting). The receiver-drier assembly accommodates charge fluctuations from changes in system load. It accommodates an overcharge of refrigerant to compensate for system leaks and hose permeation. The assembly houses the high-side filter and desiccant. Mechanical integrity (freedom from powdering) is important because of the vibration to which the assembly is exposed. For this reason, molded desiccants have not obtained wide acceptance. Moisture retention at elevated temperatures is also important. Consider the rate of release with temperature increase and the reaction while accumulating high concentration. Design temperatures should be at least 60°C. Receivers are usually (though not always) mounted on or near the condenser. They should be located so that they are ventilated by ambient air. Pressure drop should be minimal. Typically, a receiver- drier has a pressure switch or a pressure transducer installed that controls A/C system operation at high pressure. Suction-Line Accumulators. A suction-line accumulator is re- quired with an orifice tube to ensure uniform return of refrigerant and oil to the compressor, to prevent slugging, and to cool the compressor. It also stores excess refrigerant. A typical suction-line accumulator is shown in Figure 8. A bleed hole at the bottom of the standpipe meters oil and liquid refrigerant back to the compressor. The filter and desiccant are contained in the accumulator because no receiver-drier is used with this system. Evaporator. The evaporator connects the air side of the air- conditioning system to the refrigerant side. Design aspects for the air side are discussed in the Air-Handling Subsystem section. The ![image](/image/placeholder) INLET STAND PIPE MOLECULAR SIEVE FILTER PADS CONTAINERS 9 OUTLET Fig. 8 Schematic of Typical Accumulator-Dehydrator primary design consideration for the refrigerant side of the evapora- tor is low pressure drop. Because the evaporator operates at satura- tion, higher-pressure-drop evaporators cause nonuniform discharge temperatures unless they are designed with careful attention to pass arrangement. The space available in an automotive system does not allow for distribution manifolds and capillary tube systems outside of the evaporator envelope; this must be done within the evaporator itself. Automotive evaporators must also mask the variation in com- pressor capacity that occurs with accelerating and decelerating. To avoid undesirable temperature splits, sufficient liquid refrigerant should be retained at the last pass to ensure continued cooling during acceleration. High refrigerant pressure loss in the evaporator requires exter- nally equalized expansion valves. A bulbless expansion valve, called a block valve, provides external pressure equalization with- out the added expense of an external equalizer. The evaporator must provide stable refrigerant flow under all operating conditions and have sufficient capacity to ensure rapid cooldown of the vehicle after it has been standing in the sun. Auxiliary Evaporators. Many sport-utility vehicles, vans, and limousines are equipped with auxiliary or secondary air-conditioning modules located to cool rear-seat passengers. These system exten- sions provide some unique challenges. Most of these systems oper- ate only when there are passengers in the rear space. Consequently, sometimes there is refrigerant flow through the primary ACM and none through the secondary. Pay careful attention to refrigerant plumbing to avoid refrigerant and oil traps in the suction line. The auxiliary suction line must never allow liquid oil to run downhill from the front system when there is no flow to carry it back to the accumulator-dehydrator. Designing highly efficient oil separators into the line set results in frequent compressor failure. Refrigerants and Lubricants. The 1997 Kyoto Protocol identi- fied the almost universally used R-134a as a global warming gas, sparking a search for alternatives among vehicle manufacturers and their suppliers. To address the global warming concerns of R-134a, some OEMs around the world have started using hydrofluoroolefin (HFO-1234yf) as a replacement for HFC-134a. HFO-1234yf offers a good combination of energy efficiency, safety, and ease of cus- tomer conversion. It has a global warming potential (GWP) of less Inc. ASHRAE, 2019 user. single for Licensed | {}
a7d373fc-6753-425c-ba67-10368205597b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 11.12 2019 ASHRAE Handbook-HVAC Applications (SI) Chart Type: line 150-100 200-250 250-300 300-350 350-400 400-450 450-500 500-550 item_01 1Bar 3Bar 4Bar 10Bar 20Bar 30Bar 40Bar 10Bar Reference State: h = 178.36 kJ/kg for saturated liquid at 0°C ENTHALPY, kJ/kg Chart Type: line -10 -5 0 5 10 15 20 item_01 12kg/m3 14kg/m3 16kg/m3 18kg/m3 22kg/m3 29kg/m3 32kg/m3 Fig. 9 Comparison of Thermodynamic Cycle Between Base Case (R-134a) and HFO-1234yf (Spatz and Minor 2008) than 1, which is 99.9% lower than HFC-134a, and is even less than CO2 (GWP = 1). HFO-1234yf offers atmospheric lifetime and fuel efficiency benefits as well. This refrigerant has excellent environ- mental properties, low toxicity (similar to R-134a), and system per- formance similar to that ofR-134a. It is being considered as a drop- in refrigerant for current mobile air-conditioning systems (MACS). Testing shows that both polyalkylene glycol (PAG) and polylol ester (POE) lubricants are compatible with HFO-1234yfin A/C sys- tems with different types of compressors (Koban 2009; Spatz and Minor 2008, 2009). HFO-1234yf is being used by many OEMs globally, and as of December 2017, 45 million vehicles on the road used this refrigerant (Honeywell 2018). Figure 9 compares R-134a and HFO-1234yf A/C cycles on the p-h diagram along with vapor density at suction temperatures (Spatz and Minor 2008). For HFO-1234yf, the latent heat of vaporization is lower and the vapor density at suction temperature is greater, com- pared to an R-134a system. Thus, for the same cooling capacity, the refrigerant mass flow rate for HFO-1234yf should be higher than in an R-134a system. Figure 10 compares the vapor pressures of the two fluids (Kontomaris and Leck 2009). Typical evaporating satura- tion pressures for HFO-1234yf are higher than for R-134a; HFO- 1234yf pressure equals R-134a pressure at 37.8°C; and HFO-1234yf pressure is lower than R-134a above 37.8°C. Hence, in comparison to R-134a, a slightly higher evaporating pressure and slightly lower condensing pressure for HFO-1234yf reduces the pressure ratio, thereby improving system coefficient of performance (COP). Sev- eral OEMs and suppliers (Bang 2008; Mathur 2010a, 2010b, 2011a, 2011b, 2012, 2013, 2018a; Meyer 2008, 2009; Minor 2008) have conducted independent tests with HFO-1234yf. SAE also conducted tests with alternative refrigerants, including HFO-1234yf (Atkinson 2008), through cooperative research projects (Hill 2008). European Regulation ofMobile Air Conditioning. The E.U. direc- tive (Directive 2006/40/EC) scheduled phaseout of HFC-134a to start on January 1, 2011, for all new or significantly redesigned mod- els introduced that year. As of that date, retrofitting vehicles with HFC-134a is not allowed. From January 1, 2017, no new vehicles sold in the E.U. can use HFC-134a or any fluorinated gas with a glob- al warming potential higher than 150; all models must be redesigned by the 2017 deadline. Acceptable refrigerants (with a GWP < 150) include HFC-152a, CO2, and HFO-1234yf. Refrigerant leakage rates for single- and dual-evaporator A/C systems have been defined as HFO-1234yf : VAPOR PRESSURE Chart Title: HFO-1234vi: VAPOR PRESSURE X-Axis: Temperature °C Y-Axis: VAPOR PRESSURE (MPa) Chart Type: line -40°C -20°C 0°C 20°C 40°C 60°C 80°C 100°C item_01 0.0MPa 0.2MPa 0.3MPa 0.4MPa 0.7MPa 1.2MPa 2.6MPa 0.9MPa TEMPERATURE, Fig. 10 Comparison of Vapor Pressure Between Base Case (R-134a) and HFO-1234yf (Kontomaris and Leck 2009) less than 40 and 60 g, respectively. Using non-refillable containers is no longer allowed. All fluorinated gases covered by the Kyoto pro- tocol will be recovered. Enhanced R-134a Systems. SAE initiated a program to improve the performance of existing R-134a systems. The goals are to (1) identify technologies to reduce mobile air-conditioning system R-134a refrigerant leakage by 50%, (2) improve R-134a mobile air-conditioning system COP by 30%, (3) reduce vehicle soak and driving heat loads by 30% over current vehicles to reduce cooling requirements, and (4) reduce refrigerant loss during service and at end of life by 50%. Suction Line Heat Exchanger. A/C system performance can be improved by adding a suction line heat exchanger into the system. This directly influences the thermal comfort for the occupant along with fuel economy and exhaust emissions. A suction line heat ex- changer in an A/C loop (1) increases system performance, (2) sub- cools liquid refrigerant to prevent flash gas formation at inlets to the expansion valve, and (3) fully evaporates any residual liquid that may remain in the suction line before reaching the compressor. Inc. ASHRAE, 2019 user. single for Licensed | {}
19d930cb-a668-4fa0-b5d7-598c85157e6e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Automobiles 11.13 ![image](/image/placeholder) INTERNAL CONDENSER COMPRESSOR AIR-MIXING DOOR INTERNAL EVAPORATOR AIR-HEATING EXPANSION VALVE ABSORBING HEAT EXTERNAL HEAT EXCHANGER AIR-COOLING EXPANSION VALVE Fig. 11 Heat Pump System in Heating Mode (Denso 2018) Performance of mobile air conditioning systems can be enhanced from 6 to 12% (Kurata et al. 2007; Mathur 2009c, 2011a). Electric Vehicles and Heat Pump Systems. Due to stricter environmental regulations and higher fuel economy standards from the government, car manufacturers are investigating different options for fuel economy. One of the options is electrification of the propulsion system, resulting in significant gains in fuel economy and a reduction of global warming gases. Currently, a majority of car makers either already offer electric vehicles (e.g., Nissan Leaf, GM Chevy Bolt, etc.) or have models in the process of design. Customers expect the same level of comfort in EVs as they are accustomed to in conventional vehicles. However, heating and/or cooling has a big influence on vehicle energy efficiency. For con- ventional vehicles, heating and cooling affects fuel economy, but waste heat from the engine is available for heating the cabin. EVs do not have this waste heat, so it is necessary to use electric positive temperature coefficient (PTC) heaters. Using a heat pump system along with a PTC heater consumes a significant amount of battery power that could severely limit the driving range of the EV. Typically, air-sourced heat pumps are used for the automotive industry (Feng and Hrnjak 2016). Heat pump systems are used in EVs to provide heating, cooling, and dehumidification. Electric compressor and electronic thermostatic expansion valves (TXVs) are used for the heat pump system to optimize for energy consump- tion. Typical automotive heat pump systems are shown in Figures 11 and 12 (Denso 2018). Heating Mode (Figure 11). The compressor compresses low- temperature, low-pressure gas refrigerant into high-temperature, high-pressure gas refrigerant. The latter warms the vehicle cabin by releasing its heat to the cabin air as it passes through the internal condenser, while being cooled and condensed into a liquid state. The liquefied refrigerant expands across the air-heating expansion valve into a low-temperature, low-pressure gas/liquid two-phase refrigerant, extracts atmospheric thermal energy via the external heat exchanger, and flows back into the compressor. Cooling Mode (Figure 12). The compressor compresses low- temperature, low-pressure gas refrigerant into high-temperature, high-pressure gas refrigerant. The high-temperature, high-pressure gas refrigerant passes through the internal condenser without heat exchange (the air-mixing door blocks the flow of air into the internal condenser) to the external heat exchanger where the refrigerant is cooled by the ambient air and condensed into a liquid state. The liq- uefied refrigerant expands across the air-cooling expansion valve into a low-temperature, low-pressure gas/liquid two-phase refrigerant, absorbs heat from the cabin air to cool the cabin as it passes through the evaporator, and then flows back into the com- pressor. Further details on the heat pump system and their opera- tions are given in Chapter 49 of the 2016 ASHRAE Handbook- - HVAC Systems and Equipment. Advanced Technologies HVAC suppliers are aggressively working on advancements for mobile HVAC to reduce energy consumption and improve thermal comfort for occupants. For instance, researchers are investigating using ventilated car seats to reduce air conditioning use and improve fuel efficiency without compromising thermal comfort (Lustbader 2005). Some other important technologies are as follows. Micro Climatic Zone for Heating and Cooling. In a conven- tional vehicle, the entire cabin is conditioned to comfort conditions based on the set point decided by the driver. Maintaining a certain cabin temperature in winter or summer uses significant energy. Typ- ically, for a midsized sedan, the total airflow through the HVAC unit is 150 L/s for cooling and 100 L/s for heating. In the United States, a vast majority of the vehicles are driven with only one occupant. In a conventional vehicle, the entire cabin has to be conditioned, even when only a single person is inside of the vehicle. Many companies (OEMS and suppliers) have been developing new concepts for heat- ing and cooling by creating "micro-zones" for cooling and heating. The objective is to reduce energy consumption by providing thermal comfort to occupants on an individualized basis. In this case, the total airflow required per person to create microzones is about 7 L/ s per person. Therefore, for a vehicle with four occupants, the total airflow will be 57 L/s, which is 38% of the total cabin airflow rate. This approach is extremely useful for EVs, because the HVAC energy consumption directly affects the vehicle's driving range. Ventilated seats are also used by some OEMs to create microzones to provide quick thermal comfort to the occupants (Berry et al. 2017; Morishita et al. 2018). Engine Start/Stop Feature for Energy Efficiency. In recent years, start/stop systems have been widely adopted for various vehi- Inc. ASHRAE, 2019 user. single for Licensed | {}
dd839290-8821-4c2b-8950-4b783fe9f98b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 11.14 2019 ASHRAE Handbook- -HVAC Applications (SI) ![image](/image/placeholder) INTERNAL CONDENSER COMPRESSOR AIR-MIXING DOOR INTERNAL EVAPORATOR AIR-HEATING EXPANSION VALVE RELEASING HEAT EXTERNAL HEAT EXCHANGER AIR-COOLING EXPANSION VALVE Fig. 12 Heat Pump System in Cooling Mode (Denso 2018) cles as a countermeasure to environmental problems caused by automobiles and to improve fuel economy. Stoppage at a red light can be 30 to 60 S; in some countries, the red light duration may be longer. According to a recent survey (Autobeat 2018), 70% of the vehicles produced in the United States will have this feature within the next 5 years. On such vehicles, air conditioner compressors driven by an engine stop when the vehicle stops at a traffic signal. As a result, comfort of occupants deteriorates because of a rise in air temperature from the A/C outlets (Uematsu et al. 2015). On the other hand, ifthe engine is started at a traffic signal to improve occu- pant comfort, the fuel economy deteriorates. To best support pas- senger comfort while the engine is stopped, the HVAC system should be able to continue providing thermal comfort. This can be accomplished using the following systems: · Secondary loop. A secondary loop cooling system incorporates two different working fluids to provide cooling. In all systems, the primary loop is a traditional direct-expansion design that uses a phase-change refrigerant (e.g., R-134A) and a compressor to cir- culate the refrigerant (Ghodbane 2000; Ghodbane et al. 2007; Menken et al. 2016). Figures 3 and 4 are both schematics for tra- ditional direct-expansion systems. A heat exchanger is used to transfer energy from the primary loop to the secondary loop, which is called a chiller (Figure 13). In most applications, the working fluid in the secondary loop is a single-phase fluid that is circulated by a pump to the cooling coil. This cooling coil is placed in the HVAC unit. Note that, in a secondary system, the heat exchanger in the HVAC is called a cooling coil (not an evaporator), given this is a single-phase fluid circuit. Typically, automotive coolant is used as the working fluid. The secondary fluid absorbs energy as the hot air passes through the cooling coil. Figure 13 is a schematic representation of this type of secondary loop. The cooled fluid is circulated in the HVAC unit through a coil that provides cold air to the cabin. The size of the chiller depends on vehicle stoppage times. · Evaporators with Phase-Change Materials (PCMs). Currently, cool-storage evaporators are used on many vehicles to continue providing thermal comfort to the occupants during stops at traffic signals (LaClair et al. 2016; Sato et al. 2016). The cool-storage evaporator prevents temperature increase both of air through ![image](/image/placeholder) Fig. 13 Automotive HVAC Unit with a Secondary Loop (Ghodbane 2007) C compressor) stops. In cool-storage evaporators, some of the plates have phase-change material that stores the energy at cold temperatures. During a vehicle stoppage, the evaporator contin- ues to provide thermal energy from the phase-change material. Figure 14 shows a cool storage evaporator (Morishita et al. 2018) that has five plates containing the phase-change material. These plates are stacked inside the evaporator so that the cold energy stored in these five plates, along with the aluminum heat exchanger, can be used to continue providing thermal comfort to occupants while the engine is off. Evaporators with thermal storage materials have been investigated for idle start/stop func- tion (Automotive Engineering 2012). Many researchers have been conducting research on improvement of heating in electric vehicles using phase-change materials. Brushless Motors. These motors are simpler than standard motors and are more reliable. Advantages include the following: (1) motor efficiency is higher, (2) commutation is accomplished electroni- cally, (3) very high speeds and torque are possible without arcing, (4) thermal resistance is lower and the operating temperature range is thus wider, and (5) the absence of brushes reduces maintenance requirements and eliminates brush residue contamination of bear- ings or the environment. Because there is no brush arcing or com- vents and of the cabin when the engine (and consequently the A/ Inc. ASHRAE, 2019 user. single for Licensed | {}
66ed5bb2-2cb6-451c-8e9d-fdc3e32f6cb8 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Automobiles 11.15 ![image](/image/placeholder) COOL STORAGE CASE → Fig. 14 Energy Storage Evaporator (Morishita et al. 2018) mutation, brushless motors are much quieter, both electrically and audibly. Positive-Temperature-Coefficient (PTC) Heaters. PTC heaters are small, ceramic-based heaters that use less energy and less time to heat more quickly than conventional units. They self- regulate at a preset temperature by regulating resistance to vary their wattage. Thus, their greater thermal dissipation results in higher efficiency. These systems are maintenance-free and very reliable. PTC heaters could be used in the HVAC system to hasten cabin heating during cold start-ups by providing heat to occupants until the engine is warm (Hauck 2003). Thermoelectric Devices. Thermoelectric devices (TEDs) are used to help create microzones to provide thermal cabin comfort. These devices work using the Peltier effect, wherein a voltage is applied between two wire joints with dissimilar materials. These devices are placed inside seats to provide quick thermal comfort to occupants (Arsie et al. 2014). w ater-Cooled Condensers. Water-cooled condensers are being investigated by OEMs and suppliers to reduce costs and space required for rejecting engine heat (Mathur et al. 2012). The advan- tage of this system is that a water-cooled condenser can be placed at any location, rather than just the front of the vehicle. However, the condenser head pressure increases due to high engine coolant tem- peratures, and that has a negative impact on vent outlet temperatures. Magnetic Cooling. Magnetic refrigeration is a promising al- ternative cooling technology (Monfared et al. 2014; Yanik and Ce- lik 2018). When a suitable magnetic material is exposed to a changing magnetic field, it undergoes a temperature change (magneto-calorific effect). When the material is magnetized (i.e., an increase in the magnetic field), its temperature increases. When the material is demagnetized (i.e., decrease in the magnetic field), its temperature decreases. The cooling intensity depends on the magnetic material used. Magnetic refrigeration essentially works by recapturing produced cooling energy via a heat transfer fluid, such as water. Magnetic cooling is quieter, safer, more compact, higher efficiency, and environmentally friendly (as no refrigerants are used for cooling). In MACS applications, approximately 200 W (at a t of20 K; Torregrosa-Jaime et al. 2013) of cooling has been achieved with the currently available magnetic materials. A lot of research and development is being done in national laboratories, universities, and suppliers (within the United States and around the world) to de- velop new materials for magnets. The new material properties will result in improvement of cooling and heating power densities with relatively small magnets. Smart Engine Cooling Systems with Electric Water Pumps (EWPs). These cooling systems use both an electric and mechan- ical water pump, or replace the mechanical water pump with a EWP (Wagner et al. 2003). Typically, an EWP system includes a 100 to 600 W electric pump, four-way water valve (Chanfreau and Farkh 2003), sensor, engine control management system, soft- ware, and a variable-speed radiator fan. At cold start-ups, allowing little or no flow to the radiator hastens engine warm-up, thus reducing emissions and improving fuel economy. Because the water (or coolant) temperature is precisely maintained, thermal stresses on the engine are less. Once the engine coolant is heated, this system can provide thermal comfort, even at idle or with the engine off, by pumping coolant through the heater core and run- ning the blower. 42 v Systems. Energy requirements of modern vehicles have in- creased significantly as the needs of motors, actuators, and other electrical equipment have increased. Auto manufacturers are inves- tigating using 42 v for high-load equipment (e.g., compressors, blower, condenser fans, PTC heaters, controls), and reserving the ex- isting 12 v grid for lighting and other smaller-load accessories. This would improve air-conditioning system performance, because com- pressor speed would be independent of engine speed. These systems could be used for hybrid, electric, or fuel-cell vehicles. Autonomous Vehicles. Autonomous vehicles (SAE Standard J3016) are self-driving, driverless, or robotic vehicles. A number of companies are working on such vehicles. Some of the proposed ar- chitecture, such as the front two seats turning 180° to face the rear occupants, is drastically different from traditional designs. These vehicles will have significant computing power (equivalent to that of about five to ten laptops) to process the data on a real-time basis. Expectations are that people will spend more time in autonomous vehicles, and that vehicle travel by nondrivers (e.g., older people who cannot drive anymore) will increase. One prediction is that a fleet of autonomous vehicles will be maintained by various compa- nies and shared by the users, with reduced vehicle ownership. Ad- vocates predict that by 2030 (Litman 2018), such vehicles will be sufficiently convenient and affordable to displace most human- operated vehicles, reduce driving stress, provide independent mo- bility to nondrivers, and be a panacea for congestion, accident, and pollution problems. The architecture of the HVAC system will be very different for autonomous vehicles. Additional heat generated by the computers will have to be removed by the HVAC system or using an independent cooling system. There is a strong need to de- velop extensive control strategies for heating, humidification, dehu- midification, and cooling for these vehicles. REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal. ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. ACGIH. 2014. 2014 TL VsⓇ and BEIsⓇ. American Council of Governmental Industrial Hygienists, Cincinnati, OH. Arsie, I., A. Cricchio, V. Marano, C. Pianese, M. De Cesare, and W. Nesci. 2014. Modeling analysis of waste heat recovery via thermo electric gen- erators for fuel economy improvement and CO2 reduction in small diesel engines. SAE International Journal of Passenger Cars- Electronic and Electrical Systems 7(1):246-255. ASHRAE. 2013. Thermal environmental conditions for human occupancy. ANSI/ASHRAE Standard 55-2017. ASHRAE. 2016. Ventilation for acceptable indoor air quality. ANSI/ ASHRAE Standard 62.1-2016. Atkinson, W. 2000. Designing mobile air conditioning systems to provide occupant comfort. SAE Paper 2000-01-1273. Society of Automotive Engineers, Warrendale, PA. Atkinson, W. 2008. Interior climate control committee activities. Mobile AC Climate Protection Partnership Meeting, U.S. Environmental Protection Agency, Washington, D.C. Inc. ASHRAE, 2019 user. single for Licensed | {}
e171eaff-a8c8-4b5e-b81e-5a72922f11ce | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 11.16 2019 ASHRAE Handbook-HVAC Applications (SI) Atkinson, W., W. Hill, and G. Mathur. 2017. The impact of increased air recirculation on interior cabin air quality. SAE Paper 2017-01-0169. Society of Automotive Engineers, Warrendale, PA. Automotive Engineering. 2012. Thermal storage evaporators offer idle-stop cost saving for A/C operation. (May.) Autobeat Daily. 2018. www.autobeatdaily.com/. Bang, S. 2008. Flammability evaluation: R-134a, HFO-1234yf and CO2. Mobile AC Climate Protection Partnership Meeting, U.S. Environ- mental Protection Agency, Washington, D.C. www.eea.europa/policy -documents/directive-2006-40-ec. Berry, S., M. Kolich, J. Line, and W. ElMaraghy. 2017. A review of human physiological, psychological & human biomechanical factors on per- ceived thermal comfort of automotive seats. SAE Paper 2017-01-1388. Society of Automotive Engineers, Warrendale, PA. Chanfreau, M., and A. Farkh. 2003. The need for an electrical water valve in a thermal management intelligent system (ThemisSt). SAE Paper 2003- 01-0274. Society of Automotive Engineers, Warrendale, PA. DOT. 2012. Windshield defrosting and defogging systems. Code ofFederal Regulations, 49 CFR 571.103. U.S. Department of Transportation, National Highway Traffic Safety Administration, Washington, D.C. www.ecfr.gov. EU. 2006. Directive 2006/40/EC relating to emissions from air-conditioning systems in motor vehicles. European Union. www.eea.europa.eu/policy -documents/directive-2006-40-ec. Feng, F , and P. Hrnjak. 2016. Experimental study ofan air-conditioning heat pump system for electric vehicles. SAE Paper 2016-01-0257. Society of Automotive Engineers, Warrendale, PA. Ghodbane, M. 2000. On vehicle performance of a secondary loop A/C sys- tem. SAE Paper 2000-01-1270. Society of Automotive Engineers, War- rendale, PA. Ghodbane, M., T.D. Craig, and J.A. Baker. 2007. Demonstration of an energy-efficient secondary loop HFC-152a mobile air conditioning system. Report EP07H001055. Environmental Protection Agency, Washington, D.C. Guan, Y., M.H. Hosni, B. W. Jones, and T.P. Gielda. 2003a. Investigation of human thermal comfort under highly transient conditions for automobile applications, part 1: Experimental design and human subject testing implementation. ASHRAE Transactions 109(2):885-897. Guan, Y., M.H. Hosni, B. W. Jones, and T.P. Gielda. 2003b. Investigation of human thermal comfort under highly transient conditions for automobile applications, part 2: Thermal sensation modeling. ASHRAE Transac- tions 109(2):898-907. Guan, Y., M.H. Hosni, B. W. Jones, and T.P. Gielda. 2003c. Literature review of the advances in thermal comfort modeling. ASHRAE Transactions 109 (2):908-916. Hauck, A. 2003. PTC air heater with electronic control units Innovative compact solutions. SAE Paper C599/058/2003. Society of Automotive Engineers, Warrendale, PA. Hill, W. 2008. Industry evaluation oflow global warming potential refriger- ant HFO-1234yf. Mobile AC Climate Protection Partnership Meeting, U.S. Environmental Protection Agency, Washington, D.C. Honeywell. 2018. Solstice� yf refrigerant. www. 1234facts.com/. Jeffers, M., L. Chaney, and J. Rugh. 2016. Climate control load reduction strategies for electric drive vehicles in cold weather. SAE International Journal of Passenger Cars-Mechanical Systems 9(1):75-82. Jokar, A., S.J. Eckels, and M.H. Hosni. 2004. Evaluation ofheat transfer and pressure drop for the heater-core in an automotive system. Proceedings ofthe ASME International Mechanical Engineering Congress, Anaheim, CA. Jones, B. W. 2002a. The quality of air in the passenger cabin. Proceedings of Cabin Health 2002, International Air Transport Association, Geneva. Jones, B. W. 2002b. Capabilities and limitations of thermal models for use in thermal comfort standards. Energy and Buildings 34(6):653-659. Koban, M. 2009. HFO-1234yf low GWP refrigerant LCCP analysis. SAE Paper 2009-01-0179. Society ofAutomotive Engineers, Warrendale, PA. Kontomaris, K., and T.J. Leck. 2009. Low GWP refrigerants for centrifugal chillers. Presented at ASHRAE Annual Conference, Louisville, KY. Kurata, S., T. Suzuki, and K. Ogura. 2007. Double-pipe internal heat ex- changer for efficiency improvement in front automotive air conditioning system. SAE Paper 2007-01-1523. In Thermal systems & management systems, Special Publication SP-2132. Society of Automotive Engi- neers, Warrendale, PA. LaClair, T., Z. Gao., 0. Abdelaziz, M. Wang, et al. 2016. Thermal storage system for electric vehicle cabin heating Component and system anal- ysis. SAE Paper 2016-01-0244. Society of Automotive Engineers, War- rendale, PA. Littman, T. 2018. Autonomous vehicle implementation predictions. Victoria Transport Policy Institute, Victoria, British Columbia. Lustbader, J.A. 2005. Evaluation of advanced automotive seats to improve thermal comfort and fuel economy. Report NREL/CP-540-37693. Na- tional Renewable Energy Laboratory, Golden, CO. www.nrel.gov/docs /gen/fy06/37693.pdf Mackenzie, P.T., P.A. Lebbin, S.J. Eckels, and M.H. Hosni. 2004. The effects of oil in circulation on the performance of an automotive air con- ditioning system. Proceedings of the ASME Heat Transfer/Fluids Engi- neering Summer Conference (HTFED '04), Charlotte, NC. Mathur, G.D. 1998. Performance of serpentine heat exchangers. SAE Paper 980057. Society of Automotive Engineers, Warrendale, PA. Mathur, G.D. 1999a. Investigation of water carryover from evaporator coils. SAE Paper 1999-01-1194. Society of Automotive Engineers, Warren- dale, PA. Mathur, G.D. 1999b. Predicting and optimizing thermal and hydrodynamic performance of parallel flow condensers. SAE Paper 1999-01-0236. Society of Automotive Engineers, Warrendale, PA. Mathur, G.D. 2000a. Simulation of thermal and hydrodynamic performance of laminate evaporators. SAE Paper 2000-01-0573. Society of Automo- tive Engineers, Warrendale, PA. Mathur, G.D. 2000b. Water carryover characteristics from evaporator coils during transitional airflows. SAE Paper 2000-01-1268. Society of Auto- motive Engineers, Warrendale, PA. Mathur, G.D. 2001. Performance prediction of a laminate evaporator with hydrocarbons as the working fluids. SAE Paper 2001-01-1251. Society of Automotive Engineers, Warrendale, PA. Mathur, G.D. 2002. Experimental investigation to determine the effect of laminated evaporators' tank position on heat transfer and pressure drop. SAE Paper 2002-01-1029. Society of Automotive Engineers, Warren- dale, PA. Mathur, G.D. 2003. Psychrometric analysis of the effect of laminate evapo- rator's tank position. SAE Paper 2003-01-0528. Society of Automotive Engineers, Warrendale, PA. Mathur, G.D. 2004a. Experimental investigation to determine accumulation of lubricating oil in a single tank evaporator with tank at the top at dif- ferent compressor operating speeds. SAE Paper 2004-01-0213. Society of Automotive Engineers, Warrendale, PA. Mathur, G.D. 2005a. Influence of cowl surface temperature on air conditioning load. SAE Paper 2005-01-2058. Society of Automotive Engineers, Warrendale, PA. Mathur, G.D. 2005b. Performance enhancement of mobile air conditioning system with improved air management for front end. SAE Paper 2005- 01-1512. Society of Automotive Engineers, Warrendale, PA. Mathur, G.D. 2006. Experimental investigation to monitor vehicle cabin indoor air quality (IAQ) in the Detroit metropolitan area. SAE Paper 2006-01-0269. Society of Automotive Engineers, Warrendale, PA. Mathur, G.D. 2007a. Experimental investigation to monitor tailpipe emis- sions entering into vehicle cabin to improve indoor air quality (IAQ). SAE Paper 2007-01-0539. SAE Transactions, vol. 116-6. Mathur, G.D. 2007b. Monitoring build-up of carbon dioxide in automobile cabin to improve indoor air quality (IAQ) and safety. Vehicle Thermal Management Systems, Nottingham, UK, Paper 051. Mathur, G.D. 2008. Field tests to monitor build-up of carbon dioxide in vehi- cle cabin with AC system operating in recirculation mode for IAQ and safety. SAE Paper 2008-01-0829. Society of Automotive Engineers, Warrendale, PA. Mathur, G.D. 2009a. Measurement of carbon dioxide in vehicle cabin to monitor IAQ during winter season with HVAC operating in OSA mode. SAE Paper 2009-01-0542. Society of Automotive Engineers, Warren- dale, PA. Mathur, G.D. 2009b. Field monitoring of carbon dioxide in vehicle cabin to monitor indoor air quality and safety in foot and defrost modes. Vehicle Thermal Management Systems- VTMS-8, SAE Paper 2009-01-3080. Society of Automotive Engineers, Warrendale, PA. Mathur, G.D. 2009c. Experimental investigation with cross fluted double pipe suction line heat exchanger to enhance AC system performance. SAE Paper 2009-01-0970. SAE Transactions 1118-6. Society of Auto- motive Engineers, Warrendale, PA. Inc. ASHRAE, 2019 user. single for Licensed | {}
3ff26cd6-c201-47cf-9430-c5d491efe1c6 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Automobiles 11.17 Mathur, G.D. 2010a. Experimental investigation of AC system performance with HFO-1234yf as the working fluid. SAE Paper 2010-01-0041. Society of Automotive Engineers, Warrendale, PA. Mathur, G.D. 2010b. Experimental performance of a parallel flow condenser with HFO-1234yf as the working fluid. SAE Paper 2010-01-0047. Society of Automotive Engineers, Warrendale, PA. Mathur, G. 2011a. Enhancing AC system performance with a suction line heat exchanger with refrigerant HFO-1234yf. SAE Paper 2011-01-0133. Society of Automotive Engineers, Warrendale, PA. Mathur, G. 2011b. Experimental investigation of the performance of a lami- nate evaporator with HFO-1234yf as the working fluid. SAE International Journal of Materials and Manufacturing 4(1):1231-1243. Mathur, G. 2012. Two-phase flow boiling heat transfer coefficients and pres- sure gradients for HFO-1234yf. SAE Paper 2012-01-1047. Society of Automotive Engineers, Warrendale, PA. Mathur, G. 2013. Experimental measurements of condensation heat transfer coefficients for refrigerant HFO-1234yf. SAE International Journal of Passenger Cars-Mechanical Systems 6(2):1001-1012. Mathur, G. 2016a. Experimental determination of effectiveness of hydro- philic coating for evaporators. SAE International Journal of Materials and Manufacturing 9(2):261-267. Mathur, G. 2016b. Experimental investigation to determine influence of build-up of cabin carbon dioxide concentrations for occupant's fatigue. SAE Paper 2016-01-0254. Society of Automotive Engineers, Warren- dale, PA. Mathur, G. 2017a. Development of a model to predict build-up of cabin car- bon dioxide concentrations in automobiles for indoor air quality. SAE Paper 2017-01-0163. Society of Automotive Engineers, Warrendale, PA. Mathur, G. 2017b. Analysis of the effectiveness of evaporator's hydrophilic coating of cores recovered from humid and arid regions. SAE Interna- tional Journal of Passenger Cars-Mechanical Systems 10(1):111-120. Mathur, G. 2018a. Correlation for predicting two-phase flow boiling heat transfer coefficients for refrigerant HFO-1234yf. SAE Paper 2018-01- 0055. Society of Automotive Engineers, Warrendale, PA. Mathur, G. 2018b. Effect of cabin volume on build-up of cabin carbon diox- ide concentrations from occupant breathing in automobiles. SAE Paper 2018-01-0074. Society of Automotive Engineers, Warrendale, PA. Mathur, G., J. Hara, M. Iwasaki, and Y. Meguriya. 2012. Development of an innovative energy efficient compact cooling system "SLIM". SAE Paper 2012-01-1201. Society of Automotive Engineers, Warrendale, PA. Menken, J., M. Ricke, T. Weustenfeld, and J. Koehler. 2016. Simulative analysis of secondary loop automotive refrigeration systems operated with an HFC and carbon dioxide. SAE International Journal of Passenger Cars-Mechanical Systems 9(1):434-440. Meyer, J.J. 2008. R-1234yf system enhancements and comparison to R- 134a. Presented at SAE Alternative Refrigerant Symposium, Society of Automotive Engineers, Warrendale, PA. Meyer, J.J. 2009. Production solutions for utilization of both R-1234yf and R-134a in a single global platform. SAE Paper 2009-01-0172. Society of Automotive Engineers, Warrendale, PA. Minor. B. 2008. HFO-1234yf low GWP refrigerant for MAC applications. Presented at Mobile AC Climate Protection Partnership Meeting, U.S. Environmental Protection Agency, Washington, D.C. Monfared, B., R. Furberg, and B. Palm. 2014. Magnetic vs. vapor- compression household refrigerators: A preliminary comparative life cycle assessment. International Journal of Refrigeration 42:69-76. Morishita, M., T. Uchida, G. Mathur, T. Kato et al. 2018. Evaluation of thermal environment in vehicles for occupant comfort using equivalent temperature of thermal manikin during start-stop function with energy storage evaporators. SAE Paper 2018-01-0059. Society of Automotive Engineers, Warrendale, PA. NOAA. 2018. Trends in atmospheric carbon dioxide. National Oceanic and Atmospheric Association, Washington, D.C. www.esrl.noaa.gov/gmd /ccgg/trends/global.html Pearson, J.K. 2001. Improving air quality-Progress and challenges for the auto industry. Society of Automotive Engineers, Warrendale, PA. Rough, J., D. Bharatan, and L. Chaney. 2005. Predicting human thermal comfort in automobiles. Advanced Simulation Technologies Confer- ence, Graz, Austria. SAE. 2011. Motor vehicle heater test procedure. Standard J638. Society of Automotive Engineers, Warrendale, PA. SAE. 2011. Safety standards for motor vehicle refrigerant vapor compres- sions systems. Standard J639. Society of Automotive Engineers, War- rendale, PA. SAE. 2018. Taxonomy and definitions for terms related to on-road motor vehicle automated driving systems. Standard J3016_201806. Society of Automotive Engineers, Warrandale, PA. Spatz, M., and B. Minor. 2008. HFO-1234yf low GWP refrigerant update. Honeywell and DuPont joint collaboration. Presented at International Refrigeration and Air Conditioning Conference, Purdue University, West Lafayette, IN. Spatz, M., and B. Minor. 2009. Low GWP Refrigerant update: Honeywell/ DuPont joint collaboration. Presented at International Refrigeration and Air Conditioning Conference, Purdue University, West Lafayette, IN. Sato, T., K. Matsunaga, and S. Tanabe. 2016. Thermal comfort in vehicle equipped cold storage evaporator. JSAE 2016 Congress (Autumn) Tech- nical Paper Summaries, 584/589. Torregrosa-Jaime, B., J. Paya, J. Corberan, C. Malvicino et al. 2013. ICE project: mobile air-conditioning system based on magnetic refrigeration. SAE Paper 2013-01-0238. Society of Automotive Engineers, Warren- dale, PA. Uematsu, S., T. Uehara, T. Uchida, and G. Mathur. 2015. Experimental investigation of factors affecting odors generating from mobile AC sys- tems equipped with idling-time reduction systems. SAE International Journal ofPassenger Cars-Mechanical Systems 8(2):399-404. Wagner, J.R., V. Srinivasan, D.M. Dawson, and E. Marotta. 2003. Smart thermostat and coolant pump control for engine thermal management systems. SAE Paper 2003-01-0272. Society of Automotive Engineers, Warrendale, PA. Yanik, E., and S. Celik. 2018. Analysis of magnetic refrigeration designs with three different magnet array geometries. ASHRAE Transactions 124(1). Paper CH-18-002. BIBLIOGRAPHY Bhatti, M.S. 1997. A critical look at R-744 and R-134a for mobile air con- ditioning systems. SAE Paper 970527. Society of Automotive Engi- neers, Warrendale, PA. Bhatti, M.S. 1999. Evolution of automotive heating Riding in comfort: Part I. ASHRAE Journal 41(8):51-57. Bhatti, M.S. 1999. Evolution of automotive air conditioning Riding in comfort: Part II. ASHRAE Journal 41(9):44-50. DOT. 1972. Flammability of interior materials- Passenger cars, multipur- pose passenger vehicles, trucks, and buses. Federal Motor Vehicle Safety Standard (FMVSS) 302. U.S. Department of Transportation, National Highway Traffic Safety Administration, Washington, D.C. Giles, G.R., R.G. Hunt, and G.F. Stevenson. 1997. Air as a refrigerant for the 21st century. Proceedings of ASHRAE/NIST Refrigerants Confer- ence: Refrigerants for the 21st Century. Jones, B. W Q. He, J.M. Sipes, and E.A. McCullough. 1994. The transient nature of thermal loads generated by people. ASHRAE Transactions 100(2):432-438. Mathur, G.D. 1998. Heat transfer coefficients for propane (R-290), isobu- tane (R-600a), and 50/50 mixture of propane and isobutane. ASHRAE Transactions 104(2):1159-1172. Mathur, G.D. 2000. Carbon dioxide as an alternate refrigerant for automotive air conditioning systems. Paper AIAA-200-2858. American Institute of Aeronautics and Astronautics, Reston, VA. Mathur, G.D. 2000d. Hydrodynamic characteristics of propane (R-290), isobutane (R-600a), and 50/50 mixture of propane and isobutane. ASHRAE Transactions 106(2):571-582. Mathur, G.D. 2001. Simulating performance of a parallel flow condenser using hydrocarbons as the working fluids. SAE Paper 2001-01-1744. Society of Automotive Engineers, Warrendale, PA. Mathur, G.D. 2003b. Heat transfer coefficients and pressure gradients for refrigerant R-152a. Presented at Alternative Refrigerant Systems Symposium, Scottsdale, AZ. Society of Automotive Engineers, Warrendale, PA. Mathur, G.D. 2004b. Vehicle thermal management: Heat exchangers & climate control. Society of Automotive Engineers, Warrendale, PA. Mathur, G. 2014. Experimental measurements of stored energy in vehicle's cockpit module at high ambient and solar load conditions. SAE Paper 2014-01-0705. Society of Automotive Engineers, Warrendale, PA. Mathur, G. 2015. Experimental measurements of stored energy in vehicle's cockpit module at cold temperatures. SAE Paper 2015-01-0365. Society of Automotive Warrendale, PA. Engineers, Inc. ASHRAE, 2019 user. single for Licensed | {}
48d14eb2-fbc2-4784-9795-d11a33392b79 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 11.18 2019 ASHRAE Handbook-HVAC Applications (SI) Mathur, G.D., and S. Furuya. 1999c. A CO2 refrigerant system for vehicle air conditioning. Presented at Alternative Refrigerant Systems Symposium, Scottsdale, AZ. Society of Automotive Engineers, Warrendale, PA. Spatz, M. W. 2006. Ultra-low GWP refrigerant for mobile air conditioning applications. Presented at JSAE Automotive Air-Conditioning Confer- ence, Tokyo. Society of Automotive Engineers of Japan, Tokyo. Inc. ASHRAE, 2019 user single for Licensed Related Commercial Resources | {}
20e27559-ae9b-4e63-b24c-90fdb4992727 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 12 MASS TRANSIT ¦ Ventilation and Thermal Comfort ¦ 12.1 ¦ ¦ --- ¦ --- ¦ ¦ Thermal Load Analysis ¦ 12.2 ¦ ¦ Bus Air Conditioning. ¦ 12.2 ¦ ¦ Rail Car Air Conditioning ¦ 12.5 ¦ ¦ Fixed-Guideway Vehicle Air Conditioning ¦ 12.7 ¦ T HIS chapter describes air-conditioning and heating systems for buses, rail cars, and fixed-guideway vehicles that transport large numbers of people, often in crowded conditions. Air-conditioning systems for these vehicles generally use commercial components, but are packaged specifically for each application, often integral with the styling. Mass, envelope, power consumption, maintainabil- ity, and reliability are important factors. Power sources may be elec- trical (ac or dc), engine crankshaft, compressed air, or hydraulic. These sources are often limited, variable, and interruptible. Charac- teristics specific to each application are discussed in the following sections. Design aspects common to all mass-transit HVAC systems include passenger comfort (ventilation, thermal comfort, air quality, expectation) and thermal load analysis (passenger dynamic meta- bolic rate, solar loading, infiltration, multiple climates, vehicle velocity, and, in urban applications, rapid interior load change). 1. VENTILA TION AND THERMAL COMFORT The requirements of ASHRAE Standards 55 and 62.1 apply for transportation applications, with special considerations, because passengers in transit have different perceptions and expectations than typical building occupants. These considerations involve length of occupancy, occupancy turnover, infiltration, outdoor air quality, frequency and duration of door openings, personal preference, inte- rior contamination sources such as smoking, and exterior contami- nation sources such as engine exhaust. Historically, in nonsmoking air-conditioning and heating applica- tions, outdoor air has been supplied to the vehicle interior by fans at 2.5 to 5 L/s per passenger at a predetermined nominal passenger loading. Nominal passenger load is based on the number of seats and may include a number of standees, up to the maximum number of standees possible if this type of loading is frequent. There are a few examples of no outdoor air being supplied by fans, but they are on short-duration trips such as people movers or urban buses with fre- quent door openings. Besides providing for survival, ventilation pro- vides odor and contamination control. The amount needed for survival is less than the latter. Contamination control from interior sources is a factor in building design, but is less of a factor in vehicle design because of the ratio of people to furnishings and the lack of interior processes such as copy machines. Exterior contamination, such as from tunnel fumes, can be a problem, however. Door open- ings, if frequent enough, provide some additional intermittent venti- lation, although this infiltration should be minimized for thermal comfort. Ventilation from doors may not be effective in controlling odors away from the doors. Fan-supplied outdoor air must be distrib- uted equally in the vehicle for effective ventilation. Symptoms of inadequate ventilation are odors noticeable to passengers initially entering an occupied vehicle or when moving from section to sec- tion. Passengers on board who are exposed to slowly increasing odor levels may not be aware of them. The preparation of this chapter is assigned to TC 9.3, Transportation Air Conditioning. Based on ASHRAE research, ASHRAE Standard 161 established a ventilation rate for aircraft passengers at 3.5 L/s per passenger. This rate was based in part on the consideration that not all spaces in the enclosed area achieve 100% ventilation effectiveness. The min- imum effective ventilation rate for several crowded but larger- volume spaces, as defined in ASHRAE Standard 62. 1, is 2.5 L/s per person. It is recommended that ground mass transit applications use 3.5 L/s of outdoor air per passenger for most transit applications. Emergency ventilation, such as windows or exits that can be opened or battery-powered ventilators, should be provided in case other systems fail. For example, a power interruption or a propulsion system failure may strand passengers in a situation where exit is not possible. Emergency situations include overtemperature, oxygen depletion, smoke, or toxic fumes. Operator-controlled dampers are now provided on some vehicles to close off fresh air when smoke or toxic fumes are encountered in tunnels. The duration that the damp- ers remain closed must be limited to avoid oxygen depletion, even though the air-conditioning system remains in operation. Fresh-air supply alone or battery-powered ventilators will not prevent over- temperatures when a full passenger load is present and/or a solar load exists in combination with high ambient temperature. Each emergency situation requires an independent solution. The nature of the transit service may be roughly categorized by average journey time per passenger and interval between station stops, and this service type affects the necessary interior conditions in the vehicle. For example, a commuter rail or intercity bus passen- ger may have a journey time of an hour or more, with few stops; pas- sengers may remove heavy outer clothing before being seated. In contrast, a subway or transit urban bus rider typically does not remove heavy clothing during a 10 min ride. Clothing and the envi- ronment from which passengers come, including how long they were exposed to those conditions and what they were doing (e.g., waiting for the train outdoors in winter), are important factors in transit comfort. At the opposite extreme, many subway stations are not climate controlled, and often reach dry-bulb temperatures over 38°C in the summer. Thus, when boarding a climate-controlled vehi- cle, these passengers immediately perceive a significant in-crease in comfort. However, a passenger adjusts to a new environment in about 10 to 20 min; after that, the traditional comfort indices begin to apply, and the same interior conditions that were perceived as comfortable may now be perceived as less than comfortable. Before stabilization, a passenger may prefer higher-velocity air or cooler or warmer temperatures, depending to some extent on clothing. At the same time, other passengers may already have stabilized and have completely different comfort control desires. Therefore, the transit system designer is presented with a number of unusual requirements in providing comfort for all. Jones et al. (1994) evaluated the heat load imposed by people under transient weather and activity conditions as opposed to tra- ditional steady-state metabolic rates. An application program, TRANMOD, was developed that allows a designer to predict the ther- mal loads imposed by passengers (Jones and He 1993). Variables are activity, clothing, wet- and dry-bulb temperatures, and precipitation. 12.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
61e5a71d-b911-4765-9fd5-53fc2d8e3076 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 12.2 2019 ASHRAE Handbook-HVAC Applications (SI) European Committee for Standardization (CEN) Standard EN 13129-1 provides guidance in the area of railroad passenger com- fort. Although this standard does not apply to countries outside the CEN, the information is valuable and may not be readily available elsewhere. 2. THERMAL LOAD ANALYSIS Cooling Design Considerations Thermal load analysis for transit applications differs from station- ary, building-based systems because vehicle orientation and occu- pant density change regularly on street-level and subway vehicles and, to a lesser degree, on commuter and long-distance transporta- tion. Summer operation is particularly affected because cooling load is affected more by solar and passenger heat gain than by outdoor air conditions. ASHRAE Standard 55 design parameters for occupant comfort may not always apply. Vehicle construction does not allow the low thermal conductivity levels of buildings, and fenestration material must have safety features not necessary in other applica- tions. For these reasons, thermal loads must be calculated differently. Because main-line passenger rail cars and buses must operate in var- ious parts of the country, the air conditioning must be designed to handle the national seasonal extreme design days. Commuter and local transit vehicles operate in a small geographical area, so only local design ambient conditions need be considered. The following cooling load components should be considered: · Ambient air conditions for locations in North America and world- wide are given in Chapter 14 of the 2017 ASHRAE Handbook- - Fundamentals. For vehicles operating in an urban area, the heat island effect should be considered if the Handbook design values are derived from remote reporting stations. For subway car oper- ation, tunnel temperatures should be considered. In humid regions, consider the wet-bulb temperature coincident with dry- bulb temperature relative to fresh-air loads. · For vehicle interior comfort conditions, consult Figure 5 in Chap- ter 9 of the 2017 ASHRAE Handbook-Fundamentals. Total heat gain from passengers depends on passenger activity before board- ing the vehicle, waiting time, journey time, and whether they are standing or seated during the journey. Representative values are given in Table 1 in Chapter 18 of the 2017 ASHRAE Handbook Fundamentals. · Ventilation air loads should be calculated using the method in Chapter 18 of the 2017 ASHRAE Handbook-Fundamentals, in the section on Infiltration and Moisture Migration Heat Gains. Air leakage and air entering during door dwell time should be taken into account. · Interior heat includes that produced by the evaporator fan motor, indoor lighting, and electrical controls. · The vehicle 's conductivity, in W/K, should be provided by the vehicle designers. For outdoor skin temperature guidance, use the values in Table 1 in Chapter 29 ofthe 1997 ASHRAE Handbook- - Fundamentals; however, consider that air over a vehicle in motion reduces these temperatures The car design dry bulb should be used as the interior temperature. · The instantaneous solar gain through the glazing should be calcu- lated using summer midafternoon data listed in Chapter 29 of the 1997 ASHRAE Handbook-Fundamentals, and the glass shading coefficient. The glass shading coefficient must be obtained from the window supplier. Adjustments for frequent change in vehicle direction or intermittent solar exposure may be justified. Addi- tional information is shown in Chapter 15 of the 2017 ASHRAE Handbook-Fundamentals The summer cooling analysis should be completed for different times of the day and different passenger densities to verify a reliable result. Cooling equipment capacity should consider fouling and eventual deterioration of heat transfer surfaces. Heating Design Considerations Winter outdoor design conditions can be taken from Chapter 14 of the 2017 ASHRAE Handbook-Fundamentals. Interior tempera- tures can be taken from Figure 5 in Chapter 9 of the 2017 ASHRAE Handbook-Fundamentals. During winter, conductivity is the major heat loss. The heat required to temper ventilation air and to counter- act infiltration through the body and during door openings must also be considered. Other Considerations Harsh environments and the incursion of dirt and dust inhibit the efficiency of HV AC units. Specifications should include precise maintenance instructions to avoid capacity loss and compromised passenger comfort. 3. BUS AIR CONDITIONING In general, bus air-conditioning systems can be classified as inter- urban, urban, or small/shuttle bus systems. Bus air-conditioning design differs from other air-conditioning applications because of climatic conditions in which the bus operates, equipment size limita- tions, vehicle engine, electrical generator, and compressor rev/s. Pro- viding a comfortable climate inside a bus passenger compartment is challenging because the occupancy rate per unit of surface and air recirculation volume is high, glazed area is very large, and outdoor conditions are highly variable. Factors such as high ambient tem- peratures, dust, rain, snow, road shocks, hail, and sleet should be con- sidered in the design. Units should operate satisfactorily in ambient conditions from -30 to 50 C. Ambient air quality must also be considered. Air intakes are usually subjected to thermal contamination from road surfaces, con- denser air recirculation, or vehicle engine radiator air discharge. Vehicle motion also introduces pressure variables that affect con- denser fan performance. In addition, engine speed governs com- pressor speed, which affects compressor capacity. R-134a is the current refrigerant of choice, but some units operate with refriger- ants such as R-22 (pre-2010 production) and R-407C. Bus air conditioners are initially performance-tested as units in a climate-controlled test cell. Performance tests encompass unit oper- ation at different compressor speeds to make sure the compressor per- formance parameters [e.g., unit operation at maximum and minimum ambient conditions, thermostatic expansion valve (TXV) sizing, oil return, and vibration/shock] are within boundaries. In addition, indi- vidual components should be qualified before use. Larger test cells that can hold a bus are commonly used to verify installed unit perfor- mance. These tests are to measure the amount of time required to reduce the vehicle's interior temperature to a specified value, and they vary in performance and time requirements. Some commonly accepted tests include the Houston pulldown (extreme heat or perfor- mance when using higher-pressure refrigerant gas such as R-407C), modified pulldown (mild to hot climates with R-134a or equivalent), white book pulldown (mild to hot climates), and the profile test (mild to hot climates, 35 and 46.1 °C ambient). All these tests are described in American Public Transportation Association (APTA) standard bus procurement and recommended practices for transit bus HV AC sys- tem instrumentation and performance testing. Reliability and ease of maintenance are also important design considerations. All parts requiring service or regular maintenance should be readily accessible, and repairs should be achievable without removing any additional components and within a minimum time. Heat Load The main parameters that must be considered in bus air- conditioning system design include Inc. ASHRAE, 2019 user. single for Licensed | {}
3ea2547b-31d0-48a7-8ad0-4302e1b9fd5f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Mass Transit 12.3 · Occupancy data (number of passengers, distance traveled, dis- tance traveled between stops, typical permanence time) · Dimensions and optical properties of glass · Outdoor weather conditions (temperature, relative humidity, solar radiation) · Dimensions and thermal properties of materials in bus body · Indoor design conditions (temperature, humidity, air velocity) · Power and torque limitations of bus engine The heating or cooling load in a passenger bus may be estimated by summing the heat flux from the following loads: · Solid walls (side panels, roof, floor) · Glass (side, front, and rear windows) · Passengers · Engine and ventilation (difference in enthalpy between outdoor and indoor air) · Evaporator fan motor Extreme loads for both summer and winter should be calculated. The cooling load is the most difficult load to handle; the heating load is normally handled by heat recovered from the engine, exter- nal heater, or electrical heat elements. An exception is that an idling engine provides marginal heat in very cold climates. Andre et al. (1994) and Jones and He (1993) describe computational models for calculating the heat load in vehicles, as well as for simulating the thermal behavior of the passenger compartment. The following conditions can be assumed for calculating the summer heat load in an interurban vehicle similar to that shown in Figure 1: · Capacity of 50 passengers · Insulation thickness of 25 to 40 mm · Double-pane tinted windows · Outdoor air intake of 190 L/s · Road speed of 100 km/h · Indoor design temperatures of 16 to 27°C and 50% rh · Ambient temperatures for location as listed in Chapter 14 of the 2017 ASHRAE Handbook-Fundamentals Loads from 12 to 35 kW are calculated, depending on outdoor weather conditions and geographic location. The typical distribu- tion of the different heat loads during a summer day at 40 north latitude is shown in Figure 2. ![image](/image/placeholder) RADIATION CONVECTION AND CONDUCTION Fig. 1 Distribution of Heat Load (Summer) Air Distribution Air-conditioning units are configured to deliver air through ducts to outlets above the windows and to the middle aisle or to act as free- blow units. In the case of free-blow units, louvers guide the air dis- tribution inside the bus. Interurban Buses These buses are designed to accommodate up to 56 passengers. The air-conditioning system is usually designed to handle extreme conditions. Interurban buses produced in North America are likely to have the evaporator and heater located under the passenger com- partment floor. A four- or six-cylinder reciprocating compressor, in which some cylinders are equipped with unloaders, is popular. Some interurban buses have a separate engine-driven compressor, prefer- ably scroll, to give more constant system performance. Figure 3 shows a typical air-conditioning arrangement for an interurban bus. Urban Buses Urban bus heating and cooling loads are greater than those of the interurban bus. A city bus may seat up to 50 passengers and carry a "crush load" of standing passengers. The fresh-air load is greater because of the number of door openings and the infiltration around Chart Type: bar GLASS OCCUPANTS VENTILATION WITH OUTSIDE AIR INTERIOR OBJECTS WALLS ENGINE item_01 11kW 6kW 5kW 2kW 2kW 1kW SUMMER DAY CONDITIONS AT 40° N. LATITUDE Fig. 2 Typical Main Heat Fluxes in Bus ![image](/image/placeholder) PARCEL RACK EVAPORATOR WITH THERMOSTAT DRIVER EVAPORATOR CONDENSER MAIN EVAPORATOR ROADSIDE PARCEL RACK EVAPORATOR COMPRESSOR MAIN EVAPORATOR CURBSIDE Fig. 3 Typical Arrangement of Air-Conditioning in Interurban Bus Inc. ASHRAE, 2019 user. single for Licensed | {}
e0848df6-b3d5-41dc-8abe-49d514ccb071 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 12.4 doors. Cooling capacity required for a typical 50-seat urban bus is from 20 to 35 kW. The buses are usually equipped with a roof- or rear-mounted unit, as shown in Figure 4. One or two compressors are usually belt- or shaft-driven from the propulsion engine. Capacity control is very important, because the compressor may turn more quickly than necessary at high engine speeds. Therefore, capacity control must compensate for not only the thermal load but also the engine-induced load. Cylinder unloaders are the primary means of capacity control, although evaporator pressure regulators have been used with non-unloading compressors, as shown in Figure 4. This configuration was used on buses produced between 1975 and 1995. The heater is located just downstream of the evaporator. Hot coolant from the engine-cooling system provides sufficient heat for most operations; however, additional sources may be required in colder climates for longer idling durations. Additional floor heaters may also be required to reduce the effects of stratification. Condi- tioned air is delivered through overhead combination light fixture/ diffuser ducts (see Figure 5). Low-profile, self-contained, rooftop-mounted units are used for urban and interurban buses. These units contain the entire air- conditioning system except for the compressor, which is shaft- or belt-driven from the bus engine (see Figure 6). Because of increased air pollution and other environmental issues (e.g., noise, fuel consumption, unnecessary engine wear), using tra- ditional engine-driven compressors for interurban, urban, or school bus or motor home air comfort systems is a great disadvantage, especially for parked vehicles. In response to these issues, most ![image](/image/placeholder) LEVEL INDICATORS LIQUID SOLENOID VALVES FILTER-DRIERS CONDENSER FANS HIGH/LOW SWITCHES CONDENSER EVAPORATOR PORTS HIGH-SIDE PORTS BACK- PRESSURE REGULATORS LOW-SIDE Pu PORTS EXPANSION VALVES AUTOMOTIVE COMPRESSORS EVAPORATOR DUAL INDEPENDENT (HEATER NOT SHOWN) REFRIGERATION CIRCUITS Fig. 4 Typical Mounting Location of Urban Bus Air-Conditioning Equipment ![image](/image/placeholder) CONDENSER AIR INTAKE DUCTED SUPPLY CONDENSER AIR FANS FRESH AIR (0000 INTAKE REFRIGERANT LINES COMPRESSOR Fig. 5 Typical Mounting Location of Urban Bus Air- Conditioning Equipment with Single Compressor 2019 ASHRAE Handbook- - HVAC Applications (SI) modern and efficient buses use unitized electric packaged air- conditioning (UEPAC) units, as shown in Figures 7 and 8. UEPACs have a self-contained, lightweight, integrated, modular design in- corporating evaporators, condensers, valves, liquid receiver, filter- drier, electric heater elements, automatic climate controls, and scroll compressors. Electric power is supplied to the UEPAC system from onboard sources for hybrid electric and fuel-cell buses, or by a main-engine-driven generator on more traditional fuel or hybrid applications without an accessory power option. These systems enable use of shore (wayside) power while parked, eliminating idling where power is available. Small or Shuttle Buses For small or shuttle buses such as those typically operating around airports or for schools, the evaporator is usually mounted in the rear and the condenser on the side or the roof of the bus. The evaporator unit is typically a free-blow unit. Refrigerant Piping See Chapters 1 and 8 of the 2018 ASHRAE Handbook- Refrig- eration for standard refrigerant piping practices. All components in the bus air-conditioning system are interconnected by copper tubing ![image](/image/placeholder) EVAPORATOR COILS CONDENSER HEATER COILS FANS FRESH AIR INTAKE 취 BLOWER ASSEMBLIES COMPRESSOR Fig. 6 Typical Mounting Location of Roof-Mounted Urban Bus Air-Conditioning Equipment with Single Compressor ![image](/image/placeholder) EVAPORATOR CONDENSER CONDENSER BLOWER INTAKE CONDENSER FANS DUCTED SUPPLY AND EXHAUST AIR HERMETIC SCROLL COMPRESSOR RETURN FRESH AIR INTAKE AIR HEATER LINES POWER CABLES GENERATOR Fig. 7 Typical Mounting Location of Urban Bus Fully Electric Rear-Mounted Air-Conditioning Equipment with ac Generator Inc. ASHRAE, 2019 user. single for Licensed | {}
fc9ee902-bf9b-41ae-a73e-ee3d23bf756a | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Mass Transit 12.5 ![image](/image/placeholder) CONDENSER FANS AND HERMETIC SCROLL COMPRESSORS EXHAUST CONDENSER HEATER COILS SECTION EVAPORATOR COILS FRESH AIR INTAKE POWER DISTRIBUTION BOX BLOWER ASSEMBLIES GENERATOR EXTERNAL "SHORE" POWER CONNECTION Fig. 8 Typical Mounting Location of Urban Bus Fully Electric Roof-Mounted Air Conditioning Equipment with ac Generator or refrigerant hose. When using copper tubing, care should be taken to analyze the effect of vibration on the tubing. Vibrational effects can be minimized by using vibration absorbers or other shock-cush- ioning devices. When using refrigerant hose, properties such as moisture ingression, effusion, maximum operating temperature, and burst pressure need to be taken into account. The refrigerant hose chosen should have the minimum amount of wax extractables on interaction with oil and the refrigerant. Shock and Vibration Most transport air-conditioning manufacturers design compo- nents for shock loading and vibrational inputs. Vibration elimina- tors, flexible lines, and other shock-cushioning devices interconnect the various air-conditioning components. The vibration characteris- tics of each component are different; in addition, the evaporator and the condenser must undergo individual vibration and shake tests. The input levels for the shake test can be based on the worst road conditions that the bus will encounter. This input level will vary because of the mass of the unit and its mounting. System Safety Per the U.S. Department of Transportation, all buses with air- conditioning systems operating in North America should conform to Federal Motor Vehicle Safety Standard (FMVSS) 302 for flam- mability standards. In addition, all evaporator units inside the vehi- cle should be mounted away from the head impact zone, as specified by FMVSS 222. Controls Most buses have a simple driver control to select air condition- ing, heating, or automatic operation (air conditioning, heating, and reheat). In both modes, a thermal sensing element controls these systems with on/off circuitry and actuators. Many systems use solid-state control modules to interpret the bus interior and outdoor ambient temperatures and to generate signals to operate full or par- tial cooling, reheat, or heating functions. These systems use therm- istor temperature sensors, which are usually more stable and reliable than electromechanical controls. Control systems for urban buses can also include an outdoor-air ventilation cycle. The percent- age of fresh-air intake during the ventilation cycle can vary based on individual requirements. 4. RAIL CAR AIR CONDITIONING Passenger rail car air-conditioning systems are generally electro- mechanical, direct-expansion units. R-22, a hydrochlorofluorocar- bon (HCFC), has been the refrigerant most commonly used since the phase-out for R-12. R-134a, a medium-pressure refrigerant, has been used as a retrofit refrigerant in North America on systems orig- inally designed to operate with R-12, and is commonly used in Europe for new equipment, mainly variable-speed screw compres- sors that are competitive in mass to R-22 reciprocating compressors. Most equipment placed in service before the January 1, 2010, ban on manufacturing new R-22 equipment has used R-407C as the refrigerant. R-410A has been used in some equipment; however, it can only be used in relatively mild climates because the condensing temperatures found in transit applications may approach the refrig- erant's critical point. In 2009, the U.S. Environmental Protection Agency (EPA) added R-438A to its significant new alternatives pol- icy (SNAP) list of approved refrigerants for motor vehicle air con- ditioning use. Electronic, automatic controls are common, with a trend toward microprocessor control with increasing capability for fault monitor- ing and logging. Electric heating elements in the air-conditioning unit or supply duct temper outdoor air brought in for ventilation and are also used to control humidity by reheating the conditioned sup- ply air during cooling partial-load conditions. Air-cycle technology has been tested for passenger rail car air conditioning in Germany (Giles et al. 1997); however, issues of greater mass, higher cost, and low efficiency need to be addressed before it is widely accepted. Vehicle Types Main-line intercity passenger rail service generally operates single and multilevel cars hauled by a locomotive. Locomotive- driven alternators or solid-state inverters distribute power via an intercar cable power bus to air-conditioning equipment in each car. A typical rail car has a control package and two air-conditioning systems. The units are usually either split, with the compressor/ condenser units located in the car undercarriage area and the evaporator-blower portion mounted in the ceiling area, or self- contained packages mounted in interior equipment rooms. Under- floor and roof-mounted package units are less common in intercity cars. Subway and elevated rapid-transit cars usually operate on a third-rail dc power supply. In the past, the air-conditioning system motors were commonly powered directly from the third-rail dc sup- ply voltage. Most new equipment operates from three-phase ac power provided by a solid-state inverter. The inverter may be either an independent system or a component of the HVAC system. Split air-conditioning systems are common, with evaporators in the inte- rior ceiling area and underfloor-mounted condensing sections, although unitary package units mounted on the roof or under the floor are increasingly common. Commuter cars used to provide passenger service from the sub- urbs into and around large cities are similar in size to main-line cars. Air-conditioning equipment generally consists of two evaporator- heater fan units mounted above the ceiling with a common or two separate underfloor-mounted compressor-condenser unit(s) and a control package, or self-contained packaged units mounted on the roof. These cars may be locomotive hauled, with air-conditioning arrangements similar to main-line intercity cars, but they are often self propelled by high-voltage direct-current (dc) or alternating- current (ac) power supplied from an overhead catenary or from a dc- supplied third-rail system. On such cars, the air conditioning may operate on ac or dc power. Self-propelled diesel-driven vehicles that use onboard-generated power for the air-conditioning systems still operate in a few areas. Inc. ASHRAE, 2019 user. single for Licensed | {}
24beedc9-17e2-4106-8e95-c84ea98da329 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 12.6 2019 ASHRAE Handbook-HVAC Applications (SI) ![image](/image/placeholder) ELECTRICAL SWITCHBOARD FRESH AIR BLOWER FRESH AIR FILTER BOX FRESH AIR FILTER EVAPORATOR ELECTRIC HEATER ELECTRIC MOTOR CONDENSER FANS BLOWERS ELECTRIC HEATER EVAPORATOR COMPRESSOR CONDENSER UNIT Fig. 9 Typical Light Rail Vehicle with Roof-Mounted HVAC System Streetcars and light-rail vehicles usually run on ac or dc power transmitted via an overhead catenary wire, and have air-conditioning equipment similar to rapid-transit cars. Roof-mounted packages are used more often than undercar or split systems. This is largely because of the lack of undercar space. Figure 9 shows a typical con- figuration for these vehicles. Equipment Design Considerations Design considerations unique to transit HVAC equipment include the characteristics of the available power supply, mass lim- its, type of vehicle, and vehicle service parameters. Thus, ac-pow- ered, semihermetic or hermetic compressors, which are lighter than open machines with dc motor drives, are a common choice. How- ever, each car design must be examined in this respect because dc/ ac inverters may increase not only the total mass, but also the total power draw, because of conversion losses. Other concerns in equipment selection include the space re- quired, location, accessibility, reliability, and maintainability. Inte- rior and exterior equipment noise levels must be considered both during the early stages of design and later, when the equipment is coordinated with the car builder's ductwork and grilles. Compressors. Reciprocating and vane compressors are com- monly used, although scroll compressors are becoming increasingly common. The scroll compressor is inherently more tolerant of flooded starts and liquid slugging common in the rail application than any other type of positive-displacement compressor. The low clearance volume ofthe scroll compressor allows it to operate at high discharge pressure more effectively than reciprocating compressors. Lower mass and less vibration and noise are benefits, as well. Power Supply Characteristics. Vehicles that draw their power from a stationary supply, such as a third rail or overhead catenary wire, are subject to frequent power interruptions as the train passes through gaps in the third rail or phase breaks in the overhead. These interruptions cause the HVAC equipment to shut down inde- pendently of the control system, and the design must take into account these losses of power and the subsequent need to restart the equipment. Vehicles that generate electrical power from an onboard source are less affected by power interruptions, although their capac- ity is limited. In either case, HVAC system control design must be coordinated with the vehicle's power supply and distribution system to avoid overloading vehicle systems during both steady-state and start-up (in-rush current) conditions. Additionally, it is desirable to prevent the vehicle's power supply from intentionally removing power from the HVAC equipment without an orderly shutdown sequence (including a pump-down cycle, if necessary). Configuration and Space Constraints. Space underneath and inside a rail car is at a premium. Components are usually built to fit the configuration of the available space. Overall car height, roof profile, ceiling cavity, and wayside clearance restrictions often determine the shape and size of equipment. Special Environmental Considerations. Dirt and corrosion constitute an important design factor, especially if the equipment is beneath the car floor, where it is subject to extremes of weather and severe dirt conditions. For this reason, corrosion-resistant materials and coatings must be selected. Aluminum has not proved durable in exterior exposed applications; the sandblasting effect tends to degrade any surface treatment on it. Because dirt pickup cannot be avoided, the equipment must be designed for quick and easy clean- ing; access doors should be provided, and evaporator and condenser fin spacing is usually limited to 2.5 to 3.2 mm. Closer spacing causes more rapid dirt build-up and higher cleaning costs. Dirt and severe environmental conditions must also be considered in select- ing motors and controls. Maintenance Provisions. Railroad HVAC equipment is sub- jected to mechanical shock and vibration during operation, is fre- quently required to operate under conditions of elevated condensing temperature and pressure, and is subjected to frequent on/off cycling because of power supply interruptions and other conditions that are not typical for a stationary application. As a consequence, the rail HV AC system 's components are more highly stressed than equivalent components in a stationary system, and thus require more frequent maintenance and servicing. Because a passenger rail car with sealed windows and a well-insulated structure becomes almost unusable if the air conditioning fails, high reliability is important. Equipment design needs to consider the ease of routine service and time needed to diagnose and repair the system. The con- trol equipment thus often incorporates monitoring and diagnostic capabilities to allow quick diagnosis and correction of a failure. However, many trains are designed with several individual vehicles permanently coupled together, in which case the failure of a single HVAC unit causes multiple cars to become unavailable for service while the HVAC system is diagnosed and repaired. The time to diagnose and repair a system varies. Railroads, by their nature, are schedule driven, and varying, unknown repair time is incompatible with the need to provide scheduled service. Therefore, many users are moving away from fully on-car-serviceable air conditioners and toward modular, self-contained units with hermetically sealed re- frigerant systems. These units are designed for rapid removal and replacement to allow the vehicle to return to service in a short, pre- dictable time. The faulty HVAC equipment is diagnosed and re- paired off-car in a dedicated air-conditioning service area. Safety. Security of the air-conditioning equipment attachment to the vehicle must be considered, especially on equipment located beneath the car. Vibration isolators and supports should be designed to safely retain the equipment on the vehicle, even if the vibration isolators or fasteners fail completely. A piece of equipment that dan- gles or drops off could cause a train derailment. All belt drives and other rotating equipment must be safety guarded. High-voltage con- trols and equipment must be labeled by approved warning signs. Pressure vessels and coils must meet ASME test specifications for protection of passengers and maintenance personnel. Materials selection criteria include low flammability, low toxicity, and low smoke emission. Special Design Considerations. The design, location, and in- stallation of air-cooled condenser sections must allow for the possi- bility ofhot condenser discharge air recirculation into the condenser Inc. ASHRAE, 2019 user. single for Licensed | {}
facee1f2-af86-400b-a5c7-266978e05fa9 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Mass Transit 12.7 inlet (in the case of split systems), or into the outdoor air intakes (in the case of roof-mounted unitary systems), as well as hot condenser discharge from trains on adjacent tracks that may occur at passenger loading platforms or in tunnels. To prevent a total system shutdown because ofhigh discharge pressure, a capacity reduction control de- vice is typically used to reduce the cooling capacity before system pressure reaches the high-pressure safety switch setting, thus tem- porarily reducing discharge pressure. Even with coordination between the HVAC controls and the vehicle's power supply or distribution system, abrupt shutdown of the refrigeration system caused by power loss is common. The typ- ical split-system arrangement places the compressor at or near the low point in the system. The combination of these factors results in undesired migration of refrigerant to the compressor during the off cycle. To reduce the likelihood of flooded compressor starts, using a suction line accumulator and crankcase heater is recommended. Other Requirements Most cars are equipped with both overhead and floor heat, typi- cally provided by electric resistance elements. The control design commonly uses overhead heat to raise the temperature of the recir- culated and ventilation air mixture to slightly above the car design temperature, while floor heat offsets heat loss through the car body. This arrangement is intended to limit stratification in the passenger compartment by promoting buoyant, convective air circulation. Times of maximum occupancy, outdoor ambient, and solar gain must be ascertained. The peak cooling load on urban transit cars usually coincides with the evening rush hour, and the peak load on intercity rail cars occurs in the midafternoon. Heating capacity for the car depends on body construction, car size, and the design area-averaged relative wind-vehicle velocity. In some instances, minimum car warm-up time may be the governing factor. On long-distance trains, the toilets, galley, and lounges often have exhaust fans. Ventilation airflow must exceed forced exhaust air rates sufficiently to maintain positive car pressure. Ventilation air pressurizes the car and reduces infiltration. Air Distribution and Ventilation The most common air distribution system is a centerline supply duct running the length of the car between the ceiling and the roof. Air outlets are usually ceiling-mounted linear slot air diffusers. Lou- vered or egg crate recirculation grilles are positioned in the ceiling beneath the evaporator units. The main supply duct must be insu- lated from the ceiling cavity to prevent thermal gain/loss and con- densation. Taking ventilation air from both sides of the roof line helps overcome the effect of wind. Adequate snow and rain louvers and, in some cases, internal baffles, must be installed on the outdoor air intakes. Separate outdoor air filters are usually combined with either a return or mixed-air filter. Disposable media or permanent, cleanable air filters are used and are usually serviced every month. Some long-haul cars, such as sleeper cars, require a network of delivered-air and return ducts. Duct design should consider noise and static pressure losses. Piping Design Standard refrigerant piping practice is followed. Pipe joints should be accessible for inspection and, on split systems, not con- cealed in car walls. Evacuation, leak testing, and dehydration must be completed successfully after installation and before charging. Piping should be supported adequately and installed without traps that could retard the flow of lubricant back to the compressor. Pipe sizing and arrangement should be in accordance with Chapter 1 of the 2018 ASHRAE Handbook-Refrigeration. Evacuation, dehydra- tion, and charging should be performed as described in Chapter 8 of that volume. Piping on packaged units should also conform to these recommendations. Control Requirements Rail HVAC control systems typically automatically transition between cooling and heating operation, based on interior and exte- rior dry-bulb temperature. The cooling and heating set points are generally different. This difference provides a control dead band to prevent the system from cycling directly between cooling and heat- ing, and accommodates passengers' seasonal clothing. System capacity is matched to part-load conditions with some combination of evaporator coil staging, evaporator fan speed control, compres- sor cylinder unloading, or variable-speed compressor control in cooling mode, and staging or duty cycling of heat in heating mode. The control system typically does not consider latent heat informa- tion in the control algorithm, although reheat is commonly used to increase the apparent interior sensible load as the interior dry-bulb temperature falls below the desired cooling set point, to maintain humidity removal. Unitary systems may use hot-gas bypass for this purpose rather than electric reheat. Ifthe interior dry-bulb tempera- ture falls below the desired cooling set point, even with capacity reduction and reheat, the refrigeration system will shut down and the HV AC system will provide ventilation only. Ifthe interior tem- perature drops to the heating set point, the system transitions to heating mode. Before the development of analog electronic or microprocessor control systems, this dry-bulb based control algo- rithm was implemented by banks of thermostats. This arrangement resulted in multiple, load-dependent interior set points as the sys- tem established quasi-equilibrium conditions within the dead band of each individual thermostat. When analog electronic controls were introduced in the early 1980s, they emulated this thermostat- based control algorithm, which is still often followed today in North America. Recently, several European and Asian HV AC man- ufacturers have introduced proportional-integral-derivative (PID) control systems, common in those markets for several years, to the North American market. Higher energy costs and greater environ- mental concern in Europe and Asia have led some manufacturers to include energy conservation algorithms in controls intended for use in those markets. The availability of robust, low-cost humidity sensors may lead to the use of latent heat information in control algorithms. A pumpdown cycle and low-ambient lockout are recommended on split systems to protect the compressor from damage caused by liquid flooding the compressor and subsequent flooded starts. In addition, the compressor may be fitted with a crankcase heater that is energized during the compressor off cycle. 5. FIXED-GUIDEWAY VEHICLE AIR CONDITIONING Fixed-guideway (FGW) systems, commonly called people mov- ers, can be monorails or rubber-tired cars running on an elevated or grade-level guideway, as seen at airports and in urban areas. The guideway directs and steers the vehicle and provides electrical power to operate the car's traction motors (in some cases, the vehi- cle is propelled by a metal cable, driven by a motor mounted at the end of the guideway), lighting, electronics, air conditioner, and heater. People movers are usually unstaffed and computer-con- trolled from a central point. Operations control determines vehicle speed, headway, and the length of time doors stay open, based on telemetry from individual cars or trains. Therefore, reliable and effective environmental control is essential. People movers are usually smaller than most other mass-transit vehicles, generally having spaces for 8 to 40 seated passengers and generous floor space for standing passengers. Under some condi- tions of passenger loading, a 12 m car can accommodate 100 pas- sengers. The wide range of passenger loading and solar exposure make it essential that the car's air conditioner be especially respon- sive to the amount of cooling required at a given moment. Inc. ASHRAE, 2019 user. single for Licensed | {}
b7ce5dee-68bb-4aac-92cc-2750f197d11a | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 12.8 2019 ASHRAE Handbook- - HVAC Applications (SI) System Types The HVAC for a people mover is usually one of three types: · Conventional undercar condensing unit and compressor unit (which includes control box) connected with refrigerant piping to an evaporator/blower unit mounted above the car ceiling · Packaged, roof-mounted unit having all components in one en- closure and mated to an air distribution system built into the car ceiling · Packaged, undercar-mounted unit mated to supply and return air ducts built into the car body Some vehicles are equipped with two systems, one at each end; each system provides one-half ofthe maximum cooling requirement. U.S. systems usually operate on the guideway's power supply of 460 to 600 v (ac), 60 Hz. Some newer systems with dc track power oper- ate on 240 V (ac), 60 Hz from an inverter. Figures 10 and 11 show some arrangements used with fixed-guideway people mover vehi- cles, although similar arrangements could also apply to rail. Refrigeration Components Because commercial electrical power is available, standard semihermetic reciprocating compressors and commercially avail- able fan motors and other components can be used. Compressors ![image](/image/placeholder) EVAPORATOR FILTER HEATER FRESH AIR INTAKE CONDENSER FAN CONDENSER BLOWER EVAPORATOR HEATER COMPRESSOR Fig. 10 Typical Small Fixed-Guideway Vehicle with Roof-Mounted HV AC System generally have one or two stages of unloaders, and/or hot-gas bypass is used to maintain cooling at low loads. Newer systems use scroll compressors with speed control, displacement control, or hot-gas bypass to control capacity. Condenser and evaporator coils are copper tube with copper or aluminum fins. Generally, flat fins are preferred for undercar condensers to make it simpler to clean the coils. Evaporator/blower sections must often be designed for the specific vehicle and fitted to its ceiling contours. Condensing units must also be arranged to fit in the limited space available and still ensure good airflow across the condenser coil. Because of the phaseout ofR-22, R-407C is commonly used to meet environmental standards (zero ozone depletion potential). Some existing R-22 sys- tems are being retrofitted with R-407C and R-422D. Heating Where heating must be provided, electric resistance heaters that operate on the guideway power supply are installed at the evaporator unit discharge. One or two stages of heat control are used, depend- ing on the size of the heaters. Controls A solid-state control is usually used to maintain interior condi- tions, although newer systems use programmable logic controller (PLC) microprocessor-based controllers. The cooling set point is typically between 23 and 24°C. For heating, the set point is 15.6 to 20°C. Some controls provide humidity control by using electric heat. Between the cooling and heating set points, blowers continue to operate on a ventilation cycle. On rare occasions, two-speed blower motors are used, switching to low speed for the heating cycle. Some controls have internal diagnostic capability and can signal the operations center when a cooling or heating malfunction occurs. Ventilation With overhead air-handling equipment, outdoor air is introduced into the return airstream at the evaporator entrance. Outdoor air is usually taken from a grilled or louvered opening in the end or side of the car. Depending on the configuration of components, fresh air is filtered separately or directed so that the return air filter can han- dle both airstreams. For undercar systems, a similar procedure is used, except air is introduced into the system through an intake in the undercar enclosure. In some cases, a separate fan is used to induce outdoor air into the system. The amount of mechanical outdoor air ventilation is usually expressed as litres per second per passenger on a full-load continu- ous basis. Passenger loading is not continuous at full load in this application, with the net result that more outdoor air is provided ![image](/image/placeholder) COMPRESSOR FAN EVAPORATORS, HEATERS EVAPORATOR, HEATER, BLOWERS FRESH AIR INTAKE ○ FRESH AIR FAN CONDENSER CONDENSERS A. ROOF-MOUNTED B. SPLIT SYSTEM Fig. 11 Example Monorail HVAC System Configurations Inc. ASHRAE, 2019 user. single for Licensed | {}
840a1b4e-8336-4051-949a-2ee6d10b7cfa | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Mass Transit 12.9 than indicated. The passengers may load and unload in groups, which causes additional air exchange with the outdoors. Frequent door openings, sometimes on both sides at once, allows additional natural ventilation. The effective outdoor air ventilation per passen- ger is a summation of all these factors. The amount of outdoor air introduced through the HVAC system varies. Some new vehicles have no mechanical outdoor air supply, whereas others provide up to 4.25 L/s per passenger. Lower values of mechanical ventilation, typically 1.4 to 2.4 L/s or less per passenger, are associated with travel times ofless than 2 min and large passenger turnover. Longer rides justify higher rates of mechanical ventilation. Green initiatives have caused designers to take a closer look at all aspects of energy savings. Some systems are now designed with variable outdoor air rates, which are automatically lowered under low passenger load conditions or extreme temperature loads. This approach yields lower system cooling capacities and saves energy. Air Distribution With overhead equipment, air is distributed through linear ceil- ing diffusers that are often constructed as a part of the overhead lighting fixtures. Undercar equipment usually makes use ofthe void spaces in the sidewalls and below fixed seating. In all cases, the spaces used for air supply must be adequately insulated to prevent condensation on surfaces and, in the case of voids below seating, to avoid cold seating surfaces. The supply air discharge from undercar systems can be from overhead diffusers through sidewall duct or a windowsill diffuser. Recirculation air from overhead equipment flows through ceiling-mounted grilles. For undercar systems, return air grilles are usually found in the door wells or beneath seats. Because of the vehicle's typical small size and low ceilings, care must be taken to design the air supply so that it does not blow directly on passengers' heads or shoulders. Because high flow rates are nec- essary to achieve capacities, diffuser design and placement are important. Some systems are designed so the air supply discharge hugs the vehicle's ceiling and walls to avoid drafts on passengers. Total air quantity and discharge temperature must be carefully cal- culated to provide passenger comfort. Interior noise levels are typi- cally 72 to 74 dBA for a stationary vehicle with doors shut. REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. Andre, J.C.S., E.Z.E. Conceicao, M.C.G. Silva, and D.X. Viegas. 1994. Inte- gral simulation of air conditioning in passenger buses. Fourth Interna- tional Conference on Air Distribution in Rooms (ROOMVENT '94). ASHRAE. 2013. Thermal environmental conditions for human occupancy. ANSI/ASHRAE Standard 55-2013. ASHRAE. 2013. Ventilation for acceptable indoor air quality. ANSI/ ASHRAE Standard 62.1-2013. ASHRAE. 2013. Air quality within commercial aircraft. ANSI/ASHRAE Standard 161-2013. CEN. 2002. Railway applications-Air conditioning for main line rolling stock-Part 1: Comfort parameters. Standard EN 13129.1-2002. Euro- pean Committee for Standardization, Brussels. DOT. 1977. School bus passenger seating and crash protection. Federal Motor Vehicle Safety Standard (FMVSS) 222. U.S. Department of Transportation, National Highway Traffic Safety Administration, Wash- ington, D.C. DOT. 1972. Flammability of interior materials- Passenger cars, multipur- pose passenger vehicles, trucks, and buses. Federal Motor Vehicle Safety Standard (FMVSS) 302. U.S. Department of Transportation, National Highway Traffic Safety Administration, Washington, D.C. Giles, G.R., R.G. Hunt, and G.F. Stevenson. 1997. Air as a refrigerant for the 21st century. Proceedings ASHRAE/NIST Refrigerants Conference: Refrigerants for the 21st Century. Jones, B. W., and Q. He. 1993. User manual: Transient human heat transfer model (includes application TRANMOD). Institute of Environmental Research, Kansas State University, Manhattan. Jones, B. W., Q. He, J.M. Sipes, and E.A. McCullough. 1994. The transient nature of thermal loads generated by people. ASHRAE Transactions 100 (2):432-438. U.S. EPA. 2013. Substitutes in motor vehicle air conditioners. U.S. Environ- mental Protection Agency, Washington, D.C. Available at www.epa.gov /ozone/snap/refrigerants/lists/tmvacs.html. BIBLIOGRAPHY APTA. 1999. Standard bus procurement guidelines for high floor diesel. American Public Transportation Association, Washington, D.C. APTA. 2000. Standard bus procurement guidelines for low floor diesel. American Public Transportation Association, Washington, D.C. Conceicao, E.Z.E., M.C.G. Silva, and D.X. Viegas. 1997. Airflow around a passenger seated in a bus. International Journal of HVAC&R Research (now Science and Technologyfor the Built Environment) 3(4):311-323. Conceicao, E.Z.E., M.C.G. Silva, and D.X. Viegas. 1997. Air quality inside the passenger compartment of a bus. Journal of Exposure Analysis & Environmental Epidemiology 7:521-534. DOT. 1994. Windshield defrosting and defogging systems- Passenger cars, multipurpose vehicles, trucks, and buses. Federal Motor Vehicle Safety Standard (FMVSS) 103. U.S. Department of Transportation, National Highway Traffic Safety Administration, Washington, D.C. Guan, Y., M.H. Hosni, B. W. Jones, and T.P. Gielda. 2003. Literature review of the advances in thermal comfort modeling. ASHRAE Transactions 109(2):908-916. Jones, B.W. 2002. The quality of air in the passenger cabin. Proceedings of Cabin Health 2002, International Air Transport Association, Geneva. Jones, B. W. 2002. Capabilities and limitations of thermal models for use in thermal comfort standards. Energy and Buildings 34(6):653-659. Silva, M.C.G., and D.X. Viegas. 1994. External flow field around an inter- city bus. Second International Conference on Experimental Fluid Mechanics. Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
8362ec4b-984d-4ff7-b908-48fb007da3ca | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 13 AIRCRAFT ¦ Design Conditions ¦ 13.1 ¦ ¦ --- ¦ --- ¦ ¦ Typical Flight ¦ 13.11 ¦ ¦ Air Quality ··· ¦ 13. 13 ¦ ¦ Regulations ¦ 13.14 ¦ E NVIRONMENTAL control system (ECS) is a generic term used in the aircraft industry for the systems and equipment asso- ciated with ventilation, heating, cooling, humidity/contamination control, and pressurization in the occupied compartments, cargo compartments, and electronic equipment bays. The term ECS often encompasses other functions such as windshield defog, airfoil anti- ice, oxygen systems, and other pneumatic demands. The regulatory or design requirements of these related functions are not covered in this chapter. 1. DESIGN CONDITIONS Design conditions for aircraft applications differ in several ways from other HVAC applications. Commercial transport aircraft often operate in a physical environment thatis otherwise not survivable for humans. In flight, the ambient air may be extremely cold and dry, and can contain high levels of ozone. On the ground, the ambient air may be hot, humid, and contain many pollutants such as particulate matter, aerosols, and hydrocarbons. These conditions change quickly from ground operations to flight. A hot-day, high-humidity ground condition usually dictates the thermal capacity of the air- conditioning equipment, and flight conditions determine the supply air compressor's capacity. Maximum heating requirements can be de- termined by either cold-day ground or flight operations. In addition to essential safety requirements, the ECS should pro- vide a comfortable cabin environment for the passengers and crew. This presents a unique challenge because of the high-density seating of the passengers. Furthermore, aircraft systems must be low in mass, accessible for quick inspection and servicing, highly reliable, able to withstand aircraft vibratory and maneuver loads, and able to compensate for various possible system failures. Ambient Temperature, Humidity, and Pressure Figure 1 shows typical design ambient temperature profiles for hot, standard, and cold days. The ambient temperatures used for the design of a particular aircraft may be higher or lower than those shown in Figure 1, depending on the regions in which the aircraft is to be operated. The design ambient moisture content at various alti- tudes as recommended for commercial aircraft is shown in Figure 2. However, operation at moisture levels exceeding 30 g/kg of dry air is possible in some regions. The variation in ambient pressure with alti- tude is shown in Figure 3. Refer to the psychrometric chart for higher altitudes for cabin humidity calculations. Figure 4 shows a psychro- metric chart for 2440 m altitude. Heating/Air Conditioning Load Determination The cooling and heating loads for a particular aircraft model are determined by a heat transfer study ofthe several elements that com- prise the air-conditioning load. Heat transfer involves the following factors: · Convection between the boundary layer and the outer aircraft skin The preparation of this chapter is assigned to TC 9.3, Transportation Air Conditioning. °C TEMPERATURE, AMBIENT X-Axis: Altitude, m Chart Type: line MAXIMUM HOT DAY INTERNATIONAL STANDARD ATMOSPHERE (ISA) COLD DAY item_01 4500 3000 2000 1500 1000 500 Fig. 1 Ambient Temperature Profiles X-Axis: Altitude, km Y-Axis: Ambient Moisture, g/kg (dry air) Chart Type: line 0-2 km 2-4 km 4-6 km 6-8 km 8-10 km 10-12 km item_01 18 18 12 6 4 2 Fig. 2 Design Humidity Ratio 13.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
58b3d64e-4f1f-4fd1-b149-f88cb7f2b7cc | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 13.2 2019 ASHRAE Handbook-HVAC Applications (SI) kPa PRESSURE, AMBIENT Chart Type: line 0 km 2 km 4 km 6 km 8 km 10 km 12 km 14 km 16 km item_01 100% 80% 70% 50% 40% 30% 20% 10% 10% · Radiation between the outer aircraft skin and the external envi- ronment · Solar radiation through windows, on the fuselage, and reflected from the ground. · Conduction through cabin walls and the aircraft structure · Convection between the interior cabin surface and the cabin air · Convection and radiation between the cabin and occupants · Convection and radiation from internal sources ofheat (e.g., elec- trical equipment) · Latent heat from vapor cycle systems Ambient Air Temperature in Flight During flight, very cold ambient air adjacent to the outer surface ofthe aircraft increases in temperature through ram effects, and may be calculated from the following equations: TAW = Too +r(Tr-To) k-1 M2 TT= Too 1 + 2 or k 2 M2 TAW = Too 1 + r = Pr1/3 Fig. 3 Cabin Pressure Versus Altitude where Pr = Prandtl number for air (e.g., Pr = 0.73 at 240 K Too = ambient static temperature, K ![image](/image/placeholder) 0.03 120 0.028 90% 110 0.026 80% 0.024 do 70 0.022 VOLUME m3 PER K9 DRY 25 0.02 g0 60% 0.018 olo ENTHALPY (h) kJ/kg OF DRY AIR 100 80 0.016 40% 70 AIR 0.014 2 % 0.012 60 30 0.01 40 20% 0.008 20 5 0.006 10% RH 0.004 0.002 유 0 0 5 10 15 20 25 30 35 40 45 50 DRY-BULB TEMPERATURE, °C AIR kg DRY PER kg MOISTURE (w) RATIO HUMIDITY Fig. 4 Psychrometric Chart for Cabin Altitude of 2440 m Inc. ASHRAE, 2019 user. single for Licensed | {}
66be2e5f-3807-42ea-8b6f-d3db07ca42fa | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Aircraft 13.3 ¦ TT = ambient total temperature, K ¦ ¦ --- ¦ ¦ k = ratio of specific heat; for air, k = 1.4 ¦ ¦ M = airplane Mach number ¦ ¦ r = recovery factor for turbulent boundary layer (i.e., fraction of total temperature recovered in boundary layer as air molecules rest on the surface) ¦ ¦ TAW = recovery temperature (or adiabatic wall temperature), K ¦ Example 1. The International Civil Aviation Organization (ICAO) cold day at 9144 to 12 192 m altitude has a static temperature of -65°C (208 K) and a Prandtl number of 0.739. If an airplane is traveling at 0.8 Mach, what would the external temperature be at the airplane's skin? Solution: Iteration is usually required. First guess for r 》 0.9: Pr = 0.728 at 0.9(240 -208) + 208 = 236.8 K r=Pr=(0.728)1/3 = 0.8996 TT = Too 1+ 늘 M = 208 1 + 14-1[0.8]2 = 235 K TAW = To+r(TT-To) = 208 + 0.8996(235-208) = 232.3 K (-41°C) Air Speed and Mach Number The airplane airspeed is related to the airplane Mach number by the local speed of sound: u。 = M VkRT。 where k = ratio of specific heats; 1.4 for air R = gas constant; 287 m2/(s2.K) M = airplane Mach number U。 = airplane airspeed, m/s Ambient Pressure in Flight The static pressure over most of the fuselage (the structure around the cabin) is essentially equal to the ambient pressure at the appropriate altitude. Ps = Pinf+ Cp 를 poou2 2 where Ps pressure surrounding the fuselage, N/m2 Cp pressure coefficient, dimensionless; approximately zero for passenger section of fuselage Poo = free-stream or ambient air density, kg/m3 External Heat Transfer Coefficient in Flight The fact that the fuselage is essentially at free-stream static pres- sure implies that a flat-plate analogy can be used to determine the external heat transfer coefficient at any point on the fuselage: -2,584 -2/3 h = Pwcpu000.185(log10Rex) Pr (note: 10 7 10°) < Rex < Pmux Rex = m Pw Cp, 14, Pr TAW+ T° evaluated at T* = + 0.22(TAW- T� ) 2 q = hA(T- TAW) where ![image](/image/placeholder) h = external heat transfer coefficient, W/(m2.K) Rex = local Reynolds number, dimensionless x = distance along the fuselage from nose to point of interest, m cp = constant-pressure specific heat; for air, J/(kg·K) Pw = ambient air (weight) density at film temperature T*, kg/m3 m = absolute viscosity ofair at T* : 3.673 x 10-9(7*)3/2 [408.2/(T* + 120)] kg/(m ·s)(mPa - s) A = outside surface area, m2 T = outer skin temperature, K 9 = convective heat loss from outer skin, W U。 = airplane airspeed, m/s External Heat Transfer Coefficient on Ground The dominant means of convective heat transfer depends on wind speed, fuselage temperature, and other factors. The (free con- vection) heat transfer coefficient for a large, horizontal cylinder in still air is entirely buoyancy-driven and is represented as follows: g(�)(�T)d3 Gr = 2 v for 109 ≤ GrPr ≤ 1012: 1/3 0.13k(GrPr) hfree d where g = gravitational acceleration, 9.8 m/s2 k = thermal conductivity of air, W/(m·K) V = kinematic viscosity, m2/s d = fuselage diameter, m hfree = free-convection heat transfer coefficient, W/(m2.K) B = expansion coefficient of air = VTf, where Tf=(Tskin + Too)/2, K AT = Tskin - Too Tskin = skin temperature, K Too = ambient temperature, K Gr = Grashof number Pr = Prandtl number A relatively light breeze introduces a significant amount of heat loss from the same horizontal cylinder. The forced-convection heat transfer coefficient for a cylinder may be extrapolated from the fol- lowing: Vd Re = V for 4x 104 ≤ Re≤4x 105 0.805 1/3 0.0266k(Re) Pr hforced = where V is wind speed in m/s, and V is evaluated at Tf = (Tskin + T__)/2. Example 2. One approximation of the fuselage is a cylinder in cross-flow. The fuselage is 3.7 m in diameter and 37 m long, in a 4.3 m/s crosswind and a film temperature of 319 K. The surface temperature varies with the paint color and the degree of solar heating. For instance, a typical white paint could be 17 K higher than the ambient air temperature, so the heat transfer from the fuselage would be Free convection: g(�)(�T)d3 Gr = 9.8(0.00313)(17)(3.7)3 = 8.43 x 1010 2 10~5 2 v (1.77 x Inc. ASHRAE, 2019 user. single for Licensed for 109 ≤ GrPr ≤ 1012. | {}
9c03568a-3d01-45cd-ba57-aa27729b48a0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 13.4 1/3 1/3 (0.704)] 0.13k(GrPr) 0.13(0.028)[8.43 x 1010 hfree d 3.7 = = 3.84 W/(m2.K) Forced convection: Vd 4.3(3.7) Re = = = 8.98 x 105 V 5 1.77 x 10 for 4 x 104 ≤ Re≤4x 105. Note that, although this Reynolds number is beyond the recommended range, the extrapolation has about a 10% error (underprediction) when compared to other more complicated methods. Comparison of heat transfer coefficients shows that, in this situ- ation, heat transfer is dominated by forced convection, so the free- convection aspect can be ignored. External Radiation The section of airplane fuselage that surrounds the cabin radiates primarily to the sky. At sea level, the sky temperature is about 17 K cooler than the surrounding air temperature (depending on humidity and other factors). As the airplane climbs, there is a decreasing amount of air above to radiate to, so the difference between air tem- perature and sky temperature increases. For example, at a cruising altitude of 9000 to 11 000 m, the sky temperature is about 56 K cooler than the air temperature (free-stream static). The limiting condition, of course, is outer space, where the sky temperature is the cosmic background radiation (CBR). The sky temperature in this case is only about 3 K. The heat loss to the sky by radiation is qR = A�(�) (T4 - T sky) where qR = radiation heat loss from outer skin, W A = outside surface area, m2 T = outer skin temperature, K 0 = Stephan-Boltzmann constant, 5.67 X 10-8 W/(m2. K4) 8 = emissivity of surface, paint, etc. Tsky temperature, K = sky Inc. ASHRAE, 2019 user. single for Licensed Solar radiation on the ground is covered in detail elsewhere (e.g., Chapter 36); however, during cruising, the incident solar radiation should be adjusted for altitude. The column of air between the sun and the airplane varies with time of day (angle) and altitude. Stan- dard sea-level solar flux, for a given latitude and time of day, can be adjusted for altitude using Beer's law: ISL = I⌀e-nams Iv = I⌀e-namsm Cy= Iv/ISL Is = A�(Cy)I where I = solar radiation to a surface at sea level after accounting for latitude and time of day, W/m2 solar constant, 1355 W/m2 normal solar flux at altitude, W/m2 ISL normal solar flux at sea level, W/m2 Cy = correction factor for altitude n turbidity factor: 2.0 for clear air, 4 to 5 for smog m relative thickness of air mass, Py/PSL = (altitude pressure)/(sea level barometric pressure) ams molecular scattering coefficient = 0.128-0.054 log10(m) a = solar absorptivity of surface, window, paint, etc. A = outside surface area, m2 ![image](/image/placeholder) RIBS OUTER SKIN CABIN WALL INSULATING BLANKETS INSULATING CAPS 2019 ASHRAE Handbook-HVAC Applications (SI) Fig. 5 Example of Aircraft Insulation Arrangement Conduction The conductive path from the air in the cabin to the surrounding environment is generally described as several heat transfer elements in series and in parallel with each other. The structure is typically quite conductive (e.g., aluminum), and must be insulated to avoid a direct heat path from inside to outside. The structure typically has an outer skin supported by circumferential and longitudinal ribs. The members require a structurally efficient attachment, which often is also thermally efficient, so that the entire structure is essentially at the same temperature. As a result, the effective "fin" area may be much larger than the simple outside surface area ofthe fuselage. Figure 5 shows an example of an aircraft insulation arrangement. For occupant comfort, the cabin wall temperature should not be drastically different from the air temperature within the cabin, be- cause the passengers frequently are in contact with this and other in- terior surfaces. The insulation accommodates this requirement as well as noise reduction, which on occasion is the dominant requirement. Stack Pressure across Cabin Wall The cold outer skin during flight generates buoyancy-driven flow between the cabin and the cavity formed by the cabin wall and the outer skin. Because this cavity is normally filled with insulation blankets, it may be relatively porous to airflow. The outer skin is fre- quently below the cabin dew point (and below freezing), so water condenses on the structure and ice may build up with time. The amount of flow in and out of the cavity depends on the leakage area of the cabin wall. Leakage commonly occurs through panel joints and gaps surrounding penetrations, as well as around doors, where additional structure and mechanisms may provide addition thermal conductivity and air passages to the outer skin. A certain amount of flow in and out of the cavity is unavoidable because of normal pres- surization and depressurization of the cabin during descent and climb. The driving pressure, or stack pressure, is simply the density difference between the connected volumes: AP = (Pcavity1 - Pcavity2)gh stack 1 1 P gy cabin T T cavity1 cavity2 R where y = cavity height, m T = temperature, K | {}
e6ab2b81-8092-42d8-8b53-120c2896de8c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Aircraft 13.5 ¦ p = air density, kg/m3 ¦ ¦ --- ¦ ¦ g = gravitational constant =9.8 m/s2 ¦ ¦ R = gas constant, 287 m2/(s2.K) ¦ ¦ AP = stack pressure, Pa ¦ ¦ = absolute cabin N/m2 ¦ P cabin pressure, Metabolic Heat from Occupants A thorough treatment of metabolic heat from humans is covered in Chapter 9 of the 2017 ASHRAE Handbook-Fundamentals. Be- cause an airplane cabin is frequently at higher altitudes, the balance between sensible and latent heat changes slightly from that given in that chapter. To correct for altitude, the following approach is rec- ommended. First, examining the heat transfer coefficient: For low air velocity (V < 0.2 m/s), flow is dominated by natural convection: p2gB(△7)d3Pr 2m h = JC(GrPr)" = kac 2 → h oc p m m For a cylindrical approximation of an adult at rest, Gr = 107, so C= 0.59 and m = 1/4, which leads to 0.5 2(1/4) Palt Palt halt PSL = hSL = hSL PSL For higher air velocity (0.2 < V<4 m/s), flow is dominated by forced convection: n Cp,air Pr → h⌀ p" h = KC(Re)"Pr 1/3 kac pVd 1/3 = m For a cylindrical approximation of an adult at rest, Re > 4000, so C= 0.193 and n = 0.618, which leads to 0.618 0.618 Palt Palt halt PSL = hSL = hSL PSL These two correction factors have been combined (see Equation [37] in Chapter 9 ofthe 2017 ASHRAE Handbook-Fundamentals) to produce a simpler relationship that applies to the full velocity range (0 < V<4 m/s): 0.55 Palt halt = hSL PSL Next, examining the evaporation or mass transfer from the occu- pants, the evaporative heat transfer coefficient varies inversely with the ambient pressure (see Equation [38] in Chapter 9 of the 2017 ASHRAE Handbook-Fundamentals): he = (LR)(h) 0.55 he,SL Palt he,alt PSL and hsL LRSL = LRalthSL 0.55 Palt he.SL he,alt LRSL PSL = LRalthSL Substitute 2/3 Dv Rairhfg a LRalt = Paltcp,airRw 0.45 2/3 Dv Rairhfg a LRSL = PSLCp,airRw PSL he,alt Palt = he,SL where h = heat transfer coefficient, W/(m2.K) LR = Lewis relation, °C/Pa hSL = heat transfer coefficient at sea level, W/(m2.K) he = evaporative heat transfer coefficient, W/(m2·Pa) = = he,alt evaporative heat transfer coefficient at altitude, W/(m2·Pa) he,SL evaporative heat transfer coefficient at sea level, W/(m2·Pa) = = P alt cabin pressure at altitude, N/m2 = PSL pressure at sea level; 2116 N/m2 Rair gas constant for air; 286.5 m2/(s2.K) hfg = evaporation enthalpy at human skin temperature, 2.41 x 106 J/kg Dv = mass diffusivity of water vapor in air; 2.55 x 10-5 m2/s a = diffusivity; 2.16 X 10-5 m2/s = specific heat of air; 1005 J/(kg·K) About 70% of the metabolic heat is lost through convection/ radiation (72 W sensible or 29 W convection, h = 0.55, plus 43 W radiation, h, = 0.83) and 30% through evaporation (31 W latent) while seated at rest at sea level (see Table 1). At 2440 m cabin alti- tude, in still air, the sensible heat would drop to (2.67/3.12)29 = 25 W convection, the radiation would remain at 43 W, and the latent heat would rise to (732/642)31 = 35 W for a total of 103 W. This would indicate a slightly higher temperature for comfort, or a net effect of a slightly cooler sensation at altitude, compared to the 102.6 W total required. Rw = gas constant for water vapor; approximately 461 m2/(s2.K) When considering heat sources in the cabin, there are several parallels to commercial and residential HVAC. Many heat sources such as appliances (refrigerators, conventional ovens, microwave ovens), lighting, and entertainment (TV, stereo), may be in the cabin. In addition, the electronics and equipment associated with the Internal Heat Sources Table 1 Heat and Mass Transfer Coefficients for Human Body Versus Altitude ¦ Altitude, m ¦ Pressure, kPa ¦ Convection h, W/(m2.K) ¦ Convection h, W/(m2.K) ¦ Evaporation h⌀ W/(m2·Pa) ¦ Evaporation h⌀ W/(m2·Pa) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Altitude, m ¦ Pressure, kPa ¦ V<0.2 ¦ 0.2 ¦ V<0.2 ¦ 0.2 ¦ ¦ 0 ¦ 10.33 ¦ 3.12 ¦ 0.061 V0.6 ¦ 642 ¦ 12.5V0.6 ¦ ¦ 305 ¦ 9.97 ¦ 3.07 ¦ 0.060V0.6 ¦ 653 ¦ 12.7V0.6 ¦ ¦ 610 ¦ 9.61 ¦ 3.01 ¦ 0.059V0.6 ¦ 664 ¦ 12.9V0.6 ¦ ¦ 915 ¦ 9.26 ¦ 2.95 ¦ 0.057V0.6 ¦ 676 ¦ 13.1V0.6 ¦ ¦ 1220 ¦ 8.93 ¦ 2.90 ¦ 0.056V0.6 ¦ 687 ¦ 13.4V0.6 ¦ ¦ 1525 ¦ 8.60 ¦ 2.84 ¦ 0.055V0.6 ¦ 698 ¦ 13.6V0.6 ¦ ¦ 1830 ¦ 8.28 ¦ 2.78 ¦ 0.054V0.6 ¦ 710 ¦ 13.8V0.6 ¦ ¦ 2135 ¦ 7.97 ¦ 2.73 ¦ 0.053V0.6 ¦ 721 ¦ 14.0V0.6 ¦ ¦ 2440 ¦ 7.68 ¦ 2.67 ¦ 0.052V0.6 ¦ 732 ¦ 14.3V0.6 ¦ Inc. ASHRAE, 2019 user. single for Licensed | {}
8fec354e-a6ad-4acc-b007-409ee0434da7 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 13.6 2019 ASHRAE Handbook-HVAC Applications (SI) operation of a commercial aircraft put demands on the airplane's environmental control system. Cooling Requirements. The sizing criteria for air conditioning are usually ground operation on a hot, humid day with the aircraft fully loaded and the doors closed. A second consideration is cool- down of an empty, heat-soaked aircraft before passenger loading; a cooldown time of less than 30 min is usually desired. A cabin tem- perature ofbetween 24 and 27°C is typically specified for these hot- day ground design conditions. During cruise, the system should maintain a cabin temperature of 24°C with a full passenger load. The cooling load is entirely sensible in most cases when air-cycle machines are used. When a vapor-cycle recirculation system is used, latent heat is added. Heating Requirements. Heating requirements are based on a partially loaded aircraft on a very cold day. Cabin temperature warm-up for a cold-soaked aircraft is desired to be within 30 min as well. A cabin temperature of 21°C is typically specified for cold- day ground-operating conditions. During cruise, the system should able to maintain a cabin temperature of 24°C with a 20% passenger load, a cargo compartment temperature above 4.4°C, and cargo floor temperatures above 0°C to prevent freezing of cargo. Temperature Control Whenever a section of the cabin or flight deck has capability for independent supply temperature control, it is termed a zone. Com- mercial aircraft (over 19 passengers) can have as few as two zones (cockpit and cabin) and as many as seven. These crew and passenger zones are individually temperature-controlled to a crew-selected temperature for each zone, ranging from 18 to 29°C. Some systems have limited temperature control in the passenger zones that can be adjusted by the flight attendants. The selected zone temperature is controlled to within 1 K of the sensed temperature, and temperature uniformity in the zone should be within 3 K. Separate temperature controls can be provided for cargo compartments. Temperature control may also be the predominant driver of ven- tilation requirements. The interior of the fuselage has several elec- tronic/electrical heat sources that are required for the aircraft's operation, as well as heat loads from ambient and from occupants and their activities. These increasing heat loads are accommodated by reducing supply temperatures: qsources Tsupply c p m = Tcabin Inc. ASHRAE, 2019 user. single for Licensed where all heat into cabin, W qsources m air mass flow, kg/s Cp = specific heat; 1006 J/(kg· K) for air T = temperature, K Supply temperatures in each of the zones have practical limits, such as the freezing temperature of water (humidity), when either the heat loads are too large or the mass flow is too low. Air Velocity The passenger cabin is most similar to buildings with very high occupant densities, such as theaters or lecture halls. In these situ- ations, the air-conditioning system is typically in cooling mode (i.e., the supply diffuser temperature is cooler than the room tem- perature). The ducting and diffuser networks are best described as cold-air systems, in which the duct velocities are higher, duct tem- peratures lower, and the fraction of recirculated air smaller (about 50% of the mixture) than in buildings (which use up to 95%). The cold-air diffuser is also in much closer proximity to the occupants in an aircraft cabin. The design challenge is to deliver cool air to the passengers without uncomfortable drafts. X-Axis: Time, s Y-Axis: Velocity, fpm Chart Type: line initial_value peak_value final_value item_01 80ppm 50ppm 100ppm Fig. 6 Transient Air Velocity Measured in Seated Area of Aircraft Cabin The velocity characteristics of an airplane cabin are uniquely affected by transitional flow behavior. The supply diffuser Reynolds number is typically between 3000 and 5000. Turbulence induced by the diffuser affects the perceived draftiness. Figure 6 shows the unsteady velocity variations measured in an aircraft cabin. At any instant in time, the velocity field in the cabin will change, but an overall pattern develops for the time-averaged velocity. An example of this comes from computational fluid dynamics (CFD) modeling of a passenger cabin. Ventilation air enters the cabin near the center and blows outward in two directions. Air leaves near the floor on both sides, as shown in Figure 7. Several comfort indices are used to evaluate air velocity, such as predicted percent dissatisfied (PPD) or predicted mean vote (PMV). Draft-sensitive areas of the body such as the ankles or neck receive special attention during air distribution system design. The velocity requirements are described in detail in Chapter 9 of the 2017 ASHRAE Handbook Fundamentals and ASHRAE Standard 55. Ventilation Air drawn from the compressor section of the jet engine is called bleed air (also known as outside air, fresh air, outdoor air, or ambient air). When air is provided by sources other than the engine, it is not bleed air in the strict sense, because it is no longer bled from the engines. The current FAA requirement is to provide 4 g/s of bleed/ outdoor air per person. Because this requirement is expressed as a mass flow, the bleed air ventilation rate as a volumetric flow varies with cabin pressure and temperature. Cabin altitude is a convenient way of expressing cabin pressure by referencing the cabin pressure to a standard atmosphere. The required 4 g/s is equivalent to about 3.3 L/s at sea level and 24°C. Based on ASHRAE research, ASHRAE Standard 161 established a ventilation rate for aircraft passengers at 3.5 L/s per passenger. This rate was based in part on the consideration that not all spaces in the enclosed area achieve 100% ventilation effectiveness. At other cabin pressures or alti- tudes, flow volumes can be found with the following equation: mRTc m m �FR = = p P C c RTc where m = 0.00416 kg/s R = 0.2865 m2/(s2.K) Tc = cabin temperature; 21°C = 294 K P = cabin pressure from Table 2, kPa In many aircraft, the bleed/outdoor air flow is augmented by fil- tered or recirculated air. There are currently no regulatory require- | {}
4b6d86c2-33be-4392-a603-dd0170ba3010 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Aircraft 13.7 Chart Type: line Seats item_01 90% Fig. 7 Cabin Air Velocities from CFD, fpm (Lin et al. 2005) ments on the amount of recirculated air that enters the cabin, but it is customary to provide about 4.7 L/s per person of recirculated air in addition to the bleed air required by regulation, for a total of about 9.4 L/s per person at 2440 m cabin altitude. Ventilation Effectiveness. ASHRAE Standards 62.1-2018 and 161-2018 address ventilation effectiveness (VE), a measure of mix- ing within the volume relative to a perfectly mixed system (Standard 62.1 uses the term zone air distribution effectiveness Ez instead of VE). Itis described with the following equations: Cmixed c in VE= Clocal - Cin where c = contaminant concentration, or Qlocal VE Qcabin where Clocal = local contaminant concentration by volume = inlet contaminant concentration ¦ Cin ¦ ¦ ¦ --- ¦ --- ¦ ¦ Cmixed = ¦ concentration if perfectly mixed ¦ ¦ Qcabin = ¦ contaminant flow to cabin or zone, L/s ¦ ¦ Qlocal = ¦ flow delivered to breathing zone, L/s ¦ Contaminant concentrations in a perfectly mixed system are the same in the cabin volume as at the exit (floor grilles), and the concen- tration in the exit is based only on the ventilation rate and generation rate (including source and sink). Therefore, ventilation effectiveness indicates the degree of contaminant stratification with the volume. VE > 1 means that concentrations in the breathing zone are lower than in a perfectly mixed system; VE < 1 means they are higher. There is a distinction between VE for bleed air and VE for total ventilation. For bleed air, the inlet concentration Cin is the concentration of gases in the supply air to the entire system (i.e., bleed air concentration). The local concentration will be Table 2 FAA-Specified Bleed Air Flow per Person ¦ Cabin Pressure, kPa ¦ Altitude, m ¦ Required Flow per Person at 24°C, L/s ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 101.325 ¦ 0 ¦ 3.49 ¦ ¦ 99.505 ¦ 150 ¦ 3.54 ¦ ¦ 97.719 ¦ 305 ¦ 3.63 ¦ ¦ 95.954 ¦ 460 ¦ 3.68 ¦ ¦ 94.210 ¦ 610 ¦ 3.78 ¦ ¦ 92.500 ¦ 760 ¦ 3.82 ¦ ¦ 90.811 ¦ 915 ¦ 3.92 ¦ ¦ 89.149 ¦ 1070 ¦ 3.96 ¦ ¦ 87.508 ¦ 1220 ¦ 4.06 ¦ ¦ 85.895 ¦ 1370 ¦ 4.11 ¦ ¦ 84.309 ¦ 1525 ¦ 4.20 ¦ ¦ 82.744 ¦ 1680 ¦ 4.29 ¦ ¦ 81,200 ¦ 1830 ¦ 4.34 ¦ ¦ 79.683 ¦ 1980 ¦ 4.44 ¦ ¦ 78.187 ¦ 2135 ¦ 4.53 ¦ ¦ 76.711 ¦ 2290 ¦ 4.63 ¦ ¦ 75.263 ¦ 2440 ¦ 4.72 ¦ larger than the inlet concentration only if the contaminant is generated within the cabin. For total ventilation, VE uses the Cin at the nozzle (i.e., supply mixture concentration) and includes contaminants from the recirculation system. The practical use of this VE applies to particulate levels in the cabin, because the recirculated air is equivalent to bleed air in this regard. Contaminant concentrations in the cabin can be converted to flows delivered to the breathing zone �local using the following rela- tionship: qgen Qlocal Clocal - Cin Inc. ASHRAE, 2019 user. single for Licensed | {}
cca6c58f-8769-415e-a2b8-9592b7997c77 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 13.8 Substitute qgen supplied (c mixed cin) = 0 Cmixed - Cin Qlocal = �supplied Clocal - Cin where qgen = CO2 generation rate, 0.005 L/s at standard conditions = local CO2 concentration by volume Clocal Cin = inlet CO2 concentration �supplied or zone, L/s = flow to cabin Qlocal = flow delivered to breathing zone, L/s Some consideration can be given to distribution effectiveness (DE), where flows to higher-occupant-density sections ofthe cabin (e.g., coach) are used to set minimum flows to the cabin, and lower- density sections (e.g., first class) may subsequently be over- ventilated: Qzone/ nzone DE Qcabin ncabin / where Qzonenzone = flow per person in zone Qcabin/ncabin = average flow per person for entire cabin Distribution effectiveness accounts for a system that provides a uniform flow per length of cabin yet has varying seating densities along the length. For bleed air distribution, this effectiveness is tem- pered somewhat by occupant diversity D (see ASHRAE Standard 62.1), because underventilated zones feed into the same recircula- tion flow. For total flow (bleed + recirculated) and for systems with- out recirculation, however, occupant diversity does not apply. System ventilation efficiency (SVE) is a measure of how well mixed the recirculated air is with the bleed air before it enters the cabin. The SVE can be determined from the concentration varia- tions in the ducts leaving the mix manifold (see Figure 11), for instance. The SVE is similar to VE in formulation: Call zones amb - c SVE = Czone amb - c Inc. ASHRAE, 2019 user. single for Licensed where Call zones average concentration of all supply ducts = concentration in individual supply duct Czone Camb Cfr (bleed air concentration) = ambient reference concentration = Dilution Ventilation and TLV Contaminants that are present in the supply air and are also gen- erated within the cabin require increasing dilution flows to avoid reaching Threshold Limit Values (TLVsⓇ) (ACGIH). For example, suppose carbon monoxide is present in the atmosphere at 210 ppb and that each person generates 0.168 mL CO per minute, or 2.8 x 10- 6 L/s (Owens and Rossano 1969). The amount of bleed air required to stay below the EPA guideline of 9000 ppb will depend on the ambient CO levels, the human generation rate, and the CO contribu- tion of the ventilation system: qgen qgen Qreq - AC Cfr CTLV- C CTLV supply system where CTLV = allowable concentration system AC = concentration rise from system C supply = concentration in supply (air entering cabin) = CO 2019 ASHRAE Handbook-HVAC Applications (SI) Example 3. Ifthe ventilation system does not contribute carbon monoxide to the supply air, then the required ventilation rate to stay below the threshold is CTLV = 9000 ppb = 0.000009 9gen = 2.8 x 10-6 L/s AC = 0 system Cfr = 210 ppb = 2.1 x 10-7 qgen 2.8 x 10 6 Qreq CTLV- AC Cfr 0.000009 - 0 - 2.1 x 10 system = 0.32 L/(s·person) If, however, the ventilation system produces a 1000 ppb rise in car- bon monoxide, then the required ventilation is 9gen = 2.8 x 10-6 L/s AC = 1000 ppb = 0.000001 system Cfr = 210 ppb = 2.1 x 10-7 CTLV = 9000 ppb = 0.000009 6 qgen 2.8 x 10 Qreq AC Cfr 0.000009 - 0.000001 - 2.1 x 10 CTLV- system = 0.36 L/(s·person) It is important to note that, under certain circumstances, qgen and AC may change sign as contaminant sources become contaminant system sinks. This simplified approach shown here is more conservative, and could overpredict contaminant levels in real situations. Air Exchange High occupant density ventilation systems have higher air exchange rates than most buildings (i.e., offices). The typical air- plane may have an air exchange rate of 10 to 20 air changes per hour (ach), whereas an office might have 1 ach. The air is not replaced in a mixed system at every air exchange. Actually, the ratio Q/V (air exchange rate) is more like the inverse of decay time constant T. An airplane cabin can be approximated as a partially mixed volume (a volume with ventilation effectiveness) as long as the contaminant sources are uniformly distributed throughout the volume. For a well-mixed volume, contaminant in equals contaminant out plus contaminant accumulated in the volume, or dc Qcin = Qcout + V dt Accounting for ventilation effectiveness, the concentration leaving the volume Cout to the concentration within the is related volume c and the concentration entering the volume Cin by the ven- tilation effectiveness VE: Cmixed - Camb Cout - Camb VE = → c out Cin + VE(c-cin) = Clocal c amb Clocal - c amb Substituting, Qcin = Q[cm + VE(c-cin)]+ V dc dt qgen generated per person Cfr = concentration in bleed air which leads to Q(VE) / c = Cin - (cin - c。)e | {}
f3ddf509-c8c6-45b1-a162-60777f655064 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Aircraft 13.9 Although air exchange rates are occasionally used as require- ments on the ventilation system, in the case of cabin ventilation, there is no basis for setting one. Air exchange rate can be a surro- gate (only for similarly sized volumes) for temperature uniformity, air quality, or smoke clearance. The flow-per-person specification is preferred, because it can be related to the predominant pollutant source more directly. Air exchange rates therefore indirectly pro- vide valid ventilation comparisons between airplanes of similar volume and seating density. However, comparisons with buildings are misleading: occupant densities could be 30 times higher in air- craft, and bioeffluent doses (defined here as the time integral of the concentration of occupant-generated contaminants) for the same ventilation rate per person are greater in aircraft passenger cabins, depending upon occupancy times (see the section on Air Quality). Filtration Most airplane manufacturers have provisions for recirculated air filtration. Common practice is to install high-efficiency particulate air (HEPA) filters. The current industry standard for new build pro- duction aircraft is EU class H13 according to EN Standard 1822-1 and ISO Standard 29463-1 class 35H (i.e., 99.95% minimum re- moval efficiency by sodium flame test) (Eurovent 4/4, BS3928). This is equivalent to 99.97% minimum removal efficiency of ap- proximately 0.3 um when tested according to Institute of Environ- mental Sciences and Technology Recommended Practice RP- CC001.5 (IEST 1997). Filters are required to have sufficient particulate capacity to remain effective between normal maintenance intervals. The life of the filter is related to the recirculation system pressure drop, system operating pressure, and the recirculation fan curve. As the filter becomes loaded, pressure drop increases. When added to the system losses, the effect is a reduction in flow, as shown in Figure 8. It is important to change the filters at least as often as recom- mended by the manufacturer to maintain flow capacity. Carbon/HEPA filters are available on the recirculation system for some aircraft models. Performance is not fully characterized. Filters must be tested and certified for each aircraft design. Currently avail- able designs are intended to replace standard HEPA filters. The system designer must verify with the filter manufacturer the service life of the filter for the intended application. Most systems have no filtration of the engine bleed air supply as standard equipment, al- though some technologies (e.g., combined VOC/ozone converters Chart Type: line Pressure Loaded New System Curves item_01 0Not specified 1Not specified 25Not specified 75Not specified Fig. 8 Flow Reduction Caused by Filter Loading and bleed air centrifugal cleaners) are sometimes offered as optional equipment. Pressurization/Oxygen Cabin pressurization achieves the required partial pressures of oxygen for the crew and passengers during high-altitude flight. At altitudes above 2440 m, the occupied cabin must be pressurized to an equivalent altitude of 2440 m or less to allow normal physiolog- ical functions without supplemental oxygen. The maximum pres- sure difference between the cabin and outside environment is limited by aircraft structural design limits. The differential pressure control provides a cabin pressure based on the flight altitude of the aircraft. A typical cabin altitude schedule is shown in Figure 3. Additional provisions that are separate from normal cabin pressure controls must be provided for positive- and negative-pressure relief to protect the aircraft structure. A DOT-sponsored study (DOT 1989) concluded that current pres- surization criteria and regulations are generally adequate to protect the traveling public. The study also noted that the normal maximum rates of change of cabin pressure (approximately 2.5 m/s in increas- ing altitude and 1.5 m/s in decreasing altitude) do not pose a problem for the typical passenger. However, pressurization ofthe cabin to equivalent altitudes of up to 2440 m, as well as changes in the normal rates of pressure during climb and descent, may create discomfort for some people, such as those suffering from upper respiratory or sinus infections, obstruc- tive pulmonary diseases, anemia, or certain cardiovascular condi- tions. In those cases, supplemental oxygen may be recommended. Children and infants sometimes experience discomfort or pain because of pressure changes during climb and descent. Injury to the middle ear has occurred to susceptible people, but is rare. During a sudden cabin depressurization in flight, passengers and crew are provided with overhead masks supplying supplemental oxygen. Passengers with respiratory diseases can bring portable oxygen containers on board. Humans at rest breathe at a rate of approximately 0.15 L/s while consuming oxygen at a rate of 0.007 L/s at 2440 m. The percent oxygen makeup of the supply air remains at approximately 21% at cruise altitude. A person receiving 4. 7 L/s of outside air and 4.7 L/ s of recirculation air would therefore receive approximately 2 L/s of oxygen. The level drops to 1.98 L/s as it leaves the cabin. Conse- quently, the content of oxygen in cabin air is little affected by breathing (i.e., it drops 0.33%). Although the percentage of oxygen in cabin air remains virtually unchanged (20.93%) at all normal flight altitudes, the partial pressure of oxygen decreases with increasing altitude, which decreases the amount of oxygen held by the blood's hemoglobin. The increase in cabin altitude may cause low-grade hypoxia (reduced tissue oxygen levels) in some people. However, the National Academy of Sciences (NAS 1986, 2002) concluded that pressurization of the cabin to an equivalent altitude of 1524 to 2440 m is physiologically safe for healthy individuals: no supplemental oxygen is needed to maintain sufficient arterial oxy- gen saturation. System Description The outdoor air supplied to the airplane cabin is usually provided by the compressor stages ofthe engine, and cooled by air-conditioning packs located under the wing center section. An air-conditioning pack uses the compressed ambient air as the refrigerant in air-cycle cooling. Air is supplied and exhausted from the cabin on a continuous basis. As shown in Figure 9, air enters the passenger cabin from supply nozzles that run the length of the cabin. Exhaust air leaves the cabin through return air grilles located in the sidewalls near the floor, running the length of the cabin on both sides. Exhaust air is continuously extracted from below the cabin floor by recirculation Inc. ASHRAE, 2019 user. single for Licensed | {}
b1e46904-8b3d-4466-805c-eb70550fc2ee | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 13.10 2019 ASHRAE Handbook-HVAC Applications (SI) fans that return part of the air to the distribution system. The remaining exhaust air passes to an outflow valve, which directs the air overboard. The cabin ventilation system is designed to deliver air uniformly along the length of the cabin. Pneumatic System The pneumatic system, or engine bleed air system, extracts a small amount of the gas turbine engine compressor air to ventilate and pressurize the aircraft compartments. A schematic of a typical system is shown in Figure 10. During climb and cruise, bleed air is usually taken from the mid-stage engine bleed port for minimum- horsepower extraction (bleed penalty). During idle descent it is taken from the high-stage engine bleed port, where maximum avail- able pressure is required to maintain cabin pressure and ventilation. The auxiliary power unit (APU) is also capable of providing the pneumatic system with compressed air on the ground and in flight. Bleed air is pressure-controlled to meet the requirements of the sys- tem using it, and it is usually cooled to limit bleed manifold tem- peratures to meet fuel safety requirements. In fan jets, engine fan air is extracted for use as a heat sink for bleed air using an air-to-air heat exchanger called a precooler; for turboprop engines, ram air is used, which usually requires an ejector or fan for static operation. Other components include bleed-shutoff and modulating valves, a fan-air- modulating valve, sensors, controllers, and ozone converters. The pneumatic system is also used intermittently for airfoil and engine cowl anti-icing, engine start, and several other pneumatic functions. Each engine has an identical bleed air system for redundancy and to equalize the compressor air bled from the engines. The equip- ment is sized to provide the necessary temperature and airflow for airfoil and cowl anti-icing, or cabin pressurization and air ![image](/image/placeholder) SUPPLY NOZZLE CABIN RISER DUCT FLOOR FAN RETURN MANI- AIR GRILLES FOLD AIR FROM ENGINE COMPRESSOR FILTER EXHAUST HEAT AIR CYCLE MACHINE OUTFLOW FLOW VALVE Fig. 9 Cabin Airflow Path ![image](/image/placeholder) STARTER VALVE (Reference) ENGINE S TARTER BUILT-IN- ( Reference) FAN AIR TO COWL S VALVE ANTI-ICE TEST MOD MODULE CHECK PRECOOLER VALVE T LEFT ENGINE GH PRESSUE PRESSURE CONTROL RE U A NG AND TOFF VA LVE TEMPERATURE AIRPLANE TO RESSURE PRECOOLER 정부 SH VAL E S = STARTER Ⓕ = FAN ⓛ = INTERMEDIATE STAGE Ⓗ = HIGH STAGE Fig. 10 Engine/APU Bleed System conditioning with one system or engine inoperative. The bleed air used for airfoil anti-icing is controlled by valves feeding piccolo tubes extending along the wing leading edge. Similar arrangements may be used for anti-icing the engine cowl and tail section. Air Conditioning Air-cycle refrigeration is the predominant means of air condi- tioning for commercial and military aircraft. The reverse-Brayton cycle or Brayton refrigeration cycle is used, as opposed to the Brayton power cycle that is used in gas turbine engines. The differ- ence between the two cycles is that, in the power cycle, fuel in a combustion chamber adds heat, and in the refrigeration cycle, a ram-air heat exchanger removes heat. The familiar Rankine vapor cycle, which is used in building and automotive air conditioning and in domestic and commercial refrigeration, is used for military air- craft as well as galley cooling on larger commercial transports. In an air cycle, compression of the ambient air by the gas tur- bine engine compressor provides the power input. The heat of compression is removed in a heat exchanger using ambient air as the heat sink. This cooled air is refrigerated by expansion across a turbine powered by the compressed bleed air. The turbine energy resulting from the isentropic expansion is absorbed by a second rotor, which is either a ram air fan, bleed air compressor, or both. This assembly is called an air cycle machine (ACM). The most common types of air-conditioning cycles for com- mercial transport aircraft are shown in Figure 11. All equipment in common use on commercial and military aircraft is open loop, although many commercial aircraft systems include various means of recirculating cabin air to minimize engine bleed air use without sacrificing cabin comfort. The basic differences between the systems are the type of air cycle machine used and its means of water sepa- ration. Hybrid ACM/vapor cycle systems are discussed in Chapter 27 of the 2018 ASHRAE Handbook-Refrigeration. The most common of these air cycle machines in use are the bootstrap ACM consisting of a turbine and compressor; the three- wheel ACM consisting of a turbine, compressor, and fan; and the four-wheel ACM consisting of two turbines, a compressor, and a fan. The bootstrap ACM is most commonly used for military appli- cations, although many older commercial aircraft models use the bootstrap cycle. The three-wheel ACM (simple bootstrap cycle) is used on most ofthe newer commercial aircraft, including commuter aircraft and business aircraft. The four-wheel ACM (condensing cycle) was first applied in 777 aircraft. The compartment supply temperature may be controlled by mix- ing ram-cooled bleed air with the refrigerated air to satisfy the range of heating and cooling. Other more sophisticated means of tem- perature control are often used; these include ram air modulation, various bypass schemes in the air-conditioning pack, and down- stream controls that add heat for individual zone temperature control. The bleed airflow is controlled by a valve at the inlet of the air- conditioning pack. The flow control valve regulates flow to the cabin for ventilation and repressurization during descent. Most aircraft use two or three air cycle packs operating in parallel to com- pensate for failures during flight and to allow the aircraft to be dispatched with certain failures. However, many business and com- muter aircraft use a single pack. High-altitude aircraft that have a single pack also have emergency pressurization equipment that uses ram-cooled bleed air. If the engine ingests water, or if the air cycle drops significantly below the dew point, some water separation devices are installed to avoid water spray in the cabin. Low- or high-pressure water sepa- ration may be used. A low-pressure water separator, located downstream from the cooling turbine, has a cloth lining that coalesces fine water particles entrained in the turbine discharge air into droplets. The droplets are collected, drained, and sprayed into the ram airstream using a bleed-air-powered ejector; this process Inc. ASHRAE, 2019 user. single for Licensed | {}
cb54b09b-fc78-424a-8d68-18b82bf4831d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Aircraft 13.11 ![image](/image/placeholder) AMBIENT AIR FAN OPTIONAL RETURN AIR HEAT EXCHANGER PRESSURE BULKHEAD FAN M WATER ▶ ▶ SEPARATOR BLEED AIR CONDITIONED AIR TURBINE COMPRESSOR BOOTSTRAP CYCLE AMBIENT AIR OPTIONAL RETURN AIR HEAT EXCHANGER PRESSURE BULKHEAD FAN M WATER FAN ▶ ▶ SEPARATOR BLEED AIR CONDITIONED AIR TURBINE COMPRESSOR SIMPLE/BOOTSTRAP CYCLE ![image](/image/placeholder) AMBIENT AIR RETURN AIR HEAT EXCHANGER PRESSURE BULKHEAD TURBINE FAN M FAN CONDENSER ▶ BLEED AIR CONDITIONED AIR COMPRESSOR CHILLED RECIRCULATION CYCLE AMBIENT AIR PRESSURE HEAT EXCHANGER BULKHEAD RETURN AIR CONDENSER FAN M FAN ▶ ◀ . CONDITIONED AIR BLEED AIR . TURBINE TURBINE COMPRESSOR CONDENSING CYCLE Fig. 11 Some Aircraft Refrigeration Cycles increases pack cooling capacity by depressing the ram air heat sink temperature. The high-pressure water separator condenses and removes moisture at high pressure upstream of the cooling turbine. A heat exchanger uses turbine discharge air to cool the high-pressure air suf- ficiently to condense most of the moisture present in the bleed air supply. The moisture is collected and sprayed into the ram airstream. In the condensing cycle one turbine removes the high-pressure water and the second turbine does the final expansion to subfreezing temperature air that is to be mixed with filtered, recirculated cabin air. Separating these functions recovers the heat of condensation, which results in a higher cycle efficiency. It also eliminates con- denser freezing problems because the condensing heat exchanger is operated above freezing conditions. The air-conditioning packs are located in unpressurized areas of the aircraft to minimize structural requirements ofthe ram air circuit that provides the necessary heat sink for the air-conditioning cycle. This location also provides protection against cabin depressuriza- tion in the event of a bleed or ram air duct rupture. The most com- mon areas for the air-conditioning packs are the underwing/wheel ![image](/image/placeholder) TRIM AIR BUSKT の FORWARD AFT CABIN CABIN ZONE ZONE ZONE TRIM AIR RAM AIR RAM AIR VALVE CONDENSER BLEED REHEA ER AIR SUPPLY MIX FLOW 0 MANIFOLD CONTROL 0 VALVE FROM OTHER OO PACK WATER AIR CYCLE RECIR- PRIMARY HEAT CULATING MACHINE EXCHANGER FAN WATER COLLECTOR SECONDARY HEAT RECIRCULATING FILTER EXCHANGER RECIRCULATED CABIN AIR = TEMPERATURE CONTROL VALVE = CHECK VALVE Fig. 12 Aircraft Air-Conditioning Schematic well area and the tail cone area aft of the rear pressure bulkhead. Other areas include the areas adjacent to the nose wheel and over- wing fairing. The temperature control components and recirculating fans are located throughout the distribution system in the pressur- ized compartments. The electronic pack and zone temperature controllers are located in the electrical/electronic (E/E) bay. The air- conditioning control panel is located in the flight deck. A schematic of a typical air-conditioning system is shown in Figure 12. Cabin Pressure Control Cabin pressure is controlled by modulating airflow discharged from the pressurized cabin through one or more cabin outflow valves. The cabin pressure control includes the outflow valves, con- troller, selector panel, and redundant positive-pressure relief valves. Provisions for negative-pressure relief are incorporated in the relief valves and/or included in the aircraft structure (door). The system controls the cabin ascent and descent rates to acceptable comfort levels, and maintains cabin pressure altitude in accordance with cabin-to-ambient differential pressure schedules. Modern controls usually set landing field altitude, if not available from the flight management system (FMS), and monitor aircraft flight through the FMS and the air data computer (ADC) to minimize cabin pressure altitude and rate of change. The cabin-pressure-modulating and safety valves (positive- pressure relief valves) are located either on the aircraft skin, in the case of large commercial aircraft, or on the fuselage pressure bulk- head, in the case of commuter, business, and military aircraft. Locating outflow valves on the aircraft skin precludes handling of large airflows in the unpressurized tailcone or nose areas and pro- vides some thrust recovery; however, these double-gate valves are more complex than the butterfly or poppet-type valves used for bulkhead installations. Safety valves are poppet-type valves for either installation. Most commercial aircraft have electronic con- trollers located in the E/E bay. The cabin pressure selector panel is located in the flight deck. 2. TYPICAL FLIGHT A typical flight scenario from London , s Heathrow Airport to Los Angeles International Airport would be as follows: Inc. ASHRAE, 2019 user. single for Licensed While the aircraft is at the gate and the engines have not been started yet, the ECS can be powered by compressed air supplied by the auxiliary power unit (APU), or bleed air from a ground cart. The APU or ground-cart bleed air is ducted directly to the bleed air man- ifold upstream of the air-conditioning packs. Once started, the | {}
85be7bc1-ea69-44dc-99dc-d0a2b6511a18 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 13.12 2019 ASHRAE Handbook- - HVAC Applications (SI) engines become the compressed air source and the ground carts are disconnected. Taxiing from the gate at Heathrow, the outside air temperature is 15°C with an atmospheric pressure of 101.3 kPa. The aircraft en- gines are at low thrust, pushing the aircraft slowly along the taxiway. Engine Bleed Air Control As air from outside enters the compressor stages of the engine, it is compressed to 220 kPa (gage) and a temperature of 166°C. Some of this air is then extracted from the engine core through one of two openings (bleed ports) in the side of the engine. Which bleed port extracts the air depends on the positioning of valves that control the ports. One bleed port is at a higher engine compressor stage (e.g., fifteenth stage), commonly called high stage. The second is at a lower compressor stage (e.g., eighth stage), commonly called low stage or intermediate stage. The exact stage varies depending on engine type. At low engine power, the high stage is the only source of air at sufficient pressure to meet the needs of the bleed system. Bleed stage selection is totally automatic, except for a shutoff selec- tion available to the pilots on the overhead panel in the flight deck. As the aircraft turns onto the runway, the pilots advance the engine thrust to takeoff power. The engine s high stage compresses the air to 650°C and 2965 kPa. This energy level exceeds the requirements for the air-conditioning packs and other pneumatic services; approximately 50% of the total energy available at the high-stage port cannot be used, so the bleed system automatically switches to the low-stage port to conserve energy. Because the engine must cope with widely varying conditions from ground level to flight at an altitude of up to 13 140 m, during all seasons and throughout the world, air at the high or low stage of the engine compressor seldom exactly matches the pneumatic sys- tems' needs. Excess energy must be discarded as waste heat. The bleed system constantly monitors engine conditions and selects the least wasteful port. Even so, bleed port temperatures often exceed fuel auto-ignition temperatures. The precooler automatically dis- charges excess energy to the atmosphere to ensure that the tempera- ture of the pneumatic manifold is well below that which could ignite fuel in the event of a fuel leak. The aircraft climbs to a cruise altitude of 11 900 m, where the outside air temperature is -57°C at an atmospheric pressure of 20 kPa, and the partial pressure of oxygen is 4 kPa. Until the start of descent to Los Angeles, the low-stage compressor is able to compress the low-pressure cold outdoor air to more than 210 kPa and above 200°C. This conditioning of the air is all accomplished through the heat of compression: fuel is added only after the air has passed through the compressor stages of the engine core. Figure 13 shows the temperature of the air leaving the bleed system (labeled "to airplane" in Figure 10) from the time of depar- ture to the time of arrival at Los Angeles. The air then passes through an ozone converter on its way to the air-conditioning packs located under the wing at the center of the aircraft. Ozone Protection While flying at 11 900 m, several ozone plumes are encountered. Some have ozone concentrations as high as 0.8 ppm, or 0.62 ppm sea-level equivalent (SLE). This assumes a worst-case flight during the month of April, when ozone concentrations are highest. If this concentration of ozone were introduced into the cabin, passengers and crew could experience chest pain, coughing, shortness of breath, fatigue, headache, nasal congestion, and eye irritation. Atmospheric ozone dissociation occurs when ozone goes through the compressor stages of the engine, the ozone catalytic converter (which is on aircraft with a route structure that can encounter high ozone concentrations), and the air-conditioning packs. The ozone further dissociates when contacting ducts, interior surfaces, and the Chart Type: line CLIMB CRUISE 10700 m CRUISE 12200 m DESCENT item_01 290°C 220°C 210°C 160°C Fig. 13 Bleed Air Temperatures recirculation system. The ozone converter dissociates ozone to oxygen molecules by using a noble catalyst such as palladium. A new converter dissociates approximately 95% ofthe ozone entering the converter to oxygen. It has a useful life of about 12 000 flight hours. As the air leaves the ozone converter, itis still at 204°C and a pres- sure of 207 kPa. Assuming a worst case when the converter is ap- proaching the end of its useful life, with an ozone conversion efficiency of 60%, the ozone concentration leaving the converter is about 0.25 ppm SLE. This air goes through the air-conditioning packs and enters the cabin. The ozone concentration in the cabin is about 0.09 ppm. As mentioned in the section on Regulations, the FAA sets a 3 h time-weighted average ozone concentration limit in the cabin of 0.1 ppm and a peak ozone concentration limit of 0.25 ppm. Air Conditioning and Temperature Control Air next enters the air-conditioning packs, which provide es- sentially dry, sterile, and dust-free conditioned air to the airplane cabin at the proper temperature, flow rate, and pressure to satisfy pressurization and temperature control requirements. For most aircraft, this is approximately 2.4 L/s per passenger. To ensure re- dundancy, typically two (or more) air-conditioning packs provide a total of about 4.8 L/s of conditioned air per passenger. An equal quantity of filtered, recirculated air is mixed with air from the air- conditioning packs for a total of approximately 9.5 L/s per passen- ger. Automatic control for the air-conditioning packs constantly monitors airplane flight parameters, the flight crew's selection for temperature zones, cabin zone temperature, and mixed distribu- tion air temperature. The control automatically adjusts the various valves for a comfortable environment under normal conditions. The pilot's controls are located on the overhead panel in the flight deck, along with the bleed system controls. Normally, pilots are required only to periodically monitor the compartment tempera- tures from the overhead panel. Temperatures can be adjusted based on flight attendant reports of passengers being too hot or too cold. Various selections are available to the pilots to accommodate abnormal operational situations. Air Recirculation The air has now been cooled and leaves the air-conditioning packs. It leaves the packs at 16°C and 81 kPa. The relative humidity is less than 1% and ozone concentration is less than 0.25 ppm. The Inc. ASHRAE, 2019 user. single for Licensed | {}
79aa0edf-8d97-4f6a-9f06-ff22048884c9 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Aircraft 13.13 carbon dioxide concentration remains unchanged from that of the outside air at about 350 ppm. As this air enters a mixing chamber, it is combined with recirculated air. The recirculated air is filtered before entering the mix manifold. Over 99.9% of the bacteria and viruses that reach the recirculation filters are removed from recirculated air by HEPA filters, which are used on most modern aircraft. Air Distribution The filtered and bleed air mixture leaves the mixing chamber on its way through the air distribution system. At this time, its humidity has increased relative to bleed air by about 5 to 10% rh. The tem- perature of the mixture is determined by the cooling requirements of the dominant zone. Control for the remaining zones is achieved by adding hot air to the zone supply. The hot-air source is the same bleed supply as the packs, so very small amounts of air are required to adjust the temperature. Carbon dioxide levels in the distribution system are about half- way between the levels in bleed air and in the cabin. At a 1830 m cabin altitude, the level is about 1000 ppm in the distribution system. The mixture leaves the air distribution system and enters the cabin through high-velocity diffusers. The diffusers run the length of the cabin. In order to minimize fore-to-aft flow and mixing between zones, flow is provided at a uniform amount per unit length of cabin. Even though the air change rates are high compared to buildings, they are low when looking at the plug flow velocity. If ventilation air were provided uniformly across the cabin, as in plug flow, the veloc- ity would be less than 0.025 m/s. Momentum from the diffusers increases velocity up to comfortable levels of 0.08 to 0.33 m/s. Once the air mixes with the air in the cabin, the humidity rises by another 5 to 10% rh to stabilize at 10 to 20% rh, and the carbon dioxide level rests at about 1700 ppm (at 1830 m cabin altitude). Cabin Pressure Control The cabin pressure control system continuously monitors ground and flight modes, altitude, climb, cruise or descent modes, and the airplane's holding patterns at various altitudes. It uses this informa- tion to position the cabin pressure outflow valve to maintain cabin pressure as close to sea level as practical, without exceeding a cabin- to-outside pressure differential of 59.3 kPa. At a 11 900 m cruise altitude, the cabin pressure is equivalent to 2100 m or a pressure of 80 kPa. In addition, the outflow valve repositions itself to allow more or less air to escape as the airplane changes altitude. The resulting cabin altitude is consistent with airplane altitude within the constraints of keeping pressure changes comfortable for passengers. The cabin pressure control system panel is located in the pilot's overhead panel near the other air-conditioning controls. Normally, the cabin pressure control system is totally automatic, requiring no attention from the pilots. Finally, as descent to LAX begins, the cabin pressure controller follows a prescribed schedule for repressurization. The cabin alti- tude eventually reaches sea level, the doors can then be opened at the gate, and passengers depart. 3. AIR QUALITY Factors Affecting Perceived Air Quality Several factors can influence comfort and perceived cabin air quality. These cabin environmental parameters, in combination with maintenance-, operations-, individual-, and job-related factors, col- lectively influence the cabin crew and passenger perceptions of the cabin environment. Cabin environmental quality (CEQ) must be differentiated from cabin air quality (CAQ), because many symp- toms, such as eye irritation, for example, may be caused by humidity (CEQ) as well as contaminants (CAQ). Chart Type: pie AIR QUALITY AIRPLAVERY MINUFACTURERS PHIJECT MULTIPLE FACTORS OPERATIONS item_01 25% 15% 10% 10% 5% 5% Fig. 14 Multiple Comfort Factors (Adapted, with permission, from STP 1393-Air Quality and Comfort in Airliner Cabins, copyright ASTM International, 100 Barr Harbor Drive, West Conshohocken, PA 19428) Strictly, air quality is a measure of pollutant levels. Aircraft cabin air quality is function of many variables including: the quantity of ventilation flow, ambient air quality, the design of the cabin volume, the design ofthe ventilation and pressurization systems, the way the systems are operated and maintained, the presence of sources of contaminants, and the strength of such sources. Figure 14 depicts the three groups that can influence cabin envi- ronmental quality: manufacturers, airlines, and the occupants them- selves. Airplane manufacturers influence the physical environment by the design ofthe environmental control system integrated with the rest of the systems on the airplane. Airlines affect the environmental conditions in the cabin by seating configuration, amenities offered, and procedures for maintaining and operating the aircraft. Finally, cabin environmental comfort is influenced by the individual and job- related activities of the cabin crew and passengers. Factors that can individually or collectively affect aircraft cabin air quality are discussed in the following sections. Airflow The airflow per unit length of the airplane is typically the same for all sections. However, economy class has a lower airflow per passenger because of its greater seating density compared to first class and business class. The flight deck is provided with a higher airflow per person than the cabin in order to (1) maintain a positive pressure in the cockpit to prevent smoke ingress from adjacent areas (abnormal condition), (2) provide cooling for electrical equipment, and (3) account for increased solar loads and night heat loss through the airplane skin and windows. The bleed or outdoor air quantity supplied on some aircraft mod- els can be reduced by shutting off one air-conditioning pack. The flight crew has control of these packs to provide flexibility in case of a system failure or for special use of the aircraft. However, packs should be in full operation whenever passengers are on board. Air Changes Confusion abounds over the use of air exchange rate (also called "air change rate") when making comparisons between dissimilar systems. Further, there is no air quality equivalence in the compar- Inc. ASHRAE, 2019 user. single for Licensed | {}
ac30b353-9bc1-49f3-b8fa-b33fc4f0f0ac | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 13.14 ison of systems unless the occupied volumes are equal. This is be- cause high air exchange rates can be achieved in two ways. As airflow increases, the air change rate increases; however, as volume decreases, the air change rate also increases but without a propor- tionate increase in air quality. Air exchange rate is the ratio of ven- tilation flow to volume: 0 ACR = V where ACR = air change rate, h-1 0 = flow, m3/h V = volume, m3 A close inspection of the definition reveals the subtle relation- ship between air quality c= q/Q (steady state) and air exchange rate: c = Air quality = q/(ACR)V where c = contaminant levels 9 = contaminant generation rate It is incorrect to assume that a smaller, single-aisle aircraft has better air quality than a larger, double-aisle aircraft simply because the air exchange rate is higher. Similarly, comparisons of buildings are in error. Remember, air quality is related to flow, which is the product of air change and volume. The air exchange rate (bleed air to volume ratio) for an airplane cabin is typically between 1 1 and 15 ach [air changes per hour (ACH)]. Dilution rates for these air changes are between 25 and 18 min for replacement of99% of the air. The particulate equivalent of an air exchange rate (total ventilation to volume ratio, where total ventilation = bleed + HEPA filtered recirculation) is between 20 and 30 equivalent air changes per hour. Ozone Inc. ASHRAE, 2019 user. single for Licensed Ozone is present in the atmosphere as a consequence of the pho- tochemical conversion of oxygen by solar ultraviolet radiation. Ozone levels vary with season, altitude, latitude, and weather sys- tems. A marked and progressive increase in ozone concentration occurs in the flight altitude of commercial aircraft. The mean ambi- ent ozone concentration increases with increasing latitude, is max- imal during the spring (fall season for southern latitudes), and often varies when weather causes high ozone plumes to descend. Residual cabin ozone concentration is a function of the ambient concentration; design, operation, and maintenance of the air distri- bution system; and whether catalytic ozone converters are installed. Cabin ozone limits are set by FAR Standards 121.578 and 25.832. Catalytic ozone converters are generally required on air- planes flying mission profiles where the cabin ozone levels are predicted to exceed these limits (refer to the FAA Code of Federal Regulations for other compliance methods). Microbial Aerosols Biologically derived particles that become airborne include viruses, bacteria, actinomycetes, fungal spores and hyphae, arthro- pod fragments and droppings, and animal and human dander. One study has documented the occurrence of an outbreak of infectious disease related to airplane use. In 1977, because of an engine mal- function, an airliner with 54 persons onboard was delayed on the ground for 3 h, during which the airplane ventilation system was reportedly turned off. Within 3 days of the incident, 72% of the pas- sengers became ill with influenza. One passenger (the index case) was ill while the airplane was delayed. With the ventilation system shut off, no bleed air was introduced into the cabin to dilute micro- bial aerosols and CO2 or to control cabin temperatures. 2019 ASHRAE Handbook-HVAC Applications (SI) The airplane ventilation system should never be shut off when passengers are on board, although the air packs (but not recircula- tion fans) may be shut off for a short time during takeoff only. To remove particulates and biological particles from the recircu- lated air, use filter assemblies that contain a HEPA filter with a min- imum efficiency of 99.97% on a dioctyl phthalate (DOP) test, as measured by MIL-STD-282. A HEPA filter is rated using 0.3 um size particles. A filter' s efficiency increases over time as particulates become trapped by the filter. However, system performance de- grades because of increased pressure drop. Overlapping capture mechanisms in a filter also increase efficiency for particles smaller and larger than the most penetrating particle size (MPPS). For an airplane filter, the MPPS is about 0.1 to 0.2 �m. Viruses typically range from about 0.01 to 0.2 �m, and are ef- fectively removed by the air filtration mechanism of diffusional interception. Bacteria are typically about 0.5 to 1.5 um, and are ef- fectively removed by inertial impaction. Activity Levels Respiratory rates (also called minute ventilation) and, hence, air contaminant doses vary with activity level. Elevated activity levels increase respiration rate, and thereby may increase the dose of some airborne contaminants. Breathing rates range from approximately 0.14 L/s for a seated passenger to 0.28 L/s for a working flight atten- dant. Volatile organic compounds (VOCs) can be emitted by material used in furnishings, pesticides, disinfectants, cleaning fluids, and food and beverages. v olatile Organic Compounds Carbon Dioxide Carbon dioxide is the product of normal human metabolism, which is CO2 's predominant source in aircraft cabins. Concentra- tion in the cabin varies with bleed-air flow rate, number of people present, and their individual rates of CO2 production, which vary with activity and, to a smaller degree, with diet and health. CO2 has been widely used as an indicator of indoor air quality, typically serving the function of a surrogate. According to the DOT (1989), measured cabin CO2 values of 92 randomly selected smoking and nonsmoking flights averaged 1500 ppm. 4. REGULATIONS The environmental exposure limit adopted by the Association of German Engineers (VDI 2004) and the American Conference of Governmental Industrial Hygienists (ACGIH) is 5000 ppm as the time-weighted average (TW A) limit for CO2; this value corre- sponds to a bleed air ventilation rate of about 1.1 L/s per person at sea level, if the only source of CO2 is the occupants at rest. Other sources of CO2 within the cabin or cargo (e.g., dry ice) would of course require more ventilation. 14CFR/CS/JAR 25.831 also lim- its CO2 to 5000 ppm (0.5%). The Federal Aviation Administration (FAA) regulates the design of transport category aircraft for operation in the United States under section 14 of the Code of Federal Regulation (CFR) Part 25 (com- monly referred to as the Federal Aviation Regulations [FARs]). ECS equipment and systems must meet these requirements, which are pri- marily related to safety of the occupants. Certification and operation of these aircraft in the United States is regulated by the FAA in FAR Part 121. Similar regulations are applied to European nations by the European Aviation Safety Agency (EASA), which represents the combined requirements of the airworthiness authorities of the partic- ipating nations; the current equivalent design regulation is Certifica- tion Specification (CS) 25, although many airplanes were designed and certified to the former Joint Aviation Regulations (JARs) Part 25. Operating rules based on FAA or EASA regulations are applied in- | {}
63e42821-d0d9-479c-90da-dd2255170e74 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Aircraft 13.15 dividually by the nation ofregistry. Regulatory agencies may impose special conditions on the design, and compliance is mandatory. Several 14 CFR and CS/JAR Part 25 paragraphs apply directly to transport category aircraft ECS. Those most germane to the ECS design requirements of this chapter are as follows: · 14CFR/CS/JAR 25.831 Ventilation · 14CFR/CS 25.832 Cabin ozone concentration · 14CFR/CS/JAR 25.841 Pressurized cabins · 14CFR/CS/JAR 25.1301 Function and installation · 14CFR/CS/JAR 25.1309 Equipment, systems, and installations · 14CFR/CS/JAR 25.1438 Pressurization and pneumatic systems · 14CFR/CS/JAR 25.1461 Equipment containing high energy rotors These regulatory requirements are summarized in the following sections; however, the applicable FAR, CS and JAR paragraphs, amendments and advisory material should be consulted for the latest revisions and full extent of the rules. 14 CFR/CS/JAR Paragraph 25.831: Ventilation · Each passenger and crew compartment must be ventilated. · Each crew member must have enough bleed air to perform their duties without undue fatigue or discomfort (minimum of 4.8 L/s). · Crew and passenger compartment air must be free from hazard- ous concentration of gases and vapors: · CO limit is 1 part in 20 000 parts of air · CO2 limit is 0.5% by volume, sea level equivalent. Many air- planes were designed/certified to a carbon dioxide limit of 3% by volume (the former requirement) · CO and CO2 limits must be met after reasonably probable failures · Smoke evacuation from the cockpit must be readily accomplished without depressurization. · Occupants of the flight deck, crew rest area, and other isolated areas must be able to control the temperature and quantity of ven- tilating air to their compartments independently. 14 CFR 25.831, Amendment 25-87 (specifies new requirements) · Under normal operating conditions, the ventilation system must be designed to provide each occupant with airflow containing at least 0.25 kg of bleed air per minute (or about 4.8 L/s at 2440 m). · The maximum exposure at any given temperature is specified as a function of the temperature exposure. FAA Advisory Circular (AC) 25-20/ Acceptable Means of Compliance/Advisory Circular-Joint 25.831 · The ventilation system should be designed to provide enough fresh air to prevent accumulation of odors and pollutants such as carbon dioxide. · In the event of loss of one source or probable failure conditions, the supply of bleed air should not be less than 0.25 kg/min per person for any period exceeding 5 min. This is derived from the ventilation rate procedure of ASHRAE Standard 62-1981. How- ever, temporary reductions below this flow rate may be accepted if the compartment environment can be maintained at a level that is not hazardous to the occupant. 14 CFR/CS 25.832: Cabin Ozone Concentration Specifies the cabin ozone concentration during flight must be shown not to exceed the following: · 0.25 ppm by volume, sea level equivalent, at any time above flight level 320 (9750 m) · 0.10 ppm by volume, sea level equivalent, time-weighted average during any 3 h interval above flight level 270 (8230 m) At present, JAR 25 has no requirement for cabin ozone concen- tration. 14 CFR/CS/JAR 25.841: Pressurized Cabins · Maximum cabin pressure altitude is limited to 2440 m at the max- imum aircraft operating altitude under normal operating condi- tions. · For operation above 7620 m, a cabin pressure altitude of not more than 4570 m must be maintained in the event of any reasonably probable failure or malfunction in the pressurization system. · The makeup of the cabin pressure control components, instru- ments, and warning indication is specified to ensure the necessary redundancy and flight crew information. 14 CFR Amendment 25-87 This revision imposes additional rules for high-altitude operation. 14 CFR/CS/JAR 25.1301: Function and Installation Each item of installed equipment must be of a kind and design appropriate to its intended function, be properly labeled, be installed according to limitations specified for that equipment, and function properly. 14 CFR/CS/JAR 25.1309: Equipment, Systems, and Installations · Systems and associated components must be designed such that any failure that would prevent continued safe flight and landing is extremely improbable, and any other failure that reduces the abil- ity of the aircraft or crew to cope with adverse operating condi- tions is improbable. · Warning information must be provided to alert the crew to unsafe system operating conditions so they can take corrective action. · Analysis in compliance with these requirements must consider possible failure modes, probability of multiple failures, unde- tected failures, current operating condition, crew warning, and fault detection. FAR Advisory Circular AC 25.1309-1A, CS AMJ 25.1309, and JAR ACJs 1 to 25.1309 define the required failure probabilities for the various failure classifications: probable, improbable, and ex- tremely improbable for the FAR requirements; and frequent, rea- sonably probable, remote, and extremely remote for the CS/JAR requirements. 14 CFR/CS 25.1438: Pressurization and Pneumatic Systems This standard specifies the proof and burst pressure factors for pressurization and pneumatic systems as follows: · · Pressurization system elements · Proof pressure: 1.5 times max normal pressure · Burst pressure: 2.0 times maximum normal pressure Pneumatic system elements · Proof pressure: 1.5 times maximum normal pressure · Burst pressure: 3.0 times maximum normal pressure CS/JAR 25.1438 and AMJ/ACJ 25.1438 specify the proof and burst pressure factors for pressurization and pneumatic systems as follows: · Proof pressure Inc. ASHRAE, 2019 user. single for Licensed · 1.5 times worst normal operation · 1.33 times worst reasonable probable failure · 1.0 times worst remote failure | {}
612fcb92-12ee-43d6-9d73-1a577273a832 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 13.16 2019 ASHRAE Handbook-HVAC Applications (SI) · Burst pressure · 3.0 times worst normal operation · 2.66 times worst reasonably probable failure · 2.0 times worst remote failure · 1.0 times worst extremely remote failure 14 CFR/CS/JAR 25.1461: Equipment Containing High-Energy Rotors Equipment must comply with at least one of the following three requirements: · High-energy rotors contained in equipment must be able to with- stand damage caused by malfunctions, vibration, and abnormal temperatures. · Auxiliary rotor cases must be able to contain damage caused by high-energy rotor blades. · Equipment control devices must reasonably ensure that oper- ating limitations affecting the integrity of high-energy rotors will not be exceeded in service. · Testing must show that equipment containing high-energy rotors can contain any failure that occurs at the highest speed attainable with normal speed control devices inoperative. · Equipment containing high-energy rotors must be located where rotor failure will neither endanger the occupants nor adversely affect continued safe flight. Categories and Definitions Commercial users categorize their ECS equipment in accordance with the Air Transport Association of America (ATAA) Specifica- tion 100. The following ATAA chapters define ECS functions and components: · Chapter 21, Air Conditioning, discusses heating, cooling, moisture/ contaminant control, temperature control, distribution, and cabin pressure control. Common system names are the air-conditioning system (ACS) and the cabin pressure control system (CPCS). · Chapter 30, Ice and Rain Protection, covers airfoil ice protection; engine cowl ice protection; and windshield ice, frost, or rain pro- tection. · Chapter 35, Oxygen, includes components that store, regulate, and deliver oxygen to the passengers and crew. · Chapter 36, Pneumatic, covers ducts and components that deliver compressed (bleed) air from a power source (main engine or aux- iliary power unit) to connecting points for the using systems (which are detailed in Chapters 21, 30, and 80). The pneumatic system is also commonly called the engine bleed air system (EBAS). REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. ACGIH. Annual. TLVsⓇ and BEIsⓇ. American Conference of Governmen- tal Industrial Hygienists, Cincinnati, OH. ATAA. (no date). Specification for manufacturers technical data. Specifi- cation 100. Air Transport Association of America, Washington, D.C. ASHRAE. 2017. Thermal environmental conditions for human occupancy. ANSI/ASHRAE Standard 55-2017. ASHRAE. 2018. Air quality within commercial aircraft. ANSI/ASHRAE Standard 161-2018. ASHRAE. 2018. Ventilation for acceptable indoor air quality. ANSI/ ASHRAE Standard 62.1-2018. CEN. 2017. High efficiency air filters (EPA, HEPA and ULPA)-Part 1: Classification, performance testing, marking. European Committee for Standardization, Brussels. CFR. (annual). Aeronautics and space: Airworthiness standards: Transport category airplanes: Ventilation. 14CFR/CS/JAR 25.831. Code of Fed- eral Regulations, U.S. Government Printing Office, Washington, D.C. www.ecfr.gov. DOT. 1989. Airliner cabin environment: Contaminant measurements, health risks, and mitigation options. U.S. Department of Transportation, Wash- ington, D.C. EASA. 2003.Large aeroplanes. Certification Specification CS 25. Euro- pean Aviation Safety Agency, Cologne, Germany. FAA. 1996. Pressurization, ventilation, and oxygen systems for subsonic flight, including high altitude operation. Advisory Circular AC 25-20. Federal Aviation Administration, Washington, D.C. www.ecfr.gov. FAA. 2011. Airworthiness standards: Transport category airplanes. Fed- eral Aviation Regulations, 14 CFR Part 25. Advisory Circular AC 25- 20. Federal Aviation Administration, Washington, D.C. www.ecfr.gov. FAA. 2011. Certification and operations: Domestic, flag and supplemental air carriers and commercial operators of large aircraft. Federal Aviation Regulations, 14 CFR Part 121. Advisory Circular AC 25-20. Federal Aviation Administration, Washington, D.C. www.ecfr.gov. IEST. 2017. HEPA and ULPA filters. Recommended Practice IEST-RP- CC001.6. Institute of Environmental Sciences and Technology, Arling- ton Heights, IL. ISO. 2017. High efficiency filters and filter media for removing particles from air-Part 1: Classification, performance, testing and marking. Standard 29463-1. International Organization for Standardization, Geneva. Lin, C.H., R. Horstman, M.F. Ahlers, L.M. Sedgwick, K.H. Dunn, J.L. Topmiller, J.S. Bennett, and S. Wirogo. 2005. Numerical simulation of airflow and airborne pathogen transport in aircraft cabins-Part I: Numerical simulation of the flow field. ASHRAE Transactions 111(1): 755-763. NAS. 1986. The airliner cabin environment: Air quality and safety. Na- tional Academy of Sciences, National Academy Press, Washington, D.C. NAS. 2002. The airliner cabin environment and the health of passengers and crew. National Academy of Sciences, National Academy Press, Washington, D.C. Owens, D.F., and A.T. Rossano. 1969. Design procedures to control ciga- rette smoke and other air pollutants. ASHRAE Transactions 75(1):93- 102. VDI. 2004. Hygiene standards for ventilation technology in passenger vehicles. VDI Guideline 6032. Verein Deutscher Ingenieure (Associa- tion of German Engineers), Dusseldorf. BIBLIOGRAPHY ATAA. 1994. Airline cabin air quality study. Air Transport Association of America, Washington, D.C. Space, D.R., R.A. Johnson, W.L. Rankin, and N.L. Nagda. 2000. The air- plane cabin environment: Past, present and future research. In Air Quali- ty and Comfort in Airliner Cabins, ASTM STP 1393, N.L. Nagda, ed. American Society for Testing and Materials, West Conshohocken, PA. Thibeault, C. 1997. Special committee report on cabin air quality. Aero- space Medical Association, Alexandria, VA. Walkinshaw, D.S. 2001. Investigating the impacts of occupancy density & ventilation on IAQ in offices, classrooms and aircraft. Seminar present- ed at 2001 ASHRAE Annual Meeting. Washington State Department of Health. 2007. Indoor air quality. www.doh . wa.gov Potais/I/Docurnens 5500VEH-IMAQCT.pdf Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
3ce75a34-401d-4d76-9e15-6300436bddce | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 14 SHIPS Merchant Ships 14.1 Naval Surface Ships 14.3 T vessels, including naval ships, commercial vessels, fishing HIS chapter covers air conditioning for oceangoing surface boats, luxury liners, pleasure craft, and inland and coastal boats, as well as oil rigs. Although the general principles of air conditioning for land installations also apply to marine applications, factors such as weight, size, fire protection, smoke control, and corrosion resis- tance take on greater importance, and new factors (e.g., tolerance for pitch and roll, shipboard vibration, watertightness) come into play. The importance of shipboard air conditioning depends on a ship 's mission. On passenger vessels that focus completely on passenger comfort, such as cruise ships and casino vessels, air conditioning is vital and a significant energy consumer. Aboard commercial vessels (tankers, bulkers, container ships, etc.), air conditioning provides an environment in which personnel can live and work without heat stress. Shipboard air conditioning also improves reliability of elec- tronic and other critical equipment, as well as weapons systems aboard naval ships. Air conditioning on oil rigs serves the same purpose as with commercial vessels (i.e., providing a suitable envi- ronment for workers), and for larger rigs with significant accommo- dation areas, the amount of cooling can be substantial, similar to passenger vessels. Oil rig applications also introduce the additional consideration of operating within areas classified as hazardous. This chapter discusses merchant ships, which includes passenger and commercial vessels, and naval surface ships. In general, the details of merchant ship air conditioning also apply to warships. However, all ships are governed by their specific ship specifications, and warships are often also governed by military specifications, which ensure air-conditioning system and equipment performance in the extreme environment of warship duty. 1. MERCHANT SHIPS Load Calculations The cooling load estimate considers the following factors (dis- cussed in Chapter 18 of the 2017 ASHRAE Handbook-Fundamen- tals): · Solar radiation · Heat transmission through hull, decks, and bulkheads · Heat (latent and sensible) dissipation from occupants · Heat gain from lights · Heat (latent and sensible) gain from ventilation air · Heat gain from motors or other electrical equipment · Heat gain from piping, machinery, and equipment The heating load estimate should include the following: · Heat losses through decks and bulkheads · Ventilation air · Infiltration (when specified) In addition, the construction and transient nature of ships present some complications, as addressed in the following: SN AME. The Society ofNaval Architects and Marine Engineers (SNAME 2015) Technical and Research Bulletin 4-16 can be used as a guide for shipboard load calculations. The preparation of this chapter is assigned to TC 9.3, Transportation Air Conditioning. ISO. The International Organization for Standardization 's (ISO) Standard 7547 discusses design conditions and calculations for marine HVAC systems. Outdoor Ambient Temperature and Humidity. The service and type of vessel determine the proper outdoor design temperature, which should be based on temperatures prevalent in a ship , s area of operation. Use Chapter 14 of the 2017 ASHRAE Handbook-Funda- mentals to select ambient conditions, with special attention paid to high-wet-bulb data; a ship 's load is often driven by the latent load associated with the outdoor air. It is also common for different loca- tions to be used for cooling and heating criteria. In general, for cool- ing, outdoor design conditions are 35°C db and 25.5°C wb; for semitropical runs, 35°C db and 26.5°C wb; and for tropical runs, 35°C db and 28°C wb. For heating, -18°C is usually the design tem- perature, unless the vessel will always operate in warmer climates. Design temperatures for seawater are 32°C in summer and -2°C in winter. Solar Gain. Ships require special consideration for solar gain be- cause (1) they do not constantly face in one direction and (2) the re- flective properties of water increase solar load on outer boundaries not directly exposed to sunlight. For compartments with only one exterior boundary, the temperature difference (outdoor dry-bulb temperature - indoor dry-bulb temperature) across horizontal surfaces should be in- creased by 28 K and vertical surfaces by 17 K. For compartments with more than one exterior boundary, the temperature difference should be increased by 19 K for horizontal surfaces and 11 K for vertical sur- faces. For glass surfaces, the solar cooling load (SCL) is taken to be 500 W/m2 for spaces with one exterior boundary and 380 W/m2 for spaces with more than one exterior boundary. A more modern ap- proach is to use appropriate building energy simulation software (a full list of which is maintained by the U.S. Department of Energy) to mod- el the ship ' s accommodation spaces. These programs generally allow building exposure to be changed globally, making it easy to examine the change in ship loads as the route direction changes. Infiltration. Infiltration through weather doors is generally dis- regarded. However, specifications for merchant ships occasionally require an assumed infiltration load for heating steering gear rooms and the pilothouse. Transmission Between Spaces. For heating loads, heat trans- mission through boundaries of machinery spaces in either direction is not of consequence. Allowances are not made for heat gain from warmer adjacent spaces. For cooling loads, the cooling effect of ad- jacent spaces is not considered unless temperatures are maintained with refrigeration or air-conditioning equipment. Ventilation Requirements. Ventilation is a very important con- sideration, because it is frequently the main contributor to overall energy usage of the system. Rules and guidance are provided by con- flicting standards, including ISO Standard 7547, SNAME Technical and Research Bulletin 4-16, and ASHRAE Standard 62.1-2016. UI- timately, that stated in the ship ' s specification and what is acceptable to the authority having jurisdiction (AHJ) govern ventilation require- ments. However, given the opportunity to reduce energy (fuel) con- sumption and the need to ensure passenger health and safety, it behooves the system designer to apply modern tools, such as building energy simulation and demand-controlled ventilation to optimize the quantity of fresh air introduced under all conditions. There is a unique 14.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
1e00fc13-8e60-407d-8ddb-aced7c2eeb38 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 14.2 2019 ASHRAE Handbook-HVAC Applications (SI) opportunity for fresh-air optimization aboard ships because the number of passengers is fixed and each person can only be in one lo- cation at a time. Significant overventilation that can occur by cater- ing to the maximum fresh-air requirement in each space simultaneously. Heat Transmission Coefficients. The overall heat transmission coefficients U for the composite structures common to shipboard construction do not lend themselves to theoretical derivation; they are usually obtained from full-scale panel tests. SNAME Bulletin 4-7 gives a method to determine these coefficients when tested data are unavailable. ISO Standard 7547 also gives some guidance in this area, as well as default values if better information is not available. Indoor Air Temperature and Humidity. Thermal environmental conditions for human occupancy are given in ASHRAE Standard 55-2017. People. Ships normally carry a fixed number of people. The en- gineer must select the location where the ship's fixed complement of people creates the greatest heat load, and then not apply the people load elsewhere. Note that occupants are only counted once when determining the chiller or condensing-unit load; however, air coils in each zone must be capable of removing the heat load asso- ciated with the maximum number of people in the zone. Ventilation in the zone can also be reduced when occupants are not present. For the ventilation load, occupants are counted once, in the location where they create the greatest ventilation requirement. The practical way to apply this concept is by measuring CO2 levels in a space and adjusting outdoor air accordingly. Although using this principle can reduce required chiller or condensing-unit capac- ity on all ships, it is most significant for passenger ships. Equipment In general, equipment used for ships is much more rugged than that used on land. Sections 6 through 10 of ASHRAE Standard 26 list HV AC equipment requirements for marine applications. When selecting marine duty air-conditioning equipment, consider the fol- lowing: · It should function properly under dynamic roll and pitch and static trim and heel conditions. This is especially important for compressor oil sumps, oil separators, refrigerant drainage from a condenser and receiver, accumulators, and condensate drainage from drain pans. · Construction materials should withstand the corrosive effects of salt air and seawater. Materials such as stainless steel, nickel- copper, copper-nickel, bronze alloys, and hot-dipped galvanized steel are used extensively. · It should be designed for uninterrupted operation during the voy- age and continuous year-round operation. Because ships en route cannot be easily serviced, some standby capacity, spare parts for all essential items, and extra oil and refrigerant charge should be carried. · It should have no objectionable noise or vibration, and must meet noise criteria required by the ship's specification. · It should occupy minimum space, commensurate with its cost and reliability. Mass should also be minimized. · A ship may pass through one or more complete cycles of seasons on a single voyage and may experience a change from winter to summer operation in a matter of hours. Systems should be flexible enough to compensate for climatic changes with minimal attention from the ship s crew. The following general items should be considered when selecting specific air conditioning components: Fans. Fans must be selected for stable performance over their full range of operation and should have adequate isolation to prevent transmitting vibration to the deck. Because fan rooms are often adja- cent to or near living quarters, effective sound treatment is essential. Cooling Coils. If more than 30% outdoor air is brought across a cooling coil, consider using copper tube, copper fin, epoxy-coated coils, or other special treatment. To account for the ship s move- ment, drain pans should have two drain connections, and should ide- ally be dual sloping, with extra depth. Because of size constraints, care must be taken to prevent moisture carryover. Face velocity limits (in m/s) for different coil materials and different fin spacing are as follows: ¦ Fin Spacing, mm ¦ Aluminum Fins ¦ Copper or Coated Fins ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 3.2 ¦ 2.8 ¦ 2.6 ¦ ¦ 2.3 ¦ 2.8 ¦ 2.1 ¦ ¦ 1.8 ¦ 2.8 ¦ 1.9 ¦ Off-coil temperatures are another concern. Ships typically have low ceiling heights and cannot tolerate low air-introduction tem- peratures. Typically 12.8°C db and 12.2°C wb are used as limiting off-coil temperatures. Electric Heaters. U.S. Coast Guard (USCG) approved sheathed- element heaters are typically required. The only exception is when the electric heaters, approved by a regulatory body such as UL, are incorporated in a packaged unit. Air Diffusers. Care must be taken with selection of air diffusers because of the low ceilings typical of shipboard applications. Air-Conditioning Compressors. Compressors of all types are used for marine applications. Care must be taken when using a cen- trifugal compressor because low-load, high-condensing tempera- ture is a common off-load condition. When high discharge temperatures are a concern, seawater- cooled heads are not normally an option; other methods such as fan cooling or liquid injection must be considered for maintaining acceptable discharge temperatures. Typical Systems All types of systems may be considered for each marine applica- tion. The systems are the same as in land applications; the difference is the relative weighting of their advantages and disadvantages for marine use. This section does not review all the systems used aboard ships, but rather some of the more common ones. Direct refrigerant cooling systems are often used for small, single-zone applications. Aboard ships, places like control rooms and pilot houses lend themselves to a direct refrigerant system. For larger spaces, air distribution is of more concern; direct refrigerant cooling is thus less likely to be the optimum solution. Two-pipe and four-pipe fan coil systems are often used for large systems. The water piping used in these systems takes up only a fraction of the space used by an all-air ducted system. Fan noise in the space being cooled is the disadvantage. In addition, limited hu- midity control and fresh-air requirements often need to be addressed separately. Many types of all-air systems are used aboard ships. Space, cost, noise, and complexity are among the leading parameters when comparing different all-air systems. Using high-velocity air distri- bution for an all-air system offers many advantages; unitary (factory- assembled) central air-handling equipment and prefabricated piping, clamps, and fittings facilitate installation for both new construction and conversions. Substantial space-saving is possible compared to conventional low-velocity sheet metal ducts. Maintenance is also reduced. Noise is the one major drawback ofa high-velocity system, which often leads to selection of a low-velocity system. Terminal reheat air conditioning (described in Chapter 4 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment) is com- monly used because of its simplicity and good zone control charac- teristics. However, as systems become larger, this system 's energy Inc. ASHRAE, 2019 user. single for Licensed | {}
a7e0e580-9e18-443e-a572-72c94d9931d8 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Ships 14.3 inefficiency becomes a significant drawback. For large passenger ships, where energy efficiency is absolutely essential, the designer should consider more modern approaches. One method is delivering tempered ventilation air from a central-station air handler to the pas- senger staterooms, each of which is outfitted with a dedicated cabin fan-coil unit, including a chilled-water-cooling and hot-water-heat- ing coil. The individual cabin is then either heated or cooled from a neutral temperature, using central loops, depending on specific needs. The efficiency of this approach is further improved by having reclaimed heat sources (e.g., from the central chillers or the main engine cooling system) to maintain the hot-water loop temperature. Dual-duct systems (also described in Chapter 4 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment) have the fol- lowing advantages: · All conditioning equipment is centrally located, simplifying maintenance and operation · Can heat and cool adjacent spaces simultaneously without cycle changeover and with minimum automatic controls · Because only air is distributed from fan rooms, no water or steam piping, electrical equipment, or wiring are in conditioned spaces The major drawback is the inability to finely control temperature and humidity. This disadvantage is enough to preclude the use of these systems in many passenger vessel applications. Aboard ships, constant-volume systems are most common. Their advantages include simplicity (for maintenance, operation, and repair) and low cost. However, for large passenger vessels, the energy efficiency and the tight control of zone temperature make variable-volume/temperature systems very attractive. Air Distribution Methods Good air distribution in staterooms and public spaces is difficult to achieve because of low ceiling heights and compact space ar- rangements. Design should consider room dimensions, ceiling height, volume of air handled, air temperature difference between supply and room air, location of berths, and allowable noise. For major installations, mock-up tests are often used to establish exacting performance criteria. Air usually returns from individual small spaces either by a sight- tight louver mounted in the door or by an undercut in the door leading to the passageway. An undercut door can only be used with air quantities of 35 L/s or less. Louvers are usually sized for face velocity of2 m/s based on free area. Ductwork on merchant ships is generally constructed of steel. Ducts, other than those requiring heavier construction because of susceptibility to damage or corrosion, are usually made with riveted seams sealed with hot solder or fire-resistant duct sealer, welded seams, or hooked seams and laps. They are made ofhot-dipped, gal- vanized, copper-bearing sheet steel, suitably stiffened externally. The minimum thickness of material is determined by the diameter of round ducts or by the largest dimension of rectangular ducts, as listed in Table 1. The increased use of high-velocity, high-pressure systems has resulted in greater use of prefabricated round pipe and fittings, including spiral-formed sheet metal ducts. It is important that field- fabricated ducts and fittings be airtight. Using factory-fabricated fittings, clamps, and joints effectively minimizes air leakage for these high-pressure ducts. In addition to the space advantage, small ductwork saves mass, another important consideration for this application. Control The conditioning load, even on a single voyage, varies over a wide range within short periods. Not only must the refrigeration plant meet these load variations, but the controls must readily adjust the system to sudden climatic changes. Accordingly, it is general prac- Table 1 Minimum Thickness of Steel Ducts ¦ All vertical exposed ducts ¦ 16 USSG ¦ 1.52 mm ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Horizontal or concealed vertical ducts ¦ Horizontal or concealed vertical ducts ¦ Horizontal or concealed vertical ducts ¦ ¦ less than 150 mm ¦ 24 USSG ¦ 0.62 mm ¦ ¦ 160 to 300 mm ¦ 22 USSG ¦ 0.76 mm ¦ ¦ 310 to 460 mm ¦ 20 USSG ¦ 0.91 mm ¦ ¦ 470 to 760 mm ¦ 18 USSG ¦ 1.21 mm ¦ ¦ over 760 mm ¦ 16 USSG ¦ 1.52 mm ¦ tice to equip the plant with automatic controls. Increasingly, fully communicating network controls are being applied to optimize oper- ation ofthe entire system under transient conditions. Moreover, such controls now can collect large amounts of operational data and offer proactive diagnostics based on these data, helping the ship operator maximize efficiency and reliability throughout the life cycle. Regulatory Agencies Merchant vessels that operate under the U.S. flag come under the jurisdiction of the U.S. Coast Guard. Accordingly, the installation and components must conform to the Marine Engineering Rules and Marine Standards of the Coast Guard covered under the Guide to Structural Fire Protection (USCG 2010). Certified pressure vessels and electric components approved by independent agencies (e.g., ASME, UL) must be used. Wherever possible, equipment used should comply with ABS rules and regula- tions. This is especially important when vessels are equipped for car- rying cargo refrigeration, because air-conditioning compressors may serve as standby units in the event of a cargo compressor failure. This compliance eliminates the need for a separate, spare cargo compres- sor. The International Convention for the Safety of Life at Sea (SOLAS) (IMO 2014) governs the use of fire-dampers and duct wall thickness when passageways or fire boundaries are crossed. 2. NAV AL SURFACE SHIPS Design Criteria Indoor Temperature. Naval ships are generally designed for space temperatures of 26.5°C db with a maximum of 55% rh for most areas requiring air conditioning. USN (1969) gives design conditions established for specific areas, and USMA (1965) lists temperatures for ventilated spaces. Outdoor Ambient Temperature. Design conditions for naval vessels have been established as a compromise, considering the large cooling plants required for internal heat loads generated by machinery, weapons, electronics, and personnel. Temperatures of 32°C db and 27°C wb are used for worldwide applications, with 29.5°C seawater temperatures. Heating-season temperatures are - 12°C for outdoor air and -2°C for seawater. Ventilation Requirements. As for merchant ships, there is con- flicting guidance regarding ventilation requirements; see ISO Stan- dard 7547, SNAME Technical and Research Bulletin 4-16, and ASHRAE Standard 62.1-2016. Ventilation must meet the require- ments of the ship s specification and the U.S. government, but as with merchant ships, the system designer should apply modern tools, such as building energy simulation and demand controlled ventilation, to optimize the quantity of fresh air introduced under all conditions, ensuring safe operation and technical justification. Air-Conditioned Spaces. Naval ship design requires that air- conditioning systems serving living and berthing areas on surface ships replenish air in accordance with damage control classifica- tions, as specified in USN (1969): · Class Z systems: 2.4 L/s per person · Class W systems for troop berthing areas: 2.4 L/s per person Inc. ASHRAE, 2019 user. single for Licensed | {}
d9a4133f-a216-4041-a8f4-d296f55aa703 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 14.4 2019 ASHRAE Handbook-HVAC Applications (SI) · All other Class W systems: 4.7 L/s per person. The flow rate is in- creased only to meet either a 35 L/s minimum branch requirement or to balance exhaust requirements. Outdoor air should be kept at a minimum to limit the size of the air-conditioning plant. Load Determination The cooling load estimate consists of coefficients from USN's Design Data Sheet DDS511-2, General Specifications for Building Naval Ships, or Document 0938-018-0010 (USN 1969) and has allowances for the following: · Solar radiation · Heat transmission through hull, decks, and bulkheads · Heat (latent and sensible) gain of occupants · Heat gain from lights · Heat (latent and sensible) gain from ventilation air · Heat gain from motors or other electrical equipment · Heat gain from piping, machinery, and equipment Loads should be derived from requirements indicated in USN (1969). The heating load estimate should include the following: · Heat losses through hull, decks, and bulkheads · Ventilation air · Infiltration (when specified) Some electronic spaces listed in USN (1969) require adding 15% to the calculated cooling load for future growth and using one-third of the cooling-season equipment heat dissipation (less the 15% added for growth) as heat gain in the heating season. Heat Transmission Coefficients. The overall heat transmission coefficient U between the conditioned space and the adjacent bound- ary should be estimated from USN's Design Data Sheet DDS511-2. Where new materials or constructions are used, new coefficients may be used from SNAME (2015) or calculated using methods found in DDS511-2 and SNAME. Heat Gain from People. USN (1969) gives heat gain values for people in various activities and room conditions. Heat Gain from Sources in the Space. USN (1969) gives heat gain from lights and motors driving ventilation equipment. Heat gain and use factors for other motors and electrical and electronic equipment may be obtained from the manufacturer or from Chapter 18 of the 2017 ASHRAE Handbook -Fundamentals. Inc. ASHRAE, 2019 user. single for Licensed Equipment Selection The equipment described for merchant ships also applies to U.S. naval vessels, except as follows: Fans. A family of standard fans is used by the navy, including vaneaxial, tubeaxial, and centrifugal fans. Selection curves used for system design are found on USN's NA VSEA Standard Draw- ings 810-921984, 810-925368, and 803-5001058. Manufacturers are required to furnish fans that are dimensionally identical to the standard plan and within 5% ofthe delivery. No belt-driven fans are included. Cooling Coils. The U.S. Navy uses eight standard sizes of direct- expansion and chilled-water cooling coils. All coils have eight rows in the direction of airflow, with a face area range of 0.06 to 0.93 m2. Coils are selected for a face velocity of 2.5 m/s maximum; how- ever, sizes 54 DW to 58 DW may have face velocity up to 3.2 m/s if the bottom of the duct on the discharge is sloped up at 15° for a dis- tance equal to the height of the coil. Construction and materials are specified in MIL-PRF-2939G. Chilled-water coils are most common and are selected based on 7.2°C inlet water with approximately a 3. 7 K rise in water tempera- ture through the coil. This is equivalent to 65 mL/s per kilowatt of cooling. Heating Coils. The standard naval steam and electric duct heaters have specifications as follows: Steam Duct Heaters · Maximum face velocity is 9.1 m/s. · Preheater leaving air temperature is 5.5 to 10°C. · Steam heaters are served from a 350 kPa (gage) steam system. Electric Duct Heaters · Maximum face velocity is 7.1 m/s. · Temperature rise through the heater is per MIL-PRF-22594C, but is in no case more than 27 K. · Power supply for the smallest heaters is 120 V, three-phase, 60 Hz. All remaining power supplies are 440 V, three-phase, 60 Hz. · Pressure drop through the heater must not exceed 85 Pa at 5 m/s. Use manufacturers' tested data in system design. Filters. Characteristics of the seven standard filter sizes used by the U.S. Navy are as follows: · Filters are available in steel or aluminum. · Filter face velocity is between 1.9 and 4.6 m/s. · A filter-cleaning station on board ship includes facilities to wash, oil, and drain filters. Air Diffusers. Although the U.S. Navy also uses standard dif- fusers for air conditioning, they are generally a commercial type similar to those used for merchant ships. Air-Conditioning Compressors. In the past, the U.S. Navy pri- marily used reciprocating compressors up to approximately 530 kW; for larger capacities, open, direct-drive centrifugal compressors are used. On new designs, the U.S. Navy primarily uses rotary compres- sors (e.g., screw and centrifugal), frequently semihermetic. R-134a is the U.S. Navy' s primary refrigerant. Seawater is used for con- denser cooling at 90 mL/s per kilowatt for reciprocal compressors and 72 mL/s per kilowatt for centrifugal compressors, but in all cases, the maximum seawater velocity of 1.8 m/s must be deferred to in order to prevent tube erosion. Typical Air Systems On naval ships, zone reheat is used for most applications. Some ships with sufficient electric power use low-velocity terminal reheat systems with electric heaters in the space. Some newer ships use a fan-coil unit with fan, chilled-water cooling coil, and electric heating coil in spaces with low to medium sensible heat per unit area of space requirements. The unit is supplemented by conventional systems serving spaces with high sensible or latent loads. Air Distribution Methods Methods used on naval ships are similar to those discussed in the section on Merchant Ships. The minimum thickness of materials for ducts is listed in Table 2. Control The navy' s principal air-conditioning control uses a two-position dual thermostat that controls a cooling coil and an electric or steam reheater. This thermostat can be set for summer operation and does not require resetting for winter operation. Steam preheaters use a regulating valve with (1) a weather bulb controlling approximately 25% of the valve's capacity to prevent freeze-up, and (2) a line bulb in the duct downstream of the heater to control the temperature between 5.5 and 10°C. Other controls are used to suit special needs. Pneumatic/electric controls can be used when close tolerances in temperature and humidity control are required, as in operating rooms. Thyristor con- trols are sometimes used on electric reheaters in ventilation systems. Modern ship designs use fully communicating networked con- trols that optimize system operation and provide useful data and feedback to the operator. The Navy is increasingly implementing energy-saving measures aboard all of its ships. | {}
3e456f51-2755-4161-a585-c12408948c99 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Ships 14.5 Table 2 Minimum Thickness of Materials for Ducts ¦ Sheet for Fabricated Ductwork ¦ Sheet for Fabricated Ductwork ¦ Sheet for Fabricated Ductwork ¦ Sheet for Fabricated Ductwork ¦ Sheet for Fabricated Ductwork ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ Non- Watertight ¦ Non- Watertight ¦ Watertight ¦ Watertight ¦ ¦ Diameter or Longer Side ¦ Galvanized Steel ¦ Aluminum ¦ Galvanized Steel ¦ Aluminum ¦ ¦ Up to 150 ¦ 0.46 ¦ 0.64 ¦ 1.90 ¦ 2.69 ¦ ¦ 160 to 300 ¦ 0.76 ¦ 1.02 ¦ 2.54 ¦ 3.56 ¦ ¦ 310 to 460 ¦ 0.91 ¦ 1.27 ¦ 3.00 ¦ 4.06 ¦ ¦ 470 to 760 ¦ 1.22 ¦ 1.52 ¦ 3.00 ¦ 4.06 ¦ ¦ Above 760 ¦ 1.52 ¦ 2.24 ¦ 3.00 ¦ 4.06 ¦ ¦ Welded or Seamless Aluminum Tubing ¦ Welded or Seamless Aluminum Tubing ¦ Welded or Seamless Aluminum Tubing ¦ Welded or Seamless Aluminum Tubing ¦ Welded or Seamless Aluminum Tubing ¦ ¦ Tubing Size ¦ Non-Watertight ¦ Non-Watertight ¦ Watertight ¦ Watertight ¦ ¦ 50 to 150 ¦ 0.89 ¦ 0.89 ¦ 2.69 ¦ 2.69 ¦ ¦ 160 to 300 ¦ 1.27 ¦ 1.27 ¦ 3.56 ¦ 3.56 ¦ ¦ Spirally Wound Duct (Non-Watertight) ¦ Spirally Wound Duct (Non-Watertight) ¦ Spirally Wound Duct (Non-Watertight) ¦ Spirally Wound Duct (Non-Watertight) ¦ Spirally Wound Duct (Non-Watertight) ¦ ¦ Diameter ¦ Steel ¦ Steel ¦ Aluminum ¦ Aluminum ¦ ¦ Up to 200 ¦ 0.46 ¦ 0.46 ¦ 0.64 ¦ 0.64 ¦ ¦ Over 200 ¦ 0.76 ¦ 0.76 ¦ 0.81 ¦ 0.81 ¦ Note: All dimensions in millimetres. REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. ASHRAE. 2010. Mechanical refrigeration and air conditioning installations aboard ship. ANSI/ASHRAE Standard 26-2010. ASHRAE. 2017. Thermal environmental conditions for human occupancy. ANSI/ASHRAE Standard 55-2017. ASHRAE. 2016. Ventilation for acceptable inside air quality. ANSI/ASHRAE Standard 62.1-2016. IMO. 2014. International convention for the safety of life at sea (SOLAS). International Maritime Organization, London. ISO. 2002. Ships and marine technology-Air-conditioning and ventilation of accommodation spaces-Design conditions and basis of calculations. Standard 7547-2002 (R2008). International Organization for Standard- ization, Geneva. SNAME. 1963. Thermal insulation report. Technical and Research Bulletin 4-7. Society ofNaval Architects and Marine Engineers, Jersey City, NJ. SNAME. 2015. Calculations for merchant ship heating, ventilation and air conditioning design. Technical and Research Bulletin 4-16. Society of Naval Architects and Marine Engineers, Jersey City, NJ. USCG. 2010. Guide to structural fire protection. Publication COMDT PUB 16700.4, NVIC 9-97, CHI. U.S. Department ofHomeland Security, U.S. Coast Guard, Washington, D.C. USMA. 1965. Standard specificationfor cargo ship construction. U.S. Mar- itime Administration, Washington, D.C. USN. 1969. The air conditioning, ventilation and heating design criteria manual for surface ships ofthe United States Navy. Document 0938-018- 0010. Naval Sea Systems Command, Department of the Navy, Washing- ton, D.C. USN. NAVSEA Drawing 810-921984, NAVSEA Drawing 810-925368, and NA VSEA Drawing 803-5001058. Naval Sea Systems Command, Department of the Navy, Washington, D.C. USN. Guidance in selection ofheat transfer coefficients. DDS511-2. Naval Sea Systems Washington, D.C. USN. General specifications for building naval ships. Naval Sea Systems Command, Department of the Navy, Washington, D.C. Note: MIL specifications are available from Commanding Officer, Naval Publications and Forms Center, ATTN: NPFC 105, 5801 Tabor Ave., Philadelphia, PA 19120. BIBLIOGRAPHY SNAME. 1992. Marine engineering. R. Harrington, ed. Society of Naval Architects and Marine Engineers, Jersey City, NJ. Orosa, J.A. 2010. Thermal comfort conditions in ships. Journal ofShip Pro- duction 26(1):60-65. Society of Naval Architects and Marine Engineers, Jersey City, NJ. Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
db293979-8fc0-439b-8042-a8d6cf8a84a9 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 15 INDUSTRIAL AIR CONDITIONING ¦ General Requirements ¦ 15.1 ¦ Cooling Systems ¦ 15.8 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Process and Product Requirements ¦ 15.1 ¦ Air Filtration Systems ¦ 15.9 ¦ ¦ Personnel Requirements ¦ 15.5 ¦ Exhaust Systems ¦ 15.9 ¦ ¦ Design Considerations ¦ 15.5 ¦ Operation and Maintenance ¦ 15.9 ¦ ¦ Load Calculations ¦ 15.6 ¦ Heat Recovery and Energy Conservation ¦ 15.10 ¦ ¦ Pressurization ¦ 15.7 ¦ Control Systems ¦ 15.10 ¦ ¦ System and Equipment Selection ¦ 15.7 ¦ Life and Property Safety ¦ 15.10 ¦ ¦ Heating Systems ¦ 15.8 ¦ Commissioning ¦ 15.11 ¦ T HIS chapter addresses air-conditioning systems for industrial facilities such as manufacturing plants, laboratories, processing plants, and power plants. HV AC systems provide the process envi- ronment (including temperature, humidity, air motion, air quality, noise, and cleanliness) to facilitate industrial processes and provide for the health, safety, and comfort of personnel. Many industrial buildings require large amounts of energy, in both manufacturing and maintaining building environmental conditions. This chapter provides system and building design guidance for energy conservation by using insulation, ventilation, and waste heat recovery. 1. GENERAL REQUIREMENTS Typical temperatures, relative humidities, and specific filtration requirements for storage, manufacture, and processing of various commodities are listed in Table 1 Requirements for a specific appli- cation may differ from those in the table. Industrial processes or regulatory requirements may change over time; thus, systems should be able to provide for future requirements (to the extent practical). Outdoor design requirements and indoor temperature, humidity, cleanliness, noise, and allowable variations should be established by agreement with the owner. A compromise between requirements for product or process conditions and those for comfort may optimize quality and production costs. An environment that allows a worker to safely perform assigned duties without fatigue caused by temperature and humidity may enhance performance. Special Warning: Some industrial spaces may contain flammable, combustible, and/or toxic concentrations of vapors or dusts under either normal or abnormal conditions. In spaces such as these, there are safety issues that this chapter may not completely ad- dress. Special precautions must be taken in accordance with require- ments of recognized authorities such as the National Fire Protection Association (NFPA), the Occupational Safety and Health Adminis- tration (OSHA), the American Conference of Governmental Indus- trial Hygienists (ACGIH), and the American National Standards Institute (ANSI). In all situations, engineers, designers, and installers who encounter conflicting codes and standards must defer to the code or standard that best addresses personnel safety. The cascade-ventilation-system design for toxic agents or similar hazardous materials is a potential fit for such facilities. This can in- clude a once-through, "push-pull" system, drawing air from the highly toxic areas to lower ones, with air change rates varying from 10 to 60 ach; pressures from -808.6 Pa to -62.2 Pa; and temperatures of 10 to 38°C. Applicable federal, state, and industry codes, and standards must be applied in the design of these facilities. The preparation of this chapter is assigned to TC 9.2, Industrial Air Condi- tioning. Terminology The supply system includes air-handling units (AHUs) with steam and hot water heating and chilled water cooling coils, ductwork, dampers, and accessories. Transfer air (TA) assemblies consist of ductwork, dampers, blast valves, fast-actuating dampers, and accessories. The exhaust air filtration system includes exhaust air filter units (EAFUs) with two HEPA filters and six charcoal filters to cap- ture highly toxic agent vapors, ductwork, dampers, accessories, and stacks. The HVAC units are powered by off-site and essential power, and the instrumentation and facility control system (FCS) are fed from uninterruptible power supply (UPS). FCS is a safety instru- mented system (SIS). 2. PROCESS AND PRODUCT REQUIREMENTS An industrial product or process may require control of the indoor environment ifit affects one or more of the following factors. Rate of Chemical Reaction Some processes require temperature and humidity control to reg- ulate chemical reactions. In rayon manufacturing, for example, pulp sheets are conditioned, cut to size, and mercerized. The temperature directly controls the rate of reaction, and the relative humidity main- tains the solution at a constant strength and rate of evaporation. In drying varnish, oxidizing depends on temperature. Desirable temperatures vary with the type of varnish. High relative humidity retards surface oxidation and allows internal gases to escape as chemical oxidizers cure the varnish from within. Thus, a bubble- free surface is maintained with a homogeneous film throughout. Rate of Crystallization The cooling rate determines the size of crystals formed from a saturated solution. Both temperature and relative humidity affect the cooling rate and change the solution density by evaporation. In coating pans for pills, a heavy sugar solution is added to the tumbling mass. As water evaporates, sugar crystals cover each pill. Moving the correct quantity of air over the pills at the correct tem- perature and relative humidity forms a smooth, opaque coating. If cooling and drying are too slow, the coating will be rough, translu- cent, and have an unsatisfactory appearance. If the cooling and drying are too fast, the coating will chip through to the interior. Rate of Biochemical Reaction Inc. ASHRAE, 2019 user. single for Licensed Fermentation requires both temperature and humidity control to regulate the rate of biochemical reactions. Many fermentation vessels are jacketed to maintain consistent internal temperatures. Fermentors are held at different temperatures, depending on the process involved. In brewing, typical fermentor temperatures range from 7 to 11°C. 15.1 | {}
5b2c4048-e3ee-4bec-852d-092e8404e645 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 15.2 2019 ASHRAE Handbook-HVAC Applications (SI) Table 1 Design Requirements for Industrial Air Conditioning1 Process °C % ¦ ¦ Dry Bulb, rh, ¦ ¦ --- ¦ --- ¦ ¦ ABRASIVE ¦ ABRASIVE ¦ ¦ Manufacture ¦ 26 50 ¦ ¦ CERAMICS ¦ CERAMICS ¦ ¦ Refractory ¦ 43 to 66 50 to 90 ¦ ¦ Molding room ¦ 27 60 to 70 ¦ ¦ Clay storage ¦ 16 to 27 35 to 65 ¦ ¦ Decalcomania production ¦ 24 to 27 48 ¦ ¦ Decorating room ¦ 24 27 ¦ ¦ to 48 Use high-efficiency (MERV 13 or better) in decorating room. To mini- mize the danger of silicosis in other areas, a dust-collecting system or particulate air filtration may be required. ¦ ¦ ¦ medium-efficiency DISTILLING ¦ medium-efficiency DISTILLING ¦ ¦ General manufacturing Aging ¦ 16 to 24 45 to 60 18 to 22 50 to 60 ¦ ¦ Low humidity and dust control are important where grains are ground. Use high-efficiency filtration for all areas to prevent mold spore and bacteria Use ultrahigh-efficiency filtration where bulk flash pasteurization is ¦ Low humidity and dust control are important where grains are ground. Use high-efficiency filtration for all areas to prevent mold spore and bacteria Use ultrahigh-efficiency filtration where bulk flash pasteurization is ¦ ¦ growth. performed. ELECTRICAL PRODUCTS ¦ growth. performed. ELECTRICAL PRODUCTS ¦ ¦ Electronics and x-ray ¦ ¦ ¦ Coil and transformer winding ¦ 22 15 ¦ ¦ Semiconductor industry ¦ 21 45 ¦ ¦ Electrical instruments ¦ Electrical instruments ¦ ¦ Manufacture and laboratory ¦ 21 50 to 55 ¦ ¦ Thermostat assembly and calibration ¦ 24 50 to 55 ¦ ¦ Humidistat assembly and calibration ¦ 24 50 to 55 ¦ ¦ Small mechanisms ¦ Small mechanisms ¦ ¦ Close tolerance assembly ¦ 22* 40 to 45 ¦ ¦ Meter assembly and test ¦ 24 60 to 63 ¦ ¦ Switchgear ¦ Switchgear ¦ ¦ Fuse and cutout assembly ¦ 23 50 ¦ ¦ Capacitor winding ¦ 23 50 ¦ ¦ Paper storage ¦ 23 50 ¦ ¦ Conductor wrapping with yarn ¦ 24 65 to 70 ¦ ¦ Lightning arrester assembly ¦ 20 20 to 40 ¦ ¦ Thermal circuit breakers assembly and test ¦ 24 30 to 60 ¦ ¦ High-voltage transformer repair ¦ 26 5 ¦ ¦ Water wheel generators ¦ Water wheel generators ¦ ¦ Thrust runner lapping ¦ 21 30 to 50 ¦ ¦ Rectifiers ¦ ¦ ¦ Processing selenium and copper oxide plates ¦ 23 30 to 40 ¦ ¦ *Temperature to be held constant. Dust control is essential in these processes. Minimum control requires medium-efficiency filters (MERV 11 or better). Degree of filtration depends on the type of function in the area. Smaller tolerances and miniature compo- nents suggest high-efficiency particulate air (HEPA) filters. ¦ *Temperature to be held constant. Dust control is essential in these processes. Minimum control requires medium-efficiency filters (MERV 11 or better). Degree of filtration depends on the type of function in the area. Smaller tolerances and miniature compo- nents suggest high-efficiency particulate air (HEPA) filters. ¦ ¦ FLOOR COVERING ¦ FLOOR COVERING ¦ ¦ Linoleum ¦ ¦ ¦ Mechanical oxidizing of linseed oil* ¦ 32 to 38 27 ¦ ¦ Printing ¦ 70 to 120 ¦ ¦ Stoving process *Precise temperature control required. Medium-efficiency particulate air filtration is recommended for the stov- ing process. ¦ Stoving process *Precise temperature control required. Medium-efficiency particulate air filtration is recommended for the stov- ing process. ¦ ¦ Process ¦ Dry Bulb, °C rh, % ¦ ¦ --- ¦ --- ¦ ¦ FOUNDRIES* ¦ FOUNDRIES* ¦ ¦ Core making ¦ 16 to 21 ¦ ¦ Mold making ¦ ¦ ¦ Bench work ¦ 16 to 21 ¦ ¦ Floor work ¦ 13 to 18 ¦ ¦ Pouring ¦ 4 ¦ ¦ Shakeout ¦ 4 to 10 ¦ ¦ Cleaning room ¦ 13 to 18 ¦ *Winter dressing room temperatures. Spot coolers are sometimes used in larger installations. In mold making, provide exhaust hoods at transfer points with wet- collector dust removal system. Use 280 to 380 L/s per hood, with a target capture velocity of approximately 2.5 m/s. In shakeout room, provide exhaust hoods with wet-collector dust removal system. Exhaust 190 to 240 L/s in grate area. Room ventilators are generally not effective. In cleaning room, provide exhaust hoods for grinders and cleaning equip- ment with dry cyclones or bag-type collectors. In core making, oven and adjacent cooling areas require fume exhaust hoods. Pouring rooms require two-speed powered roof ventilators. Design for minimum of 10 L/s of floor area at low speed. Shielding is required to control radiation from hot sur- faces. Proper introduction of air minimizes preheat requirements. ¦ FUR ¦ FUR ¦ FUR ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Drying ¦ 43 ¦ 43 ¦ ¦ Shock treatment ¦ -8 to -7 ¦ -8 to -7 ¦ ¦ Storage ¦ 4 to 10 ¦ 55 to 80 ¦ ¦ Shock treatment or eradication of any insect infestations requires lower- ing the temperature to -8 to -7°C for 3 to 4 days, then raising it to 16 to 21°C for 2 days, then lowering it again for 2 days and raising it to the stor- age temperature. Furs remain pliable, oxidation is reduced, and color and luster are pre- served when stored at 4 to 10°C. Humidity control is required to prevent mold growth (which is prevalent with humidities above 80%) and hair splitting (which is common with humidities lower than 55%). ¦ Shock treatment or eradication of any insect infestations requires lower- ing the temperature to -8 to -7°C for 3 to 4 days, then raising it to 16 to 21°C for 2 days, then lowering it again for 2 days and raising it to the stor- age temperature. Furs remain pliable, oxidation is reduced, and color and luster are pre- served when stored at 4 to 10°C. Humidity control is required to prevent mold growth (which is prevalent with humidities above 80%) and hair splitting (which is common with humidities lower than 55%). ¦ Shock treatment or eradication of any insect infestations requires lower- ing the temperature to -8 to -7°C for 3 to 4 days, then raising it to 16 to 21°C for 2 days, then lowering it again for 2 days and raising it to the stor- age temperature. Furs remain pliable, oxidation is reduced, and color and luster are pre- served when stored at 4 to 10°C. Humidity control is required to prevent mold growth (which is prevalent with humidities above 80%) and hair splitting (which is common with humidities lower than 55%). ¦ ¦ GUM ¦ GUM ¦ GUM ¦ ¦ Manufacturing ¦ 25 ¦ 33 ¦ ¦ Rolling ¦ 20 ¦ 63 ¦ ¦ Stripping ¦ 22 ¦ 53 ¦ ¦ Breaking ¦ 23 ¦ 47 ¦ ¦ Wrapping ¦ 23 ¦ 58 ¦ ¦ LEATHER ¦ LEATHER ¦ LEATHER ¦ ¦ Drying ¦ 20 to 52 ¦ 75 ¦ ¦ Storage, winter room temperature ¦ 10 to 16 ¦ 40 to 60 ¦ ¦ After leather is moistened in preparation for rolling and stretching, it is placed in an atmosphere of room temperature and 95% relative humidity. Leather is usually stored in warehouses without temperature and humidity control. However, it is necessary to keep humidity sufficiently low to prevent mildew. Medium-efficiency particulate air filtration is recommended for fine ¦ After leather is moistened in preparation for rolling and stretching, it is placed in an atmosphere of room temperature and 95% relative humidity. Leather is usually stored in warehouses without temperature and humidity control. However, it is necessary to keep humidity sufficiently low to prevent mildew. Medium-efficiency particulate air filtration is recommended for fine ¦ After leather is moistened in preparation for rolling and stretching, it is placed in an atmosphere of room temperature and 95% relative humidity. Leather is usually stored in warehouses without temperature and humidity control. However, it is necessary to keep humidity sufficiently low to prevent mildew. Medium-efficiency particulate air filtration is recommended for fine ¦ ¦ finish. ¦ finish. ¦ finish. ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ ¦ 45 ¦ ¦ ¦ ¦ ¦ ¦ LENSES (OPTICAL) Fusing ¦ ¦ ¦ ¦ Grinding ¦ 24 27 ¦ 80 ¦ Inc. ASHRAE, 2019 user. single for Licensed | {}
318f4bea-3fa2-4a36-8225-6c5ba16c164c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Industrial Air Conditioning 15.3 Table 1 Design Requirements for Industrial Air Conditioning1 (Continued) ¦ Process ¦ Dry Bulb, °C ¦ rh, % ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ MATCHES ¦ MATCHES ¦ MATCHES ¦ ¦ Manufacture ¦ 22 to 23 ¦ 50 ¦ ¦ Drying ¦ 21 to 24 ¦ 60 ¦ ¦ Storage ¦ 16 to 17 ¦ 50 ¦ ¦ Water evaporates with the setting of the glue. The amount of water evapo- rated is 8 to 9 kg per million matches. The actual match production rate must be known to determine the actual moisture load in the space. ¦ Water evaporates with the setting of the glue. The amount of water evapo- rated is 8 to 9 kg per million matches. The actual match production rate must be known to determine the actual moisture load in the space. ¦ Water evaporates with the setting of the glue. The amount of water evapo- rated is 8 to 9 kg per million matches. The actual match production rate must be known to determine the actual moisture load in the space. ¦ ¦ PAINT APPLICATION ¦ PAINT APPLICATION ¦ PAINT APPLICATION ¦ ¦ Lacquers: Baking ¦ 150 to 180 ¦ ¦ ¦ Oil paints: Paint spraying ¦ 16 to 32 ¦ 80 ¦ The required air filtration efficiency depends on the painting process. On fine finishes, such as car bodies, high-efficiency particulate air filters are required for the outdoor air supply. Other products may require only low- or medium-efficiency filters. Makeup air must be preheated. Spray booths must have 0.5 m/s face velocity if spraying is performed by humans; lower air quantities can be used if robots perform spraying. Ovens must have air exhausted to maintain fumes below explosive concentration. Equipment must be explosion-proof. Exhaust must be cleaned by filtration and solvents reclaimed or scrubbed. ¦ PHOTO STUDIO ¦ PHOTO STUDIO ¦ PHOTO STUDIO ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Dressing room ¦ 22 to 23 ¦ 40 to 50 ¦ ¦ Studio (camera room) ¦ 22 to 23 ¦ 40 to 50 ¦ ¦ Film darkroom ¦ 21 to 22 ¦ 45 to 55 ¦ ¦ Print darkroom ¦ 21 to 22 ¦ 45 to 55 ¦ ¦ Drying room ¦ 32 to 38 ¦ 35 to 45 ¦ ¦ Finishing room ¦ 22 to 24 ¦ 40 to 55 ¦ ¦ Storage room (black and white film and paper) ¦ 22 to 24 ¦ 40 to 60 ¦ ¦ Storage room (color film and paper) ¦ 40 to 50 ¦ 40 to 50 ¦ ¦ Motion picture studio ¦ 22 ¦ 40 to 55 ¦ The above data pertain to average conditions. In some color processes, elevated temperatures as high as 40°C are used, and a higher room tempera- ture is required. Conversely, ideal storage conditions for color materials necessitate refrig- erated or deep-freeze temperatures to ensure quality and color balance when long storage times are anticipated. Heat liberated during printing, enlarging, and drying processes is removed through an independent exhaust system, which also serves the lamp houses and dryer hoods. All areas except finished film storage require a minimum of medium-efficiency particulate air filters. 1Filtration as discussed in the table should correspond to the following minimums as defined in ASHRAE Standard 52.2: ¦ Low efficiency ¦ MERV 7 to MERV 8 ¦ ¦ --- ¦ --- ¦ ¦ Medium efficiency ¦ MERV 10 to MERV 12 ¦ ¦ High efficiency ¦ MERV 13 to MERV 14 ¦ ¦ Ultrahigh efficiency ¦ MERV 15 ¦ ¦ HEPA ¦ MERV 17 to MERV 20 ¦ The process engineer and owner should determine the process and HVAC filtration specifications for the specific application. Because of vessel jacketing, tight control of room temperature may not be required. Usually, space temperatures should be held as close as practical to the process temperature inside the fermentation vessel. Designing such spaces should take into account gases and other by- products generated by fermentation. Typically, carbon dioxide is the most prevalent by-product of fermentation in brewing and presents the greatest potential hazard if a fermentor overpressurizes the seal. Pro- vide adequate ventilation in case carbon dioxide escapes the process. In biopharmaceutical processes, hazardous organisms can escape a fermentor; design of spaces using those fermentors should allow ¦ Process ¦ Dry Bulb, °C ¦ rh, % ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ PLASTICS ¦ PLASTICS ¦ PLASTICS ¦ ¦ Manufacturing areas ¦ ¦ ¦ ¦ Thermosetting molding compounds ¦ 27 ¦ 25 to 30 ¦ ¦ Cellophane wrapping ¦ 24 to 27 ¦ 45 to 65 ¦ ¦ In manufacturing areas where plastic is exposed in the liquid state or molded, high-efficiency particulate air filters may be required. Dust collection and fume control are essential. ¦ In manufacturing areas where plastic is exposed in the liquid state or molded, high-efficiency particulate air filters may be required. Dust collection and fume control are essential. ¦ In manufacturing areas where plastic is exposed in the liquid state or molded, high-efficiency particulate air filters may be required. Dust collection and fume control are essential. ¦ ¦ PLYWOOD Hot pressing (resin) ¦ 32 ¦ 60 ¦ ¦ Cold pressing ¦ 32 ¦ 15 to 25 ¦ ¦ RUBBER-DIPPED GOODS ¦ RUBBER-DIPPED GOODS ¦ RUBBER-DIPPED GOODS ¦ ¦ Manufacture ¦ 32 ¦ ¦ ¦ Cementing ¦ 27 ¦ 25 to 30* ¦ ¦ Dipping surgical articles ¦ 24 to 27 ¦ 25 to 30* ¦ ¦ Storage prior to manufacture ¦ 16 to 24 ¦ 40 to 50* ¦ ¦ Testing laboratory ¦ 23 ¦ 50* ¦ *Dew point of air must be below evaporation temperature of solvent. Solvents used in manufacturing processes are often explosive and toxic, requiring positive ventilation. Volume manufacturers usually install a solvent recovery system for area exhaust systems. ¦ TEA ¦ TEA ¦ TEA ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Packaging ¦ 18 ¦ 65 ¦ ¦ Ideal moisture content is 5 to 6% for quality and mass. Low-limit moisture content for quality is 4%. ¦ Ideal moisture content is 5 to 6% for quality and mass. Low-limit moisture content for quality is 4%. ¦ Ideal moisture content is 5 to 6% for quality and mass. Low-limit moisture content for quality is 4%. ¦ ¦ TOBACCO ¦ TOBACCO ¦ TOBACCO ¦ ¦ Cigar and cigarette making ¦ 21 to 24 ¦ 55 to 65* ¦ ¦ Softening ¦ 32 ¦ 85 to 88 ¦ ¦ Stemming and stripping ¦ 24 to 29 ¦ 70 to 75 ¦ ¦ Packing and shipping ¦ 23 to 24 ¦ 65 ¦ ¦ Filler tobacco casing and conditioning ¦ 24 ¦ 75 ¦ ¦ Filter tobacco storage and preparation ¦ 25 ¦ 70 ¦ ¦ Wrapper tobacco storage and conditioning ¦ 24 ¦ 75 ¦ ¦ *Relative humidity fairly constant with range as set by cigarette machine. Before stripping, tobacco undergoes a softening operation. ¦ *Relative humidity fairly constant with range as set by cigarette machine. Before stripping, tobacco undergoes a softening operation. ¦ *Relative humidity fairly constant with range as set by cigarette machine. Before stripping, tobacco undergoes a softening operation. ¦ ¦ TOXIC AGENTS/HAZARDOUS MATERIALS ¦ TOXIC AGENTS/HAZARDOUS MATERIALS ¦ TOXIC AGENTS/HAZARDOUS MATERIALS ¦ ¦ Process areas ¦ 20 to 39 ¦ <65 ¦ containment. Heat gains from steam-sparged vessels should also be accounted for in such spaces. Product Accuracy and Uniformity Air temperature and cleanliness affect quality in manufacturing precision instruments, lenses, and tools. When manufacturing toler- ances are within 5 �m, close temperature control (typically ±2.8 K) prevents expansion and contraction of the material; constant tem- perature over time is more important than the temperature level. Inc. ASHRAE, 2019 user. single for Licensed | {}
4422c05c-0327-49d2-bd71-e9a316ae03e1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 15.4 2019 ASHRAE Handbook-HVAC Applications (SI) Table 2 Regain of Hygroscopic Materials* ¦ ¦ ¦ ¦ Relative Humidity ¦ Relative Humidity ¦ Relative Humidity ¦ Relative Humidity ¦ Relative Humidity ¦ Relative Humidity ¦ Relative Humidity ¦ Relative Humidity ¦ Relative Humidity ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Classification ¦ Material ¦ Description ¦ 10 ¦ 20 ¦ 30 ¦ 40 ¦ 50 ¦ 60 ¦ 70 ¦ 80 ¦ 90 ¦ ¦ Natural textile fibers ¦ Cotton ¦ Sea island roving ¦ 2.5 ¦ 3.7 ¦ 4.6 ¦ 5.5 ¦ 6.6 ¦ 7.9 ¦ 9.5 ¦ 11.5 ¦ 14.1 ¦ ¦ Natural textile fibers ¦ Cotton ¦ American cloth ¦ 2.6 ¦ 3.7 ¦ 4.4 ¦ 5.2 ¦ 5.9 ¦ 6.8 ¦ 8.1 ¦ 10.0 ¦ 14.3 ¦ ¦ Natural textile fibers ¦ Cotton ¦ Absorbent ¦ 4.8 ¦ 9.0 ¦ 12.5 ¦ 15.7 ¦ 18.5 ¦ 20.8 ¦ 22.8 ¦ 24.3 ¦ 25.8 ¦ ¦ Natural textile fibers ¦ Wool ¦ Australian merino skein ¦ 4.7 ¦ 7.0 ¦ 8.9 ¦ 10.8 ¦ 12.8 ¦ 14.9 ¦ 17.2 ¦ 19.9 ¦ 23.4 ¦ ¦ Natural textile fibers ¦ Silk ¦ Raw chevennes skein ¦ 3.2 ¦ 5.5 ¦ 6.9 ¦ 8.0 ¦ 8.9 ¦ 10.2 ¦ 11.9 ¦ 14.3 ¦ 18.3 ¦ ¦ Natural textile fibers ¦ Linen ¦ Table cloth ¦ 1.9 ¦ 2.9 ¦ 3.6 ¦ 4.3 ¦ 5.1 ¦ 6.1 ¦ 7.0 ¦ 8.4 ¦ 10.2 ¦ ¦ Natural textile fibers ¦ Linen ¦ Dry spun-yarn ¦ 3.6 ¦ 5.4 ¦ 6.5 ¦ 7.3 ¦ 8.1 ¦ 8.9 ¦ 9.8 ¦ 11.2 ¦ 13.8 ¦ ¦ Natural textile fibers ¦ Jute ¦ Average of several grades ¦ 3.1 ¦ 5.2 ¦ 6.9 ¦ 8.5 ¦ 10.2 ¦ 12.2 ¦ 14.4 ¦ 17.1 ¦ 20.2 ¦ ¦ Natural textile fibers ¦ Hemp ¦ Manila and sisal rope ¦ 2.7 ¦ 4.7 ¦ 6.0 ¦ 7.2 ¦ 8.5 ¦ 9.9 ¦ 11.6 ¦ 13.6 ¦ 15.7 ¦ ¦ Rayons ¦ Viscose nitrocellulose ¦ Average skein ¦ 4.0 ¦ 5.7 ¦ 6.8 ¦ 7.9 ¦ 9.2 ¦ 10.8 ¦ 12.4 ¦ 14.2 ¦ 16.0 ¦ ¦ Rayons ¦ Cuprammonium cellulose acetate ¦ Average skein ¦ 0.8 ¦ 1.1 ¦ 1.4 ¦ 1.9 ¦ 2.4 ¦ 3.0 ¦ 3.6 ¦ 4.3 ¦ 5.3 ¦ ¦ Paper ¦ M.F. newsprint ¦ Wood pulp 24% ash ¦ 2.1 ¦ 3.2 ¦ 4.0 ¦ 4.7 ¦ 5.3 ¦ 6.1 ¦ 7.2 ¦ 8.7 ¦ 10.6 ¦ ¦ Paper ¦ H.M.F. writing ¦ Wood pulp 3% ash ¦ 3.0 ¦ 4.2 ¦ 5.2 ¦ 6.2 ¦ 7.2 ¦ 8.3 ¦ 9.9 ¦ 11.9 ¦ 14.2 ¦ ¦ Paper ¦ White bond ¦ Rag-1% ash ¦ 2.4 ¦ 3.7 ¦ 4.7 ¦ 5.5 ¦ 6.5 ¦ 7.5 ¦ 8.8 ¦ 10.8 ¦ 13.2 ¦ ¦ Paper ¦ Comm. ledger ¦ 75% rag-1% ash ¦ 3.2 ¦ 4.2 ¦ 5.0 ¦ 5.6 ¦ 6.2 ¦ 6.9 ¦ 8.1 ¦ 10.3 ¦ 13.9 ¦ ¦ Paper ¦ Kraft wrapping ¦ Coniferous ¦ 3.2 ¦ 4.6 ¦ 5.7 ¦ 6.6 ¦ 7.6 ¦ 8.9 ¦ 10.5 ¦ 12.6 ¦ 14.9 ¦ ¦ Miscellaneous organic materials ¦ Leather ¦ Sole oak- -tanned ¦ 5.0 ¦ 8.5 ¦ 11.2 ¦ 13.6 ¦ 16.0 ¦ 18.3 ¦ 20.6 ¦ 24.0 ¦ 29.2 ¦ ¦ Miscellaneous organic materials ¦ Catgut ¦ Racquet strings ¦ 4.6 ¦ 7.2 ¦ 8.6 ¦ 10.2 ¦ 12.0 ¦ 14.3 ¦ 17.3 ¦ 19.8 ¦ 21.7 ¦ ¦ Miscellaneous organic materials ¦ Glue ¦ Hide ¦ 3.4 ¦ 4.8 ¦ 5.8 ¦ 6.6 ¦ 7.6 ¦ 9.0 ¦ 10.7 ¦ 11.8 ¦ 12.5 ¦ ¦ Miscellaneous organic materials ¦ Rubber ¦ Solid tires ¦ 0.11 ¦ 0.21 ¦ 0.32 ¦ 0.44 ¦ 0.54 ¦ 0.66 ¦ 0.76 ¦ 0.88 ¦ 0.99 ¦ ¦ Miscellaneous organic materials ¦ Wood ¦ Timber (average) ¦ 3.0 ¦ 4.4 ¦ 5.9 ¦ 7.6 ¦ 9.3 ¦ 11.3 ¦ 14.0 ¦ 17.5 ¦ 22.0 ¦ ¦ Miscellaneous organic materials ¦ Soap ¦ White ¦ 1.9 ¦ 3.8 ¦ 5.7 ¦ 7.6 ¦ 10.0 ¦ 12.9 ¦ 16.1 ¦ 19.8 ¦ 23.8 ¦ ¦ Miscellaneous organic materials ¦ Tobacco ¦ Cigarette ¦ 5.4 ¦ 8.6 ¦ 11.0 ¦ 13.3 ¦ 16.0 ¦ 19.5 ¦ 25.0 ¦ 33.5 ¦ 50.0 ¦ ¦ Miscellaneous inorganic materials ¦ Asbestos fiber ¦ Finely divided ¦ 0.16 ¦ 0.24 ¦ 0.26 ¦ 0.32 ¦ 0.41 ¦ 0.51 ¦ 0.62 ¦ 0.73 ¦ 0.84 ¦ ¦ Miscellaneous inorganic materials ¦ Silica gel ¦ Finely divided ¦ 5.7 ¦ 9.8 ¦ 12.7 ¦ 15.2 ¦ 17.2 ¦ 18.8 ¦ 20.2 ¦ 21.5 ¦ 22.6 ¦ ¦ Miscellaneous inorganic materials ¦ Domestic coke ¦ Finely divided ¦ 0.20 ¦ 0.40 ¦ 0.61 ¦ 0.81 ¦ 1.03 ¦ 1.24 ¦ 1.46 ¦ 1.67 ¦ 1.89 ¦ ¦ Miscellaneous inorganic materials ¦ Activated charcoal ¦ Steam activated ¦ 7.1 ¦ 14.3 ¦ 22.8 ¦ 26.2 ¦ 28.3 ¦ 29.2 ¦ 30.0 ¦ 31.1 ¦ 32.7 ¦ ¦ Miscellaneous inorganic materials ¦ Sulfuric acid ¦ Steam activated ¦ 33.0 ¦ 41.0 ¦ 47.5 ¦ 52.5 ¦ 57.0 ¦ 61.5 ¦ 67.0 ¦ 73.5 ¦ 82.5 ¦ *Moisture content expressed in percent of dry mass of the substance at various relative humidities, temperature 24°C. Usually, conditions are selected for personnel comfort and to prevent a film of moisture on the surface. A high-efficiency par- ticulate air (HEPA) or ultralow-penetration air (ULPA) filter may be required. Product Formability Manufacturing pharmaceutical tablets requires close control of humidity for optimum tablet formation. Tableting typically requires less than 40% rh at 20°C. Moisture Regain Air temperature and relative humidity markedly influence pro- duction rate and product mass, strength, appearance, and quality in manufacturing or processing hygroscopic materials such as textiles, paper, wood, leather, and tobacco. Moisture in vegetable and animal materials (and some minerals) reaches equilibrium with moisture in the surrounding air by regain (the percentage of absorbed moisture in a material compared to that material's bone-dry mass). For exam- ple, if a material sample with a mass of 2.5 kg has a mass of only 2.25 kg after thorough drying under standard conditions of 105 to 110°C, the mass of absorbed moisture is 0.25 kg, 10% of the sam- ple's bone-dry mass. Therefore, the regain is 10%. Table 2 lists typical regain values for materials at 24°C in equilib- rium at various relative humidities. Temperature change affects the rate of absorption or drying, which generally varies with the thick- ness, density, and nature of the material. Sudden temperature changes cause slight changes in regain even with fixed relative humidity, but the major change occurs as a function of relative humidity. Hygroscopic materials deliver sensible heat to the air in an amount equal to the latent heat of the absorbed moisture. The amount of heat liberated should be added to the cooling load ifit is significant, but it is usually quite small. Manufacturing economy requires regain to be maintained at a level suitable for rapid and satisfactory manipulation. Uniform relative humidity allows high- speed machinery to operate efficiently. Some materials may be exposed to the required humidity during manufacturing or processing, and others may be treated separately after conditioning and drying. Conditioning removes or adds hygroscopic moisture. Drying removes both hygroscopic moisture and free moisture in excess of that in equilibrium. Drying and conditioning can be combined to remove moisture and accu- rately regulate the final moisture content in products such as tobacco and textiles. Conditioning or drying is frequently a con- tinuous process in which the material is conveyed through a tunnel and subjected to controlled atmospheric conditions. For more detail, see Chapter 24 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment. Corrosion, Rust, and Abrasion In manufacturing metal products, temperature and relative hu- midity must be kept sufficiently low to prevent hands from sweating, thus protecting the finished article from fingerprints, tarnish, and/or etching. Salt and acid in perspiration can cause corrosion and rust in as little as a few hours. Manufacture ofpolished surfaces and of steel- belted radial tires usually requires medium-efficiency to HEPA fil- tering to prevent surface abrasion. Air Cleanliness Each application must be evaluated to determine the filtration needed to counter the adverse effects on the product or process of dust particles, airborne bacteria, smoke, spores, pollen, and radio- active particles. These effects include chemically altering production material, spoiling perishable goods, and clogging small openings in Inc. ASHRAE, 2019 user. single for Licensed | {}
2e55a478-4b02-43c1-bc5f-d66b8b514549 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Industrial Air Conditioning 15.5 precision machinery. See Chapter 29 of the 2016 ASHRAE Hand- book-HVAC Systems and Equipment for details. Static Electricity Static electricity is often detrimental in processing light materi- als such as textile fibers and paper, and extremely dangerous where potentially explosive atmospheres or materials are present. Static electric charges are generally minimized when relative humidity is above 35%. Room relative humidity may need to be maintained at 65% or higher because machinery heat raises the machine ambient temperature well above the room temperature, creating localized areas of low relative humidity. Such areas could be sources of static electricity. The parts assembly area of an ammunition plant should have design conditions of 24°C and 40 to 60% rh. In addition, air- moving equipment (fans) should be spark resistant. According to NFPA Standard 77, humidification increases a material's surface conductivity, but the static electric charge dissi- pates only if there is a conductive path to ground. However, humidification is not a cure-all for static electricity problems. Some insulators do not adsorb or absorb moisture from the air, and high humidity does not noticeably decrease their surface resistivity. Examples include uncontaminated surfaces of some poly- meric materials (e.g., plastic piping and containers, films), and the surface of petroleum liquids. These surfaces can accumulate static electric charge even when the atmosphere has a humidity of 100%. 3. PERSONNEL REQUIREMENTS Space conditions required by health and safety standards to avoid excess exposure to high temperatures and airborne contaminants are often established by the American Conference of Governmental Industrial Hygienists (ACGIH). In the United States, the National Institute of Occupational Safety and Health (NIOSH) does research and recommends guidelines for workplace environments. The Occupational Safety and Health Administration (OSHA) sets stan- dards based on these guidelines, with enforcement usually assigned to a corresponding state agency. Standards for safe levels of contaminants in the work environ- ment or in air exhausted from facilities do not cover everything that may be encountered. Minimum safety standards and design criteria are available from U.S. Department of Health agencies such as the National Institute of Health, National Cancer Institute, and Public Health Service. The U.S. Department of Energy and Nuclear Regulatory Commission establish standards for radioac- tive substances. Thermal Control Levels Industrial plants are usually designed for an internal temperature of 16 to 32°C and a maximum of 60% rh. Tighter controls are often dictated by the specific operations and processes located in the building. ACGIH (2016) established guidelines to evaluate high temperature and humidity levels in terms of heat stress (Dukes- Dobos and Henschel 1971). See Chapter 9 of the 2017 ASHRAE Handbook-Fundamentals for a more detailed analysis of work rate, air velocity, rest, and the effects of radiant heat. Temperature control becomes tighter and more specific if person- nel comfort, rather than avoidance of heat stress, becomes the crite- rion. Nearly sedentary workers prefer a winter temperature of 22°C and a summer temperature of 26°C at a maximum of 60% rh. Work- ers at a high rate of activity prefer 18°C; they are less sensitive to temperature changes and can be cooled by increasing the air veloc- ity. ASHRAE Standard 55 provides more detailed information. Contamination Control Levels Toxic and/or hazardous materials are present in many industrial plants and laboratories. Gases and vapors are found near acid baths and tanks holding process chemicals. Plating operations, spraying, mixing, abrasive cleaning, and other processes generate dust, fumes, and mists. Many animal and laboratory procedures (e.g., grinding, blending, sonication, weighing) generate aerosols. Air- conditioning and ventilation systems must minimize exposure to these materials. When airborne, these materials greatly expand their range and potential for affecting more people. Chapter 11 of the 2017 ASHRAE Handbook-Fundamentals, OSHA requirements, and ACGIH (2016) give guidance on the health effects of various materials. Concentrations of gaseous flammable substances must also be kept below explosive limits. Acceptable concentrations of these substances are a maximum of 25% of the lower explosive limit. Chapter 11 of the 2017 ASHRAE Handbook-Fundamentals pro- vides data on flammable limits and their means of control. Instruments are available to measure concentrations of common gases and vapors, but specific monitoring requirements and methods must be developed for uncommon ones. 4. DESIGN CONSIDERA TIONS Required environmental conditions for equipment, process, and personnel comfort must be known before selecting HVAC equip- ment. The engineer and owner jointly establish design criteria, in- cluding the space-by-space environment in facilities, process heat loads and exhaust requirements, heat and cooling energy recovery, load factors and equipment diversity, lighting, cleanliness, etc. Con- sider separating dirty processes from areas that require progressively cleaner air. Insulation should be evaluated for initial cost and operating and energy cost savings. When high levels of moisture are required in the building, the air-conditioning and structural envelope must prevent unwanted condensation and ensure a high-quality product. Condensation can be prevented by eliminating thermal short cir- cuits, installing proper insulation, and using vapor barriers. See Chapters 25 and 27 of the 2017 ASHRAE Handbook- -Fundamen- tals for further details. Personnel engaged in some industrial processes may be subject to a wide range of activity levels for which a broad range of tempera- tures and humidities are desirable. Chapter 9 of the 2017 ASHRAE Handbook-Fundamentals addresses recommended indoor condi- tions for a variety of activity levels. Iflayout and construction drawings are not available, a complete survey of existing premises and a checklist for proposed facilities are necessary (Table 3). New industrial buildings are typically single story with a flat roof and ample height to distribute air and utilities without interfering with process operations. Fluorescent fixtures are commonly mounted at heights up to 4 m, high-output fluorescent fixtures up to 6 m, and high-pressure sodium or metal halide fixtures above 6 m; LED fix- tures are used at all heights. Lighting design considers light quality, diffusion, room size, mounting height, and economics. Illumination levels should conform to recommendations of the Illuminating Engi- neering Society of North America. Air-conditioning systems can be located on the roof of the build- ing or (ideally) in an interior equipment room. Air intakes should not be located too close to loading docks or other sources of contamina- tion. (See the section on Air Filtration Systems.) HVAC system installation must be coordinated with other systems and equipment that compete for building space, such as piping systems, electrical bus, fire sprinklers, lighting, cranes, structural elements, etc. Operations in the building must also be considered: some require close control of temperature, humidity, and/or contaminants. A schedule of operations is helpful in determining heating and cooling loads. Inc. ASHRAE, 2019 user. single for Licensed | {}
00d72f01-0d0d-4107-834b-45be818c9adb | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 15.6 2019 ASHRAE Handbook-HVAC Applications (SI) Table 3 Facilities Checklist Construction 1. Single or multistory 2. Type and location of doors, windows, crack lengths 3. Structural design live loads 4. Floor construction 5. Exposed wall materials 6. Roof materials and color 7. Insulation type and thicknesses 8. Location of existing inlet and exhaust equipment 9. Building orientation Use of Building 1. Product needs 2. Surface cleanliness; acceptable airborne contamination level 3. Process equipment: type, location, and exhaust requirements 4. Personnel needs, temperature levels, required activity levels, and special workplace requirements 5. Floor area occupied by machines and materials 6. Clearance above floor required for material-handling equipment, piping, lights, or air distribution systems 7. Unusual occurrences and their frequency, such as large cold or hot masses of material moved indoors 8. Frequency and length of time doors open for loading or unloading 9. Lighting: location, type, and capacity 10. Acoustical levels 11. Machinery loads, such as electric motors (size, diversity), large latent loads, or radiant loads from furnaces and ovens 12. Potential for temperature stratification Design Conditions 1. Design temperatures: indoor and outdoor dry and wet bulb 2. Altitude 3. Wind velocity 4. Makeup air required 5. Indoor temperature and allowable variance 6. Indoor relative humidity and allowable variance 7. Indoor air quality definition and allowable variance 8. Outdoor temperature occurrence frequencies 9. Operational periods: number per day and duration 10. Waste heat availability and energy conservation incentives 11. Pressurization required 12. Mass loads from the energy release of productive materials Inc. ASHRAE, 2019 user. single for Licensed Code and Insurance Requirements 1. State and local code requirements for ventilation rates, etc. 2. Occupational health and safety requirements 3. Insuring agency requirements Utilities Available and Required 1. Gas, oil, compressed air (pressure), electricity (characteristics), steam (pressure), water (pressure), wastewater, interior and site drainage 2. Rate structures for each utility 3. Potable and fire water Material Handling (MH) Airlock Interface Material handling airlock interfaces can be used in facilities that process toxic agents or similarly hazardous materials. Each MH conveyor airlock has one in gate and one out gate. These gates are equipped with position switches that send signals to the FCS to indi- cate the gate positions (open/closed). When both gates are closed, continuous air purging is required; when either of the gates is open, sufficient capture velocity is required to prevent backflow. Both gates should not be open simultaneously. Each MH airlock is provided with one set of inlet and outlet transfer air assemblies. The inlet assembly consists of one big and one small on/off isolation damper. The outlet assembly has a pres- sure control damper. The FCS opens both inlet isolation dampers and modulates the outlet pressure control damper to satisfy the design airlock pressure. When one gate is open, the FCS adjusts the positions of the isolation and pressure control dampers to allow an airflow rate that satisfies both ventilation and design capture veloc- ity requirements. Process Exhaust Interface with Exhaust System. Offgas treat- ment (OT) process exhausts are discharged from the process blow- ers into the HVAC exhaust air inlet headers. The FCS enables OT blower operation only when HVAC exhaust air inlet headers are maintained at the set negative pressure. Space pressure controllers ofthe adjacent rooms modulate the respective dampers in the supply air ducts to balance airflow and keep the downstream room at set negative pressure. System Shutdown. The ventilation/filtration system of toxic areas is in continuous operation. If negative pressure cannot be maintained because of a loss of essential power off site, the system is automatically shut down via the FCS, and all normally open TA isolation dampers in the toxic areas of the cascading airflow paths are closed to prevent toxic vapor migration. The fast-actuating iso- lation valves remain open to keep the blast resistant rooms vented to the EAFUs. 5. LOAD CALCULA TIONS Table 1 and specific product chapters of this Handbook discuss product requirements. Chapter 18 of the 2017 ASHRAE Hand- book-Fundamentals provides appropriate heating and cooling load calculation techniques. Solar and Transmission The roof load is usually the largest solar load on the envelope. Solar loads on walls are often insignificant, particularly because modern factory buildings tend to be windowless. Insulating the building walls and roof almost always benefits HV AC cost and performance. Because roof surfaces can become dirty, use a dark roof color in load calculations. Internal Heat Generation Internal heat generated by equipment and processes, as well as products, lighting, people, and utilities, may satisfy heating load re- quirements. Understanding equipment operating schedules allows an appropriate diversity factor to be applied to the actual power con- sumption. Using connected loads may greatly oversize the system. Processes tend to operate continuously, but may be shut down on weekends or at night. Heating to some minimal level without equip- ment and/or process load should be considered. Consult ASHRAE research project RP-1104 (White and Pahwa 2003) for further infor- mation. The latent load in most industrial facilities is minimal, with peo- ple and outdoor air being the primary contributors, but some pro- cesses and products do generate a latent load, which can dominate the HVAC system design. Mist collectors serving operations that use heated washers or water-based coolants operating above the tar- geted space temperature can contribute excessive latent loading in wet machining operations. Quantifying the latent impact for each source can help determine which exhaust streams should be dis- charged outdoors and not recirculated back to the space. Moisture condensation on cold surfaces must be managed when the latent load becomes very large. Stratification Effect The cooling load may be dramatically reduced in a work space that takes advantage of temperature stratification. A stagnant blanket of warm air directly under the roofhas little effect on occu- pants or equipment as long as it remains undisturbed. Heat sources near the stagnant air have little effect on the cooling load. When the ceiling or roofis high, 20 to 60% of the heat energy rises out of the cooling zone, depending on building construction and the tempera- ture of heat sources. Switching to a return air location near the roof | {}
75552731-49e6-4132-9073-0473219f7ce0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Industrial Air Conditioning 15.7 could be cost effective, because it takes advantage of higher tem- peratures at the roof. Supply and return air ducts should be installed as low as prac- tical to avoid mixing the warm boundary layers in cooling mode. The location of supply air diffusers generally establishes the strat- ified air boundary. Spaces with a low occupant-to-floor-area ratio adapt well to using low quantities of supply air with spot cooling for personnel. Makeup Air Makeup air provides ventilation and building pressurization. It must be filtered and conditioned to blend with return air and then distributed to the conditioned space. The quantity of makeup air must exceed that of the exhaust air to positively pressurize the building. Makeup air quantity may be varied to accommodate an exhaust system with intermittently operating elements. Heat and cooling recovery from the exhaust airstream can substantially reduce the outdoor air load. Processes requiring an extensive amount of exhaust air should ideally be placed in an area of the plant provided with minimal heating and no refrigerated air conditioning. Ventilation air may be required to reduce the quantity of health-threatening fumes, airborne bacteria, fugitive aerosols, or radioactive particles. Min- imum ventilation rates must meet the requirements of ASHRAE Standard 62.1. Consult the owner' s industrial hygiene or engi- neering representative to determine if ventilation rates in excess of this standard may be warranted. Economizers can take advantage of ambient conditions and possibly satisfy HVAC loads without added heating or cooling for much of the year. Fan Heat Heat is generated by fans that move and pressurize the air. This heat is not felt by the occupants but does add to the cooling load. The discharge air temperature of a draw-through cooling arrange- ment requires cooler air to the fan to accommodate the tempera- ture increase of air passing through the fan. The increase is more significant in systems with higher discharge air pressures. 6. PRESSURIZA TION Room-to-room pressurization is an essential method for contam- ination control. Without pressurization, surrounding contamination (e.g., particulates, gases, hot or cold air, moisture) can enter the room by infiltration through doors, windows, cracks, pass-throughs and penetrations for pipes or ducts, etc. The cleanest room should have the highest room pressure, with decreasing pressure corre- sponding to decreasing cleanliness. A differential pressure around 12.5 or 25 Pa is often used. Pressurization calculations can be performed by using the pro- cedures and charts in Chapter 18 ofthe 2017 ASHRAE Handbook- Fundamentals, or those in Chapter 5 of Spitler (2009). Using the charts in Spitler, calculate the building exfiltration at designated room pressurization level. Also, in accordance with ASHRAE Standard 62.1, determine the required outdoor air rate using the actual number of occupants, and identify the total exhaust air vol- ume from the building. The sum of exfiltration air volume plus exhaust rate (or required outdoor air, whichever is greater) is the total ventilation rate under the designated building pressurization. To ensure the designated pressurization level, perform a leak test for exterior and interior walls, partitions, doors, and windows between two adjacent areas with different pressurization levels, roof, exterior doors and windows, connections between wall and roof, and any building elements between two areas with different pressurization levels. All major leaks must be eliminated before HV AC systems start-up. If pressurization is a critical attribute for maintaining room cleanliness in areas such as plant process control rooms, computer rooms, etc., then the crack area may need to be estimated and the pressurization air quantity calculated using an equation such as Equation (11) or (12) in Chapter 54, where the crack is treated as an orifice and the required airflow is defined as a function of pressure differential. Adequate design margins should be incorporated in the pressurization system design to allow for building envelope seal degradation over the structure , s life. Ifthe pressurization is required for safety or code compliance, make provisions in the design for periodic surveillance and testing. Explosion Management Particularly in facilities that process toxic agents and other haz- ardous materials, the possibility of explosion should be addressed. Blast valve assemblies are installed at points of air transfer and exhaust air penetrations through the blast-resistant building enve- lope. An explosion-generated pressure wave of 103.5 kPa or greater immediately closes the affected blast valves (spring balanced pres- sure disks). The inlet and outlet blast valves close within 10 ms. The fast-actuating dampers are provided in series with the blast valve assemblies. On receiving alarms from explosion switches located within the affected blast-resistant rooms, the FCS automatically closes the corresponding fast-actuating isolation dampers, and fast- actuating isolation dampers powered by the nitrogen system close within 500 ms. The blast valves are fully automatic in operation. After an explo- sion, when the room pressure decreases to the facility-specific set pressure, the FCS opens the exhaust-side fast-acting dampers first, and then opens those in the transfer air assemblies when the room pressure decreases to a lower (facility specific) set pressure, to restore the cascading ventilation path. Any room involved in an explosion immediately raises all related upstream room pressures due to the cascading airflow blockage. Based on the room pressure control, the FCS automatically throttles the respective pressure dampers installed in the supply air ducts to minimize the pressure upset in the upstream rooms. The airflow blockage may create a ripple effect that causes the system header pressure controller to slow the fan speeds of the EAFU and supply AHU. In some rooms, there is a bypass exhaust pathway open to bypass exhaust to allow venting from rooms to the exhaust header. 7. SYSTEM AND EQUIPMENT SELECTION Industrial air-conditioning equipment includes heating and cooling sources, air-handling and air-conditioning apparatus, filters, and an air distribution system. Components should be selected and the system designed for long life with low maintenance and operat- ing costs conducive to low life-cycle cost. Systems may consist of the following: · Heating-only in cool climates, where ventilation air provides comfort for workers · Air washer systems, where high humidities are desired and where the climate requires cooling · Heating and evaporative cooling, where the climate is dry · Heating and mechanical cooling, where temperature and humidity control are required and other means of cooling are insufficient All systems include air filtration appropriate to the contaminant control required. Careful evaluation should determine zones that require tempera- ture control, especially in large, high-bay areas where the occupied zone is a small portion of space volume. ASHRAE Standard 55 defines the occupied zones as from the floor to 1.8 m high, more than 1 m from exterior walls or fixed conditioning equipment, and 0.3 m from interior walls. Inc. ASHRAE, 2019 user. single for Licensed | {}
0d8d56fc-2fde-4ef7-834b-e10a0a241959 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 15.8 2019 ASHRAE Handbook-HVAC Applications (SI) 8. HEATING SYSTEMS Floor Heating Floor heating is often desirable in industrial buildings, particu- larly in large, high-bay buildings, garages, and assembly areas where workers must be near the floor, or where large or fluctuating outdoor air loads make maintaining ambient temperature difficult. Floors may be tempered to 18 to 21°C by embedded hydronic systems, electrical resistance cables, or warm air ducts as an auxil- iary to the main heating system. Heating elements may be buried deep in the floor (150 to 450 mm) to allow slab warm-up at off-peak times, thus using the floor mass as heat storage to save energy during periods of high use. Floor heating may be the primary or sole heating means, but floor temperatures above 29°C are uncomfortable, so such use should be limited to small, well-insulated spaces. Unit and Ducted Heaters Gas, oil, electric, hot-water, or steam-fired unit heaters with cen- trifugal or propeller fans are used for spot heating areas and may be arranged in multiples for heating an entire building. Temperatures can be varied by individual thermostatic control. Unit heaters should be located so that the discharge (throw) reaches the floor ad- jacent to and parallel with the outer wall, and spaced to produce a ring of warm air moving peripherally around the building. In indus- trial buildings with heat-producing processes, heat tends to stratify in high-bay areas. In large buildings, additional heaters should be placed in the interior so that their discharge reaches the floor to re- duce stratification. Downward-discharge unit heaters in high bays and large areas may have a revolving discharge. Gas- and oil-fired unit heaters should not be used where corrosive vapors are present. Furthermore, care must be taken to avoid selecting a unit configu- ration wherein return air from the space is drawn through the com- bustion zone of any direct-fired gas burners, because unintended byproducts of combustion may result. Ducted heaters include large direct- or indirect-fired heaters, door heaters, and heating and ventilating units. They usually have centrifugal fans. Inc. ASHRAE, 2019 user. single for Licensed Unit heaters and makeup air heaters commonly temper outdoor air that enters buildings through open doors. Mixing quickly brings the space temperature back to the desired setting after the door is closed. The makeup air heater should be applied as a door heater in buildings where the doors are large and open for extended periods, such as doors for large trucks or railroad cars. Such large doors often use ductwork drops across the top and along both sides of the door, with slotted diffusers to induce an air-curtain effect. Unit heaters are also needed in buildings that have considerable leakage or a sizeable negative pressure. These units help pressurize the door area, mix the incoming cold air, temper it, and quickly bring the area back to the desired temperature after the door is closed. Door heating units that resemble a vestibule operate with airflow down across the opening and recirculated from the bottom, which helps reduce cold drafts across the floor. These units are effective on high-usage doors under 3 m tall. Additional information on heating is given in Chapter 27 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment. Infrared Heaters High-intensity gas, oil, or electric infrared heaters transfer heat directly to the occupants, equipment, and floor in the space without appreciably warming the air, though some air heating occurs by convection from objects heated by the infrared heaters. These heat- ers are classified as either near- or far-infrared heaters, depending on how close the wavelengths they emit are to visible light. Near- infrared heaters emit a substantial amount of visible light. Both vented and unvented gas-fired infrared heaters are available as either individual radiant panels or as a continuous radiant pipe. Pipe-type heaters include burners 4.5 to 9 m apart and an exhaust vent fan at the end of the pipe. Unvented heaters require exhaust ven- tilation to remove flue products from the building and to prevent moisture from collecting on the walls and ceiling. Infrared heaters are common in the following applications: · High-bay buildings, where heaters are usually mounted 3 to 9 m above the floor, along outer walls, and tilted to direct maximum radiation to the floor. If the building is poorly insulated, the con- trolling thermostat should be shielded to avoid influence from the radiant effect of the walls and the cold walls. · Semi-open and outdoor areas, where people can be comfortably heated directly and objects can be heated to avoid condensation. · Loading docks, where snow and ice can be controlled by strategic placement of near-infrared heaters. Additional information on both electric and gas infrared heating is given in Chapter 16 of the 2016 ASHRAE Handbook- -HVAC Sys- tems and Equipment. 9. COOLING SYSTEMS Common cooling systems include refrigeration equipment, evap- orative coolers, and high-velocity ventilation air. For manufacturing operations, particularly in heavy industry where mechanical cooling cannot be economically justified, evapo- rative cooling systems often provide good working conditions, as discussed in Chapter 41 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment. If the operation requires heavy physical work, spot cooling by ventilation, evaporative coolers, or refriger- ated air can be used. To minimize summer discomfort, high outdoor ventilation rates may be adequate in some hot-process areas. A me- chanical air supply with good distribution is needed in all these op- erations. Refrigerated Cooling Systems The most commonly used refrigerated cooling systems are roof- mounted, direct-expansion packaged units. Larger systems may use chilled water distributed to air-handling units. Central system condenser water rejects heat through a cooling tower. Refrigerated heat recovery is particularly advantageous in buildings with simultaneous need to heat exterior spaces and cool interior spaces. Mechanical cooling equipment should be selected in multiple units. This lets the equipment match its response to fluctuations in the load and allows maintenance during off-peak operation periods. Packaged refrigeration equipment commonly uses positive-displacement (reciprocating, scroll, or screw) compressors with air-cooled condensers. When equipment is on the roof, the con- densing temperature may be affected by warm ambient air, often 5 to 10 K higher than design outdoor air temperature. ASHRAE Stan- dard 15 provides rules for the type and quantity of refrigerant in direct air-to-refrigerant exchangers. Desiccant-based systems should be considered for processes that require dew points below 10°C (e.g., pharmaceutical processing). Evaporative Cooling Systems Evaporative cooling systems may be direct or indirect evapora- tive coolers or air washers. Evaporative coolers have water sprayed directly on wet surfaces through which air passes. Any excess water drains off. Air washers recirculate water, and the air flows through a heavily misted area. Water atomized in the airstream evaporates, cooling the air. For either type, using refrigerated water simultane- ously cools and dehumidifies the air. For spaces that require an air washer and high relative humidities (e.g., tobacco and textile pro- cessing areas), heat provided to the sump should provide sufficient | {}
0ebc779d-db4e-448e-8799-8d0952f9d6c4 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Industrial Air Conditioning 15.9 energy for humidification beyond that recovered in the return air- stream. Temperature and humidity of the exit airstream may be con- trolled by varying the temperature of the chilled water and reheat coil and by varying the quantity of air passing through the reheat coil with a dew-point thermostat. It may be necessary to filter air entering the evaporative cooler to ensure that dust or lint does not accumulate and clog the nozzles or evaporating pads. Chemical treatment of the water may be neces- sary to prevent mineral build-up or biological growth on the pads or in the pans. 10. AIR FILTRA TION SYSTEMS Air filtration systems remove contaminants from the building sup- ply or exhaust airstreams. Supply air filtration at the equipment in- take removes particulate contamination that may foul heat exchange surfaces, contaminant products, or present a health hazard to people, animals, or plants. Gaseous contaminants must sometimes be re- moved to prevent exposing personnel to odors or health-threatening fumes. Return air with a significant potential for carrying contam- inants should be recirculated only if it can be filtered enough to minimize personnel exposure. Return air should be exhausted if monitoring and contaminant control cannot be ensured. The supply filtration system usually includes collection media or a filter, a media-retaining device or filter frame, and a filter housing or plenum. For more on filtration systems, see Chapter 29 of the 2016 ASHRAE Handbook- -HVAC Systems and Equipment. Exhaust Air Filtration Systems Exhaust air systems are either (1) general systems that remove air from large spaces or (2) local systems that capture aerosols, heat, or gases at specific locations in a room and transport them so they can be collected, inactivated, and safely discharged to the atmosphere. Air in a general system usually requires minimal or no treatment before being discharged to the atmosphere. Air from local exhaust systems can sometimes be safely discharged to the atmosphere, but may require contaminant removal before being discharged. Exhausted air must meet appropriate air quality standards when defined as a release point based on plant air permitting requirements. Chapters 31 and 32 of this volume and Chapter 30 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment have more information on industrial ventilation and exhaust systems. In exhaust air emission control, fabric-bag filters, glass-fiber fil- ters, venturi scrubbers, and electrostatic precipitators all collect par- ticles. Packed-bed or sieve towers can absorb toxic gases. Activated carbon columns or beds, often with oxidizing agents, are frequently used to absorb toxic or odorous organics and radioactive gases. Outdoor air intakes should be carefully located to avoid recircu- lating contaminated exhaust air. Wind direction, building shape, and location of effluent source strongly influence concentration patterns. Air patterns from wind flowing over buildings are discussed in Chapter 24 of the 2017 ASHRAE Handbook-Fundamentals. The leading edge of the roof interrupts smooth airflow, reducing air pressure at the roof and on the lee side. Exhaust air must be dis- charged through either a vertical stack terminating above the building turbulent-air boundary or a shorter stack with a high enough discharge velocity to project the effluent through the air boundary into the undisturbed air passing over the building. The high discharge prevents fume damage to both the roof and roof- mounted equipment, and keeps fumes away from building air intakes. A high vertical stack is the safest, simplest solution to fume dispersal. Contamination Control In addition to maintaining thermal conditions, air-conditioning systems should control contaminant levels to provide a safe and healthy environment, good housekeeping, and quality control for the processes. Contaminants may include gases, fumes, mists, or airborne particulate matter. They may be produced by a process in the building or contained in the outdoor air. Contamination can be controlled by preventing the release of aerosols or gases into the room and by diluting room air contami- nants. Ifthe process cannot be enclosed, itis best to capture aerosols and gases near their source with a local exhaust system that includes a hood or enclosure, ducts, fan, motor, and exhaust stack. Dilution controls contamination in many applications but may not provide uniform safety for personnel. High local concentrations of contaminants can exist despite a high overall dilution rate. 11. EXHAUST SYSTEMS An exhaust system draws a contaminant away from its source and removes it from the space. An exhaust hood surrounding the point of generation contains the contaminant as much as is practical. The contaminant is transported through ductwork from the space, cleaned as required, and exhausted to the atmosphere. The hood inlet air quantity is established by the velocities required to convey the airborne contaminant. Chapter 33 has more information on local exhaust systems. Design values for average and minimum face velocities are a func- tion of the characteristics of the most hazardous material the hood is expected to handle. Minimum values may be prescribed in codes for exhaust systems. Contaminants with greater mass may require higher face velocities for control. Design face velocities should be set care- fully: too high a velocity can be as hazardous as one too low. Refer to ACGIH (2016) and ASHRAE Standard 110 for more information. Exhaust ductwork should be sized to provide velocities high enough to keep contaminants in suspension. Velocities should ex- ceed the settling velocities for the expected particle size distribution. Selection of materials and construction of exhaust ductwork and fans depend on the nature of the contaminant, ambient temperature, lengths and arrangement of ducts, method of hood fan operation, and flame and smoke spread ratings. Exhausts containing acids, alkalis, solvents, or oils should address corrosion, dissolution, and melting. Condensation in ferrous metal ducts may contribute to corrosion. Consider the dew point of process gases with respect to the sur- rounding ambient temperature. Condensation can be managed by reducing the dew point of the exhaust stream, by vapor barriers, or by using thermal insulation. 12. OPERA TION AND MAINTENANCE Equipment room layout should provide space for cleaning, ser- vicing, and replacing components quickly to minimize system out- ages. Maintenance of refrigeration and heat rejection equipment is essential for proper performance without energy waste. Mainte- nance includes changing system filters periodically. Industrial ap- plications are dirty, so proper selection of filters, careful installation to avoid air bypassing the filter, and prudent filter changing to pre- vent overloading and blowout are required. Dirt lodging on the tips of forward-curved fan blades appreciably reduces air-handling ca- pacity. Fan and motor bearings require lubrication, and fan belts need periodic inspection. Direct- and indirect-fired heaters should be inspected annually. Steam and hot-water heaters have fewer maintenance requirements than comparable equipment with gas or oil burners. For system compatibility, water treatment is essential. Air washers and cooling towers should not be operated unless the water is properly treated. Inc. ASHRAE, 2019 user. single for Licensed | {}
e3034f34-9b2e-4342-92e2-6206e390dcff | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 15.10 13. HEAT RECOVERY AND ENERGY CONSERVATION The process industry often presents opportunities to recover heat from the exhaust airstream for use in preconditioning makeup air. Extreme care must be taken to ensure compatibility of heat ex- changer components and materials with contaminants often found in exhaust streams. For example, brewery spaces are held between 1.7 and 10°C. Exhaust air passes over a heat recovery wheel to pre- condition outdoor makeup air, which in turn controls the level of carbon dioxide contamination. Coated aluminum heat recovery wheels can be subject to premature failure because of caustic clean- ing materials conveyed in the exhaust system. ASHRAE, Inc. Additional consideration should be given to the assessment ofrisk associated with the heat recovery strategy. Frequently, downtime in large industrial facilities can exceed millions of dollars per hour. Costs associated with failure of a heat recovery device can easily overcome savings in energy costs if the result is a facility shutdown. 2019 Control systems for industrial processes and air-conditioning systems differ from commercial direct digital control (DDC) sys- tems in important ways. Modern industrial control systems fall into three categories: 14. CONTROL SYSTEMS user. single for Licensed · Programmable logic controller (PLC) systems. These systems are chosen for industrial environments because of their inherent robustness and speed. They are rated to operate in environments of 50°C, as opposed to 40°C for DDC systems. Also, because the controller does not look up point information from a central data- base, the program scan speed is much greater: a total program scan time of less than 0.1 s is not unusual. Local display screens are available for field panel mounting; however, one of the fol- lowing two systems is required to provide overall plantwide data gathering and reporting. · Distributed control systems (DCS). Like commercial DDC sys- tems, DCS systems are defined as shared logic controllers as opposed to programmable logic controllers. A shared logic con- troller shares the resources a common database of point names to provide point attribute data such as units (% rh, kPa, etc.), point range (0 to 100% rh, 0 to 690 kPa, etc.), logical point name, and software address. This information is shared across all controllers in a given network of controllers and then reported to the user through the graphical user interface (GUI). DCS systems can provide an embedded GUI like DDC systems do, or can work seamlessly with a third-party SCADA system. · Supervisory control and data acquisition (SCADA) systems. SCADA systems are typically overlays that acquire and store data from subordinate DCS, PLC, or other systems. They provide the GUI and display operating system parameters. By contrast, com- mercial DDC or building management systems (BMS) have the graphic engine and data acquisition and storage system embedded into the base operating system. Industrial requirements typically preclude DDC systems to act as a SCADA system because of their limited data communication networks and inability to reli- ably handle large numbers (> 10,000) ofinput and output points in a given system. Industrial controllers can be installed, configured, and/or main- tained by third-party providers (known as system integrators) or by the manufacturer themselves. They have open communication pro- tocols and exchange information over various network protocols such as Modbus (North America) or Profibus (EU). These protocols allow communication between different brands of controllers and the overall network, with BACnet� capability for occasional inte- gration with commercial DDC system where deemed necessary. Industrial systems also allow Ethernet-based protocol (TCP/IP) for 2019 ASHRAE Handbook-HVAC Applications (SI) data exchange in high-speed networks as well as remote Internet- based monitoring and control. Industrial control systems are documented differently than commercial-based DDC systems. The American National Stan- dards Institute (ANSI), in cooperation with International Society of Measurement and Control (ISA), established a standard that defines how engineering documents are prepared (e.g., process and instru- mentation diagrams [P&IDs], instrument naming or tagging con- vention). Commercial systems generally are documented using standards defined by the system manufacturer, who installs and maintains the systems, and their technicians can operate across sev- eral facilities or in different cities. Industrial instrumentation is also quite different from commer- cial DDC systems. Instruments are typically in housings listed for hazardous environments that also provide excellent protection from the moisture, dust, and dirt frequently found in an industrial envi- ronment. Signal types are usually 4 to 20 mA over the range of 0 to 100% of the transmitter span. Hazardous locations use instruments listed specifically for the hazard division and group. Intrinsic safety barriers provide a level of protection by limiting the amount of power consumed by these devices to 1 W or less. 15. LIFE AND PROPERTY SAFETY Human life and property safety must be thoroughly considered in all types ofindustrial project design, construction, installation, start- up, testing, operation, and maintenance. The life and property safety concern should include (but not be limited to) hazards generated in the property and related prevention, effective fire and hazardous gas detection and alarm systems, active fire protection systems, room- to-room pressurization and smoke control, homeland security and emergency response plans, etc. Refer to related NFPA and ACGIH publications for detailed regulations. Toxic Agent/Hazardous Materials Processing Facility Fire. When the fire alarm control panel (FACP) receives alarm signals from local smoke/heat detectors, it sends signals to shut off the smoke/fire dampers (BDs) in the affected fire zone. The FACP also sends an alarm signal to the FCS. The position switch from each BD sends a feedback signal to FCS confirming that the BD has been fully closed; otherwise, a fault alarm is activated at the FCS. Due to airflow blockage, the cascading system upstream room pres- sure increases, and downstream room pressure decreases further. To minimize room pressure upsets, the FCS automatically throttles the upstream supply air pressure control dampers and downstream exhaust air pressure control dampers. During the pressure surge transition, the cascading system pres- sures may rise at the supply air plenum and become more negative at the exhaust air inlet headers. FCS pressure feedback control auto- matically reduces the fan speed of the AHUs and EAFUs accord- ingly. If pressure surges are significant and occur faster than the FCS pressure control response, pressure and vacuum relief dampers in the supply and exhaust headers automatically open to protect ductwork from damage. After the fire has been cleared, the smoke/fire dampers are man- ually reset to the open position from the FACP. Bypass exhausts are provided within fire zones and located strategically to mitigate pres- sure excursion resulting from a fire in critical process rooms. When the bypass mode is initiated, FCS closes the inlet transfer air isola- tion dampers to suppress fire spread, which prevents heat and smoke damage to the EAFUs; activates the bypass exhaust; and places pressure controllers into automatic pressure control mode to minimize pressure surge and airflow impact to surrounding rooms. Loss of Power. During loss of off-site power, essential power is provided to EAFUs and AHUs by the dedicated generator and the standby generators to maintain the toxic areas at slight negative | {}
43d19f88-553f-4090-b915-f5fe4e0137f7 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Industrial Air Conditioning 15.11 pressure relative to ambient to prevent toxic vapor escaping. The adjustable-speed drives (ASDs) of the fans ofEAFUs and AHUs are programmed to allow fast ramp-up when power is restored. Ifa ded- icated generator starts and standby generators fail, the FCS contin- uously monitors and controls the cascading ventilation system to maintain slight negative pressure with reduced flows. When all the generators fail to start, and the total exhaust airflow rate drops to 15% of the system design capacity, the FCS starts closing all TA isolation dampers to prevent toxic vapor migration from highly toxic areas to areas of lower concentrations. 16. COMMISSIONING Several types of HVAC commissioning processes are used for industrial HVAC projects: (1) overall HV AC project commission- ing, (2) construction HVAC project commissioning, and (3) existing-building HVAC commissioning (retrocommissioning). The process described here applies to both new construction and major renovations. For new construction, commissioning should start at the project's inception during the predesign phase, and continue through design, construction, acceptance, training, operation, maintenance, and postacceptance. The owner should retain an HVAC commissioning authority (CA) at the very beginning ofthe predesign phase. The CA develops the scope ofthe commissioning and reviews the design intent during predesign to ensure the project accommodates the commissioning process. The CA also coordinates with the owner, design engineer, and HVAC contractor during preparation of project design and con- struction documents; this includes the overall project execution schedule, preparation and issue of commissioning and construction specifications, and review of contractor submittals. This paves the way for commissioning, and the CA continues to carry out and com- plete the implementation of the planning commissioning process. Participants include the start-up personnel listed during start up, the test and balance company, the process operators, the owner's project authorities, and the commissioning personnel. Commissioning documents include the following: · Certificates and warranties of system completion, along with a complete set of as-built drawings submitted by mechanical, elec- trical, plumbing, control, and fire protection contractors. · If available, all major equipment installation, operation, and maintenance (IOM) manuals from equipment manufacturers. · Records of significant problems and solutions that occurred during start-up and testing. · Certified system test and balance reports, including verified major equipment models and capacities, and tested performance values conforming to system criteria. · A complete room-to-room pressurization map submitted by the test and balance company. · A control system IOM submitted by the control contractor. · When applicable, a certificate of as-built cleanroom cleanliness. The report should be based on testing when the cleanroom facility is complete and all services are connected and functional, but without equipment and operating personnel in the cleanroom. · If the contract scope requires, a certificate of cleanroom cleanli- ness with process running and with operating personnel in the facility. · A commissioning report signed by all attendees. Commissioning requirements for industrial air-conditioning sys- tems (particularly central heating and cooling equipment such as chillers, boilers, air compressors, etc., or nonprocess air-handling systems) often can follow the procedures outlined in ASHRAE Guidelines 0 and 1.1, which use statistical evaluations to define the scope of commissioning activities. Most industrial applications, however, use full commissioning of each point instead of statistical evaluation, because of the process requirements for reliability and the basic functional requirements. In facilities regulated by government agencies, qualification (or validation) of the air-conditioning systems may be required. In these cases, use the appropriate government and industry-specific guidelines instead of ASHRAE Guidelines 0 and 1.1. Qualification follows a more rigorous set of standards for acceptance than com- mercial commissioning: · Risk assessment determines the level of qualification that a given system should undergo. It considers the severity the risk presents (e.g., loss oflife or ofthe system) and the likelihood of occurrence (e.g., once during system life, once a year). The highest risks are those that have the greatest severity as well as the most likely occurrence. In those cases, the qualification requirements are the highest. · Life-cycle assessment is most often used in industrial control systems. Required documentation typically consists of specifica- tions for user requirements, functionality, and design, and the system is qualified under an installation qualification to verify the design specification. An operational qualification verifies the requirements of the functional specification, and the performance qualification verifies the requirements of the user requirement specification. · Testing plans and strategies should reflect the results of the risk assessment and life-cycle assessment. The plans and strategies should also address the resources required to conduct the qualifi- cation, the documentation to be developed, and the appropriate owner team to accept the results. Most importantly, it defines the procedure to be followed when a discrepancy is found. Testing documentation is developed to qualify the system so it can pass an audit by the regulatory agency or a third party retained by the owner. For more information on commissioning, see Chapter 44 and ASHRAE Standard 202-2013. REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal. ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. ACGIH. 2016. Industrial ventilation: A manual of recommended practice, 29th ed. American Conference of Governmental Industrial Hygienists, Cincinnati, OH. ASHRAE. 2013. The commissioning process. ASHRAE Guideline 0-2013. ASHRAE. 2007. HV AC&R technical requirements for the commissioning process. ASHRAE Guideline 1.1-2007. ASHRAE. 2016. Safety code for mechanical refrigeration. ANSI/ASHRAE Standard 15-2016. ASHRAE. 2017. Thermal environmental conditions for human occupancy. ANSI/ASHRAE Standard 55-2017. ASHRAE. 2016. Ventilation for acceptable indoor air quality. ANSI/ ASHRAE Standard 62.1-2016. ASHRAE. 2016. Method of testing performance of laboratory fume hoods. ANSI/ASHRAE Standard 110-2016. ASHRAE. 2013. Commissioning process for buildings and systems. ANSI/ ASHRAE/IES Standard 202-2013. Dukes-Dobos, F., and A. Henschel. 1971. The modification of the WNGT Index for establishing permissible heat exposure limits in occupational work. U.S. Public Health Service Publication TR-69. NFPA. 2014. Recommended practice on static electricity. Standard 77. National Fire Protection Association, Quincy, MA. Spitler, J.D. 2009. Infiltration. Ch. 5 of Load calculation applications manual. ASHRAE. White, W.N., and A. Pahwa. 2003. Heat gain from electrical and control (RP-1104). ASHRAE Research Project, Final Report. equipment Inc. ASHRAE, 2019 user. single for Licensed | {}
40bd9d99-12e2-47cd-a84a-2663facf4836 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 15.12 2019 ASHRAE Handbook- -HVAC Applications (SI) BIBLIOGRAPHY Azer, N.Z. 1982. Design guidelines for spot cooling systems. Parts 1 and 2. ASHRAE Transactions 88(2):81-95 and 88(2):97-116. Papers HO-2667 and HO-2668. Gorton, R.L., and H.M. Bagheri. 1987. Verification of stratified air condi- tioning design. ASHRAE Transactions 93(2):211-227. Paper 3067. Gorton, R.L., and H.M. Bagheri. 1987. Performance characteristics of a system designed for stratified cooling operation during the heating sea- son. ASHRAE Transactions 93(2):367-381. Paper 3077. ISPE. 2008. GAMPⓇ 5: A risk-based approach to compliant GxP comput- erized systems. International Society for Pharmaceutical Engineering, Tampa, FL. ISA. 2009. Instrumentation symbols and identification. ANSI/ISA Standard 5.1-2009. International Society of Automation, Research Triangle Park, NC. NFPA. 2018. Flammable and combustible liquids code. Standard 30. Na- tional Fire Protection Association, Quincy, MA. NFPA. 2018. National fuel gas code. Standard 54. National Fire Protection Association, Quincy, MA. NFPA. 2017. Standard for fire and explosion prevention during cleaning and purging of flammable gas piping systems. Standard 56. National Fire Protection Association, Quincy, MA. NFPA. 2016. Standard for the productions, storage, and handling of lique- fied natural gas (LNG). Standard 59A. National Fire Protection Associ- ation, Quincy, MA. NFPA. 2015. Boiler and combustion systems hazards code. Standard 85. National Fire Protection Association, Quincy, MA. NFPA. 2018. Life safety codeⓇ. Standard 101. National Fire Protection Association, Quincy, MA. NFPA. 2017. Standard for the prevention of fires and explosions in wood processing and woodworking facilities. Standard 664. National Fire Pro- tection Association, Quincy, MA. NFPA. 2016. Standard on disaster/emergency management and business continuity programs. Standard 1600. National Fire Protection Associa- tion, Quincy, MA. West, D.L. 1977. Contamination dispersion and dilution in a ventilated space. ASHRAE Transactions 83(1):125-140. White, W. 2010. Heat gain from electrical and control equipment in indus- trial plants, part II (RP-1395). ASHRAE Research Project, Final Report. Yamazaki, K. 1982. Factorial analysis on conditions affecting the sense of comfort of workers in the air conditioned working environment. ASHRAE Transactions 88(1):241-254. Paper HO-2677. Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
36a8d6f1-bab3-4caf-9c48-f8413963b77e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 16 ENCLOSED VEHICULAR FACILITIES ¦ Tunnels ¦ 16.1 ¦ ¦ --- ¦ --- ¦ ¦ Parking Garages ¦ 16.18 ¦ ¦ Automotive Repair Facilities ¦ 16.23 ¦ ¦ Bus Garages ¦ 16.24 ¦ ¦ Bus Terminals ¦ 16.26 ¦ E NCLOSED vehicular facilities include buildings and infra- through which vehicles travel, are stored, or are re- paired. Vehicles can include those driven by internal combustion en- gines or electric motors. This chapter discusses ventilation requirements for these facilities, accounting for climate and tem- perature control, contaminant level control, and emergency smoke management. Design approaches for various natural and mechanical ventilation systems are covered in this chapter. Tunnel issues are addressed first, followed by the unique aspects of rail and road tunnels, rail stations, bus garages, bus terminals, and enclosed spaces for equipment maintenance in later sections. Finally, information on applicable ventilation equipment is presented. 1. TUNNELS Transport tunnels are unique; vehicles travel at normal speeds, possibly carrying cargo (which may be unknown in road tunnels), and may include the traveling public (as passengers and/ or motor- ists) during both normal and emergency operations. A tunnel is a linear-configured facility, as opposed to most buildings, which are typically more rectangular. This concept is important when con- fronting the need to fight a fire within a tunnel. A tunnel cannot be compartmentalized as readily as a building, which means the fire can only be fought from within the actual fire zone. Limited access and compartmentation create difficulties with containing and sup- pressing a fire. This combination of circumstances requires unique design approaches to both normal and emergency operation. Tunnel Ventilation Concepts Tunnel ventilation must accommodate normal, congested, and emergency conditions. In some cases, temporary ventilation may also be necessary. Normal Mode. Normal ventilation is required during normal operations to control temperature, provide comfort, or control level of pollutants in the facility during normal operations and under normal operating conditions, primarily to ensure the health and comfort of patrons and employees. Congested Mode. Congested ventilation is required during service periods where traffic is slow moving, leading to a reduction or elimi- nation of piston effect. The goals are the same as for normal mode. Emergency Mode. Emergency ventilation is required during an emergency to facilitate safe evacuation and to support firefighting and rescue operations. This is often due to a fire, butit can be any non- normal incident that requires unusual control of the environment in the facility. This includes control of smoke and high temperature from a fire, control of exceedingly high levels of contaminants, and/ or control of other abnormal environmental conditions. Temporary Mode. Temporary ventilation is needed during orig- inal construction or while maintenance-related work is carried out in a tunnel, usually during nonoperational hours. The temporary ventilation is typically removed after construction or after the main- The preparation of this chapter is assigned to TC 5.9, Enclosed Vehicular Facilities. ¦ Tollbooths ¦ 16.29 ¦ ¦ --- ¦ --- ¦ ¦ Diesel Locomotive Facilities ¦ 16.30 ¦ ¦ Equipment ¦ 16.35 ¦ ¦ National and International Safety Standards and Guidelines ¦ 16.40 ¦ tenance work is completed. Ventilation requirements for such tem- porary systems are specified by either state or local mining laws, industrial codes, or the U.S. Occupational Safety and Health Ad- ministration (OSHA) and are not addressed specifically in this chapter. Tunnel Ventilation Systems There are two categories of ventilation systems used in most tun- nels: natural and mechanical. Natural Ventilation. Naturally ventilated facilities rely primarily on atmospheric conditions to maintain airflow and provide a satisfactory environment in the facility. The chief factor affecting the facility environment is the pressure differential created by differ- ences in elevation, ambient air temperature, or wind effects at the boundaries of the facility. Unfortunately, most of these factors are highly variable with time, and thus the resultant natural ventilation is often neither reliable nor consistent. If vehicles are moving through a tunnel-type facility, the piston effect created by the moving vehi- cles may provide additional natural airflow. Mechanical v entilation. A tunnel that is long, has a heavy traffic flow, or experiences frequent adverse atmospheric condi- tions requires fan-based mechanical ventilation. Among the alter- natives available are longitudinal and transverse ventilation. Longitudinal Ventilation. This type of ventilation introduces or removes air from the tunnel at a limited number of points, primarily creating longitudinal airflow along its length. Longitudinal ventila- tion can be accomplished either by injection, using central fans, using jet fans mounted in the facility, or a combination of injection and extraction at intermediate points. Transverse Ventilation. Transverse ventilation uses both a supply duct system and an exhaust duct system to uniformly distribute supply air and collect vitiated air throughout the length of the facility. The supply and exhaust ducts are served by a series of fixed fans, usually housed in a ventilation building or structure. A variant of this type of ventilation is semitransverse ventilation, which uses either a supply or exhaust duct, not both. The balance of airflow is made up via the tunnel portals. Design Approach General Design Criteria. The air quality and corresponding ventilation system airflow requirements in enclosed vehicular spaces are determined primarily by the type and quantity of contam- inants that are generated or introduced into the tunnel and the amount of ventilation needed to limit the high air temperatures or concentrations of these contaminants to acceptable levels for the specific time exposures. Normal and Congested Modes. The maximum allowable concen- trations and levels of exposure for most contaminants are determined by national governing agencies such as the U.S. Environmental Protection Agency (EPA), OSHA, and the American Conference of Governmental Industrial Hygienists (ACGIH). The contaminant generators can be as varied as gasoline or diesel automobiles, diesel or compressed natural gas (CNG) buses and trucks, and diesel locomotives. Even heat generated by air conditioning on 16.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
a3e40f47-e9e9-4e54-a092-d858fc92f055 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 16.2 2019 ASHRAE Handbook-HVAC Applications (SI) electric trains stopped at stations and the pressure transients generated by rapid-transit moving trains can be considered contaminants, the effects of which need to be mitigated. Emergency Mode. Design provisions may be necessary to manage smoke and other products of combustion released during fires to allow safe evacuation, to support firefighting and rescue operations, and to protect the tunnel structure and station infrastruc- ture during fires (Bendelius 2008). In designing for fires, the design fire scenario and associated fire heat release rate need to be quantified. Depending on the level of anal- ysis, the generation of smoke and other products of combustion may also need to be quantified. As a minimum, design for life safety during fires must conform to the specific standards or guidelines of the National Fire Protection Association (NFPA), where applicable. NFPA Standard 130's ventilation requirements are for systems to maintain a "tenable environment along the pathway ofegress from the fire. Standard 130 (2017) defines a tenable environment as "an envi- ronment that permits self-rescue of occupants for a specific period of time"; NFPA Standard 502 (2017) includes a similar definition. Other NFPA codes and standards; ICC (2009a, 2009b, 2009c) building, mechanical, and fire codes; and other statutory require- ments may apply. Separation and pressurization requirements be- tween adjacent facilities should also be considered. Temporary. A temporary mode may be necessary during con- struction or other special condition. Technical Approach. The technical approach differs with facility type; however, there are many similarities in the initial stages of the design process. Determining the length, gradient, and cross section for tunnels is an important first step. Establishing the facility's dynamic clearance envelope is of extreme importance, especially for a tunnel, because all appurtenances, equipment, ductwork, jet fans, etc., must be located outside the envelope, and this may eventually determine the type of ventilation system used. Vehicle speeds, vehicle cross-sectional areas, vehicle design fire scenarios, and fuel-carrying capacity are important considerations for road tunnels, as are train speeds, train headway, and rail car com- bustibility and design fire scenarios for rapid transit and railroad tunnels. Types of cargo to be allowed through the facility, and their re- spective design fire scenarios, should be investigated to determine the ventilation rates and the best system for the application. Simi- larly, for railroad tunnels, it should be determined whether passenger, freight, or both types of trains will be using the facility and if the passenger trains will be powered by diesel/electric power or by electric traction power. The emergency ventilation approach must be fully coordinated with the overall fire protection strategy, the evacuation plan, and the emergency response plan, providing a comprehensive overall life safety program for the tunnel or station. Egress systems must pro- vide for safe evacuation under a wide range of emergency condi- tions. The emergency response plan must help facilitate evacuation and allow for appropriate response to emergencies. Rail and bus stations are large unique structures designed to allow efficient movement oflarge populations and to serve occupants that often arrive in large groups. Stations can be below ground, above ground, or at grade. Although each type of station poses specific challenges, underground facilities tend be the most challenging. Stations can be further complicated by connections to non-transit structures (Tubbs and Meacham 2007). Rail and road tunnels pose a different set of evacuation chal- lenges. These facilities are long, narrow, and underground, often with limited opportunities for stairwells to grade. The linear nature limits initial evacuation, which can pose challenges to the ventila- tion design. Further, the trackway in rail tunnels can be a dangerous environment for untrained occupants. The ventilation and other protection systems must support the evacuation plan. NFPA Standards 502 and 130 provide specific cri- teria for components of the life safety and evacuation systems, but are not universally adopted by authorities. Where road and rail in- frastructure interface with buildings, the International Building CodeⓇ and International Fire CodeⓇ may apply. Several docu- ments are available to provide additional guidance on life safety concepts, evacuation strategies, and calculation methodologies (Bendelius 2008; Colino and Rosenstein 2006; Fruin 1987; Gwynne and Rosenbaum 2008; Proulx 2008; Tubbs and Meacham 2007). Critical Velocity. Manual calculations and resources for the emission and combustion data are given for each enclosed vehicular facility type in the respective sections. A first step in determining the order of magnitude for the ventilation rate required to control the movement ofthe heat and smoke layer generated by a fire in a tunnel is to apply the critical velocity criterion. This approach is described here, and can be used for all types of tunnel applications. The simultaneous solution of Equations (1) and (2), by iteration, determines the critical velocity (Kennedy et al. 1996), which is the minimum steady-state average bulk velocity of ventilation air moving toward the fire needed to prevent backlayering: 1/3 gHq Vc = K1KG cpATF (1) q TF = + T cpAV c where (2) ¦ Vc = critical velocity, m/s ¦ ¦ --- ¦ ¦ TF = average temperature of fire site gases, K ¦ ¦ K1 = 0.606 ¦ ¦ KG = grade factor (see Figure 1) ¦ ¦ g = acceleration caused by gravity, m/s2 ¦ ¦ H = height of duct or tunnel at fire site, m ¦ ¦ q = heat that fire adds directly to air at fire site, kW = average density of approach (upstream) air, kg/m3 ¦ A = area perpendicular to flow, m2 Cp = specific heat of air, kJ/(kg · K) T = temperature of approach air, K It is usual to study several alternative ventilation schemes, each using different variants and/or combinations of ventilation systems (longitudinal, transverse, etc.). Some types of systems, such as fully transverse, are almost exclusively used on road tunnels only. When selecting ventilation equipment and the number of fans and types of drives, consideration should be given to efficiency, reliability, and noise. Most of these equipment attributes are re- flected in a life-cycle cost analysis of the alternatives. Chart Type: line 6 4 2 0 -2 -4 -6 item_01 1.0% 1.0% 1.0% 1.0% 1.1% 1.1% 1.1% Fig. 1 Roadway Grade Factor Inc. ASHRAE, 2019 user. single for Licensed | {}
7a418cb2-5fed-465b-8f21-7e6869aa11a5 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Enclosed Vehicular Facilities 16.3 Ifthe effectiveness ofthe system to provide for fire life-safety con- ditions is not evident from the manual analysis or one-dimensional computer models such as subway environment simulation (SES), the designer should investigate using a computational fluid dynamics (CFD) program to accurately determine the smoke and temperature distribution in both the steady-state and transient conditions. Computer Modeling and Simulation. The applicable NFPA standards for road tunnels (NFPA Standard 502) and for railroad rapid transit tunnels (NFPA Standard 130) require engineering anal- ysis for tunnels greater than a certain length, to prove that the smoke and heat layer is controlled. Often the best way to show that the re- quirements are met is by using a CFD program with post-processing capabilities that feed the results into another program capable of pro- ducing a still picture and/or animated graphical representation of the results. All the commonly used computer programs and their specific capabilities are discussed in the following paragraphs. SES. The predominant worldwide tool for analyzing the aero- thermodynamic environment of rapid transit rail tunnels is the Subway Environment Simulation (SES) computer program (DOT 1997a). SES is a one-dimensional network model that is used to evaluate longitudinal airflow in tunnels. The model predicts air- flow rates, velocities and temperatures in the subway environment caused by train movement or fans, as well as the station cooling loads required to maintain the public areas of the station to prede- termined design conditions throughout the year. This program contains a fire model that can simulate longitudinal airflow required to overcome backlayering and control smoke movement in a tunnel. Output from the SES can be applied as boundary or ini- tial conditions for three-dimensional CFD modelling of the tunnel and station environments. The SES program is in the public domain, available from the Volpe National Transportation Sys- tems Center in Cambridge, MA. TUNVEN. This program solves coupled one-dimensional, steady- state tunnel aerodynamic and advection equations. It can predict quasi-steady-state longitudinal air velocities and concentrations of CO, NOx, and total hydrocarbons along a road tunnel for a wide range of tunnel designs, traffic loads, and external ambient conditions. The program can also be used to model all common road tunnel ventilation systems (i.e., natural, longitudinal, semitransverse, and transverse). The user must update emissions data for the calendar year of interest. The program is available from the National Techni- cal Information Service (NTIS 1980). Computational Fluid Dynamics (CFD). CFD software can model operating conditions in tunnels and stations and predict the resulting environment. In areas of geometrical complexity, CFD is the appro- priate tool to predict three-dimensional patterns of airflow, tempera- ture, and other flow variables, including concentration of species, which may vary with time and space. Computational fluid dynamics software is the design tool of choice to obtain an optimum design, because experimental methods are costly, complex, and yield lim- ited information. SOL VENT. SOL VENT is a specific CFD model developed as part of the Memorial Tunnel Fire Ventilation Test Program for simulat- ing road tunnel fluid flow, heat transfer, and smoke transport. SOL- VENT can be applied to all ventilation systems used in road tunnels, including those based on natural airflow. The program results have been validated against data from Massachusetts Highway Depart- ment and Federal Highway Authority (MHD/FHWA 1995). Fire Dynamics Simulator (FDS). FDS is a Computational Fluid Dynamics (CFD) model of buoyancy-driven fluid flow from a fire. A separate code called Smokeview is used to visualize data output from FDS. These applications can also be configured to model pol- lutant levels outside the portals and around the exhaust stacks of tunnels. Both of these public domain programs are under active development and can be obtained from National Institute of Stan- dards and Technology (NIST). Other CFD programs (too numerous to include here), both com- mercially available and in the public domain, have been used to model fire scenarios in road and rapid transit tunnels and stations. The strengths and weaknesses of each program should be investi- gated beforehand, and validation of results against experimental data or an equivalent program is encouraged. Tunnel Fires Fires occurring in tunnels are more difficult to deal with than those occurring in one of the other enclosed vehicular facilities, in a normal building, or in the open. In a tunnel, firefighting is extremely complex, because access to the tunnel is difficult in the event of a fire. The fire cannot be fought from outside the tunnel, as can be done with a building; it must be fought from within the tunnel, often in the same space where the fire is burning. Fires occur in tunnels far less frequently than in buildings; how- ever, because of the unique nature of a tunnel fire, they are more dif- ficult to suppress and extinguish and usually get more attention. There is a long list of tunnel fires; the most complete history of fires in tunnels exists for road tunnels, a partial listing of which is in- cluded in Table 1 . Similar information is available for rail fires (Meacham et al. 2010). Design Fires. Design fires form the base input for emergency ventilation design analyses and are defined in terms of heat release rate, species output, and soot yields as functions of time. A design fire scenario is an input parameter that defines the igni- tion source, fire growth on the first item, possible spread of fire to adjacent combustibles, interaction between the fire and the enclo- sure and environment, and eventual fire decay and extinction. Limited data are available regarding the magnitude and severity of vehicle design fires. In the absence of more specific data, the information available provides first-order guidance in selecting an appropriate design fire for the evaluation of an enclosed vehicular facility such as a tunnel (road or rail) or station (bus or rail). PIARC (1999) and NFPA Standard 502 provide summaries of vehicle fire tests. Additional information can be found in Atkinson et al. (2001), Ingason (2006), Joyeux (1997), and Mangs and Keski- Rahkonen (1994a, 1994b). Fire Detection. Fire detection systems are necessary to alert tunnel operators of potential unsafe conditions. There are a range of methods available to detect fire and smoke within road/rail tunnels and rail stations, including linear (line-type) heat detection, CCTV video image smoke detection, flame detection, smoke and heat detectors, and spot-type detection. Fire detection systems should be selected to support the fire safety goals and objectives and the overall fire safety program, which can include notifying occupants to allow for safe evacuation, modifying tunnel ventilation or opera- tions, and notifying emergency responders. NFPA Standards 130 and 502 provide general requirements for fire detections systems in transportation tunnels. These documents reference codes, such as NFPA Standard 72, that provide design requirements for fire detection and occupant notification. Publi- cations developed by the Road Tunnel Operation Technical Com- mittee of PIARC (2007b, 2008) include specific guidance on the application of these systems. There have been several research projects that can also provide additional information to assist with developing detection system concepts and designs (Liu et al. 2006, 2009; Kashef et al. 2009; Zalosh and Chantranuwat 2003). Bende- lius (2008) provides information on advantages and disadvantages and selection of fire detection methods in tunnels. Road Tunnels A road tunnel is an enclosed vehicular facility with an operating roadway for motor vehicles passing through it. Road tunnels may be underwater (subaqueous), mountain, or urban, or may be created by air-right structures over a roadway or overbuilds of a roadway. Inc. ASHRAE, 2019 user. single for Licensed | {}
df64d580-ebfe-4384-931a-9e2c99cc5adc | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 16.4 2019 ASHRAE Handbook- - HVAC Applications (SI) Table 1 List of Road Tunnel Fires ¦ ¦ ¦ ¦ ¦ ¦ Damage ¦ Damage ¦ Damage ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Year ¦ Tunnel ¦ Country ¦ Length, m ¦ Fire Duration ¦ People ¦ Vehicles ¦ Structure ¦ ¦ 1949 ¦ Holland ¦ United States ¦ 2 550 ¦ 4h ¦ 66 injured ¦ 10 trucks 13 cars ¦ Serious ¦ ¦ 1974 ¦ Mont Blanc ¦ France/Italy ¦ 11 600 ¦ 15 min ¦ 1 injured ¦ ¦ ¦ ¦ 1976 ¦ Crossing BP ¦ France ¦ 430 ¦ 1 h ¦ 12 injured ¦ 1 truck ¦ Serious ¦ ¦ 1978 ¦ Velsen ¦ Netherlands ¦ 770 ¦ 1 h 20 min ¦ 5 dead 5 injured ¦ 4 trucks 2 cars ¦ Serious ¦ ¦ 1979 ¦ Nihonzaka ¦ Japan ¦ 2 045 ¦ 159 h ¦ 7 dead 1 injured ¦ 127 trucks 46 cars ¦ Serious ¦ ¦ 1980 ¦ Kajiwara ¦ Japan ¦ 740 ¦ ¦ 1 dead ¦ 2 trucks ¦ Serious ¦ ¦ 1982 ¦ Caldecott ¦ United States ¦ 1 028 ¦ 2 h 40 min ¦ 7 dead 2 injured ¦ 3 trucks 1 bus 4 cars ¦ Serious ¦ ¦ 1983 ¦ Pecorila Galleria ¦ Italy ¦ 662 ¦ ¦ 9 dead 22 injured ¦ 10 cars ¦ Limited ¦ ¦ 1986 ¦ L 'Arme ¦ France ¦ 1 105 ¦ - ¦ 3 dead 5 injured ¦ 1 truck 4 cars ¦ Limited ¦ ¦ 1987 ¦ Gumefens ¦ Switzerland ¦ 343 ¦ 2h ¦ 2 dead ¦ 2 trucks 1 van ¦ Slight ¦ ¦ 1990 ¦ R⌀ldal ¦ Norway ¦ 4 656 ¦ 50 min ¦ 1 injured ¦ ¦ Limited ¦ ¦ 1990 ¦ Mont Blanc ¦ France/Italy ¦ 11 600 ¦ ¦ 2 injured ¦ 1 truck ¦ Limited ¦ ¦ 1993 ¦ Serra Ripoli ¦ Italy ¦ 442 ¦ 2h 30 min ¦ 4 dead 4 injured ¦ 5 trucks 11 cars ¦ Limited ¦ ¦ 1993 ¦ Hovden ¦ Norway ¦ 1 290 ¦ 1 h ¦ 5 injured ¦ 1 motorcycle 2 cars ¦ Limited ¦ ¦ 1994 ¦ Huguenot ¦ South Africa ¦ 3 914 ¦ 1 h ¦ 1 dead 28 injured ¦ 1 bus ¦ Serious ¦ ¦ 1995 ¦ Pfander ¦ Austria ¦ 6 719 ¦ 1 h ¦ 3 dead 4 injured ¦ 1 truck 1 van 1 car ¦ Serious ¦ ¦ 1996 ¦ Isola delle Femmine ¦ Italy ¦ 148 ¦ ¦ 5 dead 20 injured ¦ 1 tanker 1 bus 18 cars ¦ Serious ¦ ¦ 1999 ¦ Mont Blanc ¦ France/Italy ¦ 11 600 ¦ ¦ 39 dead ¦ 23 trucks 10 cars 1 motorcycle 2 fire engines ¦ Serious ¦ ¦ 1999 ¦ Tauern ¦ Austria ¦ 6 401 ¦ ¦ 12 dead 49 injured ¦ 14 trucks 26 cars ¦ Serious ¦ ¦ 2000 ¦ Seljestad ¦ Norway ¦ 1 272 ¦ 45 min ¦ 6 injured ¦ 1 truck 4 cars 1 motorcycle ¦ ¦ ¦ 2001 ¦ Praponti ¦ Italy ¦ 4 409 ¦ ¦ 19 injured ¦ ¦ Serious ¦ ¦ 2001 ¦ Gleinalm ¦ Austria ¦ 8 320 ¦ ¦ 5 dead 4 injured ¦ ¦ ¦ ¦ 2001 ¦ Propontin ¦ Italy ¦ 4 409 ¦ ¦ 14 injured ¦ 1 car ¦ ¦ ¦ 2001 ¦ Gleinalm ¦ Austria ¦ 8 300 ¦ ¦ 5 dead 4 injured ¦ ¦ ¦ ¦ 2001 ¦ Guldborgsund ¦ Denmark ¦ 460 ¦ ¦ 5 dead 6 injured ¦ ¦ ¦ ¦ 2001 ¦ St. Gotthard ¦ Switzerland ¦ 16 920 ¦ ¦ 11 dead ¦ 2 heavy-goods vehicle ¦ ¦ ¦ 2002 ¦ Ostwaldiberg ¦ Austria ¦ ¦ ¦ 1 dead ¦ ¦ ¦ ¦ 2003 ¦ 44-France ¦ France ¦ 618 ¦ ¦ 2 dead ¦ 1 car 1 motorcycle ¦ ¦ ¦ 2003 ¦ Baregg ¦ Switzerland ¦ 1 390 ¦ ¦ 2 dead 21 injured ¦ 4 trucks 3 fire engines ¦ Serious ¦ ¦ 2004 ¦ Baregg ¦ Switzerland ¦ 1 080 ¦ ¦ 1 dead 1 injured ¦ 1 car 1 truck ¦ ¦ ¦ 2005 ¦ Frejus ¦ France-Italy ¦ 12 870 ¦ 6h ¦ 2 dead ¦ 4 trucks 1 fire engine ¦ ¦ ¦ 2006 ¦ Viamala ¦ Switzerland ¦ 742 ¦ ¦ 9 dead 6 injured ¦ ¦ ¦ Source: PIARC (2007a, 2007b) Inc. ASHRAE, 2019 user. single for Licensed | {}
d117cd93-1f74-4dc4-9650-ce98398e1ff4 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Enclosed Vehicular Facilities 16.5 All road tunnels require ventilation to remove contaminants pro- duced during normal engine operation. Normal ventilation may be provided by natural means, by traffic-induced piston effects, or by mechanical equipment. The method selected should be the most economical in both construction and operating costs. Ventilation must also provide control of smoke and heated gases from a fire in the tunnel. Smoke flow control is needed to provide an environment suitable for both evacuation and rescue in the evacua- tion path. Emergency ventilation can be provided by natural means, by taking advantage of the buoyancy of smoke and hot gases, or by mechanical means. Ventilation Modes. A range of mechanical ventilation is typically considered for road tunnels: normal, congested, emergency, and tem- porary, as discussed in the section on Tunnel Ventilation Concepts. v entilation Systems. v entilation must dilute contaminants during normal and congested tunnel operations and control smoke during emergency operations. Factors affecting ventilation system selection include tunnel length, cross section, and grade; surrounding environment; traffic volume, direction (i.e., unidirec- tional or bidirectional), and mix; and construction cost. Natural and traffic-induced ventilation systems are adequate for relatively short tunnels, and for those with low traffic volume or density. Long, heavily traveled tunnels should have mechanical ventilation systems. The tunnel length at which this change takes effect is somewhere between 350 and 650 m. Natural Ventilation. Airflow through a naturally ventilated tunnel can be portal-to-portal (Figure 2A) or portal-to-shaft (Fig- ure 2B). Portal-to-portal flow functions best with unidirectional traffic, which produces a consistent, positive airflow. In this case, air speed in the roadway area is relatively uniform, and the con- taminant concentration increases to a maximum at the exit portal. Under adverse atmospheric conditions, air speed may decrease and contaminant concentration may increase, as shown by the dashed line in Figure 2A. Introducing bidirectional traffic into such a tunnel further re- duces longitudinal airflow and increases the average contaminant concentration. The maximum contaminant level in a tunnel with bidirectional traffic will not likely occur at the portal, and will not necessarily occur at the midpoint of the tunnel. ![image](/image/placeholder) EFFECT OF ADVERSE METEOROLOGICAL CONDITIONS CONTAMINANT CONCENTRATION IN TUNNEL A. PORTAL-TO-PORTAL SHAFT CONTAMINANT CONCENTRATION IN TUNNEL B. PORTAL-TO-SHAFT Fig. 2 Natural Ventilation A naturally ventilated tunnel with an intermediate shaft (Figure 2B) is better suited for bidirectional traffic; however, airflow through the shaft is also affected by adverse atmospheric conditions. The stack effect benefit of the shaft depends on air/rock temperatures, wind, and shaft height. Adding more than one shaft to a tunnel may be more of a disadvantage than an advantage, because a pocket of contaminated air can be trapped between the shafts. Naturally ventilated tunnels under 1000 m long do not require emergency ventilation to extract smoke and hot gases generated during a fire if it can be shown by an engineering analysis that the level of safety provided by a mechanical ventilation system can be equaled or exceeded by enhancing the means of egress, natural ven- tilation, or the use of smoke storage as approved by the authority having jurisdiction (per NFPA Standard 502). Because of the un- certainties of natural ventilation, especially the effects of adverse meteorological and operating conditions, reliance on natural venti- lation to maintain carbon monoxide (CO) levels for tunnels over 240 m long should be thoroughly evaluated. This is particularly important for tunnels with anticipated heavy or congested traffic. If natural ventilation is deemed inadequate, a mechanical system should be considered for normal operations. Smoke from a fire in a tunnel with only natural ventilation is driven primarily by the buoyant effects of hot gases and tends to flow upgrade. The steeper the grade, the faster the smoke moves, thus restricting the ability of motorists trapped between the incident and a portal at higher elevation to evacuate the tunnel safely. As shown in Table 2, the Massachusetts Highway Department and Fed- eral Highway Administration (MHD/FHW A) (1995) demonstrated how smoke moves in a naturally ventilated tunnel. Mechanical Ventilation. A tunnel that is long, has a heavy traffic flow, or experiences frequent adverse atmospheric conditions, requires fan-based mechanical ventilation. Options include longitu- dinal ventilation, semitransverse ventilation, and full transverse ventilation. Longitudinal ventilation introduces or removes air from the tunnel at a limited number of points, creating longitudinal airflow along the roadway. Longitudinal ventilation can be accomplished either by push-pull vent shafts, injection, jet fan operation, or a combination of injection and extraction at intermediate points in the tunnel. Injectors and jet fans are classified as impulse systems, because they impart a momentum to the tunnel flow, as the primary high-velocity jet diffuses out. At start-up, this thrust causes the air in the tunnel to accelerate until equilibrium is established between this force and the opposing drag forces due to viscous friction and the additional pressure losses at the tunnel portals, traffic, wind, and fire, etc. Injection longitudinal ventilation, frequently used in rail tun- nels, uses externally located fans to inject air into the tunnel through a high-velocity Saccardo nozzle, as shown in Figure 3A. This air injection, usually in the direction of traffic flow, induces additional longitudinal airflow. The Saccardo nozzle functions on the principle that a high-velocity air jet injected at a small angle to the tunnel axis can induce a high-volume longitudinal airflow in the tunnel. The Table 2 Smoke Movement During Natural Ventilation Tests ¦ Test No. ¦ Fire Heat Release Rate, MW ¦ Fire Heat Release Rate, MW ¦ Smoke Layer Begins Descent, min ¦ Smoke Fills Tunnel Roadway, min ¦ Peak Smoke Velocity, m/s ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Test No. ¦ Nominal ¦ Peak ¦ Smoke Layer Begins Descent, min ¦ Smoke Fills Tunnel Roadway, min ¦ Peak Smoke Velocity, m/s ¦ ¦ 501 ¦ 20 ¦ 29 ¦ 3+ ¦ 5 ¦ 6.1 ¦ ¦ 502 ¦ 50 ¦ 57 ¦ 1+ ¦ 3 ¦ 8.1 ¦ Note: Tunnel grade is 3.2%. Inc. ASHRAE, 2019 user. single for Licensed | {}
d0cebda0-516d-4162-9944-98cafc356536 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 16.6 2019 ASHRAE Handbook-HVAC Applications (SI) ![image](/image/placeholder) FAN EFFECT OF ADVERSE CONCENTRATION METEOROLOGICAL CONTAMINANT CONDITIONS TUNNEL IN A. WITH JET INJECTION FAN � 호 EFFECT OF ONE-WAY TRAFFIC OR ADVERSE METEOROLOGICAL CONDITIONS CONCENTRATION CONTAMINANT IN TUNNEL B. WITH ONE SHAFT FAN FAN CONCENTRATION EFFECT OF ADVERSE CONTAMINANT METEOROLOGICAL CONDITIONS IN TUNNEL C. WITH TWO SHAFTS AND JET INJECTION FAN CONCENTRATION CONTAMINANT TUNNEL IN D. WITH JET FANS Fig. 3 Longitudinal Ventilation amount of induced flow depends primarily on the nozzle area, dis- charge velocity and angle of the nozzle, as well as downstream air resistances. This type of ventilation is most effective with unidirec- tional traffic flow. With injection longitudinal ventilation, air speed remains uni- form throughout the tunnel, and the contaminant concentration in- creases from zero at the entrance to a maximum at the exit. Adverse atmospheric conditions can reduce system effectiveness. The con- taminant level at the exit increases as airflow decreases or tunnel length increases. Injection longitudinal ventilation, with supply at a limited number of tunnel locations, is economical because it requires the fewest fans, places the least operating burden on fans, and requires no distribution air ducts. As the length of the tunnel increases, how- ever, disadvantages become apparent, such as excessive air veloci- ties in the roadway and smoke being drawn the entire length of the roadway during an emergency. The main aerodynamic differences between the jet fan and Sac- cardo injectors are that the injectors impart thrust at one location in the tunnel, whereas in jet fan systems this thrust is distributed along the tunnel. Injectors use outdoor air as primary flow, whereas the primary airflow in jet fans enters the fan inlet from the tunnel. Saccardo injectors may operate in a flow induction mode (low tunnel air resistance) or flow rejection (high tunnel air resistance); both are acceptable. This means there may be flow reversal at the nozzle position with flow exiting the near portal, whereas jet fans always induce flow from one portal to the other. Flow under jet fans in a highly resistive tunnel may recirculate, but this is a strictly local feature. A brief comparison of the technical and economic features of the two longitudinal impulse ventilation systems reveals the following: · Jet fans have little or no civil engineering costs for installation, but have significant electrical cabling costs. Saccardo injectors require expensive civil engineering work to install the fans at the tunnel portal, with no cabling distribution costs. · Routine maintenance or emergency repair work on jet fans usually requires disruption of normal tunnel service and availability; this is not the case for Saccardo injectors, which can be accessed externally. · Saccardo injectors eliminate electrical cabling in the tunnel, pro- viding a clear safety and cost advantage over jet fans. · Jet fans take up headroom in the tunnel ceiling, which limits the effective dynamic clearance envelope of the traffic, whereas Sac- cardo injectors are located outside the tunnel, making them ideal in tightly configured tunnels. · Saccardo injectors deliver their thrust at a single point, making them quite vulnerable to local tunnel fixtures. For example, a badly placed traffic sign, LED display, lighting equipment, or any significant blockage near the outlet of an ejector can cause a dramatic drop in ejector performance, whereas jet fans are less affected, because their thrust is distributed. · Jet fans are also derated when operating at elevated temperatures during a fire (lower density), whereas injectors are both safely outside the fire's reach as well as immune to thrust reduction by virtue of using fresh air for primary intake. This makes Saccardo injectors ideal for emergency smoke clearance. The high air velocities in the path of egress should be assessed. These relative merits are crucial at the initial concept phase, when deciding on the type of ventilation system for any particular tunnel. A longitudinal ventilation system with one fan shaft (Figure 3B) is similar to the naturally ventilated system with a shaft, except that it provides a positive stack effect. Bidirectional traffic in a tunnel ventilated this way causes peak contaminant concentration at the shaft. For unidirectional tunnels, contaminant levels become unbal- anced. Inc. ASHRAE, 2019 user. single for Licensed | {}
632e8c97-795b-43f2-99b7-953e256a60b8 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Enclosed Vehicular Facilities 16.7 Another form of longitudinal system has two shafts near the cen- ter of the tunnel: one for exhaust and one for supply (Figure 3C). In this arrangement, part of the air flowing in the roadway is replaced by the interaction at the shafts, which reduces the concentration of contaminants in the second half of the tunnel. This concept is only effective for tunnels with unidirectional traffic flow. Adverse wind conditions can reduce tunnel airflow by short-circuiting the flow of air from the supply fan shaft/injection port to the exhaust fan/shaft, which causes contaminant concentrations to increase in the second half of the tunnel. Construction costs of two-shaft tunnels can be reduced if a single shaft with a dividing wall is constructed. However, this significantly increases the potential for short-circuited airflows from supply shaft to exhaust shaft; under these circumstances, the separation between exhaust shaft and intake shaft should be maximized. Jet fan longitudinal ventilation has been installed in a number of tunnels worldwide. With this scheme, specially designed axial fans (jet fans) are mounted at the tunnel ceiling (Figure 3D). This system eliminates the space needed to house ventilation fans in a sep- arate structure or ventilation building, but may require greater tunnel height or width to accommodate the jet fans so that they are outside of the tunnel's dynamic clearance envelope. This envelope, formed by the vertical and horizontal planes surrounding the roadway in a tunnel, defines the maximum limits of the predicted vertical and lat- eral movement of vehicles traveling on the roadway at design speed. As tunnel length increases, however, disadvantages become apparent, such as excessive air speed in the roadway and smoke being drawn the entire length of the roadway during an emergency. Longitudinal ventilation is the most effective method of smoke control in a road tunnel with unidirectional traffic. A ventilation system must generate sufficient longitudinal air velocity to prevent backlayering of smoke (movement of smoke and hot gases against ventilation airflow in the tunnel roadway). The air velocity neces- sary to prevent backlayering over stalled or blocked motor vehicles is the minimum velocity needed for smoke control in a longitudinal ventilation system and is known as the critical velocity. Semitransverse ventilation can be configured for supply or exhaust. This type of ventilation involves the uniform distribution (supply) or collection (exhaust) of air throughout the length of a road tunnel. Semitransverse ventilation is normally used in tunnels up to about 2000 m; beyond that length, tunnel air velocity near the portals becomes excessive. Supply semitransverse ventilation in a tunnel with bidirec- tional traffic produces a uniform level of contaminants throughout, because air and vehicle exhaust gases enter the roadway area at the same uniform rate. With unidirectional traffic, additional airflow is generated by vehicle movement, thus reducing the contaminant level in the first half of the tunnel (Figure 4A). Because tunnel airflow is fan-generated, this type of ventilation is not adversely affected by atmospheric conditions. Air flows the length of the tunnel in a duct with supply outlets spaced at predeter- mined distances. Fresh air is best introduced at vehicle exhaust pipe level to dilute exhaust gases immediately. The pressure differential between the duct and the roadway must be enough to counteract the effects of piston action and adverse atmospheric winds. If a fire occurs in the tunnel, the supply air initially dilutes the smoke. Supply semitransverse ventilation should be operated in reverse mode for the emergency, so that fresh air enters through the portals and creates a tenable environment for both emergency egress and firefighter ingress. Therefore, a supply semitransverse ventila- tion system should preferably have a ceiling supply (in spite of the disadvantage during normal operations) and reversible fans, so that smoke can be drawn up to the ceiling during a tunnel fire. Exhaust semitransverse ventilation (Figure 4B) in a tunnel with unidirectional traffic flow produces a maximum contaminant concentration at the exit portal. In a tunnel with bidirectional traffic ![image](/image/placeholder) REVERSIBLE FAN SUPPLY AIR DUCT FAN SUPPLY AIR DUCT EFFECT OF TWO-WAY TRAFFIC OR ADVERSE METEOROLOGICAL CONCENTRATION CONDITIONS CONTAMINANT IN TUNNEL ONE-WAY TRAFFIC A. WITH SUPPLY DUCT FAN EXHAUST AIR DUCT CONCENTRATION CONTAMINANT TWO-WAY TRAFFIC TUNNEL ONE-WAY TRAFFIC IN (b) B. WITH EXHAUST DUCT FAN EXHAUST AIR FAN DUCT SUPPLY AIR DUCT CONCENTRATION CONTAMINANT ![image](/image/placeholder) TWO-WAYTRAFFIC ONE-WAY TRAFFIC IN TUNNEL C. WITH SUPPLY AND EXHAUST DUCT Fig. 4 Semitransverse Ventilation Inc. ASHRAE, 2019 user. single for Licensed | {}
7263ba89-87e8-48e9-bf86-381e1ab3e3ef | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 16.8 flow, the maximum concentration of contaminants is located near the center of the tunnel. A combination supply and exhaust semi- transverse system (Figure 4C) should be applied only in a unidirec- tional tunnel where air entering with the traffic stream is exhausted in the first half of the tunnel, and air supplied in the second half of the tunnel is exhausted through the exit portal. In a fire emergency, both exhaust semitransverse ventilation and (reversed) semitransverse supply create a longitudinal air velocity in the tunnel roadway, and extract smoke and hot gases at uniform intervals. Full transverse ventilation is used in extremely long tunnels and in tunnels with heavy traffic volume. It uses both a supply and an exhaust duct system to uniformly distribute supply air and collect vitiated air throughout the tunnel length (Figure 5). Because a tun- nel with full transverse ventilation is typically long and served by more than one mechanical ventilation system, it is usually config- ured into ventilation zones, each served by a dedicated set of supply and exhaust fans. Each zone can be operated independently of adja- cent zones, so the tunnel operator can change the direction of air- flow in the tunnel by varying the level of operation of the supply and exhaust fans. This feature is important during fire emergencies. With this ventilation system arrangement in balanced operation, air pressure along the roadway is uniform and there is no longi- tudinal airflow except that generated by the traffic piston effect, which tends to reduce contaminant levels. The pressure differential between the ducts and the roadway must be sufficient to ensure proper air distribution under all ventilation conditions. During a fire, exhaust fans in the full transverse system should operate at the highest available capacity, and supply fans should operate at a somewhat lower capacity. This allows the stratified smoke layer (at the tunnel ceiling) to remain at that higher elevation and be extracted by the exhaust system without mixing, and allows fresh air to enter through the portals, which creates a tenable environment for both emergency egress and firefighter ingress. In longer tunnels, individual ventilation zones should be able to control smoke flow so that the zone with traffic trapped behind a fire is provided with maximum supply and no exhaust, and the zone on the other side of the fire (where unimpeded traffic has continued onward) is provided with maximum exhaust and minimum or no supply. Full-scale tests conducted by Fieldner et al. (1921) showed that supply air inlets should be at vehicle exhaust pipe level, and exhaust outlets should be in the tunnel ceiling for rapid dilution of exhaust gases under nonemergency operation. Depending on ![image](/image/placeholder) FAN FAN EXHAUST AIR DUCT SUPPLY AIR DUCT CONCENTRATION CONTAMINANT ONE-WAY TRAFFIC M TUNNEL Fig. 5 Full Transverse Ventilation 2019 ASHRAE Handbook-HVAC Applications (SI) the number of traffic lanes and tunnel width, airflow can be con- centrated on one side, or divided over two sides. Other Ventilation Systems. There are many variations and combina- tions of the road tunnel ventilation systems described here. Most hybrid systems are configured to solve a particular problem faced in the devel- opment and planning of a specific tunnel, such as excessive air contam- inants exiting at the portal(s). Figure 6 shows a hybrid system developed for a tunnel with a near-zero level of acceptable contaminant discharge at one portal. This system is essentially a semitransverse sup- ply system, with a semitransverse exhaust system added in section 3. The exhaust system minimizes pollutant discharge at the exit portal, which is located near extremely sensitive environmental receptors. Ventilation System Enhancements. Single-point extraction is an enhancement to a transverse system that adds large openings to the extraction (or exhaust) duct. These openings include devices that can be operated during a fire emergency to extract a large volume of smoke as close to the fire source as possible. Tests proved this con- cept effective in reducing air temperature and smoke volume in the tunnel. The size ofthe duct openings tested ranged from 9.3 to 28 m2 (MHD/FHWA 1995). Oversized exhaust ports are simply expanded exhaust ports installed in the exhaust duct of a transverse or semitransverse ventilation system. Two methods are used to create this configura- tion. One is to install a damper with a fusible link; another uses a material that, when heated to a specific temperature, melts and opens the airway. Meltable materials showed only limited success in testing (MHD/FHWA 1995). Normal Ventilation Air Quantities. Contaminant Emission Rates. Because of the asphyxiate nature of the gas, CO is the exhaust gas constituent of greatest concern from spark-ignition engines. From compression-ignition (diesel) engines, the critical contaminants are nitrogen oxides (NOx) such as nitric oxide (NO) and nitrogen dioxide (NO2). Tests and operating experience indi- cate that, when CO level is properly diluted, other dangerous and objec- tionable exhaust by-products are also diluted to acceptable levels, although this trend needs review with respect to newer vehicle fleets. An exception is the large amount of unburned hydrocarbons from vehi- cles with diesel engines; when diesel-engine vehicles exceed 15% of the traffic mix, visibility in the tunnel can become a serious concern. In addition, suspended particles from tires and general road dust are grad- ually forming a larger percentage of particulate matter in the tunnel environment, and must be considered in addition to engine emissions. The section on Bus Terminals includes further information on diesel engine contaminants and their dilution. v ehicle emissions of CO, NO V hydrocarbons for any given and calendar year can be predicted for cars and trucks operating in the United States by using the MOBILE models, developed and main- tained by the U.S. Environmental Protection Agency (EPA 2002). In contaminant emission rate analyses, the following practices and assumptions may be implemented: ![image](/image/placeholder) EXHAUST FAN SUPPLY ▼▼ SUPPLY FANS 입원 EXHAUST ROADWAY FANS DUCT EXHAUST DICTION OF サ1- SUPPLY DUCT SUPPLY DUCT SECTION 1 SECTION 2 SECTION 3 Fig. 6 Combined Ventilation System Inc. ASHRAE, 2019 user. single for Licensed | {}
5967c9e0-a9af-4952-bff4-dba69376078f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Enclosed Vehicular Facilities 16.9 · CO emission rates are higher during acceleration and deceleration than at constant speed; this effect may be accounted for by adding a 10% safety factor to the computations. · The effect of positive or negative grades up to 2% is usually neglected. Engineers should use judgment, or available data, in applying correction factors for positive grades greater than 2%. · Traffic is assumed to move as a unit, with a constant space interval between vehicles, regardless of roadway grade. · Average passenger vehicle dimensions may be assumed where specific vehicle data are unavailable. Table 3 presents typical physical data for automobiles for use in normal ventilation air quantity analyses. Allowable Carbon Monoxide. EPA 's (1975) supplement to its Guidelines for Review of Environmental Impact Statements con- cerns the concentration of CO in tunnels. This supplement evolved into a design approach based on keeping CO concentration at or below 143 mg/m3 (125 ppm), for a maximum 1 h exposure time, for tunnels located at or below an altitude of 1000 m. In 1989, the EPA revised its recommendations for maximum CO levels in tunnels located at or below an altitude of 1500 m to the following: · A maximum of 137 mg/m3 (120 ppm) for 15 min exposure · A maximum of 74 mg/m3 (65 ppm) for 30 min exposure · A maximum of 52 mg/m3 (45 ppm) for 45 min exposure · A maximum of 40 mg/m3 (35 ppm) for 60 min exposure These guidelines do not apply to tunnels in operation before the adoption date. At higher elevations, vehicle CO emissions are greatly increased, and human tolerance to CO exposure is reduced. For tunnels above 1500 m, the engineer should consult with medical authorities to establish a proper design value for CO concentrations. Unless otherwise specified, the material in this chapter refers to tunnels at or below an altitude of 1500 m. Outdoor air standards and regulations such as those from the Occupational Safety and Health Administration (OSHA) and the American Conference of Governmental Industrial Hygienists (ACGIH) are discussed in the section on Bus Terminals. Emergency Ventilation Air Quantities. A road tunnel ven- tilation system must be able to protect the traveling public during the most adverse and dangerous conditions (e.g., fires), as well as during normal conditions. Establishing the requisite air vol- ume requirements is difficult because of many uncontrollable variables, such as the possible number of vehicle combinations and traffic situations that could occur during the lifetime of the facility. For many years, the rule of thumb has been 0.155 m3/s per lane- metre. The Memorial Tunnel Fire Ventilation Test Program (MHD/ FHWA 1995) showed that this value is, in fact, a reasonable first pass at an emergency ventilation rate for a road tunnel. Longitudinal flow, single-point extraction, and dilution are three primary methods for controlling smoke flow in a tunnel. Both lon- gitudinal flow and single-point extraction depend on the ability of Table 3 Average Dimensional Data for Automobiles Sold in the United States ¦ Size/Class ¦ Wheelbase, m ¦ Length, m ¦ Frontal Area, m2 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Subcompact ¦ 2.4 ¦ 4.3 ¦ 1.6 ¦ ¦ Compact ¦ 2.7 ¦ 4.8 ¦ 1.8 ¦ ¦ Midsize ¦ 3.0 ¦ 5.5 ¦ 2.0 ¦ ¦ Large ¦ 3.0 ¦ 5.6 ¦ 2.1 ¦ ¦ Average ¦ 2.80 ¦ 5.06 ¦ 1.89 ¦ the emergency ventilation system to generate the critical velocity necessary to prevent backlayering. Critical Velocity. The concept of critical velocity is addressed in the section on Design Approach, under Tunnels. Design Fire Size. The design fire size selected significantly affects the magnitude ofthe critical velocity needed to prevent back- layering. Table 4 provides typical fire size data for a selection of road tunnel vehicles. Temperature. A fire in a tunnel significantly increases air tem- perature in the tunnel roadway and exhaust duct. Thus, both the tunnel structure and ventilation equipment are exposed to the high smoke/gas temperature. The air temperatures shown in Table 5 provide guidance in selecting design exposure temperatures for ventilation equipment. Testing. The Memorial Tunnel Fire Ventilation Test Program was a full-scale test program conducted to evaluate the effectiveness of various tunnel ventilation systems and ventilation airflow rates to control smoke from a fire (MHD/FHWA 1995). The results are useful in developing both emergency tunnel ventilation systems and emergency operational procedures. Pressure Evaluation. Air pressure losses in tunnel ducts must be evaluated to compute the fan pressure and drive requirements. Fan selection should be based on total pressure across the fans, not on static pressure alone. Fan total pressure (FTP) is defined by ASHRAE Standard 51/ AMCA Standard 210 as the algebraic difference between the total pressures at fan discharge (TP2) and fan inlet (TP 1), as shown in Fig- ure 7. The fan velocity pressure (FVP) is defined as the pressure (VP2) corresponding to the bulk air velocity and air density at the fan discharge: FVP = VP2 (3) Fan static pressure (FSP) is equal to the difference between fan total pressure and the fan velocity pressure: Table 4 Typical Fire Size Data for Road Vehicles ¦ Cause of Fire ¦ Peak Fire Heat Release Rate, MW ¦ ¦ --- ¦ --- ¦ ¦ Passenger car ¦ 5 to 10 ¦ ¦ Multiple passenger cars (2 to 4 Vehicles) ¦ 10 to 20 ¦ ¦ Bus ¦ 20 to 30 ¦ ¦ Heavy goods truck ¦ 70 to 200 ¦ ¦ Tanker3 ¦ 200 to 300 ¦ Source: NFPA Standard 502 (2008). Notes: 1. The designer should consider rate of fire development peak heat release rates may be reached within 10 min), number of vehicles that could be involved in fire, and potential for fire to spread from one vehicle to another. 2. Temperatures directly above fire can be expected to be as high as 1000 to 1400°C. 3. Flammable and combustible liquids for tanker fire design should include adequate drainage to limit area of pool fire and its duration. Heat release rate may be greater than listed if more than one vehicle is involved. Table 5 Maximum Air Temperatures at Ventilation Fans During Memorial Tunnel Fire Ventilation Test Program ¦ Nominal FHRR, MW ¦ Temperatureat Central Fans,a °C ¦ Temperature at Jet Fans, b °C ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 20 ¦ 107 ¦ 232 ¦ ¦ 50 ¦ 124 ¦ 371 ¦ ¦ 100 ¦ 163 ¦ 677 ¦ Source: MHD/FHWA (1995) FHRR = Fire heat release rate aCentral fans located 213 m from fire site. bJet fans located 52 m downstream of fire site. Inc. ASHRAE, 2019 user. single for Licensed | {}
2a25dd90-b665-4af1-aedb-b88f4058b5ac | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 16.10 ![image](/image/placeholder) INLET DUCT FAN DISCHARGE DUCT PRESSURE TP. DUCT 2 SP PRESSURE VP3 = TP3 IN DISCHARGE VP 0 VP 2 VP 0 FSP TOTAL TOTAL SP3 LOSS DUCT IN TP 0 FAN LOSS SP 0 INLET T I TP 1 I I SP 1 I I I I I I 0 1 2 3 FTP = TP1 -TP2 FSP = FTP - FVP = SP2- TP1 Fig. 7 Fan Total Pressure FSP = FTP - FVP (4) TP2 must equal total pressure losses TP2-3 in the discharge duct and exit pressure TP3. Static pressure at the exit SP3 is equal to zero. TP2 = TP2-3 + TP3 = TP2-3 + VP3 (5) Likewise, total pressure at fan inlet TP1 must equal the total pres- sure losses in the inlet duct and the inlet pressure: TP1 = TPO + TP0-1 Straight Ducts. Straight ducts in tunnel ventilation systems either (1) transport air or (2) uniformly distribute (supply) or collect (ex- haust) air. Several methods have been developed to predict pressure losses in a duct of constant cross-sectional area that uniformly dis- tributes or collects air. The most widely used method was developed for the Holland Tunnel in New Y ork (Singstad 1929). The following relationships, based on Singstad's work, give pressure losses at any point in a duct. (6) Inc. ASHRAE, 2019 user. single for Licensed Total pressure for a supply duct V 공 LZ3 LZ a P T = P 1 - 1 - K 22 + + 2 3H 2 gc 2H Static pressure loss for an exhaust duct (7) 망 LZ 3 3Z2 LZ a Ps = P1 + + 2 3 + c H 2 + c 2H 3 gc 1 + c where (8) PT total pressure loss at any point in duct, Pa Ps static pressure loss at any point in duct, Pa = P1 pressure at last outlet, Pa a density of air, kg/m3 V。 = velocity of air entering duct, m/s L = total length of duct, m X = distance from duct entrance to any location, m Z = (L -X)/L H = hydraulic radius, m K = constant accounting for turbulence = 0.615 constant related to coefficient of friction for concrete = 0.0035 constant related to coefficient of friction for concrete 2019 ASHRAE Handbook-HVAC Applications (SI) = 0.00012 m4/s2 c = constant relating to turbulence of exhaust port = 0.20 for exhaust rates less than 0.31 m3/s per metre = 0.25 for exhaust rates greater than 0.31 m3/s per metre gc = gravitational constant = 1.0 (m · kg)/(N·s2) The geometry of the exhaust air slot connection to the main duct is a concern in deriving the exhaust duct equation. The deri- vation is based on a 45° angle between the slot discharge and the main airstream axes. Variations in this angle can greatly affect the energy losses at the convergence from each exhaust slot, with total pressure losses for a 90° connection increasing by 50 to 100% over those associated with 45° angles (Haerter 1963). For distribution ducts with sections that differ along their length, these equations may also be solved sequentially for each constant-area section, with transition losses considered at each change in section area. For a transport duct with constant cross- sectional area and constant air velocity, pressure losses are due to friction alone and can be computed using the standard expressions for losses in ducts and fittings (see Chapter 21 of the 2017 ASHRAE Handbook- -Fundamentals). Carbon Monoxide Analyzers and Recorders. Air quality in a tunnel should be monitored continuously at several key points. CO is the contaminant usually selected as the prime indicator of tunnel air quality, although in some of the more recent European road tun- nels, NOx and visibility levels are now the main indicators driving ventilation requirements, perhaps because of the prominence of die- sel cars. CO-analyzing instruments base their measurements on one of the following three processes: · Catalytic oxidation (metal oxide) analysis offers reliability and stability at a moderate initial cost. Maintenance requirements are low, plus these instruments can be calibrated and serviced by maintenance personnel after only brief instruction. · Infrared analysis is sensitive and responsive, but has a high initial cost. This instrument is precise but complex, and requires a highly trained technician for maintenance and servicing. · Electrochemical analysis is precise; the units are compact, light- weight, and moderately priced, but they have a limited life (usually not exceeding two years) and thus require periodic replacement. As shown in Figures 1 to 4, the location of the peak emission concentration level in a road tunnel is a function ofboth traffic oper- ation (unidirectional versus bidirectional) and type of ventilation provided (natural, longitudinal, semitransverse, or full transverse). Generally, time-averaged CO concentrations for the full length of the tunnel are needed to determine appropriate ventilation rates and/ or required regulatory reporting. Time-averaged concentrations are particularly important in road tunnels where the ventilation system control is integrated with the CO monitoring system. CO sampling locations in a road tunnel should be selected care- fully to ensure meaningful results. For example, samples taken too close to an entry or exit portal do not accurately represent the overall level that can be expected throughout the tunnel. Multiple sampling locations are recommended to ensure that a reasonable average is reported. Multiple analyzers are also recommended to provide a reasonable level ofredundancy in case of analyzer failure or loss of calibration. In longer road tunnels, which may have mul- tiple, independently operated ventilation zones, the selected sam- pling locations should provide a representative CO concentration level for each ventilation zone. Strip chart recorders and micropro- cessors are commonly used to keep a permanent record of road tunnel CO levels. CO analyzers and their probes should not be located directly in a roadway tunnel or in its exhaust plenum. Instead, an air pump should draw samples from the tunnel/exhaust duct through a sample line to the CO analyzer. This configuration eliminates the possibility ofin-tunnel air velocities adversely affecting the instrument's accu- | {}
3dccdeb2-2f9c-4e40-afd6-4c6a41669f58 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Enclosed Vehicular Facilities 16.11 racy. The length of piping between sampling point and CO analyzer should be as short as possible to maintain a reasonable air sample transport time. Haze or smoke detectors have been used on a limited scale, but most of these instruments are optical devices and require frequent or constant cleaning with a compressed airjet. Iftraffic is predominantly diesel-powered, smoke haze and NOx gases require individual moni- toring in addition to that provided for CO. Local regulations should be reviewed to determine whether ven- tilation exhaust monitoring is required for a particular road tunnel. If so, for tunnels using full transverse ventilation systems, CO and NO2 pollutant sampling points should be placed carefully within the exhaust stacks/plenums. For longitudinally ventilated tunnels, sam- pling points should be located at least 30 m in from the exit portal. Controls. Centralized Control. To expedite emergency response and to reduce the number of operating personnel for a given tunnel, all ventilating equipment should be controlled at a central location. New tunnels are typically provided with computer-based control systems, which function from operational control centers. In some older tunnel facilities, fan operation is manually controlled by an operator at a central control board. The control structure for newer road tunnel ventilation systems is typically supervisory control and data acquisition (SCADA), with programmable logic control- lers (PLCs) providing direct control hardware over the associated electrical equipment. The operational control center varies from one stand-alone PC (with SCADA software providing dedicated ventilation control), to redundant client/server configurations pro- viding an integrated control system and real-time database and alarm systems for tunnel operations (Buraczynski 1997). Commu- nication links are required between the supervisory SCADA and PLCs. The SCADA system operator controls the ventilation equipment through a graphical user interface, developed as part of the ventila- tion system design. Preprogrammed responses allow the operator to select the appropriate ventilation plan or incident response mode. The SCADA system allows the operator to view equipment status, trend data values, log data, and use an alarm system. Whereas older tunnel facilities used chart recorders for each sampling point to demonstrate that the tunnel was sufficiently ventilated and com- pliant with environmental air quality standards, new tunnels use SCADA to log CO levels directly onto a nonvolatile medium, such as a CD-ROM. Emergency response functions for road tunnel ventilation re- quire that control system design meets life safety system standards. A high-availability system is required to respond on demand to fire incidents. High availability is obtained by using high-quality indus- trial components, and by adding built-in redundancy. The design must protect the system against common event failures; therefore, redundant communication links are segregated and physically routed in separate raceways. High-integrity software for both the PLCs and the SCADA system is another major consideration. Once a supervisory command is received, the PLC control handles equipment sequencing (e.g., fan and damper start-up sequence), least-hours-run algorithms, staggered starting of fans, and all interlocks. The PLC also receives instrumentation data from the fan and fan motor, and can directly shut down the fan if needed (e.g., because of high vibration). Conditions such as high vibration and high temperature are tolerated during emergency operation. CO-Based Control. When input to the PLC, recorded tunnel air quality data allow fan control algorithms to be run automatically. The PLC controls fans during periods of rising and falling CO lev- els. Fan operations are usually based on the highest level recorded from several analyzers. Spurious high levels can occur at sampling points; the PLC control algorithm prevents the ventilation system from responding to short-lived high or low levels. PLC control also simplifies hardwired systems in older tunnel facilities, and increases flexibility through program changes. Timed Control. This automatic fan control system is best suited for installations that experience heavy rush-hour traffic. With timed control, the fan operation schedule is programmed to increase the ventilation level, in preset increments, before the anticipated traffic increase; it can also be programmed for weekend and public holiday conditions. The timed control system is relatively simple and is easily revised to suit changing traffic patterns. Because it anticipates an increased airflow requirement, the associated ventilation system can be made to respond slowly and thus avoid expensive demand charges from the local utility company. One variation of timed con- trol is to schedule the minimum anticipated number of fans to run, and to start additional fans if high CO levels are experienced. As with the CO-based control system, a manual override is needed to cope with unanticipated conditions. Traffic-Actuated Control. Several automatic fan control systems have been based on the recorded flow of traffic. Most require instal- lation of computers and other electronic equipment needing specific maintenance expertise. Local Fan Control. Local control panels are typically provided for back-up emergency ventilation control and for maintenance/ser- vicing requirements. The local panels are often hardwired to the fan starters to make them independent from the normal SCADA/PLC control system. Protocols for handing over fan control from the SCADA/ PLC system to the local panel must also be established, so that fans do not receive conflicting operational signals during an emergency. Rapid Transit Tunnels and Stations Modern high-performance, air-conditioned subway vehicles consume most of the energy required to operate rapid transit and are the greatest source of heat in the underground areas of a transit system. An environmental control system (ECS) is intended to maintain reasonable comfort during normal train operations and help keep passengers safe during a fire emergency. Minimizing trac- tion power consumption and vehicle combustible contents reduces ventilation requirements. The large amount of heat produced by rolling stock, if not properly controlled, can cause passenger dis- comfort, shorten equipment life, and increase maintenance require- ments. Tropical climates present additional concerns for underground rail transit systems and make environment control more critical. Temperature, humidity, air velocity, air pressure change, and rate of air pressure change help determine ECS performance. These con- ditions are affected by time of day (i.e., morning peak, evening peak, or off-peak), circumstance (i.e., normal, congested, or emergency op- erations), and location in the system (i.e., tunnel, station platform, en- trance, or stairway). The Subway Environmental Design Handbook (SEDH) (DOT 1976) provides comprehensive and authoritative de- sign aids on ECS performance; information in the SEDH is based on design experience, validated by field and model testing. Normal operations involve trains moving through the subway system and stopping at stations according to schedule, and passengers traveling smoothly through stations to and from transit vehicles. The piston action of moving trains is the chief means of providing ventilation and maintaining an acceptable environment (i.e., air velocity and temperature) in the tunnels. Because normal operations are predominant, considerable effort should be made to optimize ECS performance during this mode. One concern is limiting the air velocity caused by approaching trains on passengers waiting on the platform. Piston-induced plat- form air velocities can be reduced by providing a pressure relief shaft (also known as a blast shaft) at each end of affected platforms. Inc. ASHRAE, 2019 user. single for Licensed | {}
51435b43-46d3-4e8c-b962-a93b839f3a75 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 16.12 During normal train operations, platform passenger comfort is a function of the temperature and humidity of ambient and station air, platform air velocity, and duration of exposure to the station environ- ment. For example, a person entering a 29°C station from 32°C outdoor conditions will momentarily feel more comfortable, partic- ularly after a fast-paced walk ending with total rest, even if standing. However, in a short time, usually about 6 min, the person 's metabo- lism adjusts to the new environment and produces a similar level of comfort as before. If a train were to arrive during this period, a rela- tively high station air temperature would be acceptable. Traditionally, the relative warmth index (R WI) has quantified this transient effect, allowing the designer to select an appropriate design air temperature for the station based on the transient, rather than steady-state, sensation of comfort. More recently, new transient thermal comfort models have been developed, leading to more ad- vanced comfort indices being proposed (Gilbey 2006; Guan et al. 2009). Design temperatures based on the transient approach are typ- ically higher (often 3 to 5 K) than those selected by the steady-state approach, and hence result in reduced cooling load and air- conditioning system requirements. Congested operations result from delays or operational prob- lems that prevent the normal dispatch of trains, such as missed head- ways or low-speed train operations. Trains may wait in stations, or stop at predetermined locations in tunnels during congested opera- tions. Delays usually range from 30 s to 20 min, although longer delays may occasionally be experienced. Passenger evacuations or endangerment are not expected to occur. Congested ventilation analyses should focus on the potential need for forced (mechanical) ventilation, which may be required to control tunnel air tempera- tures in support of continued operation of train air-conditioning units. The aim of forced ventilation is to maintain onboard passen- ger comfort during congestion by operating the vehicle air condi- tioning system to prevent passengers from evacuating the train. Design Concepts. Elements of underground rail transit ventila- tion design may be divided into four interrelated categories: natural, mechanical, and emergency ventilation; and station air conditioning. Emergency operations occur as a result of a fire in a subway tunnel or station. Fire emergencies include trash fires, track electri- cal fires, train electrical fires, and acts of arson. Some fires may involve entire train cars. Station fires are mostly trashcan fires. Sta- tistically, most fire incidents reported in mass transit systems (up to 99%) are small and low in smoke generation; these fires typically cause only minor injuries and operational disturbances. The most serious emergency condition is a fire on a stopped train in a tunnel; this event disrupts traffic and requires passenger evacuation. For this case, adequate tunnel ventilation is required to control smoke flow and enable safe passenger evacuation and safe ingress of emergency response personnel. Though rare, tunnel fires must be considered because of their potential life-safety ramifications. Natural Ventilation. Natural ventilation (e.g., ambient air infil- tration and exfiltration) in subway systems primarily results from trains moving in tightly fitting tunnels, where air generally moves in the direction of train travel. The positive air pressure generated in front of a moving train expels warm air from the subway through tunnel portals, pressure relief shafts, station entrances, and other openings; the negative pressure in the wake induces airflow into the subway through these same openings. Considerable short-circuiting of airflow occurs in subways when two trains, traveling in opposite directions, pass each other; espe- cially in stations or tunnels with porous walls (those with intermittent openings to allow air passage between trackways). Short-circuiting can also occur in stations and tunnels with nonporous walls where alternative airflow paths (e.g., open bypasses, cross-passageways, adits, crossovers) exist between the trackways. This short-circuited airflow reduces the net ventilation rate and increases air velocities on platforms and in entrances. During peak operating periods and high 2019 ASHRAE Handbook-HVAC Applications (SI) ambient temperatures, short-circuited airflow can cause undesirable heat build-up in the station. To counter the negative effects of short-circuiting airflow, venti- lation shafts are customarily located near interfaces between tunnels and stations. Shafts in station approach tunnels are often called blast shafts, because part of the tunnel air pushed by an approaching train is expelled through them before it affects the station environment. Shafts in station departure tunnels are known as relief shafts, because they relieve the negative air pressure created by departing trains. Relief shafts also induce outdoor airflow through the shaft, rather than through station entrances. Additional shafts may be provided for natural ventilation be- tween stations (or between portals, for underwater crossings), as dictated by tunnel length. The high cost of such ventilation struc- tures necessitates a design that optimizes effectiveness and effi- ciency. Internal resistance from offsets and bends in the ventilation shaft should be kept to a minimum; shaft cross-sectional area should approximately equal the cross-sectional area of a single-track tunnel (DOT 1976). Mechanical Ventilation. Mechanical ventilation in subways (1) supplements the natural ventilation effects of moving trains, (2) expels warm air from the system, (3) introduces fresh outdoor air, (4) supplies makeup air for exhaust, (5) restores the cooling potential of the tunnel heat sink by extracting heat stored during off hours or system shutdown, (6) reduces airflow between the tunnel and station, (7) provides outdoor air for passengers in stations or tunnels during an emergency or other unscheduled interruptions of traffic, and (8) purges smoke from the system during a fire, protect- ing the passengers' evacuation. The most cost-effective design for a mechanical ventilation sys- tem serves multiple purposes. For example, a vent shaft designed for natural ventilation may also be used for emergency ventilation if a fan is installed in parallel, as part of a bypass (Figure 8). Current safety standards require emergency fans to be reversible (NFPA Standard 130). Several ventilation shafts and fan plants may be required to work together to achieve many, if not all, of the eight design objectives. Depending on the shaft location, design, and local train operating characteristics, a shaft with an open bypass damper and a closed fan damper may serve as a blast or relief shaft. With the fan damper open and the bypass damper closed, air can be mechanically sup- plied to or exhausted from the tunnel, depending on fan rotation direction. Except for emergency ventilation, fan rotation direction is usually predetermined for various operating modes. If a station is not air conditioned, warm air in the subway should be exchanged, at the maximum rate possible, with cooler outdoor ![image](/image/placeholder) GRATING GRADE DISCHARGE/INTAKE PLENUM TUNNEL SHAFT TUNNEL VENTILATION FAN MECHANICAL VENTILATION NORMAL VENTILATION TUNNEL Fig. 8 Tunnel Ventilation Shaft Inc. ASHRAE, 2019 user. single for Licensed | {}
fb2d0581-a8d4-4304-bb07-c4d5c0b747d9 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Enclosed Vehicular Facilities 16.13 air. If a station is air conditioned below the ambient temperature, inflow of warmer outdoor air should be limited and controlled. Figure 9 shows a typical tunnel ventilation system between two subway stations. Here, flow of warm tunnel air into the station is min- imized by either normal or mechanical ventilation effects. In Figure 9A, air pushed ahead of the train on Track 2 diverts partially to the bypass ventilation shaft and partially into the wake of a train on Track 1, as a result of pressure differences. Figure 9B shows an alter- native operation with the same ventilation system where mid-tunnel fans operate in exhaust mode; when outdoor air conditions are favor- able, makeup air is introduced through the bypass ventilation shafts. This alternative can also either provide or supplement station ventila- tion. To achieve this, the bypass shafts are closed, and makeup air for the mid-tunnel exhaust fans enters through station entrances. For forced air flow blown under car brake resistor grids, a more direct mechanical ventilation system (Figure 10) can be designed to remove station heat at its primary source, the underside of the train. Field tests have shown that trackway ventilation systems not only reduce upwelling of warm air into the platform areas, but also remove significant portions of heat generated by other undercar sources, such as dynamic-braking resistor grids and, in some cases, air-conditioning condenser units (DOT 1976), as long as consistent and steady air movement can be maintained from the heat source towards the exhaust grille. Ideally, makeup air for trackway exhaust should be introduced at track level, as in Figure 10A, to provide pos- itive control over the direction of airflow; however, obstructions in the vehicle undercarriage area must be avoided when planning underplatform exhaust port and makeup air supply locations. A more direct mechanical ventilation system (Figure 10) can be designed to remove station heat at its primary source, the underside of the train. Field tests have shown that trackway ventilation sys- tems not only reduce upwelling of warm air into the platform areas, but also remove significant portions of heat generated by other undercar sources, such as dynamic-braking resistor grids and, in some cases, air-conditioning condenser units (DOT 1976). Ideally, makeup air for trackway exhaust should be introduced at track level, as in Figure 10A, to provide positive control over the direction of airflow; however, obstructions in the vehicle undercarriage area must be avoided when planning underplatform exhaust port and makeup air supply locations. A trackway ventilation system without a dedicated makeup air supply (Figure 10B), also known as an underplatform exhaust (UPE) system, is the least effective alternative for heat removal. General design experience shows that where UPE grilles cannot be ![image](/image/placeholder) SHAFT TO GRADE (TYPICAL) PLATFORM PLATFORM T RAIN RACK NO. 7 STATION STATION TRACK NO. 2 RAIN + 료 ₩ PLATFORM PLATFORM EMERGENCY FAN MIDTUNNEL FAN EMERGENCY FAN WITH BYPASS WITH BYPASS WITH BYPASS A. NORMAL VENTILATION BETWEEN STATIONS ![image](/image/placeholder) SHAFT TO GRADE (TYPICAL) PLATFORM PLATFORM A TRACK NO 1 STATION STATION TRACK NO. 2 ₩ 료 PLATFORM PLATFORM EMERGENCY FAN MIDTUNNEL FAN EMERGENCY FAN WITH BYPASS OPEN OPERATING WITH BYPASS OPEN B. MECHANICAL VENTILATION BETWEEN STATIONS Fig. 9 Tunnel Ventilation Concept placed in close proximity to the source of undercar heat because of space constraints, or when a steady airflow cannot be established over the heat source towards the UPE grilles, heated undercar air can escape up through the gap between the car and platform edge, and the UPE effectiveness is reduced (Tabarra and Guan 2009). With a UPE system, a quantity of air equal to that withdrawn by the underplat- form exhaust enters the station control volume, either from the out- doors or from the tunnels. When the ambient, or tunnel, air temperature is higher than the station design air temperature, a UPE system reduces station heat load by removing undercar heat, but it also increases station heat load by drawing in warmer air, which may affect platform passenger comfort. Because of these drawbacks, the effectiveness of a UPE system should be carefully considered and if possible modeled early, before the station design advances too far. Figure 10C shows a cost-effective compromise: makeup air is introduced from the ceiling above the platform. Although heat re- moval effectiveness of this system may be less than that of the system with track-level makeup air, the inflow of warm tunnel air that may occur in a system without makeup air supply is negated. Newer vehicles have air-conditioning grids above, generating heat near the ceiling during dwell time in the station. To exhaust this heat, an overtrack exhaust (OTE) system should be provided. OTE may be appropriate to remove fire smoke and heat. If analysis indi- cates that acceptable environmental conditions are achieved with OTE under normal and emergency conditions, the designer may consider evaluating the efficiency of the UPE system. The relative geometries of heat sources must be verified early in the design cycle, to enable the designer to make an informed decision. Emergency Ventilation. During a subway tunnel fire, mechanical ventilation is an important part of the response and smoke control ![image](/image/placeholder) MEZZANINE LEVEL RA STATION PLATFORM SIDE PLATFORM INLET 0 EXHAUST PLENUM OUTSIDE AIR MAKEUP PLENUM A. OUTDOOR AIR MAKEUP AT TRACK LEVEL MEZZANINE MEZZANINE STATION STATION TRACK PLATFORM PLATFORM SIDE INL E INLET T I T EXHAUST PLENUM EXHAUST PLENUM SIDE INLETS TRACK CENTERLINE INLETS B. NO MAKEUP AIR SUPPLY MEZZANINE LEVEL RA IN STATION VERTICAL BRANCH DUCT IN FURRING PLATFORM PLATFORM 0 T T MAKEUP AIR SUPPLY PLENUM EXHAUST (CONDITIONED OR OUTDOOR AIR) PLENUM C. MAKEUP AIR SUPPLY AT CEILING LEVEL Fig. 10 Trackway Ventilation Concept (Cross-Sections) Inc. ASHRAE, 2019 user. single for Licensed | {}
a7be512d-85c3-4f13-92cf-df730780ce25 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 16.14 2019 ASHRAE Handbook-HVAC Applications (SI) strategy. Within subway systems or other enclosed trainways, an emergency ventilation system is necessary to control the direction of smoke migration and allow safe evacuation of passengers and access by firefighters (see NFPA Standard 130). Depending on vehicle configuration, ventilation fan sizes, and tunnel geometry, emergency ventilation has the potential to affect fire size and smoke generation. The most common method of ventilating a tunnel during a fire is push-pull fan operation: fans on one side of the fire operate in supply mode, while fans on the opposite side operate in exhaust mode. Emergency ventilation analyses should focus on determining the airflow required to preserve tenable conditions in a single evac- uation path from the train. The criterion used to design emergency ventilation for underground transit systems is critical velocity, sim- ilar to that presented in the section on Road Tunnels. The presence of nonincident trains should be considered in planning the emer- gency ventilation system response to specific fire incidents. Emergency ventilation system design must allow for the unpre- dictable location of both the disabled train and the fire source. Therefore, emergency ventilation fans should have full reverse-flow capability, so that fans on either side of a disabled train can operate together to control airflow direction and counteract undesired smoke migration. When a disabled train is stopped between two stations and fire or smoke is discovered, outdoor air is supplied by the emergency ven- tilation fans at the nearest station, and smoke-laden air is exhausted past the opposite end of the train by emergency ventilation fans at the next station, unless the location of the fire dictates otherwise. Passengers can then be evacuated along the tunnel walkways via the shortest possible route (Figure 1 1). Emergency ventilation analysis should consider the possibility of nonincident trains stopped behind the disabled train. In this case, emergency fans should be operated so that nonincident trains are kept in the fresh airstream; if possible, they may be used to evacuate incident-train passengers. For long subway tunnels, in particular, analysis should also consider evacuating passengers to a nonin- cident trackway (through cross passageways), where a dedicated rescue train can move them to safety. Emergency ventilation analyses should identify passenger evacuation/firefighter ingress routes for evaluated scenarios, and fan modes to preserve tenable conditions in those routes. When a train fire is discovered, the train should be moved if possible to the next station, to make passenger evacuation and fire suppression easier. Emergency management plans must include provisions to (1) quickly assess any fire or smoke event, (2) com- municate the situation to an operations control center, (3) establish the location of the incident train, (4) establish the general location of the fire, (5) determine the best passenger evacuation route, and (6) quickly activate emergency ventilation fans to establish smoke flow control. Midtunnel and station trackway (OTE) ventilation fans may be used to enhance emergency ventilation; therefore, these fans must also operate under high temperatures and have reverse-flow capa- bility. ![image](/image/placeholder) TRACK NO. 1 TRAIN STATION STATION DISABLED TRAIN EVACUATION TRACK NO. 2 ROU E PLATFORM PLATFORM EMERGENCY MID- EMERGENCY EMERGENCY FAN IN TUNNEL FAN IN FAN IN EXHAUST FAN IN SUPPLY SUPPLY MODE EXHAUST MODE MODE MODE Fig. 11 Emergency Ventilation Concept The possibility of a fire on the station platform or in another public area should also be considered. These fires are generally cre- ated by rubbish or wastepaper and are thus much smaller than train fires. However, small station fires can generate considerable smoke and create panic among passengers. Therefore, stations should be equipped with efficient fire suppression and smoke extraction sys- tems. Stations with platform-edge doors should have fire suppres- sion and smoke extraction systems designed specifically for that configuration. The fire heat release rate is an important parameter in subway emergency ventilation system design. The fire heat release rate for each vehicle type depends on initiation fire, combustibility of inte- rior materials, size of the compartment, and ventilation (door and window openings), and thus must be established individually (see the Design Fires section for more information). Typical fire size data for single transit vehicles are as follows: · Older transit vehicle 14.7 MW · New, hardened vehicle 10.3 MW · Light rail vehicle 8.8 MW Smoke obscuration is a key factor in defining a tenable environ- ment for passenger evacuation, and visibility is often the governing criterion for station design. The smoke release rate should be calcu- lated following acceptable procedures (e.g., Society of Fire Protec- tion Engineers [SFPE] 2008). Station Air Conditioning. Faster station approach speeds and closer headways, both made possible by computerized train control, have increased heat gains in subway stations. The net internal sen- sible heat gain for a typical two-track subway station, with 40 trains per hour per track traveling at a top speed of 80 km/h, may reach 1.5 MW, even after some tunnel heat is removed by the heat sink, sta- tion underplatform exhaust system, or tunnel ventilation system. To remove this heat from a station with a ventilation system using out- door air and a maximum air temperature increase of 1. 7 K, for example, would require roughly 660 m3/s of outdoor air. This would be costly, and air velocities on the platforms would be objectionable to passengers. The same amount of sensible heat gain, plus the latent heat and outdoor air loads (based on a station design air temperature 4 K lower than ambient), could be handled by about 2.2 MW of refrigeration. Even if station air conditioning is more expensive at the outset, long- term benefits include (1) reduced design airflow rates, (2) reduced ventilation shaft/duct sizing, (3) improved passenger comfort, (4) increased service life of other station equipment (e.g., escalators, elevators, fare collection), (5) reduced maintenance requirements for station equipment and structures, and (6) increased acceptance of the subway as a viable means of public transportation. Air conditioning should also be considered for other station ancillary areas, such as concourse levels and transfer levels. However, unless these walk- through areas are designed to attract patronage to concessions, the cost of air conditioning is usually not warranted. The physical configuration of the station platform level usually determines the cooling distribution pattern. Platform areas with high ceilings, local warm spots created by trains, high-density pas- senger accumulation, or high-level lighting may need spot cooling. Conversely, where the train length equals platform length and the ceiling height above the platform is limited to 3 to 3.5 m, isolating heat sources and using spot cooling are usually not fea- sible. In air-conditioned stations, when the enthalpy of outdoor air is higher than the station air, station air recirculation may be more economical. Thus, the station cooling system should have the flex- ibility of reducing the volume of outdoor air in favor of station air, based on suitably located temperature and humidity sensors. Pro- vision for dedicated return air ducts from platforms or concourse Inc. ASHRAE, 2019 user. single for Licensed | {}
9fc3db42-7aaa-4e3c-a1a7-df7161e96394 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Enclosed Vehicular Facilities 16.15 areas with accessible filters should be considered early in station cooling design. Air conditioning is more attractive and efficient for stations with platform-edge doors, which limit air exchange between platform and tunnels. In tropical climates, separate ventilation systems are typically used to minimize station air exfiltration and tunnel air infiltration through platform-edge doors. Space use in a station structure for air-distribution systems is of prime concern because of the high cost of underground construc- tion. Overhead distribution ductwork could add to the depth of exca- vation during subway construction. The space beneath a subway station platform is normally an excellent area for low-cost distribu- tion of supply, return, and/or exhaust air. Design Method. Subways typically have two discrete sets of envi- ronmental criteria: one for normal and congested train operations and one for emergency fire/smoke operations. Criteria for normal opera- tions include limits on tunnel air temperature (through tunnel ventila- tion or tunnel cooling) and humidity for various times of the year, minimum ventilation rates to dilute contaminants generated in the subway, and limits on the air velocity and rate of air pressure change to which passengers may be exposed. Some of these criteria are sub- jective and may vary based on demographics. Criteria for emergency operations include a minimum purge time to remove smoke from a subway, critical air velocity for smoke flow control during a tunnel fire, and minimum and maximum fan-induced tunnel air velocities. Given a set of criteria, outdoor design conditions, and appropriate tools for estimating interior heat loads, heat sink effect, ventilation requirements, tunnel air velocity, and rate of air pressure changes, design engineers can select components for the environ- mental control system (ECS). ECS design should consider controls for tunnel air temperature, velocity, and quality, and the air pressure change rate. Systems selected generally combine natural and mechanical ventilation, overtrack and underplatform exhaust, and station air conditioning. Train propulsion/braking systems and configuration of the tun- nels and stations greatly affect the subway environment. Therefore, the ECS must often be considered during the early stages of subway system design. Factors affecting a subway environmental control system are discussed in this section. The Subway Environmental Design Handbook (SEDH) (DOT 1976) and NFPA Standard 130 have additional information. Analytical Data. ECS design should be based on all the parame- ters affecting its operation, including ambient air conditions, train operating characteristics, applicable ventilation methods, new or existing ventilation structures, and calculated heat loads. ECS effi- ciency should be addressed early during transit system design. The tunnel ventilation system should be integrated with the design of other tunnel systems (including power, signaling, communications, and fire/life safety systems) and with the station ventilation system design. The ECS design must satisfy the project design criteria and comply with applicable local and national (or international) codes, standards, and regulations. The ventilation engineer should be familiar with these require- ments and apply suitable design techniques, such as computer modeling and simulations (using verified/validated engineering software). Comfort Criteria. Because passenger exposure to the subway environment is transient, comfort criteria are not as strict as those for continuous occupancy. As a general principle, the station environ- ment should provide a smooth transition between outdoor air condi- tions and thermal conditions in the transit vehicles. Except where platform edge doors are installed, train movement usually generates desirable air movement in stations, but air velocity should not exceed 5 m/s in public areas during normal train operations. Air Quality. Air quality in a subway system is influenced by many factors, some of which are not under the direct control of the HVAC engineer. Some particulates, gaseous contaminants, and odorants in the ambient air can be prevented from entering the subway system by judicious selection of ventilation shaft locations. Particulate matter, including iron and graphite dust generated by normal train opera- tions, is best controlled by regularly cleaning stations and tunnels. However, the only viable way to control gaseous contaminants, such as ozone (produced by electrical equipment) and CO2 (from human respiration), in a subway system is through adequate ventilation with outdoor air. Subway system air quality should be analyzed either by engi- neering calculations or by computer modeling and simulations. The analysis should consider both the tunnel airflow induced by the pis- ton effect of moving trains and the outdoor airflow required to dilute gaseous contaminants to acceptable levels. The results should com- ply with the Subway Environmental Design Handbook (DOT 1976) recommendation for at least 4 ach, as well as the recommendation of ASHRAE Standard 62.1 to have a minimum of 3.5 L/s outdoor air per person. Maximum station occupancy should be used in the anal- ysis. Pressure Transients. Trains passing through aerodynamic dis- continuities in a subway cause changes in tunnel static pressure, which can irritate passengers' ears and sinuses. Based on nuisance factor criteria, if the total change in the air pressure is greater than 697 Pa, the rate of static pressure change should be kept below 423 Pa/s. Pressure transients also add to the dynamic load on vari- ous equipment (e.g., fans, dampers) and appurtenances (e.g., acous- tical panels). The formula and methodology of pressure transient calculations are complex; this information is presented in the SEDH (DOT 1976). Air Velocity. During fires, emergency ventilation must be pro- vided in the tunnels to control smoke flow and reduce air tempera- tures to permit both passenger evacuations and firefighting operations. The minimum air velocity in the affected tunnel should be sufficient to prevent smoke from backlayering (flowing in the upper cross section of the tunnel in the direction opposite the forced ventilation airflow). The method for ascertaining this critical air velocity is provided in the section on Design Approach, under Tun- nels. The maximum tunnel air velocity experienced by evacuating passengers should not exceed 11 m/s. Interior Heat Loads. Heat in a subway is generated mostly by the following sources: · Train deceleration/braking: Between 40 and 50% of heat generated in a subway arises from train deceleration/braking. Many vehicles use non-regenerative braking systems, in which the kinetic energy of the train is dissipated to the tunnel as heat, through dynamic and/or frictional brakes, rolling resistance, and aerodynamic drag. Regenerative systems dissipate less braking heat. · Train acceleration: Heat is also generated as a train accelerates. Many vehicles use cam-controlled variable-resistance elements to regulate voltage across dc traction motors during acceleration. Electrical power is dissipated by these resistors (and the third rail) as heat into the subway. The heat released during train acceleration also comes from traction motor losses, rolling resistance, and aero- dynamic drag. Heat from acceleration generally amounts to 10 to 20% of the total heat released in a subway system. In subway systems with closely spaced stations, more heat is generated because of the frequent acceleration and deceleration. · Vehicle air conditioning: Most new transit vehicles are fully climate controlled. Air-conditioning equipment removes passenger and lighting heat from the cars and transfers it, along with condenser fan and compressor heat, into the subway. Vehicle air-conditioning system capacities generally range from 35 kW per vehicle for shorter rail cars (about 15 m long), up to about 70 kW for longer rail cars (about 21 m long). Heat from vehicle air Inc. ASHRAE, 2019 user. single for Licensed | {}
d099791b-6c48-4492-b0ba-9365fcd38901 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 16.16 2019 ASHRAE Handbook-HVAC Applications (SI) Table 6 Typical Heat Source Emission Values ¦ Source of Heat ¦ Heat Rejection, kW ¦ ¦ --- ¦ --- ¦ ¦ Train A/C system (per vehicle) ¦ 42 ¦ ¦ Escalator (7.5 kW, 75% load factor) ¦ 5.6a ¦ ¦ Fare collection machine ¦ 0.8a ¦ ¦ Station lighting ¦ 0.032 per square metrea ¦ ¦ People (walking, standing) ¦ 0.073 sensibleb ¦ ¦ ¦ 0.073 latentb ¦ aSee Subway Environmental Design Handbook, Part 3 (DOT 1976). bSee 2017 ASHRAE Handbook-Fundamentals, Chapter 9. conditioning and other accessories is generally 25 to 30% oftotal heat generated in a subway. · Other sources: Tunnel heat also comes from people, lighting, induced outdoor air, miscellaneous equipment (e.g., fare collecting machines, escalators), and third-rail/catenary systems. These sources can generate 10 to 30% of the total heat released in a subway. In a typical subway heat balance analysis, a control volume is defined around each station and heat sources are identified and quantified. The control volume usually includes the station and its various approach/departure tunnels. Typical values for heat emis- sion/rejection data are given in Table 6. Heat Sink. The amount of heat flow from tunnel air to subway walls varies seasonally, as well as during morning and evening rush- hour operations. Short periods of abnormally high or low outdoor temperature may cause a temporary departure from the normal heat sink effect in unconditioned areas of the subway, changing the average tunnel air temperature. However, any change from the normal condition is diminished by the thermal inertia ofthe subway structure. During abnormally hot periods, heat flow from the tunnel air to sub- way walls increases. Similarly, during abnormally cold periods, heat flow from the subway walls to tunnel air increases. For subway systems where daily station air temperatures are held constant by dedicated heating and cooling systems, heat flux from station walls is negligible. Depending on the amount of station air flowing into adjoining tunnels, heat flux from tunnel sections may also be reduced. Other factors affecting the heat sink component are soil type (dense rock or light, dry soil), extent of migrating ground- water or the local water table, and surface configuration of tunnel walls (ribbed or flat). Measures to Limit Heat Loads. Various measures have been proposed to limit interior heat loads in subway systems, including regenerative braking, thyristor motor controls, track profile opti- mization, underplatform exhaust systems, and cooling dumping. Electrical regenerative braking converts kinetic energy into electrical energy for use by other trains. Flywheel energy storage, an alternative form of regenerative braking, stores part of the braking energy in high-speed flywheels for use during vehicle acceleration. These methods can reduce the heat generated in train braking by approximately 25%. Cam-controlled propulsion applies a set ofresistance elements to regulate traction motor current during acceleration. Electrical energy dissipated by these resistors appears as waste heat in a sub- way. Thyristor motor controls replace the acceleration resistors with solid-state controls, which reduce acceleration-related heat losses by about 10% on high-speed subways, and by about 25% on low-speed subways. Track profile optimization refers to a tunnel design that is lower between the stations. Less power is used for acceleration, because some ofthe potential energy ofa standing train is converted to kinetic energy as the train accelerates toward the tunnel low point. Con- versely, some of the kinetic energy of a train at maximum speed is converted to potential energy during braking, as the train approaches the next station. Track profile optimization reduces the maximum vehicle heat loss from acceleration and braking by about 10%. An overtrack exhaust (OTE) and/or underplatform exhaust (UPE) system, described in the section on Mechanical Ventilation, uses extract grilles at regular intervals to remove heat generated by vehicle equipment located either at car roof level or under the car (e.g., resistors, compressors, air-conditioning condensers) from the station environment. For forced-blown resistor grids and cases where the airflow pattern is well controlled over the source of the undercar heat, SEDH (DOT 1976) provides a table (based on field test results in a given station platform geometry) of various UPE airflow rates versus UPE system efficiency. Care should be taken when extending these data to other platform geometries. For prelim- inary calculations, it may be assumed that (1) the train heat release (from braking and air conditioning) in the station box is about two- thirds ofthe control-volume heat load, and (2) the UPE is about 50% effective (provided the geometry and airflow pattern conditions are fulfilled). Sanchez (2003) studied the impact of OTE/UPE for air- conditioned stations. In tropical areas, where there are only small daily differences in the ambient air temperature, tunnel walls do not cool off during the night; consequently the heat sink effect is negligible. In such cases, cooling dumping (releasing cooler air from the vehicle or its air- conditioning system) can be considered to limit heat accumulation in subway tunnels. However, the effect of cooling dumping on vehi- cle air-conditioning systems must be considered. Railroad Tunnels Railroad tunnels for diesel locomotives require ventilation to remove residual diesel exhaust, so that each succeeding train is exposed to a relatively clean air environment. Ventilation is also required to prevent locomotives from overheating while in the tunnel. For short tunnels, ventilation generated by the piston effect of a train, followed by natural ventilation, is usually sufficient to purge the tunnel of diesel exhaust in a reasonable time period. Mechanical ventilation for locomotive cooling is usually not required in short tunnels, because the time that a train is in the tunnel is typically less than the time it would take for a locomotive to over- heat. However, under certain conditions, such as for excessively slow trains or during hot weather, locomotive overheating can still become a problem. For long tunnels, mechanical ventilation is required to purge the tunnel of diesel exhaust, and may also be required for locomotive cooling, depending on the speed of the train and the number and arrangement of locomotives used. The diesel locomotive is essentially a fuel-driven, electrically powered vehicle. The diesel engine drives a generator, which in turn supplies electrical power to the traction motors. The power of these engines ranges from about 750 to 4500 kW. Because the overall efficiency of the locomotive is generally under 30%, most of the energy generated by the combustion process must be dissipated as heat to the surrounding environment. Most of this heat is released above the locomotive through the engine exhaust stack and the radi- ator discharge (Figure 12). In a tunnel, this heat is confined to the region surrounding the train. Most commercial trains are powered by more than one loco- motive, so the last unit is subjected to heat and exhaust smoke released by preceding units. If sufficient ventilation is not provided, the air temperature entering the radiator of the last locomotive will exceed its allowable limit. Depending on the engine protection system, this locomotive will then either shut down or drop to a lower throttle position. In either event, the train will slow down. But, as discussed in the next section, a train relies on its speed to generate sufficient ventilation for cooling. As a result of the train slowing down, a domino effect takes place, which may cause the train to stall in the tunnel. Inc. ASHRAE, 2019 user. single for Licensed | {}
79eb650d-450d-439c-b906-0c7b9ef39ee3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Enclosed Vehicular Facilities 16.17 ![image](/image/placeholder) ENGINE EXHAUST STACK RADIATOR DISCHARGE ENGINE INTAKE RADIATOR INTAKES (BOTH SIDES) DIESEL LOCOMOTIVE RADIATOR DISCHARGE C PROFILE OF LOCOMOTIVE AT RADIATOR SECTION RADIATOR INTAKE CONCRETE-LINED TUNNEL TOP OF RAIL DIESEL LOCOMOTIVE CROSS SECTION IN TUNNEL Fig. 12 Typical Diesel Locomotive Arrangement Design Concepts. Most long railroad tunnels (over 8 km) in the western hemisphere that serve diesel operation use a ventilation concept using both a tunnel door and a system of fans and dampers, all located at one end of the tunnel. When a train moves through the tunnel, ventilation air for locomotive cooling is generated by the piston effect of the train moving toward (or away from) the closed portal door. This effect often creates a sufficient flow of air past the train for self-cooling. Under certain conditions, when the piston effect cannot provide required airflow, fans supplement the flow and cool the tunnel. When the train exits at the portal, the tunnel is purged of residual smoke and diesel contaminants by running the fans (with the door closed) to move fresh air from one end of the tunnel to the other. Because the airflow and pressure required for cooling and purge modes may be substantially different, multiple fan systems or variable-volume fans may be required for the two operations. Also, dampers are provided to relieve the pressure across the door, which facilitates its operation while the train is in the tunnel. Application of this basic ventilation concept varies depending on the length and grade of the tunnel, type and speed of the train, envi- ronmental and structural site constraints, and train traffic flow. One design, for a 14.5 km long tunnel (Levy and Danziger 1985), extended the basic concept by including a mid-tunnel door and a partitioned shaft, which was connected to the tunnel on both sides of the mid-tunnel door. The combination of mid-tunnel door and par- titioned shaft divided the tunnel into two segments, each with its own ventilation system. Thus, the ventilation requirement of each segment was satisfied independently. The need for such a system was dictated by the length of the tunnel, relatively low speed of the trains, and traffic pattern. Locomotive Cooling Requirements. A breakdown of the heat emitted by a locomotive to the surrounding air can be determined by performing an energy balance. Starting with the fuel consump- tion rate (as a function of the throttle position), the heat release rates (as provided by the engine manufacturer) at the engine exhaust stack and radiator discharge, and the gross power deliv- ered by the engine shaft (as determined from manufacturer's data), the amount of miscellaneous heat radiated by a locomotive can be determined as follows: qM = FH - qs-qR - PG (9) where 9M = miscellaneous heat radiated from locomotive engine, W F = locomotive fuel consumption, kg/s H = heating value of fuel, J/kg qs = heat rejected at engine exhaust stack, W qR = heat rejected at radiator discharge, W = PG gross power at engine shaft, W Because locomotive auxiliaries are driven off the engine shaft, with the remaining power used for traction power through the main engine generator, heat released by the main engine generator can be determined as follows: qG = (PG-LA)(1 - G) (10) where 9G = main generator heat loss, W LA power driving locomotive auxiliaries, W = main generator efficiency G Heat loss from the traction motors and gear trains can be deter- mined as follows: 9TM = PG-LA-qG- P TE (11) where 9TM = heat loss from traction motors and gear trains, W PTE = locomotive tractive effort power, W The total locomotive heat release rate 9�can then be determined: 9T = qs + qR + qm + LA + 9G + 9TM (12) For a train with N locomotives, the average air temperature approaching the last locomotive is determined from 9T N - 1 tAN = tAT + cpQR where tan = average tunnel air temperature approaching Nth locomotive, °C tAT = average tunnel air temperature approaching locomotive consist, °C = density of tunnel air approaching locomotive consist, kg/m3 cp = specific heat of air, J/(kg·°C) QR = tunnel airflow rate relative to train, m3/s The inlet air temperature to the locomotive radiators is used to judge the adequacy of the ventilation system. For most locomotives running at maximum throttle position, the maximum inlet air tem- perature recommended by manufacturers is about 46°C. Field tests in operating tunnels (Aisiks and Danziger 1969; Levy and Elpi- dorou 1991) showed, however, that some units can operate contin- uously with radiator inlet air temperatures as high as 57°C. The allowable inlet air temperature for each locomotive type should be obtained from the manufacturer when contemplating a design. (13) To determine the airflow rate required to prevent a locomotive from overheating, the relationship between the average tunnel air temperature approaching the last unit and the radiator inlet air temperature must be known or conservatively estimated. This rela- tionship depends on variables such as the number of locomotives in the consist, air velocity relative to the train, tunnel cross-sectional area/configuration, type oftunnel lining, and locomotive orientation (i.e., facing forward or backward). For trains traveling under 32 km/ h, Levy and Elpidorou (1991) showed that a reasonable estimate is Inc. ASHRAE, 2019 user. single for Licensed | {}
748de640-8a3b-4375-86d7-2754e73b77f7 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 16.18 to assume the radiator inlet air temperature to be about 6 K higher than the average air temperature approaching the unit. For trains moving at 50 km/h or more, a reasonable estimate is to assume that the radiator inlet air temperature equals the average air temperature approaching the unit. When the last unit of the train consist faces forward, thereby putting the exhaust stack ahead of its own radia- tors, the stack heat release rate must be included when evaluating the radiator inlet air temperature. Tunnel. Aerodynamics. When designing a ventilation system for a railroad tunnel, airflow and pressure distribution throughout the tunnel (as a function of train type, train speed, and ventilation system operating mode) must be determined. This information is required to determine (1) whether sufficient ventilation is provided for locomotive cooling, (2) the pressure that the fans are required to deliver, and (3) the pressure that the structural and ventilation ele- ments of the tunnel must be designed to withstand. The following equation, from DOT (1997a), relates the piston effect of the train, steady-state airflow from fans to the tunnel, and pressure across the tunnel door. This expression assumes that air leakage across the tunnel door is negligible. Figure 13 shows the dimensional variables on a schematic of a typical tunnel. p PA -PB Hg = gc 2 AV+AVATCDVB AVCDVF ATV+ Qs + + 2 AT 2A7gC AT-Av 2 2 Stlvpt Avv⌀ Qs vLvPv ATV+ Qs + + 3 3 8 AT-Av gc 8 AT-Av gc (14) fT LT- Lv PTQ2S KO2S + + 3 2 8AT gc 2AT gc where p = static pressure across tunnel door, Pa = density of air, kg/m3 PA = barometric pressure at portal A, Pa PB = barometric pressure at portal B, Pa H = difference in elevation between portals, m g = acceleration of gravity = 9.81 m/s2 gc gravitational constant = 1.0 (m·kg)/N·s2 Av = train cross-sectional area, m2 AT = tunnel cross-sectional area, m2 ![image](/image/placeholder) PORTAL DOOR PB S TRAIN V PA H PT= TUNNEL PERIMETER AT = TUNNEL AREA Av = TRAIN AREA Pv = TRAIN PERIMETER Fig. 13 Railroad Tunnel Aerodynamic Related Variables 2019 ASHRAE Handbook- -HVAC Applications (SI) CDVB = drag coefficient at back end of train CDVF = drag coefficient at front end of train V = velocity of train, m/s 2s airflow delivered by fan, m3/s tunnel wall friction factor tunnel length, m L V train length, m PT = tunnel perimeter, m Pv = train perimeter, m V train skin friction factor K = miscellaneous tunnel loss coefficient The pressure across the tunnel door generated only by train pis- ton action is evaluated by setting Qs equal to zero. The airflow rate, relative to the train, required to evaluate locomotive cooling require- ments is Qrel = ATV + Qs (15) where Qrel is the airflow rate relative to the train, m3/s. Typical values for CDVB and CDVF are about 0.5 and 0.8, respec- tively. Because trains passing through a railroad tunnel are often more than 1.6 km long, the parameter that most affects the generated air pressure is the train skin friction coefficient. For dedicated coal or grain trains, which essentially use uniform cars throughout, a value of 0.09 for the skin friction coefficient results in air pressure predictions that conform closely to those observed in various rail- road tunnels. For trains with non-uniform car distribution, the skin friction coefficient may be as high as 1.5 times that for a uniform car distribution. The wall surface friction factor corresponds to the coefficient used in the Darcy- W eisbach equation for friction losses in pipe flow. Typical effective values for tunnels constructed with a formed con- crete lining and having a ballasted track range from 0.015 to 0.017. Tunnel Purge. The leading end of a locomotive must be exposed to an environment that is relatively free of smoke and diesel contam- inants emitted by preceding trains. Railroad tunnels are usually purged by displacing contaminated tunnel air with fresh air by mechanical means after a train has left the tunnel. With the tunnel door closed, air is either supplied to or exhausted from the tunnel, moving fresh air from one end of the tunnel to the other. Observa- tions at the downstream end of tunnels have found that an effective purge time is usually based on displacing 1.25 times the tunnel vol- ume with outdoor air. The time required for purging is primarily determined by opera- tions schedule needs. A long purging time limits traffic; a short purging time may necessitate very high ventilation airflow rates and result in high electrical energy demand and consumption. Conse- quently, multiple factors must be considered, including the overall ventilation concept, when establishing the purge rate. 2. PARKING GARAGES Automobile parking garages (car parks) can be either fully enclosed or partially open. Fully enclosed parking areas are often underground and require mechanical ventilation. Partially open parking garages are generally above-grade structural decks having open sides (except for barricades), with a complete deck above. Nat- ural ventilation, mechanical ventilation, or a combination can be used for partially open garages. Parking garages provide a unique set of challenges because there is a continuous influx of potentially harmful contaminants on a reg- ular basis. In addition, smoke from any fire must be controlled prop- erly to ensure the safety of occupants. The ventilation system should (1) remove toxic gases during nonemergency operation (CO and NOx) and (2) control smoke and hot gases in the event of a fire. Nonemergency operation of automobiles in parking garages pres- ents two concerns. The more serious is emission of CO, with its Inc. ASHRAE, 2019 user. single for Licensed | {}
a88e1beb-83c2-4496-af6a-608edab3b675 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Enclosed Vehicular Facilities 16.19 known risks. The other concern is oil and gasoline fumes, which may cause nausea and headaches and also represent potential fire haz- ards. Additional concerns about NOx and smoke haze from diesel engines may also require consideration. However, the ventilation rate required to dilute CO to acceptable levels is usually satisfactory to control the level of other contaminants as well, provided the per- centage of diesel vehicles does not exceed 20%. For many years, the various model codes, ASHRAE Standard 62.1, and its predecessor standards recommended a flat exhaust rate of either 0.0038 m3/(s. m2) or 6 ach for enclosed parking garages. But because vehicle emissions have been reduced over the years, ASHRAE sponsored a study to determine ventilation rates required to control contaminant levels in enclosed parking facilities (Krarti and Ayari 1998). The study found that, in some cases, much less ventila- tion than 0.0075 m3/(s. m2) was satisfactory. The study's methodology for determining whether a reduced ventilation rate would be effective is included below. However, the current ASHRAE Standard 62.1 and the International Code Council's International Mechanical CodeⓇ (ICC 2009a) allow 0.0038 m3/(s·m2) ventilation, whereas NFPA Standard 88A recommends a minimum of 0.005 m3/ (s·m2), so the engineer must understand the specific codes and stan- dards that apply. The engineer may be required to request a variation, or waiver, from authorities having jurisdiction before implementing a lesser ventilation system design. If larger fans are installed to meet code requirements, they will not necessarily increase overall power consumption; with proper CO level monitoring and ventilation system control, fans will run for shorter time periods to maintain acceptable CO levels. With increased attention on reducing energy consumption, CO-based ventilation system control can provide substantial cost savings in the operation of parking garages. Ventilation Requirements and Design ASHRAE research project RP-945 (Krarti and Ayari 1998) found that the design ventilation rate required for an enclosed parking facility depends chiefly on four factors: · Acceptable level of contaminants in the parking facility · Number of cars in operation during peak conditions · Length of travel and the operating time for cars in the garage · Emission rate of a typical car under various conditions Contaminant Level Criteria. ACGIH (1998) recommends a threshold CO limit of 29 mg/m3 (25 ppm) for an 8 h exposure, and the U.S. EPA (2000) determined that exposure, at or near sea level, to a CO concentration of 40 mg/m3 (35 ppm) for up to 1 h is accept- able. For parking garages more than 1000 m above sea level, more stringent limits are required. In Europe, an average concentration of 40 mg/m3 (35 ppm) and a maximum level of 230 mg/m3 (200 ppm) are usually maintained in parking garages. Various agencies and countries differ on the acceptable level of CO in parking garages, but a reasonable solution is a ventilation rate designed to maintain a CO level of 40 mg/m3 (35 ppm) for 1 h expo- sure, with a maximum of 29 mg/m3 (25 ppm) for an 8 h exposure. Because the time associated with driving in and parking, or driving out of a garage, is on the order of minutes, 40 mg/m3 (35 ppm) is probably an acceptable level of exposure. However, Figure 14 pro- vides nomographs for 15 and 25 ppm maximum exposures as well, to allow the designer to conform to more stringent regulations. Number of Cars in Operation. The number of cars operating at any one time depends on the type of facility served by the parking garage. For distributed, continuous use, such as an apartment build- ing or shopping area, the variation is generally 3 to 5% of the total vehicle capacity. The operating capacity could reach 15 to 20% in other facilities, such as sports stadiums or short-haul airports. Chart Type: line Normalized CO GENERATION RATE 1 Normalized CO GENERATION RATE 1 min COmax 15 ppm item_01 1ppm 1ppm 1ppm Fig. 14 Ventilation Requirement for Enclosed Parking Garage Inc. ASHRAE, 2019 user. single for Licensed | {}
ae00882f-9f9d-42df-a71f-d3a2623a97ea | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 16.20 2019 ASHRAE Handbook- - HVAC Applications (SI) Table 7 Average Entrance and Exit Times for Vehicles Q = Cf ¦ Level ¦ Average Entrance Time, s ¦ Average Exit Time, s ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 1 ¦ 35 ¦ 45 ¦ ¦ 3* ¦ 40 ¦ 50 ¦ ¦ 5 ¦ 70 ¦ 100 ¦ (18) Source: Stankunas et al. (1980). * Average pass-through time = 30 s. Table 8 Predicted CO Emissions in Parking Garages ¦ ¦ Hot Emission (Stabilized), g/min ¦ Hot Emission (Stabilized), g/min ¦ Cold Emission, g/min ¦ Cold Emission, g/min ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Season ¦ 1991 ¦ 1996 ¦ 1991 ¦ 1996 ¦ ¦ Summer, 32°C ¦ 2.54 ¦ 1.89 ¦ 4.27 ¦ 3.66 ¦ ¦ Winter, 0°C ¦ 3.61 ¦ 3.38 ¦ 20.74 ¦ 18.96 ¦ Results from EPA MOBILE3, version NYC-2.2 (1984); sea level location. Note: Assumed vehicle speed is 8 km/h. Length of Time of Operation. The length of time that a car remains in operation in a parking garage is a function ofthe size and layout of the garage, and the number of cars attempting to enter or exit at a given time. The operating time could vary from as much as 60 to 600 s, but on average usually ranges from 60 to 180 s. Table 7 lists approximate data for average vehicle entrance and exit times; these data should be adjusted to suit the specific physical configu- ration of the facility. Inc. ASHRAE, 2019 user. single for Licensed Car Emission Rate. Operating a car in a parking garage differs considerably from normal vehicle operation, including thatin a road tunnel. Most car movements in and around a parking garage occur in low gear. A car entering a garage travels slowly, but the engine is usually hot. As a car exits from a garage, the engine is usually cold and operating in low gear, with a rich fuel mixture. Emissions for a cold start are considerably higher, so the distinction between hot and cold emission plays a critical role in determining the ventilation rate. Motor vehicle emission factors for hot- and cold-start opera- tion are presented in Table 8. An accurate analysis requires correla- tion of CO readings with the survey data on car movements (Hama et al. 1974); the data should be adjusted to suit the specific physical configuration of the facility and the design year. Step 1. Collect the following data: · Number of cars N in operation during peak hour use · Average CO emission rate E for a typical car, g/h · Average length of operation and travel time for a typical car, s in the garage, ppm · Acceptable CO concentration CO max · Total floor area of parking facility Af, m2 Step 2. Evaluate CO generation rate: (1) Determine the peak CO generation rate per unit floor area G, in g/(h·m2), for the parking garage: G = NE/Af (2) Normalize the peak CO generation rate using the reference value G⌀= 26.7 g/(h·m2) and Equation (17). This reference value is based on an actual enclosed parking facility (Krarti and Ayari 1998): f= 100G/G0 (16) (17) Step 3. Determine the minimum required ventilation rate 0 per unit floor area using Figure 14, or the correlation presented by Equation (18), depending on CO max* where C = 1.204 106 (m3/s)/(m2.s) for CO max ppm = 15 = 25 ppm = 0.692 106 (m3/s)/(m2.s) for CO max = 0.481 10-6 (m3/s)/(m2-s) for CO max 35 ppm = Example 1. Consider a two-level enclosed parking garage with a total capacity of 450 cars, a total floor area of 8360 m2, and an average height of 2.75 m. The total length of time for a typical car operation is 2 min (120 s). Determine the required ventilation rate for the enclosed parking garage in m3/(s·m2) and in air changes per hour so that the CO level never exceeds 25 ppm. Assume that the number of cars in opera- tion during peak use is 40% of the total vehicle capacity. Solution: Step 1. Garage data: N = 450 0.4 = 180 cars E = 11.67 g/min = 700 g/h, the average of all values of emis- sion rate for a winter day, from Table 8 CO max ppm = 25 = 120 s Step 2. Calculate the normalized CO generation rate: G = (180 700 g/h)/8360 m2 = 15.1 g/(h·m2) f = 100 (15.1 g/h .m2)/26.7 g/(h·m2) = 56.6 Step 3. Determine the ventilation requirement, using Figure 14 or the correlation of Equation (18) for CO max 25 ppm. = 0 = 0.692 10-6 (m3/s)/(m2.s) 56.6 120 s = 0.0047 m3/(s·m2) Or, for air changes per hour, Notes: (0.0047 (m3/s)/m2 3600 s/h)/2.74 m = 6.2 1. Ifthe average vehicle CO emission rate is reduced to E = 6.60 g/min, because of, for instance, better emission standards or better maintained cars, the required minimum ventilation rate decreases to 0.0027 m3/ (s·m2) or 3.5 ach. 2. Once calculations are made and a decision reached to use CO demand ventilation control, increasing airflow through a safety margin does not increase operating costs; larger fans work for shorter periods to sweep the garage and maintain satisfactory conditions. CO Demand v entilation Control. A parking garage ventilation system should meet applicable codes and maintain acceptable con- taminant levels. If permitted by local codes, the ventilation airflow rate should be varied according to CO levels to conserve energy. For example, the ventilation system could consist of multiple fans, with single- or two-speed motors, or variable-pitch blades. In mul- tilevel parking garages or single-level structures of extensive area, independent fan systems with individual controls are preferred. The International Mechanical CodeⓇ (ICC 2009a) allows ventila- tion system operation to be reduced from 0.0038 to 0.00025 m3/ (s·m2) with the use of a CO monitoring system that restores full ventilation when CO levels of29 mg/m3 (25 ppm) are detected. Figure 15 shows the maximum CO level in a tested parking garage (Krarti and Ayari1998) for three car movement profiles and the following ventilation control strategies: · Constant-volume (CV), where the ventilation system is kept on during the entire occupancy period · On/off control, with fans stopped and started based on input from CO sensors · Variable-air-volume (VAV) control, using either two-speed fans or axial fans with variable-pitch blades, based on input from CO sensors Figure 15 also shows typical fan energy savings achieved by on/ off and VAV systems relative to constant-volume systems. Signifi- | {}
98e2ceb1-626e-433b-a656-23ad7cbe575d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Enclosed Vehicular Facilities 16.21 Chart Type: bar CONSTANT CONSTANT ON/OFF VARIABLE CONSTANT item_01 25ppm 20ppm 25ppm 25ppm Fig. 15 Typical Energy Savings and Maximum CO Level Obtained for Demand CO-Ventilation Controls Chart Type: line 6 AM 7 AM 9 AM 11 AM 1 PM 3 PM 5 PM 7 PM item_01 10% 20% 30% 80% 100% 120% 100% 100% Fig. 16 Three Car Movement Profiles cant fan energy savings can be obtained using a CO-based demand ventilation control strategy to operate the ventilation system, main- taining CO levels below 29 mg/m3 (25 ppm). Wear and tear and maintenance on mechanical and electrical equipment are reduced with a CO-based demand strategy. Figure 16 is based on maintaining a 29 mg/m3 (25 ppm) CO level. With most systems, actual energy usage is further reduced if 40 mg/m3 (35 ppm) is maintained. The actual ppm level should fol- low local codes and standards. In cold climates, the additional cost of heating makeup air is also reduced with a CO-based demand strategy. Energy stored in the mass of the structure usually helps maintain the parking garage air temperature at an acceptable level. If only outdoor air openings are used to draw in ventilation air, or ifinfiltration is allowed, the stored energy is lost to the incoming cold air. Types of Ventilation Systems for Enclosed Parking Garages Natural ventilation is not an option for enclosed vehicular facil- ities, but there are two mechanical options available: ducted and ductless. Both options can be effective at controlling contaminants and smoke. However, one method may be more desirable than the other when considering the needs of a particular space. Ducted Systems. Enclosed vehicular facilities require mechanical ventilation. In the United States, this is traditionally done with ducts across the parking structure. Figure 1 7 shows a typ- ical design. Intakes are both high and low and distributed across the parking structure. ![image](/image/placeholder) 0 00 00 Fig. 17 Section View of Typical Ducted System Design Considerations/Issues. Typical design considerations for ducted systems include the following: · Appropriate duct sizing to ensure proper supply and exhaust throughout the space · Clearance height requirements to allow traffic flow underneath duct · Distribution strategy through parking garage to keep cost at a minimum · Areas of higher contaminant injection that may require a nonuni- form exhaust Ductless Systems. Like some tunnel ventilation systems designs, ductless designs use jet fans to dilute and remove contam- inants and control smoke. Ductless ventilation systems are consid- ered acceptable to many global AHJs and continue to grow in popularity. However, the corresponding design methodologies and requirements vary substantially across the globe. Tunnel ventilation projects have used jet fans for many years to induce flow and move pollutants and smoke through the tunnel. Research projects like the Memorial Tunnel Fire v entilation Test program (1995) proved that jet fans have the capability to induce air movement to create a tenable environment for occupant egress. In the late 1990s, jet fan systems for enclosed parking garages began to spread across Europe and continue to grow in the Middle East, Asia, and America. In the United States, example projects include the Children's Hospital ofPhiladelphia and the Ikea Merriam in Kansas. There are several basic components required in a ductless sys- tem: (1) a supply and exhaust fan system, which is required to pro- vide the primary air changes for the space; (2) jet fans used to mix the air and eliminate any dead spots in the system (but do not im- pact the air changes per hour); and (3) control panels combined with contaminant sensors to save energy by controlling the contam- inant levels only as needed (demand based). High-temperature ca- bling is also required in most regions, which can be a significantly high portion of total system cost. Finally, a computational fluid dynamic analysis (CFD) is re- quired in many regions to validate the placement of the fans. This is the case in the United Kingdom and India, as referenced in BS Standard 7346 and National Building Code of India (NBC; BIS 2015), respectively. The projectis then completed with installation, commissioning, and, in some regions, a cold or hot smoke test used as another visual indication of the system performance. Design Considerations/Issues. There are several design consid- erations when designing ductless systems: Inc. ASHRAE, 2019 user. single for Licensed · When conducting the CFD analysis, it is important to identify appropriate contaminant levels, and ensure that simulations accu- rately represent the space. This requires a three-dimensional model of the area. Parameters should be evaluated carefully when comparing different simulations. · Height clearance requirements must be evaluated to ensure traffic can safely pass beneath the equipment. | {}
4f2ad6f7-9d10-4692-a351-cecb3c2ed5d8 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 16.22 · If designing a demand-based system, the designer must consider where the sensors are placed, along with which sensors corre- spond to which jet fans. · When designing for smoke control, the designer must consider how fan placement directs smoke away from pedestrian exits. · Cabling cost can make up a significant cost of the system. Jet fan placement and corresponding control panels can have a signifi- cant impact on cabling cost. Ductless Design Methodology Smoke Control. The role of parking garage ventilation systems during a fire event varies around the world. Specifically, some re- quirements dictate that the ventilation system to be turned off, whereas others require the ventilation system to continuously op- erate to control the spread and purge smoke. Where mechanical ventilation is used for smoke control, it is important to distinguish between emergency ventilation mode (when the fire is active), and smoke purge mode (when the fire is extinguished). Local codes and standards provide the proper design requirements. For example, the U.K. standard BS7346-7:2013 cites two poten- tial purposes for smoke ventilation design for a ductless system. The simplest goal is to assist firefighters clearing smoke during and after the fire. This method does not necessarily control the smoke in any particular manner and operates the same regardless of the fire loca- tion. A ducted system is typically designed this way to purge smoke by operating in exhaust. It is conceivable to create a ducted system with control dampers that target the smoke-filled areas. However, the cost of the system would increase due to the additional controls and dampers. The other potential goal is to create a smoke-free access point for firefighters and to maintain a tenable path of egress. The fire depart- ment needs to enter the building to set up their equipment and extin- guish the fire. Similarly, the means of egress for building occupants should be tenable to ensure that there is at least one exit available independent of the fire location. An optimal smoke-control system accomplishes both of these goals. The ductless design, along with a grid-based fire detection system, allows the designer to create smoke control zones and only operate the necessary jet fans. Smoke Control Zones. The purpose of a smoke control zone is to limit the spread of smoke from one area to another. Requirements for the sizing of these areas vary greatly, depending on the AHJ and on what other fire suppression systems are installed. For example, 2019 ASHRAE Handbook-HVAC Applications (SI) India requires a smoke zone to be 3000 m2, per NBC 2015. The United Kingdom requires 2000 m2 per zone. For the smoke control zone to work properly, it must have sepa- rate supply and exhaust locations in each zone, and the jet fans must be placed so that smoke does not cross between zones in the event of a fire. Also, the control panels are separated so if one panel is damaged from the fire, the other areas in the system still operate. Requirements for smoke zone control add redundancy and safety to the system, but can significantly drive up initial cost for ductless systems. In contrast, ducted systems already clear smoke locally due to the fully distributed duct network, so they typically do not require any additional equipment to satisfy a smoke control zone requirement. Supply and Exhaust Placement Once the contaminant levels and purpose of smoke control are designed, the next step is to determine how many supply and ex- haust shafts are required, and where they are placed. This is a crit- ical design step that can significantly impact the number ofjet fans required and the overall ventilation performance. Figure 18 shows two common design examples. Both designs have louvers and dampers on each level. However, the design on the left has a single, larger exhaust fan placed at the top of the shaft, whereas the other has smaller fans placed at each level. When there is a fire, dampers on the nonfire floor typically close to prevent smoke from entering. The method on the left is preferred, because in the case of a fire on the second floor as indicated, the dampers will close. If there is a damper failure on Basement 1, then the smoke will still be pulled up by the fan. In the design on the right, the smoke may push back into Basement 1 if there is a damper failure. Additionally, some regions require that the exhaust shafts are dedicated to each floor, as shown in Figure 19, to eliminate the pos- sibility of smoke entering nonfire floors. This is the safest approach but adds initial cost to the building by requiring a larger footprint for the exhaust shafts. Often, designers attempt to save cost by using the ramps as fresh air supply with no additional mechanical supply. This may work if there are only one or two levels maximum. However, this usually requires significantly more jet fans due to the contaminated air from the other levels. Thus, it typically involves both lower initial and operating cost to have forced air supply on all levels of the parking garage, because fewer total fans are usually initially installed and fewer fans operate. The ramps are a source for fresh air and should be considered, and placing an additional mechanical supply helps. ![image](/image/placeholder) SUPPLY FAN EXHAUST FAN SUPPLY FAN RETURN/EXHAUST BASEMENT 1 BASEMENT2 BASEMENT 3 LOUVER DAMPER LOUVER DAMPER Fig. 18 Typical Three-Level Underground Parking Garage with Shared Supply and Exhaust System Inc. ASHRAE, 2019 user. single for Licensed | {}
25fd32d9-caa2-4a52-b7ab-d0880a9abe79 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Enclosed Vehicular Facilities 16.23 ![image](/image/placeholder) SUPPLY FAN RETURN/EXHAUST ↗ LOUVER DAMPER Fig. 19 Typical Three-Level Underground Parking Garage with Separate Exhaust Jet Fan Design and Placement Two primary types ofjet fans are used in parking garage design: (1) axial (impulse), the most common, and (2) centrifugal (induc- tion). The number of jet fans can be greatly reduced with a proper supply and exhaust design. Initial jet fan quantity is typically de- termined by rule of thumb, which may vary depending on the de- signer. For example, a common axial jet fan is 315 mm and generates about 25 N thrust. A typical rule of thumb states that a jet fan with 1 N of thrust can cover an area of 10 to 15 m2. Therefore, a 25 N fan could cover 2250 to 375 m2. The range depends on the layout of the space and the locations of the supply and exhaust. If the supply and exhaust are opposite each other, creating a longitu- dinal flow across the floor, then the fans could cover an even greater area. However, ifthe placement creates a lot of dead spots and short circuiting of air, more jet fans could be required. The initial jet fan placement is done in a way conducive to moving fresh air into areas that would not otherwise be reached. To minimize the number ofjet fans, this placement is typically not uni- form across the parking structure. The goal is to mix the air and guide fresh air from the supply to the exhaust. Throw diagrams can help determine the distance between fans. A throw diagram shows the velocity of the air as it exits a jet fan. Generally, it is desirable to keep the air moving at 0.2 to 0.5 m/s. CFD Analysis Once the initial placement is complete, a CFD analysis is recom- mended. The CFD analysis can assist with the following: · Optimizing the number and placement of fans · Simulating the space in normal and fire-mode operation · Determining the visibility, smoke, contaminate levels, and tem- perature throughout the garage When performing a CFD analysis, some important input param- eters to consider are design fires size, method of pollutant injection, boundary conditions, meshing strategy, and physics models. Ensure that these parameters are the same when comparing different CFD models, as they may give conflicting results. Control Sequencing Once the design is finalized, the control sequencing is relatively straightforward. The following sequence is an example for a normal ventilation, demand-based sequence. This example measures CO, but for other contaminants the appropriate levels should be chosen. · 0 ppm: only supply and exhaust fans on (if required to maintain minimal ACH) · CO > 15 ppm: supply and exhaust fans on · 15 < CO < 35 ppm: select jet fans on · CO > 35 ppm: all jet fans on · CO > 100 ppm: all fans on high speed An example sequence in the case of a fire is as follows: 1. Heat or smoke sensor triggers. 2. Waiting period to confirm fire or timeout (in case of sensor fail- ure). 3. Fire alarm goes off. 4. Turn on supply/exhaust fans on fire floor to maintain negative pressure. Close exhaust dampers on nonfire floors. If local codes allow ventilation system operation during a fire event. 5. Wait an evacuation delay period. 6. Turn on all jet fans at full speed. 7. Run system until the fire department turns it off. The jet fans are not turned on immediately because the smoke has not had sufficient time to accumulate and cause harm to occu- pants. Turning the fans on immediately may unnecessarily spread the smoke. For example, BS Standard 7346-7 recommends a wait- ing period, with the length based on building type, size, and number and type of occupants. Also note that the above operation may require a control panel for the fire department, to allow for individ- ual fan control. High-Temperature Product Requirements In some areas, ductless parking garage ventilation designs are intended to be both a normal-mode and smoke-control system to optimize cost. Therefore, the equipment must be selected to operate during a fire. High-temperature fans and cabling, or some other fire protection method such as concrete encasement, are required. As with other requirements, the temperature requirement varies across the globe. The United States typically designs for 250°C for four hours. India varies regionally from 250°C to 300°C for two hours. United Arab Emirates and other Middle Eastern countries are tran- sitioning to even higher temperatures, requiring 400°C for two hours. High-temperature cabling must similarly be selected to ensure the equipment will run in the case of fire. Other Considerations Access tunnels or long, fully enclosed ramps should be designed in the same way as road tunnels. When natural ventilation is used, wall openings or free area should be as large as possible. Part of the free area should be at floor level. For parking levels with large interior floor areas, a central emer- gency smoke exhaust system should be considered for removing smoke (in conjunction with other fire emergency systems) or vehicle fumes under normal conditions. Noise. In general, parking garage ventilation systems move large quantities of air through large openings without extensive ductwork. These conditions, and the highly reverberant nature of the space, contribute to high noise levels, so sound attenuation should be con- sidered in the ventilation system design. This is a pedestrian safety concern, as well, because high fan noise levels in a parking garage may mask the sound of an approaching vehicle. Ambient Standards and Contaminant Control. Air exhausted from a parking garage should meet state and local air pollution con- trol requirements. 3. AUTOMOTIVE REP AIR FACILITIES Automotive repair activities are defined as any repair, modifica- tion, service, or restoration activity to a motor vehicle. This in- cludes, but is not limited to, brake work, engine work, machining Inc. ASHRAE, 2019 user. single for Licensed | {}
7cbe50f2-c65f-4228-bf5d-fa70d52931e2 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 16.24 operations, and general degreasing of engines, motor vehicles, parts, or tools. ASHRAE Standard 62.1 recommends a ventilation rate of 0.0075 m3/(s·m2) for automotive service stations; the Interna- tional Mechanical CodeⓇ (ICC 2009a) allows 0.00375 m3/(s·m2). The designer must determine which code is applicable. The high ventilation rate indicates that contaminants are not related to the occupants, but are produced by the variety of tasks and materials used in the facility. Outdoor ventilation is introduced into the space, and an approximately equal quantity is exhausted through a dedicated exhaust system. As repairs or maintenance are performed on vehicles, it may be necessary to operate the vehicle inside the facility to test and vali- date the work. Additional mechanical ventilation is required to exhaust combustion by-products directly outdoors. An independent source capture system that connects directly to the exhaust pipe of the vehicle must be installed in the facility. These systems are avail- able in either an above- or belowground configuration. Flow rates for individual service bays vary from 0.024 to 0.190 m3/s for auto- mobiles. A large diesel truck will require considerably more airflow per service bay than an automobile. The above-grade system consists of an exhaust fan, associated ductwork, and flexible hoses that attach to the tailpipe of the vehicle in operation. Generally, the system is installed at a high elevation to maintain maximum clearances above floor level. The hose connec- tions are stored in reels positioned near each service bay. The ser- vice technician pulls the hose down and attaches it to the tailpipe by a proprietary connection. The below-grade system is similar in design to an overhead exhaust system. Care must be taken to select an appropriate corrosion-resistant material to be installed underground, because the condensing products of combustion are corrosive to traditional duct materials. The flexible tailpipe exhaust connectors are stored inside the underground duct. After sliding the flex back inside the duct, a hinged cover plate covers the opening flush to the floor. Although there is a diversity factor in the system capacity calcu- lations, both systems must be designed to operate at 100% capacity. A constant-volume fan is used, with all air being exhausted from the space. With a single outlet in use, some means of relief is provided to maintain constant flow through the fan. This equipment can be set up to run continuously or intermittently. Intermittent use requires the general exhaust system to vary between the maximum supply air delivered to the space when the capture system is in use and a lower exhaust flow rate reduced by the amount of air exhausted through the capture system. 4. BUS GARAGES Bus garages generally include a maintenance and repair area, service lane (where buses are fueled and cleaned), storage area (where buses are parked), and support areas such as offices, stock room, lunch room, and locker rooms. The location and layout of these spaces can depend on factors such as local climate, size of the bus fleet, and type of fuel used by the buses. Bus servicing and stor- age areas may be located outside in a temperate region, but are often inside in colder climates. However, large bus fleets cannot always be stored indoors; for smaller fleets, maintenance areas may double as storage space. Local building and/or fire codes may also prohibit dispensing certain types of fuel indoors. In general, bus maintenance or service areas should be ventilated using 100% outdoor air with no recirculation. Therefore, using heat recovery devices should be considered in colder climates. Tailpipe emissions should be exhausted directly from buses at fixed inspection and repair stations in maintenance areas. Offices and similar support areas should be kept under positive pressure to prevent infiltration of bus emissions. 2019 ASHRAE Handbook-HVAC Applications (SI) Maintenance and Repair Areas ASHRAE Standard 62. 1 recommends a minimum ventilation of 0.0075 m3/(s·m2) and the International Mechanical CodeⓇ (ICC 2009a) recommends 0.00375 m3/(s · m2) of floor area in vehicle repair garages, with no recirculation. The designer should deter- mine which code is applicable. However, because the interior ceil- ing height may vary greatly from garage to garage, the designer should consider making a volumetric analysis of contaminant gen- eration and air exchange rates. The section on Bus Terminals con- tains information on diesel engine emissions and ventilation airflow rates needed to control contaminant concentrations in areas where buses are operated. Maintenance and repair areas often include below-grade inspec- tion and repair pits for working underneath buses. Because vapors produced by conventional bus fuels are heavier than air, they tend to settle in these pit areas, so a separate exhaust system should be pro- vided to prevent their accumulation. NFPA Standard 30A recom- mends a minimum of 0.005 m3/(s. m2) in pit areas and the installation of exhaust registers near the floor of the pit. Fixed repair stations, such as inspection/repair pits or hydraulic lift areas, should include a direct exhaust system for tailpipe emis- sions. Such direct exhaust systems have a flexible hose and coupling attached to the bus tailpipe; emissions are discharged to the out- doors by an exhaust fan. The system may be of the overhead reel, overhead tube, or underfloor duct type, depending on the tailpipe location. For heavy diesel engines, a minimum exhaust rate of 0.28 m3/s per station is recommended to capture emissions without creating excessive backpressure in the vehicle. Fans, ductwork, and hoses should be able to receive vehicle exhaust at temperatures exceeding 260°C without degradation. Bus garages often include areas for battery charging, which can produce potentially explosive concentrations of corrosive, toxic gases. There are no published code requirements for ventilating battery-charging areas, but DuCharme (1991) suggested using a combination of floor and ceiling exhaust registers to remove gas- eous by-products. The recommended exhaust rates are 0.0114 m3/ (s·m2) of room area at floor level to remove acid vapors and 0.0038 m3/ (s·m2) of room area at ceiling level to remove hydrogen gases. The associated supply air volume should be 10 to 20% less than exhaust air volume, but designed to provide a minimum termi- nal velocity of0.5 m/s at floor level. If the battery-charging space is located in the general maintenance area rather than in a dedicated space, an exhaust hood should be provided to capture gaseous by- products. Chapter 33 contains specific information on exhaust hood design. Makeup air should be provided to replace that removed by the exhaust hood. Garages may also contain spray booths, or rooms for painting buses. Most model codes reference NFPA Standard 33 for spray booth requirements; this standard should be reviewed when designing heating and ventilating systems for such areas. Servicing Areas For indoor service lanes, ASHRAE Standard 62.1 recommends a minimum ventilation of 0.0075 m3/(s·m2) and the International Mechanical CodeⓇ (ICC 2009a) recommends 0.00375 m3/(s·m2) of floor area in vehicle repair garages, with no recirculation. The designer should determine which code is applicable. However, because the interior ceiling height may vary greatly from garage to garage, the designer should consider making a volumetric analysis of contaminant generation and air exchange rates. The section on Bus Terminals contains information on diesel engine emissions and ventilation airflow rates needed to control contaminant concentra- tions in areas where buses are operated. Because of the increased potential for concentrations of flamma- ble or combustible vapor, HVAC systems for bus service lanes Inc. ASHRAE, 2019 user. single for Licensed | {}
a586473c-ecae-4c05-912c-1b7332b0b535 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Enclosed Vehicular Facilities 16.25 should not be interconnected with systems serving other parts of the bus garage. Service-lane HVAC systems should be interlocked with fuel-dispensing equipment, to prevent operation of the latter if the former is shut off or fails. Exhaust inlets should be located both at ceiling level and 75 to 300 mm above the finished floor, with supply and exhaust diffusers/registers arranged to provide air movement across all planes of the dispensing area. A typical equipment arrangement is shown in Figure 20. Another feature in some service lanes is the cyclone cleaning system: these devices have a dynamic connection to the front door(s) of the bus, through which a large-volume fan vacuums dirt and debris from inside the bus. A large cyclone assembly then re- moves dirt and debris from the airstream and deposits it into a large hopper for disposal. Because of the large volume of air involved, the designer should consider the discharge and makeup air systems required to complete the cycle. Recirculation and energy recovery should be considered, especially during winter. To aid in contami- nant and heat removal during summer, some systems discharge the cyclone air to the outdoors and provide untempered makeup air through relief hoods above the service lane. Storage Areas Where buses are stored inside, the minimum ventilation standard is based upon the applicable code: 0.00375 m3/(s·m2) for the Inter- national Mechanical CodeⓇ. or 0.0075 m3/(s·m2) for ASHRAE , Standard 62.1, subject to volumetric considerations. The designer should also consider the increased contaminant levels present during peak traffic periods. One example is morning pullout, when the majority of the fleet is dispatched for rush-hour commute. It is common practice to start and idle a large number of buses during this period to warm up the engines and check for defects. As a result, the emissions concentra- tion in the storage area rises, and additional ventilation may be required to maintain contaminant levels in acceptable limits. Using supplemental purge fans is a common solution to this problem. These purge fans can either be (1) interlocked with a timing device to operate during peak traffic periods, (2) started manually on an as- needed basis, or (3) connected to an air quality monitoring system that activates them when contaminant levels exceed some preset limit. ![image](/image/placeholder) SUPPLY AND EXHAUST SYSTEMS FOR SERVICE LANE INDEPENDENT FROM SYSTEMS SERVING OTHER 100% AREAS IN GARAGE MAKEUP AIR UNIT EXHAUST FAN SUPPLY DIFFUSERS EXHAUST INLETS AND EXHAUST INLETS LOCATED AT ARRANGED TO PROVIDE CEILING LEVEL AIR MOVEMENT ACROSS AND 75 TO 300 mm ALL PLANES OF ABOVE FINISHED BUS SERVICING DISPENSING AREA FLOOR AREA INTERLOCK EXHAUST FANS AND MAKEUP AIR UNITS WITH DISPENSING EQUIPMENT Fig. 20 Typical Equipment Arrangement for Bus Garage Design Considerations and Equipment Selection Most model codes require that open-flame heating equipment, such as unit heaters, be located at least 2.4 m above the finished floor or, where located in active trafficways, 0.6 m above the tallest vehicle. Fuel-burning equipment outside the garage area, such as boilers in a mechanical room, should be installed with the combus- tion chamber at least 460 mm above the floor. Combustion air should be drawn from outside the building. Exhaust fans should be nonsparking, with their motors located outside the airstream. Infrared heating systems and air curtains are often considered for bus repair garages because of the size of the facility and amount of infiltration through the large doors needed to move buses in and out of the garage. However, infrared heating must be used cautiously in areas where buses are parked or stored for extended periods, because the buses may absorb most of the heat, which is then lost when the buses leave the garage. This is especially true during morning pullout. Infrared heating can be applied with more success in the service lane or at fixed repair positions. Air curtains should be considered for high-traffic doorways to limit both heat loss and infiltration of cold air. Where air quality monitoring systems control ventilation equip- ment, maintainability is a key factor in determining success of the application. The high concentration of particulate matter in bus emissions can adversely affect monitoring equipment, which often has filtering media at sampling ports to protect sensors and instru- mentation. The location of sampling ports, effects of emissions fouling, and calibration requirements should be considered when selecting monitoring equipment to control ventilation systems and air quality of a bus garage. NO2 and CO exposure limits published by OSHA and the EPA should be consulted to determine contami- nant levels at which exhaust fans should be activated. Effects of Alternative Fuel Use Because of legislation limiting contaminant concentrations in diesel bus engine emissions, the transportation industry has begun using buses that operate on alternative fuels, including methanol, ethanol, hydrogen (and fuel cells), compressed natural gas (CNG), liquefied natural gas (LNG), and liquefied petroleum gas (LPG). Flammability, emission, and vapor dispersion characteristics of these fuels differ from those of conventional fuels, for which cur- rent code requirements and design standards were developed. Thus, established ventilation requirements may not be valid for bus garage facilities used by alternative-fuel vehicles. The designer should consult current literature on HVAC system design for these facilities rather than relying on conventional practices. One source is the Alternative Fuels Data Center at the U.S. Department of En- ergy in Washington, D.C; their web site (www.eere.energy.gov/afdc) includes design recommendations for various alternative fuels. The DOT (1996a, 1996b, 1996c, 1997b, 1998) Volpe Transportation Center has also issued several guidelines for alternative-fuel bus facilities, which can be consulted for additional suggestions. CNG Vehicle Facilities. For CNG bus facilities, NFPA Stan- dard 52 recommends a separate mechanical ventilation system pro- viding at least 0.017 m3/s per 12 m3, or 5 ach, for indoor fueling and gas processing/storage areas. The ventilation system should oper- ate continuously or be activated by a continuously monitoring nat- ural gas detector when a gas concentration of not more than 20% of the lower flammability limit (LFL) is present. The fueling or fuel- compression equipment should be interlocked to shut down if the mechanical ventilation system fails. Supply inlets should be located near floor level; exhaust outlets should be located high in the roof or exterior wall structure. The International Mechanical CodeⓇ (ICC 2009a) has identical requirements, except that it re- quires activation of the ventilation system at 25% of the LFL, and Inc. ASHRAE, 2019 user. single for Licensed | {}
4f6cb78c-c676-4abf-9135-f57d75d11b38 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 16.26 2019 ASHRAE Handbook-HVAC Applications (SI) the requirements apply to maintenance and repair areas as well as indoor fueling facilities. DOT (1996a) guidelines for CNG facilities address bus storage and maintenance areas, as well as bus fueling areas. DOT recommen- dations include (1) minimizing potential for dead-air zones and gas pockets (which may require coordination with architectural and struc- tural designers); (2) using a normal ventilation rate of6 ach, with pro- visions to increase that rate by an additional 6 ach in the event of a gas release; (3) using nonsparking exhaust fans rated for use in Class 1, Division 2 areas (as defined by NFPA Standard 70); and (4) increas- ing the minimum ventilation rate in smaller facilities to maintain dilu- tion levels similar to those in larger facilities. Open-flame heating equipment should not be used, and the surface temperature ofheating units should not exceed 425°C. In the event of a gas release, de- energizing supply fans that discharge near the ceiling level should be considered, to avoid spreading the gas plume. LNG Vehicle Facilities. NFPA Standard 52 includes require- ments for LNG bus facilities. The standard recommends a separate mechanical ventilation system providing at least 0.017 m3/s per 12 m3, or 5 ach, for indoor fueling areas. The ventilation system should operate continuously or be activated by a continuously mon- itoring natural gas detection system when a gas concentration of not more than 20% of the LFL is present. Fueling equipment should be interlocked to shut down in case the mechanical ventilation system fails. DOT (1997b) provides further information on LNG fuel. LPG Vehicle Facilities. NFPA Standard 58 and the Interna- tional Fuel Gas CodeⓇ (ICC 2009d) contain similar provisions relating specifically to LPG-fueled vehicles. Both standards pro- hibit indoor fueling of all LPG vehicles, allowing only an ade- quately ventilated weather shelter or canopy for fueling operations. However, the term "adequately ventilated" is not defined by any prescriptive rate. Vehicles are permitted to be stored and serviced indoors under NFPA Standard 58, provided they are not parked near sources of heat, open flames (or similar sources of ignition), or "inadequately ventilated" pits. That standard does not recommend a ventilation rate for bus repair and storage facilities, but it does rec- ommend a minimum of 0.005 m3/(s·m2) in buildings and structures housing LPG distribution facilities. DOT (1996b) provides addi- tional information on LPG fuel. Hydrogen Vehicle Facilities. NFPA Standard 52 includes re- quirements for gaseous and liquid hydrogen bus facilities. The stan- dard recommends a separate mechanical ventilation system providing at least 0.017 m3/s per 12 m3, but not less than 0.005 m3/ (s·m2), or 5 ach, for indoor gaseous hydrogen fueling areas. The ventilation system should operate continuously or be activated by a continuously monitoring natural gas detection system when a gas concentration of not more than 25% of the LFL is present. Fu- eling equipment should be interlocked to shut down in case the me- chanical ventilation system fails. Liquid hydrogen fueling facilities are prohibited indoors. The International Mechanical CodeⓇ (ICC 2009a) has the same requirements, which apply to maintenance and repair areas as well as indoor fueling facilities. DOT (1998) provides additional information on hydrogen fuel. 5. BUS TERMINALS The physical configuration of bus terminals varies considerably. Most terminals are fully enclosed spaces containing passenger wait- ing areas, ticket counters, and some retail areas. Buses load and un- load outside the building, generally under a canopy for weather protection. In larger cities, where space is at a premium and bus ser- vice is extensive or integrated with subway service, bus terminals may have comprehensive customer services and enclosed (or semi- enclosed) multilevel structures, busway tunnels, and access ramps. Waiting rooms and consumer spaces should have controlled envi- ronments in accordance with normal HV AC system design practices for public terminal occupancies. In addition to providing the recom- mended ventilation air rate in accordance with ASHRAE Standard 62.1, the space should be pressurized against infiltration from the busway environment. Pressurized vestibules should be installed at each doorway to further reduce contaminant migration and to main- tain acceptable air quality. Waiting rooms, passenger concourse ar- eas, and platforms are typically subjected to a highly variable people load. The average occupant density may reach 1.0 m2 per person and, during periods of extreme congestion, 0.3 to 0.5 m2 per person. The choice between natural and mechanical ventilation should be based on the physical characteristics of the bus terminal and the airflow required to maintain acceptable air quality. When natural ventilation is selected, the individual levels of the bus terminal should be open on all sides, and the slab-to-ceiling dimension should be sufficiently high, or the space contoured, to allow free air circulation. Jet fans can be used to improve natural airflow in the busway, with relatively low energy consumption. Mechanical sys- tems that ventilate open platforms or gate positions should be con- figured to serve bus operating areas, as shown in Figures 21 and 22. Platforms Platform design and orientation should be tailored to expedite passenger loading and unloading, to minimize both passenger expo- sure to the busway environment and dwell time of an idling bus in an enclosed terminal. Naturally ventilated drive-through platforms may expose passengers to inclement weather and strong winds. An enclosed platform (except for an open front), with the appropriate mechanical ventilation system, should be considered. Partially enclosed platforms can trap contaminants and may require mechan- ical ventilation to achieve acceptable air quality. Multilevel bus terminals have limited headroom, which restricts natural ventilation system performance. These terminals should have mechanical ventilation, and all platforms should be either partially or fully enclosed. The platform ventilation system should not induce contaminated airflow from the busway environment. Supply air velocity should also be limited to 1.3 m/s to avoid drafts on the platform. Partially enclosed platforms require large amounts of outdoor air to hinder fume penetration; experience indicates that a minimum of 0.086 m3/(s · m2) of platform area is typically required during rush hours, and about half this rate is required during other ![image](/image/placeholder) VENTILATION AIR FROM UNCONTAMINATED SOURCE FAN PLATFORM CURB PARTIAL ENCLOSURE BUS DISTRIBUTION DUCT SUPPLY AND DISCHARGE REGISTERS PLAN VIEW DISTRIBUTION DUCT PARTIAL ENCLOSURE SUPPLY REGISTER BUS PLATFORM ROADWAY SECTION VIEW Fig. 21 Partially Enclosed Platform, Drive-Through Type Inc. ASHRAE, 2019 user. single for Licensed | {}
75e95043-29c6-4449-8942-7fd8ea9c618e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Enclosed Vehicular Facilities 16.27 ![image](/image/placeholder) SAWTOOTH CURB AIR SUPPLY DUCT (VENTILATION AIR FROM LEAST CONTAMINATED SOURCE) BUS FULLY ENCLOSED WAITING ROOM BUS WAITING ROOM WALL FULL HEIGHT BUS Fig. 22 Fully Enclosed Waiting Room with Sawtooth Gates periods. Figure 21 shows a partially enclosed drive-through plat- form with an air distribution system. Platform air quality should remain essentially the same as that of the ventilation air introduced. Because ofthe piston effect, however, some momentarily high concentrations of contaminants may occur on the platform. Separate ventilation systems with two-speed fans (for each platform) allow operational flexibility, in both fan usage frequency and supply airflow rate for any one platform. Fans should be controlled automatically to conform to bus operating schedules. In cold climates, mechanical ventilation may need to be reduced or heated during extreme winter weather conditions. For large terminals with heavy bus traffic, fully enclosed platforms are strongly recommended. Fully enclosed platforms can be ade- quately pressurized and ventilated with normal heating and cooling air quantities, depending on the construction tightness and number of boarding doors and other openings. Conventional air distribution can be used; air should not be recirculated. Openings around doors and in the enclosure walls are usually adequate to relieve air pressure, unless the platform construction is extraordinarily tight. Figure 22 shows a fully enclosed waiting room with sawtooth gates. Doors between sawtooth gates and the waiting room should re- main closed, except for passenger loading and unloading. The waiting room ventilation system should provide positive pressurization to minimize infiltration of contaminants from the busway environment. Supply air from a suitable source should be provided at the passenger boarding area to dilute local contaminants to acceptable levels. Bus Operation Areas Ventilation for bus operation areas should be designed and evalu- ated to maintain engine exhaust contaminant concentrations within the limits set by federal and local regulations and guidelines. With the proliferation of alternative fuels, such as biodiesel, ethanol, methanol, compressed natural gas (CNG), and liquefied natural gas (LNG), a bus terminal ventilation system should not only be de- Table 9 8 h TWA Exposure Limits for Gaseous Pollutants from Diesel Engine Exhaust, ppm ¦ Substance ¦ OSHA PEL ¦ ACGIH TLV ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Carbon monoxide (CO) ¦ 50 ¦ 25 ¦ ¦ Carbon dioxide (CO2) ¦ 5000 ¦ 5000 ¦ ¦ Nitric oxide (NO) ¦ 25 ¦ 25 ¦ ¦ Nitrogen dioxide (NO2) ¦ 5.0* ¦ 3.0 ¦ ¦ Formaldehyde (HCHO) ¦ 0.75 ¦ 0.30* ¦ ¦ Sulfur dioxide (SO2) ¦ 5 ¦ 2.0 ¦ *Ceiling value Note: For data on diesel bus and truck engine emissions, see Watson et al. (1988). signed for maintaining acceptable air quality, but should also consid- er the safety risks associated with potential leakage from buses operating with alternative fuel loads. In an enclosed or semi- enclosed area, a comprehensive risk assessment should be performed for the specific types of buses operating in the bus terminal. The nature of the bus engines should be determined for each project. Contaminants. Of all the different types of buses in operation, engine exhaust from diesel buses has the most harmful quantities of contaminants. Some diesel buses also have small auxiliary gasoline engines to drive the vehicle air-conditioning system. Excessive exposure to diesel exhaust can cause adverse health effects, ranging from headache and nausea to cancer and respiratory disease. Tests on the volume and composition of exhaust gases emitted from diesel engines during various traffic conditions indicate large variations depending on the (1) local air temperature and humidity; (2) manu- facturer, size, and adjustment of the engine; and (3) type of fuel used. Components of diesel engine exhaust gases that affect the venti- lation system design are NOx, hydrocarbons, formaldehyde, odor constituents, aldehydes, smoke particles, sulfur dioxide, and a rela- tively small amount of CO. Diesel engines operating in enclosed spaces also reduce visibility, and generate both odors and particulate matter. Table 9 lists major health-threatening contaminants found in die- sel engine exhaust and the exposure limits set by OSHA and ACGIH. OSHA permissible exposure limits (PEL) are legally enforce- able limits, whereas the ACGIH threshold limit values (TL V) are industrial hygiene recommendations. All the limits are time- weighted averages (TWAs) for 8 h exposure, unless noted as a ceil- ing value. NOx occurs in two basic forms: nitrogen dioxide (NO2) and nitric oxide (NO). NO2 is the major contaminant considered in bus terminal ventilation system design. Prolonged exposure to NO2 concentrations of more than 5 ppm causes health problems. Further- more, NO2 affects light transmission and thereby reduces visibility. NO2 is intensely colored and absorbs light over the entire visible spectrum, especially at shorter wavelengths. Odor perception of NO2 is immediate at 0.42 ppm, but can be perceived by some at levels as low as 0.12 ppm. Bus terminal operations also affect the quality of surrounding ambient air. The ventilation airflow rate, contaminant levels in ex- haust air, and location and design of the air intakes and discharges determine the effect of the bus terminal on local ambient air quality. State and local regulations, which require consideration of local atmospheric conditions and ambient contaminant levels in bus ter- minal ventilation system design, must be followed. Calculation of Ventilation Rate To calculate the ventilation rate, the total amount of engine exhaust gases should be determined using the bus operating schedule and amount of time that the buses are in various modes of operation (i.e., cruising, decelerating, idling, and accelerating). The designer must Inc. ASHRAE, 2019 user. single for Licensed | {}
52cc2a01-34ab-4346-9561-c36063945c7f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 16.28 2019 ASHRAE Handbook-HVAC Applications (SI) Table 10 EPA Emission Standards for Urban Bus Diesel Engines ¦ ¦ Emissions, g/(h·kW) ¦ Emissions, g/(h·kW) ¦ Emissions, g/(h·kW) ¦ Emissions, g/(h·kW) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Model Year ¦ Hydrocarbons (HC) ¦ Carbon Monoxide (CO) ¦ Oxides of Nitrogen (NOx) ¦ Particulate Matter (PM) ¦ ¦ 1991 ¦ 1.74 ¦ 20.8 ¦ 6.72 ¦ 0.335 ¦ ¦ 1993 ¦ 1.74 ¦ 20.8 ¦ 6.72 ¦ 0.135 ¦ ¦ 1994 ¦ 1.74 ¦ 20.8 ¦ 6.72 ¦ 0.094 ¦ ¦ 1996 ¦ 1.74 ¦ 20.8 ¦ 6.72 ¦ 0.067* ¦ ¦ 1998 to 2003 ¦ 1.74 ¦ 20.8 ¦ 5.37 ¦ 0.067* ¦ ¦ 2004 to 2006 ¦ 1.74 ¦ 20.8 ¦ 2.68 to 3.35 ¦ 0.067* ¦ ¦ 2007 and later ¦ 0.198 ¦ 20.8 ¦ 0.027 ¦ 0.014 ¦ *In-use PM standard 0.094 g/(h·kW) ascertain the grade (if any) in the terminal, and whether platforms are drive-through, drive-through with bypass lanes, or sawtooth. Bus headway, bus speed, and various platform departure patterns must also be considered. For instance, with sawtooth platforms, the departing bus must accelerate backward, brake, and then accelerate forward. The drive-through platform requires a different pattern of departure. Certain codes prescribe a maximum idling time for bus engines, usually 3 to 5 min. Normally, 1 to 2 min of engine operation is required to build up brake air pressure. EPA emission standards for urban bus engines are summarized in Table 10 (bus emission stan- dards in the state of California are more restrictive). The latest version of the EPA emission factor algorithm should be used to esti- mate bus tailpipe emissions. MOBILE6.2 (EPA 2002) has been replaced by MOVES2010 (EPA 2009, 2010). Input parameters (e.g., local vehicular inspection and maintenance requirements) suitable for a specific facility should be obtained from the appropri- ate air quality regulatory agency. Discharged contaminant quantities should be diluted by natural and/or mechanical ventilation to accepted, legally prescribed levels. To maintain odor control and visibility, exhaust gas contaminants should be diluted with outdoor air in the proportion 75 to 1. Where urban-suburban bus operations are involved, the ventila- tion rate varies considerably throughout the day and also between weekdays and weekends. Fan speed or blade pitch control should be used to conserve energy. The required ventilation airflow may be reduced by removing contaminant emissions as quickly as possible. This can be achieved by mounting exhaust capture hoods in the ter- minal ceiling, above each bus exhaust stack. Exhaust air collected by the hoods is then discharged outside of the facility through a ded- icated exhaust system. Effects of Alternative Fuel Use. As discussed in the section on Bus Garages, alternative fuels are being used more widely in lieu of conventional diesel fuel, especially for urban-suburban bus routes, as opposed to long-distance bus service. Current codes and design standards developed for conventional fuels may not be valid for alternative-fuel buses. Comprehensive design guidelines are not yet available; there is a lack of design standards and long-term safety records for the alternative-fuel buses and their components. Special attention should be given to both risk assessment and design of HVAC and electrical systems for these facilities with regard to a fuel tank or fuel line leak. Research is con- tinuing in this application; further information may be available from the DOT Volpe Transportation Center and NFPA Standards 52 and 58. Bus terminal design should include a risk assessment to review terminal operations and identify potential hazards from alternative fuel buses. Facility managers should adopt safety principles to determine the acceptability of these hazards, based on severity and frequency of occurrence. All hazards deemed undesirable or unac- ceptable should be eliminated by system design or by modifications to operations. Natural Gas (NG) Buses. Fuel burned in LNG and CNG buses has a composition of up to 98% methane (CH4). Methane burns in a self-sustained reaction only when the volume percentage of fuel and air is in specific limits. The lower and upper flammability, or explosive, limits (LEL and UEL) for methane are 5.3% and 15.0% by volume, respectively. At standard conditions, the fuel/air mixture burns only in this range and in the presence of an ignition source, or when the spontaneous ignition temperature of 540°C is exceeded. Electrical and mechanical systems in a bus terminal facility should be designed to minimize the number of ignition sources at locations where an explosive natural gas mixture can accumulate. Although emissions from an NG bus engine include unburned methane, design of the bus terminal ventilation system must be based on maintaining facility air quality below the LEL in the event of a natural gas leak. A worst-case scenario for natural gas accumu- lation in a facility is a leak from the bus fuel line or fuel tank, or a sudden high-pressure release of natural gas from a CNG bus fuel tank through its pressure relief device (PRD). For instance, a typical CNG bus may have multiple fuel tanks, each holding gas at 25 MPa and 21°C. If the PRD on a single tank were to open, the tank con- tents would escape rapidly. After 1 min, 50% of the fuel would be released to the surroundings, after 2 min, 80% would be released, and 90% would be released after 3 min. Because such a large quantity of fuel is released so quickly, prompt activation of a ventilation purge mode is essential. Where installed, a methane detection system should activate a ventilation purge and an alarm at 20% of the LEL. Placement of methane detectors is very important; stagnant areas, bus travel lanes, and bus loading areas must be considered. In addition, although methane is lighter than air (the relative density of CH4 is 0.55), some research indicates that it may not rise immediately after a leak. In a natural gas release from a PRD, the rapid throttle-like flow through the small-diameter orifice of the device may actually cool the fuel, mak- ing it heavier than air. Under these conditions, the fuel may migrate toward the floor until reaching thermal equilibrium with the sur- rounding environment; then, natural buoyancy forces drive the fuel/ air mixture to the ceiling. Thus, the designer may consider locating methane detectors at both ceiling and floor levels of the facility. Although no specific ventilation criteria have been published for natural gas vehicles in bus terminals, NFPA Standard 52 recom- mends a blanket rate of 5 ach in fueling areas. DOT (1996a) guide- lines for CNG transit facility design recommend a slightly more conservative 6 ach for normal ventilation rates in bus storage areas, with capability for 12 ach ventilation purge rate (on activation by the methane sensors). The designer can also calculate a ventilation purge rate based on the volumetric flow rate of methane released, duration of the release, and size of the facility. The size of the bus terminal significantly affects the volume flow of ventilation air required to maintain the average concentration of methane below 10% ofthe LEL. The larger the facility, the lower the number of air changes required. However, a methane concentration that exceeds the LEL can be expected in the immediate area of the leak, regardless of the ventilation rate used. The size of the plume and location/duration of the unsafe methane concentration may be determined using comprehensive modeling analysis, such as com- putational fluid dynamics. Source of Ventilation Air. Because dilution is the primary means of contaminant level control, the ventilation air source is extremely important. The cleanest available ambient air should be used for ventilation; in an urban area, the cleanest air is generally above roof level. Surveys of contaminant levels in ambient air should be conducted, and the most favorable source of ventilation air should be used. The possibility of short-circuiting exhaust air, Inc. ASHRAE, 2019 user. single for Licensed | {}
30e5efaf-5972-4491-91df-3941fe2ac683 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Enclosed Vehicular Facilities 16.29 because of prevailing winds and/or building airflow patterns, should also be evaluated. If the only available ambient air has contaminant levels exceeding EPA ambient air quality standards, the air should be treated to control offending contaminants. Air-cleaning systems for removing gases, vapors, and dust should be installed to achieve nec- essary air quality. Control by Contaminant Level Monitoring. Time clocks are one of the most practical means of controlling a bus terminal venti- lation system. Time-clock-based ventilation control systems are typically coordinated with both bus movement schedules and in- stalled smoke monitoring devices (i.e., obscurity meters). A bus terminal ventilation system can also be controlled by monitoring levels ofindividual gases, such as CO, CO2, NO2, methane, or other toxic or combustible gases. Dispatcher's Booth. The bus dispatcher's booth should be kept under positive air pressure to prevent infiltration of engine exhaust fumes. Because the booth is occupied for sustained periods, both normal interior comfort conditions and minimized gas contaminant levels must be maintained during the hours of occupancy. 6. TOLLBOOTHS Toll plazas for vehicular tunnels, bridges, and toll roads gener- ally include a series of individual tollbooths. An overhead weather canopy and a utility tunnel (located below the roadway surface) are frequently provided for each toll plaza. The canopy allows installa- tion of roadway signs, air distribution ductwork, and lighting. The utility tunnel is used to install electrical and mechanical systems; it also provides access to each tollbooth. An administration building is usually situated nearby. The current trend in toll collection facility design favors automatic toll collection methods that use magnetic tags. However, new and retrofit toll plazas still include a number of manual toll collection lanes with individual tollbooths. Toll collectors and supervisors are exposed to adverse environ- mental conditions similar to those in bus terminals and under- ground parking garages. Automotive emission levels are considerably higher at a toll facility than on a highway because of vehicle deceleration, idling, and acceleration. Increased levels of CO, NOx, diesel particulates, gasoline fumes, and other automotive emissions have a potentially detrimental effect on health. Toll collectors cannot totally rely on physical barriers to isolate them from automotive emissions, because open windows are necessary for collecting tolls. Frequent opening and closing of the window makes the heating and cooling loads of each booth fluctuate independently. Heat loss or gain is extremely high, because all four sides (and frequently the ceiling) of the relatively small tollbooth are exposed to the outdoor ambient air temperature. HVAC air distribution requirements for a toll facility should be carefully evaluated to maintain an acceptable environment inside the tollbooth and minimize the adverse ambient conditions to which toll-collecting personnel are exposed. Air Quality Criteria w orkplace air quality standards are mandated by local, state, and federal agencies. Government health agencies differ on acceptable CO levels. ACGIH (1998) recommends a threshold limit of 29 mg/ m3 (25 ppm) of CO for an 8 h exposure. OSHA (2001a) regulations are for 55 mg/m3 (50 ppm) for repeated daily 8 h exposure to CO in the ambient air. The U.S. National Institute for Occupational Safety and Health (NIOSH 2005) recommends maintaining an average of 40 mg/m3 (35 ppm) and a maximum level of230 mg/m3 (200 ppm). Criteria for maximum acceptable CO levels should be developed with the proper jurisdiction. As a minimum, the ventilation system should be designed to maintain CO levels below the threshold limit for an 8 h exposure. Deceleration, idling, and acceleration of vehi- cles, and varying traffic patterns make it difficult to estimate CO lev- els around specific toll-collecting facilities without using computer programs. Longitudinal tunnel ventilation systems with jet fans or Saccardo nozzles are increasingly popular for vehicular tunnels with unidi- rectional traffic flow. These longitudinal ventilation systems dis- charge air contaminants from the tunnel through the exit portal. If toll plazas are situated near the exit portal, resultant CO levels around the facilities may be higher than for other toll facilities. If a recirculating HVAC system were used for a toll collection facility, any contaminants entering a particular tollbooth would remain in the ventilation air. Therefore, tollbooth ventilation sys- tems should distribute 100% outdoor air to each booth to prevent both intrusion and recirculation of airborne contaminants. Design Considerations The toll plaza ventilation system should pressurize booths to keep out contaminants emitted by traffic. Opening the window during toll collection varies depending on booth design and the habits of the individual toll collector. The amount of ventilation air required for pressurization varies accordingly. Variable-air-volume (V A V) systems that are achievable with con- trols now available can vary the air supply rate based on either the pressure differential between the tollbooth and the outdoor environ- ment, or the position of the tollbooth window. A fixed (maximum/ minimum) volume arrangement may also be used at toll plazas with a central VA v system. Because the area of the window opening varies with individual toll collector habits and booth architecture, the design air supply rate may be determined based on an estimated average window open area. The minimum air supply (when the booth window is closed) should be based on the amount of air required to meet the heating/ cooling requirements of the booth and that required to prevent infil- tration of contaminants through the door and window cracks. Where the minimum supply rate exceeds the exfiltration rate, provisions to relieve excess air should be made to prevent overpressurization. The space between the booth roof and the overhead canopy may be used to install individual HVAC units, fan-coil units, or VA v boxes. Air ducts and HVAC piping may be installed on top of the plaza canopy or in the utility tunnel. The ducts or piping should be insulated as needed. The amount of ventilation air is typically high compared to the size of the booth; the resulting rate of air change is also high. Supply air outlets should be sized and arranged to deliver air at low velocity. Air reheating should be considered where the supply air tempera- ture is considered too low. In summer, the ideal air supply location is the ceiling of the booth, which allows cooler air to descend through the booth. In winter, the ideal air supply location is from the bottom of the booth, or at floor level. It is not always possible to design ideal distribution for both cooling and heating. When air is supplied from the ceiling, other means for providing heat at floor level (e.g., electric forced-air heaters, electric radiant heating, heating coils in the floor) should be considered. The supply air intake should be located so that air drawn into the system is as free as practicable of vehicle exhaust fumes. The prevailing wind should be considered when locating the intake, which should be as far from the roadway as is practicable to provide better-quality ventilation air. Particle filtration of supply air for booths should be carefully evaluated. The specific level and type of filtering should be based on the ambient level of particulate matter and the desired level of removal. See Chapter 1 1 of the 2017 ASHRAE Handbook-Fundamentals and Chapter 29 in the 2016 ASHRAE Handbook- -HVAC Systems and Equipment for more information. Inc. ASHRAE, 2019 user. single for Licensed | {}
d9026acb-b97b-4ba5-ab64-97291f395c2f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 16.30 Equipment Selection Individual HVAC units and central HVAC are commonly used for toll plazas. Individual HVAC units allow each toll collector to choose between heating, cooling, or ventilation modes. Mainte- nance ofindividual units can be performed without affecting HVAC units in other booths. In contrast, a central HVAC system should have redundancy to avoid a shutdown of the entire toll plaza system during maintenance operations. The design emphasis on booth pressurization requires using 100% outdoor air; high-efficiency air filters should therefore be considered. When a VAV system is used to reduce operating cost, varying the supply rate of 100% outdoor air requires a complex tem- perature control system that is not normally available for individual HVAC units. Individual HV AC units should be considered only where the toll plaza is small or where the tollbooths are so dispersed that a central HVAC system is not economically justifiable. Where hot-, chilled-, or secondary water service is available from an adjacent administration building, an individual fan-coil for each tollbooth and a central air handler for supplying the total volume of ventilation air may be economical. When the operating hours for the booths and administration building are significantly different, sepa- rate heating and cooling for the toll-collecting facility should be con- sidered. Central air distribution system selection should be based on the maximum number of open traffic lanes during peak hours and the minimum number of open traffic lanes during off-peak hours. The HVAC system for a toll plaza is generally required to operate continuously. Minimum ventilation air may be supplied to unoccu- pied tollbooths to prevent infiltration of exhaust fumes. Otherwise, consideration should be given to remotely flushing the closed toll- booths with ventilation air before their scheduled occupancy. 7. DIESEL LOCOMOTIVE FACILITIES Diesel locomotive facilities include shops where locomotives are maintained and repaired, enclosed servicing areas where supplies are replenished, and overbuilds where locomotives routinely oper- ate inside an enclosed space and where railroad workers and/or train passengers may be present. In general, these areas should be kept under slightly negative air pressure to help removal of fumes and contaminants. Ventilation should use 100% outdoor air. However, recirculation may be used to maintain space temperature when a facility is unoccupied or when engines are not running. Heat recovery devices should be considered for facilities in colder cli- mates, though they may require additional maintenance. Historically, ventilation guidelines for locomotive facilities have recommended simple exhaust rates, usually based on the volume of the facility. These were developed over many years of experience and were based on the assumption of nitrogen dioxide as the most critical contaminant. Because contaminant limits for constituents of diesel exhaust have been and are likely to continue changing, ASH- RAE sponsored research project RP-1 191 (Musser and Tan 2004), which included field measurements in several facilities and a para- metric study of design options using computational fluid dynamics. The study resulted in a simplified contaminant-based design proce- dure that allows designers flexibility to adapt to other critical contaminants or concentrations. Both the traditional and RP-1191 approaches are discussed here. Ventilation Guidelines and Facility Types Maintenance and Repair Areas. ASHRAE Standard 62.1 and most model codes require a minimum outdoor air ventilation rate of 0.0075 m3/(s·m2) in vehicle repair garages, with no recirculation recommended. Because the ceiling is usually high in locomotive repair shops, the designer should consider making a volumetric analysis of contaminant generation and air exchange rates rather than using the 0.0075 m3/(s·m2) ventilation rate as a blanket stan- 2019 ASHRAE Handbook-HVAC Applications (SI) dard. The sections on Contaminant Level Criteria and Contaminant Emission Rate have more information on diesel engine exhaust emissions. Information in the section on Bus Garages also applies to loco- motive shops, especially for below-grade pits, battery charging areas, and paint spray booths. However, diesel locomotives gener- ally have much larger engines (ranging to over 4500 kW) than buses. Ventilation is needed to reduce crew and worker exposure to exhaust gas contaminants, and to remove heat emitted from engine radiators. Where possible, diesel engines should not be operated in shops. Shop practices should restrict diesel engine activity and engine operating speeds/intervals; however, some shops require that locomotives be load-tested at high engine speeds. This should be done outdoors if possible, both to reduce indoor contaminants and to avoid problems associated with high heat (sprinkler activation, fire risk, etc.). A dedicated area should be established for diesel engine opera- tions; hoods should be used to capture engine exhaust in this area. If hoods are impractical because of physical obstructions, then dilu- tion ventilation must be used. In designing hoods, the location of each exhaust point on each type of locomotive must be identified so that each hood can be cen- tered and located as close as possible to each exhaust point. Local and state railroad clearance regulations must be followed, along with occupational safety requirements. In some cases, high ceilings or overhead cranes may limit hood use. Some newer systems at- tempt to avoid this problem by using a flexible connection that at- taches to the exhaust. The hood design should not increase backpressure on locomo- tive exhaust; the throat velocity should be kept less than twice the exhaust discharge velocity. The associated duct design should in- clude access doors and provisions for cleaning oily residue, which increases the risk of fire. Fans and other ventilation equipment in the airstream should be selected with regard to the elevated tem- perature of the exhaust air and the effects of the oily residue in the emissions. Sometimes high ceilings or overhead cranes limit the use of hoods. The Manualfor Railway Engineering (AREMA 2007) notes that 6 air changes per hour are usually sufficient to provide adequate dilution for both idling locomotives and short engine runs at high speed. This guideline was developed with nitrogen dioxide as the critical contaminant, with an allowable maximum concentration of 5 ppm(v). Even dilution systems can and should take advantage of thermal buoyancy by removing exhaust air at the ceiling level or a high point in the shop and introducing makeup air at floor level. If exhaust gases are allowed to cool and drop to floor level, locomotive radiator fans (if operating) can cause further mixing in the occupied zone, making removal less effective. Shops in colder climates should be heated both for worker com- fort and to prevent freezing of facility equipment and piping. The heating system may consist of a combination of perimeter con- vectors to offset building transmission losses, underfloor slab or infrared radiation for comfort, and makeup air units for ventilation. Where natural gas is available and local codes allow, direct-fired gas heaters can be an economical compromise to provide a high degree of worker comfort. Air curtains or door heaters are not needed in shops where doors are opened infrequently. Enclosed Servicing Areas. Although most locomotive servicing is done outside, some railroads use enclosed servicing areas for protection from weather and extreme cold. Servicing operations include refilling fuel tanks, replenishing sand (used to aid traction), draining toilet holding tanks, checking lubrication oil and radiator coolant levels, and performing minor repairs. Generally, a locomo- tive spends less than 1 h in the servicing area. Ventilation is needed to reduce personnel exposure to exhaust gas contaminants and remove heat emitted from engine radiators. The designer should Inc. ASHRAE, 2019 user. single for Licensed | {}
f8bf1961-b3cd-445e-8c05-3cc3b6ff6f7e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Enclosed Vehicular Facilities 16.31 also consider the presence of vapors from fuel oil dispensing and sil- ica dust from sanding. Heating may also be included in the design, depending on the need for worker comfort and the operations per- formed. Ventilation for servicing areas should be similar to that for main- tenance and repair areas. Where possible, hoods should be used in lieu of dilution ventilation. However, coordinating hood locations with engine exhaust points may be difficult because different types of locomotives may be coupled together in consists. Elevated sanding towers and distribution piping may also interfere. Contam- inant levels might be higher in servicing areas than in the shops because of constantly idling locomotives and occasional higher- speed movements in servicing areas. For dilution ventilation, the designer should ascertain the type of operations planned for the facility and make a volumetric analysis of expected rates of contam- inant generation and air exchange. Infrared radiation should be considered for heating. As with maintenance and repair areas, direct-fired gas heaters may be eco- nomical. Door heaters or air curtains may be justified because offre- quent opening of doors or a lack of doors. Overbuilds. With increasing real estate costs, the space above trackways and station platforms is commonly built over to enclose the locomotive operation area. Ventilation is needed in overbuilds to reduce crew and passenger exposure to exhaust gases and to remove heat emitted from engine radiators and vehicle air-conditioning sys- tems. Overbuilds are generally not heated. Exhaust emissions from a diesel passenger locomotive operat- ing in an overbuild are greater than those from an idling locomotive because of head-end power requirements. The designer should de- termine the types of locomotives to be used and the operating prac- tices in the overbuild. As with locomotive repair shops and servicing areas, hoods are recommended to capture engine exhaust. According to the Overbuild ofAmtrak Right-of- Way Design Policy (Amtrak 2005), the air temperature at the exhaust source will be be- tween 175 and 510°C. A typical ventilation design could have hoods approximately 5.5 to 7 m above the top of the rail, with throat velocities between 9 and 11 m/s. For dilution ventilation, the de- signer should perform a volumetric analysis of contaminant gener- ation and air exchange rates. Contaminant Level Criteria In most locations, diesel exhaust is not regulated specifically, although concentrations of many substances found in diesel exhaust are regulated. The U.S. Occupational Safety and Health Administra- tion (OSHA 2001a, 2001b) identifies carbon dioxide (CO2), carbon monoxide (CO), nitrogen dioxide (NO2), nitric oxide (NO), diesel particulate matter (DPM), and sulfur dioxide (SO2) as major compo- nents of diesel exhaust. Thirty-one additional substances are identi- fied as minor components, with seventeen of these being polycyclic aromatic hydrocarbons (PAH). These minor components are ele- ments of DPM. Federal OSHA requirements establish limits for these com- pounds in the United States, although a few states may set more restrictive requirements. Also, the American Council of Govern- mental and Industrial Hygienists (ACGIH) publishes guideline val- ues for use in industrial hygiene that are not legally enforceable, but may evolve more quickly than OSHA requirements (ACGIH 2001). Other countries set their own contaminant limits, though these may draw heavily from the ACGIH and other U.S. publications. When no regulations exist for DPM, nitrogen dioxide (NO2) is present in diesel exhaust emissions at the highest levels relative to its published limits. In these circumstances, systems designed to control nitrogen dioxide will maintain other exhaust-related contaminants well below their respective limits. Table 1 1 shows published exposure limits in parts per million (ppm). Federal OSHA, ACGIH, and NIOSH limits are current as of at least February 2003. Other lim- Table 11 Contaminant Exposure Limits for NO2 (For information only; check updated local regulations) ¦ ¦ NO2, mg/m3 ¦ NO2, mg/m3 ¦ NO2, mg/m3 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Entity ¦ 8 h ¦ 15 min ¦ Ceiling ¦ ¦ OSHA: USA (PEL) ¦ ¦ ¦ 9 ¦ ¦ ACGIH: USA (TLV) ¦ 6 ¦ 9 ¦ ¦ ¦ NIOSH: USA (REL) ¦ ¦ 2 ¦ ¦ ¦ Australia ¦ 6 ¦ 9 ¦ ¦ ¦ Belgium ¦ 6 ¦ 9 ¦ ¦ ¦ Denmark ¦ 6 ¦ 9 ¦ ¦ ¦ Finland ¦ 6 ¦ 11 ¦ ¦ ¦ France ¦ ¦ 6 ¦ ¦ ¦ Germany ¦ ¦ ¦ 9 ¦ ¦ Japan ¦ ¦ ¦ ¦ ¦ Sweden ¦ 2* ¦ ¦ ¦ ¦ Switzerland ¦ 6 ¦ 11 ¦ ¦ ¦ United Kingdom ¦ 6 ¦ 9 ¦ ¦ ¦ China ¦ ¦ ¦ 5 ¦ *Limit specifically for NO2 from exhaust fumes. its are taken primarily from an international database ofparticipating countries (ILO 2003; Lu 1993). Contaminant limits are often ex- pressed in mg/m3, even in regions where I-P units are used. Most authorities do not currently distinguish DPM from other particulates; however, this may change. The ACGIH has added DPM measured as elemental carbon to its TLVs (ACGIH 2003). A 0.1 mg/m3 limit for elemental carbon in diesel environments has been established in Germany. Laws enacted by the Mine Safety and Health Administration are targeted toward limiting DPM in mining environments (MSHA 2001a, 2001b). These changes may fore- shadow action by OSHA. In this changing environment, designers must check local regulations in the time and place of construction for applicable limits. Contaminant Emission Rate Locomotive contaminant emissions have been measured primar- ily for environmental reasons, and data for some models have been published in the environmental literature (Table 12). These data are classified for different duty-cycles of operation and different throttle settings, and were obtained from controlled tests conducted under steady-state operation. Engine speed, engine power, fuel rate, and engine airflow are typically reported. Emissions are usually re- ported for carbon monoxide (CO), oxides of nitrogen (NOx), hydro- carbons, sulfur dioxide (SO2), and particulates. Manufacturers can provide this information for specific engine models and should be consulted for current and specific data for design projects. Note that passenger locomotives consume a greater amount of power when idling with head-end power (HEP) to serve passenger- related needs. A passenger train idle at HEP can produce five times the amount of NOx emissions as the same train idling with no HEP effects (Fritz 1994). Thus, this is an important distinction between passenger railway stations, where HEP is likely to be required, and repair facilities, where HEP is not likely to be needed. Available emissions data have been targeted toward outdoor pollution concerns, which imposes some limitations in application to indoor settings. Only recent tests document exhaust tempera- tures, a quantity useful to design engineers concerned with sprin- kler systems. Emissions data come from steady-state tests on engines whose operation has been allowed to stabilize for an hour or more, so a safety factor is suggested to allow for higher emis- sions related to cold start and transient operation. Also, the data include only a combined NOx emissions value. Field measure- ments in locomotive facilities found that about 13% (by mass) of ambient NOx could be attributed to NO2 (Musser and Tan 2004). This factor can be used estimate NO2 source emissions from avail- Inc. ASHRAE, 2019 user. single for Licensed | {}
f4356c29-6c53-4efe-9b0d-a8fe59fb0df7 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 16.32 2019 ASHRAE Handbook- - HVAC Applications (SI) Table 12 Sample Diesel Locomotive Engine Emission Dataa ¦ Throttle Position (Notch) ¦ Engine Speed, rpm ¦ Engine Power, kW ¦ Engine Airflow,b m3/s ¦ Fuel Rate, kg/h ¦ NO x g/min ¦ CO, g/min ¦ HC, g/min ¦ SO2, g/min ¦ Particulates, g/min ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Four-Stroke Cycle, With Head End Power (HEP) ¦ Four-Stroke Cycle, With Head End Power (HEP) ¦ Four-Stroke Cycle, With Head End Power (HEP) ¦ Four-Stroke Cycle, With Head End Power (HEP) ¦ Four-Stroke Cycle, With Head End Power (HEP) ¦ Four-Stroke Cycle, With Head End Power (HEP) ¦ Four-Stroke Cycle, With Head End Power (HEP) ¦ Four-Stroke Cycle, With Head End Power (HEP) ¦ Four-Stroke Cycle, With Head End Power (HEP) ¦ Four-Stroke Cycle, With Head End Power (HEP) ¦ ¦ 8, Freight ¦ 1050 ¦ 2437 ¦ 4.161 ¦ 500 ¦ 612 ¦ 45 ¦ 29 ¦ 3.8 ¦ 7.2 ¦ ¦ 7, HEP ¦ 900 ¦ 2066 ¦ 3.336 ¦ 421 ¦ 540 ¦ 95 ¦ 23 ¦ 3.2 ¦ 8.1 ¦ ¦ 6, HEP ¦ 900 ¦ 1681 ¦ 2.675 ¦ 346 ¦ 471 ¦ 87 ¦ 20 ¦ 2.7 ¦ 7.0 ¦ ¦ 5, HEP ¦ 900 ¦ 1325 ¦ 2.092 ¦ 276 ¦ 386 ¦ 76 ¦ 12 ¦ 2.1 ¦ 4.9 ¦ ¦ 4, HEP ¦ 900 ¦ 763 ¦ 1.263 ¦ 167 ¦ 253 ¦ 25 ¦ 9.1 ¦ 1.3 ¦ 3.9 ¦ ¦ 3, HEP ¦ 900 ¦ 532 ¦ 0.970 ¦ 121 ¦ 170 ¦ 18 ¦ 7.1 ¦ 0.93 ¦ 3.7 ¦ ¦ 2, HEP ¦ 900 ¦ 321 ¦ 0.782 ¦ 79 ¦ 109 ¦ 12 ¦ 6.6 ¦ 0.60 ¦ 4.1 ¦ ¦ 1, HEP ¦ 900 ¦ 240 ¦ 0.779 ¦ 65 ¦ 96 ¦ 12 ¦ 6.9 ¦ 0.50 ¦ 4.9 ¦ ¦ HEP idle ¦ 900 ¦ 138 ¦ 0.713 ¦ 37 ¦ 48 ¦ 15 ¦ 8.3 ¦ 0.28 ¦ 6.9 ¦ ¦ Standby ¦ 720 ¦ 382 ¦ 0.680 ¦ 86 ¦ 118 ¦ 14 ¦ 6.2 ¦ 0.65 ¦ 5.0 ¦ ¦ High idle ¦ 450 ¦ 25 ¦ 0.220 ¦ 10 ¦ 15 ¦ 3.7 ¦ 3.0 ¦ 0.08 ¦ 1.0 ¦ ¦ Low idle ¦ 370 ¦ 16 ¦ NAc ¦ 8 ¦ 8.6 ¦ 5.3 ¦ 2.7 ¦ 0.07 ¦ 0.78 ¦ ¦ Two-Stroke Cycle, No Head End Power (HEP) ¦ Two-Stroke Cycle, No Head End Power (HEP) ¦ Two-Stroke Cycle, No Head End Power (HEP) ¦ Two-Stroke Cycle, No Head End Power (HEP) ¦ Two-Stroke Cycle, No Head End Power (HEP) ¦ Two-Stroke Cycle, No Head End Power (HEP) ¦ Two-Stroke Cycle, No Head End Power (HEP) ¦ Two-Stroke Cycle, No Head End Power (HEP) ¦ Two-Stroke Cycle, No Head End Power (HEP) ¦ Two-Stroke Cycle, No Head End Power (HEP) ¦ ¦ 8 ¦ 903 ¦ 2394 ¦ 4.2 ¦ 481 ¦ 647 ¦ 61 ¦ 15 ¦ 3.7 ¦ 11 ¦ ¦ 7 ¦ 821 ¦ 1894 ¦ 3.4 ¦ 378 ¦ 424 ¦ 31 ¦ 9.3 ¦ 2.9 ¦ 7.3 ¦ ¦ 6 ¦ 726 ¦ 1268 ¦ 2.5 ¦ 259 ¦ 290 ¦ 11 ¦ 6.4 ¦ 2.0 ¦ 4.9 ¦ ¦ 5 ¦ 647 ¦ 1037 ¦ 2.2 ¦ 218 ¦ 248 ¦ 10 ¦ 6.0 ¦ 1.7 ¦ 4.4 ¦ ¦ 4 ¦ 563 ¦ 790 ¦ 1.9 ¦ 167 ¦ 213 ¦ 4.6 ¦ 4.8 ¦ 1.3 ¦ 3.2 ¦ ¦ 3 ¦ 489 ¦ 532 ¦ 1.6 ¦ 115 ¦ 178 ¦ 3.2 ¦ 3.9 ¦ 0.88 ¦ 2.3 ¦ ¦ 2 ¦ 337 ¦ 276 ¦ 1.0 ¦ 64 ¦ 100 ¦ 3.5 ¦ 2.5 ¦ 0.50 ¦ 0.90 ¦ ¦ 1 ¦ 337 ¦ 154 ¦ 1.1 ¦ 41 ¦ 58 ¦ 2.6 ¦ 1.9 ¦ 0.32 ¦ 0.50 ¦ ¦ High idle ¦ 339 ¦ 10 ¦ 1.1 ¦ 15 ¦ 19 ¦ 1.3 ¦ 1.6 ¦ 0.12 ¦ 0.40 ¦ ¦ Low idle ¦ 201 ¦ 7 ¦ 0.62 ¦ 6 ¦ 9.9 ¦ 0.60 ¦ 0.58 ¦ 0.05 ¦ 0.13 ¦ ¦ Auxiliary Engine/Alternator for Head End Power (HEP) ¦ Auxiliary Engine/Alternator for Head End Power (HEP) ¦ Auxiliary Engine/Alternator for Head End Power (HEP) ¦ Auxiliary Engine/Alternator for Head End Power (HEP) ¦ Auxiliary Engine/Alternator for Head End Power (HEP) ¦ Auxiliary Engine/Alternator for Head End Power (HEP) ¦ Auxiliary Engine/Alternator for Head End Power (HEP) ¦ Auxiliary Engine/Alternator for Head End Power (HEP) ¦ Auxiliary Engine/Alternator for Head End Power (HEP) ¦ Auxiliary Engine/Alternator for Head End Power (HEP) ¦ ¦ N/A ¦ 1800 ¦ 521 ¦ 0.91 ¦ 125 ¦ 127 ¦ 55 ¦ 5.3 ¦ 1.0 ¦ 2.8 ¦ ¦ N/A ¦ 1800 ¦ 422 ¦ 1.0 ¦ 103 ¦ 129 ¦ 8.2 ¦ 5.9 ¦ 0.78 ¦ NAc ¦ ¦ N/A ¦ 1800 ¦ 327 ¦ 0.95 ¦ 81 ¦ 97 ¦ 4.0 ¦ 5.1 ¦ 0.62 ¦ 2.0 ¦ ¦ N/A ¦ 1800 ¦ 281 ¦ 0.90 ¦ 71 ¦ 78 ¦ 3.0 ¦ 4.6 ¦ 0.55 ¦ 1.9 ¦ ¦ N/A ¦ 1800 ¦ 227 ¦ 0.85 ¦ 61 ¦ 63 ¦ 3.0 ¦ 4.3 ¦ 0.47 ¦ 1.7 ¦ ¦ N/A ¦ 1800 ¦ 177 ¦ 0.81 ¦ 52 ¦ 49 ¦ 3.0 ¦ 4.3 ¦ 0.40 ¦ 1.5 ¦ ¦ N/A ¦ 1800 ¦ 129 ¦ 0.77 ¦ 43 ¦ 36 ¦ 3.1 ¦ 4.1 ¦ 0.33 ¦ 1.3 ¦ ¦ N/A ¦ 1800 ¦ 23 ¦ 0.70 ¦ 25 ¦ 17 ¦ 3.5 ¦ 4.6 ¦ 0.20 ¦ 1.2 ¦ ¦ aData from Southwest Research Institute (SwRI 1992). ¦ aData from Southwest Research Institute (SwRI 1992). ¦ aData from Southwest Research Institute (SwRI 1992). ¦ aData from Southwest Research Institute (SwRI 1992). ¦ bIntake, corrected to standard air density 1.203 kg/m3. ¦ bIntake, corrected to standard air density 1.203 kg/m3. ¦ bIntake, corrected to standard air density 1.203 kg/m3. ¦ bIntake, corrected to standard air density 1.203 kg/m3. ¦ bIntake, corrected to standard air density 1.203 kg/m3. ¦ °Data not available. ¦ able data. The applicability of these data to design applications is supported by comparisons of CFD models based on published emissions data and field measurements taken in repair shops that showed reasonable agreement between the measured and predicted values (Musser and Tan 2004). Locomotive Operation Designers need to anticipate locomotive operation during the design phase, particularly when estimating source strength based on published locomotive emissions data. Some important param- eters include the number of operating locomotives and the loca- tion, duration, and throttle position at which they operate. The number of locomotives likely to be operating can be estimated based on shop or station schedules. Although it is important to remember that a locomotive could idle at any location inside a facility, there are often practical cues to identify the most common or likely locations. These include platforms, facility layout, loca- tion of equipment for servicing toilets, fuel stations, or other ser- vice equipment. In small shops, the layout may create one or two convenient positions in which locomotives are very likely to be parked. Other operating parameters may be more difficult to estimate, particularly in shops. Field observations for ASHRAE research project RP-1191 recorded locomotive operation in several shops varying from a few minutes to an hour in duration, usually at idle and low throttle settings (Musser and Tan 2004). Operation was influenced by shop rules, practices, and conventions, which are valuable to consider during the design phase. The cooperation and involvement of shop employees in the design stage can help inte- grate these practices so that the design conforms to the needs of the facility, rather than the other way around. Design Methods General Exhaust Systems. A contaminant-based procedure using a simplified equation developed with computational fluid dynamics can be used to design general exhaust systems using the steps below. The simplified equation was developed to flexibly adapt to changes in contaminant limits. Figures 23 and 24 show schematic drawings of such a system. Step 1: Verify that design parameters to be used in the simplified equation fall within the ranges for which the equation is valid. · Ceiling height Z must be 6 to 13.7 m. · Fan spacing X must be 6 to 18 m. · Exhaust fan flow 0 must provide 5 to 12 air changes per hour (ach). Step 2: Verify that other facility characteristics show reasonable agreement with the assumptions of the parametric study: Inc. ASHRAE, 2019 user. single for Licensed | {}
1e75306d-a34c-4ed3-94c6-6d45f2904d23 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Enclosed Vehicular Facilities 16.33 ![image](/image/placeholder) L I CEILING EXHAUST INTAKE Q C, T.F Z LOCOMOTIVE Y Fig. 23 Section View of Locomotive and General Exhaust System · Fan dimensions L: Exhaust fan or duct dimensions are 1.5 by 1.5 m. · Fan placement: Exhaust fans or duct openings are centered above each track. · Locomotive exhaust temperature T: 177°C. · Locomotive exhaust flow rate F: 1 m3/s. · Radiator fans: For many locomotive models, radiator fans do not operate when the locomotive is idling, and no radiator fan flow was modeled in this study. If radiator fans will be operating, they may alter the indoor airflow patterns. · Operating time: The equation is based on steady state conditions, so it is not necessary to assume a maximum operating time. · Concurrent operation: The equation allows for concurrent opera- tion on different tracks. However, it does not include concurrent operation of more than one locomotive on the same track. · Track-to-track spacing Y: 7.6 m. · Ambient temperature: 32°C. This was selected because warmer ambient temperatures tend to reduce the upward buoyancy of warm exhaust gases. Step 3: Obtain emissions data for critical contaminants and deter- mine the design indoor concentration limit for the critical con- taminant. · Emissions data for some locomotive models are published in the environmental literature, and data for specific locomotives can be obtained from the manufacturer. The emissions rate for a given locomotive model depends on throttle position and whether head- end power is used. · Acceptable indoor concentration limits can be determined from legal requirements at the location and time of construction. The designer may also wish to consider recommended limits from or- ganizations such as ACGIH. To allow a safety margin, a designer might choose a contaminant limit that is lower than the published legal limit. Contaminant limits are often expressed in mg/m3, even in regions where I-P units are used. A contaminant limit in ppm(v) can be converted to mg/m3 for use in the simplified equation as follows (ASHRAE Standard 62.1): ![image](/image/placeholder) X EXHAUST Q CEILING INTAKE L Z C, T,F LOCOMOTIVE Fig. 24 Elevation View of Locomotive and General Exhaust System Table 13 Constants for Equation (20) ¦ Constant ¦ No Platform ¦ With 1.7 m Platform ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ a ¦ 20.0 ¦ 22.5 ¦ ¦ b ¦ -0.551 ¦ -0.773 ¦ ¦ C ¦ -3.32 ¦ -2.09 ¦ ¦ d ¦ -0.106 ¦ -0.109 ¦ ¦ e ¦ -0.308 ¦ -0.346 ¦ ¦ f ¦ 0.0119 ¦ 0.0159 ¦ ¦ g ¦ 0.235 ¦ 0.236 ¦ ¦ h ¦ 0.0792 ¦ 0.0407 ¦ ¦ i ¦ 0.00191 ¦ 0.00190 ¦ ¦ ¦ -0.00505 ¦ -0.00499 ¦ Molecular mass ppm(v) = mg/m3 24.45 (19) Step 4: Select a fan flow rate and calculate the maximum concen- tration to which occupants would be exposed using Equation (20). Table 13 gives values for constants a toj whether occupants will be standing on the floor or a 1.2 m high platform. C a + bQ+ cP+ dX+ eZ C occ = 10 3 emissions (20) + fQZ + gPX + hPZ + iXZ +jPXZ where Cocc = maximum time-averaged concentration of critical contaminant to which occupants could be exposed, mg/m3 Cemissions = concentration of critical contaminant in exhaust emissions, mg/ m3 a to i = constants found in Table 13 0 = total exhaust fan flow rate required, ach; must be between 5 and 12 ach Z = ceiling height; must be 6 to 13.7 m X = fan spacing; must be 6 to 18 m P = locomotive offset position, dimensionless; P = 0 under fan and P = 1 between fans. Other values for P can be calculated based on the distance of locomotive stack from the nearest exhaust fan d and fan spacing X: d P = 2 X (21) Step 5: Compare Cocc obtained in step 4 with the concentration limit < Climit, the selected flow rate C limit determined in step 3. If C occ is adequate. If Cocc limit repeat step 4 with a higher flow rate > C until a concentration less than the limit is obtained. Inc. ASHRAE, 2019 user. single for Licensed | {}
0ff21c4d-3b12-408d-a920-4da9dcccae5e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 16.34 2019 ASHRAE Handbook- -HVAC Applications (SI) Step 6: Verify that the result is between 5 and 12 ach. · Ifthe flow rate obtained is between 5 and 12 ach, this is the system size. · If the flow rate obtained is less than 5 ach, the designer could · Design for 5 ach. · Perform a more detailed analysis to verify that less than 5 ach will provide acceptable contaminant control. For rates less than the 0.0075 m3/(s .m2) recommended by ASHRAE Stan- dard 62.1 or in the case of unusual sources, the presence of contaminants other than those from diesel exhaust in the space (e.g., liquid fuel) should also be considered. · Ifthe flow rate obtained is greater than 12 ach, the designer could · Adjust the other parameters to attempt to reduce the air change requirement. · Perform a more detailed analysis to verify the necessary air flow requirement. Example 2. Perform design calculations for a passenger locomotive repair shop. Step 1: Verify design parameters. The planned facility ceiling height is 9.1 m, which falls within the 6 to 13.7 m range for which the simplified equation is valid. The planned fan spacing is 15.2 m, which also falls within the required range of 6 to 18 m. Step 2: Verify other facility characteristics. · Exhaust fans: Exhaust openings with an area of approximately 2.3 m2 will be used, and fans will be centered above each track. · Locomotive: Operating locomotives are usually high idle or lower. When moving in, they will not exceed throttle position 1. Information obtained from the manufacturer of the locomotive most commonly ser- viced in this facility indicates an exhaust flow rate of 1.085 m3/s, an exhaust temperature of 190°C, and NOx generation of 3,475 kg/h. Radiator fans will not operate in the high idle position for this locomo- tive. · Track-to-track spacing is 8.3 m. Locomotives may operate concur- rently on adjacent tracks, but concurrent operation on the same track is not planned. · These characteristics are reasonably similar to the assumptions upon which the simplified equation is based. Step 3: Obtain emissions data and determine the design limit. · The critical contaminant for this design is nitrogen dioxide (NO2). Emission data from the manufacturer state that the NOx generation rate is 3.475 kg/h. Field measurements conducted for ASHRAE research project RP-1191 (Musser and Tan 2004) showed that ambient NO2 concentrations were about 13% of ambient NOx levels. Therefore, the NO2 generation rate is estimated to be 13% of the total, or 452 g/h. For an exhaust flow rate of 1.085 m3/s, the concentration of NO2 in the exhaust is 116 mg/m3. 452 g/h 1 Cemissions 3600 s/h (1000 mg/g) 1.085 m /s = 116 mg/m3 · OSHA currently requires a 5 ppm(v) ceiling for NO2, but NIOSH and other sources recommend a 1 ppm(v) 15 min short-term exposure limit (STEL). The designer decides to select the lower 1 ppm(v) limit and to design for 0.5 ppm(v) (i.e., 0.94 mg/m3) to allow for a safety factor for variations in emissions or operation. 0.5 ppm(v) 46 = 0.94 mg/m3 24.45 Step 4: Select a flow rate and solve for the contaminant concentration. Ceiling height is 9.1 m, and fan spacing is 15.2 m. Based on the place- ment of services in the shop, expect that the stack of an operating loco- motive will be at most 3.8 m from the nearest exhaust fan, so P = 0.5. The shop does have a 1.2 m high platform where workers may stand, ![image](/image/placeholder) W EXHAUST CEILING HOOD Q : I H : Z C, T, F LOCOMOTIVE Y Fig. 25 Section View of Locomotive and Exhaust Hood System ![image](/image/placeholder) X CEILING EXHAUST HOODS Q Q L C, T,F Z LOCOMOTIVE Fig. 26 Elevation View of Locomotive and Exhaust Hood System so Equation (20) is solved using a platform. First, try fans that provide 5 ach: 3 3 0.773Q - 2.09P- 0.109X C = 10 116 mg/m 22.5 occ - 0.346Z + 0.0159QZ + 0.236PX + 0.0407PZ 3 + 0.00190XZ - 0.00499PXZ) = 1.13 mg/m · Iterate between steps 5 and 4. With 5 ach, Cocc = 1.13 mg/m3. This is greater than the desired limit of 0.94 mg/m3. If the fan flow rate is increased to provide 10.5 ach, Cocc mg/m3. This decreases to 0.94 meets the design criterion. Step 5: Verify that the fan flow rate is between 5 and 12 ach. No further analysis is needed. Exhaust Hood Design. A similar equation was also developed for design ofexhaust hood systems. However, results from the parametric set of computational fluid dynamics simulations performed to de- velop the equation were shown to be highly specific to the situation and geometry shown in Figures 25 and 26. Therefore, these equations should not be used unless the given assumptions are exactly matched. For further information on hood design, see ACGIH (1998). Inc. ASHRAE, 2019 user. single for Licensed | {}
65c5aa0c-ccdb-4a53-9bb9-45c4f92a60a6 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Enclosed Vehicular Facilities 16.35 Table 14 Constants for Equation (22) Step 1: Verify that the design parameters to be used in the simplified equation fall within the ranges for which it is valid. · Hood mounting height H must be 0.9 to 2.4 m. · Hood length L must be 1.5 to 3.4 m. · Exhaust fan flow 0 must provide 5 to 12 ach. Step 2: Verify that other facility characteristics agree with the assump- tions of the parametric study. These assumptions are as follows: · Hood width W: 1.5 m. · Hood placement: Hoods are centered above each track at 18.3 m intervals. · Hood operation: All hoods switched on together. · Ceiling height Z: 7.6 m. · Locomotive exhaust temperature T: 177°C. · Locomotive exhaust flow rate F: 0.944 m3/s. · Radiator fans: Radiator fans do not operate. · Operating time: The results of the study are based on steady-state conditions, so it is not necessary to assume a maximum operating time. · Concurrent operation: The study allows for concurrent operation on different tracks, but not for concurrent operation of more than one locomotive on the same track. · Track-to-track spacing Y: 7.6 m. · Ambient temperature: 32°C. Step 3: Obtain emissions data for critical contaminants and deter- mine the design indoor concentration limit for the critical contami- nant. This can be done using the procedure described for general exhaust systems. Step 4: Select a fan flow rate and calculate the maximum concen- tration to which occupants would be exposed using Equation (22). Table 14 gives values for constants a to I for occupants standing on the floor or on a 1.2 m high platform. C a + bQ + cP + dH + eL +fQP C = 10 3 occ emissions + gQH + hQL + iPH +jHL + kQPH + IQHL where C, occ time-averaged concentration of critical = maximum contaminant to which occupants could be exposed, mg/m3 Cemissions = concentration of critical contaminant in exhaust emissions, mg/m3 a to I = constants in Table 14 0 = total exhaust fan flow rate required, ach; must be 5 to 12 ach H = hood mounting height; must be 0.9 to 2.4 m L = fan spacing; must be 1.5 to 3.4 m P = locomotive offset position; dimensionless; P = 0 centered under hood and P = 1 under edge of hood. Other values for P can be calculated based on distance d of locomotive stack from center of nearest exhaust hood and hood length L: 2d P = L Step 5: Compare Cocc obtained in step 4 with the concentration limit determined in step 3. If C occ Climin rate is Climit the selected flow < adequate. If Cocc limit' repeat step 4 with a higher flow rate until > C a concentration less than the limit is obtained. Step 6: Verify that the result is between 5 and 12 ach. · Ifthe flow rate obtained is between 5 and 12 ach, this is the system size. · Ifthe flow rate obtained is less than 5 ach, the designer could · Design for 5 ach. ¦ Constant ¦ No Platform ¦ With 1.2 m Platform ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ a ¦ 0.717 ¦ 2.19 ¦ ¦ b ¦ -0.160 ¦ -0.401 ¦ ¦ c ¦ 0.900 ¦ 2.18 ¦ ¦ d ¦ -0.168 ¦ -0.283 ¦ ¦ e ¦ -0.0508 ¦ -0.275 ¦ ¦ f ¦ -0.129 ¦ -0.332 ¦ ¦ g ¦ 0.0381 ¦ 0.0684 ¦ ¦ h ¦ 0.0245 ¦ 0.0846 ¦ ¦ i ¦ -0.174 ¦ -0.351 ¦ ¦ j ¦ 0.0294 ¦ 0.0575 ¦ ¦ k ¦ 0.0290 ¦ 0.0560 ¦ ¦ / ¦ -0.00588 ¦ -0.0134 ¦ · Perform a more detailed analysis to verify that less than 5 ach will provide acceptable contaminant control. For rates less than the 0.0075 m3/(s·m2) recommended by ASHRAE Standard 62.1 or in the case of unusual sources, the presence of contam- inants other than those from diesel exhaust in the space should also be considered (e.g., liquid fuel). · Ifthe flow rate obtained is greater than 12 ach, the designer could · Adjust other parameters to attempt to reduce the air change re- quirement. · Perform a more detailed analysis to verify the necessary airflow requirement. 8. EQUIPMENT (22) An enclosed vehicular facility's ability to function depends mostly on the effectiveness and reliability of its ventilation system, which must operate effectively under the most adverse environmental, climatic, and vehicle traffic conditions. A tunnel ventilation system should also have more than one dependable power source, to prevent interruption of service. Fans Fan manufacturers should be prequalified and should be respon- sible under one contract for furnishing and installing the fans, bear- ings, drives (including any variable-speed components), motors, vibration devices, sound attenuators, discharge/inlet dampers, actu- ators, and limit switches. Other ventilation-related equipment, such as ductwork, may be provided under a subcontract. The primary concerns in selecting the type, size, and number of fans include the total theoretical ventilation airflow capacity required and a reasonable comfort margin. Fan selection is also influenced by how reserve ventilation capacity is provided either when a fan is inop- erative, or during maintenance or repair of either the equipment or the power supply. (23) Selection (i.e., number and size) of fans needed to meet normal, emergency, and reserve ventilation capacity requirements of the system is based on the principle of parallel fan operation. Actual air- flow capacities can be determined by plotting fan performance and system curves on the same pressure-volume diagram. Fans selected for parallel operation may be required to operate in a particular region of their performance curves, so that airflow capacity is not transferred back and forth between fans. This is done by selecting a fan size and speed such that the duty-point total pres- sure, no matter how many fans are operating, falls below the mini- mum total pressure characterized by the bottom of the stall dip or unstable performance range. This may require consultation with the fan manufacturer, because this information is not typically available from published fan performance data. Fans operating in parallel should be of equal size and have identical performance curves. If airflow is regulated by speed control, all fans should operate at the Inc. ASHRAE, 2019 user. single for Licensed | {}
847569cc-f12c-486e-a3f8-05ff60cfb349 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 16.36 Inc. ASHRAE, 2019 user. single for Licensed 2019 ASHRAE Handbook-HVAC Applications (SI) same speed. If airflow is regulated by dampers or by inlet vane controls, all dampers or inlet vanes should be set at the same angle. For axial-flow fans, blades on all fans should be set at the same pitch or stagger angle. Jet fans can be used for longitudinal ventilation to provide a pos- itive means of smoke and air temperature management in tunnels. This concept was proven as part of the Memorial Tunnel Fire Ven- tilation Test Program (MHD/FHWA 1995). Although jet fans de- liver relatively small air quantities at high velocity, the momentum produced is transferred to the entire tunnel, inducing airflow in the desired direction. Jet fans are normally rated in terms of thrust rather than airflow and pressure, and can be either unidirectional or reversible. Number and Size of Fans. The number and size of fans should be selected by comparing several fan arrangements based on the fea- sibility, efficiency, and overall economy ofthe arrangement, and the duty required. Factors that should be studied include (1) annual power cost for operation, (2) annual capital cost of equipment (usu- ally capitalized over an assumed equipment life of30 years for mass transit tunnel fans, or 50 years for highway and railroad tunnel fans), and (3) annual capital cost of the structure required to house the equipment (usually capitalized over an arbitrary structure life of 50 years). Two views are widely held regarding the proper number and size of fans: the first advocates a few high-capacity fans and the second prefers numerous low-capacity fans. In most cases, a compromise arrangement produces the greatest efficiency. The number and size of the fans should be selected to build sufficient flexibility into the system to meet the varying ventilation demands created by daily and seasonal traffic fluctuations and emergency conditions. Consider- ation should be given to satisfying emergency conditions during fan outages for maintenance or unplanned downtime. In general, when selecting the number of fans, several issues may need to be considered, ranging from redundancy and space alloca- tion, to design issues such as determining the number of control boxes, dampers, silencers, and similar equipment. In tunnel ventila- tion, the required fan airflow capacity is typically very large. If one fan is installed, the fan must be large, and this design provides zero redundancy in case of failure or maintenance. However, if many fans are installed, more space is required than for a single fan. Designs need to balance space allocation with an acceptable level of redundancy. Jet fan sizing is usually limited by space available for installation in the tunnel. Typically mounted on the tunnel ceiling (above the vehicle traffic lanes) or on the tunnel walls (outside the vehicle traf- fic lanes), jet fans are sometimes placed in niches to minimize the height or width of the entire tunnel boundary. However, niches must be adequately sized to avoid reducing the thrust of the fans. A typ- ical jet fan niche arrangement is provided in Figure 27. For longitudinal ventilation using jet fans, the required number of fans is defined (once fan size and tunnel airflow requirements have been determined) by the total thrust required to overcome the tunnel resistance (pressure loss), divided by the individual jet fan ![image](/image/placeholder) SUPPORT SILENCER JET FAN 15.0° 8 。 0 2.5D 2D D 2D 2.5D Fig. 27 Typical Jet Fan Arrangement in Niche thrust, which is a function of the mean air velocity in the tunnel. Jet fans installed longitudinally should be at least 7 to 10 tunnel hydraulic diameters apart so that the jet velocity does not affect the performance of downstream fans. Jet fans installed side by side should be at least two fan diameters (centerline to centerline) apart. Type of Fan. Normally, ventilating an enclosed vehicular facility requires a large volume of air at relatively low pressure. Some fans have low efficiencies under these conditions, so the choice of a suitable fan type is often limited to a centrifugal, vaneax- ial, or jet fan. Special Considerations. Special attention must be given to a fan installed where airflow and pressure transients are caused by vehicle passage. Ifthe transient tends to increase airflow through the fan (i.e., positive flow in front of the vehicle toward an exhaust fan, or negative flow behind the vehicle toward a supply fan), blade load- ing must not become high enough to produce long-term fatigue fail- ures. If the disturbance tends to decrease airflow through the fan (i.e., negative flow behind the vehicle toward an exhaust fan or positive flow in front of the vehicle toward a supply fan), the fan performance characteristic must have adequate comfort margins to prevent an aerodynamic stall. If the pressure pulses are large relative to the fan 's total pressure capability, at either full or planned reduced-speed operation, it can result in an overblown condition. Motors, power, and mechanical systems should be designed for overblown operation if the motor needs to operate under these conditions. The ability to rapidly reverse the rotation of a tunnel ventilation fan is important during an emergency. This requirement must be considered in selection and design of the fan and drive system. Fan Design and Operation. Fans and fan components (e.g., blade-positioning mechanisms, drives, bearings, motors, controls, etc.) that must operate in the exhaust airstream during a fire or smoke emergency should be capable of operating at maximum speed under the temperatures specified by the following standards or calculation procedures: · NFPA Standard 130 for mass transit and passenger rail tunnels · NFPA Standard 502 for road tunnels · Computer simulations or other calculations for the maximum expected temperatures, in railroad tunnels and other enclosed vehicular facilities Fans and dampers that are operated infrequently or for emer- gency service only should be activated and tested at least once every month to ensure that all rotating elements are in good con- dition and properly lubricated. The period of activity should be long enough to achieve stabilized temperatures in fan bearings and motor windings. Inlet boxes can be used to protect centrifugal fan bearings and drives from high temperatures, corrosive gases, and particulate matter in exhaust air during emergency operating mode. This arrangement requires special attention to fan shaft design because of overhung drive loads (see the section on Fan Shafts). Reversible axial flow fans should be able to be rapidly reversed from the maximum design speed in one direction to the maximum design speed in the opposite direction in less than 60 s. Fan design should include the effects of temperature changes associated with reversing airflow direction. All components of reversible fans should be designed for a minimum of 5000 cycles without damage. Housings for variable-pitch axial flow fans should be furnished with instruments to measure airflow in both directions. Capped con- nections should be provided for measuring the pressure developed across the fan. The fan should also be protected from operating in a stall region. To minimize blade failure in axial flow fans, the following pre- cautions should be taken: | {}
a214bf2a-8172-4d7f-9140-2cb7a2973843 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Enclosed Vehicular Facilities 16.37 · Blades should be secured to the hub by positive locking devices. · The fan inlet (and discharge, if reversible) should be protected against entry of foreign objects that could damage the rotating assembly. · The natural frequency (static and rotating) ofthe blade and the max- imum stress on the blade surface (for all operating points on the fan characteristic curve) should be measured during factory testing. · For mass transit and rail systems, fans subjected to airflow and air pressure reversals caused by train passage should be designed (and tested, for verification) to withstand 4 000 000 cycles of air- flow reversals. When a fan includes a variable-frequency drive (VFD), factory testing with a production version of the VFD should be done to ensure adequate operation and compatibility with the fan system. Fans that are run by VFDs should have an installed static blade with a first bending natural frequency at least four times higher than the maximum intended running speed (e.g., an 1180 rpm fan's first bending frequency should be at least 79 Hz). If installed blades have a first bending frequency below this value, the VFD should be programmed to avoid speeds that are potentially problematic. Jet fan blades should be strong enough to withstand the air tem- peratures created by a fire. Design calculations for jet fans should consider that the fire might destroy the fan(s) at the fire location, and that the jet fans downstream of the fire will operate under high tem- peratures and reduced thrust. Fan Shafts. Fan shafts should be designed so that the maximum deflection of assembled fan components, including forces associ- ated with the fan drive, does not exceed 0.42 mm per metre of shaft length between centers of the bearings. For centrifugal fans where the shaft overhangs the bearing, the maximum deflection at the cen- terline of the fan drive pulley should not exceed 0.42 mm per metre of shaft length between the center of the bearing and the center of the fan drive pulley. Good practice suggests that the fundamental bending mode fre- quency of the assembled shaft, wheel, or rotor be more than 50% higher than the highest fan speed. The first resonant speed of all rotational components should be at least 125% above the maximum speed. The fan assembly should be designed to withstand, for at least 3 min, all stresses and loads from an overspeed test at 110% of maximum design fan speed. Bearings. Fan and motor bearings should have a minimum equivalent L10 rated life of 10 000 h, as defined by the American Bearing Manufacturers Association (ANSI/ABMA 2000). Special attention must be given to belt-driven fans, because improper ten- sioning or overtensioning ofbelts can drastically reduce the bearing life, belt life, and possibly shaft life. For axial-flow fans and jet fans, each fan motor bearing and fan bearing should have a monitoring system that senses individual bear- ing vibrations and temperatures, and provides a warning alarm if either rises above the manufacturer-specified range. Jet fan motors should have an industrial protection class (IP rating) of 55 or higher, which has bearings with washdown-rated seals. Because of their low speed (generally less than 450 rpm), cen- trifugal fans are not always provided with bearing vibration sen- sors, but they do require temperature sensors with warning alarm and automatic fan shutdown. Bearing pedestals for centrifugal fans should provide rigid support for the bearings with negligible imped- iments to airflow. Static and dynamic loading of the shaft and the impeller, and the maximum force from tension in the belts, should be considered. Corrosion-Resistant Materials. Choosing a particular material or coating to protect a ventilation fan from corrosive gas is a matter of economics. Selection of the material and/or coating should be based on the installation environment, fan duty, and an expected service life of 50 years. Sound. For ventilation fan sound attenuator design, construction documents should specify the following: · Speed and direction of airflow, and number of operating fans · Maximum dBA rating or NC curve(s) acceptable under installed conditions, and locations of fan supply inlet and exhaust outlet where these requirements apply · OSHA or local requirements for jet-fan-generated noise limits, which may require silencers of 1 to 2 fan diameters in length · The dBA rating required at certain specific locations, such as intake louvers, discharge louvers, or discharge stacks, may not exceed OSHA or local requirements · That the fan manufacturer must furnish and install the acoustical treatment needed to bring the sound level down to an acceptable value if measured sound values exceed the specified maximum values at the defined boundaries of the fan manufacturer's scope of supply · NFPA-recommended maximum noise levels for emergency fan operations Dampers Dampers play a major role in overall tunnel safety and the suc- cessful operation of a tunnel ventilation system. Dampers regulate airflow into and out of the tunnel, through either natural or forced ventilation, to maintain acceptable temperatures. Dampers also relieve pressure: opening and closing dampers allows tunnel air to be driven out of ventilation shafts located in front of moving vehi- cles, and for fresh air to be drawn into tunnels by ventilation shafts located behind moving vehicles. Dampers are also used with fans to dilute or remove carbon monoxide (CO), flammable gases, or other toxic fumes from tunnels. However, the most important function of dampers is to direct ventilation air and smoke flow during a fire emergency. In this function, fans and dampers operate in conjunc- tion to exhaust smoke and control its flow in the tunnel in support of passenger evacuations and firefighter ingress. Damper Design. Tunnel ventilation damper design requires a thorough understanding of design criteria, installation methods, envi- ronmental surroundings, equipment life expectancy, maintenance re- quirements, and operating system. Damper construction varies, but the general construction is based on the following design criteria: · Maximum fan operating pressure · Normal and rogue tunnel air pressures · Maximum air temperature · Maximum air velocity · Corrosion protection · Maintainability and life expectancy of equipment · Maximum damper module size · Maximum air leakage Fan Pressure. The maximum operating pressure that the damper will withstand during normal or emergency ventilation operations is typically the maximum pressure that the fan can generate at shutoff. This air pressure is generally 1.0 to 12.5 kPa. Normal and Rogue Tunnel Pressures. Some dampers in the track area of a train tunnel see much higher positive- and negative- pressure pulses than the maximum pressure generated by the fan. These high-pressure pulses are caused by the piston action of trains moving through the tunnel. A closed damper is subjected to positive pressures as trains approach, and to negative pressures as trains pass. This pressure reversal subjects damper blades and related components to reverse bending loads that must be considered to pre- vent premature fatigue failures. The magnitude of the pulsating pressure depends on factors such as maximum train speed, unidirec- tional or bidirectional traffic, tunnel length, blockage ratio, clear- ance between train and tunnel walls, and amount of air pushed through the dampers. Inc. ASHRAE, 2019 user. single for Licensed | {}
c9d70ce6-7019-417f-b787-f16eeac0a1a3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 16.38 2019 ASHRAE Handbook-HVAC Applications (SI) Pulsating pressure is part of normal tunnel operation. However, a rogue train condition (e.g., a train operating at high speed during an emergency or a runaway train) could occur once or twice during the lifetime of a tunnel ventilation system. Dampers must be designed for both day-to-day fatigue and for maximum train-speed conditions. Design specifications should require that the damper and its components meet reverse bending load criteria for 1 to 6 million reverse bending cycles for normal, day-to-day train operations. This number equates to a train passing a damper once every 5 to 20 min for 30 to 50 years. The number of cycles can be adjusted for each application. In addition, the specifying engineer should indicate the pressure that could result from a (once or twice in a lifetime) rogue train condition. Typically, actuators for tunnel dampers must be selected to operate against the maximum fan pressure. Because reversing pres- sures only occur briefly, and because normal train operations cease during an emergency, actuators are not expected to operate under either reverse pressure or rogue train conditions. Temperature. The maximum temperature can vary for each tun- nel project; some specifying engineers use the temperature limits recommended by NFPA. Typical equipment specifications state that dampers, actuators, and accessories should meet the operational requirements of the emergency ventilation fan system described in NFPA Standard 130: "Emergency ventilation fans, their motors, and all related components exposed to the exhaust airflow shall be designed to operate in an ambient atmosphere of 250°C for a minimum of 1 h with actual values to be determined by design anal- ysis. In no case shall the operating temperatures be less than 150°C. " Some tunnel design engineers have specified higher air tempera- ture criteria based on additional design considerations. A few road tunnels have been designed for the possibility of two tanker trucks carrying flammable liquids exploding from an accident in the tunnel, which would subject tunnel dampers to very high temperatures. Dampers for projects of this type, or other projects with special con- siderations, have been designed for maximum temperatures up to 425°C. The specifying engineer must evaluate design conditions for each project and determine what the maximum temperature could be. Dampers, and especially damper actuators, must be specially constructed to operate reliably in high-temperature conditions for extended periods. It is important to verify that the proposed equip- ment can provide this required safety function. Because standard testing procedures have not been developed, a custom high- temperature test of a sample damper and actuator should be con- sidered for inclusion in the equipment specifications. Air Velocity. The maximum air velocity for a tunnel damper design is determined from the maximum airflow expected through the damper during any operating condition. Maximum airflow could be generated from more than one fan, depending on the sys- tem design. Actuators for tunnel dampers are typically selected to operate against the maximum airflow that dampers will be exposed to in a worst-case scenario. Thus, the maximum airflow must be specified. It is important that the engineer understands the effect of damper free area on expected airflow and pressure loss. Air velocity through a damper can vary significantly depending on damper con- struction and the installation configuration used. A multiple-panel damper assembly usually has less free area than a single panel damper because of the additional blockage caused by its vertical and/or horizontal mullions. A multiple-panel damper assembly with 60 to 70% free area can have two to four times the pressure loss of a single-panel damper with 80% free area. There- fore, airflow through the multiple-panel damper assembly can be sig- nificantly lower than that through a comparable single-panel damper. The configuration of the damper installation can also affect free area, airflow, and pressure loss. For example, a damper can either be mounted to the face of an opening or in the opening itself. The damper mounted in the opening has a smaller free area because of the additional blockage of the damper frame, resulting in lower air- flow and higher pressure loss. Damper performance also depends on where the damper is mounted (e.g., in a chamber, at one or the other end of a duct). AMCA Standard 500-D has more information on damper mounting configurations. Corrosion Protection. Construction materials for tunnel projects vary considerably; their selection is usually determined based on one or more of the following reasons: · Initial project cost · Environmental conditions · Life expectancy of the equipment · Success or failure of previous materials used on similar projects · Engineer's knowledge of and/or experience with the materials required to provide corrosion protection · Design criteria (e.g., tunnel air pressure, temperature, velocity) The corrosion resistance of a damper should be determined by the environment in which it will operate. A damper installation near a saltwater or heavy industrial area may need superior corrosion protection compared to one in a rural, non-industrialized city. Underground or indoor dampers may need less corrosion protec- tion. However, many underground dampers are also exposed to rain, snow, and sleet. These and other factors must be evaluated by the engineer before a proper specification can be written. Tunnel dampers have been made from commercial-quality galvanized steel, hot-dipped galvanized steel, anodized aluminum, aluminum with a duranodic finish, carbon steel with various finishes, and stainless steel, including types 304, 304L, 316, 316L, and 317. Maintainability and Life Expectancy ofEquipment. These issues are of great concern when specifying dampers that may be difficult to access regularly for servicing, inspection, or maintenance. In addition, the equipment may be difficult to replace ifit fails prema- turely because it was marginally designed for the pressures, tem- peratures, corrosion resistance, etc., required for the application. Thus, some specifying engineers purposely design dampers with a more robust construction. Dampers may be specified with heavier and/or more corrosion-resistant materials than may be required for the application, in hopes of reducing operational problems and maintenance costs and extending the life expectancy of the product. Typical methods used to design dampers of more robust construc- tion include the following: · Limiting blade, frame, and linkage deflections to a maximum of L/360 · Selecting actuators for 200 to 300% of the actual damper torque required · Using large safety factors for stresses and deflections of high stress components · Specifying heavier material sizes and gages than necessary · Using more corrosion-resistant materials and finishes than required · Using slower damper activation times (from full-close to full- open and vice versa) Many damper specifications include a quality assurance (QA) or system assurance program (SAP) to ensure that required perfor- mance levels are met. Others include an experience criterion that requires damper manufacturers to have five installations with five or more years of operating experience; a list of projects and contact names must be submitted so the current customer can com- municate with past customers regarding the product performance. These requirements help ensure that reliable products are sup- plied. Module Size. The maximum damper module size is one of the most important initial-cost factors. Many dampers can be made as a single-module assembly, or in several sections that can be field Inc. ASHRAE, 2019 user. single for Licensed | {}
3a5420e6-24db-491e-9944-359302437911 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Enclosed Vehicular Facilities 16.39 assembled into a single-module damper. However, some damper openings are very large and it may not be practical to manufacture the damper in a one-piece frame construction because of shipping, handling, and/or installation problems. Generally, initial cost is lower with fewer modules because they have fewer blades, frames, jackshafts, actuators, and mullion sup- ports. However, other factors, such as job site access, lifting capa- bilities, and installation labor costs, must also be included in the initial-cost analysis. These factors vary for each project, so the spec- ifying engineer must evaluate each application separately. Air Leakage. The specifying engineer must consider air leakage through the damper when evaluating a design. Leakage is usually specified in terms of cubic metres per second per square metre of damper face area, at a specific air pressure. As differential air pres- sure increases across the damper, so does air leakage. Leakage is, therefore, a function of air pressure and damper crack area, rather than of airflow. To reduce leakage, the number or size of leakage paths must be reduced. The most common method is adding damper blades and/or jamb seals, which can reduce leakage to an acceptable value. Some specifications note the allowable damper air leakage as a percentage of the normal or maximum airflow. However, it is important to recognize that this is only an acceptable practice if the airflow and associated pressure are known. Damper Applications and Types. Dampers allow or restrict air- flow into a tunnel, and balance airflow in a tunnel. Fan isolation dampers can be installed in multiple-fan systems to (1) isolate any parallel, nonoperating fan from those operating, to prevent short- circuiting and airflow/pressure losses through the inoperative fan; (2) prevent serious windmilling of an inoperative fan; and (3) pro- vide a safe environment for maintenance and repair work on each fan. Single-fan installations may also have a fan isolation damper to prevent serious windmilling from natural or piston-effect drafts and facilitate fan maintenance. Ventilation dampers control the amount of fresh air supplied to and exhausted from the tunnel and station areas. They may also serve as smoke exhaust dampers (SEDs), bypass dampers (BDs), volume dampers (VDs), and fire dampers (FDs), depending on their location and design. Two types of ventilation dampers are gen- erally used: (1) trapdoor, which is installed in a vertical duct, such that the door lies horizontal when closed; and, (2) multiblade louver with parallel-operating blades. Both types can be driven by either an electric or pneumatic actuator; the fan controller operates the damper actuator. During normal operation, the damper usually closes when the fan is shut off and opens when the fan is turned on. The trapdoor damper is simple and works satisfactorily where a vertical duct enters a plenum fan room through an opening in the floor. This damper is usually constructed of steel plate, with welded angle iron reinforcements; it is hinged on one side and closed by gravity against the embedded angle frame of the opening. The open- ing mechanism is usually a shaft sprocket-and-chain device. The drive motor and gear drive mechanism, or actuator, must develop suf- ficient force to open the damper door against the maximum (static) air pressure differential that the fan can develop. This pressure can be ob- tained from the fan performance curves. Limit switches start and stop the gear-motor drive or actuator at the proper position. Fan isolation and ventilation dampers in places other than vertical ducts should have multiblade louvers. These dampers usu- ally consist of a rugged channel frame, the flanges of which are bolted to the flanges ofthe fan, duct, wall, or floor opening. Damper blades are assembled with shafts that turn the bearings mounted on the outside of the channel frame. This arrangement requires access outside the duct for bearing and shaft lubrication, maintenance, and linkage operation space. Multiblade dampers should have blade edge and/or end seals to meet air leakage requirements for the appli- cation. The trapdoor damper, properly fabricated, is inherently a low- leakage design because of its weight and the overlap at its edges. Multiblade dampers can also have low air leakage, but they must be carefully constructed to ensure tightness on closing. The pressure drop across a fully opened damper and the air leakage rate across a fully closed damper should be verified by the appropriate test pro- cedure in AMCA Standard 500-D. A damper that leaks excessively under pressure can cause the fan to rotate counter to its power rota- tion, thus making restarting dangerous and possibly damaging to the fan motor drive. Actuators and Accessory Selections. Tunnel damper specifica- tions typically call for dampers, actuators, and accessories to meet the operational requirements of emergency ventilation fans, as described by NFPA Standard 130. Damper actuators are normally specified to be electric or pneumatic. Actuator selection is deter- mined by the engineer or the customer and is usually decided by available power or initial and/or long-term operating cost. Pneumatic Actuators. Pneumatic actuators are available in many sizes and designs; rack and pinion, air cylinder, and Scotch yoke are common configurations. Each can be of either double-action (i.e., air is supplied to operate the damper in both directions) or spring- return construction. A spring-return design uses air to power it in one direction and a spring to drive it in the opposite direction; it is selected when it is desirable to have the damper fail to a set posi- tion on loss of air supply. Many manufacturers make pneumatic actuators; several manufacturers make both double-acting and spring-return designs capable of operating at 250°C for 1 h. Electric Actuators. Electric actuators are also available in a variety of designs and sizes. They can be powered in both directions to open and close the damper; in this case the actuator usually fails in its last position on loss of power. Electric actuators that are pow- ered in one direction and spring-driven in the opposite direction are also available. As with pneumatic actuators, spring return is selected when it is desirable to have the damper fail to a particular position on loss of power. There are fewer manufacturers of electric actua- tors than pneumatic actuators, and most do not make a spring-return design, especially in larger-torque models. Also, very few electric actuators are capable of operating at 250°C for 1 h, particularly for spring-return designs. Actuator Selection. Actuators for tunnel dampers are typically sized to operate against the maximum airflow or velocity and pres- sure that will occur in a worst-case scenario. The maximum air velocity corresponds to the maximum airflow expected through the damper during any of its operating conditions. In addition, the max- imum airflow could come from more than one fan, depending on system design. The maximum pressure on the damper during normal or emergency ventilation is typically the maximum pressure that the fan can generate at shutoff. Actuators are sized and selected to (1) overcome the frictional resistance of blade bearings, linkage pivots, jackshafting assem- blies, etc.; and (2) compress the blade and jamb seals to meet spec- ified air leakage requirements. Therefore, the specifying engineer must determine maximum airflow (or air velocity) and pressure conditions, and maximum air leakage criteria. Other factors in actuator selection are reliability and mainte- nance requirements. Although pneumatic actuators are considered more reliable than electric ones, the larger number of components in a pneumatic system and the cumulative risk of failure of any one component make the overall reliability of both systems similar. Safety factors in actuator selection are not always addressed in tunnel damper specifications. This omission can result in opera- tional problems if a manufacturer selects actuators too close to the required operating torque. Tunnel dampers are expected to function for many years when properly maintained. Also, damper manufac- turers determine their torque requirements based on square, plumb, and true installations. These factors, plus the fact that dirt and debris Inc. ASHRAE, 2019 user. single for Licensed | {}
8199b3a4-b7dc-443d-838e-72bd90c2fcf5 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 16.40 2019 ASHRAE Handbook-HVAC Applications (SI) build-up can increase damper torque, suggest that a minimum safety factor of at least 50% should be specified. Greater safety factors can be specified for some applications; however, larger actuators require larger drive shafts with higher initial cost. Supply Air Intake. Supply air intakes require careful design to ensure that air drawn into the ventilation system is of the best quality available. Factors such as recirculation of exhaust air or intake of contaminants from nearby sources should be considered. Louvers or grilles are usually installed over air intakes for aes- thetic, security, or safety reasons. Bird screens are also necessary if the openings between louver blades or grilles are large enough to allow birds to enter. Because of the large volumes of air required in some ventilation systems, it may not be possible for intake louvers to have face air velocities low enough to be weatherproof. Therefore, intake ple- nums, ventilation shafts, fan rooms, and fan housings often need water drains. Windblown snow can also enter the fan room or ple- num, but snow accumulation usually does not prevent the ventila- tion system from operating satisfactorily, if additional floor drains are located near the louvers. Sound attenuation devices may be needed in fresh air intakes or exhaust outlets to keep fan-generated noise from disturbing the out- door environment. If noise reduction is required, the total system (i.e., fans, housings, plenums, ventilation building, and location and size of air intakes and exhaust outlets), should be investigated. Fan selection should be based on the total system, including pressure drop from sound attenuation devices. Exhaust Outlets. Exhaust air from ventilation systems should be discharged above street level and away from areas with human occupancy. Contaminant concentrations in exhaust air should not be a concern if the system is working effectively. However, odors and entrained particulate matter in exhaust make discharge into occu- pied areas undesirable. Exhaust stack discharge velocity, usually a minimum of 10 m/s, should be high enough to disperse contami- nants into the atmosphere. Evase (flared) outlets have been used to regain some static pres- sure and thereby reduce exhaust fan energy consumption. Unless the fan discharge velocity is over 10 m/s, the energy savings may not offset the cost of the evase outlets. In a vertical or near-vertical exhaust fan discharge connection to an exhaust duct or shaft, rainwater runs down the inside of the stack into the fan. This water dissolves material deposited from vehicle exhaust on the inner surface of the stack and becomes extremely corrosive. Therefore, fan housings should be corrosion-resistant or specially coated to protect the metal. Discharge louvers and gratings should be sized and located so that their discharge is not objectionable to pedestrians or contami- nating to nearby air intakes. Airflow resistance across the louver or grating should also be minimized. Discharge air velocities through sidewalk gratings are usually limited to 2.5 m/s. Bird screens should be provided ifthe exhaust airstream is not continuous (i.e., 24 h/day, 7 days/week), and the openings between louver blades are large enough to allow birds to enter. Corrosion resistance of the louver or grating should be deter- mined by the corrosiveness of the exhaust air and the installation environment. Pressure drop across the louvers should be verified by the design engineer using the appropriate test procedure in AMCA Standard 500-L. 9. NATIONAL AND INTERNA TIONAL SAFETY STANDARDS AND GUIDELINES National Fire Protection Association (NFPA) NFPA developed fire protection standards for both road tunnels and for rapid transit facilities. The standard for transit systems is known as NFPA Standard 130, and the standard for road tunnels, bridges, and other limited-access roads is NFPA Standard 502. In addition to Standards 130 and 502, NFPA publishes many standards and codes that are applicable to enclosed vehicular facil- ities, including the following: · Standard for Portable Fire Extinguishers, NFPA 10, 2010 · Standard for the Installation of Sprinkler Systems, NFPA 13, 2010 · Standard for the Installation of Standpipe and Hose Systems, NFPA 14, 2010 · Standard for the Installation of Stationary Pumps for Fire Protec- tion, NFPA 20, 2010 · Standard for Water Tanks for Private Fire Protection, NFPA 22, 2008 · Flammable and Combustible Liquids Code, NFPA 30, 2008 · Code for Motor Fuel Dispensing Facilities and Repair Garages, NFPA 30A, 2008 · Standard for Spray Application using Flammable or Combustible Materials, NFPA 33, 2011 · Vehicular Gaseous Fuel Systems Code, NFPA 52, 2010 · Liquefied Natural Gas (LNG) Vehicular Fuel Systems Code, NFPA 57, 2002 · Liquefied Petroleum Gas Code, NFPA 58, 2011 · National Electrical Code�, NFPA 70, 2011 · Recommended Practice for Electrical Equipment Maintenance, NFPA 70B, 2010 · National Fire Alarm and Signaling Code�, NFPA 72Ⓡ, 2010 · Standard for Fire Doors and Other Opening Protectives, NFPA 80, 2010 · Standard for Parking Structures, NFPA 88A, 2011 · Standard for Repair Garages, NFPA 88B, 1997 · Life Safety CodeⓇ, NFPA 101Ⓡ, 2009 · Standard for Emergency and Standby Power Systems, NFPA 110, 2010 · Standard on Stored Electrical Energy Emergency and Standby Power Systems, NFPA 111, 2010 · Standard for Safeguarding Construction, Alteration, and Demoli- tion Operations, NFPA 241, 2009 · Standard on Emergency Services Incident Management System, NFPA 1561, 2008 · Standard for Fire Hose Connections, NFPA 1963, 2009 World Road Association (PIARC) PIARC, or the W orld Road Association (formerly the Permanent International Association of Road Congresses), has for many years published technical reports on tunnels and tunnel ventilation in con- junction with their quadrennial W orld Road Congresses. The PIARC Technical Committee on Road Tunnel Operation (C3.3) and its working groups published several important specific documents on tunnel ventilation and fire safety: · Classification of Tunnels, Existing Guidelines and Experiences, Recommendations, 05.03.B, 1995 · Road Tunnels: Emissions, Environment, Ventilation, 05.02.B, 1996 · Fire and Smoke Control in Road Tunnels, 05.05.B, 1999 · Pollution by Nitrogen Dioxide in Road Tunnels, 05.09.B, 2000 · Cross Section Geometry in Unidirectional Tunnels, 05.11.B, 2002 · Cross Section Design of Bidirectional Road Tunnels, 05.12.B, 2004 · Good Practice for the Operation and Maintenance of Road Tun- nels, 05.13.B, 2004 · Road Tunnels: Vehicle Emissions and Air Demand for Ventila- tion, 05.14.B, 2004 · Traffic Incident Management Systems Used in Road Tunnels, 05.15.B, 2004 · Systems and Equipment for Fire and Smoke Control in Road Tun- nels, 05.16.B, 2007 Inc. ASHRAE, 2019 user. single for Licensed | {}
1d6f3cff-08ce-4907-b4a5-cd6f7700aab9 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Enclosed Vehicular Facilities 16.41 · Integrated Approach to Road Tunnel Safety, 2007R07, 2007 · Risk Analysis for Road Tunnels, 2008R02, 2008 · Management of the Operator- Emergency Teams Interface in Road Tunnels, 2008R03, 2008 · Road Tunnels: A Guide to Optimising the Air Quality Impact upon the Environment, 2008R04, 2008 · Road Tunnels: An Assessment of Fixed Fire Fighting Systems, 2008R07, 2008 · Tools for Road Tunnel Safety Management, 2009R08, 2009 Country-Specific Standards and Guidelines Many countries publish tunnel guidelines and standards primarily for use in their country; however, many of these docu- ments do provide an insight into numerous unique tunnel applica- tions. A partial list of those available is as follows: · Design Guidelines Tunnel Ventilation, RVS 9.261 & RVS 9.262, Transportation and Road Research Association, National Roads Administration, Austria, 1997 · Regulations on Technical Standards and Conditions for Design and Construction of Tunnels on Roads, Croatia, 1991 · Design of Road Tunnels, Standard CSN 73 7507, Czech Republic · Road Tunnel Equipment, Guideline TP 98, Czech Republic · Inter-Ministerial Circular 2000-63: Safety in the Tunnels of the National Highways Network, Ministry of the Establishment, Transport and Housing, France, 2000 · Guidelines for Equipment and Operation of Road Tunnels, Road and Transportation Research Association (RABT), Federal Min- istry of Traffic, Germany, 2006 · Safety of Traffic in Road Tunnels with Particular Reference to Vehicles Transporting Dangerous Materials, Italy, 1999 · National Safety Standard of Emergency Facilities in Road Tun- nels, Japan Road Association, Japan, 2001 · Recommendations for the Ventilation of Road Tunnels Public W orks and Water Management (RWS), the Netherlands, 2005 · Norwegian Design Guide-Road Tunnels, Public Roads Admin- istration, Directorate of Public Roads, Norway, 1992 · Ventilation of Road Tunnels, Sub-Committee 61, Nordisk Vejteknisk Forbund (NVF), Report 6, 1993 · Manual for the Design, Construction and Operation of Tunnels, IOS-98, Spain, 1998 · Tunnel 2004 General Technical Specification for New Tunnels and Upgrading of Old Tunnels, Swedish National Road Associa- tion, Sweden, 2004 · Ventilation for Road Tunnels, Swiss Federal Roads Authority (FEDRO), 2004 · TSI Technical Specification for Interoperability, Safety in Rail- way Tunnels, European Railway Association, 2008 · Design ofRoad Tunnels, the Highways Agency, United Kingdom, 1999 · Road Tunnel Design Guidelines, Federal Highway Administra- tion, FHWA-IF-05-023, United States, 2004 Building and Fire Codes Often, building and fire codes have supplementary information and requirements applicable to a specific type of facility. For example, ventilation of a vehicle parking garage is also governed by the applicable building code. Some of the commonly used codes are as follows: · The International Building CodeⓇ (IBCⓇ) with its own subset of mechanical codes such as the International Plumbing CodeⓇ (IPCⓇ) and the International Mechanical CodeⓇ (IMCⓇ), as well as the International Existing Buildings CodeⓇ International Fire Code�, and International Fuel Gas CodeⓇ. · National building codes were the Uniform Building Code (UBC), Building Officials Code Association (BOCA), and the Southern Building Code Conference (SBCC), each of which was applicable in different parts of the country but now have been replaced by the IBC. · Most states have their own state building and fire codes with specific modifications to the IBC or other as applicable for the conditions specific to the state, such as seismic requirements. · Many cities and municipalities have their own local building and fire codes. The designer should be aware of the local code governing the facility. Many cities have adopted specific NFPA standards into their codes and some amend these standards. The facility's design is required to conform to the requirements of the amended standard, unless a specific waiver is applied for and obtained. Ancillary areas of tunnels such as electrical and mechanical equipment rooms, which are often adjacent to the tunnel they serve, are governed by the applicable building codes. For separation requirements between these ancillary spaces and the tunnel, the more stringent of the requirements between the building code and the applicable NFPA standard applies. The authority having juris- diction should always be consulted when there is any doubt in the application of this separation requirement. REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. ACGIH. 1998. Industrial ventilation: A manual of recommended practice, 23rd ed., Appendix A. American Conference of Governmental Industrial Hygienists, Cincinnati, OH. ACGIH. 2001. 2001 TLVs and BEIs: Threshold limit values for chemical substances and physical agents & biological exposure indices. American Conference of Governmental and Industrial Hygienists, Cincinnati, OH. ACGIH. 2003. ACGIH Board Ratifies 2003 TL Vs and BEIs. Press Release, Jan. 27. American Conference of Governmental and Industrial Hygien- ists, Cincinnati, OH. Aisiks, E.G., and N.H. Danziger. 1969. Ventilation research program at Cas- cade Tunnel, Great Northern Railway. American Railway Engineering Association. AMCA. 1998. Laboratory methods of testing dampers for rating. Standard 500-D. Air Movement and Control Association, Arlington Heights, IL. AMCA. 1999. Laboratory methods of testing louvers for rating. Standard 500-L. Air Movement and Control Association, Arlington Heights, IL. Amtrak. 2005. Overbuild ofAmtrak right-of-way design policy. Engineering Practice EP4006 issued by the Chief Engineer, Structures, National Rail- road Passenger Corporation, Philadelphia. ANSI/ABMA. 2000. Load and life rating for ball bearings. American Bearing Manufacturers Association, Washington, D.C. AREMA. 2007. Buildings and support facilities. Chapter 6, Part 4, Section 4.7 in Manual for railway engineering. American Railway Engineering and Maintenance-of- W ay Association, Landover, MD. ASHRAE. 1999. Laboratory methods oftesting fans for rating. Standard 51- 1999 (AMCA Standard 210-99). ASHRAE. 2004. Ventilation for acceptable indoor air quality. ANSI/ ASHRAE Standard 62.1-2004. Atkinson, G., S. Jagger, and K. Moodie. 2001. Fire survival of rolling stock: Current standards and experience from the Ladbrook Grove crash. Inter- national Seminar: Fire in Trains, Escape and Crash Survival, Heathrow, England. Bendelius, A.G. 2008. Road tunnels and bridges. In Fire protection hand- book, R.E. Cote, C.C. Grant, J.R. Hall, R.E. Solomon, and P.A. Powell, eds. National Fire Protection Association, Quincy, MA. Buraczynski, J.J. 1997. Integrated control systems at the Cumberland Gap Tunnel. Independent Technical Conferences Limited, Second Interna- tional Conference: Tunnel Control and Communication, Amsterdam, The Netherlands. BIS. National building code of India (NBC). Bureau of Indian Standards. Delhi, India. Inc. ASHRAE, 2019 user. single for Licensed | {}
a9912894-f9a9-4910-ae2e-4ae39fdddf44 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 16.42 2019 ASHRAE Handbook-HVAC Applications (SI) BSI. 2013. Components for smoke and heat control systems. Code of prac- tice on functional recommendations and calculation methods for smoke and heat control systems for covered car parks. BSI Standard BS 7346- 7:2013. British Standards Institution, United Kingdom. Colino, M.P., and E.B. Rosenstein. 2006. Tunnel emergency egress and the mid train fire. ASHRAE Transactions 112(2):251-265. DOT. 1976. Subway environmental design handbook (SEDH). Urban Mass Transportation Administration, U.S. Government Printing Office, Wash- ington, D.C. DOT. 1996a. Design guidelines for bus transit systems using compressed natural gas as an alternative fuel. Federal Transit Administration, U.S. Government Printing Office, Washington, D.C. DOT. 1996b. Design guidelinesfor bus transit systems using liquefiedpetro- leum gas (LPG) as an alternative fuel. Federal Transit Administration, U.S. Government Printing Office, Washington, D.C. DOT. 1996c. Design guidelines for bus transit systems using alcohol fuel (methanol and ethanol) as an alternative fuel. Federal Transit Adminis- tration, U.S. Government Printing Office, Washington, D.C. DOT. 1997a. Subway Environment Simulation (SES) computer program version 4: User's manual and programmer's manual. Issued as Volume II of Subway Environmental Design Handbook. Pub. No. FTA-MA-26- 7022-97-1. US Department of Transportation, Washington, D.C. Also available from Volpe Transportation Center, Cambridge, MA. DOT. 1997b. Design guidelines for bus transit systems using liquefied nat- ural gas (LNG) as an alternative fuel. Federal Transit Administration, U.S. Government Printing Office, Washington, D.C. DOT. 1998. Design guidelines for bus transit systems using hydrogen as an alternativefuel. Federal Transit Administration, U.S. Government Print- ing Office, Washington, D.C. DuCharme, G.N. 1991. Ventilation for battery charging. Heating/Piping/Air Conditioning (February). EPA. 1975. Supplement to the guidelinesfor review ofenvironmental impact statements. Volume 1: Highway projects. Environmental Protection Agency, Research Triangle Park, NC. EPA. 1984. MOBILE3 mobile emissions factor model. EPA 460/3-84-002. Environmental Protection Agency, Research Triangle Park, NC. EPA. 2000. Air quality criteria for carbon monoxide. EPA/600/P-99/001F. U.S. Environmental Protection Agency, Research Triangle Park, NC. EPA. 2002. MOBILE6.2 mobile emissions factor model. EPA 420-R-02- 001. Environmental Protection Agency, Research Triangle Park, NC. EPA. 2009. Draft motor vehicle emission simulator (MOVES) 2009, soft- ware design and reference manual. EPA-420-B-09-007. U.S. Environ- mental Protection Agency, Washington, D.C. EPA. 2010. Motor vehicle emission simulator (MOVES), user guide for MOVES2010a. EPA-420-B-10-036. U.S. Environmental Protection Agency, Washington, D.C. Fieldner, A.C., S.H. Katz, and S.P. Kinney. 1921. Ventilation of vehicular tunnels. Report of the U.S. Bureau of Mines to New York State Bridge and Tunnel Commission and New Jersey Interstate Bridge and Tunnel Commission. American Society of Heating and Ventilating Engineers (ASHVE). Fritz, S. 1994. Exhaust emissions from two intercity passenger locomotives. Journal of Engineeringfor Gas Turbines and Power 116:774-783. Fruin, J.J. 1987. Pedestrian planning and design. Elevator World, Mobile, AL. Gilbey, M. 2006. Transient thermal comfort indices in subway. Presented at 12th International Symposium of Aerodynamics and Ventilation of Vehicle Tunnels, British Hydromechanics Research Group, Portoroz, Slovenia. Guan, D., D. Abi-Zadeh, M. Tabarra, and H. Zhang. 2009. Transient thermal comfort model for subways. Presented at 13th International Symposium of Aerodynamics and Ventilation of Vehicle Tunnels, British Hydro- mechanics Research Group, New Jersey. Gwynne, S., and E. Rosenbaum. 2008. Employing the hydraulic model in assessing emergency movement. In SFPE handbook offire protection engineering, 4th ed. P.J. DiNenno, D. Drysdale, C.L. Beyler, W.D. Walton, R.L.P. Custer, J.R. Hall, and J.M. Watts, eds. National Fire Pro- tection Association, Quincy, MA. Haerter, A. 1963. Flow distribution and pressure change along slotted or branched ducts. ASHVE Transactions 69:124-137. Hama, G.M., W.G. Frederick, and H.G. Monteith. 1974. How to design ventilation systems for underground garages: Air engineering. Study by the Detroit Bureau of Industrial Hygiene, Detroit (April). ICC. 2009a. International mechanical code�. International Code Council, Country Club Hills, IL. ICC. 2009b. International building codeⓇ. International Code Council, Country Club Hills, IL. ICC. 2009c. Internationalfire codeⓇ. International Code Council, Country Club Hills, IL. ICC. 2009d. International fuel gas codeⓇ. International Code Council, Country Club Hills, IL. ILO. 2003. CIS chemical information database. International Labor Orga- nization, Occupational Safety and Health Information Centre, Geneva. www.inchem.org/pages/about.html. Ingason, H. 2006. Design fires in tunnels. Safe and Reliable Tunnels. Joyeux, D. 1997. Natural fires in closed car parks-Car fire tests. Report INC-96/294d-DJ/NB, Centre Technique Industriel de la Construction Metallique, Metz, France. Kashef, A., G.D. Lougheed, G.P. Crampton, Z. Liu, K. Yoon, G.V. Had- jisophocleous, and K.H. Almand. 2009. Findings of the international road tunnel fire detection research project. Fire Technology 45:221- 237. Kennedy, W.D., J.A. Gonzalez, and J.G. Sanchez. 1996. Derivation and application of the SES critical velocity equations. ASHRAE Transac- tions 102(2):40-44. Krarti, M., and A. Ayari. 1998. Overview of existing regulations for ven- tilation requirements of enclosed vehicular parking facilities (RP-945). ASHRAE Transactions 105(2):18-26. Levy, S.S., and N.H. Danziger. 1985. Ventilation of the Mount Macdonald Tunnel. Presented at Fifth International Symposium on Aerodynamics and Ventilation of Vehicle Tunnels, British Hydromechanics Research Group, Lille, France. Levy, S.S., and D.P. Elpidorou. 1991. Ventilation of Mount Shaughnessy Tunnel. Presented at Seventh International Symposium on Aerodynam- ics and Ventilation of Vehicle Tunnels, Brighton, UK. Liu, Z.G., A. Kashef, G.D. Lougheed, J.Z. Su, N. Benichou, and K.H. Almand. 2006. An overview of the international road tunnel fire detec- tion research project. Presented at 10th Fire Suppression and Detection Research Application Symposium, Orlando. Liu, Z.G., A. Kashef, G.D. Lougheed, G.P. Crampton, Y. Ko, and G.V. Hadjisophocleous. 2009. Parameters affecting the performance of detection systems in road tunnels. Presented at 13th International Sym- posium on Aerodynamics and Ventilation of Vehicle Tunnels, New Brunswick, NJ. Lu, Y. 1993. Practical handbook of heating, ventilation, and air conditioning. China Building Industry Press. Mangs, J., and 0. Keski-Rahkonen. 1994a. Characterisation of the fire behaviour of a burning passenger car, part I: Car fire experiments. Fire Safety Journal 23(1):17-35. Mangs, J., and 0. Keski-Rahkonen. 1994b. Characterization of the fire behaviour of a burning passenger car, part II: Parametrization of mea- sured rate of heat release curves. Fire Safety Journal 23(1):37-49. Meacham, B.J., N.A. Dembsey, K. Schebel, J.S. Tubbs, M.A. Johann, A. Kimball, and A. Neviackas. 2010. Rail vehicle fire hazard guidance- Final summary report. Worcester Polytechnic Institute/Arup, Worces- ter, MA, for U.S. Department ofHomeland Security, Science and Tech- nology Directorate, International Programs Division, Grant #2009-ST- 108-000013. MHD/FHW A. 1995. Memorial Tunnelfire ventilation test program, com- prehensive test report. Massachusetts Highway Dept., Boston, and Federal Highway Administration, Washington, D.C. MSHA. 2001a. Diesel particulate matter exposure of underground coal miners; Final Rule. 30CFR72. Code of Federal Regulations, U.S. Department of Labor, Mine Safety and Health Administration, Wash- ington, D.C. MSHA. 2001b. Diesel particulate matter exposure of underground metal and nonmetal miners; Final Rule. 30CFR57. Code of Federal Regula- tions, U.S. Department of Labor, Mine Safety and Health Administra- tion, Washington, D.C. Musser, A., and L. Tan. 2004. Control of diesel exhaust fumes in enclosed locomotive facilities (RP-1191). ASHRAE Research Project, Final Report. NFPA. 2008. Code for motor fuel dispensing facilities and repair garages. Standard 30A. National Fire Protection Association, Quincy, MA. Inc. ASHRAE, 2019 user. single for Licensed | {}
872c90f0-5ae5-4672-841f-4fda236e04cf | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Enclosed Vehicular Facilities 16.43 NFPA. 2011. Standard for spray application using flammable or combus- tible materials. Standard 33. National Fire Protection Association, Quincy, MA. NFPA. 2010. Vehicular gaseous fuel systems code. Standard 52. National Fire Protection Association, Quincy, MA. NFPA. 2011. Liquefied petroleum gas code. Standard 58. National Fire Protection Association, Quincy, MA. NFPA. 2011. National electrical codeⓇ. Standard 70. National Fire Protec- tion Association, Quincy, MA. NFPA. 2010. National fire alarm and signaling code. Standard 72. National Fire Protection Association, Quincy, MA. NFPA. 2011. Standard for parking structures. Standard 88A. National Fire Protection Association, Quincy, MA. NFPA. 1997. Standard for repair garages. Standard 88B. National Fire Protection Association, Quincy, MA. NFPA. 2010. Standard for fixed guideway transit and passenger rail systems. Standard 130. National Fire Protection Association, Quincy, MA. NFPA. 2011. Standard for road tunnels, bridges, and other limited access highways. Standard 502. National Fire Protection Association, Quincy, MA. NIOSH. 2005. Pocket guide to chemical hazards. Publication 2005-149. National Institute for Occupational Safety and Health, Washington, D.C. www.cdc.gov/niosh/npg/. NTIS. 1980. User's guide for the TUNVEN and DUCT programs. Publica- tion PB80141575. National Technical Information Service, Springfield, VA. OSHA. 2001a. Occupational safety and health standards. 29CFR1910.1000. Code of Federal Regulations, U.S. Department of Labor, Occupational Safety and Health Administration, Washington, D.C. OSHA. 2001b. Partial list ofchemicals associated with diesel exhaust. Occu- pational Safety and Health Administration, U.S. Department of Labor, Washington, D.C. www.osia.gov/SLTChieselechaust/chemicaL.itml PIARC. 1995. Road tunnels. XXth World Road Congress, Montreal. PIARC. 1999. Fire and smoke control in road tunnels. World Road Asso- ciation (PIARC), La Defense Cedex, France. PIARC. 2007a. Systems and equipmentfor fire and smoke control in road tunnels. World Road Association (PIARC), La Defense Cedex, France. PIARC. 2007b. Integrated approach to road tunnel safety. World Road Association (PIARC), La Defense Cedex, France. PIARC. 2008. Management of the operator-Emergency teams interface in road tunnels. World Road Association (PIARC), La Defense Cedex, France. Proulx. 2008. Evacuation time. In SFPE handbook offire protection engi- neering, 4th ed. P.J. DiNenno, D. Drysdale, C.L. Beyler, W.D. Walton, R.L.P. Custer, J.R. Hall, and J.M. Watts, eds. National Fire Protection Association, Quincy, MA. Sanchez, J.G. 2003. Optimization of station air-conditioning systems for mass transit systems. Presented at 11th International Symposium of Aerodynamics and Ventilation of Vehicle Tunnels, British Hydrome- chanics Research Group, Luzern, Switzerland. SFPE. 2008. Handbook offire protection engineering, 4th ed. P.J. DiNenno, D. Drysdale, C.L. Beyler, W.D. Walton, R.L.P. Custer, J.R. Hall, and J.M. Watts, eds. National Fire Protection Association, Quincy, MA. Singstad, 0. 1929. Ventilation ofvehicular tunnels. World Engineering Con- gress, Tokyo. Stankunas, A.R., P.T. Bartlett, and K.C. Tower. 1980. Contaminant level control in parking garages. ASHRAE Transactions 86(2):584-605. SwRI. 1992. Exhaust emissions from two intercity passenger locomotives. Report 08-4976, prepared by Steven G. Fritz for California Department of Transportation. Southwest Research Institute, San Antonio. Tabarra, M., and D. Guan. 2009. How efficient is an under platform exhaust system? Presented at 13th International Symposium of Aerodynamics and Ventilation of Vehicle Tunnels, British Hydromechanics Research Group, New Jersey. Tubbs, J.S., and B.J. Meacham. 2007. Egress design solutions: A guide to evacuation and crowd management. John Wiley & Sons, Hoboken, NJ. Watson, A.Y., R.R. Bates, and D. Kennedy. 1988. Air pollution, the automobile, and public health. Sponsored by the Health Effects Institute. National Academy Press, Washington, D.C. Zalosh, R., and P. Chantranuwat. 2003. International road fire tunnel detec- tion research project-Phase 1. The Fire Protection Research Founda- tion, Quincy, MA. BIBLIOGRAPHY Bendelius, A.G. 1996. Tunnel ventilation. Chapter 20, Tunnel engineering handbook, 2nd ed., J.O. Bickel, T.R. Kuesel and E.H. King, eds. Chapman & Hall, New York. BSI. 1999. Code of practice for fire precautions in the design and construc- tion of railway passenger carrying trains. British Standard BS 6853. British Standards Institution, London. DOE. 2002. Alternative fuel news. Alternative Fuels Data Center, U.S. Department of Energy, Washington, D.C. DOT. 1995. Summary assessment of the safety, health, environmental and system risks of alternative fuels. Federal Transit Administration, U.S. Department of Transportation, Washington, D.C. Goldschmidt, T. 2017. Ductless car park ventilation: Global trends and design practice. AHR Exposition Conference Paper LV-17-C058. Las Vegas, Nevada. Ingason, H. 1994. Heat release rate measurements in tunnel fires. Proceed- ings ofthe International Conference on Fires in Tunnels, Boras, Sweden. Klote, J.H., and J.A. Milke. 2002. Principles of smoke management. ASHRAE. PIARC. 2007. Systems and equipmentforfire and smoke control in road tun- nels. World Road Association (PIARC), La Defense Cedex, France. Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
729f947a-c1b1-4d35-b0a4-6535a8ce6517 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 17 LABORATORIES GENERAL DESIGN GUIDANCE 17.1 Hazard Assessment 17.2 Design Parameters 17.2 LABORATORY EXHAUST AND CONTAINMENT DEVICES. 17.3 Biological Safety Cabinets 17.5 Miscellaneous Exhaust Devices 17.7 Laminar Flow Clean Benches 17.7 Compressed Gas Storage and Ventilation 17.8 LABORATORY VENTILATION 17.8 Exhaust Systems 17.9 Fire Safety for Ventilation Systems 17.11 Control 17.11 MODERN laboratories require regulated temperature, humid- relative static pressure, air motion, air cleanliness, sound, and exhaust. This chapter addresses biological, chemical, animal, and physical laboratories. Within these generic categories, some laboratories have unique requirements. This chapter provides an overview ofthe HVAC characteristics and design criteria for labora- tories, including a brief overview of architectural and utility con- cerns. This chapter does not cover pilot plants, which are essentially small manufacturing units. The function of a laboratory is important in determining the appropriate HVAC system selection and design. Air-handling, hydronic, control, life safety, and heating and cooling systems must function as a unit and not as independent systems. HV AC systems must conform to applicable safety and environmental regulations. Providing a safe environment for all personnel is a primary objec- tive in the design ofHVAC systems for laboratories. A vast amount ofinformation is available, and HVAC engineers must study the sub- ject thoroughly to understand all the factors that relate to proper and optimum design. This chapter serves only as an introduction to the topic of laboratory HVAC design. HVAC systems must integrate with architectural planning and design, electrical systems, structural systems, other utility systems, and the functional requirements ofthe laboratory. The HVAC engineer, then, is a member of a team that includes other facility designers, users, industrial hygienists, safety officers, security, operators, and maintenance staff. Decisions or rec- ommendations by the HVAC engineer may significantly affect con- struction, operation, and maintenance costs. Laboratories frequently use 100% outdoor air, which broadens the range of conditions to which the systems must respond. They seldom operate at maximum design conditions, so the HVAC engineer must pay particular attention to partial load operations that are continually changing due to variations in internal space loads, exhaust require- ments, external conditions, and day/night variances. Most laborato- ries will be modified at some time. Consequently, the HV AC engineer must also consider to what extent laboratory systems should be adapt- able for other needs. Both economics and integration of the systems with the rest of the facility must be considered. 1. GENERAL DESIGN GUIDANCE 1.1 LABORATORY TYPES Laboratories can be divided into the following general types: The preparation of this chapter is assigned to TC 9.10, Laboratory Systems. ¦ Stack Heights and Air Intakes ¦ 17.13 ¦ ¦ --- ¦ --- ¦ ¦ APPLICATIONS ¦ 17.14 ¦ ¦ Laboratory Animal Facilities ¦ 17.14 ¦ ¦ Ancillary Spaces for Animal Laboratories ¦ 17.16 ¦ ¦ Containment Laboratories ¦ 17.17 ¦ ¦ Scale-Up Laboratories ¦ 17.17 ¦ ¦ Teaching Laboratories ¦ 17.18 ¦ ¦ Clinical Laboratories ¦ 17.18 ¦ ¦ Radiochemistry Laboratories ¦ 17.18 ¦ ¦ Operation and Maintenance ¦ 17.18 ¦ ¦ Energy ¦ 17.19 ¦ ¦ Commissioning ¦ 17.20 ¦ ¦ Economics ¦ 17.21 ¦ · Biological laboratories are those that contain biologically active materials or involve the chemical manipulation of these materials. This includes laboratories that support such disciplines as bio- chemistry, microbiology, cell biology, biotechnology, genomics, immunology, botany, pharmacology, and toxicology. Both chem- ical fume hoods and biological safety cabinets are commonly installed in biological laboratories. · Chemical laboratories support both organic and inorganic syn- thesis and analytical functions. They may also include laboratories in the material and electronic sciences. Chemical laboratories commonly contain a number of fume hoods. · Animal laboratories are areas for manipulation, surgical modifi- cation, and pharmacological observation of laboratory animals. They also include animal holding rooms, which are similar to lab- oratories in many of the performance requirements but have an additional subset of requirements. · Physical laboratories are spaces associated with physics; they commonly incorporate lasers, optics, radioactive material, high- and low-temperature material, electronics, and analytical instru- ments. Laboratory Resource Materials The following are general or specific resource materials applicable to various types of laboratories. · ACGIH. Industrial Ventilation: A Manual ofRecommended Prac- tice. American Conference of Governmental Industrial Hygien- ists, Cincinnati, OH. · FGI guidelines for design and construction. The Facilities Guide- line Institute, American Society of Healthcare Engineering, Chi- cago, IL. · ASSE. Laboratory Ventilation. ANSI/AIHA/ASSE Standard Z9.5. American Society of Safety Engineers, Des Plaines, IL · ASHRAE Laboratory Design Guide. · CAP. Medical Laboratory Planning and Design. College of American Pathologists, Northfield, IL. · DHHS. Biosafety in Microbiological and Biomedical Laborato- ries. U.S. Department of Health and Human Services (CDC). · EEOC. Americans with Disabilities Act Handbook. Equal Em- ployment Opportunity Commission. · PSL. I2SL 's Electronic Library. i2sl.org/elibrary/index.html. Inter- national Institute for Sustainable Laboratories. · NFPA. Fire Protection Guide for Hazardous Materials. National Fire Protection Association, Quincy, MA. 17.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
c9025cc5-1c92-425a-b995-addb74ca6cf8 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 17.2 2019 ASHRAE Handbook- -HVAC Applications (SI) · NFPA. Fire Protection for Laboratories Using Chemicals. ANSI/ NFPA Standard 45. National Fire Protection Association, Quincy, MA. · NRC. Biosafety in the Laboratory: Prudent Practices for Han- dling and Disposal of Infectious Materials. National Research Council, National Academy Press, Washington, D.C. · NRC. Prudent Practices in the Laboratory: Handling and Man- agement of Chemical Hazards, updated version. National Research Council, National Academy Press, Washington, D.C. · NSF. Class II Biosafety Cabinetry. NSF/ANSI Standard 49. · OSHA. Occupational Exposure to Chemicals in Laboratories. Appendix VII, 29 CFR 1910.1450. www.ecfr.gov. · SEFA. Laboratory Fume Hoods Recommended Practices. Scien- tific Equipment and Furniture Association, Garden City, NY. Other regulations and guidelines may apply to laboratory design. All applicable institutional, local, state, and federal requirements should be identified before design begins. 1.2 HAZARD ASSESSMENT Laboratory operations potentially involve some hazard; nearly all laboratories contain some type of hazardous materials. Before the laboratory is designed, the owner's designated safety officers should perform a comprehensive hazard assessment. These safety officers include, but are not limited to, the chemical hygiene officer, radiation safety officer, biological safety officer, and fire and loss prevention officials. The hazard assessment should be incorporated into the chemical hygiene plan, radiation safety plan, and biological safety protocols. Hazard study methods such as hazard and operability analysis (HAZOP) can be used to evaluate design concepts and certify that the HVAC design conforms to the applicable safety plans. Nature and quantity of the contaminants, types of operations, and degree of hazard dictate the types of containment and local exhaust devices. For functional convenience, operations posing less hazard potential are conducted in devices that use directional airflow for personnel protection (e.g., laboratory fume hoods and biological safety cabi- nets). However, these devices do not provide absolute containment. Operations having a significant hazard potential are conducted in devices that provide greater protection but are more restrictive (e.g., sealed glove boxes). The design team should visit similar laboratories to assess suc- cessful design approaches and safe operating practices. Each labo- ratory is somewhat different. Design must be evaluated using appropriate, current standards and practices as well, rather than sim- ply duplicating existing (and possibly outmoded) facilities. 1.3 DESIGN P ARAMETERS The following ventilation system design parameters must be established for a laboratory space: · Temperature and humidity, both indoor and outdoor · Air quality, from both process and safety perspectives, including the need for air filtration and special treatment (e.g., charcoal, HEP A, or other filtration of supply or exhaust air) · Equipment and process heat gains, both sensible and latent · Minimum allowable air change rates · Equipment and process exhaust quantities · Exhaust and air intake locations · Style, capture velocities, and usage factors of the exhaust device · Need for standby equipment and emergency power · Alarm requirements. · Potential changes in the size and number of laboratory hoods · Anticipated increases in internal heat loads · Isolation and room pressurization requirements · Biological containment provisions · Decontamination provisions It is important to (1) review design parameters with the safety officers and scientific staff, (2) determine limits that should not be exceeded, and (3) establish the desirable operating conditions. For areas requiring variable temperature or humidity, these parameters must be carefully reviewed with the users to establish a clear understanding of expected operating conditions and system per- formance. Because laboratory HVAC systems often incorporate 100% out- door air systems, the selection of design parameters has a substan- tial effect on capacity, first cost, and operating costs. The selection of proper and prudent design conditions is very important. Internal Thermal Considerations In addition to the heat gain from people and lighting, laborato- ries frequently have significant sensible and latent loads from equipment and processes. Often, data for equipment used in labo- ratories are unavailable or the equipment has been custom built. Information for some common laboratory equipment is listed in the appendix of the ASHRAE Laboratory Design Guide (ASHRAE 2002). Data on heat release from animals that may be housed in the space can be found in Table 2 of this chapter and in Alereza and Breen (1984). Careful review of the equipment to be used, a detailed under- standing of how the laboratory will be used, and prudent judgment are required to obtain good estimates of the heat gains in a labora- tory. The convective portion of heat released from equipment located within exhaust devices can be discounted. Heat from equip- ment that is directly vented or heat from water-cooled equipment should not be considered part of the heat released to the room. Any unconditioned makeup air that is not directly captured by an exhaust device must be included in the load calculation for the room. In many cases, additional equipment will be obtained by the time a lab- oratory facility has been designed and constructed. The design should allow for this additional equipment. Internal load as measured in watts per square metre is the average continuous internal thermal load discharged into the space. It is not a tabulation of the connected electrical load because it is rare for all equipment to operate simultaneously, and most devices operate with a duty cycle that keeps the average electrical draw below the name- plate information. When tabulating the internal sensible heat load in a laboratory, the duty cycle of the equipment should be obtained from the manufacturer. This information, combined with the name- plate data for the item, may provide a more accurate assessment of the average thermal load. The HVAC system engineer should evaluate equipment name- plate ratings, applicable use and usage factors, and overall diversity. Review use, usage factors, and diversity with lab occupants. Much laboratory equipment includes computers, automation, sample changing, or robotics; this can result in high levels of use even during unoccupied periods. The HVAC engineer must evaluate in- ternal heat loads under all anticipated laboratory operating modes. Because of highly variable equipment heat gain, individual labora- tories should have dedicated temperature controls. See Chapter 18 in the 2017 ASHRAE Handbook-Fundamentals for more informa- tion on load calculation. Two cases encountered frequently are (1) building programs based on generic laboratory modules and (2) laboratory spaces that are to be highly flexible and adaptive. Both situations require the design team to establish heat gain on an area basis. The values for area-based heat gain vary substantially for different types oflabora- tories. Heat gains of 50 to 270 W/m2 or more are common for lab- oratories with high concentrations of equipment. Inc. ASHRAE, 2019 user. single for Licensed | {}
795de124-7e02-44d2-bb63-63361a312d56 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Laboratories 17.3 Architectural Considerations Integrating utility systems into the architectural planning, design, and detailing is essential to providing successful research facilities. The architect and the HVAC system engineer must seek an early understanding of each other's requirements and develop integrated solutions. HVAC systems may fail to perform properly if the archi- tectural requirements are not addressed correctly. Quality assurance of the installation is just as important as proper specifications. The following play key roles in the design of research facilities: Modular Planning. Most laboratory programming and planning is based on developing a module that becomes the base building block for the building layout. Laboratory planning modules are fre- quently 3 to 3.5 m wide and 6 to 9 m deep. The laboratory modules may be developed as single work areas or combined to form multi- ple-station work areas. Utility systems should be arranged to reflect the architectural planning module, with services provided for each module, or pair of modules, as appropriate. Development of Laboratory Units or Control Areas. National Fire Protection Association (NFPA) Standard 45 requires that laboratory units be designated. Similarly, the International Building CodeⓇ (ICC 2015) requires the development of control areas. Laboratory units or control areas should be developed, and the appropriate hazard levels should be determined early in the design process. The HVAC designer should review the requirements for maintaining separations between laboratories and note require- ments for exhaust ductwork to serve only a single laboratory unit or control area. Additionally, NFPA Standard 45 requires that no fire dampers be installed in laboratory exhaust ductwork. Building codes offer no leeway on maintaining required floor-to-floor fire separations. Review these criteria and the proposed solutions early in the design process with the appropriate building code officials. The combina- tion of the two requirements commonly necessitates the construc- tion of dedicated fire-rated shafts from each occupied floor to the penthouse or building roof. Provisions for Adaptability and Flexibility. Research objectives frequently require changes in laboratory operations and programs. Thus, laboratories must be flexible and adaptable, able to accommo- date these changes without significant modifications to the infrastruc- ture. For example, the utility system design can be flexible enough to supply ample cooling to support the addition of heat-producing equipment without requiring modifications to the HV AC system. Adaptable designs should allow programmatic research changes that require modifications to the laboratory' s infrastructure within the lim- its of the individual laboratory area and/or interstitial and utility cor- ridors. For example, an adaptable design would allow addition of a fume hood without requiring work outside that laboratory space. Fur- ther, the HVAC designer should consider the consequences of future programmatic changes on the sizing of main ductwork and central system components. The degree of flexibility and adaptability for which the laboratory HVAC system is designed should be determined from discussion with the researchers, laboratory programmer, and laboratory planner. The HVAC designer should have a clear under- standing of these requirements and their financial impact. Early Understanding of Utility Space Requirements. The amount and location of utility space are significantly more import- ant in research facility design than in that of most other buildings. The available ceiling space and the frequency of vertical distribution shafts are interdependent and can significantly affect architectural planning. The HVAC designer must establish these parameters early, and the design must reflect these constraints. The designer should review alternative utility distribution schemes, weighing advantages and disadvantages. High-Quality Envelope Integrity. Laboratories that have strin- gent requirements for control of temperature, humidity, relative static pressure, and background particle count generally require architectural features to allow the HVAC systems to perform prop- erly. The building envelope may need to be designed to handle rel- atively high levels of humidification and slightly negative building pressure without moisture condensation in the winter or excessive infiltration. Some of the architectural features that the HVAC designer should evaluate include · Vapor and air barriers: position, location, and kind · Insulation: location, thermal resistance, and kind · Window frames and glazing · Caulking · Internal partitions: their integrity in relation to air pressure, vapor barriers, and insulation value · Finishes: vapor permeability and potential to release particles into the space · Doors · Air locks Air Intakes and Exhaust Locations. Mechanical equipment rooms and their outdoor air intakes and exhaust stacks must be located to avoid intake of fumes into the building. As with other buildings, air intake locations must be chosen to minimize fumes from loading docks, cooling tower discharge, vehicular traffic, adja- cent structures and processes, etc. 2. LABORATORY EXHAUST AND CONTAINMENT DEVICES 2.1 FUME HOODS The Scientific Equipment and Furniture Association (SEFA 2010) defines a laboratory fume hood as a "safety device specifi- cally designed to carry undesirable effluents (generated · · - during a laboratory procedure) away from laboratory personnel and out of the building, when connected to a properly designed laboratory ven- tilation system. " The hood can be mounted on a bench, a pedestal, or the floor. Materials should mainly be flame resistant. The face open- ing has a sash and an optional additional protective shield, and usu- ally has an airfoil to reduce reverse airflow on the lower surface. The hood should have a baffle, and usually a bypass system to control airflow patterns in the hood and distribute air evenly at the opening. For variable-air-volume (VA V) systems, the bypass system may be partially blocked. Figure 1 shows the basic elements of a general- purpose benchtop fume hood. Fume hoods may be equipped with a variety of accessories, in- cluding internal lights, service outlets, sinks, air bypass openings, airfoil entry devices, flow alarms, special linings, ventilated base storage units, and exhaust filters. Under-counter cabinets for storage of flammable materials require special attention to ensure safe in- stallation. NFPA Standard 30 does not recommend venting these cabinets; however, ventilation is often required to avoid accumula- tion of toxic or hazardous vapors. Ventilation of these cabinets by a separately ducted supply and exhaust that will maintain the tem- perature rise of the cabinet interior within the limits defined by NFPA Standard 30 should be considered. Types of Fume Hoods The following are the primary types of fume hoods and their applications: Constant Volume (approximately constant-volume airflow with variable face velocity). Hood that meets basic SEFA definition. Sash may be vertical, horizontal, or combination. Application: Moderate to highly hazardous processes; varying procedures. Inc. ASHRAE, 2019 user. single for Licensed | {}
bf1fdb88-43eb-46fa-8865-59de10fc21a8 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 17.4 2019 ASHRAE Handbook-HVAC Applications (SI) Inc. ASHRAE, 2019 Variable Volume (constant face velocity). Hood has an opening or bypass designed to provide a prescribed minimum air intake when sash is closed, and an exhaust system designed to vary air- flow in accordance with sash opening. Sash may be vertical, hor- izontal, or a combination of both. Application: Moderate to highly hazardous processes; varying procedures. Auxiliary Air (approximately constant-volume airflow). A plenum above the face receives air from a secondary air supply that pro- vides partially conditioned or unconditioned outdoor air. Note: Many organizations restrict the use of this type of hood. Low Velocity or Reduced Flow (approximately constant-volume airflow with variable face velocity or variable volume). These hoods are designed to provide containment at lower average face velocities. Application: Moderate to highly hazardous processes; varying procedures. Filtered, Recirculating (approximately constant-volume airflow). Particulate filtration combined with chemical adsorption to remove contaminants. Application: Moderate process with predictable procedures. Radioisotope. Hood with special integral work surface, linings impermeable to radioactive materials, and structure strong enough to support high-density shielding materials. The interior must be constructed to prevent radioactive material buildup and allow complete cleaning. Ductwork should have flanged gas- keted joints with quick-disconnect fasteners that can be readily dismantled for decontamination. High-efficiency particulate air (HEPA) and/or charcoal filters may be needed in exhaust duct. Application: Laboratories using radioactive isotopes. Perchloric Acid. Hood with special integral work surfaces, coved corners, and nonorganic lining materials. Perchloric acid is an user. single for Licensed ![image](/image/placeholder) EXHAUST DUCT ADJUSTABLE ROOM AIR BYPASSES TOP SLOT INTO HOOD WHEN SASH IS CLOSED SASH CLOSES AIR INLET WHEN RAISED FIXED CENTER SLOT MOVABLE SASH · REAR BAFFLE ADJUSTABLE BOTTOM SLOT VERTICAL SASH (RAISED POSITION) BYPASS AIR INLET AIRFOIL Fig. 1 Bypass Fume Hood with Vertical Sash and Bypass Air Inlet extremely active oxidizing agent. Its vapors can form unstable deposits in the ductwork that present a potential explosion haz- ard. To alleviate this hazard, the exhaust system must be equipped with an internal water washdown and drainage system, and the ductwork must be constructed of smooth, impervious, cleanable materials that are resistant to acid attack. The internal washdown system must completely flush the ductwork, exhaust fan, discharge stack, and fume hood inner surfaces. Ductwork should be kept as short as possible with minimum elbows. Per- chloric acid exhaust systems with longer duct runs may need a zoned washdown system to avoid water flow rates in excess of the capacity to drain water from the hood. Because perchloric acid is an extremely active oxidizing agent, organic materials should not be used in the exhaust system in places such as joints and gaskets. Ducts should be constructed of a stainless steel material, with a chromium and nickel content not less than that of 316L stainless steel, or of a suitable nonmetallic material. Joints should be welded and ground smooth. A perchloric acid exhaust system should only be used for work involving perchloric acid. Application: Process and research laboratories using perchloric acid. Mandatory use because of explosion hazard. California. Special hood with sash openings on multiple sides (usu- ally horizontal). Application: For enclosing large and complex research apparatus that require access from two or more sides. Floor-Mounted Hood (Walk-In). Hood with sash openings to the floor. Sash can be either horizontal or vertical. Application: For enclosing large or complex research apparatus. Not designed for personnel to enter while operations are in prog- ress. Distillation. Fume hood with extra depth and 1/3- to 1/2-height benches. Application: For enclosing tall distillation apparatus. Process (approximately constant-volume airflow with approxi- mately constant face velocity). Standard hood with a fixed open- ing and without a sash. Not a fume hood. Considered a ventilated enclosure. Application: Low-hazard processes; known procedures. Canopy. Open hood with an overhead capture structure. Fume Hood Sash Configurations Application: Not a fume hood. Useful for heat or water vapor removal from some work areas. Not to be substituted for a fume hood. Not recommended when workers must bend over the source ofheat or water vapor. The work opening has operable glass sash(es) for observation and shielding. A sash may be vertically operable, horizontally oper- able, or a combination of both. A vertically operable sash can incor- porate single or multiple vertical panels. A horizontally operable sash incorporates multiple panels that slide in multiple tracks, allowing the open area to be positioned across the face of the hood. The combination of a horizontally operable sash mounted within a single vertically operable sash section allows the entire hood face to be opened for setup. The opening area can then be limited by closing the vertical panel, with only the horizontally sliding sash sections used during experimentation. Both the multiple vertical sash section and combination sash arrangement allow the use of larger fume hoods with limited opening areas, resulting in reduced exhaust air- flow requirements. Fume hoods with vertically rising sash sections should include provisions around the sash to prevent the bypass of ceiling plenum air into the fume hood. | {}
323bb1c7-03ee-41f1-95cb-14b016d5e78e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Laboratories 17.5 Fume Hood Performance Containment of hazards in a fume hood is based on the principle that a flow of air entering at the face of the fume hood, passing through the enclosure, and exiting at the exhaust port prevents the escape of airborne contaminants from the hood into the room. The following variables affect the performance of the fume hood: · Face velocity · Size of face opening · Sash position · Shape and configuration of entrance · Shape of any intermediate posts · Inside dimensions and location of work area relative to face area · Location of service fittings inside the fume hood · Heat generated in the hood · Size and number of exhaust ports · Back baffle and exhaust plenum arrangement · Bypass arrangement, if applicable. · Auxiliary air supply, if applicable · Arrangement and type of replacement supply air outlets · Air velocities near the hood · Distance from openings to spaces outside the laboratory · Movements of the researcher within the hood opening · Location, size, and type of research apparatus placed in the hood · Distance from the apparatus to the researcher's breathing zone Air Currents. Air currents external to the fume hood can jeop- ardize the hood's effectiveness and expose the researcher to materi- als used in the hood. Detrimental air currents can be produced by · Air supply distribution patterns in the laboratory · Movements of the researcher · People walking past the fume hood · Thermal convection · Opening (or open) doors and windows Caplan and Knutson (1977, 1978) conducted tests to determine the interactions between room air motion and fume hood capture velocities with respect to the spillage of contaminants into the room. Their tests indicated that the effect of room air currents is significant and of the same order of magnitude as the effect of the hood face velocity. Consequently, improper design and/or installation of the replacement air supply can lower performance of the fume hood. Disturbance velocities at the face of the hood should be no more than one-half and preferably one-third the face velocity of the hood. This is an especially critical factor in designs that use low face velocities. For example, a fume hood with a face velocity of 0.5 m/ s could tolerate a maximum disturbance velocity of 0.25 m/s. If the design face velocity were 0.3 m/s, the maximum disturbance veloc- ity would be 0.15 m/s. To the extent possible, the fume hood should be located so that traffic flow past the hood is minimal. Also, the fume hood should be placed to avoid any air currents generated from the opening of win- dows and doors. Air currents from open doors and windows can be significantly higher than acceptable maximum disturbance veloci- ties. To ensure optimum placement of the fume hoods, the HV AC system designer must take an active role early in the design process. Use of Auxiliary Air Fume Hoods. ASSE Standard Z9.5 dis- courages the use of auxiliary air fume hoods. These hoods incorpo- rate an air supply at the fume hood to reduce the amount of room air exhausted. The following difficulties and installation criteria are associated with auxiliary air fume hoods: · The auxiliary air supply must be introduced outside the fume hood to maintain appropriate velocities past the researcher. · The flow pattern ofthe auxiliary air must not degrade the contain- ment performance of the fume hood. · The volume of auxiliary air must not be enough to degrade the fume hood's containment performance. · Auxiliary air must be conditioned to avoid blowing cold air on the researcher; often the air must be cooled to maintain the required temperature and humidity within the hood. Auxiliary air can introduce additional heating and cooling loads in the laboratory. · Only vertical sash should be used in the hood. · Controls for the exhaust, auxiliary, and supply airstreams must be coordinated. · Additional coordination of utilities during installation is required to avoid spatial conflicts caused by the additional duct system. · Humidity control can be difficult; unless auxiliary air is cooled to the dew point of the specified internal conditions, there is some degradation ofhumidity control; however, ifsuch cooling is done, the rationale for using auxiliary air has been nullified. Fume Hood Performance Criteria. ASHRAE Standard 110 describes a quantitative method of determining the containment performance of a fume hood. This method requires the use of a tracer gas and instruments to measure the amount of tracer gas that enters the breathing zone of a mannequin; this simulates the con- tainment capability of the fume hood as a researcher conducts op- erations in the hood. The following tests are commonly used to judge the performance of the fume hood: (1) face velocity test, (2) flow visualization test, (3) tracer gas test, and (4) sash movement test. These tests should be performed under the following condi- tions: · Usual amount of research equipment in hood; room air balance fixed · Doors and windows in normal positions · Fume hood sash set in varying positions to simulate both static and dynamic performance All fume hoods should be tested annually, at minimum, to verify their performance. Refer to ASHRAE Standard 110 for proce- dures. 2.2 BIOLOGICAL SAFETY CABINETS A biological safety cabinet protects the researcher and, in some configurations, the research materials as well. Biological safety cabinets are also referred to as ventilated safety cabinets, laminar flow cabinets, and glove boxes. Biological safety cabinets are cat- egorized into six groups (four of which are shown in Figure 2): ¦ Class I ¦ Similar to chemical fume hood, no research material protection, 100% exhaust through a HEPA filter ¦ ¦ --- ¦ --- ¦ ¦ Class II ¦ ¦ ¦ Type A1 ¦ 70% recirculation within the cabinet; 30% exhaust through a HEPA filter; common plenum configuration; can be recirculated into the laboratory ¦ ¦ Type A2 ¦ 70% recirculation within the cabinet; 30% exhaust through a HEP. A filter; common plenum configuration; can be recirculated to the room or exhausted to the outdoor ¦ ¦ Type B1 ¦ 40% recirculation within the cabinet; 60% exhaust through a HEPA filter; separate plenum configuration, must be exhausted to the outdoor ¦ ¦ Type B2 ¦ 100% exhaust through a HEPA filter to the outdoor ¦ ¦ Class III ¦ Special applications; 100% exhaust through a HEPA filter to the outdoors; researcher manipulates material within cabinet through physical barriers (gloves) ¦ The researcher must make several key decisions before selecting a biological safety cabinet (Eagleston 1984). An important differ- ence in biological safety cabinets is their ability to handle chemical vapors properly (Stuart et al. 1983). Ofspecial concern to the HV AC Inc. ASHRAE, 2019 user. single for Licensed | {}
672857d1-d9a5-4faf-9d13-0922d4a8a8f9 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 17.6 2019 ASHRAE Handbook- -HVAC Applications (SI) ![image](/image/placeholder) HEPA EXHAUST FILTER HEPA SUPPLY FILTER FRONT VIEW END VIEW FRONT VIEW END VIEW CLASS I CLASS " TYPE A1 EXHAUST HEPA EXHAUST INTAKE FILTER EXHAUST SUPPLY AIR DIFFUSER ww EXHAUST AIR ▼▼ ▼ PLENUM ○○ HEPA FILTER FRONT VIEW END VIEW FRONT VIEW END VIEW CLASS IITYPE B1 CLASS III Fig. 2 Types of Biological Safety Cabinets engineer are the proper placement of the biological safety cabinet in the laboratory and the room's air distribution. Rake (1978) con- cluded the following: A general rule of thumb should be that, if the cross draft or other disruptive room airflow exceeds the velocity of the air curtain at the unit's face, then problems do exist. Unfortu- nately, in most laboratories such disruptive room airflows are present to various extents. Drafts from open windows and doors are the most hazardous sources because they can be far in excess of 200 fpm [1 m/s] and accompanied by substantial turbulence. Heating and air-conditioning vents perhaps pose the greatest threat to the safety cabinet because they are much less obvious and therefore seldom considered. i · It is imper- ative then that all room airflow sources and patterns be consid- ered before laboratory installation of a safety cabinet. Class II biological safety cabinets should only be placed in the laboratory in compliance with NSF International Standard 49, Class II (Laminar Flow) Biohazard Cabinetry. Assistance in procuring, testing, and evaluating performance parameters of Class II biologi- cal safety cabinets is available from NSF as part of the standard. The cabinets should be located away from drafts, active walkways, and doors. The air distribution system should be designed to avoid air patterns that impinge on the cabinet. The different biological safety cabinets have varying static pres- sure resistance requirements. Generally, Class II Type A1 cabinets have pressure drops ranging between 1 and 25 Pa. Class II Type B1 cabinets have pressure drops in the range of150 to 300 Pa, and Class II Type B2 cabinets have pressure drops ranging from 370 to 570 Pa. The manufacturer must be consulted to verify specific require- ments. Pressure requirements also vary based on filter loading and the intermittent operation of individual biological safety cabinets. Exhaust systems for biological safety cabinets must be designed with these considerations in mind. Take care when manifolding bio- logical safety cabinet exhausts to ensure that the varying pressure requirements are met. The manufacturer of the biological safety cabinet may be able to supply the transition to the duct system. The transition should include an access port for testing and balancing and an airtight damper for decontamination. As with any containment ductwork, high-integrity duct fabrication and joining systems are necessary. Biological safety cabinets may require periodic decontamination before service and filter replacement. During decontamination, the cabinet must be isolated or sealed from the laboratory and the exhaust system. The responsible safety officer should be consulted to determine the need for, and placement of, isolation dampers to facilitate decontamination operations. If provisions for decontami- nation are necessary, the ventilation system design should maintain laboratory airflow and pressure during the decontamination proce- dure. Class I Cabinets The Class I cabinet is a partial containment device designed for research operations with low- and moderate-risk etiologic agents. It does not provide protection for materials used in the cabinet. Room air flows through a fixed opening and prevents aerosols that may be generated in the cabinet enclosure from escaping into the room. Depending on cabinet usage, air exhausted through the cabinet may be HEPA filtered before being discharged into the exhaust system. The fixed opening through which the researcher works is usually 200 mm high. To provide adequate personnel protection, air veloc- ity through the fixed opening is usually at least 0.4 m/s. If approved by the appropriate safety officer, the Class I cabinet can be modified to safely contain chemical carcinogens by adding Inc. ASHRAE, 2019 user. single for Licensed | {}
71acc356-4c68-42ec-ab0d-4c6722d3b98d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Laboratories 17.7 appropriate exhaust air treatment and increasing the velocity through the opening to 0.5 m/s. Large pieces of research equipment can be placed in the cabinet if adequate shielding is provided. The Class I cabinet is not appropriate for containing systems that are vulnerable to airborne contamination because the air flowing into the cabinet is untreated. Also, the Class I cabinet is not recommended for use with highly infectious agents because an interruption of the inward airflow may allow aerosolized particles to escape. Class II Cabinets Class II cabinets provide protection to personnel, product, and the environment. The cabinets feature an open front with inward air- flow and HEPA-filtered recirculated and exhaust air. Microbiologi- cal containment, product protection, and cross-contamination performance is established for certain cabinets by NSF Interna- tional's Standard 49. Measurement techniques in NSF Standard 49 vary from those often used by building system testing and balancing agencies; therefore, it is important to coordinate activities of the bio- logical safety cabinet (BSC) certification agency and the testing and balancing agency. The Class II Type A1 cabinet has a fixed opening with a minimum inward airflow velocity of 0.4 m/s. The average downward velocity is established by the manufacturer and is typically 0.25 to 0.4 m/s. The Class II Type A1 cabinet is suitable for use with agents meeting Biosafety Level 2 criteria (DHHS 1999), and, if properly certified, can meet Biosafety Level 3. However, because approximately 70% of the airflow is recirculated, the cabinet is not suitable for use with flammable, toxic, or radioactive agents. The Class II Type A2 cabinet maintains an inward airflow veloc- ity of 0.5 m/s and is similar in performance to the Class II Type Al. The Class II Type B1 cabinet has a vertical sliding sash and main- tains an inward airflow of0.5 m/s at a sash opening of200 mm. The average downward velocity of the internal airflow is typically in the range of0.25 to 0.4 m/s. The Class II Type B1 cabinet is suitable for use with agents meeting Biosafety Level 3. Approximately 60% of the internal airflow is exhausted through HEPA filters; this allows the use of biological agents treated with limited quantities of toxic chemicals and trace amounts of radionuclides, provided the work is performed in the direct exhaust area of the cabinet. The Class II Type B2 cabinet maintains an inward airflow velocity of 0.5 m/s through the work opening. The cabinet is 100% exhausted through HEPA filters to the outdoors; all downward- velocity air is drawn from the laboratory or other supply source and is HEPA filtered before being introduced into the workspace. The Class II Type B2 cabinet may be used for the same level of work as the Class II Type B1, and is used when the primary con- sideration is protection of the material in the hood. In addition, the design allows use of small quantities of toxic chemicals and radio- nuclides in microbiological studies. In Class II Type A2 cabinets, exhaust air delivered to the outlet of the cabinet by internal blowers must be handled by the laboratory ex- haust system. This arrangement requires a delicate balance between the cabinet and the laboratory's exhaust system, and it may incorpo- rate a thimble connection between the cabinet and the laboratory ex- haust ductwork. Thimble (or canopy) connections incorporate an air gap between the biological safety cabinet and the exhaust duct. The purpose of the air gap is to buffer the effect of any exhaust system fluctuations on the biological safety cabinet airflow. The exhaust system must pull more air than is exhausted by the biological safety cabinet to make airflow in through the gap. The designer should con- firm the amount of air to be drawn through the air gap. A minimum flow is required to provide the specified level of containment, and a maximum flow cannot be exceeded without causing an imbalance through aspiration. In the event of an exhaust system failure, the air gap allows the cabinet to maintain safe intake velocity by exhausting HEPA-filtered air through the air gap. Class II Type B1 and Type B2 cabinets rely on the building ex- haust system to pull the air from the cabinet's workspace and through the exhaust HEPA filters. The pressure resistance that must be overcome by the building exhaust system can be obtained from the cabinet manufacturer. In a fire or smoke condition, exhaust flow should continue through the cabinet, as for a fume hood; therefore, fire and smoke dampers should not be installed in the exhaust ductwork. The cabinet should be provided with a gastight damper to isolate it from the downstream ductwork to allow for decontamina- tion. Because containment in this type of cabinet depends on the building's exhaust system, the exhaust fan(s) should have redun- dant back-ups and the proper controls to maintain required flow rates. Class III Cabinets The Class III cabinet is a gastight, negative-pressure contain- ment system that physically separates the agent from the worker. These cabinets provide the highest degree of personnel protection. Work is performed through arm-length rubber gloves attached to a sealed front panel. Room air is drawn into the cabinet through HEPA filters. The American Glovebox Society (AGS 2007) indi- cates that Class III cabinets should be maintained at 125 Pa below ambient pressure. Exhaust flow rate should provide a minimum of 0.5 m/s inward containment velocity through a glove port opening in the event of a glove being inadvertently removed. HEPA filtra- tion or incineration before discharge to the atmosphere removes or destroys particulate material entrained in the exhaust air. A Class III system may be designed to enclose and isolate incubators, refrigerators, freezers, centrifuges, and other research equipment. Double-door autoclaves, liquid disinfectant dunk tanks, and pass boxes are used to transfer materials into and out of the cabinet. Class III systems can contain highly infectious materials and radioactive contaminants. Although there are operational inconve- niences with these cabinets, they are the equipment of choice when a high degree of personnel protection is required. Note that explo- sions have occurred in Class III cabinets used for research involving volatile substances. 2.3 MISCELLANEOUS EXHA UST DEVICES Snorkels are used in laboratories to remove heat or nontoxic par- ticles that may be generated from benchtop research equipment. Snorkels usually have funnel-shaped inlet cones connected to 75 to 150 mm diameter flexible or semi-flexible ductwork extending from the ceiling to above the benchtop level. Benchtop slots are used to remove nontoxic particles or fumes that may be generated by benchtop equipment. Often, hoods are installed over weigh stations to contain and minimize disturbances from room air currents. 2.4 LAMINAR FLOW CLEAN BENCHES Laminar flow clean benches are available in two configurations: horizontal (crossflow) and vertical (downflow). Both configurations filter the supply air and usually discharge the air out the front open- ing into the room. Clean benches protect the experiment or product but do not protect the researcher; therefore, they should not be used with any potentially hazardous or allergenic substances. Clean benches are not recommended for any work involving hazardous biological, chemical, or radionuclide materials. Inc. ASHRAE, 2019 user. single for Licensed | {}
0064ba90-047c-401c-b174-25d2dc56949c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 17.8 2019 ASHRAE Handbook- -HVAC Applications (SI) 2.5 COMPRESSED GAS STORAGE AND VENTILATION Gas Cylinder Closets Most laboratory buildings require storage closets for cylinders of compressed gases, which may be inert, flammable, toxic, corrosive, or poisonous. The requirements for storage and ventilation are covered in building codes and NFPA standards and codes. Water sprinklers are usually required, but other types of fire suppression may be needed based on the gases stored. Explosion containment requires a separate structural study, and closets generally require an outer wall for venting. One design used by a large chemical manu- facturer to house gases with explosion potential specifies a com- pletely welded 6 mm steel inner liner for the closet, heavy-duty door latches designed to withstand the force of an internal explosion, and venting out the top of the closet. Closet temperature should not exceed 52°C per NFPA Standard 55. Ventilation for cylinder storage is established in NFPA Standard 55 at a minimum of 5 L/(s · m2). Ventilation rates can be calculated by determining both the amount of gas that could be released by complete failure of the cylinder outlet piping connection and the time the release would take, and then finding the dilution airflow required to reduce any hazard below the maximum allowable limit. Ventilation air is usually exhausted from the closet; makeup air comes from the surrounding space through openings in and around the door or through a transfer duct. That makeup air must be con- sidered for the building air balance. Ventilation for a closet contain- ing materials with explosion potential must be carefully designed, with safety considerations taken into account. See NFPA Standard 68 for information on explosion venting. Cylinder closet exhausts should be connected through a separate duct system to a dedicated exhaust fan or to a manifold system in which constant volume can be maintained under any possible man- ifold condition. A standby source of emergency power should be considered for the exhaust system fan(s). Gas Cylinder Cabinets Compressed gases that present a physical or health hazard are often placed in premanufactured gas cylinder cabinets. Gas cylinder cabinets are available for single-, dual-, or triple-cylinder configura- tions and are commonly equipped with valve manifolds, fire sprin- klers, exhaust connections, access openings, and operational and safety controls. The engineer must fully understand safety, material, and purity requirements associated with specific compressed gases when designing and selecting cylinder cabinets and the components that make up the compressed gas handling system. Exhaust from the gas cylinder cabinets is provided at a high rate. Air is drawn into the gas cylinder cabinet from the surrounding space through a filtered opening, usually on the lower front of the cylinder cabinet. Depending on the specific gas stored in the cabi- net, the exhaust system may require emission control equipment and a source of emergency power. 3. LABORATORY VENTILATION The total airflow rate for a laboratory is dictated by one of the following: · Total amount of exhaust from containment and exhaust devices · Cooling required to offset internal heat gains · Minimum ventilation rate requirements · Airflow required to maintain pressure relationships Fume hood exhaust requirements (including evaluation of alter- nate sash configurations as described in the section on Fume Hoods) must be determined in consultation with the safety officers. The HV AC engineer must determine the expected heat gains from the laboratory equipment after consulting with the laboratory staff (see the section on Internal Thermal Considerations). Minimum ventilation rates should be established to provide a safe and healthy environment under normal and expected operating conditions. The dilution ventilation provided by this airflow is no substitute for the containment performance of a laboratory fume hood or other primary containment device, regardless of the room ventilation rate. The appropriate ventilation rate for clearing a room of fugitive emissions or spills varies significantly based on the amount of release, the chemical': s evaporation rate and hazard level, and ventilation system effectiveness. Fixed minimum airflow rates of 4 to 12 air changes per hour (ach) when the space is occupied have been used in the past. Recent uni- versity research (Klein et al. 2009) has shown a significant increase in dilution and clearing performance by increasing the air change rate from 6 to 8 ach with diminishing returns above 12 ach. Similarly, CFD research (Schuyler 2009) found that increasing the lab's dilu- tion ventilation rate from 4 to 8 ach reduced the background contam- inant level by greater than a factor of 10. This indicates that minimum ventilation rates at the lower end of the 4 to 12 ach range may not be appropriate for all laboratories. Minimum ventilation rates should be established on a room-by-room basis, considering the hazard level of materials expected to be used in the room and the operation and procedures to be performed. As the operation, materi- als, and hazard level of a room change, evaluate the prospect of increasing or decreasing the minimum ventilation rate. Active sensing of air quality in individual laboratories (Sharp 2010) is an alternative approach for dealing with the variability of appropriate ventilation rates, particularly when energy efficiency is important or when hazard level is less established. With this approach, the minimum airflow rate is varied based on sensing the laboratory' s actual air quality level or air cleanliness. Sensors used to determine air quality should be evaluated for their ability to detect chemicals being used in the space. When air contaminants are sensed in the laboratory above a given threshold, the minimum air change rate is increased proportionally to an appropriate level to purge the room. When the air is clean and contaminants are below the threshold, lower minimum airflow rates may be appropriate. Extensive studies of lab room environmental conditions (Sharp 2010) have shown that the air in labs is typically clean over 98% of the time. The maximum airflow rate for the laboratory should be reviewed to ensure that supply air delivery methods are appropriate and that supply airflows do not impede performance of the exhaust devices. Laminar-flow (nonaspirating) supply air outlets can be used to create predictable air flow patterns in the laboratory, generating directional flows toward exhaust and containment device locations. Laboratory ventilation systems can be arranged for either constant-volume or variable-volume airflow. The specific type should be selected with the research staff, safety officers, and maintenance personnel. Spe- cial attention should be given to unique areas such as glass washing areas, hot and cold environmental rooms and labs, fermentation rooms, and cage washing rooms. Emergency power systems to oper- ate the laboratory ventilation equipment should be considered based on hazard assessment or other specific requirements. Ensure that an adequate amount of makeup air is available whenever exhaust fans are operated on emergency power. Additional selection criteria are described in the sections on Hazard Assessment and Operation and Maintenance. Usage Factor When considering an overall facility, all laboratory personnel, scientific equipment, and exhaust devices are seldom, if ever, pres- ent or in use simultaneously. Accordingly, the system designer Inc. ASHRAE, 2019 user. single for Licensed | {}
d12ce69c-3638-41b3-81d7-0eec4b98a6a7 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Laboratories 17.9 should consider the impact of nonsimultaneous use on the sizing and selection of building systems. Many variables influence usage factors, including · Type and size of facility · Total number of fume hoods · Number of fume hoods per researcher · Scientific equipment use diversity · Type of fume hood controls · Fume hood sash configuration and minimum airflow required · Type of laboratory ventilation systems · Number of devices that must operate continuously due to chemi- cal storage requirements or contamination prevention · Number of current and projected research programs Apply usage factors carefully when sizing equipment. For exam- ple, teaching laboratories may have a usage factor of 100% when occupied by students. Ifthe usage factor is too low, design airflow and containment per- formance cannot be maintained. It is usually expensive and disrup- tive to add capacity to an operating laboratory' s supply or exhaust system. Detailed discussions with research staff are required to ascertain maximum usage factors as well as potential future require- ments. Noise Noise level in the laboratory should be considered at the begin- ning of the design so that the sound levels do not interfere with sci- entific work. Sound generated by the building HVAC equipment should also be evaluated to ensure that excessive levels do not escape to the outdoors. Remedial correction of excessive sound lev- els can be difficult and expensive. See Chapter 48 for more infor- mation. 3.1 SUPPLY AIR SYSTEMS Supply air systems for laboratories provide the following: · Thermal comfort for occupants · Minimum and maximum airflow rates · Replacement for air exhausted through fume hoods, biological safety cabinets, or other exhaust devices · Space pressurization control · Environmental control to meet process or experimental criteria The design parameters must be well defined for selection, sizing, and layout of the supply air system. Installation and setup should be verified as part of the commissioning process. Design parameters are covered in the section on Design Parameters, and commission- ing is covered in the section on Commissioning. Laboratories in which chemicals and compressed gases are used generally require nonrecirculating air supply systems. The selection of 100% exhaust air systems versus return air systems should be made as part of the hazard assessment process, which is discussed in the section on Hazard Assessment. A 100% outdoor air system must have a very wide range of heating and cooling capacity, which requires special design and control. Filtration Filtration for the air supply depends on the requirements of the laboratory. Conventional chemistry and physics laboratories com- monly use minimum efficiency reporting value (MERV) 13 filters (see ASHRAE Standard 52.2-2012 for more on MERVs). Biological and biomedical laboratories usually require MERV 14 or 15 filtra- tion. HEPA filters should be provided for spaces where research materials or animals are particularly susceptible to contamination from external sources. HEPA filtration of the supply air is necessary for such applications as environmental studies, studies involving specific pathogen-free research animals or nude mice, dust-sensitive work, and electronic assemblies. In many instances, biological safety cabinets or laminar flow clean benches (which are HEPA filtered) may be used rather than HEPA filtration for the entire laboratory. Air Distribution Air supplied to a laboratory must be distributed to keep tempera- ture gradients and air currents to a minimum. Air outlets (preferably nonaspirating diffusers) must not discharge into the face of a fume hood, a biological safety cabinet, or an exhaust device. Acceptable room air velocities are covered in the sections on Fume Hoods and Biological Safety Cabinets. Special techniques and diffusers are often needed to introduce the large air quantities required for a lab- oratory without creating disturbances at exhaust devices or on work surfaces. 3.2 EXHAUST SYSTEMS Laboratory exhaust systems remove air from containment devices and from the laboratory itself. The exhaust system must be con- trolled and coordinated with the supply air system to maintain cor- rect pressurization. Additional information on the control of exhaust systems is included in the section on Control. Design parameters must be well defined for selection, sizing, and layout of the exhaust air system. Installation and setup should be verified as part of the commissioning process. See the sections on Design Parameters and Commissioning. Laboratory exhaust systems should be designed for high reliability and ease of maintenance. This can be achieved by providing multiple exhaust fans and by sectionalizing equipment so that maintenance work may be performed on an individual exhaust fan while the system is operating. Another option is to use predictive maintenance procedures to detect problems prior to failure and to allow for scheduled shutdowns for maintenance. To the extent pos- sible, components of exhaust systems should allow maintenance without exposing maintenance personnel to the exhaust airstream. Access to filters and the need for bag-in, bag-out filter housings should be considered during the design process. Depending on the effluent of the processes being conducted, the exhaust airstream may require filtration, scrubbing, or other emis- sion control to remove environmentally hazardous materials. Any need for emission control devices must be determined early in design so that adequate space can be provided and cost implications can be recognized. Types of Exhaust Systems Laboratory exhaust systems can be constant-volume, variable- volume, or high-low volume systems with low-, medium-, or high- pressure ductwork, depending on the static pressure of the system. Each fume hood may have its own exhaust fan, or fume hoods may be manifolded and connected to one or more common central exhaust fans. Maintenance, functional requirements, and safety must be considered when selecting an exhaust system. Part of the hazard assessment analysis is to determine the appropriateness of variable-volume systems and the need for individually ducted exhaust systems. Laboratories with a high hazard potential should be analyzed carefully before variable-volume airflow is selected, because minimum air flow requirements could affect the design criteria.Airflow monitoring and pressure-independent control may be required even with constant-volume systems. In addition, fume hoods or other devices in which extremely hazardous or radioactive materials are used should receive special review to determine whether they should be connected to a manifolded exhaust system. It is rare for all exhaust devices installed in a laboratory to be used simultaneously at full capacity, so it is possible to conserve energy and potentially to reduce equipment capacities by installing Inc. ASHRAE, 2019 user. single for Licensed | {}
c6590d61-cbc6-4295-8f2d-a5bc4b3aab9f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 17.10 2019 ASHRAE Handbook-HVAC Applications (SI) a variable-volume system that includes an overall system usage fac- tor. Selection of an appropriate usage factor is discussed in the sec- tion on Usage Factor. Manifolded Exhaust Systems. These can be classified as pres- sure dependent or independent. Pressure-dependent systems are constant volume only and incorporate manually adjusted balanc- ing dampers for each exhaust device. If an additional fume hood is added to a pressure-dependent exhaust system, the entire system must be rebalanced, and the speed of the exhaust fans may need to be adjusted. Because pressure-independent systems are more flexible, pressure-dependent systems are not common in current designs. A pressure-independent system can be constant-volume, variable-volume, or a mix of the two. It incorporates pressure- independent volume regulators with each device. The system offers two advantages: (1) flexibility to add exhaust devices without hav- ing to rebalance the entire system and (2) variable-volume control. The volume regulators can incorporate either direct measure- ment of the exhaust airflow rate or positioning of a calibrated pres- sure-independent air valve. The input to the volume regulator can be (1) a manual or timed switch to index the fume hood airflow from minimum to operational airflow, (2) sash position sensors, (3) fume hood cabinet pressure sensors, or (4) velocity sensors. The section on Control covers this topic in greater detail. Running many exhaust devices into the manifold of a common exhaust system offers the following potential benefits: · Lower ductwork cost · Fewer pieces of equipment to operate and maintain · Fewer roof penetrations and exhaust stacks · Opportunity for energy recovery · Centralized locations for exhaust discharge · Ability to take advantage of exhaust system diversity · Ability to provide a redundant exhaust system by adding one spare fan per manifold · Higher stack momentum, which can be beneficial for exhaust dis- persion Individually Ducted Exhaust Systems. These comprise a sepa- rate duct, exhaust fan, and discharge stack for each exhaust device or laboratory. The exhaust fan can be single-speed, multiple-speed, or variable-speed and can be configured for constant volume, variable volume, or a combination of the two. Potential benefits include the following: Inc. ASHRAE, 2019 user. single for Licensed · Provision for installation of special exhaust filtration or treatment systems · Customized ductwork and exhaust fan corrosion control for spe- cific applications · Provision for selected emergency power backup · Simpler initial balancing · Failure of an individual fan may affect smaller areas of the facility · Suitability for smaller laboratories Maintaining correct flow at each exhaust fan requires (1) peri- odic maintenance and balancing and (2) consideration of flow rates with the fume hood sash in different positions. One problem encountered with individually ducted exhaust systems occurs when an exhaust fan is shut down. In this case, air can be drawn in reverse flow through the exhaust ductwork into the laboratory because the laboratory is maintained at a negative pressure. A challenge in designing independently ducted exhaust systems for multistory buildings is to provide extra vertical ductwork, extra space, and other provisions for future installation of additional exhaust devices. In multistory buildings, dedicated fire-rated shafts may be required from each floor to the penthouse or roof level. This issue should be evaluated in conjunction with requirements of the relevant fire code. As a result, individually ducted exhaust systems (or vertically manifolded systems) consume greater floor space than horizontally manifolded systems. However, less height between floors may be required. Ductwork Leakage Ductwork should have low leakage rates and should be tested to confirm that the specified leakage rates have been attained. Leaks from positive-pressure exhaust ductwork can contaminate the build- ing. The design goal should be zero leakage from any positive- pressure exhaust ductwork. Designs that minimize the amount of positive-pressure ductwork are desirable. It is recommended (and required by some codes) that positive-pressure ductwork trans- porting potentially hazardous materials be located outside of the building; if these ducts must be inside the building, they should be of the highest possible integrity. The fan discharge should connect directly to the vertical discharge stack. Careful selection and proper installation of airtight flexible connectors at the exhaust fans are essential. Some feel that flexible connectors should be used on the exhaust fan inlet only. If flexible connectors are used on the dis- charge side of the exhaust fan, they must be of high quality and included on a preventative maintenance schedule, because a con- nector failure could result in the leakage ofhazardous fumes into the equipment room. Another viewpoint contends that the discharge side of the exhaust fan should be hard connected to the ductwork, without using flexible connectors. The engineer should evaluate these details carefully. The potential for vibration and noise trans- mission must also be considered. Machine rooms that house exhaust fans should be ventilated to minimize exposure to exhaust effluent (e.g., leakage from the shaft openings of exhaust fans). Containment Device Leakage Materials and Construction Leakage of the containment devices themselves must also be considered. For example, in vertical sash fume hoods, the clearance to allow sash movement creates an opening from the top of the fume hood into the ceiling space or area above. Air introduced through this leakage path also contributes to the exhaust airstream. The amount that such leakage sources contribute to the exhaust airflow depends on the fume hood design. Edge seals can be placed around sash tracks to minimize leaks. Although the volumetric flow of air exhausted through a fume hood is based on the actual face opening, appropriate allowances for air introduced through paths other than the face opening must be included. The selection of materials and the construction of exhaust ductwork and fans depend on the following: · Nature of the effluents · Ambient temperature · Ambient relative humidity · Effluent temperature · Length and arrangement of duct runs · Constant or intermittent flow · Flame spread and smoke developed ratings · Duct velocities and pressures Effluents may be classified generically as organic or inorganic chemical gases, vapors, fumes, or smoke; and qualitatively as acids, alkalis (bases), solvents, or oils. Exhaust system ducts, fans, damp- ers, flow sensors, and coatings are subject to (1) corrosion, which destroys metal by chemical or electrochemical action; (2) dissolu- tion, which destroys materials such as coatings and plastics; and (3) melting, which can occur in certain plastics and coatings at ele- vated temperatures. Common reagents used in laboratories include acids and bases. Common organic chemicals include acetone, ether, petroleum ether, chloroform, and acetic acid. The HVAC engineer should consult | {}
ab02e1fe-2125-4de9-b918-4fd0cf380434 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Laboratories 17.11 with the safety officer and scientists, because the specific research to be conducted determines the chemicals used and therefore the nec- essary duct material and construction. The ambient temperature in the space housing the ductwork and fans affects the condensation of vapors in the exhaust system. Con- densation contributes to the corrosion of metals, and the chemicals used in the laboratory may further accelerate corrosion. Ducts are less subject to corrosion when runs are short and direct, flow is maintained at reasonable velocities, and condensation is avoided. Horizontal ductwork may be more susceptible to corrosion if condensate accumulates in the bottom of the duct. Applications with moist airstreams (cage washers, sterilizers, etc.) may require conden- sate drains. The design should include provisions to minimize joint or seam corrosion problems. If flow through the ductwork is intermittent, condensate may remain for longer periods because it will be unable to reevaporate into the airstream. Moisture can also condense on the outside of ductwork exhausting cold environmental rooms. Flame spread and smoke developed ratings, which are specified by codes or insurance underwriters, must also be considered when selecting duct materials. In determining the appropriate duct mate- rial and construction, the HVAC engineer should · Determine the types of effluents (and possibly combinations) handled by the exhaust system · Classify effluents as either organic or inorganic, and determine whether they occur in the gaseous, vapor, or liquid state · Classify decontamination materials · Determine the concentration of the reagents used and the tem- perature of the effluents at the hood exhaust port (this may be impossible in research laboratories) · Estimate the highest possible dew point of the effluent · Determine the ambient temperature of the space housing the exhaust system · Estimate the degree to which condensation may occur · Determine whether flow will be constant or intermittent (inter- mittent flow conditions may be improved by adding time delays to run the exhaust system long enough to dry the duct interior prior to shutdown) · Determine whether insulation, watertight construction, or sloped and drained ductwork are required · Select materials and construction most suited for the application Considerations in selecting materials include resistance to chem- ical attack and corrosion, reaction to condensation, flame and smoke ratings, ease of installation, ease of repair or replacement, and maintenance costs. Appropriate materials can be selected from standard references and by consulting with manufacturers of specific materials. Materi- als for chemical fume exhaust systems and their characteristics include the following: Galvanized steel. Subject to acid and alkali attack, particularly at cut edges and under wet conditions; cannot be field welded with- out destroying galvanization; easily formed; low in cost. Stainless steel. Subject to acid and chloride compound attack depending on nickel and chromium content of the alloy; relatively high in cost. The most common stainless steel alloys used for labo- ratory exhaust systems are 304L and 316L. Cost increases with increasing chromium and nickel content. Asphaltum-coated steel. Resistant to acids; subject to solvent and oil attack; high flame and smoke rating; base metal vulnerable when exposed by coating imperfections and cut edges; cannot be field welded without destroying coating; moderate cost. Epoxy-coated steel. Epoxy phenolic resin coatings on mild black steel or fluoropolymer coatings on stainless steel can be selected for particular characteristics and applications; they have been successfully applied for both specific and general use, but no one compound is inert or resistive to all effluents. Requires sand blasting to prepare the surface for a shop-applied coating, which should be specified as pinhole free, and field touch-up of coating imperfections or damage caused by shipment and installation; can- not be field welded without destroying coating; cost is moderate. Plastic-coated galvanized steel. Subject to corrosion at cut edges; cannot be field welded; easily formed; moderate in cost. Fiberglass. When additional glaze coats are used, this is partic- ularly good for acid applications, including hydrofluoric acid. May require special fire-suppression provisions. Special attention to hanger types and spacing is needed to prevent damage. Plastic materials. Have particular resistance to specific corro- sive effluents; limitations include physical strength, flame spread and smoke developed rating, heat distortion, and high cost of fabrication. Special attention to hanger types and spacing is needed to prevent damage. Borosilicate glass. For specialized systems with high exposure to certain chemicals such as chlorine. 3.3 FIRE SAFETY FOR VENTILA TION SYSTEMS Fire safety for ventilation systems is addressed in the different model building codes and in NFPA Standard 45. The HVAC designer needs to understand which codes apply based on project- specific requirements. The hazard classification of the exhaust air stream, requirements for fail-safe operation of dampers, system response on the detection of fire or smoke, appropriateness of installing fire dampers in exhaust air ductwork, and placement of fume hoods away from traffic and egress paths are some of the many factors that must be understood and addressed. 3.4 CONTROL Laboratory controls must regulate temperature and humidity, control and monitor laboratory safety devices that protect personnel, and control and monitor secondary safety barriers used to protect the environment outside the laboratory from laboratory operations. Reli- ability, redundancy, accuracy, and monitoring are important factors in controlling the lab environment. Many laboratories require precise control of temperature, humidity, and airflows. Components of the control system must provide the necessary accuracy and corrosion resistance if they are exposed to corrosive environments. Laboratory controls should provide fail-safe operation, which should be defined jointly with the safety officer. A fault tree can be developed to eval- uate the impact of the failure of any control system component and to ensure that safe conditions are maintained. Thermal Control Temperature in laboratories with a constant-volume air supply is generally regulated with a room temperature sensor and controller that positions control valve on a reheat coil in the supply air. In laboratories with a variable-volume ventilation system, room ex- haust device(s) are generally regulated as well. The room exhaust device(s) are modulated to handle greater airflow in the laboratory when additional cooling is needed. The exhaust device(s) may de- termine the total supply air quantity for the laboratory. Most microprocessor-based laboratory control systems can use proportional-integral-derivative (PID) algorithms to eliminate the error between the measured temperature and the temperature set point. Anticipatory control strategies increase accuracy in tem- perature regulation by recognizing the increased reheat require- ments associated with changes in the ventilation flow rates and adjusting the position of reheat control valves before the thermostat measures space temperature changes (Marsh 1988). Inc. ASHRAE, 2019 user. single for Licensed | {}
665cdee7-e6f7-4d2a-a51d-3163659588c0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 17.12 Constant-Air- V olume (CAV) Versus Variable-Air- Volume (VAV) Room Airflow Control Several factors can influence the decision of whether VAV or CAV airflow control in a laboratory is most appropriate, including required air change rates, density of exhausted containment devices, and the potential hazards related to the lab operations. Inc. ASHRAE, 2019 user. · Static pressure changes due to filter loading · Wet or dry cooling coils · Wear of fan belts that change fan speed · Position of chemical fume hood sash or sashes · Outdoor wind speed and direction · Position of doors and windows Many laboratories that are considered CA v systems are not truly constant. Even when the fume hoods operate continuously and are of the bypass type, considerable variations in airflow may occur. Variations in airflow result from single Current controls can achieve good conformance to the require- ments of a CA V system, subject to normal deviations in control per- formance (i.e., the dead band characteristics of the controller and the hysteresis present in the control system). The same is true for VA V systems, although they are more complex. Systems may be either uncontrolled or controlled. An uncontrolled CAV system can be designed with no automatic controls for airflow other than two- speed fan motors to reduce flow during unoccupied periods. These systems are balanced by manual dampers and adjustable drive pul- leys. They provide reasonable airflow rates relating to design values but do not provide true CAV under varying conditions, maintain constant fume hood face velocity, or maintain relative static pres- sures in the spaces. For laboratories that are not considered hazard- ous and do not have stringent safety requirements, uncontrolled CAV may be satisfactory. for Licensed For laboratories housing potentially hazardous operations (i.e., involving toxic chemicals or biological hazards), a true CA V or VAV system ensures that proper airflow and room pressure relationships are maintained at all times. A true CAV system requires volume controls on the supply and exhaust systems. The principal advantage of using a VA V system is its ability to (1) ensure that face velocities of chemical fume hoods are main- tained within a set range and (2) reduce energy use by reducing lab- oratory airflow. The appropriate safety officer and the users should concur with the choice ofV A v or CA v with reduced airflow during unoccupied periods. Consider giving laboratory users the ability to reset VA v systems to full airflow volume in the event ofa chemical spill. Education of the laboratory occupants in proper use of the system is essential. The engineer should recognize that the use of variable-volume exhaust systems may result in higher concentra- tions of contaminants in the exhaust airstream, which may increase corrosion, which influences the selection of materials. Room Pressure Control In most experimental work, the laboratory apparatus, fume hood, or biological safety cabinet is considered to be the primary method of containment. The facility is considered the secondary level of con- tainment. The laboratory envelope acts as the secondary containment bar- rier. It is important that the walls surrounding, and door openings into, the laboratory be of appropriate construction. Because main- taining an airtight seal is rarely practical, air pressure in the labo- ratory must be maintained slightly negative with respect to adjoining areas. Exceptions are sterile facilities or clean spaces that may need to be maintained at a positive pressure with respect to adjoining spaces. Positively pressurized spaces in which hazardous materials are used should have an anteroom or vestibule to maintain overall negative pressurization. 2019 ASHRAE Handbook-HVAC Applications (SI) Proper isolation is accomplished through the air balance/pres- sure relationship to adjacent areas. The pressure relationship is · Negative, for hazardous isolation ofhazardous or toxic operations (dirty operations), or · Positive, for protective isolation of precious or delicate operations (clean operations) Common methods of room pressure control include manual balancing, direct pressure control, volumetric flow tracking, and cascade control. All methods manipulate airflow into or out of the space; however, each method measures a different variable. Regardless of the method of space pressure control, the goal is to maintain an inward flow of air through small gaps in the secondary barrier (room envelope). In critical applications, airlocks (entry vestibules) may be required to ensure that pressure relationships are maintained as personnel enter or leave the laboratory. The air- locks have an outer and inner door, with a vestibule in between, allowing personnel to enter or exit the lab without a direct, open passage between the laboratory and the adjoining space. Normal operation, by practice or through interlocks, keeps one door closed as the second door is opened. If interlocks are necessary, take care to prevent personnel from being trapped in the vestibule in a system malfunction. The airlocks also serve as a buffer space between the laboratory and adjoining spaces, allowing personal protective equipment (PPE) to be donned or doffed, and also provide a con- venient location for storing lab coats and for hand wash sinks. Direct Pressure Control. This method measures the pressure differential across the room envelope and adjusts the amount of sup- ply air into the laboratory to maintain the required differential pres- sure. Challenges encountered include (1) maintaining the pressure differential when the laboratory door is open, (2) finding suitable sensor locations, (3) maintaining a well-sealed laboratory envelope, and (4) obtaining and maintaining accurate pressure sensing devices. The direct pressure control arrangement requires tightly constructed and compartmentalized facilities and may require a vestibule on entry/exit doors. Engineering parameters pertinent to envelope integrity and associated flow rates are difficult to predict. Because direct pressure control works to maintain the pressure differential, the control system automatically reacts to transient dis- turbances. Entry/exit doors may need a switch to disable the control system when they are open. Pressure controls recognize and com- pensate for unquantified disturbances such as stack effects, infiltra- tion, and influences of other systems in the building. Expensive, complex controls are not required, but the controls must be sensitive and reliable. In noncorrosive environments, controls can support a combination of exhaust applications, and they are insensitive to minimum duct velocity conditions. Successful pressure control pro- vides the desired directional airflow but cannot guarantee a specific volumetric flow differential. Factors that favor direct pressure control include the following: · High pressurization level (>10 Pa) and very tight construction · Complex set of relative pressurization requirements · Slow disturbances only (e.g., stack effect, filter loading) · Poor conditions for airflow measurement v olumetric Flow Tracking Control. This method measures both exhaust and supply airflow and controls the amount of supply air to maintain the desired pressure differential. v olumetric control requires controlling air at each supply and exhaust point. It does not recognize or compensate for unquantified disturbances such as stack effects, infiltration, and influences of other systems in the building. Flow tracking is essentially independent of room door op- eration. Engineering parameters are easy to predict, and extremely tight construction is not required. Balancing is critical and must be addressed across the full operating range. The flow offset required should be greater than the accuracy of the flow measurement and | {}
e592393f-3667-40e2-b07f-ae4dec35a6b2 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Laboratories 17.13 associated control error. The error in offset airflow should be eval- uated to ensure that the space remains under proper offset control. Controls may be located in corrosive and contaminated environ- ments; however, the controls may be subject to fouling, corrosive attack, and/or loss of calibration. Flow measurement controls are sensitive to minimum duct velocity conditions. Volumetric control may not guarantee directional airflow. Factors that favor volumetric flow tracking include the follow- ing: · Low pressurization level (usually 2 to 10 Pa), less tight construc- tion · Fast disturbances (e.g., VA V fume hoods) · Simple set of relative pressurization levels (one or two levels) Cascade Control. This method measures the pressure differen- tial across the room envelope to reset the flow tracking differential set point. Cascade control includes the merits and shortcomings of both direct pressure control and flow tracking control; however, first cost is greater, and the control system is more complex to oper- ate and maintain. It is used less often than the two preceding meth- ods, but its popularity is increasing. The trend toward tighter envelope construction makes it more challenging to select effective flow offset values in pressurized suites, but using cascade control makes this selection easier. Factors that favor cascade control include fast disturbances and a complex set of relative pressurization levels. Fume Hood Control Criteria for fume hood control differ depending on the type of hood. The exhaust volumetric flow is kept constant for standard, auxiliary air, and air-bypass fume hoods. In variable-volume fume hoods, exhaust flow is varied to maintain a constant face velocity. The fume hood control method should be selected in consultation with the safety officer. Regardless of control decisions, fume hoods must be equipped with an airflow indicator for the hood user. Constant-volume fume hoods can further be split into pressure- dependent or pressure-independent systems. Although simple in configuration, the pressure-dependent system is unable to adjust the damper position in response to any fluctuation in system pressure across the exhaust damper. Variable-volume fume hood control strategies can be grouped into two categories. The first either measures the air velocity entering a small sensor in the wall of the fume hood or determines face veloc- ity by other techniques. The measured variable is used to infer the average face velocity based on an initial calibration. This calculated face velocity is then used to modulate the exhaust flow rate to main- tain the desired face velocity. The second category of variable-volume fume hood control mea- sures the fume hood sash opening and computes the exhaust flow requirement by multiplying the sash opening by the face velocity set point. The controller then adjusts the exhaust device (e.g., by a variable-frequency drive on the exhaust fan or a damper) to maintain the desired exhaust flow rate. The control system may measure the exhaust flow for closed-loop control, or it may not measure exhaust flow in an open-loop control by using linear calibrated flow control dampers. 3.5 STACK HEIGHTS AND AIR INT AKES Laboratory exhaust stacks should release effluent to the atmo- sphere without producing undesirable high concentrations at fresh air intakes, operable doors and windows, and locations on or near the building where access is uncontrolled. Three primary factors that influence the proper disposal of effluent gases are stack/intake sepa- ration, stack height, and stack height plus momentum (plume height). Chapter 24 ofthe 201 7 ASHRAE Handbook-Fundamentals and Chapter 45 of this volume cover the criteria and formulas to cal- culate the effects of these physical relationships. For complex build- ings or buildings with unique terrain or other obstacles to the airflow around the building, either scale model wind tunnel testing or com- putational fluid dynamics should be considered. However, standard k- computational fluid dynamics methods as applied to airflow around buildings need further development (Castro 2003; Murakami et al. 1996; Zhou and Stathopoulos 1996). HVAC system designers who do not have the analytical skills required to undertake a disper- sion analysis should consider retaining a specialized consultant. Stack/Intake Separation Separation of the stack discharge and air intake locations allows the atmosphere to dilute the effluent. Separation is simple to calculate with the use of short to medium-height stacks; how- ever, to achieve adequate atmospheric dilution of the effluent, greater separation than is physically possible may be required, and the building roof near the stack will be exposed to higher concen- trations of the effluent. However, when stacks are much taller than the intake, the best location for the intake may be very close to the stack but this should evaluated on a case-by-case basis. Stack Height Chapter 45 describes a geometric method to determine the stack discharge height high enough above the turbulent zone around the building so that little or no effluent gas impinges on air intakes ofthe emitting building. This technique is conservative and generally requires tall stacks that may be visually unacceptable or fail to meet building code or zoning requirements. Also, this technique does not ensure acceptably low concentrations of effluents at air intakes (e.g., if there are large releases of hazardous materials or elevated intake locations on nearby buildings). A minimum stack height of 3 m is required by ASSE Standard Z9.5 and is recommended by Appendix A of NFPA Standard 45 to protect rooftop maintenance workers. However, a taller stack height may be necessary to ensure that harm- ful contaminants are not reentrained into nearby air intakes. Stack Height plus Vertical Momentum Concentrations at downwind locations are directly related to the height of the centerline of the plume. Plume height is a function of the physical stack height and plume rise (vertical momentum). To increase the plume height, increase the volumetric flow and/or the discharge velocity to increase the discharge momentum (Momen- tum flow = Density x V olumetric flow rate x V elocity), or increase the physical stack height. The momentum of a large vertical flow lifts the plume above the stack top, thereby potentially reducing the necessary physical height of the stack and making it easier to screen from view. This technique is particularly suitable when (1) many small exhaust streams can be clustered together or manifolded prior to the exhaust fan to provide the large volumetric flow and (2) out- door air can be added through automatically controlled dampers to provide constant exhaust vertical momentum under variable load. The drawbacks to the second arrangement are the amount of energy consumed to achieve the constant high vertical momentum and the added complexity of the controls to maintain constant volumetric flow rates. Dilution equations in Chapter 45 can be used to predict the performance of a particular stack design, or performance can be validated through wind tunnel testing. Current numerical proce- dures tend to have a high degree of uncertainty, and the results should be judged accordingly. Architectural Screens Rooftop architectural screens around exhaust stacks are known to adversely affect exhaust dispersion. In general, air intakes should not be placed within the same screen enclosure as laboratory exhausts. Petersen et al. (1997) describe a method of adjusting Inc. ASHRAE, 2019 user. single for Licensed | {}
5e50df98-0c1f-468f-ad83-094dc265663c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 17.14 2019 ASHRAE Handbook-HVAC Applications (SI) dilution predictions of Chapter 45 using a stack height adjustment factor, which is essentially a function of screen porosity. Criteria for Suitable Dilution An example criterion based on Halitsky (1988) dictates that the release of 7.5 L/s of pure gas through any stack in a moderate wind (5 to 30 km/h), from any direction with a near-neutral atmospheric stability (Pasquill Gifford Class C or D), must not produce concen- trations exceeding 3 mg/kg at any air intake. This criterion is meant to simulate an accidental release such as would occur in a spill of an evaporating liquid or after the fracture of the neck of a small lec- ture bottle of gas in a fume hood. The intent of this criterion is to limit the concentration of ex- hausted gases at the air intake locations to levels below the odor thresholds of gases released in fume hoods, excluding highly odor- ous gases such as mercaptans. Laboratories that use extremely haz- ardous substances should conduct a chemical-specific analysis based on published health limits. A more lenient limit may be jus- tified for laboratories with low levels of chemical usage. Project- specific requirements must be developed in consultation with the safety officer. The equations in Chapter 45 are presented in terms of dilution, defined as the ratio of stack exit concentration to receptor concentration. The exit concentration, and therefore the dilution re- quired to meet the criterion, varies with the total volumetric flow rate of the exhaust stack. For the preceding criterion, with the emis- sion of 7.5 L/s of a pure gas, a small stack with a total flow rate of 500 L/s will have an exit concentration of 7.5/500 or 15 000 mg/kg. A dilution of 1:5000 is needed to achieve an intake concentration of 3 mg/kg. A larger stack with a flow rate of 5000 L/s will have a lower exit concentration of7 .5/5000 or 1500 mg/kg and would need a dilution of only 1:500 to achieve the 3 mg/kg intake concentration. The preceding criterion is preferred over a simple dilution stan- dard because a defined release scenario (7.5 L/s) is related to a defined intake concentration (3 mg/kg) based on odor thresholds or health limits. A simple dilution requirement may not yield safe intake concentrations for a stack with a low flow rate. Adjacent Building Effects The influence of adjacent building effects was studied under ASHRAE research project RP-897 (Wilson et al. 1998). Several guidelines were developed from this project: · Avoid locating stacks near the edge of a roof. · With the emitting building upwind, an adjacent building will always have higher dilution on a lower roof than would occur on a roof at the emitting building's height. Ignoring the step-down in roof level will produce conservative designs. · If the lower adjacent building is upwind of the emitting building, it will block flow approaching the emitting building, producing lower velocities and recirculation cavities on the emitting build- ing roof and increasing dilution by factors of 2 to 10 on the emit- ting building. · Designers should increase either the physical stack height or the vertical momentum ofthe exhaust when the plume will be trapped in the recirculation cavity from a high upwind adjacent building. · When the adjacent building is higher than the emitting building, designers should try to avoid placing air intakes on the adjacent building at heights above the roof level of the emitting building. Also see Chapter 45 for more information. 4. APPLICATIONS 4.1 LABORATORY ANIMAL FACILITIES Laboratory animals must be housed in comfortable, clean, temperature- and humidity-controlled rooms. Animal welfare must be considered in the design; the air-conditioning system must pro- vide the macroenvironment (for the animal room) and microenvi- ronment (in the animal' s primary enclosure or cage) specified by the facility's veterinarian (Besch 1975; ILAR 2011; W oods 1980). Early and detailed discussions with the veterinarian regarding air- flow patterns, cage layout, and risk assessment help ensure a suc- cessful animal room HVAC design. The elimination of research variables (fluctuating temperature and humidity, drafts, and spread of airborne diseases) is another reason for a high-quality air-condi- tioning system. See Chapter 24 for additional information on envi- ronments for laboratory animals. Primary Uses of Animal Housing Facilities Primary uses of animal facilities include the following: · Acute (short-term) studies: generally less than 90 days in length, although the animal species and particular experiments involved could affect duration. Most frequently found in pharma- ceutical, medical, or other life science laboratories, and includes · Assays and screens · Immune-suppressed animals · Pharmacology and metabolism · Infectious disease · Chronic (long-term) studies: generally more than 90 days in length, although the species and experiment involved could affect the length. Includes · Toxicology · Teratology · Neurological · Quality control · Long-term holding of animals, including · Production of materials used primarily in pharmaceuticals · Breeding · Laboratory animals · Companion animals · Food and fiber animals · Agricultural studies, including food and fiber animals Regulatory Environment There are a number of regulations and guidelines that pertain to the housing of laboratory animals. Additional regulations cover the housing of animals that may be used in some way in the production of pharmaceuticals, testing for agricultural products, or used for quality control. Pertinent regulations, as found in the United States, are outlined below. Other countries have similar regulations that should be consulted when designing animal facilities located in that country. Regulations and guidelines include the following: · Code of Federal Regulations (CFR) 21 Part 58; Good Laboratory Practices for Nonclinical Laboratory Studies Part 210; Current Good Manufacturing Practice in Manufacture, Processing, Packing or Holding ofHuman and Veterinary Drugs · Guide for the Care and Use of Laboratory Animals, National Research Council · Biosafety in Microbiological and Biomedical Laboratories, Cen- ters for Disease Control (CDC). · The Animal Welfare Act of 1966 and as subsequently amended. Regulatory authority is vested in the Secretary ofthe U.S. Depart- ment of Agriculture (USDA) and implemented by the USDA 's Animal and Plant Health Inspection Service. · American Association for Accreditation of Laboratory Animal Care (AAALAC), a nonprofit organization to which many institu- tions and corporations belong. This group provides accreditation based upon inspections and reports from member groups. Many Inc. ASHRAE, 2019 user. single for Licensed | {}
ac6c4a14-eebb-4692-b578-5a3df489d3cc | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Laboratories 17.15 Table 1 Recommended Dry-Bulb Microenvironmental Temperatures for Common Laboratory Animals ¦ Animal ¦ Temperature, °C ¦ ¦ --- ¦ --- ¦ ¦ Mouse, rat, hamster, gerbil, guinea pig* ¦ 20 to 26 ¦ ¦ Rabbit ¦ 16 to 22 ¦ ¦ Cat, dog, nonhuman primate ¦ 18 to 29 ¦ ¦ Farm animals and poultry ¦ 16 to 27 ¦ Source: ILAR (2011). Reprinted with permission. * Dry-bulb room temperature settings for rodents are typically set below the animals' lower critical temperature (LCT) to avoid heat stress, and should reflect different species-specific LCT values. Animals should be provided with adequate resources for thermoregulation (nesting material, shelter) to avoid cold stress. Note: These ranges permit scientific personnel who will use the facility to select opti- mum conditions (set points). The ranges do not represent acceptable fluctuation ranges. organizations that build or maintain animal facilities adhere to AAALAC programs and HVAC engineers are expected to design to their guidelines. Local ordinances or user organization requirements may also apply. HVAC engineers should confirm which regulations are appli- cable for any project. Temperature and Humidity Due to the nature of research programs, air-conditioning design temperature and humidity control points may be required. Research animal facilities require more precise environmental control than farm animal or production facilities (as covered in Chapter 24) because variations affect the experimental results. A totally flexible system permits control of the temperature of individual rooms to within ±1 K for any set point in a range of 18 to 29°C. This flexibil- ity requires significant capital expenditure, which can be mitigated by designing the facility for selected species and their specific requirements. Table 1 lists dry-bulb temperatures recommended by ILAR (2011) for several common species. In the case of animals in con- fined spaces, the range of daily temperature fluctuations should be kept to a minimum. Relative humidity should also be controlled. ILAR (2011) suggests the acceptable range of relative humidity is 30 to 70%. Ventilation Providing 10 to 15 fresh air changes per hour in animal housing rooms is an acceptable guideline to maintain macroenvironmental air quality by constant-volume systems, and may also ensure microen- vironmental air quality (NRC 2011). Although this range is effective in many animal housing settings, it does not take into account the range of possible heat loads; species, size, and number of animals involved; type of primary enclosure and bedding; frequency of cage changing; room dimensions; or efficiency of air distribution both in the macroenvironment and between the macro- and microenviron- ments. In some situations, using such a broad guideline might over- ventilate a macroenvironment containing few animals, thereby wasting energy, or underventilate a microenvironment containing many animals, allowing heat, moisture, and pollutants to accumulate. VA V systems allow ventilation rates to be set in accordance with heat load and other variables. These systems offer considerable advantages in flexibility and energy conservation, but should always provide a minimum amount of air exchange, as recommended for general-use laboratories. Active sensing of contaminants in the sec- ondary enclosure and varying the air change rates based on the room environmental conditions is one approach that can be considered to meet these requirements more energy efficiently. For small-animal caging systems, studies suggest that room conditions have very little influence on the cage environments. ASHRAE research project RP-730 (Maghirang et al. 1995; Riskow- ski et al. 1996) found the following: Table 2 Heat Generated by Laboratory Animals ¦ Species ¦ Mass, kg ¦ Heat Generation, w per Normally Active Animal ¦ Heat Generation, w per Normally Active Animal ¦ Heat Generation, w per Normally Active Animal ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Species ¦ Mass, kg ¦ Sensible ¦ Latent ¦ Total ¦ ¦ Mouse ¦ 0.021 ¦ 0.325 ¦ 0.158 ¦ 0.484 ¦ ¦ Hamster ¦ 0.118 ¦ 1.18 ¦ 0.58 ¦ 1.76 ¦ ¦ Rat ¦ 0.28 ¦ 2.28 ¦ 1.12 ¦ 3.40 ¦ ¦ Guinea pig ¦ 0.41 ¦ 2.99 ¦ 1.47 ¦ 4.45 ¦ ¦ Rabbit ¦ 2.45 ¦ 11.5 ¦ 5.66 ¦ 17.1 ¦ ¦ Cat ¦ 3.00 ¦ 13.4 ¦ 6.59 ¦ 20.0 ¦ ¦ Nonhuman primate ¦ 5.44 ¦ 20.9 ¦ 10.3 ¦ 31.1 ¦ ¦ Dog ¦ 10.3 ¦ 30.8 ¦ 16.5 ¦ 47.2 ¦ ¦ Dog ¦ 22.7 ¦ 67.7 ¦ 36.3 ¦ 104.0 ¦ · No relationship between room ventilation rate and cage microen- vironments for shoebox and microisolator cages exists. In fact, 5 ach provided the same cage ventilation rates for shoebox cages as did 10 and 15 ach. Memarzadeh (2000) also found this lower air change rate satisfactory. · Diffuser type (perforated square versus radial) had only a small effect on shoebox cage ventilation rates. The radial diffuser pro- vided higher wire cage ventilation rates. · One high return provided the same cage ventilation rates as four high returns or as one low return. · Room size had no effect on cage ventilation rates. This research is further discussed in Chapter 24. In certain types of animal rooms, usually those used for long- term studies involving high-value work or animals, the outdoor air change rate is maintained at 10 to 15 per hour, but the total airflow in the rooms ranges from 90 to 150 ach (mass flow spaces similar to clean rooms). The air supply is generally terminal HEPA filtered to reduce the potential for disease. These rooms are energy inten- sive, and may not be required with newer filter capability and cag- ing systems. The air-conditioning load and flow rate for an animal room should be determined by the following factors: · Desired animal microenvironment (Besch 1975, 1980; ILAR 201 1) · Species of animal(s) · Animal population · Recommended ambient temperature (Table 1) · Heat produced by motors on special animal housing units (e.g., laminar flow racks or HEP A-filtered air supply units for venti- lated racks) · Heat generated by the animals (Table 2) Additional design factors include method of animal cage venti- lation; operational use of a fume hood or a biological safety cabinet during procedures such as animal cage cleaning and animal exam- ination; airborne contaminants (generated by animals, bedding, cage cleaning, and room cleaning); and institutional animal care standards (Besch 1980; ILAR 2011). Note that ambient conditions of the animal room might not reflect the actual conditions within a specific animal cage. Animal Heat Production Air-conditioning systems must remove the sensible and latent heat produced by laboratory animals. The literature concerning the metabolic heat production appears to be divergent, but new data are consistent. Current recommended values are given in Table 2. These values are based on experimental results and the following equation: ATHG = 2.5M where ATHG = average total heat gain, W per animal Inc. ASHRAE, 2019 user. single for Licensed | {}
6d660549-daa0-4fcd-a7cd-5d0f934418bb | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 17.16 2019 ASHRAE Handbook-HVAC Applications (SI) M = metabolic rate of animal, W per animal = 3.5 W0.75 W = mass of animal, kg Conditions in animal rooms must be kept constant. This may require year-round availability of refrigeration and, in some cases, dual/standby chillers and emergency electrical power for motors and control instrumentation. Storing critical spare parts is one alter- native to installing a standby refrigeration system. Design Considerations Ifthe entire animal facility or extensive portions ofit are perma- nently planned for species with similar requirements, the range of individual adjustments may be reduced. Each animal room or group of rooms serving a common purpose should have separate temperature and humidity controls. The animal facility and human occupancy areas should be conditioned separately. The human areas may use a return air HVAC system and may have unoccupied mode setback on weekends for energy conservation. Separation prevents exposure of personnel to biological agents, allergens, and odors from animal rooms. Control of air pressure in animal housing and service areas is important to ensure directional airflow. For example, quarantine, isolation, soiled equipment, and biohazard areas should be kept under negative pressure, whereas clean equipment and pathogen- free animal housing areas and research animal laboratories should be kept under positive pressure. Supply air outlets should not cause drafts on research animals. Efficient air distribution for animal rooms is essential; this may be accomplished effectively by supplying air through ceiling outlets and exhausting air at floor level (Hessler and Moreland 1984). Sup- ply and exhaust systems should be sized to minimize noise. A study by Neil and Larsen (1982) showed that predesign eval- uation ofa full-size mock-up of the animal room and its HV AC sys- tem was a cost-effective way to select a system that distributes air to all areas of the animal-holding room. Wier (1983) describes many typical design problems and their resolutions. Evaluate room air dis- tribution using ASHRAE Standard 113 procedures to evaluate drafts and temperature gradients. HVAC ductwork and utility penetrations must be minimized and sealed. Exposed ductwork is not generally recommended; however, if constructed of316 stainless steel, in a fashion to facilitate removal for cleaning, it can provide a cost-effective alternative. Joints around diffusers, grilles, and the like should be sealed. Exhaust air grilles with 25 mm washable or disposable filters are normally used to prevent animal hair and dander from entering the ductwork. Noise from the HVAC system and sound transmission from nearby spaces should be evaluated. Sound control methods such as separate air-handling systems or sound traps should be used as required. Multiple-cubicle animal rooms enhance the operational flexibil- ity of the animal room (i.e., housing multiple species in the same room, quarantine, and isolation). Each cubicle should be treated as ifit were a separate animal room, with air exchange/balance, tem- perature, and humidity control. Caging Systems Animal facilities use a number of different caging systems that can significantly affect the environment within the cage or the total heat load in the room. The purpose of the caging systems is to · Protect the health and wellbeing of the animals · Protect support staff from antigens released or shed by the animals · Minimize exposure of animals to pheromones released by other animals in the space To provide the appropriate design, the HVAC engineer must be aware of the type of caging system to be used. Some common cag- ing systems include the following: · Cage boxes made of sheet metal, plastic, or wire mesh, with the space inside the cage open to the room so the room 's macroenvi- ronment is essentially identical to the cage , s microenvironment. · Cage boxes made primarily of plastic, with the top shielded from the room by a filter material to provide some level of isolation from the room. The filter is usually not sealed to the cage, so some open space between the room and the interior of the cage remains. Exchange of air, vapors, particulates, and gases between the room and the cage interior does occur, but the rate of exchange is reduced by the filter. The microenvironment of the interior of the cage is usually different from that of the room. · Plastic and wire cages that are part of a cage rack assembly, which provides varying degrees of isolation from the room. These usu- ally provide filtered (generally HEPA-filtered) air directly to each individual or shelf of cage boxes. In some cases, both a fan-pow- ered supply and an exhaust unit are used. In other cases, cage units are connected to the facility exhaust system to provide airflow. Facilities with this kind of caging system must be designed to accommodate the heat gain in the space if the exhaust is released in the room. Some heat gain may be excluded ifthe caging assem- bly is connected directly to the facility exhaust system. When the facility is used to provide the exhaust by direct connection to the caging assembly, the design must include provisions to control the airflow to ensure that the overall proper airflow and relative static pressure of the room and each cage rack assembly is main- tained, especially when caging and rack connections may be changed over time. The temperature and specific humidity in each cage will be higher than the ambient conditions of the room. 4.2 ANCILLARY SPACES FOR ANIMAL LABORATORIES In addition to animal holding rooms, a facility intended to pro- vide for an animal colony generally requires other areas, such as · Cage washer: Usually provided with some temperature control to minimize heat stress for occupants. In addition, specific exhaust hoods and separate exhaust ductwork should be consid- ered for the space and equipment. · Feed storage: Usually provided with temperature and humidity control to protect quality and shelf life of feed. · Diagnostic laboratory: Usually provided with laboratory-quality air conditioning. · Treatment laboratory: Usually provided with laboratory-quality air conditioning. · Quarantine spaces: To separate incoming animals from the remainder of the colony until their health can be evaluated. These rooms are frequently located near the receiving location. Animal- room-quality air conditioning is provided. · Surgery suite: Sterile-quality air conditioning is provided. The suites frequently have provisions to exhaust anesthetic gases. · Necropsy laboratory: Usually provided with laboratory-quality air conditioning and frequently fitted with special exhaust tables or other means of protecting laboratory workers from exposure to chemical preservatives or biological contamination. For high-risk or high-hazard work, Type III biological safety cabinets may be provided. · Waste-holding room: Usually only provided with heating and ventilation, but maintained at negative pressure relative to adja- cent areas. When used to store carcasses, a refrigerated storage unit of appropriate size should be provided. 4.3 CONTAINMENT LABORA TORIES With the initiation of biomedical research involving recombi- nant DNA technology, federal guidelines on laboratory safety were published that influence design teams, researchers, and others. Inc. ASHRAE, 2019 user. single for Licensed | {}
b5bac215-8eeb-4e99-b256-4538a1a7dea0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Laboratories 17.17 Containment describes safe methods for managing hazardous chemicals and infectious agents in laboratories. The three elements of containment are laboratory operational practices and proce- dures, safety equipment, and facility design. Thus, the HVAC design engineer helps decide two of the three containment ele- ments during the design phase. In the United States, the U.S. Department of Health and Human Services (DHHS), Centers for Disease Control and Prevention (CDC), and National Institutes of Health (NIH) classify biological laboratories into four levels (Biosafety Levels 1 to 4) listed in DHHS (1999). The USDA Agricultural Research Service (ARS) Manual 242.1 (ARS 2012) similarly classifies biological laborato- ries, and also identifies a BSL 3Ag containment level. Biosafety Level 1 Biosafety Level 1 is suitable for work involving well-known agents not thought to consistently cause disease in healthy adult humans, and of minimal potential hazard to laboratory personnel and the environment. The laboratory is not necessarily separated from the general traffic patterns in the building. Work is generally conducted on open benchtops using standard microbiological prac- tices. Special containment equipment is neither required nor gener- ally used. The laboratory can be cleaned easily and contains a sink for washing hands. Federal guidelines for these laboratories contain no specific HVAC requirements. Biosafety Level 2 Biosafety Level 2 is suitable for work involving agents of mod- erate potential hazard to personnel and the environment. Laboratory access is limited when certain work is in progress. The laboratory can be cleaned easily and contains a sink for washing hands. Bio- logical safety cabinets (Class I or IIA2) are used when · Procedures with a high potential for creating infectious aerosols are conducted. These include centrifuging, grinding, blending, vigorous shaking or mixing, sonic disruption, opening containers ofinfectious materials, inoculating animals intranasally, and har- vesting infected tissues or fluids from animals or eggs. · High concentrations or large volumes of infectious agents are used. Federal guidelines for these laboratories contain minimum facility standards. At this level of biohazard, most research institutions have a full- time safety officer (or safety committee) who establishes facility standards. The federal guidelines for Biosafety Level 2 contain no specific HVAC requirements; however, typical HVAC design crite- ria can include the following: · 100% outdoor air systems · 6 to 15 air changes per hour · Directional airflow into the laboratory rooms · Site-specified hood face velocity at fume hoods (many institu- tions specify 0.4 to 0.5 m/s) · An assessment of research equipment heat load in a room. · Inclusion of biological safety cabinets Most biomedical research laboratories are designed for Bio- safety Level 2. However, the laboratory director must evaluate the risks and determine the correct containment level before design begins. Biosafety Level 3 Biosafety Level 3 applies to facilities in which work is done with indigenous or exotic agents that may cause serious or poten- tially lethal disease as a result of exposure by inhalation. The Bio- safety Level 3 laboratory uses a physical barrier of two sets of self- closing doors to separate the laboratory work area from areas with unrestricted personnel access. This barrier reinforces biological containment to within the laboratory work area. The ventilation system must be single-pass, nonrecirculating, and configured to maintain the laboratory at a negative pressure rel- ative to surrounding areas. Audible alarms and visual monitoring devices are recommended to notify personnel ifthe laboratory pres- sure relationship changes from negative to positive. The user may wish to have alarms reported to a remote, constantly monitored location. Gastight dampers are required in the supply and exhaust ductwork to allow decontamination of the laboratory. Ductwork between these dampers and the laboratory must also be gastight. All penetrations of the Biosafety Level 3 laboratory envelope must be sealable for containment and to facilitate gaseous decontamination of the work area. All procedures involving the manipulation of infectious materi- als are conducted inside biological safety cabinets. The engineer must ensure that the connection of the cabinets to the exhaust system does not adversely affect performance of either cabinets or exhaust system. Refer to the section on Biological Safety Cabinets for further discussion. Exhaust air from biological safety cabinets and/or the laboratory work area may require HEPA filtration. Review the need for filtra- tion or special exhaust handling from any scientific equipment with the appropriate safety officers. If required, HEPA filters should be equipped with provisions for bag-in, bag-out filter handling systems and gastight isolation dampers for biological decontamination of the filters. Biosafety Level 4 Biosafety Level 4 is required for work with dangerous and exotic agents that pose a high risk of aerosol-transmitted laboratory infec- tions and life-threatening disease. HVAC systems for these areas have stringent design requirements that must be determined by the biological safety officer. Design ofLevel 4 laboratories requires sig- nificant specialization and understanding of best practices. Biosafety Level 3Ag Biosafety Level 3Ag is required for work with certain biological agents in large animal species. Using the containment features of the standard BSL 3 facility as a starting point, BSL 3Ag facilities are specifically designed to protect the environment by including almost all of the features ordinarily used for BSL 4 facilities as enhancements. All BSL 3Ag containment spaces must be designed, constructed, and certified as primary containment barriers. 4.4 SCALE-UP LABORA TORIES Scale-up laboratories are defined differently depending on the nature and volume of work being conducted. For laboratories per- forming recombinant DNA research, large-scale experiments gen- erally involve vessels between 10 and 100 L or more. A chemical or biological laboratory is defined as scale-up when the principal hold- ing vessels are glass or ceramic. When the vessels are constructed primarily ofmetals, the laboratory is considered a pilot plant, which this chapter does not address. The amount of experimental materials present in scale-up laboratories is generally significantly greater than the amount found in the small-scale laboratory. Experimental equipment is also larger and therefore requires more space; these may include larger chemical fume hoods or reaction cubicles that may be of the walk-in type. Significantly higher laboratory airflow rates are needed to maintain the face velocity of the chemical fume hoods or reaction cubicles, although their size frequently presents problems of airflow uniformity over the entire face area. Walk-in hoods are sometimes entered during an experimental run, so provi- sions for breathing-quality air stations and other forms of personnel protection should be considered. Environmental containment or the Inc. ASHRAE, 2019 user. single for Licensed | {}
b6b62307-317e-437e-9c92-d64976a6f154 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 17.18 2019 ASHRAE Handbook- -HVAC Applications (SI) ability to decontaminate the laboratory, the laboratory exhaust air- stream, or other effluent may be needed in the event of an accidental discharge. Scale-up laboratories may be in operation for sustained periods. For large walk-in hoods or reaction cubicles, the large volume of exhaust air required and the simultaneous requirement for supply air can result in temperature gradient problems in the space. Large hoods, similar to what sometimes are called "California hoods, may also be provided in scale-up laboratories. These hoods are large in volume and height, provide access on multiple sides, and can be customized using standard components. Before begin- ning any custom hood design, the HVAC engineer, working with the user, should first determine what activities will be conducted. Then the HVAC engineer can develop a custom hood design that considers · What access is required for setup of experimental apparatus · How the hood is expected to function during experimental runs · Which doors or sashes should be open during a run · Safety and ergonomic issues · What features should be incorporated · Airflow required to achieve satisfactory containment Testing and balancing criteria should also be defined early in the design process. Mockups and factory testing of prototypes should be considered to avoid problems with installed hoods. 4.5 TEACHING LABORATORIES Laboratories in academic settings can generally be classified as either those used for instruction or those used for research. Research laboratories vary significantly depending on the work being per- formed; they generally fit into one of the categories of laboratories described previously. The design requirements for teaching laboratories also vary based on their function. The designer should become familiar with the specific teaching program, so that a suitable hazard assessment can be made. For example, the requirements for the number and size of fume hoods vary greatly between undergraduate inorganic and graduate organic chemistry teaching laboratories. Unique aspects of teaching laboratories include the need ofthe instructor to be in visual contact with the students at their work stations and to have ready access to the controls for the fume hood operations and any safety shutoff devices and alarms. Frequently, students have not received extensive safety instruction, so easily understood controls and label- ing are necessary. Because the teaching environment depends on verbal communication, sound from the building ventilation system is an important concern. See Lewis (2007) for additional consider- ations. 4.6 CLINICAL LABORA TORIES Clinical laboratories are found in hospitals and as stand-alone operations. Work in these laboratories generally consists of handling human specimens (blood, urine, etc.) and using chemical reagents for analysis. Some samples may be infectious; because itis impossible to know which samples may be contaminated, good work practices require that all be handled as biohazardous materials. The primary protection of the staff at clinical laboratories depends on the techniques and laboratory equipment (e.g., biological safety cabinets) used to control aerosols, spills, or other inadvertent releases of samples and reagents. People outside the laboratory must also be protected. The building HVAC system can provide additional protection with suitable exhaust, ventilation, and filtration. The HV AC engineer is responsible for providing an HV AC system that meets the biolog- ical and chemical safety requirements. The engineer should consult with appropriate senior staff and safety professionals to ascertain what potentially hazardous chemical or biohazardous conditions will be in the facility and then provide suitable engineering controls to minimize risks to staff and the community. Appropriate laboratory staff and the design engineer should consider using biological safety cabinets, chemical fume hoods, and other specific exhaust systems. 4.7 RADIOCHEMISTRY LABORA TORIES In the United States, laboratories located in Department of Energy (DOE) facilities are governed by DOE regulations. All other laboratories using radioactive materials are governed by the Nuclear Regulatory Commission (NRC), state, and local regulations. Other agencies may be responsible for the regulation of other toxic and carcinogenic materials present in the facility. Laboratory contain- ment equipment for nuclear processing facilities are treated as pri- mary, secondary, or tertiary containment/confinement zones, depending on the level of radioactivity anticipated for the area and the materials to be handled. Chapter 28 has additional information on nuclear laboratories. 4.8 OPERA TION AND MAINTENANCE During long-term research studies, laboratories may need to maintain design performance conditions, with no interruptions, for long periods. Even when research needs are not so demanding, systems that maintain air balance, temperature, and humidity in lab- oratories must be highly reliable, with a minimal amount of down- time. The designer should work with operation and maintenance personnel, as well as users, early in the design of systems to gain their input and agreement. System components must be of adequate quality to achieve reli- able HV AC operation, and they should be reasonably accessible for maintenance. Laboratory work surfaces should be protected from possible leakage of coils, pipes, and humidifiers. Changeout of sup- ply and exhaust filters should require minimum downtime. Centralized monitoring of laboratory variables (e.g., pressure differentials, face velocity of fume hoods, supply flows, and exhaust flows) is useful for predictive maintenance of equipment and for ensuring safe conditions. For their safety, laboratory users should be instructed in the proper use of laboratory fume hoods, safety cabi- nets, ventilated enclosures, and local ventilation devices. They should be trained to understand the operation of the devices and the indicators and alarms that show whether they are safe to operate. Users should request periodic testing of the devices to ensure that they and the connected ventilation systems are operating properly. Personnel who know the particular nature of the contaminants in a given laboratory should be responsible for decontamination of equipment and ductwork before they are turned over to mainte- nance personnel for work. Maintenance personnel should be trained to keep laboratory systems in good operating order and should understand the critical safety requirements of those systems. Schedule preventive mainte- nance of equipment and periodic checks of air balance. High- maintenance items should be placed outside the actual laboratory (in service corridors or interstitial space) to reduce disruption of laboratory operations and exposure of the maintenance staff to lab- oratory hazards. Maintenance personnel must be aware of and trained in procedures for maintaining good indoor air quality (IAQ) in laboratories. Many IAQ problems have been traced to poor main- tenance due to poor accessibility (W oods et al. 1987). 4.9 ENERGY Because of the nature of the functions they support, laboratory HVAC systems consume large amounts of energy (high flow rates; high static pressure filtration; critical cooling, heating, and humi- dification). Efforts to reduce energy use must not compromise standards established by safety officers. Typically, HVAC systems Inc. ASHRAE, 2019 user. single for Licensed | {}
cfdff7e4-b94a-487c-94c4-cc90ad0ae7e5 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Laboratories 17.19 supporting laboratories and animal areas use 100% outdoor air and operate continuously. All HVAC systems serving laboratories can benefit from energy reduction techniques that are either an integral part of the original design or added later. Energy reduction tech- niques should be analyzed in terms of both appropriateness to the facility and economic payback. Energy-efficient design is an iterative process that begins with establishing communication among all members of the design team. Each design discipline has an effect on the energy load. On a macro scale, air change rate, building orientation, window shading de- vices, and high-performance envelopes offer opportunity for energy use reduction. On a micro scale, for example, the choice of a light- ing system can affect sensible heat gain. Energy-efficient designs should recognize the variability of exhaust, envelope, and equip- ment loads and use systems that respond appropriately and perform efficiently during partial-load conditions. The HVAC engineer must understand and respond to the scien- tific requirements of the facility. Research requirements typically include continuous control of temperature, humidity, relative static pressure, and air quality. Energy reduction systems must maintain required environmental conditions during both occupied and unoc- cupied modes. Energy Efficiency Energy can be used more efficiently in laboratories by reducing exhaust air requirements. One way to achieve this is to use variable- volume control of exhaust air through the fume hoods to reduce exhaust airflow when the fume hood sash is not fully open. Recent changes in ASSE Standard Z9.5 allow a much lower fume hood minimum flow rate with variable-volume hoods, depending on sys- tem design and aspects of laboratory operations. Any airflow con- trol must be integrated with the laboratory control system, described in the section on Control, and its setting and operation must not jeopardize the safety and function of the laboratory. Fume hood selection also affects exhaust airflow requirements and energy consumption. Modern fume hood designs use several techniques to reduce airflow requirements, including reduced-face- opening sashes and specially designed components that allow oper- ation with reduced inflow velocities. These reduced-face-opening sash hoods or low-capture-velocity hoods may reduce overall air- flow requirements to the degree that additional variable-volume controls may not be justifiable. When considering these features, it is important to obtain approval of laboratory occupants and safety personnel. Energy efficiency in laboratories and other buildings depends on many examples of dynamically adjusting consumption to match changing needs, rather than simply running systems at constant out- put. Laboratory ventilation is part of this trend. Ventilation designers and safety professionals attempt to take scientific, quantitative approach to setting airflow levels, but they face many unknown factors. They are forced to make assumptions and exercise judgment. This leads to conservatively selected venti- lation rates. Dynamic ventilation eliminates some of the uncer- tainty by using real-time information, making it possible to lower ventilation rates without sacrificing a conservative approach. It is not necessary to set one constant ventilation rate, based only on information available at design time: a range of rates can be selected, with the specific value determined according to informa- tion gained in operation (e.g., presence or absence of lab workers [ventilation setback], or measured concentration of selected con- taminants in the room air [demand-controlled ventilation]; these two example strategies are completely complementary, and can deliver benefits when used together or separately). Reducing ventilation requirements in laboratories and vivariums based on real-time sensing of contaminants in the room environ- ment offers opportunities for energy conservation. This approach can potentially safely reduce lab air change rates to as low as 2 ach when the lab air is clean and the fume hood exhaust or room cool- ing load requirements do not require higher airflow rates. Sharp (2010) showed that lab rooms are on average clean of contaminants about 98% of the time. With fixed ventilation rates, engineers are forced to design for the 2% of the time when high flow is needed; dynamic ventilation takes advantage of the 98% of the time that it is not. Using a reduced ventilation rate when the laboratory is unoccu- pied can save significant amounts of energy. The savings potential that justifies a ventilation setback depends on the amount that the ventilation can be reduced and the amount of reliably unoccupied operating time. To use it properly, ventilation designers need to confirm that premise applies: that is, when the workers cease their activities and leave the laboratory, the contamination hazard is sig- nificantly reduced. The following design steps should be considered when designing unoccupied setback ventilation systems: · Determine whether the unoccupied period presents an opportu- nity to reduce ventilation. This depends on how the lab is used and its condition at the end of the day. The designer should work with the responsible health and safety professional and the lab users to establish that their work practices lead to reduced hazard when the room is unoccupied. Lab processes that continue unattended or erratic occupancy patterns may eliminate the opportunity. · When using an unoccupied setback approach, select the minimum flow rates that apply during occupied and unoccupied periods. This step still requires making assumptions. Combining contami- nant sensing with setback can allow lower values for both periods. · A trigger approach also needs to be selected to inform the control system when to switch between occupied and unoccupied set- tings. This is a common BAS function implemented in many familiar ways: schedules, occupancy sensors, or manual switches. It is important to select the trigger or combination of triggers that work effectively for the space. · Consider an indicator for users so that anyone in the room or entering the room knows that the ventilation system is in the cor- rect mode. Train workers on the meaning of the airflow indicator and the procedure to follow if the wrong mode is indicated. · Consider connecting room HVAC operation with access control to reduce the chance oflow ventilation rates when a worker is present. · Consider coordinating HVAC operation with lighting controls and temperature setback to maximize the value of occupancy- sensing components. Laboratory exhaust systems often use constant-speed fans to dis- charge exhaust air at a constant velocity to prevent cross contami- nation with supply air intakes. Alternative approaches to reduce the considerable energy consumption of exhaust fans include using taller stacks, and real-time reduction of exhaust exit velocity based on sensing either wind direction, velocity, or reduced contaminant levels in the exhaust fan plenum. Room cooling approaches, such as hydronic cooling using local fan-coil units or noncondensing, chilled radiant ceiling panels, pas- sive chilled beams, or active chilled beams offer opportunities for energy conservation. These approaches decouple the room cooling function from the ventilation air requirements, potentially reducing outdoor air needs, overall HVAC capacity, and reheat energy. Less energy is needed to pump chilled water than to provide the equivalent amount of airflow required for a given level of cooling. Note that some form of dew-point sensing and possibly condensation monitoring is recommended (Rumsey and Weale 2007) for noncon- densing hydronic cooling approaches. Chapter 5 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment and Chapter 47 of this volume offer more information on controlling chilled beams. Inc. ASHRAE, 2019 user. single for Licensed | {}
d1e88962-1f3c-4c18-b483-2d9726f57c6b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 17.20 2019 ASHRAE Handbook-HVAC Applications (SI) Often, offices spaces have recirculating air-handling systems, and laboratory spaces have separate 100% outdoor-air-handling systems. Significant energy savings can be achieved by using com- bined air-handling systems to serve both offices and laboratories: air supplied to offices can be recirculated, and air supplied to the labo- ratory spaces exhausted. This approach, on both a peak and annual basis, reduces the amount of outdoor air that must be processed and the associated heating and cooling energy. Energy Recovery Energy can often be recovered economically from the exhaust airstream in laboratory buildings with large quantities of exhaust air. Many energy recovery systems are available, including rotary air-to-air energy exchangers or heat wheels, coil energy recovery loops (runaround cycle), twin tower enthalpy recovery loops, heat pipe heat exchangers, fixed-plate heat exchangers, and thermosi- phon heat exchangers, many of which can be coupled with direct evaporative cooling. Some of these technologies can be combined with indirect evaporative cooling for further energy recovery. See Chapters 26 and 41 of the 2016 ASHRAE Handbook-HVAC Sys- tems and Equipment for more information. Concerns about using energy recovery devices in laboratory HVAC systems include (1) the potential for cross-contamination of chemical and biological materials from exhaust air to the intake air- stream, and (2) the potential for corrosion and fouling of devices located in the exhaust airstream. It is important to understand the potential hazard of the exhaust air stream and to select the style and materials of the energy recovery equipment appropriately. Energy recovery is also possible for hydronic systems associated with HVAC. Rejected heat from centrifugal chillers can be used to produce low-temperature reheat water. Potential also exists in plumbing systems, where waste heat from washing operations can be recovered to heat makeup water. Sustainable Design Laboratories present unique challenges and opportunities for energy efficiency and sustainable design. Laboratory systems are complex, use significant energy, have health and life safety implica- tions, need long-term flexibility and adaptability, and handle poten- tially hazardous effluent with associated environmental impacts. Therefore, before implementing energy-efficiency and sustainable- design protocols, the engineer must be aware of the effects of these measures on the laboratory processes, which affect the safety of the staff, environment, and scientific procedures. Several laboratory facilities have achieved high recognition for energy efficiency and sustainable design. Sustainable design fea- tures specific to laboratory facilities include all aspects of design, construction, and operations. These features include (1) managing air and water effluent on the site; (2) reducing water used by labo- ratory processes; (3) rightsizing equipment and improving its energy efficiency; (4) hazardous material handling; ⑤ ventilation system enhancements, including modeling airflow patterns, fume hood testing, and additional safety alarming; and ⑥ laboratory- specific opportunities for innovation. 4.10 COMMISSIONING In addition to HVAC systems, electrical systems and chemical handling and storage areas should be commissioned. Training of technicians, scientists, and maintenance personnel is a critical aspect of the commissioning process. Users should understand the systems and their operation. It should be determined early in the design process whether any laboratory systems must comply with Food and Drug Administra- tion (FDA) regulations because these systems have additional design, commissioning, and potential validation requirements. Commissioning is defined in Chapter 43; the process is outlined in ASHRAE Guidelines 0 and 1.1, and further defined in ANSI/ ASHRAE/IES Standard 202. Laboratory commissioning can be more demanding than that described in ASHRAE guidelines and includes systems that are not associated with other occupancies. Requirements for commissioning should be clearly understood by all participants, including the contractors and the owner's personnel. Roles and responsibilities should be defined, and responsibilities for documenting results should be established. Laboratory commissioning starts with the intended use of the laboratory, as described in the owner's project requirements (OPR), and should include development of a commissioning plan, as out- lined in the ASHRAE guidelines. The start-up and prefunctional testing of individual components should come first; after individual components are successfully tested, the entire system should be functionally tested. This requires verification and documentation that the design meets applicable codes and standards and that it has been constructed in accordance with the design intent and owner's project requirements. Most facilities require integrated systems test- ing to verify that the HVAC system is properly coordinated with other systems, such as fire alarm or emergency power systems. Before general commissioning begins, obtain the following data: · Owner's project requirements · Basis of design (BOD) that includes the intent of system opera- tion · Definition of the use ofthe laboratory and an understanding of the work being performed · Complete set of the laboratory utility drawings · Equipment requirements · All start-up and prefunctional test results For HVAC and associated integrated system commissioning, the following should be verified and documented: · Manufacturer' s requirements for airflow for biological safety cab- inets and laminar flow clean benches have been met. · Exhaust system configuration, damper locations, and perfor- mance characteristics, including any required emission equip- ment, are correct. · Approved test and balance report. · Control system operates as specified. Controls include fume hood alarm; miscellaneous safety alarm systems; fume hood and other exhaust airflow regulation; laboratory pressurization control sys- tem; laboratory temperature control system; and main ventilation unit controls for supply, exhaust, and heat recovery systems. Control system performance verification should include speed of response, accuracy, repeatability, turndown, and stability. · Desired laboratory pressurization relationships are maintained throughout the laboratory, including entrances, adjoining areas, air locks, interior rooms, and hallways. Balancing terminal devices within 10% of design requirements will not provide ade- quate results. Additionally, internal pressure relationships can be affected by airflow around the building. See Chapter 24 of the 2017 ASHRAE Handbook-Fundamentals for more information. · Fume hood containment performance is within specification. ASHRAE Standard 110 provides criteria for this evaluation. · Dynamic response of the laboratory's control system is satisfac- tory. One method of testing the control system is to open and shut laboratory doors during fume hood performance testing. · System fault tree and failure modes are as specified, including life safety fan system shutdown impact on proper provisions for egress from the building within allowable limits of door-opening force requirements · Standby electrical power systems function properly. · Design noise criterion (NC) levels of occupied spaces have been met. Inc. ASHRAE, 2019 user. single for Licensed | {}
03bd3042-e850-40f9-b29f-31ef10ee8b33 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Laboratories 17.21 Training of facilities staff and laboratory occupants should also be considered part of the commissioning and design process. Training should address both the operation of individual system components and the overall system. 4.11 ECONOMICS In laboratories, HVAC systems make up a significant part (often 30 to 50%) of the overall construction budget. The design criteria and system requirements must be reconciled with the budget allot- ment for HVAC early in the planning stages and continually throughout the design stages to ensure that the project remains within budget. Every project must be evaluated on both its technical features and its economics. The following common economic terms are dis- cussed in Chapter 37 and defined here as follows: Initial cost: Costs to design, install, and test an HVAC system such that it is fully operational and suitable for use. Operating cost: Cost to operate a system (including energy, maintenance, and component replacements) such that the total sys- tem can function until the end of its normal useful life. Life-cycle cost: Cost related to the total cost over the life of the HVAC system, including initial capital cost, considering the time value of money. Mechanical and electrical costs related to HVAC systems are commonly assigned a depreciation life based on current tax poli- cies. This depreciation life may be different from the projected func- tional life ofthe equipment, which is influenced by the quality of the system components and of the maintenance they receive. Some parts of the system, such as ductwork, could last the full life of the building. Other components, such as air-handling units, may have a useful life of 15 to 30 years, depending on their original quality and ongoing maintenance efforts. Estimated service life of equipment is listed in Chapter 37. Engineering economics can be used to evaluate life-cycle costs of configuration (utility corridor versus interstitial space), systems, and major equipment. The user or owner makes a business decision concerning the quality and reliability of the system and its ongoing operating costs. The HVAC engineer may be asked to provide an objective analysis of energy, maintenance, and construction costs, so that an appropriate life-cycle cost analysis can be made. Other considerations that may be appropriate include economic influences related to the long-term use of energy and governmental laws and regulations. Many technical considerations and the great variety of equip- ment available influence the design of HVAC systems. Factors affecting design must be well understood to ensure appropriate comparisons between various systems and to determine the impact on either first or operating costs. REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. AGS. 2007. Guidelines for gloveboxes, 3rd ed. American Glovebox Society, Santa Rosa, CA. Alereza, T., and J. Breen, III. 1984. Estimates of recommended heat gains due to commercial appliances and equipment (RP-391). ASHRAE Trans- actions 90(2A):25-58. Paper KC-2828. ARS. 2012. Facilities design standards manual. U.S. Department of Agri- culture, Agricultural Research Service, Washington, D.C. www.afm.ars .usda.gov/ppweh/pdf/242-01m.pdf. ASHRAE. 1995. Method of testing performance of laboratory fume hoods. ANSI/ASHRAE Standard 110-1995. ASHRAE. 2013. Method of testing for room air diffusion. ANSI/ASHRAE Standard 113-2013. ASHRAE. 2013. Commissioning process for buildings and systems. ANSI/ ASHRAE/IES Standard 202-2013. ASHRAE. 2013. The commissioning process. Guideline 0-2013. ASHRAE. 2007. HV AC&R technical requirements for the commissioning process. Guideline 1.1. ASHRAE. 2002. Laboratory design guide. ASSE. 2012. Laboratory ventilation. ANSI/AIHA/ASSE Standard Z9.5. American Society of Safety Engineers, Des Plaines, IL. Besch, E. 1975. Animal cage room dry bulb and dew point temperature dif- ferentials. ASHRAE Transactions 81(2):459-458. Paper BO-75-08-3. Besch, E. 1980. Environmental quality within animal facilities. Laboratory Animal Science 30(2II):385-406. Caplan, K., and G. Knutson. 1977. The effect of room air challenge on the efficiency of laboratory fume hoods (RP-70). ASHRAE Transactions 83(1):141-156. Paper CH-2438. Caplan, K., and G. Knutson. 1978. Laboratory fume hoods: Influence of room air supply. ASHRAE Transactions 84(1):511-537. Paper AT-78- 03-2. Castro, I.P. 2003. CFD for external aerodynamics in the built environment. The QNET-CFD Network Newsletter 2(2):4-7. CDC. 2009. Biosafety in microbiological and biomedical laboratories, 5th ed. Centers for Disease Control, U.S. Department of Health and Human Services. www.cofc.govidosa.loy/publaations/initiondf. Code ofFederal Regulations. (Annual). Good laboratory practices for non- clinical laboratory studies. 21 CFR 58. U.S. Government Printing Office, Washington, D.C. www.ecfr.gov. Code of Federal Regulations. (Annual). Current good manufacturing practice in manufacturing, processing, packing, of holding of drugs. 21 CFR 210. U.S. Government Printing Office, Washington, D.C. www.ecfr.gov. DHHS. 1999. Biosafety in microbiological and biomedical laboratories, 4th ed. Publication (CDC) 93-8395. U.S. Department of Health and Human Services, NIH, Bethesda, MD. Eagleston, J., Jr. 1984. Aerosol contamination at work. In The international hospital federation yearbook. Sabrecrown Publishing, London. Halitsky, J. 1988. Dispersion of laboratory exhaust gas by large jets. 81st Annual Meeting of the Air Pollution Control Association, June, Dallas. Hessler, J., and A. Moreland. 1984. Design and management of animal facil- ities. In Laboratory animal medicine, J. Fox, B. Cohen, and F. Loew, eds. Academic Press, San Diego, CA. ICC. 2015. International building codeⓇ. International Code Council, Wash- ington, D.C. ILAR. 2011. Guidefor the care and use oflaboratory animals, 8th ed. Insti- tute for Laboratory Animal Research, National Academy of Sciences, the National Academies Press, Washington, D.C. www.nap.edu/catalog .php?record_id=12910. Klein, R., C. King, and A. Kosior. 2009. Laboratory air quality and room ventilation rates. Journal of Chemical Health and Safety (9/10). Lewis, R. 2007. A review of ASHRAE noise criteria for teaching labs rela- tive to achieved speech intelligibility. Presented at ASHRAE Annual Meeting, Long Beach, CA. PDF slides available at ashrae-tc26.org/tc26 contentppograns200706_kcoratoratovg_comini_log beach_ CA Jume_2007lashrae-teaching-lab-criteria.pdff Maghirang, R.G., G.L. Riskowski, L.L. Christianson, and P.C. Harrison. 1995. Development of ventilation rates and design information for labo- ratory animal facilities-Part I: Field study. ASHRAE Research Project RP-730. ASHRAE Transactions 101(2):208-218. Paper 3898. Marsh, C. W. 1988. DDC systems for pressurization, fume hood face veloc- ity and temperature control in variable air volume laboratories. ASHRAE Transactions 94(2):1947-1968. Paper OT-88-18-2. Memarzadeh, F. 2000. Ventilation design in animal research facilities using static microisolators. ASHRAE Transactions 106(1). Paper DA-00-14-1. Murakami, S., A. Mochida, R. Ooka, S. Kato, and S. Iizuka. 1996. Numer- ical prediction of flow around buildings with various turbulence models: Comparison of k- EVM, ASM, DSM, and LES with wind tunnel tests. , ASHRAE Transactions 102(1):741-753. Paper AT-96-10-1. Neil, D., and R. Larsen. 1982. How to develop cost-effective animal room ventilation: Build a mock-up. Laboratory Animal Science (Jan-Feb): 32-37. NFPA. 2010. Fire protection guide for hazardous materials. National Fire Protection Association, Quincy, MA. Inc. ASHRAE, 2019 user. single for Licensed | {}
4eb99579-28e4-4e0a-9594-bffe5e6f0180 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 17.22 NFPA. 2015. Flammable and combustible liquids code. ANSI/NFPA Stan- dard 30-15. National Fire Protection Association, Quincy, MA. NFPA. 2011. Fire protection for laboratories using chemicals. ANSI/NFPA Standard 45-11. National Fire Protection Association, Quincy, MA. NFPA. 2013. Compressed gases and cryogenic fluids code. NFPA Standard 55-13. National Fire Protection Association, Quincy, MA. NFPA. 2013. Explosion protection by deflagration venting. ANSI/NFPA Standard 68-13. National Fire Protection Association, Quincy, MA. NRC. 2011. Guide for the care and use of laboratory animals, 8th ed. Na- tional Research Council, National Academies Press, Washington, D.C. www.nchi.nlm.nih.gov/books/NBK.54050/ NSF. 2012. Biosafety cabinetry: Design, construction, performance, and field certification. ANSI/NSF Standard 49-12 NSF International, Ann Arbor, MI. Petersen, R.L., J. Carter, and M. Ratcliff. 1997. The influence of architec- tural screens on exhaust dilution. ASHRAE Research Project RP-805. Draft Report approved by Technical Committee June 1997. Rake, B. 1978. Influence of crossdrafts on the performance of a biological safety cabinet. Applied and Environmental Microbiology (August):278- 283. Riskowski, G.L., R.G. Maghirang, and W. Wang. 1996. Development of ventilation rates and design information for laboratory animal facili- ties-Part II: Laboratory tests. ASHRAE Research Project RP-730. ASHRAE Transactions 102(2):195-209. Paper 4001. Rumsey, P , and J. Weale. 2007. Chilled beams in labs: Eliminating reheat and saving energy on a budget. ASHRAE Journal 49(1):18-25. Schuyler, G. 2009. The effect of air change rate on recovery from a spill. In Seminar 26, presented at 2009 ASHRAE Winter Conference, Chicago. SEFA. 2010. Laboratoryfume hoods recommendedpractices. SEFA 1. Sci- entific Equipment and Furniture Association, Hilton Head, SC. Sharp, G.P. 2010. Demand-based control of lab air change rates. ASHRAE Journal 52(2):30-41. Stuart, D., M. First, R. Rones, and J. Eagleston. 1983. Comparison of chem- ical vapor handling by three types of Class II biological safety cabinets. Particulate & Microbial Control (March/April). Wier, R.C. 1983. Toxicology and animal facilities for research and develop- ment. ASHRAE Transactions 89(2B):533-541. Paper DC-83-10-1. Wilson, D.J., I.C. Fabris, J. Chen, and M.Y. Ackerman. 1998. Adjacent building effects on laboratory fume hood stack design. ASHRAE Re- search Project RP-897, Final Report. Woods, J. 1980. The animal enclosure A microenvironment. Laboratory Animal Science 30(2II):407-413. Woods, J., J. Janssen, P. Morey, and D. Rask. 1987. Resolution ofthe "sick" building syndrome. Proceedings of ASHRAE Conference: Practical Control of Indoor Air Problems, pp. 338-348. Zhou, Y., and T. Stathopoulos. 1996. Application of two-layer methods for the evaluation ofwind effects on a cubic building. ASHRAE Transactions 102(1):754-764. Paper AT-96-10-2. BIBLIOGRAPHY Abramson, B., and T. Tucker. 1988. Recapturing lost energy. ASHRAE Jour- nal 30(6):50-52. ACGIH. 2013. Industrial ventilation: A manual of recommended practice. American Conference of Governmental Industrial Hygienists, Cincin- nati, OH. Adams, J.B., Jr. 1989. Safety in the chemical laboratory: Synthesis- Labo- ratory fume hoods. Journal of Chemical Education 66(12). Ahmed, O., and S.A Bradley. 1990. An approach to determining the required response time for a VAV fume hood control system. ASHRAE Transac- tions 96(2):337-342. Paper 3421. Ahmed, O., J.W. Mitchell, and S.A. Klein. 1993. Dynamics of laboratory pressurization. ASHRAE Transactions 99(2):223-229. Paper 3713. Albern, W., F. Darling, and L. Farmer. 1988. Laboratory fume hood opera- tion. ASHRAE Journal 30(3):26-30. Anderson, S. 1987. Control techniques for zoned pressurization. ASHRAE Transactions 93(2B):1123-1139. Paper NT-87-04-1. Anderson, C.P., and K.M. Cunningham. 1988. HVAC controls in laborato- ries-A systems approach. ASHRAE Transactions 94(1):1514-1520. Paper DA-88-19-2. ASHRAE. 2017. Method of testing general ventilation air-cleaning devices for removal efficiency by particle size. ANSI/ASHRAE Standard 52.2- 2017. 2019 ASHRAE Handbook-HVAC Applications (SI) ASHRAE. 2016. Ventilation for acceptable indoor air quality. ANSI/ASH- RAE Standard 62.1-2016. Barker, K.A., 0. Ahmed, and J.A. Parker. 1993. A methodology to deter- mine laboratory energy consumption and conservation characteristics using an integrated building automation system. ASHRAE Transactions 99(2):1155-1167. Paper DE-93-21-2. Bell, G.C., E. Mills, G. Sator, D. Avery, M. Siminovitch, and M.A. Piette. 1996. A design guide for energy-efficient research laboratories. LBNL- PUB-777. Lawrence Berkeley National Laboratory, Berkeley, CA. Bossert, K.A., and S.M. McGinley. 1994. Design characteristics of clinical supply laboratories relating to HVAC systems. ASHRAE Transactions 94(100):1655-1659. Paper NO-94-29-1. Brown, W.K. 1993. An integrated approach to laboratory energy efficiency. ASHRAE Transactions 99(2):1 143-1154. Paper DE-93-21-1. Carnes, L. 1984. Air-to-air heat recovery systems for research laboratories. ASHRAE Transactions 90(2A):327. Paper KC-2847. Coogan, J.J. 1994. Experience with commissioning VAV laboratories. ASHRAE Transactions 100(1):1635-1640. Paper NO-94-28-2. Crane, J. 1994. Biological laboratory ventilation and architectural and mechanical implications of biological safety cabinet selection, location, and venting. ASHRAE Transactions 100(1):1257-1265. Paper NO-94- 18-1. CRC. 2000. CRC handbook of laboratory safety, 5th ed. CRC Press, Boca Raton, FL. www.cocnefbase.com/ishn/9781420138460 Dahan, F. 1986. HVAC systems for chemical and biochemical laboratories. Heating, Piping and Air Conditioning (May):125-130. Davis, S., and R. Benjamin. 1987. VAV with fume hood exhaust systems. Heating, Piping and Air Conditioning (August):75-78. Degenhardt, R., and J. Pfost. 1983. Fume hood system design and applica- tion for medical facilities. ASHRAE Transactions 89(2B):558-570. Paper DC-82-10-4. DiBeradinis, L., J. Baum, M. First, G. Gatwood, E. Groden, and A. Seth. 1992. Guidelines for laboratory design: Health and safety consider- ations. John Wiley & Sons, Boston. Dorgan, C.B., C.E. Dorgan, and I.B.D. McIntosh. 2002. ASHRAE labora- tory design guide. ASHRAE. Doyle, D.L., R.D. Benzuly, and J.M. O'Brien. 1993. Variable-air-volume retrofit ofan industrial research laboratory. ASHRAE Transactions 99(2): 1168-1180. Paper DE-93-21-3. EEOC. 2018. Americans with disabilities act handbook, 5th ed. Equal Em- ployment Opportunity Commission, Washington, D.C. FGI. 2018. Guidelines for design and construction of hospitals; Guidelines for design and construction of outpatientfacilities; Guidelines for design and construction ofresidential health, care, and supportfacilities. Facil- ities Guidelines Institute, American Society of Healthcare Engineering, Chicago, IL Flanherty, R.J., and R. Gracilieri. 1994. Documentation required for the validation ofHVAC systems. ASHRAE Transactions 100(1):1629-1634. Paper NO-94-28-1. Ghidoni, D.A., and R.L. Jones, Jr. 1994. Methods of exhausting a BSC to an exhaust system containing a VAV component. ASHRAE Transactions 100(1):1275-1281. Paper NO-94-18-3. Halitsky, J. 1989. A jet plume model for short stacks. APCA Journal 39(6). Hitchings, D.T . and R.S. Shull 1993. Measuring and calculating laboratory exhaust diversity-Three case studies. ASHRAE Transactions 99(2): 1059-1071. Paper DE-93-18-1. ILAR. 1996. Laboratory animal management- Rodents. ILAR News 20(3). Kirkpatrick, A.T., and R. Reither. 1998. Numerical simulation oflaboratory fume hood airflow performance. ASHRAE Transactions 104(2). Paper TO-98-15-2. Knutson, G. 1984. Effect of slot position on laboratory fume hood perfor- mance. Heating, Piping and Air Conditioning (February):93-96. Knutson, G. 1987. Testing containment laboratory hoods: A field study. ASHRAE Transactions 93(2B):1801-1812. Paper NT-87-18-1. Koenigsberg, J., and H. Schaal. 1987. Upgrading existing fume hood instal- lations. Heating, Piping and Air Conditioning (October):77-82. Koenigsberg, J., and E. Seipp. 1988. Laboratory fume hood-An analysis of this special exhaust system in the post "Knutson-Caplan" era. ASHRAE Journal 30(2):43-46. Lacey, D.R. 1994. HVAC fora low-temperature biohazard facility. ASHRAE Transactions 100(1):1282-1286. Paper NO-94-18-4. Inc. ASHRAE, 2019 user. single for Licensed | {}
decdb6c5-fe3c-4fba-9081-85903b59f56b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Laboratories 17.23 Lentz, M.S., and A.K. Seth. 1989. A procedure for modeling diversity in laboratory VAV systems. ASHRAE Transactions 95(1):114-120. Paper 3211. Maghirang, R.G., G.L. Riskowski, P.C. Harrison, H. W. Gonyou, L. Sebek, and J. McKee. 1994. An individually ventilated caging system for labo- ratory rats. ASHRAE Transactions 100(1):913-920. Paper NO-94-10-3. Maust, J., and R. Rundquist. 1987. Laboratory fume hood systems-Their use and energy conservation. ASHRAE Transactions 93(2B):1813-1821. Paper NT-87-18-2. Mikell, W., and F. Fuller. 1988. Safety in the chemical laboratory: Good hood practices for safe hood operation. Journal of Chemical Education 65(2). Moyer, R.C. 1983. Fume hood diversity for reduced energy consumption. ASHRAE Transactions 89(2B):552-557. Paper DC-83-10-3. Moyer, R., and J. Dungan. 1987. Turning fume hood diversity into energy savings. ASHRAE Transactions 93(2B): 1822-1834. Paper NT-87-18-3. NFPA. 2017. Water spray fixed systems for fire protection. ANSI/NFPA Standard 15-17. National Fire Protection Association, Quincy, MA. NFPA. 1999. Gaseous hydrogen systems at consumer sites. ANSI/NFPA Standard 50A-99. National Fire Protection Association, Quincy, MA. NFPA. 2017. Liquefied petroleum gas code. NFPA Standard 58-17. National Fire Protection Association, Quincy, MA. NFPA. 2017. National electrical code. ANSI/NFPA Standard 70-17. Na- tional Fire Protection Association, Quincy, MA. NFPA. 2018. Installation of air conditioning and ventilating systems. ANSI/ NFPA Standard 90A-18. National Fire Protection Association, Quincy, MA. NFPA. 2018. Health care facilities code. ANSI/NFPA Standard 99-18. Na- tional Fire Protection Association, Quincy, MA. NIH. 2008. Design requirements manual. National Institutes of Health, Bethesda, MD. ortiod.ningrov FriciesAndGundehnexPres Design RequirementsManual2016.aspx. Neuman, V. 1989. Design considerations for laboratory HVAC system dy- namics. ASHRAE Transactions 95(1):121-124. Paper 3212. Neuman, V. 1989. Disadvantages of auxiliary air fume hoods. ASHRAE Transactions 95(1):70-75. Paper 3204. Neuman, V. 1989. Health and safety in laboratory plumbing. Plumbing En- gineering (March):21-24. Neuman, V., and H. Guven. 1988. Laboratory building HVAC systems opti- mization. ASHRAE Transactions 94(2):432-451. Paper 3171. Neuman, V . and W. Rousseau. 1986. VAV for laboratory hoods- Design and costs. ASHRAE Transactions 92(1A):330-346. Paper 2956. Neuman, V., F. Sajed, and H. Guven. 1988. A comparison of cooling thermal storage and gas air conditioning for a lab building. ASHRAE Transac- tions 94(2):452-468. Paper 3172. NRC. 1989. Biosafety in the laboratory: Prudent practicesfor handling and disposal of infectious materials. National Research Council, National Academy Press, Washington, D.C. NRC. 2011. Prudent practices in the laboratory: Handling and management of chemical hazards, updated version. National Research Council, National Academy Press, Washington, D.C. OSHA. [Annual] Occupational exposure to chemicals in laboratories. Appendix VII, 29 CFR 1910.1450. www.ecfr.gov. Parker, J.A., 0. Ahmed, and K.A. Barker. 1993. Application of building automation system (BAS) in evaluating diversity and other characteris- tics ofa VAV laboratory.ASHRAE Transactions 99(2):1081-1089. Paper DE-93-18-3. Peterson, R. 1987. Designing building exhausts to achieve acceptable con- centrations of toxic effluents. ASHRAE Transactions 93(2):2165-2185. Paper NT-87-25-2. Peterson, R.L., E.L. Schofer, and D.W. Martin. 1983. Laboratory air sys- tems-Further testing. ASHRAE Transactions 89(2B):571-596. Paper DC-83-10-5. Pike, R. 1976. Laboratory-associated infections: Summary and analysis of 3921 cases. Health Laboratory Science 13(2):105-114. Rabiah, T.M., and J.W. Wellenbach. 1993. Determining fume hood diversity factors. ASHRAE Transactions 99(2):1090-1096. Paper DE-93-18-4. Richardson, G. 1994. Commissioning ofVA v laboratories and the problems encountered. ASHRAE Transactions 100(1):1 641-1645. Paper NO-94- 28-3. Rizzo, S. 1994. Commissioning of laboratories: A case study. ASHRAE Transactions 100(1):1 646-1652. Paper NO-94-28-4. Sandru, E. 1996. Evaluation of the laboratory equipment component of cool- ing loads. ASHRAE Transactions 102(1):732-737. Paper AT-96-09-3. Schuyler, G., and W. Waechter. 1987. Performance of fume hoods in simu- lated laboratory conditions. Report 487-1605 by Rowan Williams Davies & Irwin, Inc., under contract for Health and Welfare Canada. Schwartz, L. 1994. Heating, ventilating and air conditioning considerations for pharmaceutical companies. Pharmaceutical Engineering 14(4). Sessler, S., and R. Hoover. 1983. Laboratory fume hood noise. Heating, Pip- ing, and Air Conditioning (September):124-137. Simons, C.G. 1991. Specifying the correct biological safety cabinet. ASHRAE Journal 33(8). Simons, C.G., and R. Davoodpour. 1994. Design considerations for labora- tory facilities using molecular biology techniques. ASHRAE Transac- tions 100(1):1266-1274. Paper NO-94-18-2. Smith, W. 1994. Validating the direct digital control (DDC) system in a clin- ical supply laboratory. ASHRAE Transactions 100(1):1 669-1675. Paper NO-94-29-3. Streets, R.A., and B.S. V. Setty. 1983. Energy conservation in institutional laboratory and fume hood systems. ASHRAE Transactions 89(2B): 542- 551. Paper DC-83-10-2. Stuart, D., R. Greenier, R. Rumery, and J. Eagleston. 1982. Survey, use, and performance of biological safety cabinets. American Industrial Hygiene Association Journal 43:265-270. Varley, J.O. 1993. The measurement of fume hood use diversity in an indus- trial laboratory. ASHRAE Transactions 99(2):1072-1080. Paper DE-93- 18-2. Vzdemir, I.B., J.H. Whitelaw, and A.F. Bicen. 1993. Flow structures and their relevance to passive scalar transport in fume cupboards. Proceed- ings of the Institution ofMechanical Engineers 207:103-115. West, D.L. 1978. Assessment of risk in the research laboratory: A basis for facility design. ASHRAE Transactions 84(1):547-557. Paper AT-78- 03-4. Wilson, D.J. 1983. A design procedure for estimating air intake contamina- tion from nearby exhaust vents (RP-204). ASHRAE Transactions 89(2A): 136. Paper DC-2769. Yoshida, K., H. Hachisu, J.A. Yoshida, and S. Shumiya. 1994. Evaluation of the environmental conditions in a filter-capped cage using a one-way air- flow system. ASHRAE Transactions 100(1):901-905. Paper NO-94-10-1. Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
f8d5062b-3c25-4cea-bfb2-48211c04edb5 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 18 ENGINE TEST FACILITIES ¦ Engine Heat Release ¦ 18.1 ¦ Chassis Dynamometer Rooms ¦ 18.3 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Engine Exhaust ¦ 18.1 ¦ Ventilation ¦ 18.4 ¦ ¦ Internal Combustion Engine Test Cells ¦ 18.2 ¦ Combustion Air Supply ¦ 18.4 ¦ ¦ Test Cell Supply ¦ 18.3 ¦ Cooling Water Systems ¦ 18.4 ¦ ¦ Gas-Turbine Test Cells ¦ 18.3 ¦ Noise ¦ 18.4 ¦ INDUSTRIAL testing of turbines and internal combustion engines is performed in enclosed test spaces to control noise and isolate the test for safety or security. These spaces are ventilated or condi- tioned to control the facility environment and fumes. Isolated engines are tested in test cells; engines inside automobiles are tested on chas- sis dynamometers. The ventilation and safety principles for test cells also apply when large open areas in the plant are used for production testing and emissions measurements. Enclosed test cells are normally found in research or emissions test facilities. Test cells may require instruments to measure cooling sys- tem water flow and temperature; exhaust gas flow, temperature, and emission concentrations; fuel flow; power output; and combustion air volume and temperature. Changes in the temperature and humidity of the test cell affect these measurements. Accurate control of the testing environment is becoming more critical. For example, the U.S. Envi- ronmental Protection Agency requires tests to demonstrate control of automobile contaminants in both hot and cold environments. Air conditioning and ventilation of test cells must (1) supply and exhaust proper quantities of air to remove heat and control tempera- ture; (2) exhaust sufficient air at proper locations to prevent buildup of combustible vapors; (3) supply and modulate large quantities of air to meet changing conditions; (4) remove exhaust fumes; (5) sup- ply combustion air; ⑥ prevent noise transmission through the sys- tem; (7) provide for human comfort and safety during setup, testing, and tear-down; and (8) treat the exhaust effluent. Supply and exhaust systems for test cells may be unitary, central, or a combination of the two. Mechanical exhaust is necessary in all cases. Special w arning: Certain industrial spaces may contain flam- mable, combustible, and/or toxic concentrations of vapors or dusts under either normal or abnormal conditions. In spaces such as these, there are life-safety issues that this chapter may not completely ad- dress. Special precautions must be taken in accordance with require- ments of recognized authorities such as the National Fire Protection Association (NFPA), the Occupational Safety and Health Adminis- tration (OSHA), and the American National Standards Institute (ANSI). In all situations, engineers, designers, and installers who en- counter conflicting codes and standards must defer to the code or standard that best addresses and safeguards life safety. 1. ENGINE HEAT RELEASE The special air-conditioning requirements of an engine test facil- ity stem from burning the fuel used to run the engine. For internal combustion engines at full load, 10% of the total heat content of the fuel is radiated and convected into the room or test cell atmosphere, and 90% is fairly evenly divided between the shaft output (work), exhaust gas heating, and heating of the jacket cooling water. Air-cooled engines create a forced convection load on the test space equal to the jacket water heat that it replaces. For turbine engines, the exhaust gas carries double the heat of the internal combustion engine exhaust and there is no jacket water to heat. The engine manufacturer The preparation of this chapter is assigned to TC 9.2, Industrial Air Condi- tioning. can provide a more precise analysis of heat release characteristics at various speeds and power outputs. Test facilities use dynamometers to determine the power supplied by the engine shaft. The dynamometer converts shaft work into heat that must be accounted for by a cooling system or as heat load into the space. Often, shaft work is converted into electricity through a gen- erator and the electric power is dissipated by a resistance load bank or sold to the local utility. Inefficiencies of the various pieces of equip- ment add to the load of the space in which they are located. Heat released into the jacket water must also be removed. If a closely connected radiator is used, the heat load is added to the room load. Many test facilities include a heat exchanger, and a secondary cooling circuit transfers the heat to a cooling tower. Some engines require an oil cooler separate from the jacket water. Whichever system is used, the cooling water flow, temperature, and pressure are usually monitored as part of the test operation, and heat from these sources needs to be accommodated by the facility's air conditioning. Exhaust systems present several challenges to engine test cell design. Exhaust gases can exit the engine at 800°C or higher. Com- monly, the exhaust gas is augmented by inserting the exhaust pipe into a larger-bore exhaust system (laboratory fixed system), which draws room air into the exhaust to both cool the gas and ventilate the test cell. Both the exhausted room air and combustion air must be supplied to the room from the HVAC or from the outdoors. Radiation and convection from exhaust pipes, catalytic converter, muffler, etc., also add to the load. In most cases, the test cell's HVAC system should account for an engine that can fully load the dynamom- eter, and have capacity control for operation at partial and no load. Large gas turbine engines have unique noise and airflow require- ments; therefore, they usually are provided with dedicated test cells. Small gas turbines can often be tested in a regular engine test cell with minor modifications. 2. ENGINE EXHAUST Engine exhaust systems remove combustible products, unburned fuel vapors, and water vapor. Flow loads and operating pressure need to be established for design of the supporting HVAC. Flow loads are calculated based on the number of engines, the engine sizes and loads, and use factors or diversity. Operating pressure is the engine discharge pressure at the con- nection to the exhaust. Systems may operate at positive pressure using available engine tail-pipe pressure to force the flow of gas, or at negative pressure with mechanically induced flow. The simplest way to induce engine exhaust from a test cell is to size the exhaust pipe to minimize variations in pressure on the en- gine and to connect it directly outdoors (Figure 1A). Exhausts di- rectly connected to the outdoor are subject to wind currents and air pressure, however, and can be hazardous because of positive pres- sure in the system. Mechanical engine exhausts are either unitary or central. A uni- tary exhaust (Figure 1B) serves only one test cell, and can be closely regulated to match the engine's operation. A central exhaust (Figure 1D) serves multiple test cells with one or more exhaust fans and a Inc. ASHRAE, 2019 user. single for Licensed 18.1 | {}
b8b12546-f486-4767-873f-93cd5d3a9731 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 18.2 2019 ASHRAE Handbook-HVAC Applications (SI) ![image](/image/placeholder) FAN VOLUME CONTROL EXHAUST FAN PRESSURE REGULATOR EXHAUST FAN ENGINE ENGINE ENGINE 」 → つ A. DIRECT B. UNITARY MECHANICAL C. UNITARY MECHANICAL EXHAUST EXHAUST WITH EXHAUST WITH PRESSURE REGULATION INDIRECT CONNECTION BRANCH FAN VOLUME CONTROL PRESSURE MAIN PRESSURE REGULATOR REGULATOR ENGINE ENGINE ENGINE 0 -0 -0 - BRANCH DAMPER CENTRAL EXHAUST EXHAUST FAN HEADER D. CENTRAL MECHANICAL EXHAUST WITH PRESSURE REGULATION Fig. 1 Engine Exhaust Systems duct system with branch connections to the individual test cells. Re- lief of a possible explosion in the ductwork should be considered. Engine exhaust pressures fluctuate with changes in engine load and speed. Central exhausts should be designed to minimize effects of load variations in individual test cells on the system. Engine characteristics and diversity of operation determine the maximum airflow to be handled. Dampers and pressure regulators may be required to keep pressures within test tolerances. An indirect connection between the engine exhaust pipe and mechanical exhaust gas removal (Figure 1C) eliminates variation in back pressure and augments exhaust gas flow by inducing room air into the exhaust stream. In this system, the engine exhaust pipe ter- minates by being centered and inserted about 75 mm into the aug- mentation pipe, which is at least 25 mm larger in diameter. The induced room air is mixed with the exhaust gases, yielding a much cooler exhaust flow. However, the potential for increased corrosion in a cooler exhaust must be considered when selecting construction materials. The engine muffler should be located upstream of the augmentation connection to control noise. The indirect connection should be considered a potential point of ignition if the exhaust is fuel rich and the tail pipe reaches temperatures above 370°C. Exhaust pipes and mufflers run very hot. A ventilated heat shield or a water-jacketed pipe reduces cell heat load, and some exhausts are equipped with direct water injection. Thermal expansion, stress, and pressure fluctuations must also be considered in the design of the exhaust fan and ducting. The equipment must be adequately sup- ported and anchored to relieve the thermal expansion. Exhaust systems for chassis dynamometer installations must capture high-velocity exhaust from the tail pipe to prevent fume buildup in the room. An exhaust flow rate of 330 L/s has been used effectively for automobiles at a simulated speed of 100 km/h. Engine exhaust should discharge through a stack extending above the roof to an elevation sufficient to allow the fumes to clear the building. Chapter 46 has further details about exhaust stacks. Codes or air emission standards may require that exhaust gases be cleaned before being discharged to atmosphere. 3. INTERNAL COMBUSTION ENGINE TEST CELLS Test Cell Exhaust Ventilation for test cells is based on exhaust requirements for (1) removal of heat generated by the engine, (2) emergency purg- ing (removal of fumes after a fuel spill), and (3) continuous cell scavenging during nonoperating periods. Heat is transferred to the test cell by convection and radiation from all of the heated surfaces, such as the engine and exhaust system. At a standard air density of = 1.2 kg/m3 and specific heat Cp = 1.0 kJ/(kg·K), ![image](/image/placeholder) FILTER HEATING COIL SUPPLY DUCT FRESH AIR PLENUM SLOT OUTLET TEST CELL DYNAMOMETER CORRIDOR ENGINE Barreter GRATING ENGINE EXHAUST UNITARY CELL EXHAUST FAN Fig. 2 Engine Test Cell Showing Direct Engine Exhaust: Unitary Ventilation System 9 9 0 = c t. 1.2 t ts p e : where 0 = airflow, m3/s 9 engine heat release, kW te = temperature of exhaust air, °C ts = temperature of supply air, °C The constant (1.2) should be corrected for other temperatures and pressures. Heat radiated from the engine, dynamometer, and exhaust pip- ing warms surrounding surfaces, which release heat to the air by convection. The value for (te - ts) in the equation cannot be arbi- trarily set when a portion of 9 is radiated heat. The section on Engine Heat Release discusses other factors required to determine the overall q. v apor Removal. The exhaust should remove vapors as quickly as possible. Emergency purging, often 50 L/s per square metre of floor area, should be controlled by a manual overriding switch for each test cell. In case of fire, provisions need to be made to shut down all equipment, close fire dampers at all openings, and shut off the fuel-flow solenoid valves. Cell Scavenging. Exhaust air is the minimum amount of air required to keep combustible vapors from fuel leaks from accumu- lating. In general, the NFPA Standard 30 requirement of 5 L/s per square metre of floor area is sufficient. Because gasoline vapors are heavier than air, exhaust grilles should be low, even when an overhead duct is used. Exhausting close to the engine minimizes the convective heat that escapes into the cell. In some installations, all air is exhausted through a floor grating surrounding the engine bed plate and into a cubicle or duct below. In this arrangement, slots in the ceiling over the engine supply a curtain of air to remove the heat. This scheme is particularly suitable for a central exhaust (Figure 2). Water sprays in the underfloor exhaust lessen the danger of fire or explosion in case of fuel spills. Inc. ASHRAE, 2019 user. single for Licensed Trenches and pits should be avoided in test cells. If they exist, as in most chassis dynamometer rooms, they should be mechanically exhausted at all times. Long trenches may require multiple exhaust takeoffs. The exhaust should sweep the entire area, leaving no dead air spaces. Because of fuel spills and vapor accumulation, suspend- ed ceilings or basements should not be located directly below the engine test cell. If such spaces exist, they should be ventilated con- tinuously and have no fuel lines running through them. Detection of | {}
7667ca8e-989d-4844-a6a8-183fb2af8bc0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Engine Test Facilities 18.3 Table 1 Exhaust Quantities for Test Cells ¦ ¦ Minimum Exhaust Rates per Square Metre of Floor Area ¦ Minimum Exhaust Rates per Square Metre of Floor Area ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ L/s ¦ acha ¦ ¦ Engine testing: cell operating ¦ 50 ¦ 60b ¦ ¦ Cell idle ¦ 5 ¦ 6 ¦ ¦ Trenchesc and pits ¦ 50 ¦ ¦ ¦ Accessory testing Control rooms and corridors ¦ 20 5 ¦ 24 6 ¦ a Air changes per hour, based on cell height of 3 m. b For chassis dynamometer rooms, this quantity is usually set by test requirements. ° For large trenches, use 0.5 m/s across the cross-sectional area of the trench. exhaust in the test cell should be considered (per ACGIH) for a time-weighted average (TWA) of25 mg/kg. Table 1 lists exhaust quantities used in current practice; the ex- haust should be calculated for each test cell on the basis ofheat to be removed, evaporation of possible fuel spills, and the minimum ven- tilation needed during downtime. 4. TEST CELL SUPPLY The air supply to a test cell should be balanced to yield a slightly negative pressure This is accomplished by having either an exhaust airflow 10% greater than the supply air or a differential pressure of the test cell at least 12.5 Pa less than the surrounding space. Test cell air should not be recirculated. Air taken from nontest areas can be used if good ventilation practices are followed, such as using air that is free of unacceptable contaminants, is sufficient for temperature control, and can maintain the proper test cell pressure. Ventilation air should keep heat released from the engine away from cell occupants. Slot outlets with automatic dampers to main- tain a constant discharge velocity have been used with variable- volume systems. A variation of systems C and D in Figure 3 includes a separate air supply sized for the minimum (downtime) ventilation rate and for a cooling coil with room thermostat to regulate the coil to con- trol the temperature in the cell. This system is useful in installa- tions where much time is devoted to the setup and preparation of tests, or where constant temperature is required for complicated or sensitive instrumentation. Except for production and endurance testing, the actual engine operating time in test cells may be sur- prisingly low. The average test cell is used approximately 15 to 20% of the time. Air should be filtered to remove particulates and insects. The degree of filtration is dictated by the type of tests. Facilities in rela- tively unpolluted areas sometimes use unfiltered outdoor air. Heating coils are needed to temper supply air if there is danger of freezing equipment or iflow temperatures adversely affect tests. For low-temperature applications, a desiccant wheel with pre- and post- cooling may be needed (with qualified environmentally safe refrig- erants). If desiccant wheels are used, consider placing the fan in a self-contained unit outside of the air stream with nonsparking com- ponents, to reduce the risk of ignition source from the fan if the air- stream could contain combustible components. 5. GAS-TURBINE TEST CELLS Large gas-turbine test cells must handle large quantities of air re- quired by the turbine, attenuate the noise generated, and operate safely with a large flow offuel. These cells are unitary and use the tur- bine to draw in untreated air and exhaust it through noise attenuators. Small gas turbine engines can generally be tested in a conventional test cell with relatively minor modifications. The test-cell ventilation air supply and exhausts are sized for turbine-generated heat as for a conventional engine. The combustion air supply for the turbine is ![image](/image/placeholder) HEATING COIL HEATING COIL FILTER INLET つ ○ VANES 0 $ THERMOSTAT FILTER UNITARY UNITARY EXHAUST FAN EXHAUST SUPPLY FAN THERMOSTAT FAN A. VARIABLE-VOLUME UNITARY B. VARIABLE-VOLUME UNITARY SUPPLY AND EXHAUST EXHAUST, INDUCED SUPPLY ![image](/image/placeholder) HEATING COIL SYSTEM STATIC- PRESSURE REGULATOR FILTER CENTRAL BRANCH INLET DAMPER EXHAUST ? FAN 0 0 $ ,00 000 AK SUPPLY FAN ROOM STATIC- P P P PRESSURE STATIC- REGULATORS BRANCH PRESSURE (TYPICAL) EXHAUST REGULATOR DAMPER THERMOSTATS (TYPICAL) C. VARIABLE-VOLUME CENTRAL SUPPLY AND EXHAUST SYSTEM ![image](/image/placeholder) THERMOSTATS (TYPICAL) BRANCH EXHAUST DAMPER BRANCH INLET DAMPER P 心 0 SYSTEM STATIC- PRESSURE 0 REGULATOR , ROOM STATIC- EXHAUST PRESSURE FAN � REGULATORS (TYPICAL) (TYPICAL) SUPPLY FAN FILTER HEATING COIL D. VARIABLE-VOLUME COMBINATION SYSTEM, UNITARY EXHAUST CENTRAL SUPPLY Fig. 3 Heat Removal Ventilation Systems considerable; it may be drawn from the cell, from outdoors, or through separate conditioning units that handle only combustion air. Exhaust quantities are higher than from internal combustion en- gines and are usually ducted directly to the outdoors through muf- fling devices that provide little restriction to airflow. Exhaust air may be water-cooled, as temperature may exceed 700°C. 6. CHASSIS DYNAMOMETER ROOMS A chassis dynamometer (Figure 4) simulates road driving and acceleration conditions. The vehicle's drive wheels rest on a large roll, which drives the dynamometer. Air quantities, which are cali- brated to correspond to air velocity at a particular road speed, flow across the front of the vehicle for radiator cooling and to approxi- mate the effects of air speed on the body of the vehicle. Additional refinements may vary air temperature within prescribed limits from - 40 to 55°C, control relative humidity, and/or add shakers to simu- late road conditions. Air is usually introduced through an area approximating the frontal area of the vehicle. A duct with a return grille at the rear of the vehicle may be lowered so that air remains near the floor rather than cycling through a ceiling return air grille. Air is recirculated to air-handling equipment above the ceiling. Chassis dynamometers are also installed in · Cold rooms, where temperatures may be as low as -70°C. · Altitude chambers, where elevations up to 3700 m can be simu- lated. · Noise chambers for sound evaluation. · Electromagnetic cells for evaluation of electrical components. Inc. ASHRAE, 2019 user. single for Licensed | {}
0b9c0513-9b6d-4fae-9e32-d60a1a4b30b5 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 18.4 ![image](/image/placeholder) MONOXIDE EXHAUST WINDAGE HEATING-COOLING FAN COILS BLOWER RELIEF MAKEUP AIR DAMPERS TELESCOPIC LOUVERS SUPPLY DUCT MOVABLE EXHAUST DUCT ○ 。 ★ ENGINE EXHAUST INERTIA WEIGHTS DYNAMOMETER TRANSMISSION CHASSIS ROLLS Fig. 4 Chassis Dynamometer Room · Environmental chambers. · Full-sized wind tunnels with throat areas much larger than the cross-sectional area of the vehicle. Combustion air is drawn directly from the room, but the engine exhaust must be installed in a way that will preserve the low temperature and humidity. Where ultralow-temperature refrigeration is required for a cold room, direct cooling with toxic refrigerants is not recommended. Consider secondary cooling loops using safe low-temperature heat transfer fluids (LTHTFs) that, if released into the atmosphere of the cold test cell, do not present a significant health risk to occupants or require mitigation resources. A temperature soak space is often placed near chassis dynamom- eter rooms having a controlled temperature. This space is used to cool or heat automobiles scheduled to enter the room. Generally, 18 to 24 h is required before the temperature of the vehicle stabilizes to the temperature of the room. The soak space and the temperature- controlled room are often isolated from the rest of the facility, with entry and egress through an air lock. 7. VENTILATION Constant-volume systems with variable supply temperatures can be used; however, variable-volume, variable-temperature systems are usually selected. Ventilation is generally controlled on the ex- haust side (see Figure 3). Unitary variable-volume systems (Figure 3A) use an individual exhaust fan and makeup air supply for each cell. Supply and exhaust fans are interlocked, and their operation is coordinated with the engine, usually by sensing the temperature of the cell. Some systems have exhaust only, with supply induced di- rectly from outdoors (Figure 3B). The volume is varied by changing fan speed or damper position. Ventilation with central supply fans, central exhaust fans, or both (Figure 3C) regulates air quantities by test cell temperature control of individual dampers or by two-position switches actuated by dynamometer operations. Air balance is maintained by static pres- sure regulation in the cell. Constant pressure in the supply duct is obtained by controlling supply fan inlet vanes, modulating dampers, or varying fan speed. In systems with individual exhaust fans and central supply air, exhaust is controlled by cell temperature or a two-position switch actuated by dynamometer operation. The central supply system is controlled by a static pressure device in the cell to maintain room pressure (Figure 3D). Variable-volume exhaust airflow should not drop below minimum requirements. Exhaust requirements should override cell temperature requirements; thus, reheat may be needed. 2019 ASHRAE Handbook-HVAC Applications (SI) Table 2 Typical Noise Levels in Test Cells ¦ Type and Size of Engine ¦ Sound Level 0.9 m from Engine, dBA ¦ Sound Level 0.9 m from Engine, dBA ¦ Sound Level 0.9 m from Engine, dBA ¦ Sound Level 0.9 m from Engine, dBA ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ 63 Hz ¦ 124 Hz ¦ 500 Hz ¦ 2000 Hz ¦ ¦ Diesel ¦ Diesel ¦ Diesel ¦ Diesel ¦ Diesel ¦ ¦ Full load ¦ 105 ¦ 107 ¦ 98 ¦ 99 ¦ ¦ Part load ¦ 70 ¦ 84 ¦ 56 ¦ 49 ¦ ¦ Gasoline engine, 7.2 L at 5000 rpm ¦ Gasoline engine, 7.2 L at 5000 rpm ¦ Gasoline engine, 7.2 L at 5000 rpm ¦ Gasoline engine, 7.2 L at 5000 rpm ¦ Gasoline engine, 7.2 L at 5000 rpm ¦ ¦ Full load ¦ 107 ¦ 108 ¦ 104 ¦ 104 ¦ ¦ Part load ¦ 75 ¦ ¦ ¦ ¦ ¦ Rotary engine, 75 kW ¦ Rotary engine, 75 kW ¦ Rotary engine, 75 kW ¦ Rotary engine, 75 kW ¦ Rotary engine, 75 kW ¦ ¦ Full load ¦ 90 ¦ 90 ¦ 83.5 ¦ 86 ¦ ¦ Part load ¦ 79 ¦ 78 ¦ 75 ¦ 72 ¦ V entilation should be interlocked with fire protection to shut down the supply to and exhaust from the cell in case of fire. Exhaust fans should be nonsparking, and makeup air should be tempered. 8. COMBUSTION AIR SUPPLY Combustion air is usually drawn from the test cell or introduced directly from the outdoors. Separate dedicated units can be used if combustion air must be closely regulated and conditioning of the entire test cell is impractical. These units filter, heat, and cool the supply air and regulate its humidity and pressure; they usually pro- vide air directly to the engine air intake. Combustion air systems may be central units or portable packaged units. 9. COOLING w ATER SYSTEMS Dynamometers absorb and measure the useful output of an engine or its components. In a water-cooled dynamometer, engine work is converted to heat, which is absorbed by circulating water. Electrical dynamometers convert engine work to electrical energy, which can be used or dissipated as heat in resistance grids or load banks or sold to the local utility. Grids should be located outdoors or adequately ventilated. Heat loss from electric dynamometers is approximately 8% of the measured output, plus a constant load of about 5 kW for auxil- iaries in the cell. Recirculating water absorbs heat from the engine jacket water, oil coolers, and water cooled dynamometers through circulating pumps, cooling towers, or atmospheric coolers and hot- and cold-well collecting tanks. 10. NOISE Noise generated by internal combustion engines and gas turbines must be considered in the design of a test cell air-handling system. Part of the engine noise is discharged through the tail pipe. If pos- sible, internal mufflers should be installed to attenuate this noise at its source. Any ventilation ducts or pipe trenches that penetrate the cells must be insulated against sound transmission to other areas or to the outdoors. Attenuation equivalent to that provided by the cell structure should be applied to duct penetrations. Table 2 lists typical noise levels in test cells during engine operations. BIBLIOGRAPHY ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by non- members in the online ASHRAE Bookstore at www.ashrae.org /bookstore. ACGIH. 2016. Industrial ventilation: A manual of recommended practice, 28th ed. American Conference of Governmental Industrial Hygienists, Cincinnati, OH. Inc. ASHRAE, 2019 user. single for Licensed | {}
ef99e189-3ac2-4cbf-be8f-d349dbd90274 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Engine Test Facilities 18.5 Bannasch, L.T., and G.W. Walker. 1993. Design factors for air-conditioning systems serving climatic automobile emission test facilities. ASHRAE Transactions 99(2):614-623. Computer controls engine test cells. Control Engineering 16(75):69. NFPA. 2018. Flammable and combustible liquids code. Standard 30-2018. National Fire Protection Association, Quincy, MA. Paulsell, C.D. 1990. Description and specification for a cold weather emis- sions testingfacility. U.S. Environmental Protection Agency, Washing- ton, D.C. Schuett, J.A., and T.J. Peckham. 1986. Advancements in test cell design. SAE Transactions, Paper 861215. Society of Automotive Engineers, Warren- dale, PA. Inc. ASHRAE, 2019 user single for Licensed Related Commercial Resources | {}
3f84be6e-6873-4efb-9354-7b8b9c9f6712 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 19 CLEAN SPACES ¦ Terminology ¦ 19.1 ¦ ¦ --- ¦ --- ¦ ¦ Clean Spaces and Cleanroom Applications ¦ 19.3 ¦ ¦ Airborne Particles and Particle Control ¦ 19.3 ¦ ¦ Air Pattern Control ¦ 19.4 ¦ ¦ Airflow Direction Control Between Clean Spaces ¦ 19.8 ¦ ¦ Testing Clean Air and Clean Spaces ¦ 19.10 ¦ ¦ Pharmaceutical and Biomanufacturing Clean Spaces ······ ¦ 19.11 ¦ ¦ Start-Up and Qualification of Pharmaceutical ¦ ¦ ¦ Cleanrooms ¦ 19.16 ¦ CLEAN SPACES are defined as areas in which particle concen- and environmental conditions are controlled at or within specified limits. Design of clean spaces (or cleanrooms) covers much more than traditional control of air temperature and humidity. Addi- tional factors may include control of particle, microbial, electrostatic discharge (ESD), molecular, and gaseous contamination; airflow pat- terns; air pressurization; sound and vibration; environmental health; life safety; industrial engineering aspects; and manufacturing equip- ment layouts. The objective of good cleanroom design is to maintain effective contamination control while ensuring required levels ofreli- ability, productivity, installation, and operating costs. 1. TERMINOLOGY Acceptance Criteria. Upper and lower limits of a pharmaceuti- cal critical parameter required for product or process integrity. Ifthe measured conditions are not within the allowable limits, the pharma- ceutical product may be considered adulterated. ach. Air changes per hour. Air Lock. A small transitional space between two adjacent spaces of different cleanliness classification and air pressure set points. As-built Cleanroom. A cleanroom that is completely constructed, with all services connected and functional, but not con- taining production equipment, materials, or personnel in the space. Aseptic Space. A space controlled such that bacterial growth is contained within acceptable limits. This is not a sterile space, in which absolutely no life exists. At-rest Cleanroom. A cleanroom that is complete with produc- tion equipment and materials installed and operating, but without personnel in the room. CFU (colony-forming unit). A measure of bacteria present in a pharmaceutical processing space, measured by sampling as part of performance qualification or routine operational testing. Challenge. An airborne dispersion of particles of known sizes and concentration used to test filter integrity and filtration efficiency. Cleanroom. A specially constructed enclosed space with environ- mental control of particulates, temperatures, humidity, air pressure, airflow patterns, air motion, vibration, noise, viable organisms, and lighting. Clean Space. A defined area in which particle concentration and environmental conditions are controlled at or within specified limits. Contamination. Any unwanted material, substance, or energy, including vibration, noise, lighting, radiation, etc. Commissioning. A quality-oriented process for achieving, veri- fying, and documenting that the performance of facilities, systems, and assemblies meets defined objectives and criteria, usually begin- ning at the user requirements specification (URS) generation stage. The preparation of this chapter is assigned to TC 9.11, Clean Spaces. ¦ Semiconductor Cleanrooms ¦ 19.17 ¦ ¦ --- ¦ --- ¦ ¦ High-Bay Cleanrooms ¦ 19.21 ¦ ¦ Environmental Systems ¦ 19.22 ¦ ¦ Sustainability and Energy Conservation ¦ 19.25 ¦ ¦ Noise and Vibration Control ¦ 19.27 ¦ ¦ Space Construction and Operation ¦ 19.27 ¦ ¦ Cleanroom Installation and Test Procedures ¦ 19.28 ¦ ¦ Integration of Cleanroom Design and Construction ¦ 19.30 ¦ ¦ Life and Property Safety ¦ 19.31 ¦ Conventional-flow Cleanroom. A cleanroom with non- unidirectional or mixed airflow patterns and velocities. Critical Parameter. A space variable (e.g., temperature, humid- ity, air changes, space pressure, particulates, viable organisms) that, by law or per product development data, affects product strength, identity, safety, purity, or quality (SISPQ). Critical Surface. The part of the work surface to be protected from particulate contamination. Design conditions. The environmental conditions for which the clean space is designed. DOP. Dioctyl phthalate: an aerosol formerly used for testing effi- ciency and integrity of HEPA filters. ESD. Electrostatic discharge. EU GMP. European Union guidelines for GMP (defined in following text) pharmaceutical manufacturing. Electrically Enhanced Filtration (EEF). System that reduces fan energy requirements by using an electrical ionizing device to charge incoming particles and a high-voltage electrical field across the air filter to enhance filtration efficiency of the filter media. Exfiltration. Air leakage from a space ofhigher pressurization to one of lower pressurization through material transfer openings; gaps between personnel/pass-through access doors and their respective jambs, window frame/glass interfaces; wall/ceiling and wall/floor interfaces; electrical/data outlets and other room boundary penetra- tions. FDA. U.S. Food and Drug Administration. Inc. ASHRAE, 2019 user. single for Licensed First Air. Air supplied directly from the HEPA filter before it passes over any work location. GMP. Good manufacturing practice, as defined by Code ofFed- eral Regulations (CFR) 21 CFR 210, 211 (also, CGMP = current GMP). High-efficiency Particulate Air (HEPA) Filter. A filter with a minimum efficiency of 99.97% of 0.3 m particles. IEST. Institute of Environmental Sciences and Technology. Infiltration. Air leakage into a space from adjoining areas, such as interstitial spaces, of higher pressurization. Moisture leakage from a space of higher partial vapor pressure to one of lower partial vapor pressure may also be described as infiltration, even when one space is at a lower static pressure. ISPE. International Society for Pharmaceutical Engineering. ISO. International Organization for Standardization. ISO 14644-1. Specifies classification of air cleanliness by par- ticle concentration. Only particle populations having cumulative distributions based on threshold (lower limit) particle sizes rang- ing from 0. 1�m to 5 �m are considered for classification purposes. ISO (International Organization for Standardization) Standard 14644-1 is an international standard for cleanrooms. Table 1 and Figure 1 summarize the ISO standard classes. 19.1 | {}
0258ee70-3d09-40ff-8428-450d917e9795 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 19.2 2019 ASHRAE Handbook-HVAC Applications (SI) Table 1 Airborne Particle Concentration Limits by Cleanliness Class per ISO Standard 14644-1 (2015) ¦ ISO 14644 ¦ 0.1 ¦ m ¦ 0.2 m ¦ ¦ 0.3 m ¦ 0.5 ¦ m ¦ 1.0 ¦ m ¦ ¦ ¦ ¦ 5.0 m ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Class ¦ Particles per m3 ¦ Particles per m3 ¦ Particles per m3 ¦ Particles per m3 ¦ Particles per m3 ¦ Particles per m3 ¦ Particles per m3 ¦ Particles per m3 ¦ Particles per m3 ¦ Particles per m3 ¦ Particles per m3 ¦ Particles per m3 ¦ Particles per m3 ¦ ¦ 1 ¦ 10 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 2 ¦ ¦ 100 ¦ ¦ 24 ¦ ¦ 10 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 3 ¦ ¦ 1000 ¦ ¦ 237 ¦ ¦ 102 ¦ ¦ 35 ¦ ¦ ¦ ¦ ¦ ¦ ¦ 4 ¦ ¦ 10 000 ¦ ¦ 2370 ¦ ¦ 1020 ¦ ¦ 352 ¦ ¦ 83 ¦ ¦ ¦ ¦ ¦ 5 ¦ 100 000 ¦ ¦ ¦ 23 700 ¦ ¦ 10 200 ¦ ¦ 3520 ¦ ¦ 832 ¦ ¦ ¦ ¦ ¦ 6 ¦ ¦ 1 000 000 ¦ ¦ 237 000 ¦ ¦ 102 000 ¦ ¦ 35 200 ¦ ¦ 8320 ¦ ¦ 293 ¦ ¦ ¦ 7 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 352 000 ¦ ¦ 83 200 ¦ ¦ 2930 ¦ ¦ ¦ 8 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 3 520 000 ¦ ¦ 832 000 ¦ ¦ 29 300 ¦ ¦ ¦ 9 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 35 200 000 ¦ ¦ 8 320 000 ¦ ¦ 293 000 ¦ ¦ Source: ISO Standard 14644-1. Note: Maximum concentration limits (particles/m3 of air) for particles equal to and larger than considered sizes shown in table. All concentrations in table are cumulative (e.g., for ISO Class 5, the 10 200 particles shown at 0.3 m include all particles equal to and greater than this size). Cn = 10N(0.1/D)2.08 where Cn = concentration limits in particles/m3, N = ISO class, and D = particle diameter in m ISO 14644-2. Specifies monitoring to provide evidence of clean- room performance related to air cleanliness by particle concentration. ISO 14644-3. Specifies test methods. ISO 14644-8. Specifies classification of air cleanliness by chem- ical concentration (ACC). Laminar Flow. Air flowing in parallel paths, without mixing be- tween paths. Leakage. The movement of air into or out of a space due to un- controlled enclosure leaks and its pressure relationship to surround- ing space(s). Makeup Air. Outdoor air introduced to the air system for venti- lation, pressurization, and replacement of exhaust air. Minienvironment/Isolator. A barrier, enclosure, or glove box that isolates products from production personnel and other contam- ination sources to control or improve process consistency while re- ducing resource consumption. Monodispersed Particles. An aerosol with a narrow band of particle sizes, generally used for challenging and rating HEPA and UPLA air filters. Most Penetrating Particle Size (MPPS). The particle size that has the highest rate of filter penetration, or the particle size for which a filter has the least removal efficiency. Most penetrating arti- cle size is a function of the filter media, construction, aerosol den- sity, and air velocity. Non-unidirectional Flow Workstation. A workstation without unidirectional airflow patterns and velocities. Inc. ASHRAE, 2019 user. single for Licensed Offset Flow. The sum of all space leakage airflows; the net flow difference between supply airflow rate minus the exhaust and return airflow rates. Operational Cleanroom. A cleanroom in normal operation mode with all specified services, production equipment, materials, and personnel present and performing their normal work functions. Oral Product. A pharmaceutical product to be taken by mouth by the patient. OP. Operating parameter. PAO. Polyalphaolefin, a substitute for DOP in testing HEPA fil- ters. Parenteral Product. A pharmaceutical product to be injected into the patient. Parenterals are manufactured under aseptic conditions or are terminally sterilized to destroy bacteria and meet aseptic require- ments. Particle Concentration. The number of individual particles per unit volume of air (e.g., number per cubic meter per ISO 14644 or number per cubic foot for non ISO). Particle Size. The apparent maximum linear dimension of a par- ticle in the plane of observation. m3 PER PARTICLES X-Axis: Particle Size, μm Y-Axis: Count Chart Type: line ISO-9 ISO-8 ISO-7 ISO-6 ISO-5 ISO-3 item_01 1000000Count 1000000Count 10000Count 1000Count 100000Count 15000Count Fig. 1 Air Cleanliness Classifications in ISO Standard 14644-1 Polydispersed Particles. An aerosol with a broad band of particle sizes, generally used to leak-test filters and filter framing systems. Qualification. Formal, quality-driven, thoroughly documented pharmaceutical commissioning activities undertaken to demon- strate that utilities and equipment are suitable for their intended use, and perform properly and consistently. These activities necessarily precede manufacturing drug products at the commercial scale, and usually consist of installation, operational, and performance testing procedures generated by engineering and quality teams. Qualification Protocol (QP). A written description of activities necessary to qualify a specific cleanroom and its systems, with re- quired approval signatures. Room Classification. Room air cleanliness class (Figure 1, Table 1). SOP. Standard operating procedure. Topical Product. A pharmaceutical product to be applied to the skin or soft tissue as a liquid, cream, or ointment, which therefore does not need to be aseptic. Sterile ophthalmic products, though, are usually manufactured aseptically. ULPA (Ultralow-penetration Air) Filter. A filter with a minimum of 99.999% efficiency at 0.12 m particle size. | {}
f99cf68d-b484-48ae-be51-7daf869bc228 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Clean Spaces 19.3 Unidirectional Flow. Air flowing in a constant direction uni- formly over a defined space or region (different from laminar flow). v alidation. A systematic, quality-driven approach for verify- ing and documenting that a pharmaceutical process is designed, installed, functions, and is maintained properly, involving sequen- tial executions of installation qualification, operational qualifica- tion, and performance qualification activities. w orkstation. An open or enclosed work surface with direct air supply. 2. CLEAN SPACES AND CLEANROOM APPLICATIONS Use of clean space environments in manufacturing, packaging, and research continues to grow as technology advances and the need for control and containment of airborne particles in work environ- ments increases. This chapter focuses on state-of-the-art facility design and operations to improve quality and resource efficiency in a worldwide industry that provides great benefits and consumes sig- nificant energy. The following major industries use clean spaces for their products: · Pharmaceuticals/Biotechnology. Preparations of pharmaceuti- cal, biological, and medical products require clean spaces to con- trol viable (living) and nonviable particles that could impact product sterility. · Microelectronics/Semiconductors, Advances in semiconductor microelectronics drive cleanroom design. Semiconductor facili- ties are a significant percentage of all cleanrooms in operation in the United States, with most newer semiconductor cleanrooms being ISO Standard 14644-1 Class 5 or cleaner. · Flat Panel Display. FPD factories are some of the largest clean- rooms, with some cleanrooms greater than 200 000 m2, requiring adherence to ISO 14644-1 Classes 5 to 8 throughout the factory. They typically change cleanliness requirements by process area and risk of exposure to the product. These facilities may produce liquid crystal, light-emitting diodes (LEDs), and organic light- emitting diodes based displays. · Aerospace. Cleanrooms were first developed for aerospace appli- cations to manufacture and assemble satellites, missiles, and aero- space electronics. Most applications involve large-volume spaces with cleanliness levels ofISO Standard 14644-1 Class 8 or cleaner. · Hospitals. Operating rooms may be classified as cleanrooms, but their primary function is more to limit particular types of contam- ination than to control the quantity of particles present. Clean- rooms are used in patient isolation and surgery where risks of infection and cross contamination must be controlled, and in hos- pital pharmacies, where compounding sterile pharmaceuticals requires stringent control of the immediate and surrounding envi- ronments. For more information, see Chapter 9. · Miscellaneous Applications. Cleanrooms are also used in aseptic food processing and packaging, microelectronic and nanotech ap- plications, medical device manufacturing, automotive paint booths, crystal, laser/optic industries, and advanced materials re- search. 3. AIRBORNE PARTICLES AND PARTICLE CONTROL Airborne particles occur in nature as pollen, bacteria, miscella- neous living and dead organisms, and windblown dust and sea spray. Industry generates particles from combustion, chemical vapors, manipulation of material, and friction in moving equipment. Person- nel working in the cleanrooms are a prime source of particle gener- ation (e.g., skin flakes, hair, clothing lint, cosmetics, respiratory emissions, bacteria from perspiration). Sizes of airborne particles vary from 0.001 to several hundred micrometres ( m). Although itis common for airborne particles of sizes larger than 5.0 m to settle quickly due to gravity, it may take days for some forms of airborne particles smaller than 1.0 m to settle (barring intervention and con- trol mechanisms applied to the space). In many manufacturing pro- cesses, airborne particles are a source of contamination or facilitate spread of biological contaminants. Cleanroom designs must accom- modate particulate sources and focus on particulate control to main- tain acceptable environmental conditions. Locations and sizes of return and exhaust registers are important considerations, as are lay- outs of equipment and locations and sizes of supply registers. Particle Sources in Clean Spaces In general, the origins of cleanroom particles are described as either external or internal. · External Sources. Externally sourced particles enter the clean space from the outside via infiltration through doors, windows, wall penetrations, surface contamination on personnel, material and equipment entering the space, and outdoor makeup air enter- ing through the HVAC system. In a typical cleanroom, external particle sources normally have little effect on overall cleanroom particle concentration because HEPA filters remove particulates from the supply air and the cleanroom is operated at a higher pres- sure than surrounding spaces to prevent infiltration. However, the particle concentration in clean spaces at rest relates directly to ambient particle concentrations. Particles from external sources are controlled primarily by air filtration, room pressurization, and sealing space penetrations. · Internal Sources. People, cleanroom surface shedding, process equipment, and the manufacturing process itself can generate particles in clean spaces. Cleanroom personnel, if not properly gowned, may be the largest source of internal particulate genera- tion, generating several thousand to several million particles per minute. Personnel-generated particles are controlled with proper gowning procedures, including new cleanroom garments, and air- flow designed to continually shower critical areas with clean air and direct less-clean airstreams toward the return/exhaust regis- ters. As personnel work in the cleanroom, their movements may reentrain airborne particles from other sources by creating turbu- lent air movement, eddies, and vortexes. Other activities, such as writing, printing, or moving and bumping equipment may also cause higher particle concentrations. Door swings or equipment challenges can produce strong additional transient differential pressure excursions, which may lead to particle infiltration through crack and crevices. Though particle concentrations in the cleanroom air may be used to define its cleanliness class, actual particle deposition on the product critical surface is of greater concern. In addition to the ISO 14644-1 standard covering classification by airborne particle concentration, ISO 14644-8 specifies classification of air cleanli- ness by chemical concentration (ACC), which is critical to many organic-based processes, and ISO 14644-9 and 14644-10 cover classification of surface cleanliness by particle and chemical con- centration. The sciences of aerosols, filter theory, and fluid motions are the primary sources of understanding nonvolatile residue depo- sition and contamination control (IEST Recommended Practice RP CC016). Cleanroom designers may not be able to control or prevent internal particle generation completely, but they may anticipate internal sources and design control mechanisms and airflow pat- terns to limit their effect on the product. Particle counters are used to measure particle counts and concentrations for selected locations in the cleanroom and provide control feedback. They should be well calibrated to ensure accuracy and reliability of con- tamination control (ISO 21501). Inc. ASHRAE, 2019 user. single for Licensed | {}
69f95039-b09b-4277-b327-a482a3205877 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 19.4 2019 ASHRAE Handbook-HVAC Applications (SI) Fibrous Air Filters Proper air filtration prevents most externally generated particles from entering the cleanroom via the HV AC system. High-efficiency air filters come in two types: high-efficiency particulate air (HEPA) filters and ultralow-penetration air (ULPA) filters. HEPA or Group H filters (ISO 29463) are individually tested, and their efficiency is between 99.95 and 99.995% at most penetrating particle size (MPPS), in accordance with ISO 29463-5. ULPA or Group U (ISO 29463) filters are individually tested, and their efficiency is between 99.999 and 99.999995% at MPPS, in accordance with ISO 29463- 5. HEPA and ULPA filters use glass fiber paper technology; lami- nates and nonglass media for special applications also have been developed. HEPA and ULPA filters are usually constructed in a minipleat form with aluminum, coated string, filter paper, or hot- melt adhesives as pleating separators. Filters pleat depths are avail- able from 25 to 300 mm; available filter media surface area increases with deeper-pleated filters and closer pleat spacing, which reduces filter pressure drop and increases dirt holding capacity. There are four common mechanisms by which HEPA and ULPA filters capture particulate: (1) straining, (2) inertia, (3) interception, and (4) diffusion. In addition, some systems use electromagnetic forces to enhance HEPA and ULPA filter performance (see the sec- tion on Sustainability and Energy Conservation in Cleanrooms for details). In straining capture, sometimes called sieving, particles enter passages between two or more fibers that have dimensions less than the particle diameter (most of these particles are captured in prefilters). In inertia capture, particles traveling in airstream through fiber material have too much mass to stay in the airstream as it bends through the filter fibers; particles leave the airstream and attach to filter fibers. In interception capture, particles with mass small enough to stay in the airstream nevertheless touch the filter fiber and are attached. In diffusion capture, very small particles move randomly through Brownian motion; they touch and subse- quently attach to filter fibers. Theories and models verified by em- pirical data indicate that interception and diffusion are the more effective capture mechanisms for smaller particles in HEPA and ULPA filters. In general, fibrous filters' lowest removal efficiency corresponds to the most penetrating particle size, which is deter- mined by filter fiber diameter, volume fraction or packing density, and air velocity. For most HEPA and ULPA filters, the MPPS is be- tween 0.1 to 0.3 m. Group H (HEPA) and Group U (ULPA) filter efficiency is calculated using the MPPS per ISO 29463. Table 2 pro- vides the ISO 29463 efficiency values and typical applications for Group H and U filters. 4. AIR PATTERN CONTROL Air turbulence in the clean space may be detrimental to environ- mental quality. Turbulence is strongly influenced by air supply and return configurations, air balancing adjustments, foot traffic, buoyancy effects from hot surfaces, and process equipment layout. Specifying and optimizing airflow patterns to meet operational requirements are the first steps of good cleanroom design. User requirements for cleanliness level, process equipment layout, available space for installing air pattern control device and systems (air handlers, clean workstations, environmental control compo- nents, types of recirculation air system, etc.), and project financial considerations all affect air pattern design selection. Numerous airflow pattern configurations are possible, but they fall into two general categories: non-unidirectional airflow (com- monly called turbulent or mixed flow), and unidirectional airflow (previously, often mistakenly, called laminar flow). Non-unidirectional Airflow Non-unidirectional airflow has either multiple-pass circulating characteristics or nonparallel flow streamlines. Variations are based primarily on the location of supply and return/exhaust air registers and the associated airflow rates. Examples of non-unidirectional air- flow of cleanroom systems are shown in Figures 2 and 3. Air is typ- ically supplied to the space through supply diffusers with integral HEPA filters (Figure 2) or with HEPA filters in the supply diffuser ductwork or air handler (Figure 3). In a mixed flow configuration, air is prefiltered in the supply and then HEPA filtered at workstations in the clean space (see the left side of Figure 3). Non-unidirectional airflow may provide satisfactory contamina- tion control for ISO Standard 14644-1 Classes 6 to 8. Attaining desired cleanliness classes with designs similar to Figures 2 and 3 requires terminal or in-line mounted HEPA filters to remove airborne particulates from the supply air, which improves the interior partic- ulate concentration levels through mixing. Selected air diffusers should introduce air with least amount ofinduction (to promote mix- ing) and maximize space flushing effect. Supply terminals with per- forated sheet or low induction swirl diffusers are preferred, with low level extract or return for rooms with high process dust generation. ![image](/image/placeholder) SECONDARY AIR UNIT OUTSIDE AIR HANDLER OUTSIDE AIR ) - 99.999% HEPA OR ULPA FILTERS ISO CLASS 7 NONUNIDIRECTIONAL ISO CLASS 5 AIRFLOW UNIDIRECTIONAL AIRFLOW RETURN AIR : RETURN AIR RETURN AIR Fig. 2 ISO Class 7 Non-unidirectional Cleanroom with Ducted HEPA Filter Supply Elements and ISO Class 5 Unidirectional Cleanroom with Ducted HEPA or ULPA Filter ![image](/image/placeholder) AIR-HANDLING UNIT OUTSIDE AIR IN-LINE HEPA OR ULPA FILTER ISO CLASS 5 LOCALIZED ........ ISO CLASS 7 NONUNIDIRECTIONAL AIRFLOW RETURN AIR GRILL E RETURN AIR Fig. 3 ISO Class 7 Non-unidirectional Cleanroom with HEPA Filters Located in Supply Duct and ISO Class 5 Local Workstations Inc. ASHRAE, 2019 user. single for Licensed | {}
30da78c4-b2b2-42f2-9fec-40eba0b7edbf | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Clean Spaces 19.5 Table 2 Filter Classification, per ISO 29463, of High- Efficiency Filters and Filter Media for Removing Particles in Air ¦ Filter Class and Group ¦ Overall Value ¦ Overall Value ¦ Filter Application ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Filter Class and Group ¦ Efficiency, % ¦ Penetration, % ¦ Filter Application ¦ ¦ ISO 15 E ¦ 95 ¦ 5 ¦ General ¦ ¦ ISO 20 E ¦ 99 ¦ 1 ¦ Industrial, hospital, food ¦ ¦ ISO 25 E ¦ 99.5 ¦ 0.5 ¦ Industrial, hospital, food ¦ ¦ ISO 30 E ¦ 99.90 ¦ 0.1 ¦ Industrial, hospital, food ¦ ¦ ISO 35 H ¦ 99.95 ¦ 0.05 ¦ Industrial, hospital, food ¦ ¦ ISO 40 Hd ¦ 99.99 ¦ 0.01 ¦ Unidirectional flow (semiconductor, pharmaceuticals) ¦ ¦ ISO 45 Hd ¦ 99.995 ¦ 0.005 ¦ Nanotechnology Applications ¦ ¦ ISO 50 U ¦ 99.999 ¦ 0.001 ¦ Nanotechnology Applications ¦ ¦ ISO 55 U ¦ 99.9995 ¦ 0.0005 ¦ Nanotechnology Applications ¦ ¦ ISO 60 U ¦ 99.9999 ¦ 0.0001 ¦ Nanotechnology Applications ¦ ¦ ISO 65 U ¦ 99.99995 ¦ 0.00005 ¦ Nanotechnology Applications ¦ ¦ ISO 70 U ¦ 99.99999 ¦ 0.00001 ¦ Nanotechnology Applications ¦ ¦ ISO 75 U ¦ 99.999995 ¦ 0.000005 ¦ Nanotechnology Applications ¦ When internally generated particles are of primary concern, clean workstations can be used effectively in the clean space. Unidirectional Airflow Unidirectional airflow, though not truly laminar, is characterized as air flowing in a single pass in a single direction through a clean- room with generally parallel streamlines. Ideally, flow streamlines would be uninterrupted; although personnel and equipment in the air- stream distort the streamlines, a state of constant velocity is approx- imated. Most particles that encounter an obstruction in unidirectional airflow continue around it as the airstream reestablishes itself down- stream of the obstruction. Hot surfaces and abrupt changes in flow streamlines may occur and create internal circulating paths. Identify- ing these phenomena during the design stage by using CFD modeling can help avoid high particle concentration areas. Air patterns are optimized and air turbulence is minimized in unidirectional airflow. In a unidirectional-flow space, air is typi- cally introduced through ceiling HEPA or ULPA filters and returned through a raised access floor or at the base of sidewalls. For phar- maceutical and life sciences applications, this method is not recom- mended because of the potential for biological growth under raised floors. Instead, judicial placement of supply filters and room returns allows unidirectional flow. Often, computational fluid dynamics (CFD) is used to determine these locations before construction; see Chapter 13 of the 2017 ASHRAE Handbook-Fundamentals for details on CFD. Because air enters from the entire ceiling area, this configuration produces nominally parallel airflow. In a horizontal- flow cleanroom, air enters one wall and returns on the opposite wall. A downflow cleanroom has a ceiling with HEPA filters. As the space cleanliness classification becomes more stringent, the space air change rate and the number of HEPA filters may increase. Typ- ically, for an ISO Class 5 or cleaner space, the ceiling has 70 to 100% HEPA filter coverage. Ideally, a grated or perforated floor serves as the air return/exhaust. In this configuration, clean air flows downward past a contamination source, sweeping away the contam- ination particles, and removes them directly down through the floor to prevent the particles from contacting the critical surface of a prod- uct. However, this type of floor is inappropriate for pharmaceutical cleanroom applications, which typically have solid floors and low-level wall returns. Raised-floor configurations may not be ap- propriate where there is concern for contamination under the floor. Special attention should be given to ceiling HEPA and ULPA fil- ter design, selection, and installation to ensure a leakproof ceiling system. Properly sealed filters in the ceiling can provide the cleanest air presently available in a cleanroom. HEPA and ULPA filters may be leak tested before installation, looking for filter defects, and again after installation, looking for leaks in the system used to seal the filter into the ceiling system. In a horizontal-flow cleanroom, the supply wall consists entirely of HEPA or ULPA filters supplying air at approximately 0.45 m/s or less across the entire cross section of the space. Due to higher turbu- lence, the use of higher velocities may be necessary to address high particle generation rates, but note that 0.45 m/s may be too high for some applications, and velocities above 0.36 m/s may increase par- ticle reentrainment and particle residence time. Return/exhaust air exits through the return wall at the opposite end of the space. As with the downflow cleanroom, the horizontal-flow cleanroom removes contamination generated in the space and minimizes cross con- tamination perpendicular to airflow. However, a major limitation is that downstream air particle concentration increases from entry plane to exit plane. Air leaving the filter wall is the cleanest; it then becomes contaminated by the process as it flows past the first work- station. Process activities should be arranged to have the most critical operations at the clean end of the space, with progressively less crit- ical operations located toward the return or dirty end of the space. ISO Standard 14644-1 does not specify velocity requirements, so the actual velocity is as specified by the owner or owner's agent. IEST published rule-of-thumb air change rates for various cleanli- ness classes (IEST RP CC012.3), which should be reviewed by the owner; however, the scientific basis for the ranges is unclear. Accept- able cleanliness class has been demonstrated with much lower air change rates (Xu 2003, 2004), suggesting that the actual particle concentration and cleanliness level may also depend on filter effi- ciency, filter coverage, and particle generation rates, in addition to air change rates. ISO Standard 14644-2 requires an owner to un- derstand the risk to maintaining clean spaces' cleanliness and to prepare a monitoring plan to ensure cleanliness levels are main- tained. Monitoring plans should take into account the level of air cleanliness required, critical locations, and performance attributes of the cleanroom that may affect performance of the space. These attributes should be identified during the risk assessment and may include room pressurization, room air velocity, HEPA filter leak testing, air change rates, etc. Any reduced air change rate design should be factored into risk assessment and monitoring plans. Unidirectional airflow systems have a predictable airflow path that airborne particles tend to follow. Without good filtration prac- tices, unidirectional airflow only indicates a predictable path for particles. However, superior cleanroom performance may be ob- tained with, in addition to other measures, a good understanding of unidirectional airflow, which remains parallel to below the normal work surface height of 760 to 915 mm, but deteriorates when it en- counters obstacles (e.g., process equipment, work benches) or over excessive distances. Personnel movement also disturbs airflow pat- terns, resulting in a cleanroom with areas of good unidirectional air- flow and areas of turbulent airflow. Turbulent zones have countercurrents of air with high velocities, reverse flow, or no flow at all (stagnancy). Countercurrents can pro- duce stagnant zones where small particles may cluster and settle onto surfaces or product; they may also lift particles from contami- nated surfaces and deposit them on product surfaces. Cleanroom mockups may help designers minimize and avoid tur- bulent airflow zones and countercurrents. Smoke, neutral-buoyancy helium-filled soap bubbles, and nitrogen vapor fogs can make air streamlines visible in the mockup. Computational Fluid Dynamics (CFD) Air is the primary carrier of heat, moisture, contaminants, and particles in cleanroom facilities. The distribution of supply air deter- mines the resulting air velocities, temperatures, and concentration of Inc. ASHRAE, 2019 user. single for Licensed | {}
d2459794-8631-40c8-8328-a6b7e23b75ff | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 19.6 particles at various locations in a cleanroom. Such distribution in turn determines thermal comfort and air quality. Satisfactory ther- mal comfort for occupants, higher energy efficiency, and maintain- ing the desired cleanliness are mutually competing goals. Obtaining these goals by optimizing various design and operating parameters of cleanroom air distribution systems is a daunting task. Airflow patterns, temperature, and particle distribution in a cleanroom can depend on several interrelated factors, including location of supply diffusers, supply air flow rates (air change rates) and associated diffuser throws, supply air temperature, size and locations of room return, leakage areas and associated airflow rates, locations and strengths of various heat sources in a room, location and size of obstructions to airflow, and relative location and strength of particle-generating entities in a cleanroom. Physical testing and measurements to study the influence of all these factors on the ther- mal comfort, energy efficiency, and level of cleanliness are time consuming and labor intensive, if not impossible. In this situation, analysis of various realistic scenarios through computational fluid dynamics (CFD) simulations is an attractive alternative. In critical applications, it is good practice to verify the CFD predicted results. Computational fluid dynamics analysis can predict airflow pat- terns, resulting temperature distribution, particle concentration, relative humidity distribution, and resulting thermal comfort of oc- cupants in confined spaces such as cleanrooms. In addition, CFD is routinely used to predict wind patterns around buildings to evaluate impact of wind on environmental dispersion, wind pressure on building facade, and pedestrian comfort. In cleanroom design anal- ysis, it is used to predict the effects of room pressurization (i.e., rel- ative supply and return airflow rates, locations of supply and returns, particle generation rate on the distribution of cleanliness in a room). CFD analysis can help provide deep insight into real-life operation of cleanroom at the conceptual design stage, which in turn can help in optimizing the operating parameters and in reducing the first and operating costs of HVAC systems. CFD involves solving and analyzing transport equations of fluid flow, heat transfer, mass transfer, and turbulence. The transport of mass, momentum, energy, and chemical species are governed by a generalized conservation principle that can be described in the form of a general differential equation. During this CFD procedure, the calculation domain (extent of space) is divided into a number of nonoverlapping control volumes, such that there is one control vol- ume surrounding each grid point. Then, each governing differential equation is iteratively balanced over each control volume to con- serve the mass, momentum, energy, and other similar physical enti- ties. During iteration, the residual error for each governing equation is monitored and reduced. This process continues until the overall balance in the conservation of all the governing entities reaches the acceptable or desired level. Finally, such converged numerical solu- tions reveal a detailed distribution of pressure, velocities, turbulence parameters, temperature, concentration of chemical species, etc., in the calculation domain. CFD results can be presented in color contour plots showing three-dimensional distributions of temperature and particle concen- trations in cleanrooms. Flow path lines and vectors plots are used to reveal airflow patterns in a room. Flow animations also help in visu- alizing air and particle movement in a room. CFD models of particle trajectories, transport mechanisms, and contamination propagation are commercially available. Flow analy- sis with computer models may compare flow fields associated with different process equipment, work benches, robots, building exterior envelope, personnel, and building structural design. Flow patterns and air streamlines are analyzed by computational fluid dynamics for laminar and turbulent flow where incompressibility and uniform thermophysical properties are assumed. Using CFD modeling in actual cleanroom design and layout planning, design parameters 2019 ASHRAE Handbook-HVAC Applications (SI) may be modified and optimized to determine the effect of airflow control and space or equipment layouts on particle transport, flow streamlines, and contamination concentrations, thus reducing or avoiding the cost of mockups (Tung et al. 2010; Yang et al. 2009). Major features and benefits associated with most computer flow models are · Two- or three-dimensional modeling of cleanroom configura- tions, including people and equipment · Modeling of unidirectional airflows · Multiple air inlets and outlets of varying sizes and velocities · Allowances for varying boundary conditions associated with walls, floors, and ceilings · Aerodynamic and buoyancy effects of process equipment, work- benches, and people · Prediction of specific airflow patterns, velocities, and temperature gradients of all or part of a cleanroom · Simulation of space pressures by arranging supply, return, ex- haust, and planned exfiltration and infiltration airflows · Reduced cost associated with new cleanroom design verification · Identifying particle deposition risks to open wafers in some metrology tools · Recognition of temperature hot spots · Projection of particulate loading in the air spaces · Calculation of flow fields and their effect on particulate control · Use of chemical dispersion to aid airborne molecular contaminant (AMC) mitigation strategies · Identification of recirculation zones and design features that may lead to detrimental airflow · Raised-floor damper balancing · Determining preliminary raised floor damper position settings · Graphical representation of flow streamlines and velocity vectors to assist in flow analysis (Figures 4, 5, and 7) ![image](/image/placeholder) ↑ ↑ / ↑ / Fig. 4 Cleanroom Airflow Velocity Vectors Generated by Computer Simulation ![image](/image/placeholder) PROTECTIVE SCREENING WORK SURFACE Fig.5 Computer Modeling of Cleanroom Airflow Streamlines Inc. ASHRAE, 2019 user. single for Licensed | {}
96b107ad-5099-44a2-96c6-293233f26240 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Clean Spaces 19.7 · Graphical representation of simulated particle trajectories and propagation (Figures 6 and 8) Research has shown good agreement between flow modeling by computer and physical experimentation done in simple mockups. However, computer flow modeling software should not be consid- ered a panacea for cleanroom design because of the variability of individual project conditions. For more information on CFD, see Chapter 13 of the 2017 ASH- RAE Handbook- -Fundamentals. Air Change Rate Determination Cleanroom HVAC systems are highly energy intensive (Lowell et al. 1999), and can have an energy use index of between 2543 kWh/ m2 and 3819 kWh/m2 (Boyd 2011) for pharmaceutical factories and greater than 10 000 kWh/m2 for semiconductor factories. Airflow rates in cleanrooms must meet not only the heating and cooling loads, but also the contaminant dilution requirements to reduce room particle concentration. It is critical to realize that particle contami- nants generated in a cleanroom are not from HEP A-filtered supply air, but from activities inside the cleanroom. A very high air change rate is not typically needed for cooling, heating, or ventilation loads but mainly for controlling and diluting particle concentrations. There is a precedent of cleanroom design engineers using conservative, simplified rule-of-thumb values for air change rates published in IEST RP-12.3, supplier literature, or guidance documents from var- ious government or industry sources. This approach uses the re- quired room cleanliness class alone to suggest an air change per hour (ach) value, often arbitrarily, from a wide range specified in older documents and therefore ignores many critical variables that could significantly affect the room particle concentration in terms of air ![image](/image/placeholder) 。 。 。 · 0 。 0 。 。 。 0 0 · 。 。 。 。 0 0 。 0 。 。 0 0 。 。 。 。 0 · 0 0 。 。 。 0 · 。 o 0 0 。 · CONTAMINATION 。 。 0 0 。 SOURCE POINT ○○ 。 。 o · 。 。 。 · 0 。 。 。 · 수 。 。 。 · · PROTECTIVE 。 。 。 · · BARRIER 。 。 。 ° · 。 。 。 · · 。 。 。 · · 。 。 。 · . 。 。 。 · 0 。 。 。 · 0 。 。 。 · · 。 。 。 · · o 。 。 。 0 · 。 。 0 。 。 。 수 0 · PRODUCT 0 。 。 。 · 。 。 。 · · · LOCATION 。 ○ - 。 。 0 。 。 O · · · WORK 。 ○ 。 · 0 。 。 o 수 · · SURFACE 。 ○ ○ 。 。 0 · 。 。 。 0 · · 。 。 ○ ○ 。 0 . 0 。 。 。 . 0 · 0 。 ○ 。 。 。 0 0 。 。 。 수 。 。 ○ ○ ○ 。 。 。 。 。 。 · · 。 ○ ○ 。 。 O 。 0 。 。 。 0 · 。 。 ○ 。 ○ O 。 · 。 。 。 · 。 。 ○ ○ 。 。 。 · 。 。 。 · 0 。 ○ ○ 。 。 。 0 。 。 O 수 。 ○ ○ 。 。 。 · 。 。 。 O · 。 ○ ○ 。 。 。 · 。 。 O . 。 ○ 。 ○ 。 0 0 。 。 。 ° · 0 。 。 。 。 0 0 。 。 0 · 0 · 0 。 。 ○ 。 。 0 · 。 。 。 · 0 · O 。 。 。 。 0 · 。 。 。 · 0 · · 。 ○ 。 。 · · 。 · 。 ○ 。 。 0 · 0 · 。 。 0 0 ○ 。 。 · · 。 。 0 · 0 。 。 · · 。 。 。 · ° 。 0 0 · O . · 0 · 이 0 · 。 ° · 。 · · · 0 · 0 0 0 수 · . 수 0 · · 。 。 0 6 수 · · 0 · 0 0 0 수 · · 수 0 수 0 。 。 。 。 · · 0 ⑥ 0 。 0 0 0 후 0 0 。 。 。 。 · 0 o 0 0 0 。 。 。 o 0 0 。 · 0 0 0 0 。 。 。 。 · · 0 。 。 0 o 수 0 · 0 · 。 0 0 0 0 0 0 0 · 0 O · · · . · 。 。 0 0 0 。 。 。 0 0 0 0 0 。 。 0 0 。 0 0 0 0 0 0 0 0 。 0 · 。 Fig. 6 Computer Simulation ofParticle Propagation in Cleanroom change rate requirements. Such variables include room internal par- ticle size and generation rate, particle surface deposition, particle en- try through filtered supply air, particle exit through return and exhaust air, air leakage (particle loss or gain) under pressurization or depressurization, layout of processes, and locations of supply, return, and exhaust registers. Intuitively, for example, activities that gener- ate higher levels of particle concentration would need a higher air change rate to dilute particle concentration than those that generate lower levels of particle concentration, but existing practices use an oversimplified approach that ignores such differences. Each cleanroom facility is unique; its location, building construction, production or process activities, space configurations, HVAC systems, room cleanliness requirements, etc., can impact the air change requirement for each room. Using a rough, oversimplified approach without considering all these variables could cause either significant energy waste or poorly designed HVAC systems. Xu (2003, 2004) found that airflow rates or air velocities for cleanrooms in actual operation exhibited lower values than those described in IEST RP CC012.3. In attempts to offset expected contamination generation rates, some operating cleanrooms may be overdesigned and may operate at higher airflow rates or airflow velocities than necessary, resulting in significant energy waste. To save fan and thermal energy in clean- room HVAC systems, modeling technologies have been developed and published that provide more scientifically based, quantitative design tools (rather than rule-of-thumb values) (Sun 2008; Sun et al. 2010). Figure 9 shows the measured airflow rates and airflow velocities of actual ISO Class 5 and Class 6 cleanrooms in the United States in comparison with the typical ranges exhibited in IEST RP CC012.3. Demand Control Airflow Demand control is used in many applications such as variable- air-volume systems to control room temperature, variable water flow to control a coil's capacity, and demand control ventilation to decrease airflow to spaces during low occupancy. Additionally, demand-based control has been widely applied to research labora- tory spaces to vary lab room air change rates in real time based on active sensing of both particulate and chemical containment levels. Extensive studies of lab room environmental conditions (Sharp 2010) have shown that the air quality in labs is typically acceptable over 98% of the time, which can allow significant savings in HVAC energy costs by reducing airflow to as low as 2 ach during these time periods. For the 1 or 2% of the time that chemical or particulate con- taminants are sensed in the lab the air flow is raised to a high level to rapidly purge the lab of these contaminants. Although less commonly used, this same technology and ap- proach can also be applied to control cleanroom airflows. ASHRAE research project RP-1604, Demand Based Control for Cleanrooms (Sun [in progress]), is examining this concept and will provide qualitative data on the effectiveness of this approach. Lawrence Berkeley National Laboratory has also demonstrated the concept of demand based control in cleanrooms and shown its feasibility (Faulkner et al. 1996, 2008). The benefit of demand control in a cleanroom is a significant reduction in the average airflow rate and thus a large reduction in energy use. Typically, a room is actually challenged with particle emissions only for a small amount of time. Consequently, the best approach for controlling cleanroom air change rates is to vary the rate as needed based on the real-time quality of the cleanroom 's air. When the cleanroom is clean of particles and other potential con- taminants, the air change rate can be dropped significantly: perhaps one-halfto one-quarter the nominal operating air change rate. When particles or other contaminants are detected, the air change rate can be increased to the nominal rates or beyond, to provide a faster purge of the contaminants. Inc. ASHRAE, 2019 user. single for Licensed | {}
819ad771-24b0-4a48-a6e7-cdbd8d24727c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 19.8 2019 ASHRAE Handbook-HVAC Applications (SI) ![image](/image/placeholder) Particles (#/ft3) 100 90 80 70 60 50 40 30 20 10 0 (A) (B) Fig. 7 Computer Simulated Airflow Patterns in Minienvironment Cleanroom: (A) Unidirectional Flow and (B) Mixed Flow (CFD analysis provided by Kishor Khankari, Ph.D., President, AnSight LLC, Ann Arbor, MI) - - - ![image](/image/placeholder) Particles (#/ft3) 100 90 80 70 60 50 40 30 20 10 0 (A) (B) Fig. 8 Computer Simulated Particle Concentration in Minienvironment Cleanroom Showing (A) Lower Particle Concentration in Minienvironment and Higher Concentration near Person because of Recirculation of Air around Occupant and (B) Particle Cloud of 35 311 particles/m3 with Higher Particle Concentration near Occupant's Face (CFD analysis provided by Kishor Khankari, Ph.D., President, AnSight LLC, Ann Arbor, MI) Implementing a dynamic approach to controlling minimum air change rates requires the ability to continuously measure particles in the cleanroom, but other parameters of interest (e.g., total volatile organic compounds [TVOCs], carbon dioxide, humidity) may be desirable as well. This information may then be integrated with the building management system for control purposes. Different sensing approaches may be used to implement this con- cept. Individual sensors may be deployed in the cleanrooms ofinter- est, or a manifolded sensing system may be used for a potentially more cost-effective deployment. With this latter approach, one cen- tral set of sensors is used in a multiplexed fashion to sense not one, but many different rooms or areas. With this system, packets of air are sequentially drawn down to the central sensor for individual measurement on a periodic basis. 5. AIRFLOW DIRECTION CONTROL BETWEEN CLEAN SP ACES Airflow direction control between clean spaces having different cleanliness classifications is complex but critical to prevent air- borne cross contamination. Particulate contaminants could infil- trate a cleanroom through doors, cracks, pass-throughs, and other penetrations for pipes, ducts, conduits, etc. An effective method of contamination control is control of space pressurization: air moves from spaces with higher pressures to adjacent spaces with lower pressures. Normally, the cleanest cleanroom(s) with the most crit- ical operations should be designed with the highest pressure, having decreasing pressures correspond to lower cleanliness clas- sifications. The desired flow path should be from the area of cleanest, most critical environmental requirements to less clean Inc. ASHRAE, 2019 user. single for Licensed | {}
efa8c7e8-1271-4c72-a9a0-0f17cdce38e3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Clean Spaces 19.9 Chart Type: bar FAN TOWER DISTRI-BUTED AHU FAN-FILTER UNIT item_01 0.01/h 0.31/h 0.01/h Fig. 9 Actual versus Recommended Cleanroom Airflow Rates (Based on data from Xu 2004 and IEST RP CC012.3) areas, progressively cascading down through less clean areas, and finally down to uncontrolled (dirty) areas. Space Pressurization Controlling contaminants in cleanrooms requires controlling the direction ofairflow between adjacent spaces that have various levels of cleanliness classification(s). This is achieved by establishing and maintaining a pressure differential between the spaces. The pressur- ization set point for a space can be used to prevent contamination from entering the space by being positive relative to all surrounding spaces or to prevent contamination of other spaces by being negative relative to all surrounding spaces. Air pressure differences are cre- ated mechanically between spaces to introduce intentional air movement paths through space leakage or openings (Sun 2003, 2005). These openings could be designated (e.g., doorways, mate- rial transfer tunnel) or undesignated (e.g., air gaps around door- frames, other cracks). Pressurization resists infiltration of unfiltered external sources of contaminants. It can be achieved by arranging controlled flow rates of supply, return, and exhaust airstreams to each space based on the following rules: · Positive Pressurization: entering (supply) airflow rate is higher than leaving (exhaust and/or return) airflow rate in the space. · Negative Pressurization: entering (supply) airflow rate is lower than leaving (exhaust and/or return) airflow rate in the space. A cleanroom envelope (including doors) is a natural barrier to contain airborne contaminants' (e.g., particle, microbial, chemical gas) migration. However, when a door is opened for traffic, the ini- tial pressure differential across the door/envelope disappears much more quickly (typically in less than 0.25 s) than a door operation cycle (typically 6 to 10 s) closes the door, and is also much quicker than any airflow control devices (e.g., air valves) to modulate from prior flow positions to the new positions (1 to 2 s). The magnitude of particle migration is much higher at the door-in-operation (dynamic) condition than at the door-closed (static) condition. Additional treatment is required and associated design criteria need to be considered for the door-in-operation condition. An effective mechanism to tackle this issue is to install a two- door airlock with a proper time delay. A time delay between two doors can allow the airlock room air to be fully or partially replaced by filtered clean air. Airlock can reduce particle migration not only during door operations, but also in closed door conditions. Chart Type: line 0 1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 item_01 0ls 0ls 0ls 0ls 0ls 0ls 0ls 0ls 0ls 0ls 0ls 0ls 0ls 0ls 0ls 0ls 0ls 0ls 0ls 0ls 0ls Fig. 10 Flow Rate Through Leakage Area under Pressure Differential Recommended minimum pressure differentials ( P) across cleanroom envelopes are based on findings from ASHRAE research project RP-1431 (Sun et al. 2011). The static (door closed) P requirement is the same for adjacent rooms of all class differences: 10 Pa P across a cleanroom door in respect to adjacent areas is required to minimize particle migration. When an adjacent area across the door is two classes (or more) dirtier than the cleanliness class of the cleanroom, installation of an airlock (see Figure 12) may be required to maintain acceptable pressurization conditions when doors are opened/dynamic (depending on the daily frequency of the door operation). This requirement does vary with the respective ISO class of adjacent rooms. For a difference of only one class between rooms, no airlock installation is required. For a two-class difference, airlock installation is required only when door operation is frequent (more than 30 times daily). For a difference of three classes (or more) and cleanrooms surrounded by noncleanroom areas, airlock installation is required regardless of door use frequency. When airlock installation is necessary, · A two-door airlock should replace a single door separating the two areas. · A minimum pressure of 5 Pa is necessary across each door of the airlock. · There should be a time delay between the two doors in the airlock. Detailed information can be found in ASHRAE (2017). Differential pressure between any two spaces is normally de- signed at 12.5 Pa or less. A space's differential airflow rate is often called offset flow, which is the sum of all mechanically driven airflows (in or out, which correlates with space leakage). Figure 10 shows the relation- ship between leakage flow rates at a specific pressure differential across an opening. Each curve on the chart represents a different leakage area. Once a leakage area along a doorframe is estimated, then the air leakage rate through the door cracks while the door is closed can be calculated based on the pressure difference across the door. Space airtightness (sealing of the facility, fixtures, and penetra- tions) is the key element in the relationship between the space's flow offset value and the resulting pressure differential, and each space's airtightness is unique and unknown unless tested. Treatment of a Inc. ASHRAE, 2019 user. single for Licensed | {}
129a028f-417d-4610-8db4-d77405754ff1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 19.10 2019 ASHRAE Handbook-HVAC Applications (SI) space's offset value defines a pressurization control strategy. Typical pressurization control techniques include the following: · · Direct pressure-differential control (DP) uses a pressure dif- ferential sensor to measure the pressure difference between a controlled space and an adjacent space (e.g., a corridor). DP is suitable for a tightly constructed space with airlocks and/or lim- ited traffic. It basically ignores the specific offset value as re- quired; instead, it directly controls the airflow control devices to achieve the required pressure differential between the controlled space and an adjacent space. A door switch is recommended to trigger a reduced pressure-differential set point if the door opens or the DP control is based on average readings over a period of time (e.g., polling every 10 seconds and averaging over a minute). · Differential flow tracking control (DF) assumes an offset value and refines it through commissioning; this value is then used as a volumetric or mass flow difference between supply and return/ exhaust airflows through their airflow control devices. This method is suitable for open-style spaces or spaces with frequent traffic. DF normally maintains the same airflow offset value throughout operation to maintain constant space pressurization. A constant- percentage airflow offset value is sometimes used, but this creates a lower space pressurization at lower flow and may cause space pressurization reversal in facilities having multiple pressurization cascades. Hybrid control (DF+DP) (or cascaded control) combines the pressure accuracy of DP and the stability of DF. The offset value is resettable based on the pressure differential reading. The offset value reset schedule is predetermined, and the controller' s param- calibrated in the field. eters are adjusted or manually Multiple-Space (Suite) Pressurization Pressurization for a suite of clean manufacturing spaces is more complex. In practice, unforeseen air leakage interactions between spaces can lead to facility operational challenges. Because most of the air leaking out of one space leaks into another, adjusting one space's offset value often affects adjacent spaces' pressurization and can result in ripple effects. HVAC automation systems must provide stable control over supply, return, and exhaust to maintain the facility and environmental operational requirements. Careful facility de- signs and space layout arrangements are needed to minimize opera- tional space pressurization challenges; overlooking this can cause difficulties in commissioning and operation. Properly designed facil- ities and control systems can avoid pressurization challenges such as sporadic, unstable, or unachievable pressurization requirements. For more information and procedures, consult the sources in the Bibli- ography. A space pressure and flow (P&F) diagram for the controlled area (suite, zone, or floor) is often provided in design documents, and can be used as the basis of continuous quality control of cleanroom environmental parameters. The system flow diagrams should indicate · Airflow design settings (values) of all supply, return, and exhausts for each space inside the controlled area · Desired space pressure value with an acceptable tolerance in each pressure-controlled space · Resulting leakage flow directions (due to space pressure differen- tials) and their estimated leakage flow values through doors at closed-door conditions · Room particulate classifications The three traditional pressure-control methods (DP, DF, and DF+DP) require field adjustments of airflow offset values to achieve the differential pressurization values specified during de- sign. A robust strategy is to control all spaces' pressures together as an optimized system, instead of independently. Adaptive DF+DP directly accounts for variable leakage flows between spaces, and actively adjusts each space's airflow offset to maintain required pressurizations continuously. It uses airflow and pressure differen- tial measurements to estimate characteristics of leakage between spaces and adjust flow offsets automatically. This adaptive ap- proach can be more effective for complex suite pressurization strat- egies. For design procedures and control strategies, see the related literature in the Bibliography. 6. TESTING CLEAN AIR AND CLEAN SPACES The first standard written for a clean manufacturing room, or cleanroom, was published by the U.S. Air Force in March 1961. Technical Order (TO) 00-25-203 (USAF 1961) was the first stan- dard with wide appeal to science and industry. In 1963, a group of experts chaired by J. Gordon King created the first U.S. federal standard: U.S. General Services Administration (GSA) Federal Standard (FS) FED-STD-209, "Cleanroom and work station requirements, controlled environments. " In 1966, it was released as FED-STD-209A, "Air-borne particulate cleanliness classes in cleanrooms and clean zones, " and was revised several times over the years. Other cleanroom standards had been issued by many other countries, including Australia, France, Germany, Hol- land, Japan, and the United Kingdom. With the evolution of the global economy, the need for an international standard for clean- rooms became apparent. In 1993, International Organization for Standardization (ISO) Technical Committee TC 209 produced the first international cleanroom standard: ISO 14644, "Cleanrooms and associated controlled environments. , Finally, in 2001, FS 209 was canceled and superseded by the ISO 14644 standards, and other countries around the world followed suit. Three basic test conditions are used to evaluate a facility: (1) as built, (2) at rest, and (3) operational. As-built condition is the stage in which the cleanroom is built, but with none of the equipment or fixtures installed. At-rest condition refers to the state of having equipment and fixtures installed and operational, but without per- sonnel. Operational condition is where the equipment and fixtures are all installed and operational, and personnel are present. A clean- room cannot be fully evaluated until it is tested in operational con- dition. Thus, techniques for conducting initial performance tests and operational monitoring must be similar. Although cleanroom classification by particle concentration is the prevalent method of evaluation, additional cleanroom attributes may also be tested based on operations and products specific to a given clean space. ISO 14644 standards provide several different attribute testing methods and classification criteria. The test or tests applied are determined by the cleanliness attributes of interest. The following cleanliness attribute tests can be chosen: · Air pressure difference test · Airflow test · Airflow direction test and visualization · Recovery test · Temperature test · Humidity test · Installed filter system leakage test · Containment leak test · Electrostatic and ion generator tests · Particle deposition test · Segregation test The ISO 14644 standards also provide for certification by chem- ical concentration for clean spaces concerned with chemicals in the air, such as organic light-emitting diode (OLED) display manufac- turing or photolithographic areas in a semiconductor facility. As noted previously, sources of contamination can be generated within the space or infiltrate into the space from an external source. The level of space contamination can be monitored using discrete Inc. ASHRAE, 2019 user. single for Licensed | {}
419d86ad-3f77-4948-9a35-edeb9371780b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Clean Spaces 19.11 particle counters or aerosol photometers, which use laser or light- scattering principles for detecting particles of 0.01 to 5 m. For par- ticles 5 m and larger, microscopic counting can be used, with particles collected on a membrane filter through which a specific volume of sample air has been drawn. HEPA filters in unidirectional flow and ISO Standard 14644-1 Class 5 (or cleaner) should be tested for pinhole leaks at the filter media, sealant between media and filter frame, filter frame gasket, and filter bank supporting frames. The filter frame interface with the wall or ceiling should also be tested. A filter bank pinhole leak can be extremely critical, because the leakage rate varies inversely as the square of the pressure drop across the hole (the industry term pin- hole used to describe the leak site is a misnomer; the size is almost never that of a hole formed by a pin, but is actually many times smaller). IEST testing procedures describe 12 tests for cleanrooms. The tests that are applicable to each specific cleanroom project must be determined based on the specific cleanroom's criteria. 7. PHARMACEUTICAL AND BIOMANUFACTURING CLEAN SP ACES Pharmaceutical product manufacturing facilities require careful assessment of many factors, including HVAC, controls, room fin- ishes, process equipment, room operations, and utilities. Flow of equipment, personnel, and product must also be considered along with system flexibility, redundancy, and maintenance shutdown strategies. It is important to involve designers, operators, commis- sioning staff, quality control, maintenance, constructors, validation personnel, and the production representative during the conceptual stage of design. Critical variables for room environment and types of controls vary greatly with the clean space's intended purpose. It is particularly important to determine critical parameters with quality assurance to set limits and safety factors for temperature, humidity, room pressure, and other control requirements. In the United States, regulatory requirements and specification documents such as current good manufacturing practice (CGMP) for finished pharmaceuticals (FDA 2008) and for sterile products (FDA 2004), ISPE guidelines (ISPE 2001, 2009, 2011), and Nation- al Fire Protection Association (NFPA) standards describe CGMP requirements. The goal of CGMP is to achieve a proper and repeat- able method of producing therapeutic, medical, and similar prod- ucts free from microbial and particle contaminants. One factor that differentiates pharmaceutical processing suites from other clean spaces (e.g., for electronic and aerospace) is the requirement to meet government regulations and inspection for product licensing (e.g., U.S. Food and Drug Administration [FDA]). It is important to include the appropriate regulatory arms, such as the FDA 's Center for Biologics Evaluation and Research (CBER) or the Center for Drug Evaluation and Research (CDER), early in the concept design process. Design Process It is important to develop a qualification plan (QP) early in the design process. Functional requirement specifications (FRS), critical parameters and acceptance criteria, installation qualification (IQ), operational qualification (OQ), and performance qualification (PQ) in the cleanroom suites are all required to ensure proper process per- formance and validation. IQ, OQ, and PQ protocols, in part, set the acceptance criteria and control limits for critical environmental parameters such as temperature, humidity, room pressurization, air change rates, and operating particle counts (or air classifications). These protocols must receive defined discipline approvals in compli- ance with the owner's quality policies. The qualification plan must also address master document updates, SOPs, preventive mainte- nance (PM), and operator and maintenance personnel training. The quality of pharmaceutical products depends on the proper establishment of critical validation parameters and protocols. This ensures that the pharmaceutical manufacturing operations are executed properly and consistently, and maintained such that any deviations from the critical control parameters are identified, addressed, and mitigated. The pharmaceutical process must remain under control throughout the entire product life cycle, so it is import- ant for engineers and designers to avoid including tangential or non- process-impacting parameters on the list of validated parameters. For example, while processing room temperature and relative humidity may be critical to a product's production, the associated air handler's chilled water flow rate and/or temperature are not, as long as the critical parameters are maintained within the requirements of the pharmaceutical process. The same logic often justifies not vali- dating the facility's electrical supply or the drainage system if they do not have a direct impact on the product or process quality. Over validating can create a lot of additional paperwork in the original val- idation plan submittal, and a lot of unnecessary monitoring and reporting on deviations or excursions that don't impact the opera- tions directly. It is wise to limit the systems, sequences, and equip- ment in the validation plan to only the essential items that impact the pharmaceutical product or process. The technical design process often begins with piping and instrumentation diagrams (P&IDs) depicting the relationships between process equipment, utility systems, and control instrumen- tation. It is critical to document the physical sequence of equipment and systems throughout the design and installation processes, as well as how these systems interconnect, to ensure drug product quality and consistency. During design, these diagrams also provide the basis for developing system control schemes, process work and material flows, and further safety and operational investigations, such as the hazard and operability study (HAZOP). Piping and instrument diagrams are necessary early in the facil- ity design process to ensure design goals are achieved, with two types playing a central role in HV AC system design: · Room classification and pressurization diagrams typically consist of a facility room layout plan drawing visually coded to indicate required pharmaceutical room classifications. Room pressurization values and directions often are shown on this dia- gram because differential pressure between rooms is critical to maintain required the environmental quality. · Air handler zoning layout diagrams show the service area of each air handler system (or subsystem) on a plan view ofthe facil- ity room layout. This diagram is used to optimize HVAC system layouts to minimize cross contamination issues, and to enhance facility operational responses to equipment failure and mainte- nance service outages. It is often necessary to segregate the exhaust and return HVAC system paths from other HVAC sys- tems to prevent cross contamination. System flow and room pressurization diagrams are used through- out the facility design process, and can be used as the basis of con- tinuous quality control of cleanroom environmental parameters. Itis critical to develop HVAC system layouts in conjunction with envi- ronmental quality requirements (room classifications) to minimize process contamination risks, promote stable facility pressurization strategies, and minimize facility operational challenges during equipment servicing. Biomanufacturing and pharmaceutical aseptic clean spaces are typically arranged in operational suites based on specific process and formulation requirements. For example, common convention positions an aseptic core (ISO Standard 14644-1 Class 5) filling area in the innermost room, which is at the highest pressure, sur- rounded by areas of descending pressure and increasing particulate classes and bacterial levels (see Figure 1 1). Inc. ASHRAE, 2019 user. single for Licensed | {}
1e342bfb-63d8-4f45-a51f-771f80a1ebc2 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 19.12 In aseptic processing facilities, the area of highest cleanliness is intentionally placed with lower-cleanliness areas surrounding it, separated by airlocks and room pressure differentials. A positive pressure difference of 10 to 15 Pa between air cleanliness classifi- cations is common (FDA 2004), with the higher-cleanliness space having the higher pressure. Lower pressure differences may be acceptable if they are proven effective. A pressure differential is generally accepted as good manufacturing practice to inhibit parti- cles from entering a clean suite. Where there are spaces adjoined in series that all have different cleanliness classifications, a multiple-step pressurization cascade should be implemented, which should have air flow from the clean- est spaces to the least clean spaces. Normally, three pressure steps are used for ISO Class 6, 7, or 8 applications; four pressure steps are desirable for Class 5 or cleaner applications. Air locks are effective at minimizing potential particle contamination from surrounding nonclassified or less-clean areas; selection depends on the type of cleanroom (Figure 12), because some that involve fume or biologi- cal agent operations may have a containment provision. For biolog- ical agent operations, the U.S. Centers for Disease Control and Prevention (CDC) and National Institutes of Health (NIH) define four biosafety levels (BSL-1 to BSL-4), discussed in more detail in Chapter 16. An air lock is a transitional room between adjacent rooms to pre- vent airborne cross contamination. Based on relative space pressure levels, air locks can be classified as follows: · Cascading: Air lock pressure is between pressures in cleanroom and corridor · Bubble: Air lock pressure is above pressures in cleanroom and corridor AIR LOCK WITH INTERLOCKED DOORS ![image](/image/placeholder) PRODUCT OUT GOWN ( ++ ) ASEPTIC CORE I ( ++ ) DEGOWN ISO CLASS 7 ASEPTIC FILL ( +++ ) ( +++ ) AUTO- MECH. AUTO- OVEN MECHANICAL AUTO- CLAVE SPACE CLAVE SPACE CLAVE ( ++ ) ( + ) FORMULA GLASS WASH PREPARATION ISO CLASS 8 ISO CLASS 8 ( +) (+) (+ ) UNIDIRECTIONAL AIRFLOW (CURTAINED AREA OPTIONAL) MATERIAL EQUIPMENT PERSONNEL ( + ) = ROOM PRESSURIZATION LEVEL ABOVE ZERO REFERENCE Fig. 11 Typical Aseptic Suite 2019 ASHRAE Handbook-HVAC Applications (SI) · Sink: Air lock pressure is below pressures in cleanroom and cor- ridor · Dual-compartment: A bubble and a sink air lock are connected Double-door air locks are often used at cleanroom entrances and exits. A required time delay (RTD) needs to be specified between door openings, so both are not open simultaneously, to minimize possible contamination opportunities. The RTD should be long enough for HEPA-filtered clean supply air to partially or fully replace the entire air volume ofthe air lock room at least once before the second door is allowed to open. RTD operational procedures often use hard interlocks (i.e., the second door cannot be opened until after the required time delay) or soft interlocks, in which pro- cedures are supplemented by lights or alarms. Design Concerns for Pharmaceutical Cleanrooms Proper design and qualification of a manufacturing facility is required under part 211, subpart C, of the CGMP regulations on Buildings and Facilities. Section 501(a)(2)(B) of the Act (21 U.S.C. 351[a][2][B]) states the following: A drug 4 · 4 shall be deemed to be adulterated · · 4 if · · 4 the methods used in, or the facilities or controls used for, its manufacture, processing, packing, or holding do not con- form to or are not operated or administered in conformity with current good manufacturing practice to assure that such drug meets the requirements of this Act as to safety and has the identity and strength, and meets the quality and purity characteristics, which it purports or is repre- sented to possess. · · · CGMP regulations require that man- ufacturing processes be designed and controlled to assure that in-process materials and the finished product meet predetermined quality requirements and do so consis- tently and reliably. Qualification of utilities and equipment is critical to demonstrate and document compliance with all requirements, and generally includes the following activities: · Selecting utilities and equipment construction materials, operat- ing principles, and performance characteristics based on whether they are appropriate for their specific uses. · Verifying that utility systems and equipment are built as designed and installed in compliance with the design specifications, with proper materials, capacity, and functions, and properly connected and calibrated. · Verifying that utility systems and equipment operate in accor- dance with the process requirements in all anticipated operating ranges. This should include challenging the equipment or system functions while under load comparable to that expected during routine production. It should also include the performance of interventions, stoppage, and start-up as is expected during routine production. Operating ranges should be shown capable of being held as long as would be necessary during routine production. Before any batch from the process is commercially distributed for use by consumers, a manufacturer should have a high degree of confidence in the performance of the manufacturing process and that it will consistently produce APIs and drug products meeting requirements relating to identity, strength, quality, purity, and potency. Assurance should be obtained from objective information and data that demonstrates that the commercial manufacturing pro- cess is capable of consistently producing acceptable quality. Manufacturers must establish control procedures that monitor the output and validate the performance of manufacturing processes to prevent variability in the in-process material and the drug product. Engineering responsibility includes identifying any and all variables Inc. ASHRAE, 2019 user. single for Licensed | {}
00fe20c9-7c0b-4bf9-bcf9-c8f73085140d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Clean Spaces 19.13 that may foreseeably affect product or process quality, and assessing these potential problems during quality-driven risk analysis. Careful identification and control of variables that can affect product and process quality is necessary to ensure system performance and com- pliance. Utility system designs emphasizing performance stability and consistency through appropriate controls, alarms, and routine maintenance and inspections are required for compliance with phar- maceutical regulations. A lack of compensation for HEPA filter load- ing is a common HVAC system qualification challenge; if airflow or pressure controls are not used, appropriate alternative controls or alarms are required for documentation of continuous compliance. For most cleanroom applications, a routine environmental monitor- ing program verifies that the critical parameter of room cleanliness is being maintained. For holding rooms and other specialized applica- tions, ensuring the stability of HV AC system performance through air filter loading compensation is usually the most effective way to support consistent facility operations. The owner and designer must define the tolerable range of vari- able value (acceptance criterion) for each critical parameter. The product's safety, identity, strength, purity, and quality must be demonstrated to be unadulterated in that range. The owner should de- fine action alarm points at the limits of acceptance criteria, beyond which exposed product may be adulterated. The designer should se- lect tighter (but achievable) target design values for critical parame- ters (in the range of acceptance criteria), along with appropriate critical parameter monitoring strategies and values for warning alerts and actionable alarms. Facilities manufacturing penicillin or similar antibiotics (e.g., cephalosporins) must be physically isolated from other manufactur- ing areas and served by a dedicated HVAC system. Other processes also require dedicated HVAC systems, including high-potency formulas and formulas that must have dedicated production facili- ties. Facilities manufacturing aseptic/sterile products derived from chemical synthesis may have different requirements than those manufacturing biological or biotechnological products. The owner must define the inspecting agency's requirements. The United States Pharmacopoeia (USP) limits temperatures to which finished pharmaceutical products may be exposed to 15 to 25°C. The production facility may need tighter limits than these, based on the owner's observed product data. Personnel comfort is also a factor in design. Personnel perspiring in their protective overgarments can increase particulate and microbial counts, so lower temperatures and tighter temperature control may be advan- tageous. Relative humidity may be critical to the product' s integrity. Some products are processed or packaged cold and need a low room dew point to prevent condensation on equipment and vials. Some prod- ucts are hygroscopic and require lower humidity than a condensing coil can provide; in that case, consider desiccant dehumidification. Caution must be taken in designing low-humidity (i.e., low-vapor- pressure) spaces to ensure limited moisture migration through walls and ceilings bordering an unclean space. Low-humidity spaces should be provided with air locks to reduce moisture propa- gation into the low-humidity cleanroom. The importance of positive pressure increases when moisture infiltration potential becomes an element of the design process. Humidification is usually needed for personnel comfort but not usually for product needs; it may also be needed where dust might present an explosion hazard or where low humidity may hinder handling of dry materials. Clean steam (free of chemicals and other additives) is preferred for humidification because it is free of bacteria, but the humidification system should be free of amines or other contaminants if space air might contact the product. Humidification control systems often require careful sensor placement in critical areas and safety shutoff monitors to pre- vent overhumidification. Although airborne particles and viable organisms may be mini- mized by dilution with high air change rates and by supplying fil- tered air, the most effective control is to minimize release of these contaminants in the space. Personnel and machinery are the most common sources of contamination, and can be isolated from the product by gowning, masks, and isolation barriers. Careful study of how each space operates should reveal the most probable sources of contaminants and help the HVAC designer determine dilution air quantities and locate supply air outlets and return air inlets. Avoid duct liners and silencers in supply air ductwork where contaminants can collect and bacterial and mold spores can accumulate. Ensure special attention is paid to cleaning and degreasing of metal sheeting CLEANROOM AIR LOCK TYPES ¦ AIRFLOW CORRIDOR AIRFLOW CORRIDOR + ¦ AIRFLOW CORRIDOR AIRFLOW CORRIDOR + ¦ AIRFLOW CORRIDOR AIRFLOW CORRIDOR + ¦ AIRFLOW CORRIDOR AIRFLOW CORRIDOR + ¦ CLEANROOM AIR LOCK APPLICATION STRATEGIES ¦ CLEANROOM AIR LOCK APPLICATION STRATEGIES ¦ CLEANROOM AIR LOCK APPLICATION STRATEGIES ¦ CLEANROOM AIR LOCK APPLICATION STRATEGIES ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ AIRFLOW CORRIDOR AIRFLOW CORRIDOR + ¦ AIRFLOW CORRIDOR AIRFLOW CORRIDOR + ¦ AIRFLOW CORRIDOR AIRFLOW CORRIDOR + ¦ AIRFLOW CORRIDOR AIRFLOW CORRIDOR + ¦ Type of Cleanroom ¦ Air Lock Type ¦ Purpose of Air Lock ¦ Relative Pressure Relationship ¦ ¦ AIR LOCK ++ AIRFLOW CLEANROOM +++ ¦ ¦ ¦ AIR LOCK ++ AIRFLOW CLEANROOM ¦ · Positive pressure · No fume or bio agent · No containment needed ¦ Cascading ¦ · Prevent cleanroom being contaminated by dirty corridor air · Prevent cleanroom being contaminated from surrounding spaces through cracks ¦ Cleanroom: +++ Air lock: ++ Corridor: + ¦ ¦ AIR LOCK ++ AIRFLOW CLEANROOM +++ ¦ · Negative pressure · Has fume or bio agent contamination · Containment needed ¦ Bubble ¦ AIR LOCK ++ AIRFLOW CLEANROOM ¦ · Prevent cleanroom being contaminated by dirty corridor air · Prevent cleanroom fume or bio agent releasing to corridor ¦ Cleanroom: Air lock: ++ Corridor: + ¦ ¦ ¦ ¦ A. CASCADING B. BUBBLE ¦ A. CASCADING B. BUBBLE ¦ A. CASCADING B. BUBBLE ¦ A. CASCADING B. BUBBLE ¦ · Negative pressure · Has fume or bio agent contamination · Containment needed ¦ Sink ¦ · Provides containment · Prevent cleanroom fume or bio agent releasing to air lock. No personal protective equipment is needed. ¦ Cleanroom: Air lock: Corridor: + ¦ ¦ AIRFLOW CORRIDOR AIRFLOW CORRIDOR + - AIR LOCK ¦ AIRFLOW CORRIDOR AIRFLOW CORRIDOR + - AIR LOCK ¦ AIRFLOW CORRIDOR AIRFLOW CORRIDOR + - AIR LOCK ¦ AIRFLOW CORRIDOR AIRFLOW CORRIDOR + - AIR LOCK ¦ · Negative pressure Has toxic fume or · hazardous bio agent contamination, or has potent compound substances · Containment needed · Personal protection needed ¦ Dual- Compartment ¦ · Prevent cleanroom being contaminated by dirty corridor air · Prevent cleanroom fume or bio agent releasing to corridor · Personal protective equipment (such as pressurized suit and respirator) is required ¦ Cleanroom: - Neg. Air lock: - Pos. Air lock: ++ Corridor: - ¦ ¦ ¦ ¦ ¦ AIR LOCK AIR LOCK ++ AIRFLOW CLEANROOM ¦ · Negative pressure Has toxic fume or · hazardous bio agent contamination, or has potent compound substances · Containment needed · Personal protection needed ¦ Dual- Compartment ¦ · Prevent cleanroom being contaminated by dirty corridor air · Prevent cleanroom fume or bio agent releasing to corridor · Personal protective equipment (such as pressurized suit and respirator) is required ¦ Cleanroom: - Neg. Air lock: - Pos. Air lock: ++ Corridor: - ¦ ¦ AIRFLOW CLEANROOM C. SINK D. DUAL-COMPARTMENT ¦ AIRFLOW CLEANROOM C. SINK D. DUAL-COMPARTMENT ¦ AIRFLOW CLEANROOM C. SINK D. DUAL-COMPARTMENT ¦ AIRFLOW CLEANROOM C. SINK D. DUAL-COMPARTMENT ¦ Notes: 1. Excessive negative pressure in cleanroom is not recommended. If it is not surrounded by other clean spaces, untreated dirty air can infiltrate through cracks into cleanroom. 2. A cleanroom service corridor often must be designed slightly positive or neutral pressure. Do not design for negative pressure unless a dual-compartment lock is used. ¦ Notes: 1. Excessive negative pressure in cleanroom is not recommended. If it is not surrounded by other clean spaces, untreated dirty air can infiltrate through cracks into cleanroom. 2. A cleanroom service corridor often must be designed slightly positive or neutral pressure. Do not design for negative pressure unless a dual-compartment lock is used. ¦ Notes: 1. Excessive negative pressure in cleanroom is not recommended. If it is not surrounded by other clean spaces, untreated dirty air can infiltrate through cracks into cleanroom. 2. A cleanroom service corridor often must be designed slightly positive or neutral pressure. Do not design for negative pressure unless a dual-compartment lock is used. ¦ Notes: 1. Excessive negative pressure in cleanroom is not recommended. If it is not surrounded by other clean spaces, untreated dirty air can infiltrate through cracks into cleanroom. 2. A cleanroom service corridor often must be designed slightly positive or neutral pressure. Do not design for negative pressure unless a dual-compartment lock is used. ¦ Fig. 12 Air Lock Types and Applications Inc. ASHRAE, 2019 user. single for Licensed | {}
5e999126-df60-4ac1-9e90-779ff2994eb6 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 19.14 2019 ASHRAE Handbook-HVAC Applications (SI) and air ductwork before installation. Ensure the cleaning agent will not cause flaking of galvanized ductwork or leave residual soap. Factory-wrapped ducts and components with clean installation and inspection protocols promote cleanroom system cleanliness. Airborne particle and microbe levels in aseptic processing areas are limited by government regulations, with lower limits for more critical spaces. European and FDA particle limits are for the space in full operational mode, and can also be used conservatively as limits for the space at rest. Facilities complying with U.S. CGMPS for aseptic processing must meet particle levels with manufacturing under way. (An exception is aseptic powder processing, in which airborne partic- ulate levels at powder filling heads will exceed limits.) There should be no microbial contaminants in the critical-zone air- stream, where filling and other critical activities occur; this area should be ISO Class 5. The area immediately around the critical zone should be ISO Class 7. Ifthe critical area is within an isolator, then the area outside the isolator may be ISO Class 8. Less critical support areas can be ISO Class 8. For more detail on facility design, see FDA requirements. According to the FDA, 20 ach is usually sufficient for ISO Class 8 rooms; ISO Class 7 and 5 areas require significantly higher air change rates. Facility requirements for terminally sterilized prod- ucts are not defined. EU GMP (2008) also contains requirements for aseptic processing, and also addresses terminally sterilized products. Note that many facilities are constructed to meet both EU and U.S. GMPs (FDA 2008). Restricted access barrier systems (RABS) are an alternative to a conventional cleanroom or isolator. Use of RABS should be ap- proved by the manufacturer's quality unit during design. Once the product is in containers, the need for particulate control and minimum air changes is reduced or eliminated, depending on the degree of protection provided by product packaging. The owner should determine the necessary critical environmental parameters and acceptance criteria for each space and processing step. Return openings for space HVAC should be low on the walls, to promote downward airflow from supply to return, sweeping con- taminants to the floor and away from the product. For ISO Class 8 and lower, ceiling return or exhaust register are common. Room air quality can be improved greatly by optimizing return and exhaust register locations to route air flows away from cleaner areas, which in many cases can resolve problems more effectively than changing supply register locations. In larger spaces, internal return air col- umns may be necessary. Perforated floors are discouraged because ofthe difficulty in cleaning them. It is good design practice to avoid returning air from one air-handling unit (AHU) system to another, unless special project considerations justify this decision. Mixing AHU zones through return air pathways may lead to cross-contamination concerns and operational challenges when HVAC maintenance shutdowns affect multiple operations. Combining noncontrolled and controlled areas through return or exhaust air pathways may also lead to operational challenges by expanding controlled-area boundaries into zones with activities that may negatively influence process or product integrity. Aseptic facilities usually require pinhole-scanned (integrity- tested) HEPA filters (not ULPA) on supply air. Many facilities install HEPA filters in the supply air to nonaseptic production fa- cilities to minimize cross contamination from other manufacturing areas served by the HVAC system. To increase the life of terminal HEPA filters in aseptic facilities, and to minimize the need to re- balance the supply system because of differential loading of ter- minal HEPA filters, many designers install a high-capacity HEPA bank downstream ofthe supply air fan, with constant-volume control to compensate for primary filter pressure changes and any dehumidifier airflow. The final HEPA filter is usually in a sealed gel frame or of a one-piece lay-in design that can be caulked to the ceiling frame, maintaining the integrity of the room enve- lope. Aseptic product must be protected by pressurizing the space in which itis exposed, to about 12.5 Pa above the next lower cleanliness space classification. To keep the pressure differential from dropping to zero when a door is opened, air locks are often used between spaces of different air pressures, especially at the entrance to the aseptic fill space itself. Space pressure is a function of airflow resis- tance through cracks, openings, and permeable surfaces in the space shell. Consider all potential openings, slots, electrical outlets, annu- lar spaces around pipe penetrations, and door leakage that could affect the amount of air needed to pressurize the space. Because space offset airflows and space pressure are closely related, outdoor or makeup air requirements are often dictated by space pressures rather than by the number of occupants. The HVAC system should be able to handle more makeup air than needed for commissioning, because door seals can deteriorate over time. ISO Class 5 unidirectional hoods are commonly used in process-critical applications for aseptic processes, consisting of banks ofHEPA (or ULPA) filters, integrity-tested to be pinhole-free. Because it is difficult to maintain unidirectional flow for long dis- tances or over large areas, the hood should be located as closely as possible to product critical surfaces (work surface). Hood-face velocity is usually 0.35 to 0.45 m/s, but the user should specify velocity and uniformity requirements. The velocity measurement is commonly taken at a distance of 150 to 300 mm from the filter face to demonstrate unidirectional airflow via airflow pattern testing. A unidirectional hood usually has clear sidewalls (curtains) to promote downward airflow and prevent entrainment of space particles into the hood's zone of protection. Curtains should extend below the product critical surface and be designed to prevent accidental disruption of airflow patterns by personnel. Many production facilities prefer rigid curtains for easier cleaning and sanitization. Hood fan heat may become a problem, forcing the designer to overcool the space from which the hood draws its air or to provide sensible cooling air directly into the hood's circulating system. Decontamination Cleanrooms used for sterile operations are rarely built clean enough for their intended purpose. Before the initial use of the room or after a shutdown, the cleanroom must be decontaminated or dis- infected to ensure bioburden and particulate levels are at or below acceptable limits. For some operations, such as compounding of sterile preparations, surface disinfection is considered adequate. However, larger-scale CGMP sterile manufacturing operations typ- ically use some type of biological decontamination before final occupancy. Cleanrooms for sterile processing should be designed to accommodate decontamination or disinfection. Having originated from small-volume spaces (i.e., sealed glove boxes), most early large-volume decontamination processes includ- ed using formaldehyde gas generated by heating paraformaldehyde in a frying pan or spraying with a mild peracetic acid and wiping all surfaces, which was very labor intensive. Today, most cleanrooms are decontaminated by using either chlorine dioxide (CD) or hydro- gen peroxide. Regardless of the type of decontamination process used, the cleanroom should accommodate the process. Factors that should be considered include (1) leaktightness of the cleanroom shell, (2) compatibility of cleanroom finishes to the decontamina- tion process, and ability to (3) remotely control the process and re- circulate the gas, (4) maintain appropriate humidity levels during the decontamination process, and (5) evacuate the gas after decon- tamination is complete. Sometimes it is economically feasible to integrate the gas- generating equipment with the cleanroom air ducts. This decision is dictated by the intended gassing frequency, or by the need for Inc. ASHRAE, 2019 user. single for Licensed | {}
88c7ad70-daed-45a8-9204-d2534fe999e9 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Clean Spaces 19.15 automated recovery preparedness following any kind of bioevent. Strategically placed, airtight dampers, gas distribution nozzles, a means to agitate the gas within the cleanroom (or suite of rooms), and exhaust equipment for evacuation are some of the components necessary for automated decontamination. As with all decontami- nation procedures, protocols must be developed to demonstrate efficacy. Barrier Technology Cleanrooms designed to meet ISO Class 5 or better require con- siderable equipment, space, and maintenance. Operating such clean- rooms is expensive. Furthermore, cleanrooms typically need gowned operators inside to manipulate product and adjust machinery. Be- cause the operator can be a major source of particle generation and contamination, it is better to separate the operator from the con- trolled environment; this allows the volume of the controlled space to be reduced significantly to a point where only the process equipment is enclosed. Using such a separative device can substantially reduce capital and operating costs while meeting required airflow patterns and cleanliness levels (IEST RP CC028. 1; Xu 2007a, 2008). Separa- tive devices, including microenvironments, isolators (glove boxes), and restricted access barrier systems (RABs), are thus becoming increasingly popular. These systems are also called barrier technol- ogy in pharmaceutical applications and minienvironments in semi- conductor industries. Barrier technology systems must be designed to fit the specific application and can be highly customized to allow the tasks required to accomplish the process needs. Applications vary widely based on product, process equipment, and throughput volume. Barrier tech- nology systems are typically positive-pressure envelopes around the filling equipment with multiple glove ports for operator access, con- structed of polished stainless steel with clear, rigid view ports. Sys- tems can be fully sealed or leak into the support environment via "mouse holes" used to allow passage of vials in and out of the unit. Ancillary systems designed to prevent migration of contaminants are used for passing stoppers, containers, and tools in and out of the barrier systems. These can range from simple lock chambers to highly complex alpha/beta ports fitted with features to allow saniti- zation of the systems or contents. Important design concerns in- clude accessibility, ergonomics, integration with mating equipment, decontamination or sterilization/sanitization procedures, access to service equipment, filter change, filter certification, process valida- tion, and environmental control. Extra attention must be paid to product filling, vial, and stopper protection; access to the barrier for sterilized stoppers; interface to the vial sterilization (depyrogenation) device; sterilizing product path, including pumps and tubing; and airflow patterns inside the barrier, especially at critical points. If a vapor-forming sanitizing agent such as hydrogen peroxide is to be used as a surface sanitizer, care must be taken to ensure good circulation and adequate concen- tration inside the barrier, as well as removal of residual vapor in the required time frame. In addition, because many of the sanitizing agents are strong oxidizers, care must also be taken in selecting con- struction materials to ensure compatibility and their ability to absorb and retain or potentially outgas the sanitizing agent at a later time. Barrier technology systems may also be designed for applications requiring operator protection from high-potency and cytotoxic com- pounds (those that may have an inadvertent therapeutic effect on an operator), while maintaining a sterile internal environment. These tend to be total containment systems with totally contained product transfer ports. All internal surfaces are sealed from the external envi- ronment or potential operator exposure. Because of potential cham- ber leaks, its internal pressure may be kept negative compared to the ambient space via exhaust fans, posing an additional potential risk to the product that must be addressed by the owner. Other systems, such as a nonsterile powder control booth, may incorporate more passive barrier designs. One such design incorpo- rates a downflow sampling and weighing cubicle. This arrangement takes advantage of unidirectional airflow to wash particles down and away from the operator's breathing zone. Low-wall air returns at the rear of the cubicle capture fugitive dust. An arrangement ofroughing and final filters allows air to return to the air handlers and back to the work zone through ceiling-mounted HEPA filters. Products involv- ing noxious or solvent vapors require a once-through air design. Barrier technology allows installation in environments that might require no special control or particulate classification. Isola- tors, RABs, and containment chambers are still relatively new to the pharmaceutical industry. As such, installations for sterile products should be in a controlled ambient room condition ofISO Class 8 or better. Maintainability A facility that considers maintainability (e.g., accessibility, fre- quency of maintenance, spare parts, rapid diagnostics and repair, reliability and facility uptime) in its design will be much more reli- able and should have fewer operational and regulatory concerns. Many pharmaceutical facilities have been designed so that routine maintenance can be performed from outside the facility's clean space (except for unidirectional and terminal HEPA filters, which must be tested twice a year). Quality of materials is important to reliability, especially where failure can compromise a critical parameter or operation. Consider how much exposure and risk to product and personnel exist during maintenance (e.g., how to clean the inside of a glove box contaminated by a toxic product). Beyond cleanable room surfaces that must be sanitized, consider whether and how HVAC equipment may be decontaminated using the owner's procedures. Determine whether ductwork must be inter- nally cleaned, and how. Reduced- or no-shutdown HVAC system designs require energy-efficient and redundant components. When incorporating redundant components into systems, it is important to consider how both maintenance and removal/replacement of a com- ponent would be executed; the effect of redundancy is negated if there is no way to isolate equipment that needs to be replaced. Aligning HVAC system layouts with facility operational areas or suites can save significant operating costs and increase plant avail- ability. Controls, Monitors, and Alarms Space pressure may be maintained by passive (fixed offset) HV AC systems if there are limited airflow variables. For example, the HV AC system for a few pressurized spaces may be statically bal- anced if there is a method of maintaining supply airflow volume to compensate for filter loading to ensure minimum supply, return, and exhaust air changes. More complex designs may require dynamic pressure control. Both filling lines with conveyors and slide gates between rooms where air moves from one room to another at varying rates usually require active pressure control to maintain room 's pres- sures and their relationships at all times. It is important to avoid mul- tiple pressurization loops controlled from the same or interrelated parameters, because this can lead to space pressurization instabili- ties. Complications can result from fans in series controlling similar or related properties. Improved system stability results from con- trolling to an airflow value at the room space level, and to duct air pressure at the branch or air handler level. Pressure controls should not overreact to doors opening and closing, because it is virtually impossible to pressurize a space to 12.5 Pa with a door standing open. A door switch is often used to send a signal to space pressure control to avoid overreaction. Architectural layout may affect dynamic room pressure control. It is a good practice to position such Inc. ASHRAE, 2019 user. single for Licensed | {}
cae0c91d-c600-4538-9651-ac6a59683b6b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 19.16 2019 ASHRAE Handbook-HVAC Applications (SI) spaces away from exterior walls where wind loading exists and inte- rior corridors, which typically do not have dynamic pressure control. If space air humidity must be maintained to tolerances tighter than what normal comfort cooling can maintain, consider using active rel- ative humidity control. If a desiccant dehumidifier is needed, unit operation over its range of flow must not adversely affect the ability of the HVAC to deliver a constant air supply volume to the facility. Monitor and alarm critical parameters to prove they are under control. Log alarm data and parameter values during excursions. Logging may range from a local recorder to direct digital control (DDC) data storage with controlled access. Software source code should be traceable, with changes to software under the owner's control after qualification is complete. Commercial HVAC software is usually acceptable, but should be verified with regulatory agen- cies before detailed design begins. Also, keep complete calibration records for sensors, alarms, and recorders of critical parameter data. When establishing alarm set points, consider that for systems serving regulated industries, alarms (or deviations from operational parameter [OP] acceptance limits) often require extensive docu- mentation of the deviation, corrective actions taken, and any impact on critical processes and/or products. By setting up early warning alarm points, the operators can identify a system trending towards an operational deviation point and can intercede before the system hits its OP limits, precluding the need to prepare deviation or excur- sion reports. Noise Concerns HVAC noise is a common problem caused by attempts to over- come the pressure drop of additional air filtration. The noise level generated must be reduced in lieu of adding duct silencers, which may harbor bacteria and are difficult to clean. Separate supply and return fans running at lower tip speeds instead of a single-fan air handler may reduce generated noise levels. HV AC noise may not be an issue if production equipment is considerably noisier. For a more detailed discussion on noise and vibration issues, see Chapter 49. Nonaseptic Products Nonaseptic pharmaceutical facilities (e.g., for topical and oral products) are conceptually similar in design to those for aseptic prod- uct manufacturing (control of airborne particulate and microbial con- taminations), but with fewer critical components to be qualified. However, critical parameters such as space humidity may be more important, and airborne particle counts are not considered in the United States. If the product is potent, barrier isolation may still be advisable. Space differential pressures or airflow directions and air changes are usually critical (needed to control cross contamination of products), but no regulatory minimum pressure or air change val- ues apply. 8. START-UP AND QUALIFICA TION OF PHARMACEUTICAL CLEANROOMS Qualification of HV AC for Aseptic Pharmaceutical Manufacturing Qualification is a systematic, quality-based approach to ensuring and documenting that the pharmaceutical facility, systems, equip- ment, and processes will deliver everything required for safe and repeatable drug products, including the facility design, installation, operation, maintenance, documentation, and pharmaceutical pro- cessing, filling, capping, holding, handling, and storage. Qualifica- tion of the pharmaceutical cleanroom HVAC is part of the overall qualification of the facility. Equipment affecting critical parameters and their control must also be qualified. Other groups in the manu- facturing company (e.g., safety or environmental groups) may require similar commissioning documentation for their areas of concern. The most important objectives in meeting the approving agency's requirements are to (1) state what procedures will be fol- lowed and verify that it was done, and (2) show that product is pro- tected and space acceptance criteria are met. Qualification Plan and Acceptance Criteria Early in design, it should be determined who will be responsible for and how to produce as-built drawings, maintenance files, and training. They should create a qualification plan for the HVAC, including (1) a functional description of what the systems do along with specific process and room requirements; (2) maps of room classification and pressurizations, airflow diagrams, and cleanliness zones served by each air handler; (3) a list of critical components to be qualified, including the automation system controlling the HVAC; (4) a list of owner' s procedures that must be followed for qualification of equipment and systems that affect critical parame- ters; (5) a list of qualification procedures (IQ/OQ/PQ protocols) written especially for the project; and ⑥ a list of equipment requir- ing commissioning, determined through a risk-based product and process impact analysis. The approval procedure should be defined in the QP. It is import- ant to measure and document critical variables of a system (e.g., space pressure), but it is also important to document and record per- formance requirements and results for components that affect the critical parameters (e.g., room pressure sensors, temperature sensors, airflow volume monitor) for GMP as well as business records. Doc- umentation helps ensure that replacement parts (e.g., motors) can be specified, purchased, and installed to support critical operations. It is important to determine all components and instruments that could affect critical parameters and could, through an undetected failure, lead to product adulteration. This may be accomplished by a joint effort between the mechanical engineer, owner, quality experts, and a qualified protocol writer. If performance data are in the qualification records, replacement parts of different manufactur- ers may be installed without major change control approvals, as long as they meet performance requirements. Owner approval for the qualification plan should be obtained during detailed design. Qualification requires successfully completing the following activities for critical components and systems. The designer should understand the requirements for owner' s approval of each protocol (usually, the owner approves the blank protocol form and the sub- sequently executed protocol). The installation qualification (IQ) protocol documents con- struction inspection to verify compliance with contract documents, including completion of punch list work, for critical components. It may include material test reports, receipt verification forms, shop inspection reports, motor rotation tests, duct/equipment cleaning reports, duct leak testing, P&ID walkdowns for component instal- lation inspections, and contractor-furnished testing and balancing. It also includes calibration records for instrumentation used in com- missioning and for installed instrumentation (e.g., sensors, record- ers, transmitters, controllers, and actuators) traceable to National Institute of Standards and Technology (NIST) instruments. Control software should be bench tested, and preliminary (start- ing) tuning parameters should be entered. Control loops should be dry-loop checked to verify that subsystem installation, addressing, operation, and graphics are correct. Equipment and instruments should be tagged and wiring labeled, then field-verified against record drawings. Commissioning documentation must attest to completion of these activities and include as-built drawings and installation/operation/maintenance (IOM) manuals from contrac- tors and vendors. The operational qualification (OQ) protocol documents start- up, operation, and maintenance SOPs are correct and activated for critical systems and components. This includes individual per- formance testing of control loops under full operating pressure per- formed in a logical order (i.e., fan control before room pressure Inc. ASHRAE, 2019 user. single for Licensed | {}
7229648e-fd46-4f76-8954-793af29885b0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Clean Spaces 19.17 control). The commissioning agent must verify that operating parameters are within acceptance criteria. The HV AC system may be challenged under extremes of design load (where possible) to verify operation of alarms and recorders, to determine (and correct, if significant) weak points, and to verify control and door interlocks. Based on observations, informal alert values of critical parameters that might signify abnormal operation may be set up. Even if the product would not be adulterated at these parameter values, staff may implement an alarm to require re- sponses prior to encountering deviations from normal operation. Documented smoke tests verify space pressure and airflow in critical spaces or inside containment hoods, and show airflow pat- terns and directions around critical parts of production equipment. Many smoke tests have been videotaped, especially when space pressure differentials are lower than acceptance criteria require and pressures cannot be corrected. Files should include an updated description ofthe HV AC, describ- ing how it operates, schematics, airflow diagrams, and space pressure maps that accompany it. Copies should be readily accessible and properly filed. Operating personnel should be familiar with the data in these records and be able to explain it to an agency inspector. Other Documents. GMP documents should also include test reports for HEPA filters (efficiency or pinhole-scan integrity tests) at final operating velocities. Ifthe filter installer performed the tests, the data should be part of the IQ package. Documents should verify that instruments display, track, and store critical parameters and action alarms. Consider recording data by exception and routine documentation of data at minimal regular frequency. Systems and equipment should be entered into the owner's main- tenance program, including rough drafts of associated maintenance procedures (final drafts should reflect commissioning results). Records should document the completion of these activities, in- cluding final as-built, system diagrams, facility pressurization dia- grams, air change rate calculations, and air and water balance reports. Performance qualification (PQ) is proof that the entire HVAC system performs as intended under actual production conditions. PQ is the beginning of ongoing verification (often called validation) that the system meets acceptance criteria of the product. This in- cludes documentation of · Maintenance record keeping and final operating and maintenance procedures in place, with recommended frequency of mainte- nance, and (at the owner's option) a procedure for periodic chal- lenge of controls and alarms · Logs of critical parameters that prove the system maintains accep- tance criteria over a prescribed time · Training records of operators and maintenance personnel · Final loop tuning parameters After accepting PQ, the owner's change control procedure should limit further modifications to critical components (as shown on IQ and OQ forms) that affect the product. Much of the facility's HVAC equipment should not need qualification, but records for the entire facility must be kept up to date through quality change con- trol, and problems must be corrected before they become signifi- cant. Records of corrections should also be kept. Once the system is operational, pharmaceutical product trial lots are run in the facility (process validation) and the owner should reg- ularly monitor levels of viable (microbial) and nonviable particles, room pressurization, and other controlled parameters in the process- ing areas. 9. SEMICONDUCTOR CLEANROOMS Semiconductor wafer fabrication cleanrooms (also called wafer fabs, fabs, or chip cleanrooms) have historically been some of the largest cleanrooms. Recently, mega and giga cleanrooms (i.e., those that produce megabyte and gigabyte memory chips) have been con- structed that may exceed 40 000 m2 of under-filter clean area and produce more than 200,000 wafers per month. A new fab today may cost 10 to 15 billion U.S. dollars, is expected to be built within 10 to 12 months, and is expected to recover capital investment in less than 3 years. Wafer fabs seek to produce complicated products with extremely small feature sizes. Contamination at the wafer level can result in significant yield losses. Yield can be defined most basically as the proportion of successfully fabricated products (e.g., chips) com- pared to the total number of products that started the manufacturing process. Yield is often considered the most important financial fac- tor in the manufacturing of semiconductor devices. It is inversely proportional to manufacturing cost: the higher the yield, the lower the cost. Configuration Semiconductor wafer fabs have traditionally been designed around common manufacturing processes (e.g., photolithography, metal deposition, etching, thin film deposition, implanting, diffu- sion, planarization) These process area layouts were coupled to the subfab utility distribution with some decoupling to allow for flexi- bility in equipment tool sets. Photolithography areas, with their tight vibration, temperature, and humidity control and susceptibility to molecular contamination, were always isolated from other process areas, allowing the building structure to be tailored to the specific needs of the photo areas and save costs for other process areas. Semiconductor wafer fabs are extremely complex, with dozens of utility systems and many hazardous chemicals being used. In the absence of regulatory oversight of the manufacturing processes in pharmaceutical, medical device, and biotechnology facilities, build- ing codes have been the most consistent regulator of semiconductor fab design and construction. The collaborative development of spe- cific codes addressing semiconductors between code officials, own- ers, designers, and insurance industry has produced a set of codes that have attempted to meet the changing needs of the factories while still maintaining a safe working environment. The unique multilevel building design and operation of wafer fabs led code officials to specifically identify semiconductor fabri- cation and the special needs involved. The various code sections (building, fire, and mechanical) have addressed the handling and storage of hazardous materials, fire resistance of materials of con- struction, conveyance of hazardous materials, egress paths, safe zones, fire protection, occupancy separations, etc. Part ofthejustification of multiple levels is the need for extensive utility distribution; a typical semiconductor wafer fab can have in excess of 50 unique utilities. Fab complexity is best demonstrated by a visual of a typical multilevel wafer fab (Figure 13). Fab spaces are composed of process areas, subfabs (more than one), chases, return air plenums, and supply air plenums. Referring to Figure 13, above the ceiling of the process area are the cleanroom supply air plenums, ductwork, fan filter units (FFUs) and, in some fabs, process utilities. The ceiling structure is designed to support cleanroom filters or FFUs, the wafer automated material handling system (AMHS), lighting, ionization system, maintenance personnel, and optional monitoring devices for temperature, humidity, and particles. The area where most wafer processing occurs is typically referred to as the process area. The process area is where most cleanroom operators work and contains the process equipment main frames, wafer delivery equipment, metrology equipment, and other wafer-handling equipment. Below the process area is the subfab(s), where a hidden mass of equipment is located. Subfabs may be divided into clean and dirty subfabs, isolating potential contamination sources from the clean subfab, which in turn protects the process area. Inc. ASHRAE, 2019 user. single for Licensed | {}
43fc58dd-2a85-4f67-8811-3ed0ae77e87c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 19.18 2019 ASHRAE Handbook-HVAC Applications (SI) ![image](/image/placeholder) 4 C 00 The process area may have raised floors (most common) or a concrete slab (usually called a waffle floor due to the concrete cast- ing shape) or other structural flooring materials supporting process equipment (heavy and vibration-sensitive tools sit on isolated ped- estals and not directly on a raised floor). Some air management designs treat the space below the raised floor as an additional level, though most code authorities do not consider this a level when eval- uating building height limitations. The space below the raised floor is considered an air plenum in most jurisdictions. Contamination Control In semiconductor cleanrooms, in addition to particle concentra- tion, the most common contaminants impacting yield are airborne molecular contaminants, static charge and electromagnetic interfer- ence, and misprocessing due to electromagnetic interference with process control. Increasingly, more cleanrooms seek a controlled level of AMC concentration (i.e., chemical cleanliness class per ISO Standard 14644-8). Though not an explicit requirement, the airflow concepts used in a cleanroom have a direct impact on particle con- centration and may also affect chemical cleanliness. Cleanroom designers have had to change airflow design concepts to meet the changing semiconductor process technology. Airborne Molecular Contaminants (AMC) An increasing source of AMC in fabs is fugitive emissions asso- ciated with maintenance oflocal process exhaust scrubbers (e.g., for dopants). The fugitive emissions are exhausted to the building exte- rior and subsequently reentrained into the makeup air, and eventu- ally back into the cleanroom. Including monitoring and mitigation of these fugitive emission sources is no longer optional for a good AMC protection plan; it is essential. Wafer exposure to the chemicals in cleanroom environments presents another challenge. Deployment of fab-wide AMC filtration systems is becoming the rule rather than the exception for most pro- cess areas. Combining the fab-wide system with AMC filters at high- risk process tools helps to minimize exposure to hazardous particles. Static Charge and Electromagnetic Interference Electrostatic charge adversely impacts every phase of semicon- ductor manufacturing, causing three basic problems (SIA 2015a): · Electrostatic attraction (ESA) contamination increases as particle size decreases. ESA is becoming particularly acute with photoli- thography masks, as the use of traditional pellicles is phased out. · Electrostatic discharge (ESD) causes damage to both devices and photolithography masks. Decreasing device feature sizes means less energy is required for ESD to cause damage to a device or mask. Increased device operating speeds have decreased the effectiveness of on-chip ESD protection, and heightened device sensitivity to damage from ESD. · Equipment malfunctions caused by ESD-related electromag- netic interference (EMI) decrease overall equipment efficiency Fig. 13 Multilevel Fabs (Courtesy of M+W Group) and are becoming more frequent as equipment microprocessor operating speeds increase. Trends in ESD sensitivity will have greater impacts on manufac- turing process yields as the feature sizes of devices decrease (SIA 2015a). Cleanroom designers must understand the sources of ESD, and fab owners must verify that the installed ESD controls can han- dle these devices and must improve ESD control methods when nec- essary. EMI Control. Electromagnetic interference is defined as "the degradation of the performance of an equipment, transmission channel, or system caused by an electromagnetic disturbance" (SEMI 2012). EMI causes a number of problems for semiconductor manufacturing, such as equipment lockup and malfunction, sensor misreading, metrology errors, and sensitive component damage. Sources of EMI in semiconductor environments include electro- magnetic emission from ESD; operation of equipment, especially high-energy tools; motors and actuators; and wireless communica- tion. Colocation of sensitive equipment with high-energy tools, cabling, ground problems, improper maintenance of equipment, and other issues further aggravate EMI problems (SIA 2015a). Current practices for mitigating EMI impact are either passive-shielding the sensitive equipment or shielding the sources. Electrical transform- ers are a major source, and shielding of these in metrology areas is common practice. Semiconductor Fab Conditions Typical indoor design conditions are shown in Table 3. In the past, process requirements dictated the primary design criteria for tem- perature and humidity set points. To minimize changes in dimensions from expansion or contraction, temperature stability is needed in many atmospheric pressure processes that are exposed to the clean- room ambient temperature. Good control of dry-bulb temperature is needed to provide stability in relative humidity. Relative humidity changes can affect the performance of many hygroscopic materials used in semiconductor manufacturing. Controlling dry-bulb tem- perature and dew point can provide uniform relative humidity. Though there are hygroscopic processes in a semiconductor wafer fab, the hygroscopic forces are normally not enough to offset mois- ture gains or losses that can come from adjacent spaces with other dew points or from the introduction of makeup air. The sensible heat ratio for most wafer fabs is greater than 0.99 unless there is exposure to unconditioned spaces. Therefore, sensible cooling is the standard practice for wafer fabs. Latent cooling treatment of the entire fab recirculation air volume is normally not practical, and the adiabatic mixing of wetter or dryer air sources is a more energy-efficient method. Cleanroom Cleanliness and Airflow Concepts Design concepts are influenced by cleanroom size, building codes, process equipment footprints, cost control, energy optimiza- tion, and flexibility (among other things). Semiconductor wafer fab Inc. ASHRAE, 2019 user. single for Licensed | {}
c4988cbd-529b-4f42-a938-76fed241d08d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Clean Spaces 19.19 ![image](/image/placeholder) MANUFACTURING AUTOMATION SYSTEM CLEANROOM PROCESS EQUIPMENT MECHANICAL SYSTEM ELECTRICAL DISTRIBUTION DISTRIBUTION CRITICAL PROCESS SYSTEM FACILITY PLANT SUBSYSTEMS DISTRIBUTION EQUIPMENT TOOL INSTALL Fig. 14 Fab Environment Figures (Courtesy of M+W Group) Table 3 Process Area Environmental Conditions ¦ ¦ Temperature ¦ Temperature ¦ Relative Humidity ¦ Relative Humidity ¦ Dew Point ¦ Dew Point ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Set Point Range ¦ Tolerance ¦ Set Point Range ¦ Tolerance ¦ Set Point Range ¦ Tolerance ¦ ¦ ¦ Critical Process Areas ¦ 18 to 23°C ¦ ±0.5 to ±1°C ¦ 35 to 50% ¦ ±2 to ±3% ¦ 2.3 to 12°C ¦ ±1 to ±2°C ¦ ¦ Non-Critical Process Areas ¦ 18 to 26°C ¦ ±2°C ¦ 35 to 60% ¦ ±2 to ±5% ¦ 2.3 to 17°C ¦ ±1 to ±2°C ¦ owners expect cleanrooms that cost little per square unit area to con- struct, yet provide improved performance, are faster to build, and are easily upgraded. As product technology and the process tools have changed, so have the basic design criteria. The International Technology Roadmap for Semiconductors (ITRS) (SIA 2015b) currently recommends ISO Class 6 where operators are present and possibly ISO Class 7 in the future, though this practice is not uniformly adopted by all fab owners. ISO Class 6 does not necessarily warrant unidirectional airflow to support the cleanliness requirement. Wafer fabs continue to support unidirec- tional airflow because it makes sense in light ofthe multilevel layout of their facilities. Having air move in the same direction allows the spaces themselves to become transport conveyances. Therefore, cleanliness class does not always dictate classical unidirectional/ non-unidirectional air management paths. Options for process area air management with separate subfab airflow are (1) 100% unidirectional downflow and (2) unidirec- tional downflow for operator- and wafer-exposed areas, through the raised floor with return air upflow in service chases. Makeup Air. Makeup air plays a crucial role in the environmen- tal conditions of a wafer fab by providing replacement air for the air exhausted for process requirements, providing excess air to create positive pressure in cleanrooms, and providing a source of wetter or dryer air to help control humidity levels inside the fab. Wafer fabs require a relatively large amount of makeup air due to the physical size of their factories, and depending on the local climate, makeup air may be 20 to 30% of the total fab chiller load. Although com- mercial facilities may consider ventilation rates per person, wafer fabs tend to use a design criteria based on the area of the cleanroom. Common rates for consumer semiconductor product based wafer fabs are 50 to 100 m3/(h·m2), whereas code requirements are 18.3 m3/(h·m2). There has been a trend toward lower ventilation rates due to changes in tool configurations with fewer liquid chemical ventilation hoods (e.g., wet chemical etchants) and more dry plasma-based processes. Treatment of makeup air before its addi- tion to the cleanroom space includes moisture control (humidifica- tion or dehumidification) and filtration of external particles and airborne molecular contaminants. Humidity. Makeup air provides a means of dehumidifying or humidifying air. The makeup air introduced into the fab environ- ment is either below the space dew point, at the space dew point, or above the dew point. When itis below the space dew point, moisture must be added (humidification). When the makeup air dew point is above the space-required dew point, moisture must be removed (dehumidification). Makeup air treatment schemes must be designed for the expected climate. Fabs located in tropical climates where outdoor dew points rarely go below 20°C may not need any humidification equipment, whereas fab locations in cold or temperate climates may need both humidification and dehumidification capabilities. Control of dew point or relative humidity in a semiconductor wafer fab is also needed in many contamination control schemes. Humidity levels can affect ESD rates, particle adhesion, and cor- rosion of metal surfaces deposited on a wafer. Typically, the most Inc. ASHRAE, 2019 user. single for Licensed | {}
0094ed59-d5b3-4563-b34b-1d800fc9a3dc | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 19.20 2019 ASHRAE Handbook - HVAC Applications (SI) critical need for precise humidity control is the sensitivity of pho- toresist chemicals used in photolithography. Relative humidity and temperature are both critical for precise dimensional control and resist chemical stability. The typical semiconductor wafer fab space dew point is between 7 and 12°C, though it may be as low as -2°C or as high as 14°C to support some processes. Apart from very low dew points (less than 1.5°C), dehumidification by subcooling with chilled water is the most common method. Providing consistent dew-point control of the makeup air enables consistent moisture content of the makeup air when it is mixed with cleanroom recirculation air and can result in good relative humidity control (±2.5%) when combined with good dry-bulb temperature control. Some semiconductor wafer fabs may have process areas requiring better than ±2.0% rh. To achieve control of ±2.0% rh, the makeup air dew point must be controlled ±0.5°C. Filtration. Control of AMC is critical to maximizing yield by minimizing contamination of the photoresist and mitigating pro- gressive defects forming on masks during exposure (Mueller 2013). For makeup air equipment, including AMC filters is commonplace for most semiconductor wafer fab locations due to local pollution and reentrainment of process exhaust. AMC filters typically involve a chemical adsorption process using activated carbon, sometimes doped with other activated chemicals (e.g., permanganate-embed- ded alumina) or ion-exchange resins. Most makeup air units inte- grate their AMC filters as part of a multistep particle and AMC filtration scheme. Some AMC filters are available with particle removal efficiencies of MERV 8 to as high as MERV 15, which can help reduce the overall air pressure drop through the makeup air equipment. Air Velocity and Air Change Rate. For a given cleanroom, the supply airflow rate Q (cubic metres per second [m3/s]) is 0 = LWv 3600Q ACH = LWH or 3600L Wv 3600v ACH = LWH H where L = room length, m W = room width, m H = room height, m V = average vertical air velocity, m/s through cleanroom horizontal plane L by W ACH = air changes per hour From Equation (3), the number of air changes per hour is inversely proportional to the height of the room: the greater the height of the cleanroom, the fewer air changes per hour required, and vice versa. The exception is a clean space where contamination is generated at a (1) (2) (3) Chart Title: PSYCHROMETRIC CHART NORMAL TEMPERATURE Chart Type: line ASIA BURI NORMAL TEMPERATURE SEA LEVEL BAROMETRIC PRESSURE 101043 KPA ASHRAE 55 HUMAN COMFORT ZONE WATER FAB ENVIRONMENT item_01 -18MPA -15MPA -7MPA -4MPA -3MPA -3MPA 7MPA DRY BULB TEMPERATURE, °C Fig. 15 Wafer Fab Environment in Psychrometric Chart Inc. ASHRAE, 2019 user. single for Licensed | {}
f04c9771-2f51-4126-9b12-582ceadb203b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Clean Spaces 19.21 Table 4 High-Bay Cleanroom Air Changes per Hour Versus Average Vertical Airflow Velocity, Space Height, and Cleanliness Class ¦ ¦ ¦ Air Changes per Hour for Ceiling Height, m ¦ Air Changes per Hour for Ceiling Height, m ¦ Air Changes per Hour for Ceiling Height, m ¦ Air Changes per Hour for Ceiling Height, m ¦ Air Changes per Hour for Ceiling Height, m ¦ Air Changes per Hour for Ceiling Height, m ¦ Air Changes per Hour for Ceiling Height, m ¦ Air Changes per Hour for Ceiling Height, m ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ISO Class ¦ Velocity, m/s ¦ 12.2 ¦ 15.2 ¦ 18.4 ¦ 24.4 ¦ 30.5 ¦ 36.6 ¦ 42.7 ¦ 48.8 ¦ ¦ 2 ¦ 0.43 to 0.50 ¦ 128 to 150 ¦ 102 to 120 ¦ 85 to 100 ¦ ¦ ¦ ¦ ¦ ¦ ¦ 3 ¦ 0.35 to 0.43 ¦ 105 to 128 ¦ 84 to 102 ¦ 70 to 85 ¦ 52 to 64 ¦ ¦ ¦ ¦ ¦ ¦ 4 ¦ 0.30 to 0.35 ¦ 90 to 105 ¦ 72 to 84 ¦ 60 to 70 ¦ 45 to 52 ¦ 36 to 42 ¦ ¦ ¦ ¦ ¦ 5 ¦ 0.23 to 0.28 ¦ 68 to 83 ¦ 54 to 66 ¦ 45 to 55 ¦ 34 to 41 ¦ 27 to 33 ¦ 22 to 27 ¦ ¦ ¦ ¦ 6 ¦ 0.12 to 0.18 ¦ 38 to 53 ¦ 30 to 42 ¦ 25 to 35 ¦ 19 to 26 ¦ 15 to 21 ¦ 12 to 18 ¦ 10 to 15 ¦ ¦ ¦ 7 ¦ 0.04 to 0.08 ¦ 12 to 24 ¦ 10 to 19 ¦ 8 to 16 ¦ 6 to 12 ¦ 5 to 10 ¦ 4 to 8 ¦ 3 to 6 ¦ 3 to 2 ¦ ¦ 8 ¦ 0.02 to 0.03 ¦ 8 to 10 ¦ 5 to 7 ¦ 4 to 6 ¦ 3 to 4 ¦ 2 to 3 ¦ 2 to 3 ¦ 2 ¦ 2 ¦ ¦ 9 ¦ 0.01 to 0.015 ¦ 3 to 5 ¦ 2 to 3 ¦ 2 to 3 ¦ 2 ¦ 1 to 2 ¦ 1 to 2 ¦ 1 ¦ 1 ¦ ![image](/image/placeholder) P R H H R H C R H C PRE-FILTERS: STAGES PRE-HEAT/FREEZE FILTERS: HUMIDIFIER3 COIL TAGES FAN2 COIL FILTERS STAGES HUMIDIFIER1 DEHUMIDIFICATION REHEAT PROTECTION PRIMARY 1-2 1-3 1-2 AMC FINAL COIL: TRIM H R P H C C C HEAT RECOVERY/HEAT PIPE OPTION 1 Adiabatic or Isothermal humidifiers may be deployed. 2Fans may be in blow through position though is more common as fan heat is after primary cooling coils. 3Trim humidifiers may be located in cleanroom recirculation air path for fine humidity control in sensitive areas like photolithography. Fig. 16 Makeup Air Configuration Schemes considerable height above the finished floor. Examples include semi- conductor and flat panel display transport systems and aerospace product assembly. In these situations, the velocity may need to remain high to sweep away particles, and ACH may be fixed regard- less of the height of the space. Air Ionization. In addition to cleanroom particle control with fiber filters, air ionization can be used to control particle attraction to product surfaces by eliminating electrostatic discharge and static charge build-up. However, the emitter tip material must be carefully selected to prevent depositing particles on the product. 10. HIGH-BAY CLEANROOMS High-bay cleanrooms have ceiling heights between 12 and 50 m, with the higher ceilings used primarily in the aerospace industry for producing and testing missiles, launch vehicles, rocket engines, and communication and observation satellites, and lower ceilings pri- marily used in jet aircraft assembly, painting, and cleaning opera- tions; flat panel display manufacturing; and in crystal-pulling areas in semiconductor chips manufacturing facilities. Most high-bay cleanrooms are designed to meet ISO Class 7, Class 8 or higher as required by some U.S. Air Force and U.S. Navy specifications. Flat panel display factories may require ISO Class 5, 6, or 7. Crystal-pulling cleanrooms for semiconductor microchips are usually specified at Class 5 to Class 6 range. Table 4 shows approximate ranges of ceiling-height-dependent airflow per minute and air changes per hour by cleanroom classes derived from Equation (3). Downflow and Horizontal-Flow Designs In downflow designs, air is delivered in a unidirectional (or sim- ulated unidirectional) flow pattern from the ceiling and returned through floor return openings or low sidewall returns. The objective is to shower the object from above so that all particles are flushed to the returns. The supply air terminals may be HEPA-filter or high- volume air diffusers. Downflow spaces allow space flexibility because more than one device may be worked on in the space at the same air cleanliness level. The disadvantage is the relative difficulty of balancing airflow. High-bay cleanrooms typically have concrete floors that may include trenches to return some ofthe air not taken in atlow sidewall returns. Special care must be taken to ensure clean air at the object because the parallel flow starts to dissipate toward the floor. At the low velocities typical of unidirectional design, pathways may be created toward the returns, causing the clean air to miss the object. Any activity in the cleanroom that generates even a small amount of heat produces updrafts from buoyancy effects in downward-flowing supply air, resulting in the possibility of unforeseen turbulence. Horizontal-flow designs are always unidirectional, with the cleanest air always available to wash the object in the space. Prop- erly designed horizontal spaces are easier to balance than vertical- flow spaces because supply and return air volumes may be con- trolled at different horizontal levels in the space. Downflow designs are most widely used, but certain projects such as the space telescope and space shuttle assembly spaces may require horizontal-airflow high-bay cleanrooms (Figure 17). Air Handling Because of the large volume of air in a high-bay cleanroom, central recirculating fan systems are commonly used with minimum heating and cooling capability. A separate injection air handler provides heating, cooling, and makeup air. The injection system must include volumetric controls to ensure proper building pres- sure. Flat panel display (FPD) factories deploy thousands of fan filter units (FFUs), allowing for flexibility and ease of adding addi- tional airflow when needed. Inc. ASHRAE, 2019 user. single for Licensed | {}
7be77ba3-f7fa-4aae-8bf4-3266e60881ca | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 19.22 2019 ASHRAE Handbook-HVAC Applications (SI) ![image](/image/placeholder) RETURN DUCT SUPPLY DUCT OR CHASE OR CHASE CEILING ASSEMBLY m 45 CEILING CEILING , ↓ ↓ ↓ ↓ ↓ ↓ , · m FABRICATION FABRICATION ADMINISTRATION E↑ 15 AND SUPPLY 3 SECTION VIEW ADMINISTRATION FABRICATION ASSEMBLY FABRICATION AND SUPPLY PLAN VIEW Fig. 17 High-Bay Cleanroom Scheme Equipment and Filter Access Air-handling equipment and prefilters should be accessible from outside the cleanroom. Adequate provision must be made for chang- ing filters if air is distributed to the cleanroom with HEPA filters at the space envelope. In horizontal-flow cleanrooms, access should be from the upstream (pressure) side, and service scaffolds should be incorporated at least every 2.4 m in height of the filter bank. Down- flow ceiling filters in T-bar or gel-seal ceilings must be accessed from below using an approved gantry crane with full mobility across the ceiling or from above the ceiling with a catwalk system built into the plenum. Prefilters in the main air supply should be placed in built-up frames with both upstream and downstream access. It is important to ensure that there are no possible air bypass pathways in filter frames and their seal to the filters or to the air handler walls since this reduces the effectiveness of the air filtration. A HEPA filter bank remote from the space air-distribution system should be installed in a built-up bank with a gel or clamp seal. Access doors must be installed up- and down- stream for certification, scanning, and qualification testing. Prefilter Selection In any high-bay cleanroom cleanliness classification, air will pass through a final HEPA filter before entering the space; these final filters are usually protected by prefilters. HEPA filters for recirculating air should be protected with MERV 11 bag or rigid media filters with as few other prefilters as required. Makeup air should include minimum MERV 11 filters on the fan inlet and minimum MERV 16 filters on the fan discharge. Tight, leakproof sealing between the filters and frame/housing improves system cleanliness and reliability. Design Criteria and Indoor Air Quality The indoor design temperature range for aerospace and aircraft manufacturing cleanrooms is 23 0.3°C, with the higher tempera- tures commonly used in summer, and the lower ones in winter. However, the user should provide guidance on specific required space temperature requirements. In FPD and semiconductor crystal- pulling cleanroom design, space temperature is usually required at a constant level of22 土 0.3°C, though FPD temperature tolerance is normally within ±1 K. Another key parameter is relative humidity. For aerospace and aircraft manufacturing cleanrooms, relative humidity should not exceed 60%; FPD and semiconductor crystal-pulling cleanrooms usually require indoor relative humidity to be 50 5% as design base. Other issues include noise and vibration from process and HV AC equipment, and dusts, fumes, smoke, odors, vapors, moisture and gases generated during welding, sanding, painting, washdown, fuel filling, etc. See Chapters 8 to 12 of the 2017 ASHRAE Handbook- Fundamentals for additional information. 11. ENVIRONMENTAL SYSTEMS Cooling Loads and Cooling Methods Two major internal heat load components in cleanroom facilities are process equipment and HV AC system fans. Because most clean- rooms are located entirely within conditioned space, traditional heat sources of infiltration, fenestration, and heat conductance from adjoining spaces are typically less than 2 to 3% of the total load. Some cleanrooms have been built with windows to the outside, usu- ally for daylight awareness, and a corridor separating the cleanroom window from the exterior window. The major cooling sources designed to remove cleanroom heat and/or maintain environmental conditions are makeup air units, primary and secondary air units, and the process equipment cooling system. Some process heat, typically from electronic sources in computers and controllers, may be removed by process exhaust. In many applications, cleanroom fan systems have their motors located in the airstream, resulting in significant heat from fan opera- tion. This is especially true in ISO Class 4 or cleaner cleanrooms where recirculated airflows with air velocities of 0.45 m/s or air change rates around 500 per hour may be used. Xu (2003, 2004) found that many ISO Class 4 or 5 cleanrooms were operated with lower air velocities and lower air change rates than specified by the old or existing recommended practices, while achieving satisfactory contamination control for their specified cleanliness classes. Latent loads are primarily associated with makeup air dehumidi- fication. A low dry-bulb leaving air temperature, associated with de- humidified makeup air, supplements sensible cooling. Supplemental cooling by makeup air may account for as much as 950 W/m2 of cleanroom. Process cooling water (PCW) is used in process equipment heat exchangers, performing either simple heat transfer to cool internal heat sources, or process-specific heat transfer, in which the PCW contributes to the process reaction. Due to the superior energy effi- ciency of water cooling (versus air cooling), many process equip- ment manufacturers have redesigned their equipment to rely more on process cooling water. For many semiconductor and FPD facto- ries, process equipment loads may be used for 50 to 75% of the pro- cess equipment heat transfer. The diversity of manufacturing heat sources (the portion of total heat transferred to each cooling medium) should be well understood. When bulkhead or through-the-wall equipment is used, equipment heat loss to support chases versus to the production area affects the cooling design when the support chase is served by a different cool- ing system than the production area. Makeup Air Control of makeup air and cleanroom exhaust affects cleanroom pressurization, humidity, and room cleanliness. Makeup airflow requirements are dictated by the amounts required for (1) replacing process exhaust, (2) working personnel ventilation, and (3) meeting pressurization specifications. Makeup air volumes can be much greater than the total process exhaust volume to provide adequate pressurization and safe ventilation. Tsao et al. (2010) discusses how Inc. ASHRAE, 2019 user. single for Licensed | {}
86f05872-069b-4d70-982e-ea53b52ea835 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Clean Spaces 19.23 to optimize makeup air system design to improve its effectiveness and energy efficiency. Makeup air is frequently introduced into the primary air path on the suction side of the primary fan(s) or into a negative pressure ple- num system to enhance mixing. Makeup air volumes are adjusted with zone dampers and makeup fan controls using speed controllers, inlet vanes, etc. Opposed-blade dampers should have low leak char- acteristics and minimum hysteresis. Makeup air should be filtered before injection into the cleanroom. If the makeup air is injected upstream of the cleanroom ceiling ULPA or HEPA filters, minimum MERV 16 filters (ASHRAE Stan- dard 52.2) should be used to avoid high dust loading and reduced HEPA filter life. In addition, MERV 8 efficient prefilters followed by MERV 11 filters may be used to prolong the life of the MERV 16 filter. When makeup air is injected downstream of the main HEPA filter, further HEPA filtering of the makeup air should be added to the prefilters. In addition to particle filtering, many makeup air handlers require filters to remove chemical contaminants (e.g., salts and pollutants from industries and automobiles) present in outside air. If the makeup air is from an internal conditioned space (i.e., outdoor air is conditioned by the main facility HVAC system), the same filtration level may still be required to prevent the entry of volatile organic compounds (VOCs). These VOCs may be present from another ac- tive process in the facility or from building maintenance items such as cleaning agents and paints. Chemical filtration may be accom- plished with absorbers such as activated carbon or potassium per- manganate impregnated with activated alumina or zeolite. Process Exhaust Process exhaust handles acids, bases, solvents, toxins, pyrophoric (self-igniting) fumes, and process heat exhaust. Process exhaust should be dedicated for each fume category, by process area, or by the chemical nature of the fume and its compatibility with exhaust duct material. Typically, process exhausts are segregated into corro- sive fumes, which are ducted through plastic or fiberglass-reinforced plastic (FRP) ducts, and flammable (normally from solvents) gases and heat exhaust, which are ducted in metal ducts. Process exhaust may also be segregated by its need for pollution abatement due to air quality regulations. Care must be taken to ensure that gases cannot combine into hazardous compounds that can ignite or explode in the ductwork. Segregated heat exhausts are sometimes installed to re- cover heat, or hot uncontaminated air that may be exhausted into the suction side of the primary air path. Required process exhaust airflow rates can vary from 5 L/s per square metre of cleanroom for photolithographic process areas, to 50 L/s per square metre for wet etch, diffusion, and implant process areas. With the advent of more vacuum-based processes and less use of ambient air or wet processes, the overall exhaust rates have trend- ed downward. Many vacuum-based processes require additional abatement steps, with point-of-use (POU) abatement techniques be- ing very common. These POU abatement processes may discharge directly to the atmosphere or into one of the central exhaust systems. When specific process layouts are not designated before exhaust de- sign, an average of 25 L/s per square metre is normally acceptable for fan and abatement equipment sizing. Fume exhaust ductwork should be sized at low velocities (5 m/s) to allow for future needs. For many airborne substances, the American Conference of Gov- ernmental Industrial Hygienists (ACGIH) established requirements to avoid excessive worker exposure. The U.S. Occupational Safety and Health Administration (OSHA) set specific standards for allow- able concentrations of airborne substances. These limits are based on working experience, laboratory research, and medical data, and are subject to constant revision. See ACGIH (2007) to determine limits. Fire Safety for Exhaust International Building CodeⓇ (ICC 2012) designates semicon- ductor fabrication facilities as Group H occupancies. The Group H occupancy class should be reviewed even if the local jurisdiction does not use the IBC because it is currently the only major code in the United States specifically written for the semiconductor indus- try and, hence, can be considered usual practice. This review is par- ticularly helpful if the local jurisdiction has few semiconductor facilities. International Fire Code (IFC; ICC 2012) addresses specific re- quirements for process exhaust relating to fire safety and minimum exhaust standards. Chapter 50 of the code, Hazardous Materials, is relevant to many semiconductor cleanroom projects because of the large quantities of hazardous materials stored in these areas. Areas covered include ventilation and exhaust standards for production and storage areas, control requirements, use of gas detectors, redun- dancy and emergency power, and duct fire protection. Air Temperature and Humidity Precise air temperature control is required in most cleanrooms. Specific chemical processes may change under different tempera- tures, or masking alignment errors may occur because of product dimensional changes as a result ofthe coefficient of expansion. Tem- perature tolerances of 0.6 K are common, and precision of 0.06 to 0.3 K is likely in wafer or mask-writing process areas. Wafer reticle writing by electron beam technology requires 0.06 K, whereas photolithographic projection printers require 0.3 K tolerance. Specific process temperature control zones must be small enough to control the large air volume inertia in vertical laminar flow clean- rooms. Internal environmental controls, which allow space toler- ances of 0.6 K and larger temperature control zones, are used in many process areas. Within temperature zones of the typical semiconductor factory, latent heat loads are normally small enough to be offset by incoming makeup air. Sensible temperature is controlled with either cooling coils in the primary air stream, or unitary sensible cooling units that bypass primary air through the sensible air handler and blend con- ditioned air with unconditioned primary air. In most cleanrooms of ISO Class 6 or better, production person- nel wear full-coverage protective smocks that require cleanroom temperatures of 20°C or less. If full-coverage smocks are not used, higher temperature set points are recommended for comfort. Pro- cess temperature set points may be higher as long as product toler- ances are maintained. In semiconductor cleanrooms, air humidity levels vary from 30 to 50% rh. Humidity control and precision are necessary for the specific process requirements, prevention of condensation on cold surfaces in the cleanroom, and control of static electric forces. Humidity toler- ances vary from 0.5 to 5% rh, primarily dictated by process require- ments. Photolithographic areas have more precise standards and lower set points. The exposure timing of photoresists (used in pho- tolithography) can be affected by varying relative humidity. Negative resists typically require low (35 to 45%) relative humidity. Positive resists tend to be more stable, so the relative humidity can go up to 50% where there is less of a static electricity problem. Independent makeup units should control the dew point in places where direct-expansion refrigeration, chilled-water/glycol cooling coils, or chemical dehumidification is used. Chemical dehumidifica- tion is rarely used in semiconductor facilities because of the high maintenance cost and potential for chemical contamination in the cleanroom. Although some cleanrooms may not require significant reheat, many systems are designed to provide heat to the space to support temperature control during normal operation and when production equipment is not operating. However, when relative humidity control is required, a large amount of energy may be lost Inc. ASHRAE, 2019 user. single for Licensed | {}
2626444f-6569-462c-9d4c-192171496931 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 19.24 2019 ASHRAE Handbook-HVAC Applications (SI) when conditioning more air than necessary. Instead of bringing all the return air down to a low humidity level and then reheating, a sys- tem that optimizes the amount of return that goes through the air han- dler to avoid excesses is often significantly more energy efficient. Makeup air and/or supply air humidification often uses steam humidifiers or atomizing equipment, with steam humidifiers being the most common. Good design practices include avoiding water treatment chemicals through clean steam generation. Stainless-steel unitary packaged boilers with high-purity water and stainless-steel piping have also been used. Water sprayers in the cleanroom return use air-operated water jet sprayers. Evaporative coolers can take advantage of the sensible cooling effect in dry climates. Air Pressurization Controlling air pressures in a cleanroom is an important part of effective contamination control, providing resistance to infiltration of external sources of contaminants. In nonpressurized spaces, or spaces with air pressures lower than that of the surrounding envi- ronment, nearby particulate contaminants enter the cleanroom by infiltration through doors, cracks, pass-throughs, and other penetra- tions for pipes, ducts, etc. A cleanroom with the most stringent cleanliness requirements should have the highest air pressure rela- tive to its adjacent rooms, with decreasing room pressures corre- sponding to decreasing cleanliness levels. For small cleanrooms or clean zones in ISO Classes 8 and 9, ceil- ing supply and low sidewall return is a typical airflow arrangement. The primary air system alone can handle the internal cooling load and the required room air change rate. Pressurization system de- signs are very similar to those in pharmaceutical facilities. For semiconductor cleanrooms with ISO Class 7 or cleaner, pri- mary/secondary air systems are common. The secondary (makeup) HVAC unit takes care of the outside air and internal cooling loads, and the primary (recirculating) unit delivers the required room air change rate, and additional cooling if needed. A raised, perforated floor return is common for these classes. During balancing, manual or automatic balance dampers are usually set at fixed positions at air supply, return, and exhaust systems. In vertical- and unidirectional-flow cleanrooms, single-stage constant volume for supply and return flows is common. Because internal dust generation from people and process could be lower during nonoperating or unoccupied mode than operating or occu- pied mode, using multiple recirculating blowers to create two- or multiple-stage supply and return flow rates is feasible as long as the room cleanliness meets the designated classification at all times, validated through continuous particle count measurement. In non- operating or unoccupied mode, reduced levels of supply and return airflow rates should also ensure maintaining proper room pressur- ization level. Pressure level in the cleanroom is principally established by room airtightness and the offset flow value, which is the net flow rate difference between supply airflow rate and exhaust and return airflow rates. Process equipment exhaust rate is often determined by manufacturers' data, industrial hygienists, and codes. The design engineer should consult with the facility contamination control specialist to determine effective and efficient air change rates for each cleanroom. One common method of cleanroom pressurization is to keep the supply airflow rate constant while adjusting the return airflow rate by volume dampers at return floor panels to create a specified positive space pressure. Return air to underfloor plenum or subfloor base- ment through perforated panels floor grilles or grates (usually with a 15 to 35% free area) can be balanced to ensure a fixed flow differen- tial (offset flow) in the space. An adjustable, lockable balance damper normally is attached beneath the perforated floor panel or grate. When the damper is fully open, it normally creates a minimal pressure drop of 5 to 20 Pa. Higher pressure drops can be achieved when the dampers are turning toward the closed positions. Note that the position of balance damper opening could affect parallelism of the room s unidirectional flow. Another method uses variable-air-volume supply and return fans with volumetric airflow rates tracking to ensure the required room pressure. This method could be a reasonable choice for a single, large cleanroom, but is not flexible enough to serve a suite with dif- ferent room pressure requirements. For some industries, variable- air-volume systems may not be favorable; design engineers should consult with facility contamination control specialists before spec- ifying variable-volume systems for cleanrooms. Air locks typically are used between uncontrolled personnel cor- ridors, entrance foyers, and the protective-clothing gowning area. Air locks may also be used between the gowning room and the main cleanroom, and for process equipment staging areas before entering the cleanroom. Install air locks only when they are really necessary, because their use along traffic paths could restrict personnel access and increase evacuation time during emergencies. Commercial pressure differential sensors can reach accuracy at 0.25 Pa or better, and significant progress has been made on preci- sion room pressure control. Many processes affected by cleanroom pressure (e.g., glass deposition with saline gas) require process cham- ber pressure precision of 60 mPa. Pressurization calculations can be performed by using the proce- dures detailed in either Pedersen et al. (1998) or Spitler (2009) in the chapters on infiltration: · Using the provided charts, calculate the building exfiltration at designated room pressurization level. · In accordance with ASHRAE Standard 62.1, with the actual num- ber of occupancy, determine the required outdoor airflow rate. · Determine the total airflow rate of exhaust from the building. The sum of exfiltration airflow rate plus exhaust airflow rate, or plus the required outdoor airflow supply rate, whichever is greater, is the total ventilation rate under the designated building pressuriza- tion. To ensure the designated pressurization level, a leak test must be performed for exterior walls, interior walls, partitions, doors and windows between two adjacent rooms with different pressurization levels, and for roof, exterior doors and windows, connections between wall and roof, and any building elements between two rooms with different pressurization levels. All major leaks must be eliminated before start-up of HVAC systems. Sizing and Redundancy Environmental HV AC design must consider future requirements of the factory. Products can become obsolete in as little as two years, and process equipment may be replaced as new product designs dic- tate. As new processes are added or old ones removed (e.g., wet etch versus dry etch), the function of one cleanroom may change from high-humidity requirements to low, or the heat load many increase or decrease substantially. Thus, the cleanroom designer must design for flexibility and growth. Unless specific process equipment lay- outs are available, maximum cooling capability should be provided in all process areas at the time of installation, along with provisions for future expansions. Because cleanroom space relative humidity must be held to close tolerances and humidity excursions cannot be tolerated, the latent load removal capacity of the selected equipment should be based on high ambient dew points and not on the high mean coincident dry- bulb/wet-bulb data. In addition to proper equipment sizing, redundancy is also desir- able when economics dictate it. Many cleanroom facilities operate 24 h per day, seven days per week, and shut down only during holi- days and scheduled nonworking times. Mechanical and electrical redundancy is required ifloss of equipment would shut down critical Inc. ASHRAE, 2019 user. single for Licensed | {}
0886602d-b7a4-4957-af5c-85a74e2bd248 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Clean Spaces 19.25 and expensive manufacturing processes. For example, process exhaust fans must operate continuously for safety reasons, and par- ticularly hazardous exhaust should have two fans, both running. Most process equipment is computer-controlled with interlocks to provide safety for personnel and products. Electrical redundancy or uninterruptible power supplies may be necessary to prevent costly downtime during power outages. Redundancy should be based on life-cycle economics and careful review of all foreseeable system failure and recovery scenarios. With the proper design focus, redun- dancy improvements can provide additional benefits; for example, operating redundant fans in parallel can reduce overall power con- sumption while improving system stability during failure recoveries. Minienvironments A minienvironment is a type of separate device mainly used in microelectronics industry to maintain a level of stringent cleanliness in a tightened volume of clean spaces (IEST RP CC028.1; ISO Stan- dard 14644-7). It is a localized environment created by an enclosure to isolate or separate a product or process from the surrounding envi- ronment. A minienvironment is normally used to maintain a level of stringent, higher level of cleanliness by controlling particle concen- trations within a tightened volume of clean spaces, often by main- taining desired pressure differential or supplying unidirectional airflows. It is important to understand the characteristics of minien- vironments , design, operation, and effectiveness in environmental control, and the impacts of integration with the cleanroom that houses the minienvironment or a group of minienvironments. Xu (2007a, 2008) found that pressure differentials under 0.2 Pa can be sufficient for achieving a high level of air cleanliness to meet envi- ronmental control expectation and requirements, suggesting that existing recommended practices or guidelines (e.g., IEST RP CC028.1) may be higher than necessary, at least in some minienvi- ronment applications. Advantages of using minienvironments include upgrading clean- liness classes, process integration, and maintaining better contami- nation control. Xu (2008) also suggested that, when appropriately integrated with a cleanroom, minienvironments may improve overall cleanroom energy efficiency and offer significant cost savings and reliability. The field investigations characterized energy perfor- mance of five different minienvironments (designated as ISO Clean- liness Class 3) operating and housed in a traditional, larger ISO Cleanliness Class 4 microelectronics cleanroom. The measured energy performance and associated metrics were compared to those of cleanrooms of various cleanliness classes, and indicated that potential energy savings up to 60 to 86% were achievable by inte- grating minienvironments in traditional cleanrooms, without losing effective contamination control. Other ways to increase energy sav- ings in minienvironments include optimal design and operation, improving fan-filter unit operating efficiency, and space manage- ment in clean spaces. Fan-Filter Units A fan-filter unit (FFU) is a self-contained unit normally inserted and gasketed into cleanroom T-bar ceilings and is used to supply and clean airflows, which are fed to and then recirculated through the cleanroom space. An FFU usually consists of a small fan, a control- ler, and a HEPA or ULPA filter enclosed in a box, which fits into common cleanroom ceiling grids. Fan-filter units in air recirculating systems have become increasingly popular worldwide because of their specific contamination control, ease of installation, and adapt- ability in cleanroom construction, qualification, and operation. Common ceiling grids typically carry FFUs with unit sizes rang- ing from 1220 by 1220 mm to 1220 by 610 mm or smaller. The small internal fans force air through the HEPA or ULPA filters. Cov- erage of a cleanroom ceiling normally ranges from 25 to 100% of the total ceiling area, and thus can require many FFUs. As a result, the large number of FFU fans constitutes considerable electric pow- er demand and energy use (and noise generation) in providing air re- circulation and cleaning (Xu et al. 2007). Appropriate applications of FFUs can generate unidirectional airflows desired for certain cleanroom activities or processes. New technologies able to control the airflow rate and uniformity through a networked feedback con- trol system can improve the controllability and reliability ofindivid- ual FFUs (Chen et al. 2007). Electrically commutated (EC) motors have replaced many of the older split capacitor motors, resulting in significantly improved motor efficiency. Note that different FFUs' energy and aerodynamic performance can vary, even with similar components (Chen et al. 2007; Xu et al. 2007), and their performance may largely influence both energy efficiency and contamination control effectiveness in cleanroom design, qualifications, and operation. The energy efficiency level of the same unit may vary considerably, depending on actual operating conditions such as airflow speeds and pressure rise across the units; for instance, Xu et al. (2007) found that, when operating with the fan-wheel speed control dials at maximum, larger units tended to be more energy efficient than their smaller counterparts. To achieve sustainable development in cleanroom facilities, it is useful for designers and owners to have comparable information on FFU energy performance. This makes it feasible to select efficient units and to improve energy efficiency while maintaining or improving effectiveness in contamination control. Unfortunately, typical man- ufacturers' data sheets usually contain numbers that look similar but are not readily comparable because their approaches to reporting performance data are different from each other, and this can lead to confusion. In recent years, the interest in understanding and improving fan- filter performance has increased among users, manufacturers, energy companies, professional organizations, and research insti- tutes. Increasing energy costs in operating existing and future clean- rooms and mission-critical controlled environments have prompted end users to seek and select higher-efficiency FFUs in their clean- room applications, and motivated suppliers to develop more energy- efficient FFUs for future cleanrooms. For example, manufacturers are increasingly interested in quantification of the energy perfor- mance of their fan-filter units, and in developing a method for sys- tematically characterizing fan-filter performance as it is affected by fan-wheel design, air-path and size, unit size, motor type, availabil- ity of airflow control, and control schemes. Lawrence Berkeley National Laboratory has developed and published a standard test method to fully characterize energy and aerodynamic performance of individual FFUs in laboratory setting (Xu 2007b, 2007c). 12. SUSTAINABILITY AND ENERGY CONSERVATION Cleanroom air systems may account for a significant portion of the HVAC energy use in cleanrooms. In cleanrooms, high electric power density for fans to deliver airflows, defined as the fan , s electric power demand divided by the cleanroom floor area, would normally be expected because of large volume of airflows supplied, recircu- lated, and exhausted within a given time. Therefore, the design of cleanroom airflow systems may have a long-term impact on energy usage in that the amount of designed airflows significantly affects the operation costs associated with energy, initial equipment costs, and installation costs (Xu 2008). The major operating costs associated with a cleanroom contam- ination control systems include conditioning the air, fan energy for air movement in the cleanroom, and process exhaust. The combi- nation of environmental conditioning and control, contamination control, and process equipment electrical loads can be as much as 3 kW/m2. Besides process equipment electrical loads, most energy is Inc. ASHRAE, 2019 user. single for Licensed | {}
acebf0ec-7a45-4703-b057-4681c2d56349 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 19.26 2019 ASHRAE Handbook-HVAC Applications (SI) used for cooling, air movement, and process liquid transport (i.e., deionized water and process cooling water pumping), compressed air, vacuum systems, etc. A life-cycle cost analysis is useful to de- termine design choices and their total cost of ownership over time, as well as greenhouse gas contribution related to cleanroom design and operation. Energy Metrics. The energy use required for operating wafer fabrication plants (fabs) is intensive and is one of the major con- cerns to production power reliability. Energy performance metrics to characterize the electric energy consumption and wafer produc- tion include production efficiency index (PEI), electrical utilization index (EUI), specific energy consumption such as annual electric power consumption normalized by annual produced wafer area, and annual electric power consumption normalized by units of pro- duction (UOP), which is defined as the product of annual produced wafer area and the average number of mask layers of a wafer (Chang et al. 2009; Hu et al. 2010, 2013). To evaluate design options for HVAC systems in cleanrooms, it is convenient to compare overall efficiency using standard metrics. By using a metric such as airflow rate per kilowatt input, system efficiency for different schemes can be compared. The metric allows comparison of the amount of energy required to move a given quantity of air, and combines equipment efficiency as well as system effects. The owner can include this metric as a design cri- terion. Similarly, metrics for chilled-water system performance in terms of kilowatts per kilowatt of cooling can be established. Chiller performance and overall chilled-water system performance issues are well documented and should be consulted to set appro- priate targets. Fan Energy. Because supply airflow rates in cleanrooms can be very high, fan systems should be closely examined for right sizing and conservation of fan energy. Static air pressures and total airflow rate requirements should be designed to reduce fan power and its operating costs. Fan energy required to move recirculation air may be decreased by reducing airflow rates and/or static air pressures. Energy conservation operating modes should be verified during sys- tem qualification. If these modes are not part of the original design, the control procedure must be changed and the operational change validated. Airflow rates may be lowered by decreasing recirculation air- flow rate and minimizing cleanroom volumes in high-air-change- rate suites. A lower airflow rate could allow decreasing HEPA or ULPA filter coverage or reducing average air velocity. Reducing airflow rate can yield significant energy savings while enhancing space cleanliness through reduced turbulence. Based on a 0.45 m/ s face velocity, each square metre reduction in filter coverage area in a room can save 250 to 500 W/m2 in fan energy and cooling load. Reducing space average velocity from 0.45 to 0.40 m/s saves 50 W/ m2 in fan and cooling energy. Ifthe amount of airflow rate supplied to the cleanroom cannot be lowered, reducing static pressure can also produce energy savings. With good fan selection and transport design, up to 150 W/m2 can be saved per 250 Pa reduction in static pressure. Installing low-pressure-drop HEPA filters, pressurized plenums in lieu of ducted filters, and proper fan inlets and outlets may reduce static pressure. Many cleanrooms operate for only one shift. Airflow rate may be reduced during nonworking hours by using two-speed motors, variable-frequency drives, inverters, inlet vanes, and variable-pitch fans, or, in multifan systems, by using only some of the fans. Additional fan energy may be saved by installing more efficient motors and electrical equipment, including transformers, UPS, and motor drives. Fan selection and inlet/discharge configuration also affects energy efficiency. The choice of forward-curved centrifugal fans versus backward-inclined, airfoil, or vaneaxial fans affects effi- ciency. The number of fans used in a pressurized plenum design influences redundancy as well as total energy use. Fan size changes affect power requirements as well. Sometimes lowering airflow velocities by operating more fans can improve a system 's energy efficiency and reliability; investigate different options to ensure optimal designs and operation. Makeup Air (MUA) and Exhaust Energy. Makeup air is re- quired to replenish the lost air and to meet pressurization needs. The requirements for makeup airflow rates vary accordingly with an added amount for leakage and pressurization. The energy required to supply the conditioned makeup air can be significant. Optimizing MUA design by reducing or displacing mechanical cooling or elec- trical heating processes can improve energy efficiency, because cleanroom air-conditioning systems typically account for 30 to 65% of the total energy consumption in a high-tech facility. Different precooling and reheating/humidification schemes may result in dif- ference in energy efficiency performance of MUA systems (Tsao et al. 2010). Careful attention to the layout and design of the makeup air system, especially minimizing system pressure drop and speci- fying efficient fans and motors, is important. The type of equipment installed normally determines the quantity of exhaust airflow rates in a given facility. Heat recovery has been used effectively in pro- cess exhaust; when heat recovery is used, the heat exchanger mate- rial must be selected carefully because of the potentially corrosive atmosphere; requirements for nonhazardous cleanrooms are not as significant. Also, heat recovery equipment has the potential to cross-contaminate products in pharmaceutical facilities. Pretreating makeup air using return water (either from process or building systems) is another way to reduce energy demands on primary sys- tems serving a clean facility. Makeup air cannot normally be reduced without decreasing pro- cess exhaust, which may be difficult to do because of safety and con- tamination control requirements. Therefore, design optimization of conditioning and delivering the makeup air should be explored and costs should be investigated. Conventional HVAC methods such as using high-efficiency chillers, good equipment selection, and precise control design can also save energy. One energy-saving method for large facilities uses multiple-temperature chillers to bring outdoor air temperature to a desired dew point in steps. Cleanrooms and Resource Use: Opportunities to Improve Sustainability Because of their highly specific and complex requirements, cleanrooms generally have high demands for energy and resources (Hu et al. 2013; Xu 2003). When possible, owners, designers, and operators should look for opportunities to reduce these demands, not only for reasons of environmental stewardship, but also for cost savings and avoidance of problems and complexity associated with larger power requirements and systems. When developing a cleanroom-driven project, using integrated design and construction, under either the structured approach of integrated project delivery (IPD) or less formalized types of collab- oration or partnering, can result in major rewards in cost, schedule, and operational efficiencies. Some of the most promising areas for energy and resource use reductions include the following: · Optimizing air distribution and air change rates in clean areas. Reducing space volumes and air change rates saves energy for environmental conditioning units and fans; and may reduce equipment and system sizing, filtration pressure drops, and equipment space requirements. Proper fan selection and duct layouts can eliminate the need for sound attenuators, thus saving space and energy. For spaces having the highest air change rate or airflow rate, enlarging duct sizing, increasing fil- ter and coil area, careful fan inlet and discharge layouts, incor- porating pressurized plenums, reducing overall duct path length, using transfer fans, and grouping spaces appropriately Inc. ASHRAE, 2019 user. single for Licensed | {}
2849a668-bb76-4757-919a-29f9a6ebd57f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Clean Spaces 19.27 Chart Type: bar FAN-FILTER UNIT PRESSURIZED PLENUM DISTRIBUTED DUCTED RECIRCULATION item_01 0.5l/(s-W) 5l/(s-W) 1l/(s-W) Fig. 18 Energy Efficiency of Air Recirculation Systems (Source: Xu 2003. Figure reprinted from the Journal ofthe IEST, "Performance Evaluation of Cleanroom Environmental Systems, with permission from the Institute of Environmental Sciencesand Technology. Copyright 2003 by IEST, www.iest.org, [847] 981-0100) can reduce energy requirements and avoid extreme space differ- ential pressure challenges. In addition, spot exhaust, cooling, or heating can improve overall system efficiencies. Implementing on-demand utility distribution, such as pressure and tempera- ture reset control strategies, may provide further operational energy savings. Different system selections such as ducted dis- tribution, fan-filter units, and pressurized plenum typically induce different levels of air delivery efficiency, as shown in Figure 18 (Tschudi et al. 2005; Xu 2003). Users of fan-filter units should have the FFU performance tested using a standard method, such as that developed by Xu (2007b, 2007c), so that optimal efficiency can be achieved within common ranges of operating airflow rates. · Advanced control strategies including on-demand dynamic air flow control in response to real-time particle counts. This reduces power demand during occupied and unoccupied time, and requires testing at different operational levels to ensure consistent and reli- able process performance (see the section on Air Pattern Control for details). · Some high-performance applications use electrically enhanced filtration (EEF), which uses high frequencies or other electrical methods of charging airborne particles for significant air filtra- tion efficiency improvements, providing the required filtration effectiveness with lower resistance and less pressure drop, which reduces overall system fan power consumption (Jaisinghani et al. 2000). Typically, EEF reduces air filter penetration by at least one order of magnitude. Some EEFs use two separate fields; the field across the filter is electrostatic. Others apply one voltage to three or four electrodes to create an ionizing field to charge incoming particles, and another ionizing (not electrostatic) field to charge the filter media. This second kind also inhibits bacterial growth on the filter media and results in lower bioburden clean- rooms: in most cases, ISO Class 6 cleanrooms achieve the air- borne bioburden requirements of an ISO 5 environment. This represents a significant savings in initial and operating costs for cleanroom applications that are primarily concerned with bio- burden and have looser requirements for general particulate con- tamination. · Analyze and evaluate process chemistry, including cleaning mate- rials and methods. Reducing or eliminating VOC-based solvents, heavy metals, acids, etc., in processing reduces the need for dilu- tion air, scrubbing, treatment of effluent, and other environmental and life safety issues. This step must be integrated with process developers, operators, and regulatory compliance personnel to ensure that changes do not compromise final product quality and acceptance. · Process equipment specifications should include performance cri- teria for support utilities such as process water, compressed air, exhaust air, and electrical power. More efficient equipment saves operational and capital costs. This approach may also prove attrac- tive where process equipment is leased and will be returned to the equipment vendor, as is common in microelectronics because of the processing technologies' rapid obsolescence. For equipment or tool manufacturers, higher efficiency may enhance the toolset's resale value. The effects of these broad areas of resource use reduction and en- ergy savings on building systems should be obvious; however, there are other tangible benefits that should be considered. Reducing the resource use or environmental footprint of the cleanroom extends the site infrastructure's carrying capacity. On developed sites in de- veloped areas, this can save significant capital and operational costs by reducing the need to increase the site 's capacity or infrastructure to handle an additional building or operation. Reducing use of hazardous, toxic, or noxious materials can reduce the owner' s expo- sure to environmental health and safety risks and the need to treat discharge air and water streams. Improving HVAC energy effi- ciency can reduce equipment and penthouse space requirements, capital costs, and system-generated noise and vibrations. 13. NOISE AND VIBRA TION CONTROL Noise is difficult to control. Noise generated by contamination control equipment requires particular attention, although produc- tion equipment noise may be more significant than HV AC noise. Before beginning design, criteria for noise and vibration should be established. Chapter 49 provides more complete information on sound control. In normal applications of microelectronics contamination con- trol, equipment vibration displacement levels need not be dampened below 0.5 �m in the 1 to 50 Hz range. However, electron micro- scopes and other ultrasensitive microelectronics cleanroom instru- ments may require smaller deflections in different frequency ranges. Photolithographic areas may prohibit floor deflections greater than 0.075 �m. As a general rule, displacement should not exceed one- tenth the line width. For highly critical areas, consider using vaneaxial fans. These fans generate less noise in lower frequencies, and can be dynami- cally balanced to displacements of less than 4 um, which decreases the likelihood of transmitting vibration to sensitive areas in elec- tronics cleanrooms. Energy-efficient features of cleanroom HVAC systems, such as straight, smooth duct layouts and elimination of sound attenuators, can exacerbate noise control issues. Instead of resorting to adding sound traps, acoustic problems can be mitigated through proper, energy-efficient duct layouts and efficient fan selections that avoid sound generation from excessive fan-blade tip speeds. 14. SPACE CONSTRUCTION AND OPERA TION Control of particulate contamination from sources other than the supply air depends on the classification of the space, the type of sys- tem, and the operation involved. Important documents published by IEST and ISO are available to guide the practices (e.g., IEST RPs CC003.2, CC004.2, CC005, CC018, CC026.1, and CC027.1; ISO Standards 14644-2, 14644-3, 14644-4, and 14644-5). The follow- ing illustrate some typical details that may vary with the room class. Construction Finishes · General. Smooth, monolithic, cleanable, and chip-resistant, with minimum seams, joints, and no crevices or moldings. · Floors. Sheet vinyl, epoxy, or polyester coating with wall base carried up, or raised floor (where approved) with and without per- forations using the previously mentioned materials. · Walls. Plastic, epoxy-coated drywall, baked enamel, polyester, or porcelain with minimum projections. Inc. ASHRAE, 2019 user. single for Licensed | {}
0ff3dc74-d4cd-49c6-b7b1-d56c12e74be8 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 19.28 2019 ASHRAE Handbook- -HVAC Applications (SI) · Ceilings. Gypsum wallboard or plaster, covered with plastic, epoxy, or polyester coating or with plastic-finished, clipped acoustical tiles (ceiling tiles are not common in ISO Class 5 or cleaner pharmaceutical processing cleanrooms, and tile edges should be sealed if used for less clean areas) when entire ceiling is not fully HEPA or ULPA filtered. · Lights. Teardrop-shaped single lamp fixtures mounted between filters, sealed and installed in T-grid ceiling (gasket or gel seal) or flush-mounted and sealed. · Service penetrations. All penetrations for pipes, ducts, conduit runs, etc., fully sealed or gasketed, then caulked in place. All con- duits must have internal seals or pour stops to reduce infiltration/ exfiltration through conduit. · Appurtenances. All doors, vision panels, switches, clocks, etc., either flush-mounted or with sloped tops. · Windows. All windows flush with wall; no ledges on cleanest side. Window gaskets must be closed cell and windows caulked. · Doors. Sliding doors perform better than swinging doors in crit- ical cleanrooms. All door movements must be controlled for grad- ual, smooth motion. Personnel and Garments · Hands and face cleaned before entering area · Lotions and soap contain lanolin to lessen shedding of skin parti- cles · No cosmetics and skin medications · No smoking or eating · Lint-free smocks, coveralls, gloves, head covers, and shoe covers Materials and Equipment · Clean equipment and materials before entry, including the under- side of rolling equipment and work surfaces, and wheels. · Use nonshedding paper and ballpoint pens. Pencils and erasers are not allowed. · Handle processing equipment and hardware with gloved hands, finger cots, tweezers, and other methods to avoid transfer of skin oils and particles. · Sterile pharmaceutical product containers must be handled with sterilized tools only. Particulate Producing Operations · Electronics grinding, welding, cutting, sanding and soldering operations are shielded and exhausted. · Use nonshedding containers and pallets for transfer and storage of materials. Entries · Air locks and pass-throughs maintain pressure differentials and reduce contamination. 15. CLEANROOM INSTALLATION AND TEST PROCEDURES ISO, IEST, and the National Environmental Balancing Bureau (NEBB) have developed a set of standards for cleanroom instal- lation and test procedures (IEST RP CC006.2; ISO Standards 14644-2, 14644-3, 14644-4, and 14644-5; NEBB 2009). This sec- tion provides some descriptions of the procedures based on field experience. Installation Space Preparation. Building envelope construction should be completed, its insulation thoroughly installed. Insulation materials should meet cleanroom requirements. All leaks must have been elim- inated, construction debris removed, and floors cleaned, washed, and blow-dried. Cleanroom Installation. After space preparation is completed, the HV AC, plumbing, process piping, and cleanroom elements are then ready to start installation in the following sequence: 1. Install cleanroom HVAC piping, ductwork, plumbing, and pro- cess piping (prior to hookup with process equipment). All open ends of duct and piping must be temporarily sealed at end of each workday. 2. Install cleanroom ceiling, floor, and wall systems. 3. Any process equipment package that is larger than the access doors must be moved into the cleanroom area before installing cleanroom wall access panels. All process equipment should be protected from construction damage and remain in shipping packaging, unopened. 4. Install cleanroom access doors, pass windows, wall access pan- els, floor and ceiling access panels. Ifhard ceiling is used, do not close ceiling access before test, balance, and acceptance by the responsible HV AC engineer. 5. After completing steps 1 to 4, check the tightness of all access doors, pass windows, and other cleanroom openings, as well as edges between (a) ceiling and walls and (b) walls and floors. Leaks must be completely eliminated. Cleanroom Duct and HEPA Filters. 1. Thoroughly wash and clean air-handling unit (AHU) internals, including internals of AHU fans. 2. Use compressed air to blow dry (pressure high enough to dry, but not to damage internals of the AHU). Run the AHU at low speeds with no HEPA filters installed to blow out any loose dirt or debris before clean operation. 3. Shut down and inspect the AHU internals. If some dirt remains (especially on filter and edge areas), repeat steps 1 and 2. 4. Temporarily seal all openings on cleaned AHUs, including out- door air (OA) intakes, return and supply openings, water, steam connections, humidifier control box tubes, drain openings, and doors. 5. Wash clean and blow dry all internal surfaces of duct sections and immediately seal. This will prepare the installation of duct system and HEPA filters. 6. Temporarily seal all open ends in the duct system at end of each workday during installation. 7. Temporarily seal the installed duct systems to wait for the fin- ish of architectural internal work. Leave ceiling accesses open for ceiling HEPA filter installation and HV AC system test and balance. 8. Remove all construction debris from cleanroom. Wash and dry AHU external surfaces. 9. Wash and dry the cleanroom floor, walls, ceiling, and all mate- rials and equipment thoroughly. After this step is completed, in- stallation personnel should wear cleanroom shoe covers when entering the cleaned area to continue installation work. 10. Place the originally sealed HEPA filter packets at their instal- lation locations (avoid any cardboard or particulate shedding packaging in cleanroom; remove such packaging materials out- side of clean areas). 11. Unpack HEPA filters and install immediately. Do not open HEPA filter packets if not to be installed the same day. 12. Check HVAC control system installation and pretest to ensure the control system is functioning before HEPA filter installa- tion. 13. Check installation of fire protection, life safety, and other HVAC-related systems to ensure the systems are properly func- tioning. System Start- Up, Test, and Balance. 1. Read the major equipment and controls' installation, operation, and maintenance (IOM) manual thoroughly. Inc. ASHRAE, 2019 user. single for Licensed | {}
28234e29-745e-4068-87b3-f1d710485106 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Clean Spaces 19.29 2. Walk through entire system to be started up. 3. Check that all mechanical systems have been installed. Re- place covers, belts, gaskets, bolts, and screws if missing or damaged. 4. Check unit base concrete slabs, roof curbs, and structural sup- ports. All units should be firmly installed on level plane. 5. Check that all equipment, devices, and fittings are installed correctly and in operating condition, including room pressur- ization monitoring systems. 6. Check that all dampers, louvers, and valves are set at the cor- rect positions as shown on drawings and under the direction of test-and-balance engineer. 7. Remove all bolts and plates used for temporarily compressing internal spring isolators under AHU base during shipment. 8. Check chiller system. Ensure that the chilled-water supply and return are under operational condition. 9. If hot water is used, check the hot-water system. Check that hot-water supply and return temperature and pressure all meet HVAC system requirements. 10. If steam is used, check steam valve station. Check that the reg- ulated steam pressure meets HVAC system required range. 11. If pneumatic control is used, check compressed air system, en- suring that the supply pressure meets control system require- ment. 12. Electrical engineer should check the electric wiring and con- firm that power source voltages conform to all equipment requirements. 13. Check and correct all motors' rotation. 14. Check that the controls system has been installed, energized, and pretested by the controls contractor. 15. Check that the fire-protection system is in place, with correct links verified by the fire protection contractor and electrical engineer. 16. General mechanical/HVAC contractor should coordinate with all disciplines for overall status of preparation for cleanroom HVAC, control, and fire-protection systems start-up. A written report stating the completion of all of the preceding listed items should be submitted to the responsible HVAC engineer at min- imum two workdays before the scheduled system start-up date. The responsible HVAC engineer should determine a proper day to inform the on-site commissioning authority (CA) before start-up if commissioning is required by project scope. 17. Correct all problems that may have occurred during start-up; adjust systems to meet design conditions. Also, all system spe- cific commissioning and qualification procedures must be final- ized and accepted before placing new systems into operation. 18. Once HVAC system is running with all final filters, including HEPAs, all personnel entering clean spaces should be fully gowned to maintain the proper and clean operating state, and to ensure gowning procedures and personnel training are appro- priate. 19. Initial test, balance, and adjustment work should be performed by a licensed test-and-balance contractor during system start- up. The engineering approval for the final configuration of mechanical systems must include a verification that all systems are appropriately configured to maintain correct and consistent operation throughout the life of the system, including correct and appropriate equipment, installations, system adjustments, controls, operation and maintenance procedures and training, AHU operating point on the fan curve, proper spare capacity for filter loading, system wear and tear, seasonal and ambient envi- ronmental impacts (wind, weather extremes), and all other fore- seeable factors that may impact operations. 20. Check prefilters and final filters for cleanliness. Replace tempo- rary construction filters with filters specified by design engineer. If the design filters have reached their pressure drop limit, change them. 21. Adjust supply, return, and exhaust fan airflows and room pres- surizations to meet design rates. 22. Verify that operational testing of all system safeties (fire alarm, high-pressure limits, etc.) is completed before releasing system for automatic operational control. 23. Keep air system operating. Set room thermostat low enough to start cooling. Check chilled-water supply and return temper- atures, control valves, and condensate drain. Check room tem- perature. Note that the cooling performance test is under the condition without process heat. The responsible HVAC engi- neer should determine if the HVAC and chiller systems are capable of satisfying the additional load with process running. 24. Keep air system operating. Set room thermostat at temperature high enough to start heating system. Check steam pressure and/ or heating hot water system temperature, monitor served room temperature, and check control valves and condensate return and drain lines. 25. Keep supply air and heating system running. Set room humid- istat at level high enough temporarily start humidifier. If steam humidifier is used, check steam pressure and all connections. Monitor relative humidity of served room and check control valves. 26. Clean the space for the last time using the operationally approved pharmaceutical cleaning procedures to prepare for final test. Cleanroom dress code enforcement begins before final test. 27. Perform final test. Attendees should include all contractors, subcontractors, the responsible HVAC engineer, the cleanroom facilities engineer, the future system lead operators, lead main- tenance staff, and commissioning and quality personnel, if appropriate. 28. All problems should be solved before the project completion, including the achievement of acceptable cleanroom pressuriza- tion, particulate and bioburden levels. Keep complete records of all problems and solutions during start-up, testing, adjusting, and balancing. Pressurization Test and Map Cleanroom pressurization must be verified before commission- ing and engineering acceptance. An as-built space-to-space pressur- ization map should be submitted by the test-and-balance contractor to the responsible HVAC engineer for review and approval. The sys- tem must support acceptable room pressurizations within a narrow enough range to accommodate expected future system operational fluctuations; a retest may be performed ifthe HVAC engineer deems it necessary. Perform and document airflow pattern testing for final quality control verifications to demonstrate that particulates are being driven from the cleanest, most critical areas to less critical regions within and between rooms. Even when a room differential pressure is being maintained, it is important to find and correct counterintuitive airflow reversals through airflow pattern testing. Operation Personnel Training Program It is important that the operating and maintenance personnel responsible for systems on a particular project receive proper train- ing. Usually, training is offered by the control contractor under the supervision of the responsible HVAC engineer, and should start during functional performance testing. It is important that the oper- ating and maintenance personnel see the systems being set up, the issues encountered, and their resolution. Cleanliness Verification Test Empty (as-built) cleanroom cleanliness may be verified and determined by initial testing before process equipment installation Inc. ASHRAE, 2019 user. single for Licensed | {}
649d5a04-cd31-4c23-b990-188db372c1d7 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 19.30 2019 ASHRAE Handbook-HVAC Applications (SI) and operation. Operational cleanroom cleanliness should be tested during formal process operation to gage the influence of emissions from process materials and products, as well as the performance of process exhaust systems together with cleanroom operation rules and operating personnel activities. At-rest cleanroom status occurs after preparing the area for phar- maceutical manufacturing by installing process equipment and instrumentation, and the additional of properly gowned personnel creates operational cleanroom conditions. Space particulate levels measured at these different cleanroom operating states are import- ant to meet processing space environmental requirements. For ISO Class 3 and 4 cleanrooms, the owners will most likely prefer not to have commissioning personnel walking around the cleanroom facility during process in operation. They typically use their own professional staff to test and maintain the space cleanliness level. Therefore, as-built cleanroom cleanliness commissioning is the final step in most projects. Several publications by IEST and ISO address cleanroom testing and operation issues (IEST RP CC006.2; ISO Standards 14644-2, 14644-3, 14644-4, and 14644-5). Commissioning Participants in the commissioning process include personnel involved in the URS generation, design, start-up, test, and balance, in addition to process operators, the owner's project authorities, and commissioning personnel. Commissioning documents should include the following: · Certificates and warranties of system completion with complete set of as-built drawings submitted from mechanical, electrical, plumbing, controls, and fire-protection contractors · If available, all major equipment installation, operation, and maintenance (IOM) manuals, from the equipment manufacturers · Complete records of all problems and solutions that occurred during start-up, and tests and adjustments submitted by every individual contractor · A certified system test and balance report with verified major equipment models and capacities, and all tested performance numbers conforming to the system criteria from the licensed test- and-balance contractor. A complete space-to-space pressuriza- tion map submitted by the test-and-balance contractor · A control system installation, operation, and maintenance (IOM) manual submitted from the control contractor · A certificate of test for as-built cleanroom cleanliness (tested when cleanroom facility is complete, all services are connected and functional, but without equipment and operating personnel in the cleanroom) · If the contract scope requires, a certificate of cleanroom cleanli- ness at the condition of process running with operating personnel in the facility · Updated operating procedures, system drawings, facility flow diagrams, air handler service area diagrams, space classification, and pressurization drawings, as applicable. · Commissioning protocol forms, signed and witnessed by all attendees Process Equipment Installation (Tool Hook-up) The process equipment installation (tool hook-up) work is covered by a separate, independent contract. It starts when the as-built clean- room has been certified and accepted by the owner. The plant facility engineer is responsible for process equipment installation, and the project HVAC engineer monitors the cleanroom cleanliness while hook-up is in progress, offering consultation as needed. The follow- ing points apply to the cleanroom tool hook-up procedure: · All cleanroom equipment installation personnel should attend a cleanroom orientation class before beginning work. · All installation personnel must follow the dress code entering and working in the cleanroom area for process equipment installation, testing, adjusting, and operation. · Do not unpack process equipment before the cleanroom has been cleaned, tested, certified, and is ready for installation ofthe equip- ment. Avoid unpacking equipment in clean areas; this should be done in a material airlock following proper procedures to mini- mize particulate introduction to the cleanroom. · Do not unpack process equipment or open temporarily sealed pipe ends if not immediately installing or connecting to the equipment or pipe ends. Temporarily seal unfinished connection openings if not being connected immediately. · Do not leave cleanroom doors or pass windows open anytime during installation or test operation. · Establish a bimonthly cleanroom cleanliness retest timetable for monitoring and maintaining the cleanroom cleanliness level for the first six months. The frequency of retest can be modified according to the actual operating experience in future years. 16. INTEGRA TION OF CLEANROOM DESIGN AND CONSTRUCTION Integrated design and construction addresses all stages and aspects of cleanroom construction, to achieve better-quality, faster delivery; lower-cost, more optimized operation and maintenance; lower energy consumption; a cleaner environment; safer, more reli- able, and more productive conditions; and longer service life. Inte- grated building design (IBD) is discussed in detail in Chapter 60. A complete cleanroom project usually includes the following stages (see Figure 19): development of scope, budget, and overall project execution plan; predesign, conceptual, and schematic design; preliminary, final design, and construction documentation; and con- struction service. ![image](/image/placeholder) PROJECT CONCEPTUAL SCHEMATIC PRELIMINARY CONSTRUCTION PREDESIGN SCOPE DESIGN DESIGN DESIGN SERVICE SELECT FINAL BUDGET DESIGN DESIGN TEAM OVERALL CONSTRUCTION EXECUTION DOCUMENTATION PLAN Fig. 19 General Design and Construction Procedure Inc. ASHRAE, 2019 user. single for Licensed | {}
fc9b8e94-54e6-4002-b155-47880d827f42 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Clean Spaces 19.31 One of the most important initial steps is to have a effective pro- gramming plan that involves all stakeholders: management, owners, users; designers (architects and engineers), process engineers, builders, and utility, maintenance and operation personnel. Although the entire cleanroom building project is a large and complex operation, it may be simplified ifit is considered as an inte- grated system with a unified overall scope of work and timeline to be achieved by an integrated design and construction team (Shieh 1990, 2005). In an integrated approach, all individual systems and their components are considered as subsystems of the overall inte- grated cleanroom building project, and optimizations are imple- mented at the component, system, and facility levels, including the following: · Site/utilities. Overall site plan, entrances and gates, roads and transportation, landscape, electrical substations or electrical main connection, gas or other fuel main intake pressure regulation sta- tion, water, sewer, sanitary and storm drain piping and main con- nections, telephone, network, security and fire protection system main connections, outdoor lighting, etc. · Building. Foundations, structure system, walls, roofs, ceilings, floors, elevators, electrical, gas, fuel, water, sewer, plumbing, san- itary, mechanical, HVAC, chiller, boiler, noise control, lighting, process systems, energy and process material recovery systems, exhaust air and wastewater treatment systems, hazard control sys- tems, explosion- and corrosion-proofing, instrumentation and control systems, fire protection systems, etc. · Cleanroom. Walls; roofs; ceilings; HEPA or ULPA filters; floors; mini-clean environment; clean tunnels; clean booths; recirculat- ing air, makeup air, and exhaust air systems; lighting, process mechanical, chemical, electrical, and control systems; production lines; process conveyers; special gas supply systems; acoustics; operating personnel, material, and products access doors, win- dows, or openings; air showers; room temperature, humidity, static electricity, CO2, pressurization, and cleanliness monitoring and control systems; fire protection and after-fire recovery sys- tems; seismic design, emergency response facilities, etc. · Implementation. Design documents, submittal approvals, receiv- ing inspections, clean construction and installation work, field inspections, system start-up, test and adjustment, balancing, com- missioning, and turnover. · Building management. System operation and maintenance. 17. LIFE AND PROPERTY SAFETY Human life and property safety must be thoroughly addressed in all types of new construction or renovation projects during clean- room design, construction, installation, start-up, test, balance, oper- ation, and maintenance. The American Conference of Governmental Industrial Hygienists (ACGIH) and National Fire Protection Associ- ation (NFPA) provide detailed regulations. The following are some of the essential categories to be carefully addressed during the entire cleanroom project design, construction, commissioning, operation, and maintenance process. Hazards Generated on Cleanroom Property When hazards are present on the project property, all safety issues must be carefully addressed; otherwise, the consequences could affect not only the occupancy personnel and the property, but also the surrounding communities. One of the duties for the design and commissioning authorities is to understand and successfully address the hazards generated in the property. Different cleanrooms may be composed of many different oper- ating systems, each with distinct equipment or operating processes that present unique hazards (e.g., fuel handling, chemical transport and emissions, airborne contaminants, heated lubrication and seal oil, oil-filled transformers, cable vaults, coal handling, electrical hazards, control rooms in industrial properties, active pharmaceuti- cal ingredients [API], and medical gas supply and cross contamina- tion in hospitals). Microelectronics manufacturing can also include extremely toxic, explosive, and pyrophoric gases and materials. These can create unique EHS hazards and special evacuation or con- tainment emergency HVAC operational strategies. Fume hoods are a design challenge when located in pharmaceu- tical processing rooms because they may have a small but measur- able containment leakage rate. The processing room should be positively pressurized to promote product integrity, but fume hoods require a negatively pressurized environment to support contain- ment ofhazards. Architectural layout provides a primary solution to the issue of a processing space needing protection from inbound contamination, and addresses containment concerns to protect sur- rounding spaces. Anterooms and similar buffer zones allow the cre- ation of pressure doughnuts or pressure sinks while limiting the amount of air needed to achieve appropriate control. Implementing comprehensive human health and life protection requirements, as well as fire protection systems that include hazard detection, alarm, and suppression systems, can be a complex chal- lenge that requires commissioning authorities' thorough under- standing and experience of the intricacies of different type of individual projects. Fire and Hazardous Gas Detection, Alarm, and Suppression Systems Careful design, quality installations, continuous monitoring, and effective maintenance of explosion prevention and fire protection systems promote proper safety. Early, reliable fire and hazardous gas detection alerts personnel to the danger and initiates protective actions automatically or manually. Examples include but are not limited to the following: · Gas detectors for oil and gas skids · H2 detectors for battery rooms · Spark and flame detectors for coal conveyors and fuel oil tanks · Heat detection for oil-filled transformers and lube oil and seal oil skids · Linear heat detectors for cable galleries and fuel oil tanks · Smoke and heat detection for plant and nonplant buildings Active systems, such as pumping systems, can be automatically or manually activated for use in actual fire fighting. They network with fire and gas detection and alarm systems, deluge spray sys- tems, foam systems, CO2 detectors, clean agent systems, portable and mobile extinguishers, and fire station and fire tenders. Homeland Security and Emergency Response Plan Homeland security and emergency response have become more important in the United States since September 1 1, 2001. A wareness among first responders has raised the need to be prepared for extraordinary events. Emergency response plans need to include fire protection crews with scheduled routine training, exercise, and fire protection system testing, as well as in cooperation with homeland security and civil defense programs. Examples such as firefighter safety, first responders training, protective clothing, procedures, and equipment to deal with any predictable emergency are critical to good and sustainable operations. Refer to NFPA Standard 1600 for details. IEST RECOMMENDED PRACTICES All Recommended Practices are from the Institute of Environ- mental Sciences and Technology, Arlington Heights, IL. ¦ RP-CC001.3 ¦ HEPA and ULPA filters ¦ ¦ --- ¦ --- ¦ ¦ RP-CC002 ¦ Laminar flow clean-air devices ¦ Inc. ASHRAE, 2019 user. single for Licensed | {}
c1dcf46f-187c-45da-99ae-749671ca6b8b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 19.32 ¦ RP-CC003.2 ¦ Garment system considerations in cleanrooms and other controlled environments ¦ ¦ --- ¦ --- ¦ ¦ RP-CC004.2 ¦ Evaluating wiping materials used in cleanrooms and other controlled environments ¦ ¦ RP-CC005 ¦ Gloves and finger cots used in cleanrooms and other controlled environments ¦ ¦ RP-CC006.2 ¦ Testing cleanrooms ¦ ¦ RP-CC007.1 ¦ Testing ULPA filters ¦ ¦ RP CC008 ¦ Gas-phase adsorber cells ¦ ¦ RP-CC009.2 ¦ Compendium of standards, practices, methods, and similar documents relating to contamination control ¦ ¦ RP-CC011.2 ¦ A glossary of terms and definitions relating to contamination control ¦ ¦ RP-CC012.1 ¦ Considerations in cleanroom design ¦ ¦ RP-CC012.2 ¦ Considerations in cleanroom design ¦ ¦ RP-CC012.3 ¦ Considerations in cleanroom design ¦ ¦ RP-CC013 ¦ Equipment calibration or validation procedures ¦ ¦ RP-CC014 ¦ Calibrating particle counters ¦ ¦ RP-CC015 ¦ Cleanroom production and support equipment ¦ ¦ RP-CC016 ¦ The rate of deposition of nonvolatile residue in cleanrooms ¦ ¦ RP-CC017 ¦ Ultrapure water: Contamination analysis and control ¦ ¦ RP-CC018 ¦ Cleanroom housekeeping- Operating and mon- itoring procedures ¦ ¦ RP-CC019 ¦ Qualifications for agencies and personnel engaged in the testing and certification of clean- rooms and clean air devices ¦ ¦ RP-CC020 ¦ Substrates and forms for documentation in clean- rooms ¦ ¦ RP-CC021 ¦ Testing HEPA and ULPA filter media ¦ ¦ RP-CC022.1 ¦ Electrostatic charge in cleanrooms and other con- trolled environments ¦ ¦ RP-CC023.1 ¦ Microorganisms in cleanrooms ¦ ¦ RP-CC024.1 ¦ Measuring and reporting vibration in microelec- tronics facilities ¦ ¦ RP-CC025 ¦ Evaluation of swabs used in cleanrooms ¦ ¦ RP-CC026.1 ¦ Cleanroom operations ¦ ¦ RP-CC027.1 ¦ Personnel practices and procedures in clean- rooms and controlled environments ¦ ¦ RP-CC028.1 ¦ Minienvironments ¦ ¦ RP-CC029 ¦ Automotive paint spray applications ¦ ¦ G-CC035.1 ¦ Design considerations for AMC filtration sys- tems in cleanrooms ¦ ¦ STD- CC1246D ¦ Products cleanliness levels and contamination control program ¦ REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. ACGIH. 2007. Industrial ventilation: A manual of recommended practice, 26th ed. American Conference of Governmental Industrial Hygienists, Cincinnati, OH. ASHRAE. 2017. Method of testing general ventilation air-cleaning devices for removal efficiency by particle size. ANSI/ASHRAE Standard 52.2- 2017. ASHRAE. 2013. Ventilation for acceptable indoor air quality. ANSI/ASH- RAE Standard 62.1-2013. ASHRAE. 2017. ASHRAE design guide for cleanrooms: Fundamentals, system, and performance. Boyd, G. 2011. Development of a performance-based industrial energy effi- ciency indicator for pharmaceutical manufacturing plants. Duke Uni- versity. 2019 ASHRAE Handbook-HVAC Applications (SI) Chang, A., D.Y.-L. Chan, S.-C. Hu, R.T.-C. Hsu, and T. Xu. 2009. Specific energy consumption (SEC) for the integrated circuit assembly and test- ing (IC A/T) industry in Taiwan, ASHRAE Transactions 115:2(6):290- 298. Chen, J., C. Lan, M. Jeng, and T. Xu. 2007. The development of fan filter unit with flow rate feedback control in a cleanroom. Building and Envi- ronment 42(10):3556-3561. EU. 2008. Manufacture ofsterile medical products. Revision of Annex I to the EU guide to good manufacturing practice. European Commission, Brussels. Faulkner, D., W.J. Fisk, and J.T. Walton. 1996. Energy savings in clean- rooms from demand-controlled filtration. Journal ofthe Institute ofEnvi- ronmental Sciences 39(2):21-27. LBNL-38869. Lawrence Berkeley National Laboratory, University of California, Berkeley. Faulkner, D., D. DiBartolomeo, and D. Wang. 2008. Demand controlled fil- tration in an industrial cleanroom. Report LBNL-63420. Lawrence Berkeley National Laboratory, University of California, Berkeley. FDA. 2004. Guidancefor industry: Sterile drug products produced by aseptic processing- Current good manufacturing practice. U.S. Department of Health and Human Resources, Food and Drug Administration, Wash- ington, D.C. www. fda.gov/inwonloxis Drugy Gridance Compliance Regolating/information/Ghilances/UCMONO70242f FDA. 2008. Current good manufacturing practice forfinished pharmaceu- ticals. 21 CFR 210, 211. Code ofFederal Regulations, U.S. Government Printing Office, Washington, D.C. Hu, S.C., T. Xu, T. Chong, Y.L. Chan, and R. T.C. Hsu. 2010. Characteriza- tion of energy use in 300 mm DRAM (dynamic random access memory) wafer fabrication plants in Taiwan. Energy- The International Journal 35(9):3788-3792. Hu, S.C., A. Shiue, H. Chuang, and T. Xu. 2013. Life cycle assessment of high-technology buildings: Energy consumption and associated environ- mental impacts of wafer fabrication plants. Energy and Buildings 56:126- 133. ICC. 2012. International Building Code - International Code Council, Wash- ington, D.C. ICC. 2012. International Fire Code nternational Code Council, Wash- ington, D.C. ISO. 1999. Cleanrooms and associated controlled environments Part 1: Classification of air cleanliness. ANSI/IEST/ISO Standard 14644-1:1999. International Organization for Standardization, Geneva, Switzerland. ISO. 2000. Cleanrooms and associated controlled environments- Part 2: Specifications for testing and monitoring to prove continued compliance with ISO 14644-1. ANSI/IEST/ISO Standard 14644-2:2000. Internation- al Organization for Standardization, Geneva, Switzerland. ISO. 2005. Cleanrooms and associated controlled environments Part 3: Test methods. ANSI/IEST/ISO Standard 14644-3:2005. International Organization for Standardization, Geneva, Switzerland. ISO. 2016. Cleanrooms and associated controlled environments Part 4: Design, construction and start-up. ANSI/IEST/ISO Standard 14644- 4:2001 (R2016). International Organization for Standardization, Geneva, Switzerland. ISO. 2018. Cleanrooms and associated controlled environments Part 5: Operations. ANSI/IEST/ISO Standard 14644-5:2004 (R2018). Interna- tional Organization for Standardization, Geneva, Switzerland. ISO. 2013. Cleanrooms and associated controlled environments Part 7: Separative devices (clean air hoods, gloveboxes, isolators and mini-envi- ronments). ANSI/IEST/ISO Standard 14644-7:2004 (R2013). Interna- tional Organization for Standardization, Geneva, Switzerland. ISO. 2013. Cleanrooms and associated controlled environments- Part 8: Classification of air cleanliness by chemical concentration (ACC). ANSI/IEST/ISO Standard 14644-8:2013. International Organization for Standardization, Geneva, Switzerland. ISO. 2012. Cleanrooms and associated controlled environments- Part 9: Classification of surface cleanliness by particle concentration. ANSI/ IEST/ISO Standard 14644-9:2012. International Organization for Stan- dardization, Geneva, Switzerland. ISO. 2013. Cleanrooms and associated controlled environments Part 10: Classification of surface cleanliness by chemical concentration. ANSI/ IEST/ISO Standard 14644-10:2013. International Organization for Stan- dardization, Geneva, Switzerland. Inc. ASHRAE, 2019 user. single for Licensed | {}
3bd86f48-42c6-4095-ab38-39ec9233bd01 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Clean Spaces 19.33 2007b. An characterization offan fil- ISO. 2017. High-efficiency filters and filter media for removing particles in air-Part 5: Test method for filter elements. ANSI/ISO Standard 29463- 5:2011 (R2017). International Organization for Standardization, Geneva, Switzerland. ISPE. 2001. Baseline guide volume 5: Commissioning and qualification (for pharmaceutical facilities). International Society for Pharmaceutical En- gineering, Tampa, FL. ISPE. 2009. Baseline guide volume 2: Oral solid dosage forms, 2nd ed. In- ternational Society for Pharmaceutical Engineering, Tampa, FL. ISPE. 2011. Baseline guide volume 3: Sterile manufacturingfacilities. Inter- national Society for Pharmaceutical Engineering, Tampa, FL. Jaisinghani, R.A., G. Smith, and G. Macedo. 2000. Control and monitoring of bioburden in biotech/pharmaceutical cleanrooms. Journal of Valida- tion Technology (August): 686. Lowell, C., C. Blumstein, and D. Sartor. 1999. Clean rooms and laborato- ries for high-technology industries. California Energy Commission. Fi- nal Report. www.mang.ca.gov/prossappubloshi_aaporii_oppail NEBB. 2009. Procedural standards for certified testing of cleanrooms. Na- tional Environmental Balancing Bureau, Gaithersburg, MD. NFPA. 2013. Standard on disaster/emergency management and business continuity programs. Standard 1600. National Fire Protection Associa- tion, Quincy, MA. Pedersen, C.O., D.E. Fisher, R.J. Liesen, and J.D. Spitler. 1998. Cooling and heating load calculation principles. ASHRAE. Sharp, G.P. 2010. Demand-based control of lab air change rates. ASHRAE Journal 52(2):30-41. Shieh, C. 1990. Cleanroom HVAC design. Proceedings of the 6th Interna- tional Symposium on Heat and Mass Transfer, Miami. International As- sociation for Hydrogen Energy, Coral Gables, FL. Shieh, C. 2005. Integrated cleanroom design and construction. ASHRAE Transactions 111(1):355-362. Paper 4774. SIA. 2015. International technology roadmap for semiconductors (ITRS). Semiconductor Industry Association. Spitler, J.D. 2009. Load calculation applications manual. ASHRAE. Sun, W. 2003. Development of pressurization airflow design criteria for spaces under required pressure differentials. ASHRAE Transactions 109(1):52-64. Paper 4604. Sun, W. 2005. Automatic room pressurization test technique and adaptive flow control strategy in cleanrooms and controlled environments. ASHRAE Transactions 111(2):23-34. Paper 4787. Sun, W. 2008. Conserving fan energy in cleanrooms. ASHRAE Journal 50(7). Sun, W. (in progress). Demand based control for cleanrooms. ASHRAE Research Project RP-1604, Report. Sun, W., J. Mitchell, K. Flyzik, S.-C. Hu, J. Liu, R. Vijayakumar, and H. Fukuda. 2010. Development of cleanroom required airflow rate model based on establishment of theoretical basis and lab validation. ASHRAE Transactions 116(1):87-97. Paper OR-10-011. Sun, W., K. Flyzik, J. Mitchell, A. Watave. 2011. Analysis of transient char- acteristics, effectiveness, and optimization of cleanroom airlocks (RP- 1431). ASHRAE Research Project, Report. Tsao, J.M., S.C. Hu, T. Xu, and W. C. Kao. 2010. Capturing energy-saving opportunities in make-up air systems for cleanrooms of high-technology fabrication plants in subtropical climates. Energy and Buildings 42(11): 2005-2013. Tschudi, W., E. Mills, T. Xu, and P. Rumsey. 2005. Measuring and managing cleanroom energy use. HPAC Engineering (December):29-35. Tung, Y.C., S.-C. Hu, T. Xu, and R.H. Wang. 2010. Influence of ventilation arrangements on particle removal in industrial cleanrooms with various tool coverage. Building Simulation: An International Journal 3(1):3-13. Xu, T. 2003. Performance evaluation of cleanroom environmental systems. Journal of the IEST 46:66-73. Xu, T. 2004. Considerations for efficient airflow design in cleanrooms.Jour- nal of the IEST 47:85-97. Xu, T. 2007a. Characterization of minienvironments in a cleanroom: Design characteristics and environmental performance. Building and Environ- ment 42(8):2993-3000. Xu, T. innovative method for dynamic ter unit operation. Journal of the IEST 50(2):85-97. Xu, T. 2007c. Standard methods of characterizing performance of fan filter units, version 3.0. Report LBNL-62118. Lawrence Berkeley National Laboratory, Berkeley, CA. Xu, T. 2008. Characterization of minienvironments in a cleanroom: Assess- ing energy performance and its implications. Building and Environment 43(9):1545-1552. Xu, T., C. Lan., and M. Jeng. 2007. Performance of large fan filter units for cleanroom applications. Building and Environment 42(6): 2299-2304. Yang, C., X. Yang, T. Xu, L. Sun, and W. Gong. 2009. Optimization ofbath- room ventilation design for an ISO Class 5 clean ward. Building Simula- tion: An International Journal 2(2):133-142. BIBLIOGRAPHY ACGIH. 1999. Bioaerosols: Assessment and control. American Conference of Governmental Industrial Hygienists, Cincinnati, OH. ACGIH. 2015. Guide to occupational exposure values. American Confer- ence of Governmental Industrial Hygienists, Cincinnati, OH. ASHRAE. 1992. Gravimetric and dust-spot procedures for testing air-clean- ing devices used in general ventilation for removing particulate matter. Standard 52.1-1992 (withdrawn). CFR. Annual. Boiler water additives. 21 CFR 173.310. Code ofFederal Reg- ulations, U.S. Government Printing Office, Washington, D.C. Available at www.ecfr.gov/. ICC. 2018. International mechanical codeⓇ. International Code Council, Washington, D.C. ISO. 2008. Cleanrooms and associated controlled environments, Part 6: Vocabulary (definitions of cleanroom terms). ANSI/IEST/ISO Standard 14644-6. International Organization for Standardization, Geneva, Swit- zerland. ISO. 2003. Cleanrooms and associated controlled environments- Biocon- tamination control, part 1: General principles and methods. ISO/DIS Standard 14698-1. International Organization for Standardization, Geneva, Switzerland. ISO. 2003. Cleanrooms and associated controlled environments-Biocon- tamination control, part 2: Evaluation and interpretation of biocontami- nation data. ISO/DIS Standard 14698-2. International Organization for Standardization, Geneva, Switzerland. NFPA. 2015. Flammable and combustible liquid code. Standard 30. National Fire Protection Association, Quincy, MA. NFPA. 2015. National fuel gas code. Standard 54. National Fire Protection Association, Quincy, MA. NFPA. 2013. Standard for the production, storage, and handling liquefied natural gas (LNG). Standard 59A. National Fire Protection Association, Quincy, MA. NFPA. 2011. Boiler and combustion system hazards code. Standard 85. National Fire Protection Association, Quincy, MA. NFPA. 2015. Life safety codeⓇ Standard 101. National Fire Protection Association, Quincy, MA. NFPA. 2015. Standard for protection ofsemiconductor fabrication facilities. Standard 318. National Fire Protection Association, Quincy, MA. NFPA. 2012. Standard for the prevention of fires and explosions in wood processing and woodworking facilities. Standard 664. National Fire Pro- tection Association, Quincy, MA. Sun, W. 2018. Cleanroom airlock performance and beyond. ASHRAE Journal 60(2):64-69. U.S. DHHS. 2011. Guidance for industry- Process validation: General principles and practices. U.S. Department of Health and Human Ser- vices, U.S. Food and Drug Administration, Center for Drug Evaluation and Research, Center for Biologics Evaluation and Research, and Center for Veterinary Medicine. www.fita.gov/downloadsDrugs/Guidances /UCM070336.pdf. Whyte, W. 1999. Cleanroom design, 2nd ed. John Wiley, New York. Xu, T., and M. Jeng. 2004. Laboratory evaluation offan filter units' aerody- namic and energy performance. Journal of the IEST 47(1):116-120. Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
a309f6df-94b6-4bde-853a-fa3aa68c0949 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 20 DATA CENTERS AND TELECOMMUNICATION FACILITIES ¦ USEFUL DATACOM RESOURCES ¦ 20.1 ¦ Datacom Equipment Components ¦ 20.9 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ DATACOM EQUIPMENT, POWER TRENDS, AND ¦ ¦ DATACOM FACILITIES ¦ 20.10 ¦ ¦ ENVIRONMENTAL GUIDELINES ¦ 20.4 ¦ GENERAL CONSIDERATIONS ¦ 20.10 ¦ ¦ Datacom Equipment Workload ¦ 20.4 ¦ Air Cooling ¦ 20.14 ¦ ¦ Datacom Equipment Racks ¦ 20.4 ¦ Liquid Cooling ¦ 20.17 ¦ ¦ Datacom Equipment ¦ ¦ Water Usage ¦ 20.17 ¦ ¦ (Hardware) ¦ 20.4 ¦ Energy Efficiency ¦ 20.18 ¦ D different than most other facilities: centers and telecommunication facilities are significantly · Occupants of most facilities are people; the occupants in data cen- ters are computer hardware and software applications. · Load is more volatile and transient because hardware upgrades, software additions, and computing loads can change so rapidly. · Computer hardware is the major equipment, and equipment life- times are often measured in months rather than years. This results in upgrade/life cycle mismatches between hardware and facility power/cooling. · Often data centers have an actual power/cooling load density 10 times or more that of a typical office building. The telecommunication industry is rapidly changing from pre- dominantly regulated land lines to wireless technology that uses the same communications protocol (Internet Protocol or IP) as the data center industry. As a result, data centers and telecommunications facilities are converging. TC 9.9 uses the term "datacom" to indicate both data centers and telecommunication facilities. This chapter pro- vides some basic information about datacom facilities and where to find additional information. The main requirements for datacom facilities are space, power, cooling, and networking. Often, these are treated as services. Each service can have a service-level agreement (SLA), but the services are highly interdependent. Therefore, overall reliability/availability is best achieved when all aspects of these services are designed together, with the same performance goals. Because of the high den- sities, it is becoming increasing popular to provide metering for ser- vices at each service interface point, with centralized monitoring of the infrastructure. Because of the high capital cost and short life cycles of datacom equipment, as well as the continued evolution of both public and pri- vate cloud computing (i.e., computing as a service), the trend is to- wards companies owning less of their own datacom facilities, and renting more resources from a third-party facility owner/provider. Rented or leased services and facilities come in many varieties; a common general format is retail or wholesale colocation facilities. A colocation center (also co-location, collocation, colo, or co- loc) is a type of datacom facility where equipment, space, and band- width are available for rent. Colocation facilities provide space, power, cooling, and physical security services for server, storage, and networking equipment. Their fiber services are typically redun- dant and diverse, and connect the facilities to various telecommuni- cations and network service providers. However, the power and cooling redundancies can be significantly different from one The preparation of this chapter is assigned to TC 9.9, Mission Critical Facilities, Data Centers, Technology Spaces, and Electronic Equipment. colocation center to another, and should be evaluated before signing a contract, which should include a carefully worded SLA. Failures in these facilities can have widespread effects. Figure 1 provides an overview of the major spaces in a typical datacom facility. Datacom facilities provide space, power, cooling, and networking to datacom equipment (hardware), also known as information tech- nology equipment (ITE) in the U.S. National Electrical CodeⓇ (NFPA Standard 70). The space within the datacom facility or data center that actually houses the datacom hardware may be called the data hall, the ITE equipment room, or the white space. Figure 1 shows the various elements that may make up a complete facility. The actual elements (and their arrangements) vary considerably in each project. This chapter focuses on the most important facility requirements for the support of the datacom equipment, which include thermal, air quality, and power. 1. USEFUL DATACOM RESOURCES ASHRAE Datacom Series This series comprises 13 books produced by TC 9.9. To keep pace with the rapidly evolving datacom industry, some books have been revised several times, with new editions containing updated infor- mation. New titles are also planned for the future. These books are equally useful for experts and people new to this industry. The following includes brief descriptions of each book. Thermal Guidelines for Data Processing Environments, 4th ed. (ASHRAE 2015a). The trend toward increased equipment power density in data centers presents significant challenges to thermal design and operation. Undesirable side effects include decreased equipment availability, wasted floor space, and inefficient cooling- system operation. Avoiding a mismatch between datacom equipment environmental requirements and those of adjacent equipment, or between datacom equipment requirements and facility operating conditions, requires a standard practice solution to datacom equipment interchangeability that preserves industry innovation. ASHRAE (2015a) provides a framework to align the goals of equipment hardware manufacturers, facility designers, operators, and managers. This book covers four primary areas: equipment op- erating environment specifications, facility temperature and humid- ity measurement, equipment placement and airflow patterns, and equipment manufacturers' heat load and airflow requirements re- porting. IT Equipment Power Trends, 3rd ed. (ASHRAE 2018). Datacom equipment technology is advancing at a rapid pace, resulting in relatively short product cycles and an increased fre- quency of datacom equipment upgrades. Because datacom facilities 20.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
9afeee89-b5fe-4b19-b4ba-d673efbe081b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 20.2 2019 ASHRAE Handbook-HVAC Applications (SI) ![image](/image/placeholder) DATACOM FACILITY BUILDING ENVELOPE ELECTRIC BUILDING UTILITY TELECOM SERVICE ENTRANCE GENERAL OFFICES & SPACES NOT DIRECTLY GENERAL SUPPORTING DATA CENTER BUILDING GENERATORS TELECOM DATA CENTER DATA CENTER DATA CENTER OPERATIONS SECURE PoP STAFF OFFICES CENTER ENTRY MAIN BUILDING SWITCHBOARD SETUP & TEST DATA HALL 1 DATA HALL / INFORMATION T INFORMATION TECHNOLOGY 1 TECHNOLOGY EQUIPMENT (ITE) ROOM EQUIPMENT (ITE) ROOM STORAGE WHITE SPACE ! WHITE SPACE DATA CENTER EXTERIOR MECHANICAL (Rooftop, UNCRATE Ground Level, DATA CENTER DATA CENTER Balcony, Etc.) MECHANICAL ELECTRICAL LOADING DOCK Fig. 1 Typical Datacom Facility Space Plan and their associated HVAC infrastructure are typically built to have longer life cycles, any modern datacom facility needs the ability to seamlessly accommodate the multiple datacom equipment deploy- ments it will experience during its lifetime. Based on the latest information from leading datacom equipment manufacturers, ASHRAE (2018) provides datacom equipment power trend charts through 2025 to allow datacom facility designers to more accurately predict future equipment loads, and supplies ways of applying the trend information to datacom facility designs today. Also included is a review of various air- and liquid-cooling system capabilities and considerations for handling future loads and an invaluable appendix containing terms and definitions used by datacom equipment manufacturers, the facilities operation industry, and the cooling design and construction industry. Design Considerations for Datacom Equipment Centers (ASHRAE 2009a). The design of computer rooms and telecommunications facilities differs in fundamental ways from the design of facilities used primarily for human occupancy. As the power density of datacom equipment continues to increase, this difference has grown more extreme. This book covers basic design considerations for data and communications equipment centers. The Datacom Facility Basics section includes chapters on datacom design criteria (temperature, temperature rate of change, relative humidity, dew point, and filtration), HVAC load, computer room cooling (including both air and liquid cooling), and air distribution. The section on Other Considerations includes chapters on ancil- lary spaces (battery plants, emergency generator rooms, burn-in rooms and test labs, and spare parts rooms), contamination, acous- tical noise emissions, structural and seismic design and testing, fire detection and suppression, commissioning, availability and redun- dancy, and energy efficiency. This book does not cover electrical or electronic systems design and distribution. Liquid Cooling Guidelines for Datacom Equipment Centers, 2nd ed. (ASHRAE 2013). Datacom equipment today is predomi- nantly air cooled. However, with rack heat loads steadily climbing, the ability of many data centers to deliver either adequate airflow rates or sufficient chilled air is now being stretched to the limit. These trends in the heat load generated by datacom equipment can have detrimental side effects, such as decreased equipment avail- ability, wasted floor space, and inefficient cooling system operation. This situation is creating a need for implementing liquid cooling solutions. The overall goals ofliquid implementations include aspects such as transferring as much waste heat to the facility liquid-cooling loop as possible, reducing the overall volume of airflow needed by the racks, and reducing processor temperatures to improve computer performance. This book includes definitions for liquid and air cooling as they apply to the datacom equipment, describing the various liquid loops that can exist in a building that houses a datacom space. The book also bridges the liquid-cooling systems by providing guidelines on interface requirements between the chilled-water system and the technology-cooling system, and outlines the requirements ofliquid- cooled systems that attach to an electronics rack and are imple- mented to help datacom room thermal management. Structural and Vibration Guidelines for Datacom Equipment Centers (ASHRAE 2008a). The typical life span of datacom equip- ment is often three to five years. On the other hand, the anticipated life span of the mechanical and electrical infrastructure is 15 to 20 years, and the building's structure can last 20 to 50 years. Con- sequently, the building's infrastructure and structure may eventually house and support many vintages of datacom equipment. This book is divided into four main sections. Part 1 gives an over- view of the best practices in the design of datacom facilities, including recommendations for new and renovated building struc- tures, building infrastructure, and datacom equipment. Part 2 covers design of new and existing structures. In Part 3, structural consider- ations of the building' s infrastructure, raised-access floor systems, and vibration sources and their control are discussed in detail. Part 4 covers shock and vibration testing, seismic anchorage systems, and analysis of datacom equipment. Inc. ASHRAE, 2019 user. single for Licensed | {}
27caef16-a7cf-4c6d-9dfa-e1906d7b1232 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Data Centers and Telecommunication Facilities 20.3 Best Practices for Datacom Facility Energy Efficiency, 2nd ed. (ASHRAE 2009b). Sustainable design, global warming, dwindling fuel reserves, energy use, and operating cost are becoming increas- ingly more important. These issues are even more important in datacom facilities because of their large, concentrated use of energy (which can be 100 times the usage of an office building); 24/7 operations have about three times the annual operating hours as oth- er commercial properties. The intent of this publication is to provide detailed information to help minimize the life-cycle cost to the client and maximize energy efficiency in a datacom facility. This book covers many aspects of datacom facility energy effi- ciency, including environmental criteria, mechanical equipment and systems, economizer cycles, airflow distribution, HV AC controls and energy management, electrical distribution equipment, datacom equipment efficiency, liquid cooling, total cost of ownership, and emerging technologies. There are also appendices on topics such as facility commissioning, and operations and maintenance. High Density Data Centers- Case Studies and Other Consid- erations (ASHRAE 2008b). Data centers and telecommunications rooms that house datacom equipment are becoming increasingly more difficult to adequately cool because datacom equipment man- ufacturers continually increase datacom performance at the cost of increased heat dissipation. The objective of this book is to provide a series of case studies of high-density data centers and a range of ventilation schemes that demonstrate how loads can be cooled using a number of approaches. Particulate and Gaseous Contamination in Datacom Environ- ments, 2nd ed. (ASHRAE 2014a). Particulate and gaseous contam- ination monitoring, prevention, and control in datacom environments have gained greater importance because of an increase in datacom equipment reliability concerns arising from many factors: mission- critical societal dependence on computers; continued miniaturization of electronic circuit features; elimination of lead from printed circuit board solder metallurgies; proliferation of datacom equipment into locations with high levels of sulfur-bearing contamination; increased use of free-air cooling to conserve energy; and expansion of the al- lowable temperature-humidity datacom equipment envelope. This book describes in detail the procedures necessary to ensure airborne contaminants will not be a factor determining datacom equipment reliability. It also includes the description of a landmark ASHRAE gaseous contamination datacom facility survey that found that silver corrosion rate is a much better predictor of corrosion- related hardware failures, compared to the prior practice ofrelying on copper corrosion rate to predict failures. Real-Time Energy Consumption Measurements in Data Cen- ters (ASHRAE 2010). Data centers are dense and complex environ- ments that house a wide variety of energy-consuming equipment. With datacom equipment and associated facility equipment, there are thousands of energy consumption monitoring points. If a datacom facility operator cannot monitor a device, that device can- not be controlled. In addition, for a datacom facility to reach its opti- mal energy efficiency, all equipment on the datacom and facilities side must be monitored and controlled as an ensemble. Datacom equipment and facilities organizations in a company typically have different reporting structures, which results in a com- munication gap. This book is designed to help bridge that gap and provides an overview ofhow to instrument and monitor key power and cooling subsystems. It also includes numerous examples ofhow to use energy consumption data in calculating power usage effec- tiveness (PUE). Green Tips for Data Centers (ASHRAE 2011). The datacom in- dustry is focused on reducing energy. This focus is driven by in- creasing energy costs and capital costs to add more datacom facility capacity. Combined with the rapid growth in the industry and the in- crease in the power used by the datacom equipment, it is important that every data center operator understands the options for reducing energy. This book gives datacom facility owners and operators a clear understanding of energy-saving opportunities. It covers the build- ing's mechanical and electrical systems as well as the most promising opportunities in technology. In addition, the book's orga- nization follows a logical approach that can be used for conducting a preliminary energy assessment. PUETM: A Comprehensive Examination of the Metric (ASH- RAE 2014b). Power usage effectiveness (PUE), the industry- preferred metric for measuring the actual infrastructure energy effi- ciency for datacom facilities, is an end-user tool that helps boost en- ergy efficiency in datacom facility operations. This book provides a high level of understanding of the concepts surrounding PUE, plus in-depth application knowledge and resources to those implementing, reporting, and analyzing datacom facility metrics. It gives actionable information useful to a broad audience rang- ing from novice to expert in the datacom equipment industry, including executives, facility planners, facility operators, datacom equipment manufacturers, HVAC&R manufacturers, consulting engineers, energy audit professionals, and end users. PUE was developed by The Green Grid Association, a nonprofit, open industry consortium of end users, policy makers, technology providers, facility architects, and utility companies working to im- prove the resource efficiency of information technology and datacom facilities worldwide. Since its original publication in 2007, PUE has been globally adopted by the industry, and The Green Grid has continued to refine the metric measurement methodology with collaborative industry feedback. For further details, see the section on Power Usage Effectiveness in this chapter. Server Efficiency-Metrics for Computer Servers and Storage (ASHRAE 2015b). This book consolidates information on current server and storage subsystem energy benchmarks for use in selecting the appropriate IT hardware solutions. Each chapter describes a metric and its target market, includes examples of data generated from the subject benchmark or tool, and provides guid- ance on interpreting the data. This book supplies the information needed to select the best measure of performance and power for a variety of server applications. IT Equipment Design Impact on Data Center Solutions (ASHRAE 2016a). This book provides guidance in making the crit- ical data center infrastructure equipment selections and design con- figurations. ANSI/ASHRAE Standard 90.4-2016, Energy Standard for Data Centers (ASHRAE 2016b) This standard provides a performance-based (non-prescriptive) alternative to Standard 90.1 for demonstrating compliance with minimum datacom facility efficiency in the design stage. It balances the need for energy efficiency with the concurrent need for reliabil- ity in high-performance datacom facilities. ANSI/ASHRAE Standard 127-2012, Method of Testing for Rating Computer and Data Processing Room Unitary Air Conditioners This standard establishes a uniform set of requirements for rating computer and data processing room (CDPR) unitary air conditioners. ANSI/AHRI Standard 1361 (SI)-2017, Performance Rating of Computer and Data Processing Room Air Con- ditioners This standard establishes a uniform set ofrequirements for rating CDPR air conditioners. Inc. ASHRAE, 2019 user. single for Licensed | {}
972b8d8e-81f8-4526-9771-b0741e76daf3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 20.4 2019 ASHRAE Handbook- -HVAC Applications (SI) ANSI/TIA Standard TIA-942-B-2017, Telecommunica- tions Infrastructure Standard for Data Centers The Telecommunications Industry Association's Standard TIA- 942 specifies minimum requirements for telecommunications infra- structure of data centers and computer rooms, including single- tenant enterprise data centers and multitenant Internet hosting data centers. The TIA-942 specification references private and public domain data center requirements for applications and procedures such as network architecture, electrical design, file storage, back-up and archiving, system redundancy, network access control and security, database management, web hosting, application hosting, content distribution, environmental control, protection against physical haz- ards (fire, flood, windstorm), and power management. ANSI/BICSI Standard 002-2014, Data Center Design and Implementation Best Practices This standard from the Building Industry Consulting Service International (BICSI) provides requirements, guidelines, and best practices intended for use internationally. 2. DATACOM EQUIPMENT, POWER TRENDS, AND ENVIRONMENTAL GUIDELINES 2.1 DATACOM EQUIPMENT WORKLOAD Datacom equipment (hardware) has various workload states ranging from essentially idle/static (not performing any actual useful work) to running at its maximum performance and central processing unit (CPU) utilization. The hardware workload is driven by software. There is system or operating system software (including networking), and application software that yields calculation or data manipulation results (actual useful work). The number of applications available across all hardware types is vast (in the multimillions at least). Software can often be added or upgraded in various ways, including remotely. This means the workloads, and therefore power and cooling loads, can be very dynamic. Inc. ASHRAE, 2019 user. single for Licensed Datacom equipment life cycles are much shorter than power and cooling infrastructure life cycles. Application software life cycles are even shorter. It is critical that power and cooling infrastructure planning considers the life cycles and refresh (churn) rates of hard- ware and software. Load Characterization From a datacom power and cooling infrastructure planning per- spective, the two common means of maximum load characterization are watts per square metre and kilowatts per datacom equipment rack or cabinet. The datacom industry sometimes uses granularity as a means of describing the unit size. Many in the datacom industry think that kilowatts per rack is superior to watts per square metre. However, at the start of a project, there may be insufficient information about the quantity of racks or their expected contents, making that metric too granular. Profes- sional judgment is critical to deciding which maximum load char- acterization to use. Of equal importance is characterizing the minimum load as well as the load variation. The time increment for load variation can be very short (e.g., seconds, minutes) or very long. It is important to obtain or develop a detailed load profile including future possibili- ties. ![image](/image/placeholder) W W TWO-POST OPEN RACK FOUR-POST OPEN RACK OR CABINET (Footprint = W x Datacom Equipment Depth) (Footprint = W X D) Fig. 2 Typical Rack and Cabinet Examples 2.2 DATACOM EQUIPMENT RACKS Most datacom equipment is rack or cabinet mounted, but others come in prepackaged configurations, including large, stand-alone cabinets. Rack and cabinet sizes and equipment mounting standards are defined by the Electronic Industries Alliance (EIA 2005). The vertical dimension is expressed in terms of units (U) (some- times rack units [RU]). One U or RU represents 44.45 mm of ver- tical height within a rack. A common height for a rack is 42 U, although some are taller and some are shorter. The terms rack and cabinet are often used interchangeably, although technically they are different. A rack is an open-frame two- or four-post mounting used more for telecom and patch panels than for servers. A cabinet is a similar four-post framework, but is equipped with sides, top, and often front and rear doors (Figure 2). Typical rack widths are approximately 485 or 600 mm, depend- ing on their construction. The actual space between the mounting rails is approximately 50 mm less than the nominal panel widths, to allow room for screwing equipment flanges to the rails. Cabinets tend to be a nominal 600 to 760 mm wide and 600 to 1200 mm deep. The wider cabinets are often used to provide space for the massive amount of power and data cabling associated with full configura- tions of high density hardware. Deeper cabinets have become nec- essary to accommodate the form factors of newer datacom hardware, which are often compressed to only 1 or 2 U high, but can be quite deep as a result. Servers used for computing are available in rack mount and cus- tom configurations. Most servers are full-rack width and are often identified as having 1U, 2U, 4U, etc., form factors (Figure 3). A half-width server mounts two separate boards side-by-side in a single-width 1U high chassis, or four separate boards in a single- width 2U chassis. Larger form factors may house multiple modular servers (blade servers) in its overall chassis. 2.3 DATACOM EQUIPMENT (HARDW ARE) Datacom components (e.g., processors, memory, storage, input/ output [I/O], power supplies) are packaged into datacom equipment. This section is limited to datacom equipment requirements and interfaces; components are only addressed to the level necessary to describe the requirements and interfaces, but are covered in more depth in the section on Datacom Equipment Components. | {}
212364a2-dd63-4134-88ae-fca4b235808b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Data Centers and Telecommunication Facilities 20.5 Datacom equipment predominantly consists of servers (volume, blade, etc.), communication equipment (switches, routers, etc.), and data storage devices (storage area network [SAN], network attached storage [NAS], and other formats that are beyond the scope of this chapter). For air-cooled datacom equipment, the primary interface to the facility is the air inlet to the datacom equipment. For liquid-cooled equipment, the interface to the facility is the liquid connection to the equipment or the rack. The datacom equipment interface focuses on · Temperature · Humidity · Air quality · Coolant flow (air or liquid) Server Classifications Servers tend to be the most common equipment within a datacom space; there are many different types of servers and any type of server can go into any type of datacom facility. Although there are no set rules regarding what constitutes any specific server type, the following classifications help provide some guidance: · General purpose, volume. These servers are typically single or dual socket servers packaged in 1U, 2U, or half-width form fac- tors. They generally have many features to cover a wide variety of customer needs. These are often called small-form-factor servers because of their minimal usage of rack height, but their depths can be significantly greater than will fit into legacy 600 mm deep racks. · Cloud, volume. These systems are typically single- or dual- socket boards packaged in 1U, 2U, or half-width form factors. These servers have a limited, targeted set of features selected to address specific workloads. · Special-purpose. Mainframes and custom server designs fall into this category. Features and packaging vary widely, depending on ![image](/image/placeholder) 1U 2U ��� MMM 3U 7U 4U the target customer. Chassis sizes also vary widely and include rack-level servers and multiframe systems. · Blade. Typically, blade servers have a multi-U chassis supporting multiple individual servers constructed on independent circuit boards called blades. The blades plug into a common backplane, enabling interconnection of boards. Cooling, power, and switch functionality are shared among the boards. Datacom Equipment Airflow Standardized nomenclature defining the cooling airflow paths for datacom equipment have remained unaltered since 2004 (Figure 4). Most datacom equipment now uses the front-to-rear protocol. The exceptions are some legacy telecommunications equipment and some network switches. These may use a side-to-side protocol, or a mix of side-to-side-to-top and/or to-rear air flows, that are not shown. When airflow does not follow standardized protocol, special rack mountings and/or air deflectors may be necessary to achieve proper cooling in facilities designed predominantly for front-to-rear cooled equipment. Liquid-Cooled Datacom Equipment The increasing heat densities of modern electronics are stretching the ability to adequately cool the electronic components within servers with air. The trend to higher recommended inlet air temperatures, done with the goal of saving energy, exacerbates the problem. Liquid cooling is therefore becoming more prevalent. Liquid cooling is defined as the process where a liquid (rather than "fluid" air) is used to provide the heat removal (i.e., cooling) function. There are many different liquid-cooling solutions for data- com rooms. The most common implementations are · Liquid-cooled rack: a circulated liquid provides heat removal (cooling) at a rack or cabinet level for operation. Examples include rear-door or in-rack heat exchangers that transfer a large percentage of the datacom equipment waste heat from air to liquid. · Liquid-cooled datacom equipment: liquid is circulated within the datacom equipment for heat removal (cooling) operation. · Liquid-cooled electronics: liquid is circulated directly to the electronics for cooling, with no other heat transfer mechanisms. These definitions do not limit the cooling fluid to water. Various liquids could be considered for application, including some that could be in a vapor phase in part of the cooling loop. Figure 5 depicts one example of liquid-cooled datacom equip- ment where a liquid loop internal to the rack is used to cool the components in the rack. In this case, the heat exchange is with a liquid-to-facility-water heat exchanger. Typically, liquid circulating in the rack is kept above dew point to eliminate any condensation concerns. Fig. 3 Typical Computer Server Packaging Form Factors Chart Type: pie SIDE, LEFT (SL) FRONT (F) BOTTOM (B) SIDE, RIGHT (SR) REAR (R) TOP (T) item_01 30% 20% 10% 30% 15% 5% Chart Type: pie Dark Blue Light Blue item_01 50% 50% FACE DEFINITION SYNTAX FRONT TO TOP (F-T) ![image](/image/placeholder) AIRFLOW PROTOCOL FRONT TO TOP AND REAR (F-T/R) Fig. 4 Equipment Airflow (ASHRAE 2015a) Inc. ASHRAE, 2019 user. single for Licensed | {}
4070de5d-f1cf-4992-8171-2b91aa96ddb5 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 20.6 2019 ASHRAE Handbook-HVAC Applications (SI) CEILING STRUCTURE Chart Type: bar Liquid-Cooled Electronics Pump Facility Water Supply and Return Liquid from Electronics Floor Tiles Frack item_01 10 10 10 10 10 10 Fig. 5 Internal Liquid-Cooling Loop Exchanging Heat with Liquid-Cooling Loop External to Racks Contamination Most datacom facilities are well designed and are geographically located in areas with relatively clean environments. Therefore, they do not have significant contamination concerns. However, the overall cleanliness of the environment is only one consideration for the loca- tion of a datacom facility, so potential contamination is often not con- sidered to be a major driver. There are two types of contaminants: particulate and gaseous. Some datacom facilities may have harmful environments arising from the ingress of outdoor contamination. In some rare instances, contamination has been generated within the datacom facility itself. · Particulate matter refers to airborne solid and liquid particles. For the purposes of this chapter, the terms particle,particulate, aerosol, and dust are considered equivalent and are represented by the term particulate matter. The size of airborne particulate matter can span a vast range from about 0.001 m to more than 100 m. Agencies that monitor particulate matter from a health point of view catego- rize particle mass concentration as PM2.5 and PM10, representing particles smaller than 2.5 m and 10 m, respectively. Particulate matter may also be categorized in three size modes: fine (0.001 to 0.1 m), accumulation (0.1 to 2.5 m), and coarse (2.5 to 10 m). Coarse mode is generally limited to particles smaller than 10 m, but can include much larger airborne fibers and particles. Particu- late matter in each ofthese size categories may be composed of var- ious materials from many different sources. · Gaseous contaminants relevant to information technology (IT) and datacom equipment reliability include hydrogen sulfide, sulfur dioxide, mercaptans, and oxides of nitrogen, chlorine, and ozone, each of which can produce adverse effects on computer hardware. These harmful gases are by-products of geological, biological, agricultural, industrial, and manufacturing activities. They can, even at low g/m3 levels, act alone or in synergy with each other or with particulate matter to corrode metallic materials, causing irre- versible damage to circuit boards, connectors, integrated circuits, and other electronic components. If a datacom facility serving a critical application happens to be susceptible to gaseous or particulate contamination, the consequences could be severe. As a result, it is important to address the potential for contamination and mitigate the risk as much as practical. A number of factors can result in an increased failure rate. Changes in solder type (lead based to lead free), and an ongoing miniaturizing of datacom equipment components increase the risk. Changes in datacom room temperature and humidity operating con- ditions combined with a lower priority consideration for the sur- rounding air quality are other factors of concern. Contaminants can cause either electrical or cooling failures within datacom equipment. Electrical circuits typically fail in either an open or a shorted condition. Datacom equipment circuits are much smaller than normal power circuits, often with conductors smaller than a human hair. They are, therefore, more susceptible to damage, but they fail in a similar manner. Printed circuit boards use tiny copper wires (lands) and components are attached with silver solder, and the two common datacom equipment circuit failures are copper creep corrosion and silver creep corrosion. Airborne dust contaminants can be detected from detailed visual inspections of filters in the air-handling systems. Gaseous contam- inant presence may require seasonal or periodical monitoring and measurement through the use of copper and silver coupon testing in the datacom rooms. The coupons react when exposed to various gases, with the typical exposure period being around one month. A subsequent lab analysis of the coupons can quantify the level of con- taminants present. Filtration systems (particulate filtration or gas filtration units) can be used to mitigate the risk of contaminants in the datacom facility. More information on this topic can be found in ASHRAE (2015a). Environmental Guidelines for Air-Cooled Equipment The first edition of ASHRAE's Thermal Guidelines for Datacom Processing Environments in 2004 created a common design point: the inlet temperature for datacom equipment. The 2008 edition expanded the recommended thermal envelope, and the 2011 edition increased the datacom class definitions from two to four, with wider thermal ranges. The fourth edition (ASHRAE 2015a) makes signif- icant changes to the humidity ranges as well. All of these changes were made after a great deal of industry study and, in the case of the humidity changes, a major ASHRAE research study (Pommerenke and Swenson 2014). Important considerations include the following. Recommended Environmental Range. To achieve both energy efficiency and equipment operating reliability and longevity, facili- ties must be designed to achieve, under normal circumstances, ambient equipment inlet conditions that fall within ASHRAE rec- ommended temperature and humidity ranges. See Table 1 for this range, or use the process defined by ASHRAE (2015a). Allowable Environmental Range. The allowable envelope is where datacom equipment manufacturers test their equipment to verify that it will function within those environmental boundaries. Typically, datacom equipment manufacturers perform tests before product announcement, to verify that products meet all functional requirements within this environmental envelope. This is not a state- ment of reliability, but rather one of functionality of the datacom equipment. In addition to the allowable dry-bulb temperature and relative humidity ranges, the maximum dew point and maximum elevation values are part of the allowable operating environment definitions. Inc. ASHRAE, 2019 user. single for Licensed Practical Application. Prolonged exposure of operating equip- ment to conditions outside its recommended range, especially approaching the extremes of the allowable operating environment, can result in decreased equipment reliability and longevity (server reliability values versus inlet air temperatures are provided in ASHRAE [2015a] to provide some guidance on operating outside the recommended range). Exposure of operating equipment to con- ditions outside the allowable operating environment risks cata- strophic equipment failure. With equipment at high power density, it may be difficult to maintain the air entering the equipment within the recommended range, particularly over the entire face of the equipment. Reasonable efforts should always be made to achieve conditions within the recommended range. However, if these efforts prove unsuccessful, operation outside the recommended range, but within the allowable environmental range, is likely to be adequate, but facility operators may wish to consult with the equipment man- ufacturers regarding the risks involved. | {}
a10888f5-f3fb-4d8d-8352-14f409cfb5c7 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Data Centers and Telecommunication Facilities 20.7 Table 1 2015 Thermal Guidelines: Equipment Environment Specifications for Air Cooling ¦ ¦ Product Operationb,c ¦ Product Operationb,c ¦ Product Operationb,c ¦ Product Operationb,c ¦ Product Operationb,c ¦ Product Power Offc,d ¦ Product Power Offc,d ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Classa ¦ Dry-Bulb Temperature,�g °C ¦ Humidity Range, Noncondensingh,i,k,l ¦ Maximum Dew Point,k °C ¦ Maximum Elevation,e.j.m m ¦ Maximum Rate of Change,f K/h ¦ Dry-Bulb Temperature, °C ¦ Relative Humidity,k % ¦ ¦ Recommended (suitable for all classes; explore data center metrics in ASHRAE [2016] for conditions outside this range) ¦ Recommended (suitable for all classes; explore data center metrics in ASHRAE [2016] for conditions outside this range) ¦ Recommended (suitable for all classes; explore data center metrics in ASHRAE [2016] for conditions outside this range) ¦ Recommended (suitable for all classes; explore data center metrics in ASHRAE [2016] for conditions outside this range) ¦ Recommended (suitable for all classes; explore data center metrics in ASHRAE [2016] for conditions outside this range) ¦ Recommended (suitable for all classes; explore data center metrics in ASHRAE [2016] for conditions outside this range) ¦ Recommended (suitable for all classes; explore data center metrics in ASHRAE [2016] for conditions outside this range) ¦ Recommended (suitable for all classes; explore data center metrics in ASHRAE [2016] for conditions outside this range) ¦ ¦ Al to A4 Allowable ¦ 18 to 27 ¦ -9 to 15°C dp and 60% rh ¦ ¦ ¦ ¦ ¦ ¦ ¦ A1 ¦ 15 to 32 ¦ -12°C dp and 8% rh to 17°C dp and 80% rh ¦ 17 ¦ 3050 ¦ 5/20 ¦ 5 to 45 ¦ 8 to 80 ¦ ¦ A2 ¦ 10 to 35 ¦ -12°C dp and 8% rh to 21°C dp and 80% rh ¦ 21 ¦ 3050 ¦ 5/20 ¦ 5 to 45 ¦ 8 to 80 ¦ ¦ A3 ¦ 5 to 40 ¦ -12°C dp and 8% rh to 24°C dp and 85% rh ¦ 24 ¦ 3050 ¦ 5/20 ¦ 5 to 45 ¦ 8 to 80 ¦ ¦ A4 ¦ 5 to 45 ¦ -12°C dp and 8% rh to 24°C dp and 90% rh ¦ 24 ¦ 3050 ¦ 5/20 ¦ 5 to 45 ¦ 8 to 80 ¦ ¦ B ¦ 5 to 35 ¦ 8% to 28°C dp and 80% rh ¦ 28 ¦ 3050 ¦ N/A ¦ 5 to 45 ¦ 8 to 80 ¦ ¦ C ¦ 5 to 40 ¦ 8% to 28°C dp and 80% rh ¦ 28 ¦ 3050 ¦ N/A ¦ 5 to 45 ¦ 8 to 80 ¦ Note: For potentially greater energy savings, refer to Appendix C of ASHRAE (2015a) for the process needed to account for multiple server metrics that impact overall total cost of ownership (TCO). aClasses A3, A4, B, and C are identical to those in the 2011 edition of Thermal Guidelines for Data Processing Environments. The 2015 version of the A1 and A2 classes have expanded relative humidity levels compared to the 2011 version. bProduct equipment is powered on. Tape products require a stable and more restrictive environment (similar to Class A1). Typical requirements: temperature between 15°C and 32°C, relative humidity between 20 and 80%, maximum dew point 22°C, rate of change of temperature less than 5 K/h, rate of change of humidity less than 5% rh per hour, and no condensation. dProduct equipment is removed from original shipping container and installed but not in use (e.g., during repair, maintenance, or upgrade). Classes A1, A2, B, and C: Derate maximum allowable dry-bulb temperature 1 K/300 m above 900 m. Above 2400 m altitude, derated dry-bulb temperature takes precedence over recommended temperature. Class A3: Derate maximum allowable dry-bulb temperature 1 K/175 m above 900 m. Class A4: Derate maximum allowable dry-bulb temperature 1 K/125 m above 900 m. fFor tape storage: 5 K in an hour. For all other ITE: 20 K in an hour and no more than 5 K in any 15 min period of time. Temperature change of ITE must meet limits shown in table, and is calculated as maximum air inlet temperature minus minimum air inlet temperature within specified time window. The 5 and 20 K temperature change is considered to be a temperature change within a specified period of time and not a rate of change. See Appendix K of ASHRAE (2015a) for additional information and examples. gWith diskette in drive, minimum temperature is 10°C (not applicable to Classes A1 or A2). hMinimum humidity level for Classes Al, A2, A3, and A4 is the higher (more moisture) of the -12°C dew point and the 8% rh. These intersect at approximately 25°C. Below this intersection, the dew point represents the minimum moisture level, whereas above it, the relative humidity is the minimum. iBased on ASHRAE research and performed at low relative humidity, minimum requirements are 1. Data centers with non-ESD floors and where people are allowed to wear non-ESD shoes may want to consider increasing humidity, given that the risk of generating 8 kV increases slightly from 0.27% at 25% rh to 0.43% at 8% (see Appendix D of ASHRAE [2015a] for details). 2. All mobile furnishing/equipment must be made of conductive or static dissipative materials and bonded to ground. 3. During maintenance on any hardware, a properly functioning and grounded wrist strap must be used by any personnel who contacts ITE. jTo accommodate rounding when converting between SI and I-P units, maximum elevation is considered to have a variation of ±0.1%. The effect on ITE thermal performance in this variation range is negligible and allows use of rounded values of3050 m. Operation above 3050 m requires consultation with IT supplier for each specific piece of equipment. kSee Appendix L of ASHRAE (2015a) for graphs showing how maximum and minimum dew-point limits restrict the stated relative humidity range for each class for both product operations and product power off. 1For the upper moisture limit, the limit is the minimum absolute humidity of dew point and relative humidity stated. For lower moisture limit, the limit is the maximum absolute humidity of dew point and relative humidity stated. MOperation above 3050 m requires consultation with IT supplier for each specific piece of equipment. Environmental Class Definitions for Air-Cooled Equipment. For any piece of datacom equipment to comply with a particular environmental class (ASHRAE 2015a), it must be able to reliably provide its full operational capabilities over the entire allowable environmental range, based on nonfailure conditions. The recom- mended and allowable ranges for each datacom equipment class are given in Table 1. The allowable environmental ranges for the four datacom equipment classes are illustrated in psychrometric format in Figure 6: · Class A1: Typically, a datacom room with tightly controlled en- vironmental parameters (dew point, temperature, relative humidity) and mission critical operations; types of products typ- ically designed for this environment are enterprise servers and storage products. · Class A2/A3/A4: Typically, an information technology space with some control of environmental parameters (dew point, tem- perature, relative humidity); types of products typically designed for this environment are volume servers, storage products, per- sonal computers, and workstations. Among these three classes, A2 has the narrowest temperature and moisture requirements. A4 has the widest environmental requirements. Chart Type: line 5 10 15 20 25 30 35 40 45 item_01 5% 10% 15% 20% 25% 30% 35% 40% 45% Fig. 6 Environmental Classes for Datacom Equipment Classes (ASHRAE 2015a) Inc. ASHRAE, 2019 user. single for Licensed | {}
06c7f3dd-3bae-4a86-844c-5d58184eff70 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 20.8 2019 ASHRAE Handbook-HVAC Applications (SI) Table 2 Liquid Cooled Datacom Facility Classes (Product Operation) ¦ Class ¦ Typical Infrastructure Design ¦ Typical Infrastructure Design ¦ Facility Supply Water Temperature, °C ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Class ¦ Main Cooling Equipment ¦ Supplemental Cooling Equipment ¦ Facility Supply Water Temperature, °C ¦ ¦ W1 ¦ Chiller/cooling tower ¦ Water-side economizer ¦ 2 to 17 ¦ ¦ W2 ¦ Chiller/cooling tower ¦ Water-side economizer ¦ 2 to 27 ¦ ¦ W3 ¦ Cooling tower ¦ Chiller ¦ 2 to 32 ¦ ¦ W4 ¦ Water-sideeconomizer (with dry-cooler or cooling tower) ¦ N/A ¦ 2 to 45 ¦ ¦ W5 ¦ Building heating system ¦ Cooling tower ¦ >45 ¦ Source: ASHRAE (2013). · Class B: Typically, an office, home, or transportable environment with minimal control of environmental parameters (temperature only); types of products typically designed for this environment are personal computers, workstations, laptops, and printers. · Class C: Typically, a point-of-sale or light industrial or factory environment with weather protection, sufficient winter heating and ventilation; types of products typically designed for this envi- ronment are point-of-sale equipment, ruggedized controllers, or ruggedized computers and personal digital assistants (PDAs). Dry-bulb temperature must be derated based on altitude for all classes. See ASHRAE (2015a) for more information on derating methodology. The latest guidelines were developed with a focus on providing as much information as possible, so that datacom facility operators can maximize energy efficiency without sacrificing the reliability required by their businesses. This assumes that the designs enable them to take advantage of reduced energy operation. Environmental Guidelines for Liquid-Cooled Equipment For any piece of datacom equipment to comply with a particular environmental class, it must be able to reliably provide its full oper- ational capabilities over the entire classification temperature range based on non-failure conditions. · Class W 1/W2: Typically a data center that is traditionally cooled using chillers and a cooling tower, but with an optional water-side economizer to improve energy efficiency, depending on the facil- ity's location. · Class W3: For most locations, these data centers may be operated without chillers, although some locations require chillers. · Class W4: To take advantage of energy efficiency and reduce cap- ital expense, these data centers are operated without chillers. · Class W5: In these data centers, the temperature of water exiting the IT equipment is high enough for reuse to heat local buildings, thereby increasing energy efficiency, reducing capital expense with chiller-free operation, and making use of waste energy. For datacom equipment that meets the higher supply temperatures as referenced by the ASHRAE classes in Table 2, enhanced thermal designs are required to keep liquid-cooled components within the desired temperature limits. Generally, the higher the supply water tem- perature, the lower the cost of the datacom facility cooling solution. For classes W1 and W2, the datacom equipment should accommo- date facility water supply temperatures that may be set by a campus- wide operational requirement. In these cases, condensation preven- tion is a must. Availability of datacom equipment rated for classes W3 to W5 is limited. It is anticipated that future designs in these classes may involve trade-offs between IT cost and performance. However, these classes allow lower-cost data center infrastructure in some loca- Table 3 Workload Types ¦ Workload Type ¦ Definition/Examples ¦ ¦ --- ¦ --- ¦ ¦ Scientific ¦ Includes biological sciences, geosciences, weather forecasting, engineering, simulation, design, defense, security, and training of deep machine learning appli- cations (versus run-time) ¦ ¦ Analytics ¦ Discrete data warehousing, data analysis, big data ana- lytics, and run-time deep machine learning applica- tions ¦ ¦ Business processing ¦ Enterprise-wide line of business applications that manage transactional, operational, and customer databases ¦ ¦ Cloud/Internetportal data center (IPDC) ¦ Wikis, portals, social media, video-sharing websites, search engines, and online auction websites ¦ ¦ Visualization and audio ¦ Data center visualization applications including video processing, remote visualization, and audio process- ing ¦ ¦ Communications/ telco ¦ Wired and wireless networking applications: applica- tion, control, packet, and signal processing ¦ ¦ Storage ¦ Dedicated storage infrastructure and services includ- ing back-up, tiering, and deduplication ¦ Source: ASHRAE (2008). Facility water flow rate requirements and pressure drop values of the datacom equipment vary. Manufacturers typically provide configuration-specific flow rate and pressure differential require- ments that are based on a given facility water supply temperature and rack heat dissipation to the water. Conformance with the water quality requirements for each cooling solution is important to long-term reliability. Datacom Equipment Nameplate Ratings and Manufacturers' Heat Release A power supply nameplate rating indicates the maximum power draw for the datacom equipment': s safety and regulatory approval. A nameplate rating does not represent actual power draw during usage and should not be used as a measurement of datacom equipment heat release. Manufacturers that follow ASHRAE guidelines utilize a template for each product that tabulates heat release based on configuration and use. In addition, most major datacom equipment manufacturers have online tools that can provide even more specific and detailed heat release and airflow information. Obtaining realistic heat release and airflow information is critical to the datacom facility and data- com equipment communities for use in datacom facility planning and designs that are both ample and energy efficient. Power Trends Datacom equipment manufacturers compete to create equipment that balances power and performance based on the markets and workloads they are targeting. Datacom equipment is no longer one size and one configuration fits all. More IT departments are shifting to purpose-built servers in order to meet customers' specific busi- ness needs. These purpose-built servers include specific features and components sized to meet a customer's workload requirements. This requires facility power projections to comprehend the software workload being deployed. ASHRAE (2018) captures these power trends by select workload (Table 3) for typical and maximum equip- ment configurations. A workload-based methodology provides a much more accurate estimate of actual power consumption in a modern data center, com- pared to using the maximum power for a given server family from a datacom hardware provider. An example of this trend methodology is shown in Figure 7 (for a 2U 2-socket [i.e., two central processing units] server configuration). Inc. ASHRAE, 2019 user. single for Licensed | {}
4f2ce3e8-1935-4f71-bdf2-0018b5fda932 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Data Centers and Telecommunication Facilities 20.9 Chart Type: line 2008 2010 2012 2014 2016 2018 2020 2022 2024 2026 item_01 32000 25000 23000 24000 25000 26000 27000 28000 30000 31000 Fig. 7 ASHRAE Projected Power Trends for 2U 2-Datacom Hardware by Workload Type (ASHRAE 2018) An important addition to the 2018 edition of ASHRAE's IT Equipment Power Trends was the introduction of the power com- pound annual growth rate (CAGR) for the years 2016 to 2025. The CAGR allows the measured power of a server running a business's specific application(s) to be used to project the future power for a similar workload demand. The most striking growth rates (Figure 8) occur in the scientific (4.6%) and analytics (5.9%) workloads at maximum expected configurations. These higher growth rates can be attributed to higher-power CPUs, maximizing the number of components, and the potential use of graphical processing units (GPUs) or another application-specific processor technology. When appropriately applied, knowledge of datacom equipment power trends can be a powerful tool in considering what future loads might be in a facility or space. Future load is a critical component in the planning, design, construction, and operation of facilities to avoid ineffective expenditures, premature obsolescence, stranded cost or assets, energy waste, etc. Refer to ASHRAE (2018) for details on how the trends were cre- ated, along with how to apply them. 2.4 DATACOM EQUIPMENT COMPONENTS Thermal Design Overview The goal of a good datacom facility cooling design is to match cooling capacity to actual heat load. This requires a correct and real- istic assessment of the heat release of the projected datacom equip- ment. Even when actual datacom equipment is known, this can be challenging, and is often done incorrectly. A basic understanding of datacom equipment thermal design is therefore valuable, to comprehend how the datacom equipment interacts with the data center and vice versa. The thermal design must ensure that the temperatures of all datacom equipment components (e.g., processors, memory, storage, I/O, power supplies) are maintained between the high and low limits oftheir specifications. Datacom equipment components have functional, reliability, and damage temperature specifica- ![image](/image/placeholder) 5.0% Analytics Storage Scientific 4.7% Cloud/IPDC Audio 4.5% 4.1% & 4.0% 3.5% Processing 3.0% 2.9% CAGR 2.5% Business 2.0% 2.0% Visualization 2.0% 1.8% 1.8% Communications/Telco 1.6% ID 1.5% 1.0% 2S ☆ 2S 2S 1.0% 1.0% x GPU 0.5% SL 2022 2022 20 4014 $8.08 1/2width 25 2U1S 20-22 4U2S 6U2S 2U15 2012 or 1U2S 45 23 IU2S 1/2width 2U 1/2width 10 2 2n 01 2U2S IU 0.0% Fig. 8 ASHRAE Power Compound Annual Growth Rate for Datacom Hardware by Workload Type and Size (ASHRAE 2018) tions. Maximum functional temperature limits for silicon compo- nents are generally in the 85 to 105°C range. The thermal management system (Figure 9) in the datacom equipment must take the appropriate actions to ensure compliance with these specifications. This ensures data integrity and maximizes equipment service life. A well-designed thermal management implementation balances component temperatures, datacom equipment performance, humidity, and acoustics, to achieve reliable equipment performance with minimal power consumption. Air-Cooled Datacom Equipment Components Air-cooled solutions are currently the most common approach for datacom equipment. The information described here is applica- ble to most mainstream, air-cooled volume servers; however, the principles apply to most types of datacom equipment. Inc. ASHRAE, 2019 user. single for Licensed | {}
93514bb6-2466-448c-8d49-28a8960a7cb3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 20.10 2019 ASHRAE Handbook-HVAC Applications (SI) ![image](/image/placeholder) Damage Shutdown Temperature Functional Performance and Limit Limit Power Management Component Reliability Optimize Cooling Limit and Performance Fig. 9 System Thermal Management (ASHRAE 2016a) Self Heating Component System Ambient TSA Air Heating TComponent = Self heating + Air heating + System ambient Fig. 10 Example Component in System and Rack (ASHRAE 2016a) Typical datacom equipment relies on variable-speed, forced- convection cooling to maintain the required temperatures. Compo- nent temperature is driven by one of three factors in an air-cooled system (Figure 10): · System ambient, or inlet temperature to the datacom equipment · Air heating, or increase in air temperature caused by upstream heat sources among the datacom equipment · Self heating, or increase in component temperature above local ambient caused by heat dissipated by the component itself; driven by component packaging, power dissipation, and thermal solution (e.g., heat sink) Datacom equipment manufacturers develop component- and equipment-level cooling solutions that balance cost, performance, and energy consumption, including trade-offs between air movers and heat sink designs. Cooling performance, power consumption, acoustic signature, fan reliability, and redundancy features are also important characteristics that must factor into the overall solution. Fan or cooling zones are often used to precisely adjust specific fans to the needs of the components most coupled with those fans. Cooling zones can be proximity based or physically separated. By using a fan zone approach, total fan power and acoustic output can be minimized. Fans in a nonstressed zone can run at lower speeds than those in a more highly stressed zone. Power and Thermal and Moisture Management Thermal control enables optimization of datacom equipment system performance as a function of usage or workload, configura- tion, cooling capability, and environment. Underlying this optimi- zation is the use of fan speed control and power management operating in parallel. Optimization for differential air temperature T through the datacom equipment is generally not a significant design consideration because of the more critical requirement of ensuring that functional limits are maintained. Components and their specifications are the primary drivers in a server' s thermal design (e.g., heat sink, fan selection, airflow man- agement). Power management features enable all components to stay within temperature limits while minimizing overall power con- sumption during periods of low activity. Highly advanced control algorithms vary the datacom equipment fan speeds and airflows, and tune the fan speeds based on the data- com equipment's usage model. Multiple algorithms can be used simultaneously, with the final fan speeds determined by comparing the results of these algorithms. Sensors (and proxy sensors) create the data necessary to trigger power management, and are the basis of a cohesive thermal man- agement implementation. As important as it is to control temperature within a data center to maintain high reliability, it is equally important to control mois- ture content. If both moisture and temperature are properly con- trolled, the result will be more reliable long-term operation, plus significant energy savings in the operation of the data center. The effects of improper moisture control on a data center opera- tion are twofold: · High relative humidity has been shown to affect failure rates of electronic components. Examples include conductive anodic fail- ures, hygroscopic dust failures, tape media errors, and excessive wear and corrosion. The recommended upper moisture limit is set to limit these effects. · Low relative humidity has been historically considered a factor in electronic device susceptibility to damage by electrostatic dis- charge (ESD). However, new ASHRAE research (Pommerenke and Swenson 2014) suggests that susceptibility to low relative humidity is of far less concern than once thought. Based on Pommerenke and Swenson 's (2014) results, the recom- mended moisture limits have been greatly expanded in the fourth edition of the Thermal Guidelines for Data Processing Environ- ments (ASHRAE 2015a). The recommended lower moisture limit has been significantly reduced, as shown in Table 1 and Figure 6 for the ASHRAE environmental classes. Note that the recommended upper and lower moisture limits are represented by dew point (dp) limits rather than relative humidity. Although static concerns are actually related to relative humidity, dew point is used because it is fairly constant throughout the data center, whereas relative humidity varies widely. Because dew point can be easily monitored and con- sistently controlled, best practice is to monitor moisture content in a data center using dew point rather than relative humidity. Liquid-Cooled Datacom Equipment Components With increasingly dense datacom equipment packaging, some components may require liquid cooling to maintain the environmental specifications dictated by the manufacturer. Liquids considered for cooling electronic equipment are dielec- tric, engineered fluids, water, oils, or refrigerants. Heat transfer from the liquid-cooled datacom equipment or components to the datacom facility generally takes place through a liquid-to-liquid heat exchanger. Some liquid-cooling solutions include immersion ofthe datacom equipment components directly in a dielectric fluid, in either single- or two-phase applications. Dielectric fluids include mineral oil and fluoroketones. Inc. ASHRAE, 2019 user. single for Licensed | {}
96448e76-0963-4e00-a979-04120ee52d61 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Data Centers and Telecommunication Facilities 20.11 3. DATACOM FACILITIES 3.1 GENERAL CONSIDERATIONS Spatial and Envelope Considerations A datacom facility can be a dedicated building, or be part of a general purpose building that houses other business functions or tenants. Regardless of the type of building in which it is housed, or its location within a building structure, a datacom facility is comprised of a number of spaces having different but interrelated functions (see Figure 1). The main computing area is identified by different names: com- puter room, machine room, raised floor area, or white space. This chapter uses the term datacom room to differentiate it from the other areas that support it, and which comprise the complete datacom facility. Determining the appropriate size of a datacom room is more challenging than it has ever been. There are three major reasons: the ever-increasing demand for computing services; the consolidation, virtualization, and increasing density of datacom equipment; and the transition of many computing services to the cloud or to leased colocation facilities. It is all too common to underestimate the amount of electrical/ mechanical space required to support a datacom facility. The need for reliability in these critical facilities dictates a requirement for adequate maintenance space. Overcrowding, even if minimum legal or manufacturer-dictated service clearances are maintained, can lead to inadvertent interruption of one system while servicing another. A rule of thumb, to be used as a starting point only, is to base minimum electrical/mechanical support space requirements on a percentage of the datacom room area: · At least 50% for non-redundant facilities · From 75 to 100% for N + 1 redundant facilities (see the section on Redundancy, Reliability, and Concurrent Maintainability for defi- nitions of N + 1 and 2N) · From 100 to 150% for 2N redundant facilities Every increase in reliability requirements also increases the need for more redundant pieces of equipment, which in turn requires yet more support space. Further, highly redundant facilities require physical compartmentalization of duplicate or parallel systems by fire-rated walls, further increasing support space requirements. The structure enclosing a datacom room should provide good thermal separation from the surrounding areas, whether those are exterior or interior spaces. The primary concern with the overhead structure, regardless ofits construction or intended use, is that it not be a source of particulate contamination or water leakage. The overhead structure must be cleanly finished and sealed to avoid concrete or insulation flake-off. If it is a roof structure, take extra precautions to preclude leakage. In highly critical spaces, a double roof structure is often used for insurance. Gaps and joints should be caulked. Suspended ceiling tiles must be either metal pan or plastic encap- sulated on both sides to prevent flake-off. This is particularly im- portant when the above-ceiling plenum is used to convey return air. Cut edges must be sealed with spray paint or similar. Any suspen- sion rods that penetrate the tiles should also be sealed at the pene- trations. Metals used above a return air plenum ceiling should be either hot-dip galvanized or of a type that will not grow zinc whis- kers. Walls surrounding a datacom room should be well insulated to avoid both cooling loss and heat infiltration. All cracks should be sealed, which is mandatory if the room is also protected by a gas- based fire protection system. Although most datacom equipment can accept a broad range of allowable humidity levels, consider installing vapor barriers for datacom spaces. Avoiding condensation anywhere in the room is very important. Windows should generally be avoided in a datacom room, but if they exist or are somehow necessary, they should be double-glazed and sealed. If covering the windows is allowed, but replacement is possible from the inside only, it will be necessary to make the COV- erings removable and to avoid blocking access with large pieces of mechanical/electrical equipment. Datacom Rooms Although raised access floors are still used in many datacom rooms, they are no longer a standard requirement. Itis not only pos- sible, but now relatively common, to put the entire power, cooling, and network infrastructure overhead, particularly when close- coupled cooling is used. In these designs, the raised floor is not nec- essary to convey air. However, with the amount of piping often used to service in-row, rear-door, and direct water cooling, raised floors are often used anyway to avoid concerns about overhead water, as well as to min- imize congestion above cabinets. When power, cable tray, and light- ing are all run overhead, the vertical space can become congested and difficult to coordinate. Three-dimensional modeling of the space is highly recommended when overhead infrastructure is used, to avoid both installation conflicts and long-term operational diffi- culties. There are several advantages and disadvantages to using raised access floors, regardless of their purpose. Once it is determined that a raised access floor will be used, several factors should be consid- ered in its selection and design. The most obvious advantages of raised access floors are to pro- vide a space for permanent infrastructure such as power, piping, and cabling, but raised floors have also been historically used to convey cooling air through the plenum space. For slab variations too large to be leveled with patching, and unrealistic for self-leveling cement, they can also provide a level floor. However, a raised access floor adds total mass to the structure. It must also be maintained, which includes releveling every few years, particularly if technicians do not take care in replacing tiles where they were removed, or open too many tiles in a row and destabilize the floor. The plenum space can also become a tangle of wire and cable if care is not used in installing new cable and removing old. If the floor is used to convey air, masses of unmanaged cable can reduce or totally block airflow. If cables are located in a raised floor plenum that is also used to convey cooling air, best practice is to run cables parallel to airflow, and to provide overhead cable pathways for ad hoc cable installation. It is even better not to locate cables in an air-plenum floor space at all. The height of a raised access floor is determined by its purpose. Ifit is used to convey cooling air, it must be high enough to deliver the required air quantity while maintaining the necessary static pres- sure as evenly as possible across the floor area. Computational fluid dynamics (CFD) modeling is generally recommended to confirm air flow patterns and adjust cooling designs to maximize cooling effec- tiveness, particularly under failure-mode scenarios where redundant cooling systems are used. Further information on CFD modeling is provided in the section on Computational Fluid Dynamic (CFD) Analysis. Piping, power systems, or cable tray that will also occupy the space must be taken into consideration in determining the floor plenum height and its effect on air flow. It is generally accepted today that a raised access floor used to convey cooling air needs to be at least 600 to 760 mm high to be effective, and that even higher is better. Inc. ASHRAE, 2019 user. single for Licensed | {}
9b55009d-b5ca-4fc4-b6a6-bc437c6c8906 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 20.12 After height, the biggest consideration is floor structural strength. Raised floors for datacom rooms should use bolted string- er substructures to increase load capacity and to make it easy to re- move and replace tiles without destabilizing the floor. Newer computing equipment cabinets are usually rated for 1100 to 1360 kg, which is significantly higher than most legacy cabinets. Even if they are not full of the heaviest available equipment, floor loading must be planned as if they will be to address potential max- imum loading in the future. However, cabinets with these load ratings also tend to be larger than legacy 600 by 600 mm cabinets, so the load is spread over more than one floor tile. It is not unrealistic to specify raised-floor sys- tems designed for 700 kPa or 1360 kg rated tile capacity. Any abnor- mally heavy equipment can be supported with supplemental floor pedestals under the tiles, so long as the slab structural strength is sufficient for both the total and point loads. In selecting floor strengths, it is particularly important to examine the rolling load characteristics along with the static struc- tural ratings, because equipment must often be moved into position on small integral wheels. The rolling load tests are generally per- formed for 10 passes and 10 000 passes with mass on test wheels of particular sizes in accordance with testing methods established by the Ceilings & Interior Systems Construction Association (CISCA) (CISCA 2007). However, not all tests are performed with the same wheel sizes, and the results can be misleading. It is always safest to put thick hardboard or plywood over the floor when moving particularly heavy loads. This is especially important when rolling equipment through cold aisles with perfo- rated airflow tiles, many of which do not have a rolling load speci- fication at all and are easily deformed. The most common surface material for raised access floor panels is high-pressure laminate (HPL). This material holds up well to heavy rolling loads without deforming or cracking, has good static dissipative characteristics when properly bonded to a grounded sur- face, is available in light colors to maximize lighting effectiveness, and is easy to maintain with damp mopping. Heavy scrubbing, buffing, or waxing should never occur in a datacom room. This precludes the use of vinyl composite tile (VCT), pure vinyl tile (which can also be easily deformed under rolling loads), or linoleum (which is also too easily damaged). Car- peting, of course, should never be used in a datacom room, even if itis antistatic, because it both accumulates and generates particulate contaminants. (Note: it is generally accepted that the ground resis- tance of an installed raised-floor panel, when properly connected to a robust grounding system, should be in the range of 104 to 106 to minimize any potential for static generation.) One of the most challenging decisions in selecting materials for air plenum raised access floors is the airflow panels. A range of types is now available, including legacy perforated tiles (25% open), grate- style cast aluminum tiles (56 to 63% open), and tiles incorporating directional vanes, air boost fans, and automatic air flow control. (See further discussion of airflow tiles in the section on Underfloor Air Delivery). All air plenum raised floors leak air, and because cool air is expensive to produce and requires considerable fan energy to dis- tribute through the plenum, this wastes energy. A good-quality raised-floor installation should leak no more than 2% air. For datacom rooms designed without a raised access floor, the primary concern is that all power, cooling, and network infrastruc- ture must be routed overhead. Depending mainly on the cooling method used, this can create a congested overhead space that re- quires careful design coordination and exacting installation. As not- ed previously, 3D modeling techniques are highly recommended when designing complex overhead systems. It should also be recog- nized that the cost of overhead infrastructure, particularly if exten- 2019 ASHRAE Handbook-HVAC Applications (SI) sive ductwork is necessary, can be very similar to the cost of a raised access floor. Support and Ancillary Spaces Space must be allocated within a datacom facility for storing components and material, support equipment, and operating and servicing the datacom equipment. Some ancillary spaces may re- quire environmental conditions comparable to those of the datacom equipment, whereas others may have less stringent requirements. Continuous operation of some support spaces is often vital to the fa- cility's proper functioning. Electrical power distribution equipment can typically tolerate more variation and a wider range of temperature and humidity con- ditions than datacom equipment. Equipment in this category in- cludes incoming service/distribution switchgear, switchboards, automatic transfer switches, panel boards, transformers, and stand- by generators. Manufacturers' data should be checked to determine the amount ofheat release and design conditions for satisfactory op- eration. Further information and guidance can be found in IEEE Standards 446 and 1100. Uninterruptible power supplies (UPSs) come in various config- urations, but most use batteries as the energy storage medium. They are usually configured to provide redundancy for the central power buses, and typically operate continuously at less than full-load capacity. They must be air conditioned with sufficient redundancy and diversity to provide an operable system throughout an emer- gency or accident. UPS power monitoring and conditioning (rectifier and inverter) equipment is usually the primary source of heat release. This equip- ment usually has self-contained cooling fans that draw intake air from floor level or the equipment face, and discharge heated air at the top of the equipment. Air-distribution system design should take into account the position of the UPS air intakes and discharges. Installation of secondary battery plants as a temporary back-up power source should be in accordance with IEEE Standard 1187 and NFPA Standard 70. Refer to other applicable standards, in addi- tion to a design review with the local code official. Other relevant sources of guidance are NFPA Standards 70E and 76. Several types of batteries are used with UPS systems. Flooded lead-acid (wet cells) are generally considered the longest lasting, but also present the highest initial cost. They require special rooms with, among other things, containment for possible acid spills, del- uge shower and eye wash stations, as well as hydrogen gas detection and exhaust fans (IEEE Standard 484). It is important to locate the battery room close to the UPS room to minimize loop current losses in the large DC conductors. More commonly used today are valve- regulated lead-acid (VRLA) batteries, also known as sealed cells or maintenance free. These can be colocated with the UPS system, which can be in the datacom room (IEEE Standard 1187). However, if the ambient temperature in the datacom room is not appropriate for the batteries, battery life may be adversely affected. VRLA bat- teries are available in different qualities, but those usually supplied with a UPS system may have a service life of only three to five years before replacement is required, depending on usage conditions. The newest battery used with UPS systems is the lithium-ion (Li-ion). There is still very limited history with these batteries in this type of service, but they are promoted as having significantly longer service lives than VRLA, lower mass, and less stringent operating conditions. However, probably due to the negative public- ity associated with cellphone and other small-device battery explo- sions, local codes may preclude their use, even though the chemistries, case constructions, and reliability testing of Li-ion bat- teries intended for commercial use are all very different than for the ultra-compact batteries that have exhibited problems. Temperature in a battery area is crucial to the life expectancy and operation of the batteries. The optimum space temperature for Inc. ASHRAE, 2019 user. single for Licensed | {}
0d571492-9c91-48e5-bbbf-df6dbc0fbfc8 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Data Centers and Telecommunication Facilities 20.13 lead-calcium batteries is 25°C. Per IEEE Standard 484, ifhigher tem- peratures are maintained, it will reduce battery life; iflower tempera- tures are maintained, it may reduce the batteries' ability to hold a charge. Recommended ambient temperatures for other battery types should be verified with the battery manufacturers. Engine-driven generators used for primary or standby power typ- ically have air-cooled radiators and require large volumes of out- door air when running. Designs should ensure that engine exhaust air does not recirculate back to any building ventilation air intakes. Commonly, up to 72 h of fuel oil storage is required, so fuel oil stor- age tanks and distribution systems need to be integrated into the overall facility design and planning. The governing codes often mandate specific requirements for containment, location of fuel oil storage, fire resistance ratings, etc. However, as has been unfortu- nately demonstrated in several weather disasters, local codes may impose requirements that can negate the benefits of generators unless all potential conditions are taken into account in the designs. Fuel tanks are heavy when full, but will start to float in a flooded basement as fuel is used, breaking the pipes. Both fill and pressure relief pipes must be located high enough above ground to remain both accessible and impervious to flood waters. Generators them- selves must also be carefully located and protected from potential problems. Other Systems and Considerations Fire Protection. Datacom fire protection involves a combina- tion of strategies starting with prevention and continuing through detection, suppression, and response to a fire event. The National Fire Protection Association (NFPA) has several standards addressing design, installation, maintenance, and operation of fire protection systems in datacom facilities. Worldwide, additional fire protection standards may apply as well; consult local governments. Major NFPA standards include the following: · Standard 75, for fire protection of information technology · Standard 76, for fire protection of telecommunication facilities · Standard 70, the National Electrical CodeⓇ (NEC), for electrical system installation · Standard 72, the National Fire Alarm Code�. for detection systems , · Standard 13 for sprinkler suppression systems · Standard 2001 for gaseous extinguishing systems · Standard 750 for mist systems · Standard 25 for maintenance of fire protection systems NFPA Standards 75 and 76 offer both prescriptive and performance-based approaches. Most designers defer to the pre- scriptive path, but a growing number of firms provide performance- based designs. These offer more flexibility, and can be tailored to a company's specific risk and business models. As another alterna- tive, some companies apply provisions from both standards, and often exceed one or more portions of either standard based on their own risk assessments or experiences. There are several options for providing fire suppression in data- com rooms. Many older (and even some newer) datacom facilities use a code exemption to suppression. More commonly, however, datacom facilities are equipped with either a sprinkler or gaseous suppression system for a combination of life, structure, asset, and service protection. The conventional wisdom, invoked by many code authorities, is that gas protects equipment but sprinklers pro- tect people and structures. One thing to be aware of with inert gas fire suppression systems is that, in some cases, the discharges can cause temporary or permanent failures to hard disk drives with rotating storage media due to extreme acoustic levels and the result- ing acoustically driven vibration. This can usually be mitigated with the proper selection of gas discharge heads, although this may also increase the time for a discharge to extinguish a fire. Air containment, either hot aisle or cool aisle, has become a common method of improving cooling performance and reducing energy usage. However, when containment systems are retrofit or de- signed into a new facility, effects on the required detection, suppres- sion, release system, materials of construction, and prevention of fire must be considered. These important considerations are addressed in detail in the NFPA standards. The added obstructions often necessi- tate modifications to the suppression systems (sprinklers or gaseous agent nozzles) to ensure proper suppression release and dispersion. An alternative to suppression system changes can sometimes be par- tial containment, which has been shown to be as much as 80% as ef- fective in improving air control, but does not block existing sprinkler or gas discharge heads. (See the section on Containment.) Water Concerns. Water damage is always a concern in a datacom facility. Itis best to locate the room above grade if possible, but this is not always practical. There are other sources of water leakage as well: designs must consider the possibility ofleaks from overhead. Datacom rooms and supporting electrical equipment should not be located below bath- rooms, pantries, laboratories, or the like. If unavoidable, the space above should have waterproof membrane floors. Liquid piping should also be routed around the datacom room, but if this is not possible, should be provided with drip pans and leak detectors. Leak detectors should also be provided anywhere water can infiltrate, particularly if it could affect electrical infrastructure. A common problem in buildings not specifically designed for high-availability datacom facilities is primary power switchgear and bus duct termi- nations in the lowest level of the building, where they are subject to flooding. These conditions cannot likely be changed in existing buildings, but should be avoided in purpose-built facilities. Acoustics. The rapid increase in density and power draw of data- com equipment has brought with it commensurate increases in re- quired cooling. Air cooling requires substantial volumes of air movement, which generates sound levels that can be problematic for worker health and might require a hearing protection plan. In- creased sound pressure levels required by increasing datacom fan speeds may also lead to reduced hard disk drive (HDD) perfor- mance, due to acoustically driven vibrations. Sound level exposure limits in datacom rooms and their associ- ated mechanical/electrical plant facilities are governed in the United States by the Occupational Safety and Health Administration (OSHA [Annual]) in Code of Federal Regulations (CFR) 1910.95. Similar regulations exist in other countries. Sound emissions from heat rejection equipment (cooling towers and/or air-cooled chillers) as well as emergency and/or prime power-generating equipment for the datacom facility's mechanical/ electrical plant must also be considered. Noise generated outside the building, typically from rooftop chillers and cooling towers, must also be mitigated so that sound levels in the building are conducive to conducting normal business activities. Community sound levels, mostly from exterior heat rejection and power-generating equipment, must typically comply with state, re- gional, or local noise codes, ordinances, guidelines, and/or regula- tions. Community sound level limits are typically cited at property lines and/or anywhere on the property of a potential complainant. Sound levels of exterior equipment during normal, emergency, and test operation should allow for relatively easy communication among service personnel, as well as auditory awareness of vehicle and general service activities in the area. A sound level at or below 70 dBA in service areas and equipment yards, with all equipment operating, is an ideal goal. Vibration. Vibration levels in datacom facilities must be consid- ered as well. The greatest vibration concern in datacom installations is usually roof-mounted support equipment, such as air handlers, cooling towers, chillers, and generators, although similar equipment mounted inside the building can also create vibration issues. See the Inc. ASHRAE, 2019 user. single for Licensed | {}
d57cb714-aca1-44bd-84d7-ecd37b8fa348 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 20.14 ASHRAE TC 9.9 datacom book series, especially ASHRAE (2008a), for additional information. Some datacom equipment, such as very high-density disk drives, can be sensitive to vibration. Even vibration induced within a server (e.g., by fans) can be an issue for disk drives at the higher airflow rates required to cool some components. Wherever there is concern, vibration specifications should be obtained from manufacturers, and the datacom facility floor's vibration dynamics studied to determine compliance with vibration limits. Many locations are considered seismic zones, requiring special bracing and safety restraints for much of the infrastructure. However, the critical nature of many datacom facility operations mandates consideration of special structural supports and restraints, even where seismic regulations are minimal or do not exist. As described in ASHRAE (2008a), it is important for both the owner and the designer to understand the potential hazards, including seismic, wind, etc., of the region where the facility is located. Clear operational criteria should be established and used in system designs. These may include recommendations for structural restraints and bracing beyond what is required by law. Local code requirements must be identified and understood, as well as the requirements set forth in ASCE Standard 7, which provides further information and direction. Lighting. In datacom rooms, lighting should usually be centered in the aisles, not over equipment cabinets or cable trays where much of the light energy would be wasted. Fixtures should also be sus- pended 2.44 to 2.75 m above the floor so as to deliver maximum illumination over the heads of technicians and into cabinets. Higher mountings may be necessary to clear other overhead infrastructure, but this disperses more light energy over the tops of cabinets and other obstructions. Although lighting is a small part of datacom room energy consumption, and LED has become the light of choice, prox- imity sensors should be still used to ensure they are not left on when there is no activity. The photometric curves of many architectural luminaires are in- appropriate for datacom facility lighting. Fixtures with wide hori- zontal dispersion patterns are needed. This requirement is very similar to the lighting of library book stacks, where the purpose is more to support the reading oftitles on the books than to provide for reading books in the aisles. An illumination level of 325 lx on the vertical surfaces of cabinets is generally sufficient. Lighting systems and lighting control in datacom rooms can be provided by several different methods. All systems require sensors, and automatic control devices are recommended. Low-voltage (0 to 10 V) or power over Ethernet (PoE) controls are a good application for LED lighting control in data centers. PoE lighting controls work well in data centers because the data racks are typically already in place and the power and control wiring is run through Ethernet cabling. However, ifa PoE lighting solution is chosen, larger racks, additional power supplies, and controls may be needed. Emergency lighting for PoE systems also should be considered. UL 924-listed battery packs are now available that can be added to any PoE lighting fixture to make it into an emergency fixture. This is an advantage over conventional lighting, which requires selected fixtures to be designated and provided as emergency luminaires. Whichever emergency system is decided on, it must meet local requirements for illumination and run time in the event of loss of normal power. PoE lighting and controls can offer flexibility, low initial instal- lation and operating costs, and allow customers to monitor lighting and energy usage with a centrally hosted system control. PoE sys- tems provide reliability, scalability, and flexibility to support easy modification or expansion within a datacom room. 2019 ASHRAE Handbook-HVAC Applications (SI) Redundancy, Reliability, and Concurrent Maintainability It is axiomatic that redundant systems should improve the reli- ability of a facility, but how much redundancy is justified is always a question. Redundancy decisions must consider business and oper- ational needs as well as economic justification. Unfortunately, re- dundancy alone does not guarantee increased reliability. Itis not uncommon for large investments to be made in duplicate power and cooling systems that have been configured or installed in ways that defeat or greatly compromise their purposes. Conse- quently, a careful analysis of all possible failure modes should be an integral part of the design phase of any datacom facility. The primary goal of redundancy should be to provide for con- current maintainability. This requires a design that allows any ele- ment in the power and cooling infrastructure to be shut down and removed from service for maintenance without compromising the computing systems that depend on that infrastructure. This level of redundancy is commonly known as N+1, meaning that every system has at least one extra component and pathway. Higher levels ofredundancy require some degree of duplicate sys- tems, such as two identical and fully load-sharing chiller plants with duplicate piping systems. This is known as 2N redundancy. An even more stringent design would have duplicate systems, but with addi- tional redundant components in each. Depending on how the addi- tional redundancy is configured, the systems may be known as 2N+1, in which an additional unit (e.g., a chiller module) is made available to either of the duplicate systems, or 2(N+1) in which both redundant systems each have their own redundant modules. Several methods have been developed to classify levels ofredundancy and their result- ing reliabilities and uptimes (e.g., ANSI/TIA Standard 942-B). It is standard practice to power datacom equipment from an unin- terruptable power supply (UPS). UPSs have two main purposes: to isolate the datacom equipment from power line disturbances; and to maintain ride-through power to the datacom equipment until back-up generators start, or long enough to accomplish an orderly shutdown. With today' s heat densities, datacom systems cannot be main- tained for very long on UPS alone. The usual maximum back-up time is 15 to 20 min, before thermal rise causes a shutdown of the datacom equipment and/or the UPS. High-performance computers may shut down in minutes or even seconds if cooling is interrupted. It is there- fore necessary to have a means of maintaining cooling for the most critical systems until either generators start, or systems can be shut down properly. It is generally impractical to run large cooling systems on UPSs. If this must be done, the cooling equipment's electrical characteris- tics make it prudent to use a separate UPS. Further, the substantial power draws and high in-rush currents on compressor start-up and cycling require large and expensive UPS systems. In most datacom rooms it is not necessary to maintain full cool- ing for an extended period. If cooling can be continued to the most critical computing systems, this should suffice until both generators and full cooling restart. If a chilled-water system and close-coupled liquid-based cooling have been selected, this can be relatively easy to accomplish. There may be sufficient residual water in header pipes to cool critical systems for several minutes. If not, additional water can be stored in tanks. Long battery life is of no value if the UPS it supports is without cooling. A UPS generates substantial heat under load, as do the bat- teries when they take full load after a power failure. Batteries also emit heat as they recharge once the generators start. This heat gen- eration should be considered when choosing the location for the UPS, which is often relegated to a location that is less desirable for use as personnel spaces. This is sometimes in an electrical or mechanical room that generates additional heat, in a corner of a parking garage, or even in a roof penthouse that is exposed to high Inc. ASHRAE, 2019 user. single for Licensed | {}
5c2f83a5-283e-4240-94d4-744c1e735fd7 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Data Centers and Telecommunication Facilities 20.15 sun loads. These kinds of locations can dramatically shorten the actual back-up duration of the UPS, particularly if the batteries are also exposed to continuous heat. The cooling system in the UPS room should have the same level of redundancy as the cooling for the datacom room. 3.2 AIR COOLING Air-Cooling System Configurations Datacom equipment rooms can be conditioned with a wide variety of systems, including packaged computer room air-condi- tioning units and central-station air-handling systems. Air-handling and refrigeration equipment may be located either inside or outside the datacom equipment rooms. The following system configurations are some of the most com- monly used solutions to providing sufficient cooling to air-cooled datacom equipment. Computer Room Air-Conditioning (CRAC) and Computer Room Air-Handling (CRAH) Units. Despite the development of a variety of newer cooling technologies, CRAC and CRAH units re- main the most common datacom cooling solutions. They are specif- ically designed for datacom equipment room applications and should be built and tested in accordance with the requirements of ASHRAE Standard 127. CRAHs are special-purpose chilled-water air handlers designed for datacom applications. CRACs are compressorized cooling sys- tems and are available in several configurations, including direct expansion (DX) air-cooled, DX water-cooled, and versions that include a water- or refrigerant-cooled economizer coil. Both CRAH and CRAC units are available in either downflow or upflow designs. Downflow units are used primarily for underfloor air delivery and have top air returns. Upflow units discharge air overhead, often into ducts, and can have either front or rear air returns. Whereas older CRAH/CRAC units use belt-driven forward-curved centrifugal supply fans (and are often constant volume), newer models tend to use plenum-style plug fans, which are direct drive and paired with electronically commutated motors and variable frequency drives (VFDs) for speed control. The limited static pressure available from these newer computer room units means they are not typically as suitable for ducted applications, so are generally located in or immediately adjacent to the datacom space. As a result, they often have limited flexibility for incorporating air-side economizer solu- tions. CRAC and CRAH units are usually located in the datacom equipment room, but may also be in mechanical galleries adjacent to the datacom room, or installed remotely and ducted to the condi- tioned space. Ducted designs require consideration of the relatively low-static-pressure designs of CRAC and CRAH units with plug- type fans. Ducted designs may require conventional forward-curved fans that can work against higher static pressures, but variable-speed motors can still be used to improve energy efficiency. If CRACs or CRAHs are used in datacom rooms without a raised floor, or in rooms with a raised floor that is not used for cooling, overhead air delivery is required, which means using upflow cool- ing units. The return air grills on these units are at the bottom, so cannot efficiently capture hot return air in an open space. When upflow cooling units are used, it is necessary to also use cold aisle containment to locate the cooling units in mechanical galleries sep- arated from the datacom equipment by a demising wall, or to use ducted rear returns to efficiently get hot return air back to the units and prevent them from re-entraining their own cool discharge air. With either placement, temperature and humidity sensors must be located to properly control air delivery in order to keep inlet air conditions to the datacom equipment within specified tolerances. Centralized Air-Handling Systems. Traditionally, many tele- communications central office facilities and datacom facilities with overhead air delivery used central-station air handlers. Larger, cen- tralized air handlers, typically either roof mounted or adjacent to the datacom space, have been gaining popularity as air-side econo- mizer-based solutions have become more common. These air han- dlers may include DX cooling coils, chilled-water coils, adiabatic cooling sections, and indirect economizer solutions (such as air/air heat exchangers). Larger air handlers may use a fan array consisting of multiple direct-drive plug fans. Control of v ariable-Speed Fans. There are several ways to con- trol fan speed. The most common are underfloor pressure, cool-aisle containment pressure, differential pressure, supply air temperature, and return air temperature. Air Distribution Traditionally, telecommunication spaces had no raised floor and used overhead ducted air delivery, whereas datacom facilities used raised-flooring systems as supply air plenums. Underfloor Air Delivery. The interstitial space under the raised floor creates a large-volume air plenum that, if properly configured, can deliver relatively uniform air pressures across the entire room area. However, because the floor plenum is also often used for piping, power and cable, there are many potential obstacles to air- flow that can be challenging to mitigate. Underfloor air delivery to cold aisles is provided and balanced using a range of airflow tiles, which are available in 25% open, 56 to 63% open, and fan boosted, and both dampered and undampered. Even distribution of air through the airflow panels is a function of the evenness ofthe static pressure below the floor. However, the pressures are altered by the existence of the airflow tiles. Therefore, though it may be tempting to use high-airflow tiles to ensure sufficient air delivery to all cabinets, quantity and location must be balanced with the available air volume and static pressure. As with any fluid, air will take the path of least resistance, so too many of these tiles in one area can result in air starvation for equipment in other areas. Like- wise, tiles with integrated air-booster fans may solve a spot cooling problem, but because fans will take the air they want, adjacent cabi- nets may receive less than they require, resulting in unintended addi- tional cooling problems. Tiles with variable dampers are available to enable adjustment of airflow to match the requirements in each part of the floor. However, the addition of a damper to any airflow tile results in reduced airflow and cooling capacity, even when the damper is 100% open. In short, air balance with underfloor systems can be challenging, and specifi- cations should be carefully examined when selecting from the wide range of air flow tiles now available. Leakage between the floor tile joints will reduce the expected airflow. Likewise, air will leak and be wasted through unsealed gaps at the raised-floor-to-wall or raised-floor-to-column junctions, and through any floor cutouts for cable or chilled-water lines from the raised-floor plenum that are not correctly sealed. A properly in- stalled and maintained floor should leak no more than 2% of the de- livered air. Overhead Air Delivery. Delivering air overhead requires ducts large enough to convey the air volume needed to cool the equip- ment in each aisle, at velocities and pressures that enable air flow to be easily adjusted and balanced in each aisle. To properly control airflow to match loads in an aisle, it is important that one duct runout serve only one cold aisle, even though planning where runouts should be to accommodate future cold aisles and rows ofIT cabinets may be challenging. Irrespective of planning difficulties, overhead air delivery may still provide more effective airflow man- agement than underfloor air delivery because overhead air volume can be tied to the measured temperatures in each aisle. This means the system can dynamically increase or decrease airflow to each cold aisle in response to measured conditions. Inc. ASHRAE, 2019 user. single for Licensed | {}
15f33d7c-be79-45ef-94ce-b0c3992bb527 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 20.16 2019 ASHRAE Handbook- -HVAC Applications (SI) ![image](/image/placeholder) ↓ RACK RACK RACK RACK RACK RACK CRAH CRAH CRAH HOT-AISLE CONTAINMENT COLD-AISLE CONTAINMENT RACK-BASED CONTAINMENT Fig. 11 Examples of Main Types of Containment As noted above, CRAH and CRAC units are not easily config- ured for higher-static-pressure systems or for systems with outdoor air economizers. It is, therefore, more common to use central station air-handling systems when designing for overhead air delivery. Effects of Air Mixing. Air mixing occurs in two ways: (1) when hot air discharged from computing equipment recirculates back to the air intakes, thereby increasing the inlet air temperature at the computing equipment; and (2) when cool supply air bypasses the computing equipment and mixes with hot discharge air, thereby lowering return air temperature. Reduced return air temperature de- creases the cooling capacity of the air-conditioner coils by decreasing the system T, which requires an increase in airflow to meet the load. If air paths through or between the datacom equip- ment racks exist, then some of the cool supply air will bypass the datacom equipment, and some of the discharge air will recirculate to the front equipment intakes. Use blanking or filler panels to minimize air mixing. Ifthe supply air temperature has been set toward the upper limits of the ASHRAE recommended envelope, hot-air recirculation may result in equipment seeing inlet air that is warmer than the design temperature. Avoiding or minimizing air mixing requires separating the supply air from the return air and the datacom equipment intake air from the datacom equipment discharge air. The more complete the separation, the more effective and energy efficient the cooling system will be. Hot Aisle/Cold Aisle. The first step in avoiding air mixing is to arrange cabinets in hot aisle/cold aisle configuration. This means that racks and cabinets are installed facing back-to-back and front- to-front. This arrangement keeps the hot-air discharge from one row of cabinets from directly entering the intakes of cabinets in the next row. This, of course, assumes that all datacom hardware has been designed with industry-standard front-to-rear airflow. Equipment that uses a nonconventional airflow pattern must be dealt with using special racks, cabinets, and air deflectors, as discussed in the section on Datacom Equipment Racks. Containment. Containment further segregates the supply and return airflow paths by preventing mixing at the top of the equipment racks and at the ends of equipment rows. There are several types of containment, including hot-aisle containment (HAC) and cold-aisle containment (CAC), either of which can be full or partial; as well as rack-based containment, commonly associated with active or pas- sive chimneys. These main types of containment are illustrated in Figure 11. Computational Fluid Dynamic (CFD) Analysis One of the main challenges to maintaining the high availability required for datacom rooms is delivering cooling effectively and efficiently to all the equipment, wherever it is in the room. Com- plexities created by widely variable heat densities, plus the disrup- tions to airflow patterns created mainly by underfloor obstacles, make it difficult to envision air movement in the space. CFD simulations are a useful tool for predicting actual cooling performance. This requires building a 3D computer-generated model of the datacom room. Of most practical importance is the way in which the user defines the space (and the equipment in it): a model is only as good as the input data, regardless of the program ' s sophis- tication. A CFD model needs to represent the physical room geom- etry, and anything that might add or stimulate airflow or heat transfer, such as fans and vents. It must also include items that impede airflow, such as underfloor pipes and cables, and interactions with the sur- rounding environment, such as columns and oddly shaped walls and cabinets (the boundary conditions). Several simulations are commonly completed for datacom rooms. These may be based either on assumed datacom equipment layouts and projected heat densities, or on actual datacom equip- ment installations, and often include · Testing different cooling strategies · Comparing different arrangements and positions of cooling, power, and computing hardware · Optimizing cooling paths, including raised-floor height, ceiling height, return air plenum size, duct sizes, and containment · Testing cooling effectiveness with part-load configurations and examining failure modes, particularly in redundant designs in- tended to maintain adequate cooling during maintenance and equipment failure conditions · Determining where the highest-heat-density datacom equipment is best located from a cooling perspective Although CFD is a powerful tool, it is also easy for it to be misapplied and misinterpreted. Data centers are complex, and infrastructure and equipment must be simplified for models to be practical. It is critical, therefore, that the modeler understands the key elements of the data center and the fundamentals of CFD mod- Inc. ASHRAE, 2019 user. single for Licensed | {}
0a39ea37-c099-48ad-891e-528f088f1787 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Data Centers and Telecommunication Facilities 20.17 eling for the application of CFD to be successful. Proper use of CFD can identify and help the designer avoid most major cooling problems before construction occurs, but expecting the model to be a 100% accurate representation of the finished installation is not realistic. In conceptual design of most enterprise facilities, the modeler will probably not know detailed information about the datacom equipment type or detailed configuration. Similarly, the precise locations and routings of cables and other physical infrastructure may not be known, and even the cooling system manufacturer or model may not yet have been selected. In such instances there is little point in putting excessive detail into the model, but at the same time the modeler must interpret the results accordingly: that is, understand that the predictions are limited to high-level system design decisions and recognize that performance will likely be a best-case solution because best practice has been assumed. Where real facilities are being modeled, the models need to be more representative of the actual installation. This normally means basing the model on a physical survey of the facility, infrastructure, and datacom equipment configuration. Even so, the real infrastruc- ture and equipment cannot be represented in ultimate detail. For example, a bundle of cables will be represented by an approximate obstruction or resistance to airflow rather than explicitly modeling each and every cable. To ensure that judgments are made appropriately and that the model is accurate, compare simulation results with measurements of airflow and temperature. This is generally regarded as a cali- brated model, because actual conditions can be measured and compared. Even this will have discrepancies from the reality, which will be difficult, if not impossible, to resolve, but at least they will be known. Then, and only then, should the model be used for sensitivity studies to upgrade the facility, troubleshoot problems, or make deployment decisions. Although CFD's primary focus for datacom facilities is deter- mining the effectiveness and efficiency of cooling delivery to the computing equipment, it can also be used to analyze such things as airflow around air-cooled chillers, generators, and other critical equipment. CFD is also a recommended component of The Green Grid's (www.thegreengrid.org) most recent performance assessment tool: the Performance Indicator (PI). The PI is an extension of the PUE metric (see the section on Energy Efficiency) and examines a com- posite of energy efficiency (PUE), thermal conformance, and thermal resistance. Each of these parameters can be optimized in different ways. The PI illustrates them in a spider diagram format as an aid to achieving an efficient and cost-effective balance among the variables. Linking the PI parameters to a calibrated CFD simulation gives a clearer picture of how cooling is performing in the room, and allows scientific analysis of which physical and operational changes will deliver the most effective improvements. 3.3 LIQUID COOLING Liquid-Cooling System Configurations Liquid-cooling equipment may be integrated with a facility-level cooling system in various ways, including the following. Modular Room-Based Systems. The most common liquid cooling requires that facility chilled water be delivered to a heat exchanger (often called a cooling distribution unit [CDU]) located in or adjacent to the datacom room. The CDU has piping that con- nects to the datacom equipment; this is called the technology cool- ing system (TCS). The TCS connections may be to a centralized heat exchanger at the datacom equipment rack or may connect with the datacom equipment itself (e.g., multiple connections per rack). An example of this configuration is shown in Figure 12. ![image](/image/placeholder) BUILDING DATACOM EQUIPMENT CENTER COOLING RACK ↓ ↓ ↓ ↓ ↓ FACILITIES WATER DISTRIBUTION SYSTEM (FWS) UNIT DIRECT DATACOM LOAD COOLING EQUIPMENT- TOWER COOLING CHILLER ↓ ↓ ↓ ↓ SYSTEM (DECS) CONDENSER WATER TECHNOLOGY-COOLING SYSTEM (CWS) SYSTEMS (TCS) Fig. 12 Typical Liquid Cooling Systems/Loops Within Datacom Facility (ASHRAE 2015a) The fluid in the technology cooling system may be chilled water, deionized water, refrigerant, or other liquids. The cooling distribu- tion unit typically also contains pumps, valves, temperature moni- toring and control, and operating software. Refrigerant-based systems have many of the same components as well as compressors and/or pumps and related control components. One of the most im- portant functions of the CDU, or whatever alternative distribution and control mechanism may be utilized, is to maintain coolant temperatures above the dew point. It can be easy to create conden- sation with liquid-cooled systems. It is important to understand that many liquid-cooled datacom equipment solutions are not entirely cooled by liquid. Often, the datacom room needs to support a hybrid of air cooling and liquid cooling. A potential advantage to these systems is cooling ride- through in the event of primary cooling system failure. The residual liquid in header pipes can often be sufficient to maintain critical sys- tem cooling until generators start, and full cooling can be restored with only the addition of small supplemental pumps on UPS back- up. Chilled water or ice storage can also be used to supplement the re- sidual capacity. Direct Component Liquid Cooling. This type of system delivers the cooling medium directly to the individual datacom equipment, and often straight to the components. These systems are typically used in high-performance computing (HPC) or supercomputing platforms and have limited applications for typical commercial installations. They require completely dedicated piping distribution installations, as well as specialized heat exchangers, and related components between the liquid cooling equipment and the facility climate control systems. Immersion Cooling. In this type of system, the datacom chassis are fully immersed in a liquid bath. The cooling medium completely surrounds the devices, and circulates through the datacom enclo- sures or individual chassis subsystems. The pumped fluid transfers the heat to a dedicated coolant-to-water heat exchanger, which is connected to the facility chilled-water loop. Because of the thermal mass of the liquid vat, these systems can often "ride-through" a cooling failure with little or no supplemental circulation. Piping and Distribution Systems Facility water distribution systems that serve datacom equipment should be designed to the same standards of quality, reliability, and flexibility as other datacom room support systems. This means that itis important to configure systems so they can be expanded or mod- ified as needed to accommodate changes in datacom equipment without needing extensive system shutdowns. Further, the effects on Inc. ASHRAE, 2019 user. single for Licensed | {}
4a23c02b-8269-46ca-8083-b9aa2799a42d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 20.18 2019 ASHRAE Handbook-HVAC Applications (SI) ![image](/image/placeholder) REDUNDANT RETURN REDUNDANT SUPPLY LOOP CONNECTIONS LOOP CONNECTIONS TO CHILLER PLANT FROM CHILLER PLANT SUPPLY LOOP HEADER RETURN LOOP · HEADER VALVED BRANCH CONNECTIONS TO DECENTRALIZED AIR/WATER- COOLED EQUIPMENT (TYPICAL) HEADER SECTIONAL VALVES (TYPICAL) RETURN LOOP HEADER SUPPLY LOOP HEADER VALVED MAINS FOR CROSS CONNECTION OR EXPANSION Fig. 13 Example of Chilled- Water Distribution Piping System the distribution system when valves must be serviced should be con- sidered. Figure 13 illustrates a looped chilled-water distribution system with sectional valves and multiple valved branch connections. The branches could serve air handlers or liquid-cooled datacom equip- ment. The valves allow modifications or repairs without a complete system shutdown. Additional piping concepts are detailed in ASHRAE (2015a). 3.4 WATER USAGE Water usage in datacom facilities has gained much attention in recent years. Although water usage does not contribute as much to the total cost of ownership (TCO) as energy efficiency does, water has become a very precious commodity in many areas, and there are several environmental regulations that restrict water usage by data- com facilities. Water Usage Effectiveness (WUETM) WUE is a site-based metric, developed and popularized by The Green Grid, to assess the water used on site for operation ofthe data center. It presents a comprehensive evaluation of water usage in a datacom facility, where it is affected by a range of factors such as location, IT load, quality of available water source, type and effi- ciency of cooling equipment, and humidification loads. The for- mula for calculating WUE is the annual water usage (in litres) consumed by the entire datacom facility, divided by the IT equip- ment energy usage (in kWh). Annual water usage WUE = IT equipment energy 3.5 ENERGY EFFICIENCY Energy efficiency is at the forefront of modern building design. Datacom rooms are large energy users, and are difficult to consis- tently operate at peak efficiency because of their dynamic nature. Because cooling typically accounts for the highest energy use (after the IT equipment itself), it is often a primary focus for energy- saving measures such as economization. Although previously excluded from energy code requirements, this was changed in the 2010 edition of ASHRAE Standard 90.1, with new datacom facili- ties required to have some means of economization. In response to industry concerns about potential economizer reli- ability issues, the challenges of installing economizers on existing high-rise buildings, and the prescriptive nature of Standard 90.1, the new ASHRAE Standard 90.4 -2016, Energy Standard for Data Cen- ters, was developed. Standard 90.4 is written to specifically address data center efficiency in a nonprescriptive manner, and to recognize the balance between energy efficiency and reliability that is critical to data center design. This standard is considered a "sister standard" to Standard 90. 1, a method of confirming data center energy effi- ciency in the design stage by using whatever best practices tech- niques best suit the aggregate needs of the project (e.g., space, location, climate, cooling approach, budget). Standard 90.4 uses new metrics for both mechanical and electrical efficiencies that were developed specifically to simplify conformance calculations in the design phase of a project, as well as to make it easy to demon- strate compliance to the AHJ. Standard 90.4 applies to data centers (called "computer rooms" in Standard 90.1) with IT design loads above 10 kW, power densities above 20 W/s, and mechanical and electrical systems dedicated to the data center. Power Usage Effectiveness (PUETM) PUE is an efficiency metric developed and popularized by The Green Grid. Since the concept was introduced (see, e.g., Rawson et al. [2007]), the metric has been revised to make it more understand- able and the methods and reporting of measurement numbers more reliable, culminating in the 2014 release of a joint TGG/ASHRAE TC 9.9 publication (ASHRAE 2014b). PUE measures how effectively an operating datacom facility delivers energy to the datacom equipment inside. The formula for calculating PUE is simply the energy consumed by the entire data- com facility (measured at the meter for the facility or room) divided by the energy consumed by the facility's datacom equipment. Total facility energy PUE = Datacom equipment energy It is important to understand that the PUE metric was developed as a means for individual operations to monitor and track their own energy efficiencies. It was never intended as a means of comparing the efficiencies of different data centers, because too many condi- tions, including climate zone, can affect the number. It is also important to understand that an enterprise can take steps to reduce its total energy consumption, yet achieve a worse PUE. Extensive consolidation and virtualization, for example, and the purchase of ENERGY STAR Ⓡ rated servers, could significantly lower the data- com equipment energy number in the denominator of the PUE equa- tion. However, unless a massive renovation ofthe power and cooling systems was also done, which would probably not be justifiable in most facilities, the energy consumption of those systems would not likely be reduced in the same proportion as the datacom loads. Although that would result in a larger PUE quotient, it should still be recognized as a very positive step, because total energy use has still been reduced. It should also be recognized that the PUE metric is impractical to use as a means of quantifying projected energy efficiency in the de- sign stage of a datacom facility. The number of calculations of elec- trical path efficiencies and losses, and the precision energy modeling that would be necessary to develop a realistic number would be overwhelming, and would still not result in a number likely to be realized when the facility is put into operation, poten- Inc. ASHRAE, 2019 user. single for Licensed | {}
66ee4903-c6d3-4848-b628-f2ff98b65177 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Data Centers and Telecommunication Facilities 20.19 tially misleading owners into expecting something unachievable. It is for these reasons that different metrics were developed for use in the design stage, as set forth in the ASHRAE Standard 90.4. Partial-Load Operation A datacom facility is dynamic in terms of electrical and mechan- ical loading. The design of a datacom facility cooling system, whether single plant or modular, must be based on the maximum an- ticipated datacom equipment load of the space. However in reality, this maximum load is rarely, and sometimes never, achieved. Even if the maximum design load is someday realized, the day- one load at move-in will be much lower than the ultimate design load in order to provide for long-term growth. Additionally, over the course of its lifetime (which may be 10 to 20 years or more), the datacom facility load constantly fluctuates. The load also changes density and location within the datacom space as systems are in- stalled in one location and decommissioned in another. These below-peak, fluctuating loads mean that the cooling plant operates in part-load conditions almost all ofthe time. It is therefore critical to ensure that the cooling plant selection has good part-load efficiency. Economizers Typically, the primary energy users in a datacom facility cooling system are refrigerant compressors. Economizers, which leverage favorable ambient conditions to provide cooling without using com- pressors, are commonly integrated into cooling systems to minimize annual compressor use. There are three main classifications of econ- omizers used on datacom facilities: dry, wet, and dual-mode. A dry economizer can provide economizer cooling whenever the ambient dry-bulb conditions are suitable. This type of economizer can operate to provide cooling for a portion of the year in most cli- mates. A wet economizer consumes water to provide economizer cooling, leveraging the ambient wet-bulb conditions. This type of economizer can typically operate all year to provide some or all of the cooling required. A hybrid economizer is able to operate either wet or dry, and can be designed to transition as the ambient conditions change. Hybrid economizers offer both the energy-saving benefits of a wet econo- mizer and the water-saving and freeze protection advantages of a dry economizer. This type of economizer can be designed to opti- mize either water or power consumption in the datacom facility. Water-Side Economizers. For systems that use a water or glycol loop to remove heat from a datacom space, a water-side economizer can be incorporated. These systems are typically designed as indi- rect fluid economizers to minimize coil fouling. In such cases, to ensure continuous flow and take advantage of the most hours of economization, the heat exchanger should be placed in series with the chiller. Condenser water can still be the primary source of cooling when ambient conditions allow. This arrangement provides a continuous flow of water through the system, and valve stroke time does not become a point of failure. Figure 14 shows a sche- matic diagram of a typical water-side economizer. Air-Side Economizers. For systems where the room airis the pri- mary transport medium of the heat load, an air-side economizer may be implemented. Air-side economizers for datacom facilities are sep- arated into two general categories: direct and indirect. Schematic diagrams of these two categories are shown in Figures 15 and 16. Direct air-side economizers (DASEs) introduce ambient air directly into the space so that it flows through the datacom equip- ment to remove the heat. Indirect air-side economizers (IASEs) use ambient air to remove heat from recirculated cooling air by air-to-air heat exchangers. Either solution may incorporate evaporative cooling to extend the number of economizer hours and, in some instances, reduce the ![image](/image/placeholder) CDU + COOLING HEAT DATACOM TOWER EXCHANGER EQUIPMENT WATER CHILLER Fig. 14 Schematic of Typical w ater-Side Economizer (ASHRAE 2009b) ![image](/image/placeholder) RELIEF AIR HEATED AIR SHUTOFF CONTROL DAMPERS HOT RETURN AIR DAMPERS RACK OUTDOOR FAN AIR RACK COLD AISLE SUPPLY PLENUM AIR ROUGHING FILTER AND HIGHER- COOLING COIL EFFICIENCY EVAPORATIVE PADS WITH FILTER FACE AND BYPASS DAMPER Fig. 15 Schematic of Typical Direct Air-Side Economizer ![image](/image/placeholder) IF DX THEN OPTIONAL LOCATION OF CONDENSER FILTER DEC SCAVENGER FAN SCAVENGER AIR ② ③ 4 RECIRCULATING ⑧ ⑦ FAN FILTER COLD AISLE COOLING AIR-TO-AIR HEAT HOT AISLE SUPPLY COIL EXCHANGER RETURN Fig. 16 Schematic of Typical Indirect Air-Side Economizer capacity of the compressorized cooling equipment (trim cooling). See Chapter 41 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment for more information on evaporative air-cooling systems. Refrigerant-Side Economizers. More recently, systems with remote air-cooled condensers have integrated a refrigerant-side economizer by adding valves and a refrigerant pump to the refrig- erant circuit. As ambient conditions allow, the compressor(s) are shut off and the pump activates to move the refrigerant between the indoor evaporator coil and the outdoor condenser coil. A typical system has multiple circuits, which allow for partial economizer cooling. See Figure 17 for a schematic of a typical system. ASHRAE DATACOM SERIES Book 1: Thermal Guidelines for Data Processing Environments, 4th ed. (2015a) Inc. ASHRAE, 2019 user. single for Licensed | {}
fd553ec5-e6b4-4238-9097-3921389f0ded | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 20.20 ![image](/image/placeholder) REFRIGERANT PUMPS CHECK VALVE CONDENSER(S) SOLENOID REFRIG. CHECK VALVES PUMPS VALVE EVAPORATOR CHECK CIRCUIT 2 VALVE ELECTRONIC EXPANSION CIRCUIT 1 VALVE I COMPRESSORS INDOOR CRAC I Fig. 17 Schematic of Typical Dual-Compressor Refrigerant- Side Economizer Book 2: IT Equipment Power Trends, 3rd ed. (2018) Book 3: Design Considerations for Datacom Equipment Centers, 2nd ed. (2009a) Book 4: Liquid Cooling Guidelines for Datacom Equipment Centers, 2nd ed. (2013) Book 5: Structural and Vibration Guidelines for Datacom Equipment Cen- ters (2008a) Book 6: Best Practices for Datacom Facility Energy Efficiency, 2nd ed. (2009b) Book 7: High Density Data Centers- Case Studies and Best Practices (2008b) Book 8: Particulate and Gaseous Contamination in Datacom Environments, 2nd ed. (2014a) Book 9: Real-Time Energy Consumption Measurements in Data Centers (2010) Book 10: Green Tips for Data Centers (2011) Book 11: PUETM: A Comprehensive Examination of the Metric (2014b) Book 12: Server Efficiency - Metrics for Computer Servers and Storage (2015b) Book 13: IT Equipment Design Impact on Data Center Solutions (2016a) REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. AHRI. 2017. Standard for performance rating of computer and data processing room air conditioners. ANSI/AHRI Standard 1361 (SI)-2017. Air- Conditioning, Heating and Refrigeration Institute, Arlington, VA. ASCE. 2016. Minimum design loads and associated criteria for buildings and other structures. ASCE/SEI Standard 7-16. American Society of Civil Engineers, Reston, VA. ASHRAE. 2016. Energy standard for buildings except low-rise residential buildings. ANSI/ASHRAE/IES Standard 90.1-2016. ASHRAE. 2016. Energy standard for data centers. ANSI/ASHRAE Stan- dard 90.4-2016. ASHRAE. 2012. Method of testing for rating computer and data processing room unitary air conditioners. ANSI/ASHRAE Standard 127-2012. BICSI. 2014. Data center design and implementation best practices. ANSI/ BICSI Standard 002-2014. Building Industry Consulting Service Inter- national, Tampa, FL. 2019 ASHRAE Handbook-HVAC Applications (SI) CISCA. 2007. Recommended Test Proceduresfor Access Floors. Ceilings & Interior Systems Construction Association, Oak Brook, IL EIA. 2005. Cabinets, racks, panels and associated equipment. EIA/ECA Standard 310-E-2005. Electronics Industries Alliance through Elec- tronic Components Industry Association, Alpharetta, GA. IEEE. 1995. Recommended practice for emergency and standby power sys- tems for industrial and commercial application. Standard 446-1995. Institute of Electrical and Electronics Engineers, Piscataway, NJ. IEEE. 2008. Recommended practice for installation design and installation of vented lead-acid batteries for stationary applications. Standard 484- 2002 (R2008). Institute of Electrical and Electronics Engineers, Piscat- away, NJ. IEEE. 2005. Recommended practice for powering and grounding electronic equipment. Standard 1100-2005. Institute of Electrical and Electronics Engineers, Piscataway, NJ. IEEE. 2013. Recommended practice for installation design and installation of valve-regulated lead-acid batteries for stationary applications. Standard 1187-2013. Institute of Electrical and Electronics Engineers, Piscataway, NJ. NFPA. 2019. Installation of sprinkler systems. Standard 13. National Fire Protection Agency, Quincy, MA. NFPA. 2014. Inspection, testing, and maintenance of water-based fire pro- tection systems. Standard 25. National Fire Protection Agency, Quincy, MA. NFPA. 2017. National Electric CodeⓇ. Standard 70. National Fire Protec- tion Agency, Quincy, MA. NFPA. 2018. Handbook for electrical safety in the workplace. Standard 70E. National Fire Protection Agency, Quincy, MA. NFPA. 2019. National fire alarm and signaling code handbook. Standard 72. National Fire Protection Agency, Quincy, MA. NFPA. 2017. Fire protection of information technology equipment. Stan- dard 75. National Fire Protection Agency, Quincy, MA. NFPA. 2016. Fire protection of telecommunication facilities. Standard 76. National Fire Protection Agency, Quincy, MA. NFPA. 2019. Water mist fire protection systems. Standard 750. National Fire Protection Agency, Quincy, MA. NFPA. 2018. Clean agent fire extinguishing systems. Standard 2001. National Fire Protection Agency, Quincy, MA. OSHA. Annual. Occupational noise exposure. 29 CFR 1910.95. Code of Federal Regulations, Occupational Safety and Health Administration, Washington, D.C. www.ecfr.gov. Pommerenke, D., and D. Swenson. 2014. The effect of humidity on static electricity induced reliability issues of ICT equipment in data center. ASHRAE Research Project RP-1499, Final Report. Rawson, A., J. Pflueger, and T. Cader. 2007. The Green Grid data center power efficiency metrics: PUE and DCiE. White Paper WP#06. C. Belady, ed. The Green Grid, Beaverton, OR. TIA. 2017. Telecommunications infrastructure standard for data centers. ANSI/TIA Standard 942-B-2017. Telecommunications Industry Associ- ation, Arlington, VA. UL. 2016. Emergency lighting and power equipment. ANSI/UL Standard 924. Underwriters Laboratories, Northbrook, IL. BIBLIOGRAPHY ASHRAE. 2011. Gaseous and particulate contamination guidelines for data centers. ASHRAE TC9.9, White Paper. www.ashrae.org/File%20 LiburyTechicaNd Beourcs Profactionat/OFration/%)) Updances2011-Gason-and-Partcolate-Guines.pdff ASHRAE. 2012. IT equipment thermal management and controls. ASHRAE TC 9.9, 2012 White Paper. tc0909.ashraetcs.org/documents MAHBAIE-DICIENTAL/Epulpianvenhand and Armanant %20and%20Controls_ V1.0.pdf. ASHRAE. 2014. Data center networking Issues and best equipment- prac- tices. ASHRAE TC 9.9, 2014 White Paper. ASHRAE. 2016. BACnetTM: A data communication protocol for building automation and control networks. ANSI/ASHRAE Standard 135-2016. Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
6e82c815-db2f-4ace-8786-8d5abd5f5cdc | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 21 PRINTING PLANTS ¦ Design Criteria ¦ 21.1 ¦ ¦ --- ¦ --- ¦ ¦ Control of Paper Moisture Content ¦ 21.2 ¦ ¦ Platemaking ¦ 21.2 ¦ ¦ Relief Printing ¦ 21.2 ¦ ¦ Lithography ¦ 21.3 ¦ ¦ Rotogravure ¦ 21.4 ¦ ¦ Other Plant Functions ¦ 21.4 ¦ T HIS chapter outlines air-conditioning requirements for key printing operations. Air conditioning of printing plants can pro- vide controlled, uniform air moisture content and temperature in working spaces. Paper, the principal material used in printing, is hygroscopic and very sensitive to variations in the humidity of the surrounding air. Printing problems caused by paper expansion and contraction can be avoided by controlling the moisture content throughout the manufacture and printing of the paper. 1. DESIGN CRITERIA The following are three basic printing methods: · Relief printing (letterpress). Ink is applied to a raised surface. · Lithography. Inked surface is neither in relief nor recessed. · Gravure (intaglio printing). Inked areas are recessed below the surface. Figure 1 shows the general work flow through a printing plant. The operation begins at the publisher and ends with the finished printed product and paper waste. Paper waste, which may be as much as 20% of the total paper used, affects profitability. Proper air conditioning can help reduce the amount of paper wasted. In sheetfed printing, individual sheets are fed through a press from a stack or load of sheets and collected after printing. In webfed rotary printing, a continuous web of paper is fed through the press ![image](/image/placeholder) PUBLISHER PAPER COMPOSITION PURCHASE STORAGE HANDLING PLATEMAKING PRINTING BINDERY SALVAGE SHIPPING SYSTEM WASTE PAPER FINISHED GOODS Fig. 1 Work Flow Through a Printing Plant The preparation of this chapter is assigned to TC 9.2, Industrial Air Conditioning. from a roll. The printed material is cut, folded, and delivered from the press as signatures, which form the sections of a book. Sheetfed printing is a slow process in which the ink is essentially dry as the sheets are delivered from the press. Offsetting, the trans- ference of an image from one sheet to another, is prevented by applying a powder or starch to separate each sheet as it is delivered from the press. Starches present a housekeeping problem: the parti- cles (30 to 40 m in size) tend to fly off, eventually settling on any horizontal surface. If both temperature and relative humidity are maintained within normal human comfort limits, they have little to do with web breaks or the runnability of paper in a webfed press. At extremely low humidity, static electricity causes the paper to cling to the rollers, creating undue stress on the web, particularly with high-speed presses. Static electricity is also a hazard when flammable solvent inks are used. Special Considerations Special Warning: Certain industrial spaces may contain flam- mable, combustible, and/or toxic concentrations of vapors or dusts under either normal or abnormal conditions. In spaces such as these, there are life-safety issues that this chapter may not completely address. Special precautions must be taken in accordance with requirements ofrecognized authorities such as the National Fire Pro- tection Association (NFPA), the Occupational Safety and Health Administration (OSHA), and the American National Standards Institute (ANSI). In all situations, engineers, designers, and install- ers who encounter conflicting codes and standards must defer to the code or standard that best addresses and safeguards life safety. Various areas in printing plants require special attention to pro- cessing and heat loads. Engraving and platemaking departments must have very clean air: not as clean as that for industrial cleanrooms, but cleaner than that for offices. Engraving and photographic areas may also have special ventilation needs because of the chemicals used. Nitric acid fumes from powderless etching require careful duct mate- rial selection. Composing rooms, which contain computer equip- ment, can be treated the same as similar office areas. The excessive dust from cutting in the stitching and binding operations must be con- trolled. Stereotype departments have very high heat loads. In pressrooms, air distribution must not cause the web to flutter or force contaminants or heat (which normally would be removed by roof vents) down to the occupied level. Air should be introduced immediately above the occupied zone wherever possible to mini- mize total flow and encourage stratification. High air exchange rates may be required where solvent- or oil-based inks are used, because of the large quantity of organic solvent vapors that may be released from nonpoint sources. Exhaust emissions from dryer systems may contain substantial concentrations of solvent vapors, which must be captured and recovered or incinerated to satisfy local air pollution requirements. Where these measures are required, efforts should be 21.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
8e409604-52ef-47bf-a146-f91607cf7de3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 21.2 2019 ASHRAE Handbook-HVAC Applications (SI) made to maximize point-source capture of vapors to minimize the size, cost, and energy requirements for vapor recovery/incineration equipment. These efforts also minimize the effect of these require- ments on general ventilation systems. Conventional air-conditioning and air-handling equipment, particularly rooftop equipment, may be unable to handle the high outdoor air requirements of pressroom applications effectively. Stratified ventilation may be used in high-bay installations to reduce total system airflow and air-conditioning requirements. Pressrooms using oil- or solvent-based inks should be provided with a minimum of 2.5 L/(s·m2) of outdoor air to ensure adequate dilution of inter- nally generated volatile organic compounds. Ventilation of storage areas should be about 0.5 air changes per hour (ach); bindery venti- lation should be about 1 ach. Storage areas with materials piled high may need roof-mounted smoke- and heat-venting devices. In a bindery, loads of loose signatures are stacked near equip- ment, which makes it difficult to supply air to occupants without scattering the signatures. One solution is to run the main ducts at the ceiling with many supply branches dropped to within 2.5 to 3 m of the floor. Conventional adjustable blow diffusers, often the linear type, are used. 2. CONTROL OF PAPER MOISTURE CONTENT Controlling the moisture content and temperature of paper is important in all printing, particularly multicolor lithography. Paper should be received at the printing plant in moisture-proof wrappers, which are not broken or removed until the paper is brought to the pressroom temperature. When exposed to room temperature, paper at temperatures substantially below the room temperature rapidly absorbs moisture from the air, causing distortion. Figure 2 shows the time required to temperature-condition wrapped paper. Printers usu- ally order paper with a moisture content approximately in equilib- rium with the relative humidity maintained in their pressrooms. Papermakers find it difficult to supply paper in equilibrium with a relative humidity higher than 50%. n Inc. ASHRAE, 2019 user. single for Licensed CONDITIONING, TEMPERATURE FOR REQUIRED TIME Chart Title: VOLUME IN CUBIC METRES OF PAPER IN MOISTURE - PROOF WRAPPING X-Axis: TEMPERATURE DIFFERENCE, K Chart Type: line 0 5 10 15 20 25 30 35 item_01 0Kelvin (K) 5Kelvin (K) 10Kelvin (K) 20Kelvin (K) 40Kelvin (K) 60Kelvin (K) 80Kelvin (K) 150Kelvin (K) Fig. 2 Temperature-Conditioning Chart for Paper Digital hygrometers can be used to check the hygroscopic con- dition of paper relative to the surrounding air. The probes contain a moisture-sensitive element that measures the electrical conductivity of the paper. Intact mill wrappings and the tightness of the roll normally protect a paper roll for about six months. If the wrapper is damaged, moisture usually penetrates no more than 3 mm. 3. PLA TEMAKING Humidity and temperature control are important considerations when making lithographic and collotype plates, photoengravings, and gravure plates and cylinders. If the moisture content and temperature of the plates increase, the coatings increase in light sen- sitivity, which necessitates adjustments in the light intensity or the length of exposure to give uniformity. If platemaking rooms are maintained at constant dry-bulb tem- perature and relative humidity, plates can be produced at known control conditions. As soon as it is dry, a bichromated colloid coat- ing starts to age and harden at a rate that varies with the atmo- spheric conditions, so exposures made a few hours apart may be quite different. The rate of aging and hardening can be estimated more accurately when the space is air conditioned. Exposure can then be reduced progressively to maintain uniformity. An opti- mum relative humidity of 45% or less substantially increases the useful life of bichromated colloid coatings; the relative humidity control should be within 2%. A dry-bulb temperature of24 to 27°C maintained within 1 K is good practice. The ventilation air requirements of the plate room should be investigated. A plant with a large production of deep-etch plates should consider locating this operation outside the conditioned area. Exhausts for platemaking operations consist primarily of lateral or downdraft systems at each operation. Because of their bulkiness or mass, plates or cylinders are generally conveyed by overhead rail to the workstation, where they are lowered into the tank for plating, etching, or grinding. Exhaust ducts must be below or to one side of the working area, so lateral exhausts are generally used for open- surface tanks. Exhaust quantities vary, depending on the nature of the solution and shape of the tank, but they should provide exhaust in accordance with the recommendations of Industrial Ventilation by the Ameri- can Conference of Governmental Industrial Hygienists (ACGIH 2016) for a minimum control velocity of 0.25 m/s at the side of the tank opposite the exhaust intake. Tanks should be covered to mini- mize exhaust air quantities and increase efficiency. Excessive air turbulence above open tanks should be avoided. Because of the nature of the exhaust, ducts should be acid-resistant and liquidtight to prevent moisture condensation. W ebfed offset operations and related departments are similar to webfed letterpress operations, without the heat loads created in the composing room and stereotype departments. Special attention should be given to air cleanliness and ventilation in platemaking to avoid flaws in the plates caused by chemical fumes and dust. Reclamation or destruction systems are used to prevent photo- sensitive hydrocarbons from being exhausted into the atmosphere. Some reclamation systems use activated carbon for continuous pro- cessing. Incineration or catalytic converters may be used to produce rapid oxidation to eliminate pollutants. The amount of solvents reclaimed may exceed that added to the ink. A rotogravure plant can be hazardous because highly volatile solvents are used. Equipment must be explosionproof, and air- handling equipment must be sparkproof. Clean air must be supplied at controlled temperature and relative humidity. 4. RELIEF PRINTING In relief printing (letterpress), rollers apply ink only to the raised surface of a printing plate. Pressure is then applied to transfer the ink | {}
dcdef608-833f-4bff-9305-ecdfcc594173 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Printing Plants 21.3 from the raised surface directly to the paper. Only the raised surface touches the paper to transfer the desired image. Air conditioning in newspaper pressrooms and other webfed let- terpress printing areas minimizes problems caused by static elec- tricity, ink mist, and expansion or contraction of the paper during printing. A wide range of operating conditions is satisfactory. The temperature should be selected for operator comfort. At web speeds of5 to 10 m/s, itis not necessary to control the rel- ative humidity because inks are dried with heat. In some types of printing, moisture is applied to the web, and the web is passed over chill rolls to further set the ink. W ebfed letterpress ink is heat-set, made with high-boiling, slow- evaporating synthetic resins and petroleum oils dissolved or dis- persed in a hydrocarbon solvent. The solvent must have a narrow boiling range with a low volatility at room temperatures and a fast evaporating rate at elevated temperatures. The solvent is vaporized in the printing press dryers at temperatures from 120 to 200°C, leav- ing the resins and oils on the paper. W ebfed letterpress inks are dried after all colors are applied to the web. The inks are dried by passing the web through dryers at speeds of 5 to 10 m/s. There are several types of dryers: open-flame gas cup, flame impingement, high-velocity hot air, and steam drum. Exhaust quantities through a press dryer vary from about 3300 to 7000 L/s at standard conditions, depending on the type of dryer used and the speed of the press. Exhaust temperatures range from 120 to 200°C. Solvent-containing exhaust is heated to 700°C in an air pollution control device to incinerate the effluent. A catalyst can be used to re- duce the temperature required for combustion to 540°C, but it re- quires periodic inspection and rejuvenation. Heat recovery reduces the fuel required for incineration and can be used to heat pressroom makeup air. 5. LITHOGRAPHY Lithography uses a grease-treated printing image receptive to ink, on a surface that is neither raised nor depressed. Both grease and ink repel water. Water is applied to all areas of the plate, except the printing image. Ink is then applied only to the printing image and transferred to the paper in the printing process. In multicolor print- ing operations, the image may be printed up to four times on the same sheet of paper in different colors. Registration of images is critical to final color quality. Offset printing transfers the image first to a rubber blanket and then to the paper. Sheetfed and web offset printing are similar to let- terpress printing. The inks used are similar to those used in letter- press printing but contain water-resistant vehicles and pigment. In web offset and gravure printing, the relative humidity in the press- room should be kept constant, and the temperature should be selected for comfort or, at least, to avoid heat stress. It is important to maintain steady conditions to ensure the dimensional stability of the paper onto which the images are printed. The pressroom for sheet multicolor offset printing has more exacting humidity requirements than other printing processes. The paper must remain flat with constant dimensions during multicolor printing, in which the paper may make six or more passes through the press over a period of a week or more. Ifthe paper does not have the right moisture content at the start, or if there are significant changes in atmospheric humidity during the process, the paper will not retain its dimensions and flatness, and misregistering will result. In many cases of color printing, a register accuracy of 100 m is required. Figure 3 shows the close control of the air relative humid- ity that is necessary to achieve this register accuracy. The data shown in this figure are for composite lithographic paper. Maintaining constant moisture content of the paper is compli- cated because paper picks up moisture from the moist offset blanket X-Axis: Moleture Content Change, % Y-Axis: Dimensional Change, % Chart Type: line 0.0 0.5 1.0 1.5 2.0 2.5 3.0 3.5 4.0 item_01 0.0% 0.05% 0.0% 0.0% 0.15% 0.2% 0.25% 0.3% 0.35% Fig.3 Effects of Variation in Moisture Content on Dimensions of Printing Papers (Weber and Snyder 1934) during printing (0.1 to 0.3% for each impression). When two or more printings are made in close register work, the paper at the start of the printing process should have a moisture content in equilib- rium with air at 5 to 8% rh above the pressroom air. At this condi- tion, the moisture evaporated from the paper into the air nearly balances the moisture added by the press. In obtaining register, it is important to keep the sheet flat and free from wavy or tight edges. To do this, the relative humidity balance of the paper should be slightly above that ofthe pressroom atmosphere. This balance is not as critical in four-color roll-feed presses because the press moisture does not penetrate the paper quickly enough between colors to affect sheet dimensions or cause sheet distortion. Recommended Environment The Graphic Arts Technical Foundation recommends ideal con- ditions in a lithographic pressroom of24 to 27°C db and 43 to 47% rh, controlled to 1 K db and 2% rh (Reed 1970). Comfort and economy of operation influence the choice of temperature. The effect ofrelative humidity variations on register can be estimated for offset paper from Figure 3. Closer relative humidity control of the pressroom air is required for multicolor printing of 1930 mm sheets than for 560 mm sheets with the same register accuracy. Closer con- trol is needed for multicolor printing, where the sheet makes two or more trips through the press, than for one-color printing. Ink drying is affected by temperature and humidity, so uniform results are difficult to obtain without controlling the atmospheric conditions. Printing inks must dry rapidly to prevent offsetting and smearing. High relative humidity and high moisture content in paper tend to prevent ink penetration, so more ink remains on the surface than can be quickly oxidized. This affects drying time, intensity of color, and uniformity of ink on the surface. Relative humidity below 60% is favorable for drying at a comfortable tem- perature. Higher relative humidity may cause severe paper distor- tion and significant damage to the final product. The air conditioning for the pressroom of a lithographic plant should control air temperature and relative humidity, filter the air, supply ventilation air, and distribute the air without pronounced drafts around the presses. Using anti-offset sprays to set the ink cre- ates an additional air-filtering load from the pressroom. Drafts and high airflow over the presses lead to excessive drying of the ink and water, which causes scumming or other problems. The operating procedures of the pressroom should be analyzed to determine the heat removal load. The lighting load is high and con- stant throughout the day. The temperature of the paper brought into the pressroom and the length of time it is in the room should be con- sidered to determine the sensible load from the paper. Figure 2 shows the time required for wrapped paper to reach room temp- erature. The press motors usually generate a large portion of the internal sensible heat gain. Inc. ASHRAE, 2019 user. single for Licensed | {}
c62735b7-03b6-465e-844e-a4d94a312b35 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 21.4 2019 ASHRAE Handbook- -HVAC Applications (SI) Readings should be taken to obtain the running power load of the larger multicolor presses. The moisture content of the paper fed to the press and the relative humidity of the air must be considered when computing the internal latent heat gain. Paper is used that is in equilibrium with air at a relative humidity somewhat higher than that of the pressroom, so the paper gives up moisture to the space as it absorbs moisture during printing. Ifthe moisture transfer is in bal- ance, water used in the printing process should be included in the internal moisture load. It is preferable to determine the water evap- oration from the presses by testing. Air Conditioning Precise multicolor offset lithography printing requires either refrigeration with provision for separate humidity control, or sorption dehumidifying equipment for independent humidity control with provision for cooling. The need for humidity control in the pressroom may be determined by calculating the dimen- sional change of the paper for each percent of change in relative humidity and checking this with the required register for the printing process. Air conditioning of the photographic department is usually con- sidered secondary in importance to that of the pressroom. Most of the work in offset lithography is done on film. Air conditioning con- trols cleanliness and comfort and maintains the size of the film for register work. Air conditioning is important in the stripping department, both for comfort and for maintaining size and register. Curling of the film and flats, as well as shrinkage or stretch of materials, can be mini- mized by maintaining constant relative humidity. This is particularly important for close-register color work. The photo- graphic area, stripping room, and platemaking area usually are maintained at the same conditions as the pressroom. Dryers used for web offset printing are the same type as for web- fed letterpress. Drying is not as complex because less ink is applied and presses run at lower speeds (4 to 9 m/s). 6. ROTOGRA VURE Rotogravure printing uses a cylinder with minute inkwells etched in the surface to form the printing image. Ink is applied to the cylinder, filling the wells. Excess ink is then removed from the cyl- inder surface by doctor blades, leaving only the ink in the wells. The image is then transferred to the paper as it passes between the print- ing cylinder and an impression cylinder. In sheetfed gravure printing (as in offset printing), expansion, contraction, and distortion should be prevented to obtain correct register. The paper need not be in equilibrium with air at a relative humidity higher than that of the pressroom, because no moisture is added to the paper in the printing process. Humidity and tempera- ture control should be exacting, like in offset printing. The relative humidity should be 45 to 50%, controlled to within 2%, with a comfort temperature controlled to within 1 K. Gravure printing ink dries principally by evaporating the solvent in the ink, leaving a solid film of pigment and resin. The solvent is a low-boiling hydrocarbon, and evaporation takes place rapidly, even without the use of heat. The solvents have closed-cup flash points from -5 to 27°C and are classified as Group I or special hazard liq- uids by local code and insurance company standards. As a result, in areas adjacent to gravure press equipment and solvent and ink storage areas, electrical equipment must be Class I, Division 1 or 2, as described by the National Electrical CodeⓇ (NFPA Standard 70), and ventilation requirements (both supply and exhaust) are stringent. Ventilation should be designed for high reliability, with sensors to detect unsafe pollutant concentrations and then to initiate alarm or safety shutdown when necessary. Rotogravure printing units operate in tandem, each superimposing print over that from the preceding unit. Press speeds range from 6 to 12 m/s. Each unit is equipped with its own dryer to prevent subsequent smearing or smudging. A typical drying system consists of four dryers connected to an exhaust fan. Each dryer is equipped with fans to recirculate 2500 to 4000 L/s (at standard conditions) through a steam or hot water coil and then through jet nozzles. The hot air (55°C) impinges on the web and drives off the solvent-laden vapors from the ink. It is normal to exhaust half of this air. The system should be designed and adjusted to prevent solvent vapor concentration from exceeding 25% of its lower flammable limit (Marsailes 1970). If this is not possible, con- stant lower-flammable-limit (LFL) monitoring, concentration con- trol, and safety shutdown capability should be included. In exhaust design for a particular process, solvent vapor should be captured from the printing unit where paper enters and exits the dryer, from the fountain and sump area, and from the printed paper, which continues to release solvent vapor as it passes from one printing unit to another. Details of the process, such as ink and paper characteristics and rate of use, are required to determine exhaust quantities. When dilution ventilation is used, exhaust of 500 to 700 L/s (at standard conditions) at the floor is often provided between each unit. The makeup air units are adjusted to supply slightly less air to the pressroom than that exhausted, to keep the pressroom negative with respect to the surrounding areas. 7. OTHER PLANT FUNCTIONS Flexography Flexography uses rubber raised printing plates and functions much like a letterpress. Flexography is used principally in the pack- aging industry to print labels and also to print on smooth surfaces, such as plastics and glass. Collotype Printing Collotype or photogelatin printing is a sheetfed printing process related to lithography. The printing surface is bichromated gelatin with varying affinity for ink and moisture, depending on the degree of light exposure received. There is no mechanical dampening as in lithography, and the necessary moisture in the gelatin printing surface is maintained by operating the press in an atmosphere of high relative humidity, usually about 85%. Because the tonal val- ues printed are very sensitive to changes in the moisture content of the gelatin, the relative humidity should be maintained within 2%. Because tonal values are also very sensitive to changes in ink vis- cosity, temperature must be closely maintained; 27 °C 2 K is rec- ommended. Collotype presses are usually partitioned off from the main plant, which is kept at a lower relative humidity, and the paper is exposed to high relative humidity only while it is being printed. Salvage Salvage systems remove paper trim and shredded paper waste from production areas, and carry airborne shavings to a cyclone or baghouse collector, where they are baled for recycling. Air quanti- ties required are 2.5 to 2.8 m3 per kilogram of paper trim, and the transport velocity in the ductwork is 23 to 25 m/s (Marsailes 1970). Humidification may be provided to prevent the buildup of a static charge and consequent system blockage. Air Filtration Ventilation and air-conditioning systems for printing plants com- monly use automatic moving-curtain dry-media filters with renew- able media having a rating of MERV 13 (ASHRAE Standard 52.2). Inc. ASHRAE, 2019 user. single for Licensed | {}
a9db31d0-0b67-44f6-93a5-3e612cf02068 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Printing Plants 21.5 In sheetfed pressrooms, a high-performance final filter is used to filter starch particles, which require about a MERV 13 rating as well. In film processing areas, which require relatively dust-free conditions, high-efficiency air filters are installed, with a rating of MERV 14. A different type of filtration problem in printing is ink mist or ink fly, which is common in newspaper pressrooms and in heatset letterpress or offset pressrooms. Minute droplets ofink (5 to 10 m) are dispersed by ink rollers rotating in opposite directions. The cloud of ink droplets is electrostatically charged. Suppressors, charged to repel the ink back to the ink roller, are used to control ink mist. Additional control is provided by automatic moving curtain filters. Binding and Shipping Some printed materials must be bound. Two methods ofbinding are perfect binding and stitching. In perfect binding, sections of a book (signatures) are gathered, ruffed, glued, and trimmed. The glued edge is flat. Large books are easily bound by this type of binding. Low-pressure compressed air and a vacuum are usually required to operate a perfect binder, and paper shavings are removed by a trimmer. The use ofheated glue necessitates an exhaust system if the fumes are toxic. In stitching, sections of a book are collected and stitched (sta- pled) together. Each signature is opened individually and laid over a moving chain. Careful handling ofthe paper is important. This has the same basic air requirements as perfect binding. Mailing areas of a printing plant wrap, label, and ship the manu- factured goods. Operation of the wrapper machine can be affected by low humidity. In winter, humidification of the bindery and mail- ing area to about 40 to 50% rh may be necessary to prevent static buildup. REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. ACGIH. 2016. Industrial ventilation: A manual of recommended practice, 29th ed. American Conference of Governmental Industrial Hygienists, Cincinnati, OH. ASHRAE. 2017. Method of testing general ventilation air-cleaning devices for removal efficiency by particle size. ANSI/ASHRAE Standard 52.2- 2017. Marsailes, T.P. 1970. Ventilation, filtration and exhaust techniques applied to printing plant operation. ASHRAE Journal (December):27. NFPA. 2017. National electrical codeⓇ. ANSI/NFPA Standard 70. National Fire Protection Association, Quincy, MA. Reed, R.F. 1970. What the printer should know about paper. Graphic Arts Technical Foundation, Pittsburgh, PA. Weber, C.G., and L. W. Snyder. 1934. Reactions of lithographic papers to variations in humidity and temperature. Journal of Research 12 (January). dx.doi.org/10.6028/jres.012.006. Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
63126654-366d-42d4-a2a6-77141267228d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 22 TEXTILE PROCESSING PLANTS ¦ Terminology ¦ 22.1 ¦ ¦ --- ¦ --- ¦ ¦ Fiber Making ¦ 22.1 ¦ ¦ Yarn Making ¦ 22.2 ¦ ¦ Fabric Making ¦ 22.3 ¦ ¦ Air-Conditioning Design ¦ 22.4 ¦ ¦ Energy Conservation ¦ ・・ 22.7 ¦ T HIS chapter covers (1) basic processes for making synthetic fibers, (2) fabricating synthetic fibers into yarn and fabric, (3) relevant types of HVAC and refrigerating equipment, (4) health considerations, and (5) energy conservation procedures. Most textile manufacturing processes may be placed into one of three general classifications: synthetic fiber making, yarn making, or fabric making. Synthetic fiber manufacturing is divided into staple processing, tow-to-top conversion, and continuous fiber processing; yarn making is divided into spinning and twisting; and fabric making is divided into weaving and knitting. Although these processes vary, their descriptions reveal the principles on which air-conditioning design for textile facilities is based. 1. TERMINOLOGY The following is only a partial glossary of terms used in the textile industry. For more complete terminology, consult the sources in the Bibliography. Air permeability. Porosity, or ease with which air passes through material. Air permeability affects factors such as the wind resistance of sailcloth, air resistance of parachute cloth, and efficiency of vari- ous types of air filtration media. It is also a measure of a fabric's warmness or coolness. Bidirectional fabric. A fabric with reinforcing fibers in two di- rections: in the warp (machine) direction and filling (cross-machine) direction. Calender. A machine used in finishing to impart various surface effects to fabrics. It essentially consists oftwo or more heavy rollers, sometimes heated, through which the fabric is passed under heavy pressure. Denier. The mass, in grams, of 9000 m ofyarn. Denier is a direct numbering system in which lower numbers represent finer sizes and higher numbers the coarser sizes. Outside the United States, the Tex system is used instead. Heddle. A cord, round steel wire, or thin flat steel strip with a loop or eye near the center, through which one or more warp threads pass on the loom, so that thread movement may be controlled in weaving. Heddles are held at both ends by the harness frame. They control the weave pattern and shed as the harnesses are raised and lowered during weaving. Lubricant. An oil or emulsion finish applied to fibers to prevent damage during textile processing, or to knitting yarns to make them more pliable. Machine direction. The long direction within the plane of the fabric (i.e., the direction in which the fabric is being produced by the machine). The preparation of this chapter is assigned to TC 9.2, Industrial Air Conditioning. Pick. A single filling thread carried by one trip of the weft inser- tion device across the loom. Picks interface with the warp ends to form a woven fabric. Reed. A comblike device on a loom that separates the warp yarns and also beats each succeeding filling thread against those already woven. The space between two adjacent wires of the reed is called a dent. The fineness of the reed is calculated by the number of dents per 25.4 mm: the more dents, the finer the reed. Selvage. The narrow edge of woven fabric that runs parallel to the warp. Itis made with stronger yarns in a tighter construction than the body of the fabric, to prevent raveling. A fast selvage encloses all or part of the picks; a selvage is not fast when the filling threads are cut at the fabric edge after each pick. Shuttle. A boat-shaped device usually made of wood with a metal tip that carries filling yarns through the shed in the weaving process. Tex. The mass, in grams, of 1000 m offabric. Used primarily out- side the United States. See also Denier. Warp. The set of yarn in all woven fabrics, running lengthwise and parallel to the selvage, interwoven with the filling. 2. FIBER MAKING Processes preceding fiber extrusion have diverse ventilating and air-conditioning requirements based on principles similar to those that apply to chemical plants. Synthetic fibers are extruded from metallic spinnerets and solid- ified as continuous parallel filaments. This process, called continu- ous spinning, differs from the mechanical spinning of fibers or tow into yarn, which is generally referred to as spinning. Synthetic fibers may be formed by melt-spinning, dry-spinning, or wet-spinning. Melt-spun fibers are solidified by cooling the molten polymer; dry-spun fibers by evaporating a solvent, leaving the poly- mer in fiber form; and wet-spun fibers by hardening the extruded fil- aments in a liquid bath. The selection of a spinning method is affected by economic and chemical considerations. Generally, nylons, polyes- ters, and glass fibers are melt-spun; acetates dry-spun; rayons and aramids wet-spun; and acrylics dry- or wet-spun. For melt- and dry-spun fibers, the filaments of each spinneret are usually drawn through a long vertical tube called a chimney or quench stack, within which solidification occurs. For wet-spun fibers, the spinneret is suspended in a chemical bath where coagula- tion of the fibers takes place. Wet-spinning is followed by washing, applying a finish, and drying. Synthetic continuous fibers are extruded as a heavy denier tow for cutting into short lengths (called staple) or somewhat longer lengths for tow-to-top conversion, or they are extruded as light denier fila- ments for processing as continuous fibers. Oil is then applied to lubricate, give antistatic properties, and control fiber cohesion. The extruded filaments are usually drawn (stretched) both to align the molecules along the axis of the fiber and to improve the crystalline 22.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
8805ccea-5666-47aa-979c-94cbee37e58f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 22.2 structure of the molecules, thereby increasing the fiber's strength and resistance to stretching. Heat applied to the fiber when drawing heavy denier or high- strength synthetics releases a troublesome oil mist. In addition, the mechanical work of drawing generates a high localized heat load. If the draw is accompanied by twist, it is called draw-twist; if not, it is called draw-wind. After draw-twisting, continuous fibers may be given additional twist or may be sent directly to warping. When tow is cut to make staple, the short fibers are allowed to assume random orientation. The staple, alone or in a blend, is then usually processed as described in the Cotton System section. How- ever, tow-to-top conversion, a more efficient process, has become more popular. The longer tow is broken or cut to maintain parallel ori- entation. Most of the steps of the cotton system are bypassed; the par- allel fibers are ready for blending and mechanical spinning into yarn. In the manufacture of glass fiber yarn, light denier multifilaments are formed by attenuating molten glass through platinum bushings at high temperatures and speeds. The filaments are then drawn together while being cooled with a water spray, and a chemical size is applied to protect the fiber. This is all accomplished in a single process prior to winding the fiber for further processing. 3. YARN MAKING The fiber length determines whether spinning or twisting must be used. Spun yarns are produced by loosely gathering synthetic staple, natural fibers, or blends into rope-like form; drawing them out to increase fiber parallelism, if required; and then twisting. Twisted (continuous filament) yarns are made by twisting long mono- filaments or multifilaments. Ply yarns are made in a similar manner from spun or twisted yarns. The principles of mechanical spinning are applied in three dif- ferent systems: cotton, woolen, and worsted. The cotton system is used for all cotton, most synthetic staple, and many blends. Woolen and worsted systems are used to spin most wool yarns, some wool blends, and synthetic fibers such as acrylics. Cotton System The cotton system was originally developed for spinning cotton yarn, but now its basic machinery is used to spin all varieties of sta- ple, including wool, polyester, and blends. Most of the steps from raw materials to fabrics, along with the ranges of frequently used humidities, are outlined in Figure 1. Opening, Blending, and Picking. The compressed tufts are partly opened, most foreign matter and some short fibers are removed, and the mass is put in an organized form. Some blending is desired to average the irregularities between bales or to mix dif- ferent kinds of fiber. Synthetic staple, which is cleaner and more uniform, usually requires less preparation. The product of the picker is pneumatically conveyed to the feed rolls of the card. Carding. This process lengthens the lap into a thin web, which is gathered into a rope-like form called a sliver. Further opening and fiber separation follows, as well as partial removal of short fiber and trash. The sliver is laid in an ascending spiral in cans of various diameters. For heavy, low-count (length per unit of mass) yarns of average or lower quality, the card sliver goes directly to drawing. For lighter, high-count yarns requiring fineness, smoothness, and strength, the card sliver must first be combed. Lapping. In sliver lapping, several slivers are placed side by side and drafted. In ribbon lapping, the resulting ribbons are laid one on another and drafted again. The doubling and redoubling averages out sliver irregularities; drafting improves fiber parallelism. Some recent processes lap only once before combing. Combing. After lapping, the fibers are combed with fine metal teeth to substantially remove all fibers below a predetermined 2019 ASHRAE Handbook-HVAC Applications (SI) length, to remove any remaining foreign matter, and to improve fiber arrangement. The combed lap is then attenuated by drawing rolls and again condensed into a single sliver. Drawing. Drawing follows either carding or combing and improves uniformity and fiber parallelism by doubling and drafting several individual slivers into a single composite strand. Doubling averages the thick and thin portions; drafting further attenuates the mass and improves parallelism. Roving. Roving continues the processes of drafting and parallel- ing until the strand is a size suitable for spinning. A slight twist is inserted, and the strand is wound on large bobbins used for the next roving step or for spinning. Spinning. Mechanical spinning simultaneously applies draft and twist. The packages (any form into or on which one or more ends can be wound) of roving are creeled at the top of the frame. The unwinding strand passes progressively through gear-driven drafting rolls, a yarn guide, the C-shaped traveler, and then to the bobbin. The vertical traverse of the ring causes the yarn to be placed in pre- determined layers. The difference in peripheral speed between the back and front rolls determines the draft. Twist is determined by the rate of front roll feed, spindle speed, and drag, which is related to the traveler mass. The space between the nip or bite of the rolls is adjustable and must be slightly greater than the longest fiber. The speeds of front ![image](/image/placeholder) OPENING AND PICKING Cotton: 55-70% rh Synthetic: 50-55% rh CARDING Cotton: 55-60% rh Synthetic: 50-60% rh SLIVER LAPPING Cotton: 55-60% m Synthetic: 55-65% rh RIBBON LAPPING Cotton: 55-60% rh Synthetic: 55-65% rh COMBING FIBERS Cotton: 55-65% rh Synthetic: 55-65% rh DRAW-TWISTING DRAWING TOW-TO-TOP Cotton: 50-60% rh Synthetic: 50-60% rh ROVING FROM Cotton: 50-60% rh Synthetic: 50-60% rh FIBERS SPINNING Cotton: 35-60% rh Synthetic: 50-65% rh WINDING AND SPOOLING CONTINUUSO Cotton: 55-65% m Synthetic: 60-65% rh TWISTING Cotton: 60-65% rh Synthetic: 50-65% rh WARPING Cotton: 55-70% rh Synthetic: 50-60% rh SLASHING KNITTING WEAVING Cot.: 60-65% rh Syn.: 50-60% rh Cot.: 70-87% rh Syn.: 60-70% rh FINISHING Fig. 1 Textile Process Flowchart and Ranges of Humidity Inc. ASHRAE, 2019 user. single for Licensed | {}
a6412c3b-e3ad-4cd4-881c-bdc034fd9635 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Textile Processing Plants 22.3 and back rolls are independently adjustable. Cotton spindles nor- mally run at 8000 to 9000 rpm but may exceed 14 000 rpm. In ring twisting, drawing rolls are omitted, and a few spindles run as high as 18 000 rpm. Open-end or turbine spinning combines drawing, roving, lap- ping, and spinning. Staple fibers are fragmented as they are drawn from a sliver and fed into a small, fast-spinning centrifugal device. In this device, the fibers are oriented and discharged as yarn; twist is imparted by the rotating turbine. This system is faster, quieter, and less dusty than ring spinning. Spinning is the final step in the cotton system; the feature that distinguishes it from twisting is the application of draft. The amount and point of draft application accounts for many of the subtle dif- ferences that require different humidities for apparently identical processes. Atmospheric Conditions. From carding to roving, the loosely bound fibers are vulnerable to static electricity. In most instances, static can be adequately suppressed with humidity, which should not be so high as to cause other problems. In other instances, it is nec- essary to suppress electrostatic properties with antistatic agents. Wherever draft is applied, constant humidity is needed to maintain optimum frictional uniformity between adjacent fibers and, hence, cross-sectional uniformity. w oolen and Worsted Systems The woolen system generally makes coarser yarns, whereas the worsted system makes finer ones of a somewhat harder twist. Both may be used for lighter blends ofwool, as well as for synthetic fibers with the characteristics of wool. The machinery used in both sys- tems applies the same principles of draft and twist but differs greatly in detail and is more complex than that used for cotton. Compared to cotton, wool fibers are dirtier, greasier, and more irregular. They are scoured to remove grease and are then usually reimpregnated with controlled amounts of oil to make them less hydrophilic and to provide better interfiber behavior. Wool fibers are scaly and curly, so they are more cohesive and require different treatment. Wool, in contrast to cotton and synthetic fibers, requires higher humidities in the processes prior to and including spinning than it does in the processes that follow. Approximate humidities are given in Kirk and Othmer (2004). Twisting Filaments and Yarns Twisting was originally applied to silk filaments; several fila- ments were doubled and then twisted to improve strength, unifor- mity, and elasticity. Essentially the same process is used today, but it is now extended to spun yarns, as well as to single or multiple fil- aments of synthetic fibers. Twisting is widely used in the manufac- ture of sewing thread, twine, tire cord, tufting yarn, rug yarn, ply yarn, and some knitting yarns. Twisting and doubling is done on a down- or ring-twister, which draws in two or more ends from packages on an elevated creel, twists them together, and winds them into a package. Except for the omission of drafting, down-twisters are similar to conventional ring-spinning frames. When yarns are to be twisted without doubling, an up-twister is used. Up-twisters are primarily used for throwing synthetic mono- filaments and multifilaments to add to or vary elasticity, light reflec- tion, and abrasion resistance. As with spinning, yarn characteristics are controlled by making the twist hard or soft, right (S) or left (Z). Quality is determined largely by the uniformity of twist, which, in turn, depends primarily on the tension and stability of the atmo- spheric conditions (Figure 1). Because the frame may be double- or triple-decked, twisting requires concentrations of power. The frames are otherwise similar to those used in spinning, and they present the same air distribution problems. In twisting, lint is not a serious problem. 4. FABRIC MAKING Preparatory Processes When spinning or twisting is complete, the yarn may be prepared for weaving or knitting by processes that include winding, spooling, creeling, beaming, slashing, sizing, and dyeing. These processes have two purposes: (1) to transfer the yarn from the type of package dictated by the preceding process to a type suitable for the next and (2) to impregnate some of the yarn with sizes, gums, or other chem- icals that may not be left in the final product. Filling Yarn. Filling yarn is wound on quills for use in a loom shuttle. It is sometimes predyed and must be put into a form suitable for package or skein dyeing before it is quilled. Ifthe filling is ofrel- atively hard twist, it may be put through a twist-setting or condition- ing operation in which internal stresses are relieved by applying heat, moisture, or both. Warp Yarn. Warp yarn is impregnated with a transient coating of size or starch that strengthens the yarn 's resistance to the chafing it will receive in the loom. The yarn is first rewound onto a cone or other large package from which it will unwind speedily and smoothly. The second step is warping, which rewinds a multiplicity of ends in parallel arrangement on large spools, called warp or sec- tion beams. In the third step, slashing, the threads pass progres- sively through the sizing solution, through squeeze rolls, and then around cans, around steam-heated drying cylinders, or through an air-drying chamber. A thousand kilograms or more may be wound on a single loom beam. Knitting Yarn. If hard-spun, knitting yarn must be twist-set to minimize kinking. Filament yarns must be sized to reduce strip- backs and improve other running qualities. Both must be put in the form of cones or other suitable packages. Uniform tension is of great importance in maintaining uniform package density. Y arns tend to hang up when unwound from a hard package or slough off from a soft one, and both tendencies are aggravated by spottiness. The processes that require air condition- ing, along with recommended relative humidities, are presented in Figure 1. Weaving In the simplest form of weaving, harnesses raise or depress alternate warp threads to form an opening called a shed. A shuttle containing a quill is kicked through the opening, trailing a thread of filling behind it. The lay and the reed then beat the thread firmly into one apex of the shed and up to the fell of the previously woven cloth. Each shuttle passage forms a pick. These actions are repeated at frequencies up to five per second. Each warp thread usually passes through a drop-wire that is released by a thread break and automatically stops the loom. Another automatic mechanism inserts a new quill in the shuttle as the previous one is emptied, without stopping the loom. Other mechanisms are actuated by filling breaks, improper shuttle boxing, and the like, which stop the loom until it is manually restarted. Each cycle may leave a stop mark sufficient to cause an imperfection that may not be apparent until the fabric is dyed. Beyond this basic machine and pattern are many complex varia- tions in harness and shuttle control, which result in intricate and novel weaving effects. The most complex loom is the jacquard, with which individual warp threads may be separately controlled. Other variations appear in looms for such products as narrow fab- rics, carpets, and pile fabrics. In the Sulzer weaving machine, a special filling carrier replaces the conventional shuttle. In the rapier, a flat, spring-like tape uncoils from each side and meets in the mid- dle to transfer the grasp on the filling. In the water jet loom, a tiny jet of high-pressure water carries the filling through the shed of the warp. Other looms transport the filling with compressed air. Inc. ASHRAE, 2019 user. single for Licensed | {}
3d68e862-3058-4968-987c-cb5fba7e1c46 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 22.4 2019 ASHRAE Handbook-HVAC Applications (SI) High humidity increases the abrasion resistance of the warp. Weave rooms require 80 to 85% humidity or higher for cotton and up to 70% humidity for synthetic fibers. Many looms run faster when room humidity and temperature are precisely controlled. In the weave room, power distribution is uniform, with an aver- age concentration somewhat lower than in spinning. The rough treatment of fibers liberates many minute particles of both fiber and size, thereby creating considerable amounts of airborne dust. In this high-humidity area, air changes average from four to eight per hour. Special provisions must be made for maintaining conditions during production shutdown periods, usually at a lower relative humidity. Knitting Typical knitted products are seamless articles produced on circu- lar machines (e.g., undershirts, socks, and hosiery) and those knitted flat (e.g., full-fashioned hosiery, tricot, milanese, and warp fabrics). Knitted fabric is generated by forming millions of interlocking loops. In its simplest form, a single end is fed to needles that are actu- ated in sequence. In more complex constructions, hundreds of ends may be fed to groups of elements that function more or less in parallel. Knitting yarns may be either single strand or multifilament and must be of uniform high quality and free from neps or knots. These yarns, particularly the multifilament type, are usually treated with special sizes to provide lubrication and to keep broken filaments from stripping back. The need for precise control of yarn tension, through controlled temperature and relative humidity, increases with the fineness ofthe product. For example, in finer gages of full-fashioned hosiery, a 1 K change in temperature is the limit, and a 10% change in humidity may change the length of a stocking by 75 mm. For knitting, desir- able room conditions are approximately 24°C db and 45 to 65% rh. Dyeing and Finishing Finishing, which is the final readying of a mill product for its particular market, ranges from cleaning to imparting special char- acteristics. The specific operations involved vary considerably, depending on the type of fiber, yarn, or fabric, and the end product usage. Operations are usually done in separate plants. In addition to normal heating, ventilation, and fog removal systems, these areas also require removal ofhot, dusty, and toxic fumes from continuous ovens and tenters. Packaged chilling equipment is sometimes used to control temperatures of preshrink chemicals, dyes, and coatings that are applied to textiles and yarns before finishing. Some of these processes require corrosive-resistant materials and equipment. Inspection is the only finishing operation to which air condi- tioning is regularly applied, although most of the others require ventilation. Finishing operations that use wet processes usually keep their solutions at high temperatures and require special ven- tilation to prevent destructive condensation and fog. Spot cooling of workers may be necessary for large releases of sensible, latent, or radiant heat. 5. AIR-CONDITIONING DESIGN There are many diverse and special needs of specific areas of the textile process. Generally, a meeting with the owner' s representa- tive(s), local code officials, and the owner's insurance company is helpful in satisfying the particular requirements of the process, insurance companies, and local officials. HVAC engineers design- ing textile projects need to have a thorough understanding ofthe fol- lowing HVAC system elements: · Psychrometric process in spray systems · Humidification and dehumidification · Draft-free air distribution · Fog control · Water and air filters · Dust collectors · Industrial ductwork · Large built-up air handlers · Large water chillers · Cooling towers · Industrial piping systems · Pumping · Corrosion-resistant metallurgy · Large centrifugal air compressors · Programmable logic controllers and supervisory control and data acquisition (SCADA) systems · W ater treatment in open sump systems Consultation with mechanical contracting companies experi- enced with building and installing textile-related systems provides great insight to these attributes. Thorough understanding of the pro- cesses to be conditioned; precise calculations; familiarity with codes, regulations, and current industry standards; as well as rea- sonable owner/engineer/contractor relationships and adherence to the owner's budget are necessary for successful projects. Air washers are especially important in textile manufacturing and may be either conventional low-velocity or high-velocity units in built-up systems. Unitary high-velocity equipment using rotating eliminators, although no longer common, is still found in some plants. Contamination of air washers by airborne oils often dictates the separation of air washers and process chillers by heat exchangers, usually of the plate or frame type. Open-Sump Chilled- w ater Systems Itis common practice to use open sumps in textile processing with air washer air-handling units. Open sumps present a unique problem for the removal of lint from the basins. Many systems return the air from spinning areas, and this air carries lint and free fibers from the spinning process. These fibers are typically not completely removed by central collectors (see Figure 3). In older facilities, the central col- lectors may be totally ineffective or nonexistent. A rotating drum fil- ter is commonly used to remove lint fibers from the sumps of air washers to prevent clogging of spray nozzles and fouling of spray media. The rotating drum filters are semisubmerged in the sump and are fitted with a vacuum system that traverses the part of the drum that is exposed to air, removing the lint from the drum surface and transporting it through a high-pressure blower to a bag house, where water is separated and the lint collected for future disposal. Many textile plants have an open sump for return of chilled water from the air washers (see A in Figure 2). The chilled-water pumps draw out of these sumps through a screened inlet, C, for return of chilled water to the chillers. In designing the inlet screen, care must be taken to avoid a configuration that might lead to pump cavitation. Rotating drum filters should also be considered for these sumps to prevent fouling of chiller tubes by lint that passes the screens. These sumps must be carefully sized to receive the volume of water con- tained in the system when the air washers are shut off and their sumps drain down. Integrated Systems Many mills use a refined air washer system that combines the air-conditioning system and the collector system (see the section on Collector Systems) into an integrated unit. Air handled by the col- lector system fans and any air required to make up total return air are delivered back to the air-conditioning apparatus through a cen- tral duct. The quantity of air returned by individual yarn-processing machine cleaning systems must not exceed the quantity of air- conditioning supply air. Air discharged by these individual suction systems is carried by return air ducts directly to the air-conditioning system. Before entering the duct, some of the cleaning system air Inc. ASHRAE, 2019 user. single for Licensed | {}
683cbe8c-7b3a-4920-98a9-47576a4bf7ab | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Textile Processing Plants 22.5 ![image](/image/placeholder) U S (X し : w # � ☏ A N N 4 SPINNING 과 SPINNING FRAME FRAME aty RETURN AIR SEE ENLARGED DETAIL BELOW SERVICE BAY SPINNING ROOM INTAKE ORIFICES + DUCT RETURN AIR Fig. 2 Mechanical Spinning Room with Combined Air-Conditioning and Collector System passes over the yarn-processing machine drive motor and through a special enclosure to capture heat losses from the motor. When integrated systems occasionally exceed the supply air requirements ofthe area served, the surplus air must be reintroduced after filtering. Individual suction cleaning systems that can be integrated with air conditioning are available for cards, drawing frames, lap wind- ers, combers, roving frames, spinning frames, spoolers, and warp- ers. The following advantages result from this integration: · With a constant air supply, the best uniform air distribution can be maintained year-round. · Downward airflow can be controlled; crosscurrents in the room are minimized or eliminated; drift or fly from one process to another is minimized or eliminated. Room partitioning between systems serving different types of manufacturing processes fur- ther enhances the value of this integration by controlling room air pattern year-round. · Heat losses of the yarn-processing frame motor and any portion of the processing frame heat captured in the duct, as well as the heat ofthe collector system equipment, cannot affect room conditions; hot spots in motor alleys are eliminated, and although this heat goes into the refrigeration load, it does not enter the room. As a result, the supply air quantity can be reduced. · Uniform conditions in the room improve production; conditioned air is drawn directly to the work areas on the machines, minimiz- ing or eliminating wet or dry spots. · Maximum cleaning use is made of the air being moved. A guide for cleaning air requirements follows: ¦ Pickers ¦ 1200 to 1900 L/s per picker ¦ ¦ --- ¦ --- ¦ ¦ Cards ¦ 300 to 700 L/s per card ¦ ¦ Spinning ¦ 2 to 4 L/s per spindle ¦ ¦ Spooling ¦ 19 L/s per spool ¦ Collector Systems A collector system is a waste-capturing device that uses many ori- fices operating at high suction pressures. Each piece of production machinery is equipped with suction orifices at all points of major lint generation. The captured waste is generally collected in a fan and fil- ter unit located either on each machine or centrally to accept waste from a group of machines. A collector in the production area may discharge waste-filtered air either back into the production area or into a return duct to the air-conditioning system. It then enters the air washer or is relieved through dampers to the outdoors. Figure 2 shows a mechanical spinning room with air-conditioning and collector systems combined into an integrated unit. In this case, the collector system returns all of its air to the air-conditioning Inc. ASHRAE, 2019 user. single for Licensed | {}
16a4495b-156f-4609-b605-f0794134b541 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 22.6 2019 ASHRAE Handbook-HVAC Applications (SI) system. If supply air from the air-conditioning system exceeds the maximum that can be handled by the collector system, additional air should be returned by other means. Figure 2 also shows return air entering the air-conditioning sys- tem through damper T, passing through air washer H, and being delivered by fan J to the supply duct, which distributes it to maintain conditions within the spinning room. At the other end of each spin- ning frame are unitary filter-collectors consisting of enclosure N, collector unit screen 0, and collector unit fan P. Collector fan P draws air through the intake orifices spaced along the spinning frame. This air passes through the duct that runs length- wise to the spinning frame, passes through screen 0, and is then dis- charged into the enclosure base (beneath the fan and screen). The air quantity is not constant; it drops slightly as material builds up on the filter screen. Because the return air quantity must remain constant, and the air quantity discharged by fan P is slightly reduced at times, relief open- ings are necessary. Relief openings also may be required when the return air volume is greater than the amount of air the collector suc- tion system can handle. The discharge offan P is split, so part ofthe air cools the spinning frame drive motor before rejoining the rest ofthe air in the return air tunnel. Regardless of whether the total return air quantity enters the return air tunnel through collector units, or through a combination of collector units and floor openings beneath spinning frames, return air fan R delivers it into the apparatus, ahead of return air damper T. Consideration should be given to filtering the return air prior to its delivery into the air-conditioning apparatus. Mild-season operation causes more outdoor air to be introduced through damper U. This air is relieved through motorized damper S, which opens gradually as outdoor damper U opens, while return damper T closes in proportion. All other components perform as typical central station air-washer systems. A system having the general configuration shown in Figure 2 may also be used for carding; the collector system portion of this arrangement is shown in Figure 3. A central collector filters the lint-laden air taken from multiple points on each card. This air is discharged to return air duct A and is then either returned to the air-conditioning system, exhausted outdoors, or returned directly to the room. A central collector filter may also be used with the spinning room system of Figure 2. Inc. ASHRAE, 2019 user. single for Licensed Textile plants served by generally uniform air distribution may still require special handling for areas of load concentration. Air Distribution Continuous Spinning Area. Methods of distribution are diverse and generally not critical. However, spot cooling or localized heat removal may be required. This area may be cooled by air condition- ing, evaporative cooling, or ventilation. Chimney (Quench Stack). Carefully controlled and filtered air or other gas is delivered to the chimneys; it is returned for ![image](/image/placeholder) COLLECTOR RETURN AIR FILTER DUCT A SUPPLY DUCT CARD CARD Fig. 3 Central Collector for Carding Machine conditioning and recovery of any valuable solvents present. Dis- tribution of the air is of the utmost importance. Non-uniform tem- perature, humidity, or airflow disturbs the yarn, causing variations in fiber diameter, crystalline structure, and orientation. A fabric made of such fibers streaks when dyed. In melt spinning, the solvent concentration in the chimney air must be maintained below its explosive limit. Even with this provi- sion, care is still required to prevent vapors from being ignited by a spark or flame. The air-conditioning system must be reliable, because interruption of the spinning causes the solution to solidify in the spinnerets. Wind-Up or Take-Up Areas of Continuous Spinning. A heavy air-conditioning load is developed. Air is often delivered through branch ducts alongside each spinning machine. Low-velocity, low- aspiration diffusers must be sized to avoid agitating delicate fibers. Draw-Twist or Draw- Wind Areas of Fiber Manufacture. A heavy air-conditioning load is developed. Distribution, diffusion, and return systems are similar to those for the continuous spinning take-up area. Opening and Picking. Usually, opening and picking require only a uniform distribution system. The area is subject to shutdown ofmachinery during portions ofthe day. Generally, an all-air system with independent zoning is installed. Carding. A uniform distribution system is generally installed. There should be little air movement around the web in cotton card- ing. Central lint collecting systems are available but must be incor- porated into the system design. An all-air system is often selected for cotton carding. In wool carding, there should be less air movement than in cotton carding, not only to avoid disturbing the web, but also to reduce cross-contamination between adjacent cards. This is because differ- ent colors of predyed wool may be run side by side on adjacent cards. A split system (i.e., separate systems for each card) may be considered for wool carding to reduce air movement. The method of returning air is also critical for achieving uniform conditions. Mechanical Spinning Areas. A heavy air-conditioning load is generated, consisting of spinning frame power uniformly dis- tributed along the frame length and frame driver motor losses concentrated in the motor alley at one end of the frame. Drawing and Roving. Generally, a uniform distribution all- air system works well. Supply air ducts should run across the frames at right angles. Sidewall outlets between each of the two adjacent frames then direct the supply air down between the frames, where conditions must be maintained. Where concentrated heat loads occur, as in a double motor alley, placement of a supply air duct directly over the alley should be considered. Sidewall outlets spaced along the bottom of the duct diffuse air into the motor alley. The collecting system, whether unitary or central, with intake points distributed along the frame length at the working level, as- sists in pulling supply air down to the frame, where maintenance of conditions is most important. A small percentage of the air handled by a central collecting system may be used to convey the collected lint and yarn to a central point, thus removing that air from the spin- ning room. Machine design in spinning systems sometimes requires inter- floor air pressure control. Winding and Spooling. Generally, a uniform distribution, all-air system is used. Twisting. This area has a heavy air-conditioning load. Dis- tribution considerations are similar to those in spinning. Either all-air or split systems are installed. w arping. This area has a very light load. Long lengths of yarn may be exposed unsupported in this area. Generally, an all- air system with uniform distribution is installed. Diffusers may be of the low-aspiration type. Return air is often near the floor. | {}
3579314e-7fd1-4df5-a2db-3947a573d7ea | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Textile Processing Plants 22.7 Weaving. Generally, a uniform distribution system is necessary. Synthetic fibers are more commonly woven than natural fibers. The lower humidity requirements of synthetic fibers allow the use of an all-air system rather than the previously common split system. When lower humidity is coupled with the water jet loom, a high latent load results. Health Considerations For detailed information on control of industrial contami- nants, see Chapter 29 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment. Control of Oil Mist. When textiles coated with lubricating oils are heated above 93°C in drawing operations in ovens, heated rolls, tenterframes, or dryers, an oil mist is liberated. If the oil mist is not collected at the source of emission and disposed of, a slightly odor- ous haze results. Various devices have been proposed to separate oil mist from the exhaust air, such as fume incinerators, electrostatic precipitators, high-energy scrubbers, absorption devices, high-velocity filters, and condensers. Spinning operations that generate oil mist must be provided with a high percentage (30 to 75%) of outdoor air. In high-speed spin- ning, 100% outdoor air is commonly used. Operations such as drum cooling and air texturizing, which could contaminate the air with oil, require local exhausts. Control of Monomer Fumes. Separate exhaust systems for monomers are required, with either wet- or dry-type collectors, depending on the fiber being spun. For example, caprolactam nylon spinning requires wet exhaust scrubbers. Control of Hazardous Solvents. Provisions must be made for the containment, capture, and disposal of hazardous solvents. Control of Cotton Dust. Byssinosis, also known as brown or white lung disease, is believed to be caused by a histamine-releasing substance in cotton, flax, and hemp dust. In the early stages of the disease, a cotton worker returning to work after a weekend experi- ences difficulty in breathing that is not relieved until later in the week. After 10 to 20 years, the breathing difficulty becomes contin- uous; even leaving the mill does not provide relief. The U.S. Department of Labor enforces an OSHA standard of lint-free dust. The most promising means of control are improved exhaust procedures and filtration of recirculated air. Lint particles are 1 to 15 m in diameter, so filtration equipment must be effec- tive in this size range. Improvements in carding and picking that leave less trash in the raw cotton also help control lint. Noise Control. The noise generated by HVAC equipment can be significant, especially if the textile equipment is modified to meet present safety criteria. For procedures to analyze and correct the noise from ventilating equipment, see Chapter 49. Safety and Fire Protection Special Warning: Certain industrial spaces may contain flam- mable, combustible, and/or toxic concentrations of vapors or dusts under either normal or abnormal conditions. In spaces such as these, there are life-safety issues that this chapter may not completely address. Special precautions must be taken in accordance with requirements of recognized authorities such as the National Fire Protection Association (NFPA), the Occupational Safety and Health Administration (OSHA), and the American National Standards Institute (ANSI). In all situations, engineers, designers, and install- ers who encounter conflicting codes and standards must defer to the code or standard that best addresses and safeguards life safety. Oil mist can accumulate in ductwork and create a fire hazard. Periodic cleaning reduces the hazard, but provisions should be made to contain a fire with suppression devices such as fire-activated dampers and interior duct sprinklers. 6. ENERGY CONSERV A TION The following are some steps that can be taken to reduce energy consumption: · Applying heat recovery to water and air · Automating high-pressure dryers to save heat and compressed air · Decreasing hot-water temperatures and increasing chilled-water temperatures for rinsing and washing in dyeing operations · Replacing running washes with recirculating washes where practical · Changing double-bleaching procedures to single-bleaching where practical · Eliminating rinses and final wash in dye operations where practical · Drying by "bump and run" process · Modifying drying or curing oven air-circulation systems to pro- vide counterflow · Using energy-efficient electric motors and textile machinery · For drying operations, using discharge air humidity measure- ments to control the exhaust versus recirculation rates in full economizer cycles BIBLIOGRAPHY ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. Hearle, J., and R.H. Peters. 1960. Moisture in textiles. Textile Book Publish- ers, New York. Kirk and Othmer, eds. 2004. Kirk-Othmer encyclopedia of chemical tech- nology, 5th ed., vol. 9. Wiley-Interscience, New York. Nissan, Q.H. 1959. Textile engineering processes. Textile Book Publishers, New York. Press, J.J., ed. 1959. Man made textile encyclopedia. Textile Book Publish- ers, New York. Sachs, A. 1987. Role of process zone air conditioning. Textile Month (Octo- ber):42. Schicht, H.H. 1987. Trends in textile air engineering. Textile Month (May):41. Inc. ASHRAE, 2019 user. single for Licensed Related Commercial Resources | {}
1fe51ffe-7bb6-41f0-ab62-c28498dbe1cb | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 23 PHOTOGRAPHIC MATERIAL FACILITIES ¦ Storing Unprocessed Photographic Materials ¦ 23.1 ¦ ¦ --- ¦ --- ¦ ¦ Processing and Printing Photographic Materials ¦ 23.1 ¦ ¦ Storing Processed Film and Paper ¦ 23.3 ¦ P ROCESSING and storing sensitized photographic products requires temperature, humidity, and air quality control. Manu- facturers of photographic products and processing equipment pro- vide specific recommendations for facility design and equipment installation that should always be consulted. This chapter contains general information that can be used in conjunction with these rec- ommendations. See Chapter 31 for information on general industrial ventilation. Special Warning: Certain industrial spaces may contain flam- mable, combustible, and/or toxic concentrations of vapors or dusts under either normal or abnormal conditions. In spaces such as these, there are life-safety issues that this chapter may not completely address. Special precautions must be taken in accordance with requirements ofrecognized authorities such as the National Fire Pro- tection Association (NFPA), the Occupational Safety and Health Administration (OSHA), and the American National Standards Institute (ANSI). In all situations, engineers, designers, and install- ers who encounter conflicting codes and standards must defer to the code or standard that best addresses and safeguards life safety. 1. STORING UNPROCESSED PHOTOGRAPHIC MATERIALS Virtually all photosensitive materials deteriorate with age; the rate of photosensitivity deterioration depends largely on the storage conditions. Photosensitivity deterioration increases both at high temperature and at high relative humidity and usually decreases at lower temperature and humidity. High humidity can accelerate loss of sensitivity and contrast, increase shrinkage, produce mottle (spots or blotches of different shades or colors), cause softening of the emulsion (which can lead to scratches), and promote fungal growth. Low relative humidity can increase the susceptibility of the film or paper to static markings, abrasions, brittleness, and curl. Because different photographic products require different han- dling, product manufacturers should be consulted regarding proper temperature and humidity conditions for storage. Refrigerated stor- age may be necessary for some products in some climates. Products not packaged in sealed vaportight containers are vul- nerable to contaminants. These products must be protected from solvent, cleanser, and formaldehyde vapors (emitted by particle- board and some insulation, plastics, and glues); industrial gases; and engine exhaust. In hospitals, industrial plants, and laboratories, all photosensitive products, regardless of their packaging, must be protected from x-rays, radium, and radioactive sources. For exam- ple, films stored 8 m away from 100 mg of radium require the pro- tection of 90 mm of lead. 2. PROCESSING AND PRINTING PHOTOGRAPHIC MA TERIALS Ventilation with clean, fresh air maintains a comfortable working environment and prevents vapor-related complaints and health prob- The preparation of this chapter is assigned to TC 9.2, Industrial Air Conditioning. lems. It is also necessary for high-quality processing, safe handling, and safe storage of photographic materials. Processing produces odors, vapors, high humidity, and heat (from lamps, electric motors, dryers, mounting presses, and high- temperature processing solutions). Thus, it is important to supply plentiful clean, fresh air at the optimum temperature and relative humidity to all processing rooms. ASHRAE Standard 62. 1 speci- fies 5.0 L/(s · m2) of exhaust for darkrooms in Table 6-4. Air Conditioning for Preparatory Operations During receiving operations, exposed film is removed from its protective packaging for presplicing and processing. Presplicing combines many individual rolls of film into a long roll to be pro- cessed. At high relative humidity, photographic emulsions become soft and can be scratched. At excessively low relative humidity, the film base is prone to static, sparking, and curl deformation. The pre- splice work area should be maintained at 50 to 55% rh and 21 to 24°C db. Room pressures should cascade downward from areas of higher air quality to areas of lower air quality (clean to dirty). Air Conditioning for Processing Operations Processing exposed films or paper involves using a series of tem- pered chemical and wash tanks that emit heat, humidity, and vapors or gases (e.g., water vapor, acetic acid, benzyl alcohol, ammonia, sulfur dioxide). Room exhaust must be provided, along with local exhaust at noxious tanks. To conserve energy, air from pressurized presplice rooms can be used as makeup for processing room exhaust. Further supply air should maintain the processing space at a maxi- mum of 24°C dry bulb and 50 to 55% rh. The processed film or paper proceeds from the final wash to the dryer, which controls the moisture remaining in the product. Too lit- tle drying causes film to stick when wound, whereas too much dry- ing causes undesirable curl. Drying can be regulated by controlling drying time, humidity, and temperature. The volume of supply air should be sufficient to achieve the design condition. Airflow should be diffused or distributed to avoid objec- tionable drafts. Apart from causing personnel discomfort, drafts can cause dust problems and disturb the surface temperature uniformity of drying drums and other heated equipment. Supply and return air openings should be properly positioned (1) for good mixing and dilu- tion of the room air, (2) to ensure efficient removal of fugitive vapors, and (3) to avoid short-circuiting of supply air into return or exhaust air openings. For automated processing equipment, tempered outdoor air should be supplied from the ceiling above the feed or head end of the machine at a minimum rate of 70 L/s per machine (Figure 1). If the machine extends through a wall into another room, both rooms need to be exhausted. An exhaust system should be installed to remove humid or heated air and chemical vapors directly to the outdoors (process streams typ- ically must comply with regulations pursuant to the Clean Air Act). The room air from an open machine or tank area should be exhausted to the outdoors at a rate sufficient to achieve at least the vapor dilution levels recommended by the American Conference of Governmental Industrial Hygienists (ACGIH 2010). An exhaust rate higher than the supply rate produces a negative pressure and makes the escape of 23.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
0a0d4662-c4b3-42f5-85cf-c362835944e4 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 23.2 2019 ASHRAE Handbook- - HVAC Applications (SI) vapors or gases to adjoining rooms less likely. Depending on the pro- cess chemistry, local exhaust hoods may be needed at uncovered sta- bilizer tanks or at the bleach fix tanks (Figure 1 ). The exhaust opening should be positioned so that the flow of exhausted air is away from the operator, as illustrated in Figure 2. This air should not be recirculated. The exhaust opening should always be as close as possible to the source of the contaminant for efficient removal [see ACGIH (2010) for more information]. For a processing tank, the exhaust hood should have a narrow opening at the back of, level with, and as wide as the top edge of the tank. Processing tanks are often covered to reduce evaporation of heated processing chemical solutions (approximately 38°C). Covers on photographic processing equipment and chemical stor- age tanks can effectively minimize the amount of gases, vapors, or mists that enter the work area. If the processing tanks are enclosed and equipped with an exhaust connection, the minimum room air supply and exhaust rates may be reduced compared to an open tank (Figure 3). A sulfide-toning sink should have a local exhaust hood to vent hydrogen sulfide. However, sulfide toners are rarely used now except for some specialized art processing and archival microfilm ![image](/image/placeholder) EXHAUST TO OUTDOORS SUPPLY AIR 3 3 Fig. 1 Open Machine Ventilation ![image](/image/placeholder) EXHAUST TO OUTDOORS Fig. 2 Open-Tray Exhaust Ventilation from Processing Sink processing. The exhaust duct must be placed on the side opposite the operator so that vapor is not drawn toward the operator's face. Air distribution to the drying area must provide an acceptable environment for operators as discussed in Chapter 9 of the 2017 ASHRAE Handbook-Fundamentals and ACGIH (2010). Exposed sides of the dryer should be insulated as much as is practical to reduce the large radiant and convected heat gain to the space. Exhaust grilles above the dryer can directly remove much of its rejected heat and moisture. Supply air should be directed to offset the remaining radiant heat gain to the space. Using processor dryer heat to preheat cold incoming air during winter conditions can save energy. An economic evaluation is nec- essary to determine whether the energy savings justify the addi- tional cost of the heat recovery equipment. A canopy exhaust hood over the drying drum of continuous paper processors extracts heat and moisture. Itis important to follow the processing equipment manufacturer's recommendations for venting the dryer section of the processor. Whenever possible, dryer vents should be exhausted to the outdoors to prevent build-up of excessive temperature and humidity in the workplace. When drying motion picture film, exhaust should draw off vapor from the solvent and wax mixture that is normally applied for lubri- cation. Air Conditioning for the Printing/ Finishing Operation In printing, where a second sensitized product is exposed through the processed original, the amount of environmental control needed depends on the size and type of operation. For small-scale printing, close control of the environment is not necessary, except to minimize dust. In photofinishing plants, printers for colored prod- ucts emit substantial heat. The effect on the room can be reduced by removing the lamphouse heat directly. Computer-controlled elec- tronic printers transport the original film and raw film or paper at high speed. Proper temperature and humidity are especially import- ant because, in some cases, two or three images from many separate films may be superimposed in register onto one film. For best results, the printing room should be maintained at between 21 and 24°C and at 50 to 60% rh to prevent curl, deformation, and static. Curl and film deformation affect the register and sharpness of the images produced. Static charge should be eliminated because it leaves static marks and may also attract dust to the final product. Mounting of reversal film into slides is a critical finishing oper- ation requiring a 21 to 24°C db temperature with 50 to 55% rh. ![image](/image/placeholder) EXHAUST TO OUTDOORS SUPPLY AIR Fig. 3 Enclosed Machine Ventilation Inc. ASHRAE, 2019 user. single for Licensed | {}
d1c65798-ab5a-41e9-9492-36ba3c3858cc | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Photographic Material Facilities 23.3 Digital printing operations use equipment that generates signifi- cant heat. An exhaust system can be directly connected to the laser printer to remove heat at a flow rate specified by the equipment manufacturer. Sufficient room ventilation is required so that appli- cable occupational exposure limits are not exceeded and a favorable operating environment is maintained. Particulates in Air Air conditioning for most photographic operations requires 85% efficiency disposable bag-type filters with 30% efficiency prefilters to extend the bag filter life. In critical applications (such as high- altitude aerial films) and for microminiature images, filtering of for- eign matter is extremely important. These products are handled in a laminar airflow room or workbench with 95% efficiency HEPA fil- ters plus 30% efficiency disposable prefilters. Other Exhaust Requirements A well-ventilated room should be provided for mixing the chem- icals used in color processing and high-volume black-and-white work. The room should be furnished with movable exhaust hoods that provide a capture velocity as defined in ACGIH's (2010) Indus- trial Ventilation for the worst-case scenario. Modern photographic minilabs often use canisters of premixed processing solutions, so no chemical mixing is necessary. If prints are lacquered regularly, a spray booth is needed. Con- centrated lacquer spray is both hazardous and very objectionable to personnel; spray booth exhaust must be discharged outdoors. Processing Temperature Control Low processing volumes are typically handled in minilabs, which are often installed in retail locations. Minilabs are usually self-contained and equipped with temperature controls, heaters, and pumps. Typically, the owner only has to connect the minilab to water, electricity, exhaust (thimble connection), and a drain. Higher-volume processing is handled with processors that come from the manufacturer complete with controls, heat exchangers, pumps, and control valves designed for the process that the owner has specified. Electricity, hot water, cold water, drainage, and steam may be required, depending on the manufacturer, who typically pro- vides the specifications for these utilities. 3. STORING PROCESSED FILM AND PAPER Storage of developed film and paper differs from storage of raw stock, because the developed materials are no longer photo- sensitive, are seldom sealed against moisture, and are generally stored for much longer periods. Required storage conditions de- pend on (1) the value of the records, (2) length of storage time, (3) whether the films are on nitrate or safety base, (4) whether the pa- per base is resin coated, and (5) type of photographic image. Photographic materials must be protected against fire, water, mold, chemical or physical damage, high relative humidity, and high temperature. Relative humidity is much more critical than tem- perature. High relative humidity can cause films to stick together, (particularly roll films, but also sheet films). High humidity also damages gelatin, encourages the growth of mold, increases dimen- sional changes, accelerates the decomposition of nitrate support, and accelerates the deterioration of both black-and-white and color images. Low relative humidity causes a temporary increase in curl and decrease in flexibility, but when the humidity rises again, these conditions are usually reversed. An exception occurs when motion picture film is stored for a long time in loosely wound rolls at very low humidities. The curl causes the film roll to resemble a polygon rather than a circle when viewed from the side. This spokiness occurs because a highly curled roll of film resists being bent in the length direction when itis already bent in the width direction. When a spoky roll is stored for a long time, the film flows permanently into the spoky condition, resulting in film distortion. Very low relative humidity in storage may also cause the film or paper to crack or break if handled carelessly. Low temperature (-23 to 10°C) is desirable for film and paper storage if (1) the relative humidity of the cold air is controlled, and (2) the material can be sufficiently warmed (for 2 to 8 h) before opening to prevent moisture condensation. High temperature can accelerate film shrinkage, which may produce physical distortions and the fading of dye images. High temperature is also detrimental to the stability of nitrate film. Film Longevity The American National Standards Institute (ANSI Standard IT9.11) defines longevities of films with a life expectancy (LE) rating. The LE rating is the minimum number of years that infor- mation can be retrieved if the subject film is stored under long-term storage conditions. In order to achieve the maximum LE rating, a product must be stored under long-term storage conditions. Polyes- ter black-and-white silver gelatin films have an LE rating of 500, and acetate black-and-white silver gelatin films have an LE rating of 100. No LE ratings have been assigned to color films or black-and- white silver papers. Medium-term storage conditions have been defined for materials that are to retain their information for at least 10 years. Medium-Term Storage Rooms for medium-term storage of safety base film should be protected from accidental water damage by rain, flood, or pipe leaks. Air conditioning with controlled relative humidity is desir- able but not always essential in moderate climates. Extremes of rel- ative humidity are detrimental to film. The most desirable storage relative humidity for processed film is about 50%, although 30 to 60% is satisfactory. Air conditioning is required where the relative humidity of the storage area exceeds 60% for any appreciable period. For a small room, a dehumidifier may be used if air conditioning cannot be installed. The walls should be coated with a vapor retarder, and the controlling humid- istat should be set at about 40% rh. If the prevailing relative humidity is under 25% for long periods and problems from curl or brittleness are encountered, humidity should be controlled by a mechanical humidifier with a controlling humidistat set at 40%. For medium-term storage, a room temperature between 20 and 25°C is recommended. Higher temperatures may cause shrinkage, distortion, and dye fading. Occasional peak temperatures of 35°C should not have a serious effect. Color films should be stored below 10°C to reduce dye fading. Films stored below the ambient dew point should be allowed to warm up before being opened to prevent moisture condensation. An oxidizing or reducing atmosphere may deteriorate the film base and gradually fade the photographic image. Oxidizing agents may also cause microscopically small colored spots on fine-grain film such as microfilm (Adelstein et al. 1970). Typical gaseous con- taminants include hydrogen sulfide, sulfur dioxide, peroxides, ozone, nitrogen oxides, and paint fumes. If these fumes are present in the intended storage space, they must be eliminated, or the film must be protected from contact with the atmosphere. Long-Term Storage For films or records that are to be preserved indefinitely, long-term storage conditions should be maintained. The recommended space relative humidity ranges from 20 to 50% rh, depending on the film type. When several film types are stored within the same area, 30% rh is a good compromise. The recommended storage temperature is below 21°C. Low temperature aids preservation, but if the storage Inc. ASHRAE, 2019 user. single for Licensed | {}
1bc23483-6af7-4c73-b8b5-19ce3cbb7b20 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 23.4 Inc. ASHRAE, 2019 user. single for Licensed 2019 ASHRAE Handbook-HVAC Applications (SI) temperature is below the dew point of the outdoor air, the records must be allowed to warm up in a closed container before they are used, to prevent moisture condensation. Temperature and humidity conditions must be maintained year-round and should be continu- ously monitored. Requirements of a particular storage application can be met by any one of several air-conditioning equipment combinations. Standby equipment should be considered. Sufficient conditioned outdoor air should be provided to keep the room under a slight pos- itive pressure for ventilation and to retard the entrance of untreated air. The air-conditioning unit should be located outside the vault for ease of maintenance, with precautions taken to prevent water leak- age into the vault. The conditioner casing and all ductwork must be well insulated. Room conditions should be controlled by a dry-bulb thermostat and either a wet-bulb thermostat, humidistat, or dew- point controller. Air-conditioning installations and fire dampers in ducts carrying air to or from the storage vault should be constructed and main- tained according to National Fire Protection Association (NFPA) recommendations for air conditioning (NFPA Standard 90A) and for fire-resistant file rooms (NFPA Standard 232). All supply air should be filtered with noncombustible HEPA filters to remove dust, which may abrade the film or react with the photographic image. As with medium-term storage, gaseous con- taminants such as paint fumes, hydrogen sulfide, sulfur dioxide, peroxides, ozone, and nitrogen oxides may cause slow deterioration of the film base and gradual fading of the photographic image. When these substances cannot be avoided, an air scrubber, activated carbon adsorber, or other purification method is required. Films should be stored in metal cabinets with adjustable shelves or drawers and with louvers or openings located to facili- tate circulation of conditioned air through them. The cabinets should be arranged in the room to permit free circulation of air around them. All films should be protected from water damage due to leaks, fire sprinkler discharge, or flooding. Drains should have sufficient capacity to keep the water from sprinkler discharge from reaching a depth of 75 mm. The lowest cabinet, shelf, or drawer should be at least 150 mm off the floor and constructed so that water cannot splash through the ventilating louvers onto the records. When fire-protected storage is required, the film should be kept in either fire-resistant vaults or insulated record containers (Class 150). Fire-resistant vaults should be constructed in accordance with NFPA Standard 232. Although the NFPA advises against air condi- tioning in valuable-paper record rooms because of the possible fire hazard from outside, properly controlled air conditioning is essen- tial for long-term preservation of archival films. The fire hazard introduced by the openings in the room for air-conditioning ducts may be reduced by fire and smoke dampers activated by smoke detectors in the supply and return ducts. Storage of Cellulose Nitrate Base Film Although photographic film has not been manufactured on cel- lulose nitrate (nitrocellulose) film base for several decades, many archives, libraries, and museums still have valuable records on this material. Preserving the cellulose nitrate film will be of con- siderable importance until the records have been printed on safety base. Cellulose nitrate film base is chemically unstable and highly flammable. It decomposes slowly but continuously even under nor- mal room conditions. The decomposition produces small amounts of nitric oxide, nitrogen dioxide, and other gases. Unless the nitro- gen dioxide can escape readily, it reacts with the film base, acceler- ating the decomposition (Carrol and Calhoun 1955). The rate of decomposition is further accelerated by moisture and is approxi- mately doubled with every 6 K increase in temperature. All nitrate film must be stored in an approved vented cabinet or vault. Nitrate films should never be stored in the same vault with safety base films because any decomposition of the nitrate film will cause decomposition of the safety film. Cans in which nitrate film is stored should never be sealed, because this traps the nitrogen dioxide gas. Standards for storing nitrate film have been established (NFPA Standard 40). The National Archives and the National Institute of Standards and Technology have also investigated the effect of a num- ber of factors on fires in nitrate film vaults (Ryan et al. 1956). The storage temperature should be kept as low as economically possible. The film should be kept at less than 50% rh. Temperature and humidity recommendations for the cold storage of color film in the following section also apply to nitrate film. Storage of Color Film and Prints All dyes fade in time. ANSI Standard IT9.11 does not define an LE for color films or black-and-white images on paper. However, many valuable color films and prints exist, and it is important to pre- serve them for as long as possible. Light, heat, moisture, and atmospheric pollution contribute to fading of color photographic images. Storage temperature should be as low as possible to preserve dyes. For maximum permanence of images, materials should be stored in light-tight sealed contain- ers or in moisture-proof wrapping materials at a temperature below freezing and at a relative humidity of 20 to 50%. The con- tainers should be warmed to room temperature before opening to avoid moisture condensation on the surface. Photographic films can be brought to the recommended humidity by passing them through a conditioning cabinet with circulating air at about 20% rh for about 15 min. An alternative is the use of a storage room or cabinet controlled at a steady (noncycled) low temperature and maintained at the rec- ommended relative humidity. This eliminates the necessity of sealed containers, but involves an expensive installation. The dye- fading rate decreases rapidly with decreasing storage temperature. Storage of Black-and- White Prints The recommended storage conditions for processed black-and- white paper prints should be obtained from the manufacturer. The optimum limits for relative humidity of the ambient air are 30 to 50%, but daily cycling between these limits should be avoided. A variation in temperature can drive relative humidity beyond the acceptable range. A temperature between 15 and 25°C is accept- able, but daily variations of more than 4 K should be avoided. Pro- longed exposure to temperatures above 30°C should also be avoided. The degradative processes in black-and-white prints can be slowed considerably by low storage temperature. Exposure to air- borne particles and oxidizing or reducing atmospheres should also be avoided, as mentioned for films. Storage of Digital Images A hard drive should only be used for temporary storage, because if that drive fails, the images could be lost forever. Digital files should be backed up on alternative media (e.g., CD-ROMs) for short-term storage. Because of rapid technological develop- ment, storage media systems in 10 to 20 years may not be compat- ible with current CD-ROMs. In addition, CDs are somewhat fragile and susceptible to damage and data loss ifnot handled prop- erly. Digital images can be stored as photographic prints; these can last for generations when stored properly as described in the pre- ceding sections. REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae | {}
5e82b7c2-5d6d-4d83-88e1-9b161a195a44 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Photographic Material Facilities 23.5 BIBLIOGRAPHY .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. Adelstein, P.Z., C.L. Graham, and L.E. West. 1970. Preservation of motion picture color films having permanent value. Journal of the Society of Motion Picture and Television Engineers 79(November):1011. ACGIH. 2010. Industrial ventilation: A manual of recommended practice, 27th ed. American Conference of Governmental Industrial Hygienists, Cincinnati, OH. ANSI. 1998. Imaging media- Processed safety photographic films- Storage. Standard IT9.11-98. American National Standards Institute, New York. ASHRAE. 2010. Ventilation for acceptable indoor air quality. ANSI/ ASHRAE Standard 62.1-2010. Carrol, J.F., and J.M. Calhoun. 1955. Effect of nitrogen oxide gases on pro- cessed acetate film. Journal ofthe Society ofMotion Picture and Televi- sion Engineers 64(September):601. NFPA. 2011. Storage and handling of cellulose nitrate film. ANSI/NFPA Standard 40-11. National Fire Protection Association, Quincy, MA. NFPA. 2009. Installation of air-conditioning and ventilating systems. ANSI/ NFPA Standard 90A-09. National Fire Protection Association, Quincy, MA. NFPA. 2007. Protection of records. ANSI/NFPA Standard 232-07. National Fire Protection Association, Quincy, MA. Ryan, J.V , J.W. Cummings, and A.C. Hutton. 1956. Fire effects and fire control in nitro-cellulose photographic-film storage. Building Materi- als and Structures Report 145. U.S. Department of Commerce, Wash- D.C. (April). ington, ANSI. 1996. Imaging materials Ammonia-processed diazo photographic film-Specifications for stability. ANSI/NAPM Standard IT9.5-96. American National Standards Institute, New York. Carver, E.K., R.H. Talbot, and H.A. Loomis. 1943. Film distortions and their effect upon projection quality. Journal of the Society of Motion Picture and Television Engineers 41(July):88. Kodak. 1997. Safe handling of photographic processing chemicals. Publica- tion J-98A. Eastman Kodak, Rochester, NY. Kodak. 2002. Indoor air quality and ventilation in photographic processing facilities. Publication J-314. Eastman Kodak, Rochester, NY. Kodak. 2003. Safe handling, storage, and destruction of nitrate-based motion picture films. Publication H-182. Eastman Kodak, Rochester, NY. Kodak. 2006. Health, safety, and environment. www.kodak.com/ek /US/en JEidei_Beimmily'snww.shipWaity Suby Subpyanementm /Health_Safety_and_Environment.htm. Kodak. 2005. Storage and care of Kodak photographic materials. Publica- tion E-30. Eastman Kodak, Rochester, NY. NFPA. 2007. Static electricity. Standard 77-07. National Fire Protection Association, Quincy, MA. UL. 2001. Tests for fire resistance of record protection equipment, 15th ed. Standard 72-01. Underwriters Laboratories, Northbrook, IL. Inc. ASHRAE, 2019 user. single for Licensed Related Commercial Resources | {}
ccdef4c0-50bf-4761-ac98-af2ddd7319c8 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 24 MUSEUMS, GALLERIES, ARCHIVES, AND LIBRARIES ¦ TERMINOLOGY ¦ 24.1 ¦ CONTROLS DESIGN ¦ 24.28 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ KEY CONSIDERATIONS ¦ 24.1 ¦ CONTROL EQUIPMENT ¦ 24.32 ¦ ¦ CONTEXT AND PREDESIGN ¦ 24.3 ¦ SYSTEM DESIGN AND SELECTION ¦ 24.33 ¦ ¦ OVERVIEW OF RISKS ¦ 24.7 ¦ CONSTRUCTION ¦ 24.42 ¦ ¦ ENVIRONMENTAL EFFECTS ON COLLECTIONS ¦ 24.8 ¦ COMMISSIONING ¦ 24.42 ¦ ¦ DESIGN PARAMETERS FOR PERFORMANCE ¦ ¦ TRAINING AND DOCUMENTA TION ¦ 24.42 ¦ ¦ TARGET SPECIFICATIONS ¦ 24.19 ¦ OPTIMIZATION ¦ 24.43 ¦ T designing, and implementing environmental strategies for long- HIS chapter presents best practices and advice on planning, term preservation of cultural heritage that also support access in an economically and environmentally responsible way. It aims to sup- port a holistic approach, taking into consideration the types of col- lections, buildings, and environmental control systems that can sustain appropriate conditions for specific collections with their own climate histories. It acknowledges that any strategy will have to be an integral part of heritage preservation as a whole. The chapter is applicable to museums, galleries, nonresidential historic buildings, reference libraries, and archives, as well as to both new and existing structures. It is not designed for buildings with public access that only hold collections not intended for preservation, such as school libraries. This chapter is primarily directed at HVAC engineers and facility managers involved with indoor climate control projects in cultural heritage institutions, including new construction and extensions, renovations and upgrades of existing systems, and the adjustment of climate control strategies towards sustainability. Because this chapter has been widely used by allied professionals in a much broader context, it informs all stakeholders involved in the decision- making process on designing and implementing environmental strat- egies for cultural heritage collections. These include, but are not lim- ited to, engineers, architects, collection owners, cultural heritage administrators, collection managers, conservators, conservation sci- entists, curators and registrars. The information in this chapter focuses on mechanical and, to a limited extent, nonmechanical approaches to the control of tempera- ture, relative humidity, and indoor air quality. Tables and graphs are used to provide clear and easy access to specific information, but the underlying text is necessary to understand the full context. 1. TERMINOLOGY The terminology used in this chapter derives from the profes- sional conservation field and, except where noted, is taken from the website of the American Institute for Conservation of Historic and Artistic Works (AIC 2018). Cultural property includes objects, collections, specimens, structures, or sites that have artistic, historic, scientific, religious, or social significance. Tangible heritage includes buildings, historic places, and mon- uments, as well as objects and collections significant to the archae- ology, architecture, science, or technology of a specific culture. The preparation of this chapter is assigned to TC 9.8, Large Building Air- Conditioning Applications. Intangible heritage, according to the United Nations Educa- tional, Scientific and Cultural Organization (UNESCO), includes traditions or living expressions inherited and passed on within a cul- ture, such as oral traditions, performing arts, social practices, rituals, festive events, knowledge, and practices concerning nature and the universe or the knowledge and skills to produce traditional crafts (UNESCO 2017a). Digital heritage includes valued knowledge or expressions that have been created digitally, or converted into digital form from exist- ing analogue resources (UNESCO 2017b). Preservation is protection of cultural property through activities that minimize chemical and physical deterioration and damage and that prevent loss of informational content. The primary goal of pres- ervation is to prolong the existence of cultural property. Conservation is the profession devoted to preservation of cul- tural property for the future. Conservation activities include exam- ination, documentation, treatment, and preventive care, supported by research and education. Preventive care (also called preventive conservation) is mitiga- tion of deterioration and damage to cultural property through the for- mulation and implementation of policies and procedures for the following: appropriate environmental conditions; handling and maintenance procedures for storage, exhibition, packing, transport, and use; integrated pest management; emergency preparedness and response; and reformatting/duplication. 2. KEY CONSIDERATIONS 2.1 HERITAGE "Heritage is our legacy from the past, what we live with today, and what we pass on to future generations. Our cultural and natural heritage are both irreplaceable sources of life and inspiration" (UNESCO 2018). Cultural heritage (tangible, intangible, and digital) is considered essential to the understanding and appreciation ofhumanity's diverse cultures and history. The importance of cultural heritage may be na- tional, regional, or local, and it may have symbolic, aesthetic, cul- tural, social, historical, scientific, and monetary values that are frequently impossible to estimate. Thus, access to and preservation of cultural heritage is important and may even be legally mandated. This chapter addresses preservation of tangible heritage: physical objects such as books and documents, works of art, historic tools and utilities, archaeological artifacts, specimens of natural history, examples of popular culture, products of various technologies, and historic buildings. 24.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
52b2ab37-7cb2-4ef0-9344-43517160a78a | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 24.2 2019 ASHRAE Handbook-HVAC Applications (SI) 2.2 CONTEXT Objects are often held by various collecting institutions such as museums, galleries, historic buildings, libraries, and archives. These collections have different uses, depending on the institution's mis- sion, and require specific management policies: in museums, the majority of a collection may be kept in storage with limited access, with a smaller portion on temporary or semipermanent display, often in showcases; in archives and libraries, almost all of the collections are in storage, from which they are pulled for research or exhibition; historic houses have most of their collections on permanent open dis- play. Individual objects from collections may be on short- or long- term loan to another organization. Collections may be housed in purpose-built buildings or existing buildings ofhistoric significance; sometimes, the building may be as (or more) important than the collection it houses. Most collections have been housed in existing buildings with climate control ranging from nonmechanical strategies (e.g., thermal insulation, window shutters) to mechanical systems (e.g., localized dehumidifiers, full HVAC). As a result, collections have a specific climate history that should be taken into consideration when reviewing environmental strategies. 2.3 INTERNA TIONAL STAND ARDS To facilitate loans, cultural heritage organizations often look to follow international guidelines on environmental control. It is there- fore important to be aware of the shift in thinking about sustainable collection management that is having a major impact on standards and guidelines. The U.K. National Museum Directors' Conference (NMDC 2008) focused on a long-term, broad plan for minimizing excessive energy use in the care of collections, reducing museums' overall carbon footprint. In turn, the International Group of Orga- nizers of Large-Scale Exhibitions (Bizot Group 2015) proposed a broader set of interim temperature and relative humidity guidelines for hygroscopic materials on loan, based on the NMDC proposal; their goal was to simplify international loans, reduce costs, and decrease the carbon footprint. This prompted the Association of Art Museum Directors (AAMD) to request input from the conservation community. As a response, the international professional organizations Inter- national Institute for Conservation of Historic and Artistic Works (IIC) and International Council of Museums Committee for Con- servation (ICOM-CC) published a declaration on environmental guidelines (IIC/ICOM-CC 2014). It states ·"The issue of museum sustainability is much broader than the dis- cussion on environmental standards, and needs to be a key under- lying criterion of future principles. · "Museums and collecting institutions should seek to reduce their carbon footprint and environmental impact to mitigate climate change, by reducing their energy use and examining alternative renewable energy sources. · "Care of collections should be achieved in a way that does not assume air conditioning (HVAC). Passive methods, simple tech- nology that is easy to maintain, air circulation and lower energy solutions should be considered. · "Risk management should be embedded in museum management processes. , 2.4 PRESERV A TION AND RISK MANAGEMENT Preservation of cultural heritage involves mitigating the impact of agents of deterioration (CCI 2018). It requires a trade-off among many factors and there is no single golden rule. Instead, risk man- agement approaches are used to arrive at an appropriate solution (see the section on Overview of Risks). For example, creating an environment for preserving the collection that causes problems for the building in which it is housed is not acceptable. It is possible to substantially slow deterioration caused by envi- ronmental agents of deterioration, thus fulfilling a major function of the collecting institution. However, doing so may conflict with another important function of cultural institutions: allowing public and scholarly access. Additionally, extremely tight control over all environmental parameters comes at a price few cultural institutions can justify or afford. Managing risk, not avoiding it altogether, is the objective. Climate-induced risks should be seen in context and relation to other risks to the preservation of cultural heritage, such as natural and human-caused disasters. Frequently, it is not the greatest risk to a collection, and available funds may be spent more effectively elsewhere. Therefore, it is fundamental that an institution develops an overall preservation strategy, of which its climate control is an integral part, based on a comprehensive risk assessment. A climate- control strategy should complement mitigation plans for other risks and should not in itself create a greater hazard. Consequently, greater risk reduction can come from ensuring the reliability of the system, rather than controlling minor excursions from defined cli- matic ranges. Most threats to collection preservation, in fact, can be addressed by properly maintained housing and professional sup- port. 2.5 SUST AINABILITY This chapter advocates environmental strategies and solutions for cultural heritage collections that support their access and pres- ervation in a responsible way (i.e., that are sustainable economi- cally, socially, and environmentally). It aims to inform strategies that sustain feasible climatic conditions for the foreseeable future and takes into consideration · An organization's mission and resources · The needs of the collection and its users · Building type · Local, regional, national, or international policies · Suitable environmental systems To design and implement appropriate climate control for a specif- ic collection, it is important to involve all appropriate stakeholders, which can vary by institution but may include engineers, architects, facility managers, security staff, cultural heritage administrators, ar- chivists, collection managers, conservators, conservation scientists, curators, and registrars. Administrators are responsible for fiscal and political decisions, whereas collection managers and conservators are responsible for providing access and care of the collection. Cu- rators build the collection and design exhibitions. Registrars oversee the legal paperwork and administration related to collection manage- ment. Security staff is critical to safekeeping of the collection. Therefore, a multidisciplinary approach is required to obtain a comprehensive overview of all aspects that impact an environmental management strategy, and some of this work should be carried out before an engineer is engaged in a project. Cultural institutions frequently operate as nonprofit organizations on tight budgets with limited human and/or technical resources. In- sisting on best-available technology for extraordinary humidity con- trol or comprehensive pollutant filtration may endanger long-term fulfillment of the institutional mission. From project inception, both the design objective and realistically available operation and maintenance resources must be considered. Having reliable monitoring data is crucial in the decision-making process. Before embarking on full mechanical control solutions, efforts should be made to use or integrate strategies that do not rely on mechanical control, including passive building solutions and non- Inc. ASHRAE, 2019 user. single for Licensed | {}
5178d59e-1980-44ad-a947-a387ef7e8b52 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Museums, Galleries, Archives, and Libraries 24.3 ![image](/image/placeholder) CONTEXT CONTEXT 1. MISSION/STRATEGY 2. DETERMINE NEEDS 3. CURRENT ENVIRONMENT SECTION 2.2, 3.1 SECTION 3.2, 4, 5 SECTION 3.3, 6.1 STAKEHOLDERS PREDESIGN LEAD CONSULT INFORM 4. OVERVIEW OF RISKS 1. DIR/CUR COLL, IFM ARCH, ENG, EXT SECTION 3.4, 4 2. COLL, IFM CUR ENG COLLECTION-BUILDING-PEOPLE ACCEPT AND CONTINUE TO 3. EXT/COLL, IFM CUR/EXT, SEC ARCH, ENG 5. ACCEPT OR MODIFY ENVIRONMENT MONITOR CONTEXT SECTION 2.4, 3.5 4. EXT/COLL, IFM ENG, ARCH, DIR MODIFY CUR, EXT, SEC 6. ANALYZE/PREDICT ACHIEVABLE ENVIRONMENT 5. DIR/CUR/COLL ARCH, ENG, IFM DIR SECTION 3.6, 5, 6 6. IFM, ENG,ARCH COLL, CUR, EXT, DIR, ALL 7. SET OBJECTIVES AND CRITERIA FIXING SMALL PREDESIGN ARCH SECTION 3.7, 5, 6 PROBLEMS, MAY NOT REQUIRE 7. COLL, IFM, ENG EXT, CUR, ARCH EXT OPTIONS 8. DEVELOP OPTIONS SECTION 3.8, 6 8. ARCH/ENG/EXT CUR, COLL, ALL SEC, IFM 9. ALL EXT, ALL ALL 9. REVIEW OPTIONS AND SELECT SECTION 3.9 10. DIR/CUR, COLL, SEC, EXT, CFO ENG, ARCH, IFM COMM IMPLEMENTATION 10. PREDESIGN BRIEF 11. ENG/ARCH IFM, COLL, SEC, CUR/DIR SECTION 3. 10 EXT COMM 12. ENG/ARCH, IFM, COLL, SEC, CUR/DIR DESIGN AND IMPLEMENTATION CFO COMM 11. DESIGN OF THE SOLUTION 13. COMM, ENG IFM, EXT, CFO SEC, COLL, CUR SECTION 3.11, 6.2, 7, 8 14. IFM, ENG COLL, SEC, ALL 12. PROCUREMENT AND CONSTRUCTION AND COMM SECTION 3.12, 7.2, 8, 9 15. ENG/EXT, IFM COLL, SEC CUR/DIR 13. START-UP AND COMMISSION (if HVAC) DESIGN SECTION 3.13, 9, 10 ALL All institution staff COLL Collections staff CUR Curatorial ARCH Architect (include collections DIR Director MONITORING SHOULD 14. TRAINING AND DOCUMENTATION IFM Internal facilities staff manager, conservator, ENG Engineer CONTINUE FOR SECTION 3.14, 8.1, 11 (e.g., facilities manager, registrar) EXT External experts QUALITY CONTROL AND Commissioning SEC Security building manager) COMM RECOMMISSIONING CFO Chief financial officer agent 15. EVALUATE AND REVISE These are roles, rather than job titles, and some may overlap. It is best to SECTION 3.15, 12 involve people early in the process rather than later. Not exhaustive. Fig. 1 Decision Diagram for Environmental Management Strategies in Museums, Galleries, Archives, and Libraries (based on Taylor, forthcoming) mechanical adjustments, which can successfully provide appropriate environmental control for the collection. In accordance with the international call for reducing energy use and examining alternative renewable energy sources, solutions that can complement the local external climate should be explored first. These include building envelope improvements; integrated strate- gies that address preservation, access, and human comfort needs; hybrid systems (alternative energy sources); seasonal and diurnal adjustments; and enclosures providing microenvironments for indi- vidual or multiple objects. 3. CONTEXT AND PREDESIGN Before an appropriate environmental management strategy can be developed, many contextual factors need to be considered. Cul- tural institutions vary not only in their geographic location and building morphology, but also in their purpose, mission, and the materials, condition, and needs of their collections. The values placed on different collections, their uses, and their expected life- times all influence an environmental management strategy. This section addresses the process of developing sustainable environmental management strategies for different types of projects, from installing new or upgraded mechanical systems in new purpose-built or renovated structures, to more energy-efficient cli- mate control strategies in existing situations. Although there are sig- nificant differences between new purpose-built museums and historic houses, the decision points are similar. A schematic decision-making flowchart can be used to define the necessary, broad steps from strategic plan to evaluation (Figure 1). It is intended for both new and existing buildings with a range of environmental solutions. The diagram also accounts for situations where there may be no collection preservation problems or the environment is deemed appropriate, but there is a desire to reduce energy consumption. The components/steps in the diagram are de- scribed in the following text. Although the later steps outlined in Fig- ure 1 are not within the scope of predesign, these sections describe considerations that can be addressed during the predesign phase. Different projects require different amounts of time and re- sources for individual steps. For many cultural institutions, particu- larly those that have been operating for some time, relevant information such as collection surveys or significance assessments may already exist, reducing the time required for predesign. In all instances, however, decision making is a multidisciplinary activity involving a variety of stakeholders, whose role and level ofinvolve- ment can change throughout the project. The list on the right-hand side of Figure 1 shows the expected level of participation for stake- holders at each step: if they are making decisions, if they should be consulted or be informed. If there is doubt, it is usually advisable to engage the stakeholders earlier in the process. Inc. ASHRAE, 2019 user. single for Licensed | {}
3b2ff61d-bcd6-40d8-a9b7-9bb416f633d0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 24.4 2019 ASHRAE Handbook-HVAC Applications (SI) Table 1 Examples of Space Types in Museums, Galleries, Archives, and Libraries ¦ ¦ Collection ¦ Noncollection ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Public space ¦ Changing exhibition galleries Permanent collection galleries Reserve/scholar collections Open storage Most reading/collection study rooms ¦ Entrances/vestibules Atria Cafeteria Restaurants Shops Auditoria Education spaces Restrooms Coat/baggage rooms ¦ ¦ Nonpublic space ¦ Conservation laboratories Collection storage Workshops and mount-making areas Archive stacks Library stacks Quarantine areas Photography studios Digitization areas ¦ Offices Crate storage (controlled relative humidity may be required) Mechanical/electrical rooms Data centers/IT rooms Food preparation areas Loading bays ¦ ¦ Low-occupancy space* ¦ Cool and cold storage Low oxygen storage Low-relative-humidity rooms Off-site storage (e.g., high-density library stacks) ¦ General storage areas (sales shop inventory, event equipment, etc.) ¦ ¦ *Occupancy in these spaces is for short periods, and meeting human comfort standards may not be required. ¦ *Occupancy in these spaces is for short periods, and meeting human comfort standards may not be required. ¦ *Occupancy in these spaces is for short periods, and meeting human comfort standards may not be required. ¦ Notes: (1) Collection spaces and adjacent noncollection spaces often require substantially different types of control. Providing barriers (e.g., doors, air curtains) to limit airflow and mois- ture vapor exchange between these spaces is usually necessary for successful control. (2) As exhibition needs change and collections grow, it is common for noncollection areas to be repurposed for collection exhibition. It is important to keep this in mind when plan- ning HVAC systems. A cafe or atrium may not require relative humidity control or special filtration, but if the space is repurposed to exhibit objects that require specialized envi- ronments (relative humidity control, etc.), retrofitting a system to provide the appropriate environment can be costly and disruptive. (3) Objects may be displayed in noncollection spaces through careful object selection (e.g., statues in vestibules) or use of display cases with the necessary microclimate perfor- mance. Offices that display collection items, such as paintings, should apply the same preservation requirements as collection spaces. Classrooms or other education spaces may be used to house some collection objects for extended periods; if so, collection-appropriate environmental control may be required. A design engineer may not be involved in the early stages of this process. All these steps, however, influence the choice and delivery of the environmental management strategy and include important information for considering appropriate goals and solutions. A new building may involve developing a strategic plan and mission before a building project is started, whereas an operating museum may engage an engineer to provide a solution to an identified problem or undesirable situation. 3.1 MISSION AND STRA TEGY The purpose of any cultural institution is central to all decisions, even ifits influence is implicit. Almost all cultural institutions have a mission statement, even those where the building is yet to be con- structed. An operating museum often has statements of significance for collections, which describe the reasons for their importance. The mission of the institution and how its heritage assets are valued determines how the assets should be preserved and what is under- stood as a risk. The values of a collection directly inform the impact of a hazard, and even how different kinds of damage are regarded. An archive values the informational assets of its collection, often allowing access to individual items by researchers, increasing the risks of damage caused by handling. A fine arts museum may value aesthetic appearances that are affected by minor damage. A library and a contemporary art museum will have different expectations of the lifetimes of their objects and how their values are embodied by the material. This concept is also addressed in the section on Con- text, under Key Considerations. 3.2 DETERMINE NEEDS Although the collections are usually the principal focus for man- aging the environment in a cultural institution, the needs of occu- pants and of the building itself must be balanced (along with capital and operating costs). Historic buildings can often be more significant than the collections that they contain. The respective importance of these needs varies among institutions and even among spaces, and their requirements can conflict. The differing needs of spaces in cultural institutions can be bro- ken down into broad categories of use by considering whether they contain collections, people, or both. This also helps identify spaces that can often be more flexible in terms of control, because there are many areas in cultural institutions that do not house collections, are not open to the public, and have occupancy for short and limited periods. Table 1 shows the kinds of spaces found in cultural institu- tions and what their use could imply through a matrix of occupancy levels for collections (columns) and people (rows). Spaces that house both often require the most consideration. Given that needs often differ between people and collections, the matrix presents opportunities to emphasize certain needs. Although specifics may vary over time (e.g., long-term uses, short-term management of spaces that are unoccupied at night), Table 1 provides some guid- ance of where resources are best applied. The specific collection needs must further be addressed in context. Collection needs vary considerably with the kinds of materials, combinations of materials in a single object, and how the objects were made. Even library collections comprise a mix of materials to consider. Information about different materials can require specialist knowledge from conservation or science experts, some of whom may be external to the institution. Relevant information to determine collection needs includes · Materials · Construction/assembly · Condition and vulnerability (see Tables 2 and 13) · Current and intended uses of the collection Inc. ASHRAE, 2019 user. single for Licensed | {}
269f50ea-6fa0-487a-9f19-5dc512678a66 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Museums, Galleries, Archives, and Libraries 24.5 · Frequency and kinds of access · Specific climate history (and movement of objects over time) Relevant information to determine building needs includes · Materials and construction · Condition and vulnerability · Current and intended uses of the building · History and changes to the building Relevant information to determine human needs includes · Numbers of staff and visitors and their current and/or intended activities · Current and intended uses of spaces · Expected kinds of clothing (which can vary in historic properties) For a new institution, data gathering may involve plans and blue- prints, and collection policies, rather than assessments of specific collections, but information that can help determine needs can be found in a range of sources. In operating cultural institutions, a collection risk assessment and/or condition survey may have been carried out for the collection, which would include most of this information. Collection needs are described more comprehensively in the sections on Overview of Risks and Environmental Effects on Collections. 3.3 CURRENT ENVIRONMENT Analyzing and understanding the past and current environmental conditions in and surrounding the buildings, and the interactions among climates, buildings, people, and collections, is essential to de- veloping appropriate environmental management, even if no inter- vention is carried out in the cultural heritage institution. Information relevant to understanding the influence of the environment on the building, collection, and people includes climate zone and predicted climate change, site macrocontext and morphology, the building and its orientation, existing methods of environmental control, and mon- itoring data on each hazard (temperature, relative humidity, pollut- ants, and light) both indoors and outdoors. This often requires a year of data collection, particularly for seasonally affected parameters such as temperature and relative humidity. These data are collected regularly in cultural institutions, but the points ofmeasurement, sam- pling interval, and reasons for monitoring should be reviewed. A building management system (BMS) may provide useful informa- tion about existing environmental management, particularly with re- spect to human comfort, but in general, climate monitoring should be independent from the system that is used to control climate, and it may be necessary for data to be gathered close to objects. Other contextual factors to consider include staff, their roles, institutional policies, operating costs, and energy use, as well as an institution 's budget. Each institution should seek to understand its pattern of energy consumption and recognize the most energy- intensive activities, which usually include lighting; appliance use; and mechanical ventilation, heating, and cooling. The sampling interval for monitoring energy use should be short enough (typically 1 h or less) to evaluate daily energy consumption patterns. Energy consumption should be evaluated according to existing national or international regulations, and compared with existing benchmark- ing systems or, if no benchmarks are available, with energy con- sumption in similar cultural institutions. For further discussion on environmental context, see the section on Climate Loads. 3.4 OVERVIEW OF RISKS The impact of the environment on materials can only be under- stood when both the environmental conditions and material proper- ties are known. By connecting preservation needs to materials' responses to environmental conditions, expected changes can be un- derstood. Considering information about the institution 's values and assets along with material change clarifies decisions about future risk and priorities. Synthesizing the impact requires an overview of which factors are most important and how the collections are affected by the building and people, and vice versa; mitigating risk to one aspect may increase risk to another. Integrating the information allows a compre- hensive definition of the situation, because criteria vary between in- stitutions: for example, historic houses may place more emphasis on preserving the building than a new museum might. Understanding this impact allows comparison to other general risks (see Table 2). Developing this overview allows an institution to prioritize needs, allocate resources, and develop goals for the development of a strategy. Much of this information may already exist in the form of a risk assessment. For further discussion of col- lection risks, see the section on Overview of Risks. 3.5 ACCEPT OR MODIFY ENVIRONMENT Once information has been gathered and synthesized, modifica- tions to the environment may be considered. If the current environ- ment is appropriate for the institution s identified needs, goals, and resources, the most appropriate decision can be to do nothing at the present time and continue monitoring. Other priorities in the insti- tution may take precedence. For an operating institution, changes to existing building man- agement and/or modifications to the building envelope may be appropriate ways to address the identified risks or high energy con- sumption. Problems can be addressed without directly modifying the environment, by adjusting locations and activities such as changes in circulation patterns, use of selected spaces, and exhibi- tion policies. Dividing collections by material type is a common measure, particularly in storage locations. When planning a new building, managing the risks most relevant to the institution 's mis- sion should be addressed early, with careful consideration of build- ing morphology, envelope characteristics, and expected energy use, as recommended by the International Institute for Conservation of Historic and Artistic Works and the International Council of Muse- ums Committee for Conservation (IIC/ICOM-CC 2014). Environmental modification may involve direct intervention, either mechanical or nonmechanical; passive design measures are also available. There is no risk-free scenario, and any decision must take into account available resources and the impact on the institu- tion as a whole, as well as overall environmental impact. Even after the initial diagnosis of risks, it is likely that this consideration may require further investment and expertise before a final plan can be developed. Regardless of how big or small the expected changes to the envi- ronment or management, monitoring should be carried out to fur- ther investigate problems or check for simple solutions. For related information, see the section on Preservation and Risk Management. 3.6 ANALYZE/PREDICT ACHIEV ABLE ENVIRONMENTS AND IMPEDIMENTS Ifit is decided that a comprehensive solution is required, further analysis (e.g., diagnostic monitoring, hygrothermal modelling ofin- door spaces, deeper investigation of existing control methods) will be necessary. Assessing information already gathered indicates what environments can realistically be achieved in a given climate zone with existing control methods, or the expected impact of proposed changes in the building envelope or type of environmental control. Comparing what environment can be achieved in the current or planned space with what is identified as necessary for collection preservation indicates the kind and level of intervention that is appropriate. This could include energy-saving options where a col- lection 's sensitivity is lower than the tightest level of control that can be managed (see Tables 13A and 13B), or a new approach to envi- ronmental management in the institution. For new buildings, this Inc. ASHRAE, 2019 user. single for Licensed | {}
681259f2-315b-487a-b4eb-e74415b243fe | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 24.6 2019 ASHRAE Handbook-HVAC Applications (SI) step presents an opportunity to consider appropriate parameters and objectives for different needs in the proposed spaces based on their (potentially mixed) use. The sections on Environmental Effects on Collections and on Design Parameters for Performance Target Specifications contain further discussion of environment and impediments. 3.7 SET PARAME TERS AND OBJECTIVES Understanding what is required to sustain the collection over time, and to ensure access to and use of the collection, is essential. Knowing the resources necessary to accomplish this, as well as what is achievable with the building envelope, the environmental param- eters can be agreed upon. The expected lifetime of a collection, or its desired rate of deterioration, can be reviewed at this point, which may require input from a conservation scientist. Many collections comprise a mix of materials with differing preservation qualities. If a collection largely comprises a limited range of materials, or if materials can be easily separated from one another, specific infor- mation about the responses of those materials to environmental con- ditions can be directly applied. Ifthe collection has been in the same environment for a long time (usually longer than 10 years), it will have had time to acclimatize to those conditions. Tables 13A and 13B provide information on the expected implications (outcomes) of different kinds of climatic control for mixed collections. These parameters also must take into account human comfort (see ASHRAE Standard 55-2017) and cost implications. The sections on Environmental Effects on Collections and on Design Parameters for Performance Target Specifications contain further discussion of parameters and objectives. 3.8 DEVELOP OPTIONS How the environment is managed (according to agreed-upon pa- rameters and objectives) has multiple implications, not just for the collection and costs (financial and energy consumption), but also on facility operations. Even in small interventions, staff should have ac- cess to the information because simple measures can affect other ac- tivities, such as security or audience engagement events. A clear understanding of the resources available, including budget, staff roles, time, training, and space, is needed for control options to be de- veloped and evaluated. For a new building, the solution may be part of a larger, inte- grated approach. HVAC design options should first consider the building as a means of control (see Tables 12, 13A, and 13B). Inc. ASHRAE, 2019 user. single for Licensed For more details, see the section on Design Parameters for Per- formance Target Specifications, and ASHRAE Guideline 34-2018. 3.9 REVIEW OPTIONS AND SELECT Many criteria may be involved in selecting the most appropriate approaches to environmental management. A method to determine consensus should be decided upon, and the key stakeholders for the project identified. All staff affected by environmental management should be consulted (or represented) in terms of how the options meet the chosen criteria. This is often best carried out through facil- itated, recorded meetings where criteria are addressed systemati- cally and transparently (Cassar 1995). Such processes present the opportunity to examine different perspectives and resolve apparent conflict through discussion. Results should be archived for future reference. Criteria for evaluating approaches to environmental management may well go beyond collection preservation and cost, to include is- sues such as impact on historic building fabric and human comfort. For example, historic houses can be adversely affected by installa- tion of mechanical systems. A cultural institution's mission state- ment can be a useful reference point to weigh the importance of criteria. This stage distills much of the information gathered earlier in a clear, digestible form for all stakeholders, so informed decisions can be reached collaboratively. 3.10 PREDESIGN PROGRAM BRIEF This is an opportunity for owner's requirements to be defined be- fore the solution is designed, including approach, scope, design team, and timeline. In some cases, a design engineer might not be en- gaged until after creation of the program brief. While setting criteria for the design team, solutions outside the scope of the design team (e.g., housing objects in display cases or archival boxes) should be part of the overall project effort. This again allows project goals to be aligned with the institution 's wider mission and other goals. A range of stakeholders already engaged in the process will be involved in planning and construction, so a clear shared vision helps the cultural institution work through the devel- opment. 3.11 DESIGN OF SOLUTION Although design of the solution is discussed more comprehen- sively later in the chapter, some considerations can be addressed during predesign. All needs identified while developing the prede- sign program brief should be communicated, and a liaison with col- lection and building staff should be identified. The solution may not yet be designed, but if the general approach is known, decisions can be made about whether to move collections before work begins. Rehousing a collection requires considerable time, including measures for documentation (e.g., database, photography, radio- frequency identification [RFID]) and security, as well as environmen- tal management. If the collections are not being moved, preparation for extra protection may be needed during an implementation phase. Depending on the approach, projected growth of the collection may also be a consideration during predesign. 3.12 PROCUREMENT AND CONSTRUCTION Procurement and construction are discussed in more detail later in the chapter, but there are opportunities to prepare for this stage. A risk assessment may be required for the designed solution (espe- cially if the collection is moving). Information from the context and predesign phases about the values of the collection and building is relevant and should be accessible. For larger projects, a dedicated collections professional responsible for oversight of collections preservation issues during construction may be engaged. Cultural institutions often have historic buildings that are intended to last for a long time. The life cycle of materials, and any impact of the solution on historic values, should be understood by all parties. 3.13 ST ART-UP AND COMMISSIONING Commissioning and start-up are discussed later in the chapter. A commissioning agent should be identified and engaged during final predesign and early design stages, so they understand the underly- ing design goals and can be present through the process. 3.14 TRAINING AND DOCUMENTATION Training and documentation are discussed later in the chapter, but the data gathering that has already occurred should be instruc- tive to this process. Understanding and documenting current man- agement and maintenance practices can help communicate in-house skills and expertise to the design team. Time during a project may need to be put aside for training, and a realistic understanding of institutional and staff capacity is required before implementing a design option. Staff changes over the time horizon of larger projects may also need to be considered. | {}
5c5ddad9-2656-49e9-95bb-62e90439dddc | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Museums, Galleries, Archives, and Libraries 24.7 Table 2 Agents of Deterioration: Potential Hazards in Managing Collection Environments ¦ Agent ¦ Comments ¦ ¦ --- ¦ --- ¦ ¦ Physical forces ¦ Handling, shock, and vibration can cause immediate or accumulative long-term damage to fragile objects. Risks often increase during construction work, when collections may have to be relocated or secured in situ. Mechanical systems may present a risk if vibration is transmitted through ductwork to works hung on adjacent walls or in particularly active air drafts. Vibration transmitted to objects may cause them to move, and to fall off of exhibit and/or storage shelves. ¦ ¦ Thieves and vandals ¦ Can be addressed by limiting access to mechanical systems to improve security. ¦ ¦ Fire* ¦ Fire (and its related methods of extinction) can result in serious damage or even total loss of building(s), collections, operations, and services. Fire prevention and control, aimed at reducing the risk of a fire occurring and minimizing its effects, should be given the highest pri- ority possible. It is recommended that each HVAC system be integrated with a fire detection system, ensuring that the system is shut down in a fire alarm to limit the spread of fire, smoke, and soot. ¦ ¦ W ater* ¦ Liquid water (including rain, flood water, or water from broken pipes) is often related to incidents and disasters, but also includes dampness resulting from condensation and rising damp in buildings. Liquid water is very destructive to collections: it can stain, deform, or even dissolve materials. Wet conditions can quickly germinate mold, fungi, and bacteria, creating hazardous conditions for human health. ¦ ¦ Pests ¦ Infestations primarily include insects devouring collections; mold, fungi, and bacteria also qualify as pests. Limitation measures include avoiding high relative humidity and warm conditions, maintaining overall cleanliness, and controlling indoor air quality and ventilation (which helps reduce temperature gradients and thus relative humidity). ¦ ¦ Pollutants (or contaminants) ¦ Includes outdoor-generated gaseous and particulate contaminants that infiltrate the building and indoor-generated gaseous pollutants. Sources and effects of pollutants are detailed in the section on Airborne Pollutants/Contaminants. Particulate filtration to control both coarse and fine particles and gaseous filtration is discussed in the section on Airborne Pollutant Control Strategies. ¦ ¦ Light (or radiation) ¦ Most materials undergo some form of permanent photochemical or photophysical change from exposure to radiation (i.e., visible, infrared [IR], and ultraviolet [UV] light), which is an inevitable consequence of display. Light damage is cumulative but relatively easy to control if addressed at architectural, design, and operational levels by eliminating ultraviolet radiation, minimizing infrared radiation, and limiting light exposure by decreasing illumination intensity or its duration. ¦ ¦ Temperature ¦ When temperature increases, damaging chemical processes accelerate. Any temperature change affects the absolute humidity in the air, resulting in changes in relative humidity. Relative humidity and temperature are often considered together when deciding on a climate control strategy, especially for suscepti- ble classes of materials such as early synthetics (plastics), paper, and photography.* See the section on Temperature and Humidity for details. ¦ ¦ Relative humidity ¦ Each organic/hygroscopic material has a specific level of moisture content consistent with maximum chemical, physical, or biological stability. Relative humidity becomes a risk factor when it causes the moisture content in a material to be significantly too low or too high. Fluctuating relative humidity with large and prolonged variation in levels can also be damaging, specifically to objects of composite materials and/or restrained constructions. Inorganic (nonhygroscopic) materials can also be adversely affected by moisture in the air (e.g., corrosion of metals, salt efflorescence in porous materials). See the section on Temperature and Humidity for details. ¦ *Fire and water are often associated with building and mechanical (design) malfunctions, such as power outages, electrical short circuits or water pipe failure (especially over spaces containing collections). These failures are infrequent but do happen, and it is important to remember that a single failure could ruin a significant portion of a collection. Every effort should be made to route water lines and other utilities away from areas that house collections. Building systems also rely on the infrastructure to provide utilities and communica- tions. Where the infrastructure is not reliable or is of inadequate capacity, provisions should be made for temporary or alternative supply. 3.15 EV ALUATE AND REVISE This step is addressed later in the chapter, but data gathered at any early stage can help serve as a baseline for evaluating the solution, and should be documented and archived for future reference. This includes data on climate and pollution as well as energy costs. How environmental monitoring is carried out during predesign should inform continued monitoring beyond implementation of the solution. 4. OVERVIEW OF RISKS A collection's longevity is directly influenced by the building's architecture, any climate control systems (nonmechanical or me- chanical), and existing preservation procedures and protocols. These may positively mitigate the impact of risks or, alternatively, exacerbate them. Mechanical engineers need to consider the risks for collections even ifthey do not appear to relate directly to a build- ing's mechanical systems. The hazards listed in Table 2 are called agents of deterioration in the conservation field and may affect collections. Note that there can be interactions between different agents of deterioration, and many hazards are created by several agents in conjunction with one another (CCI 2018). Assessments are often used to identify the potential impact or magnitude ofa risk occurring. Any climate control strategy should complement mitigation strategies for other risks and should not in itself create a greater haz- ard (e.g., when an energy supply fails, or when an active HV AC sys- tem spreads fire or soot if no automatic HVAC shutdown is provided). Table 2 does not cover natural emergencies, which are often dev- astating and have effects beyond the institution. Institutions (should) have emergency response policies in place to deal with incidents, emergencies and disasters. Inc. ASHRAE, 2019 user. single for Licensed | {}
66c7249b-acf9-4243-9611-0dd16fc34ad4 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 24.8 Chart Type: line RELATIVE HUMIDITY SAFETY REGION BORDERLINE CONDITIONS DANGER REGION item_01 40°C 20°C 10°C 10°C ASSUMES RH HAS CLIMBED, NOT FALLEN, TO THESE VALUES. 。 OLD PARCHMENT BOOK MATERIALS: GROOM AND PANISSET (1933) △ STARCHED COTTON BORDER CURVE: SUMMARY OF CULTURE STUDIES □ GOAT SKIN NOT FALLEN, TO THESE VALUES. + no growth in 1300 days IN AYERST (1968) Fig. 2 Temperature and Humidity for Visible Mold in 100 to 200 days 5. ENVIRONMENTAL EFFECTS ON COLLECTIONS Providing specialized temperature and relative humidity control has been central to museum, gallery, archive, and library design since the nineteenth century, and numerous architectural and HVAC solutions have been explored. Luciani (2013) provides a detailed history of these engineering and architectural solutions throughout the twentieth century in North America and Europe. Until recently, temperature and relative humidity specifications were based on cau- tiously applied qualitative understanding (Michalski 2016), rather than quantitative understanding applied to decisions influenced by sustainability. This section summarizes the technical knowledge available to support current decisions, particularly when selecting or modifying targets. 5.1 BIOLOGICAL DAMAGE High relative humidity levels and dampness accelerate mold growth on most surfaces. Of all HVAC-controllable environmental parameters, high humidity is the most important factor. The most comprehensive mold data are from the feed and food lit- erature. Fortunately, this provides a conservative outer limit to dan- gerous conditions. Mold on museum objects occurs first on surfaces contaminated with dust, sugars, starch, oils, etc., but can also occur on objects made of grass, skin, bone, and other feed- or food-like materials. Water activity is identical to and always measured as the equilibrium relative humidity of air adjacent to the material. This provides a better measure than the equilibrium moisture content (emc) for mold germination and growth on a wide variety of materi- als (Beuchat 1987). Figure 2 shows the combined role oftemperature and relative humidity. A study by Groom and Panisset (1933) of the most vulnerable book materials concurs with the general trend of culture studies from Ayerst (1968) and comprehensive data on mold growth in buildings obtained by Sedlbauer (2001). Ohtsuki (1990) reported microscopic mold occurring on clean metal surfaces at 60% rh. The fungal DNA helix is known to collapse near 55% rh (Beuchat 1987), so a conservative limit for no mold ever, on anything, at any temperature, is below 60% rh. Chapter 26 suggests a similar lower boundary to avoid mold in food crops. 2019 ASHRAE Handbook- - HVAC Applications (SI) Chart Type: line 50 60 70 80 90 100 item_01 1000% 100% 100% 10% 1% 1% at 60% rh Fig. 3 Time Required for Visible Mold Growth LAID EGGS OF NUMBER Chart Type: bar 10 12 14 16 18 20 22 24 26 item_01 0 0 0 5 10 20 30 50 70 Fig. 4 Number of Eggs Laid by Webbing Cloth Moth (Tieneola bisselliella) as Function of Temperature Snow et al. (1944) looked for visible mold growth on materials inoculated with a mixture of mold species. These are plotted in Fig- ure 3, and follow the same trend reported by Hens (1993) for the European building industry for wall mold. Figures 2 and 3 show practical dangers: growth in less than a sum- mer season requires over 70% rh, and growth in less than a week requires over 85% rh. Care must be taken to avoid cold surfaces where condensation might occur, such as on windows and ductwork. There are relatively few experimental data on the relationship between the risk of insect infestation and climate parameters (Strang 2012). Child (2007) and Pinniger (2001) suggest that, below 15°C, pests that can damage cultural heritage collections start to be sluggish and do not fly. Also, low relative humidity further limits pest risk because eggs and young larvae are sensitive to dehydration. Child (2007) reported that the furniture beetle (Anobium punc- tatum) require relative humidity levels above 60% to reproduce. A risk index quantifying the threat of pest infestation was proposed by Brimblecombe and Lankester (2013). As shown in Figure 4, the number of eggs laid by the webbing cloth moth depends on T according to the following relationship: Inc. ASHRAE, 2019 user. single for Licensed | {}
984c9418-84b0-4727-ae41-b6355ed8c60a | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Museums, Galleries, Archives, and Libraries 24.9 ![image](/image/placeholder) 2 T2 E = 130 exp - 30 /12 30 5.2 MECHANICAL DAMAGE Very low or fluctuating relative humidity or temperature can lead to mechanical damage of objects. The fundamental cause is the ex- pansion and contraction of materials, combined with some form of internal or external restraint. Hygroscopic materials absorb moisture when relative humidity rises and desorb moisture when relative hu- midity falls, causing change in dimensions. Dimensional change caused by temperature change is more rapid, but much smaller than that caused by relative humidity in hygroscopic materials. When the dimensional change of a component in an object is restrained, the component is strained and stressed. Components can be fully re- strained by another, stronger, immobile component; partially re- strained when connected to a component with a different coefficient of expansion; or restrained within themselves when experiencing a gradient in moisture or temperature. Beyond a critical stress or strain point, irreversible deformation or fracture occurs. Concerns about mechanical damage from temperature and rela- tive humidity fluctuations have led to extremely narrow specifica- tions, such as 21 土 1°C and 50 土 3% rh (LaFontaine 1979). These "best-available technology" specifications were based on the assumption that, because very large fluctuations could be seen to cause obvious damage, any size of fluctuation must bring some degree of damage. Revisions to this assumption, based on limited quantitative research, drove the first (1999) edition of this chapter. Recent research has further strengthened the need for a more flexible approach to climate control for museum collections. The materials most sensitive to temperature and relative humid- ity fluctuations are all hygroscopic polymers, whether complex nat- ural mixtures such as wood, paper, leather, or parchment, or processed products such as animal glue, oil paints, acrylic paints, or cellulose acetate. The stress or strain that causes fracture depends on the amplitude and rate of any temperature or relative humidity change. Low temperatures, fast rates of strain, and low relative humidity lead to brittle "glassy" behavior with small tolerable strains, whereas high temperatures, slow rates of strain, and high relative humidity lead to more "rubbery" behavior and large tolera- ble strains. The transition between these two behaviors occurs at the polymer's glass transition temperature, which is a gradual change over a range that is typically10 to 20 K wide (Hagan 2017; Michal- ski 1991). Some materials, such as paints, are in their flexible but tough state at room temperature. When temperature drops, these materials be- come increasingly brittle and fragile: artists' acrylic and oil paints enter their glassy states in the range of 10 to 0°C (Daly Hartin et al. 2018; Hagan 2017; Mecklenburg and Tumosa 1991). In this tem- perature range, risk of fracture from small errors in handling greatly increases. Other materials, such as animal glue, paper size, and photo- graphic gelatin, are in their hard but strong state at room tempera- ture. High relative humidity (>75% rh), however, pushes them into their rubbery state (sticky and weak) because of the plasticizing effect of moisture (Karpowicz 1989; Krzemien et al. 2016; Meck- lenburg 1991; Michalski 1991). Wood can be more easily deformed over 75% rh; if constrained in a cabinetry joint, a wood component will be permanently deformed by high relative humidity. This leads to tensile fracture of the component if it is restrained during its return to a middle (or low) humidity. Simple models of uniformly constrained material, combined with data on the mechanical properties of painting materials in particular, suggested that a fluctuation of approximately 15% rh was tolerable within the elastic limits of such materials (Erhardt and Mecklenburg 1994; Erlebacher et al. 1992; Mecklenburg and Tumosa 1991, 2005; Mecklenburg et al. 1998; Michalski 1991, 1993). More detailed re- search has since emerged: Jakiela et al. (2008) used numerical mod- elling of large pieces of wood, as used in sculptures, to show a tolerable fluctuation of 15% rh (in the 25 to 75% rh range). Tan- tideeravit et al. (2013) showed similar tolerance using finite element modelling for delamination in paint, as did Bratasz et al. (2015) for historic textiles. Overall, the last decade of work with more detailed material data and more complex models has confirmed that, for ma- terials found in collections, uniformly constrained components tol- erate fluctuations of at least ±10% rh, whereas fluctuations beyond 20% rh cause rapidly increasing risk of fracture. Three large practical factors must be added to any simple model based on uniform restraint: stress relaxation, stress concentration, and proofed fluctuation. Stress relaxation results from the shift over time from glassy to rubbery behavior. W ood will stretch more than twice as much across the grain before fracturing if the strain is applied slowly over 3 months rather than over the course of one day (Madsen 1975). Even highly pigmented oil paint (ground), which has only very gradual relaxation, experiences only half the stress of a 10 min event if that same strain is applied gradually over 3 months (Daly Hartin et al. 2018). This general tendency to relax to about half the stress when comparing cycles lasting hours to those lasting months is the justifi- cation for equating the risk from a seasonal adjustment of 10% rh to a short-term increment of 5% rh for Types A1 and A2 in Table 13A. Stress concentration is well known to engineers, and can be described as the increase in local stress because of a flaw, groove, hole, or narrowing of the component. The fracture pattern (cracks starting at these weak points) is familiar to conservators. Stress con- centration was used to help construct categories in Table 3. Objects that fit uniform restraint models are in the category of medium sen- sitivity (i.e., stress concentration of ~1); values around 2 indicate high sensitivity, and 3 and above are very high sensitivity. These include assemblies where a weak layer bridges a joint in strong com- ponents that either diverge or shear during relative humidity change. Low-sensitivity assemblies do not restrain any components (e.g., sheets of paper or thin wood free to expand and contract). Proofed fluctuation is the phenomenon whereby restrained components that have already fractured because of an excessive fluctuation in the past will not fracture further until a fluctuation exceeds that historic "proofed" fluctuation (Michalski 1993, 2014). Consequently, higher-sensitivity objects in Table 3 move to lower sensitivity categories, and a collection ' s sensitivity both diminishes and becomes less varied. Proofed fluctuation has become part of some standards (e.g., Ente Italiano di Normazione [UNI] Standard 10969) and has been refined to include fatigue: repetitive fluctua- tions must accumulate as many cycles as have already occurred before there is significant risk of new fracture (i.e., when partway along an S-N fatigue plot depicting stress S against the number of cycles N to failure, one must move significantly along the N scale to grow the fracture). Michalski (2014) created a graphic tool using S- N plots for estimating tolerable fluctuations, given a known history of fluctuations. Proofed fluctuation implies that improved climate control beyond the historic pattern for a collection cannot be justified easily on the basis of mechanical risks, unless there is an active program of resto- ration of fractured objects, which erases proofed fluctuations. (Chemical and biological deterioration have no such limiting con- cept: they accumulate up to the point of total destruction.) Proofed fluctuation also clarifies the type of climate control risk that does warrant careful mitigation: the probability of extreme fluctuations beyond the proofed fluctuations (e.g., during HVAC system mal- function). The time span for judging reliability in museums is 100 Inc. ASHRAE, 2019 user. single for Licensed | {}
95790e78-12b0-4635-8dfc-db421130617c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 24.10 2019 ASHRAE Handbook-HVAC Applications (SI) Table 3 Sensitivity of Unproofed Objects to Relative Humidity Fluctuationsa ¦ Objects and Effects of Fluctuations ¦ Low Sensitivity ¦ Medium Sensitivity High Sensitivity ¦ Very High Sensitivityb ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Flat sheets of paper, film, tape, leather, parch- ment, metal, with image or data layer. May delaminate, fracture, or distort permanently. ¦ Support layer with finely dis- persed image/data layers. Includes most single sheets of paper with print, halftones, line drawings, inks, washes. Laminates with low differences in expansion. Includes most case-bound books (not leather or parchment book covers). Most CDs. Commercial signs painted on metal. ¦ Layered structures with moder- Layered structures with poor Large ate strength, moderate differ- strength, moderate to high dif- sheets ences in expansion. Includes ferences in expansion. Includes Includes sheets most photographs, negatives, and thick images on parchment. adhered to stretchers, 19th- film. Most magnetic records. Globes. Thick oil-resin images century on fabric and Thin, well adhered inks on parch- on paper or cloth. Objects listed stretchers. ment, such as deeds. Gouache on as medium vulnerability that at paper. Book bindings of vellum have weakened substantially and/or wood. Gilded parchment, because of UV exposure, or leather. aging already causing flaking. ¦ reactive (to fluctuations) restrained at periphery. large paper photos Large prints adhered all four corners (usually tear near the point of restraint). ¦ ¦ Wood or wood assemblies. May crack, split, delaminate, or distort perma- nently. ¦ Single wood components, or assemblies designed to elimi- nate stresses. Includes floating panels in furniture or room pan- eling; tongue-and-groove plank- ing nailed or bolted on edge only (e.g., wainscoting), wood boxes on farm machinery (unless jammed because of painting, warping), hollowed-out totem poles, wooden tool handles. Assemblies with prior damage that allows stress release. In- cludes most old tables where all screws and joints are loose, any panels already split. ¦ Wood assemblies with uniform- Wood assemblies with concen- ly distributed stresses during tration of stresses during fluc- fluctuations. Includes most plain tuations. Includes veneer over wood furniture with tight joints, corner joints, such as many no prior splits, most veneers and wardrobe doors, Art Deco furni- marquetry that cover a continu- ture. Fretwork applied wooden ous piece below, such as most 18th- and 19th-century chests of ornaments. Assemblies with drawers. Furniture made with bolts, nails, screws that hold both plywoods, such as Victorian cata- sides of a single plank. Many log pieces. Fluctuation to higher musical instruments. relative humidity may not always cause visible damage, because many joints/panels are invisibly crushed, but this makes them more likely to split during lower relative humidity. Large wooden objects. Outer layers are constrained uniformly by the inner core because of gra- dient in response to relative humidity change. ¦ w ood assemblies with attached or inlaid metal, horn, shell, etc., that spans more than 10 mm across the wood grain. Attach- ment or inlays may delaminate or buckle. Includes masks with adhered shell, 18th- and 19th- century fine furniture, clocks with inlays. ¦ ¦ Pigmented coat- Paint ings on a sup- port: gilding, May crack, inate, flake. over in heavily ¦ Acrylic paintings on canvas. Rigid paint layers in Oil paint, gilding, on wide spans Includes many paintings since to good condition. In- of wood, or paint on other flaws paintings, 1960 (may move to medium sen- cludes most organic rigid supports lacquer. sitivity if a heavy glue size was furniture, delam- used, or if adhesion between lay- water pan- elements. hair- ers is poor). seams flawed, doors or painting frames are normal, ¦ on canvas, moderate oil paintings on can- with Includes vas (may move to high sensitivity weak adhesion. Includes most if weakened by damage or panel paintings, wide gilded wood great age). els. If are with line cracks Definitely move to high sensitivity rigid fills, etc., then may become if stretched too tight, or tightened very high sensitivity. Miniatures sidered high relative humidity. on ivory, because of poor adhe- fluctuation from low rela- sion and undulations of some humidity is a much higher ivories. Heavy modern paintings to paintings on fabric than on smooth side of fiber-board from high relative humidity; how- may delaminate because of ever, over 85% rh may cause can- adhesion. vas shrinkage and flaking of the ground plus paint layers Includes oil paint, gilding on nar- row spans of wood, gilt furniture, ¦ layers bridging seams or that concentrate stress. polychromes, painted painted architectural Note that joints of usually con- not furniture. ¦ ¦ organic objects. ¦ organic materials with- materials ¦ during Note: tive risk weak picture frames. ⌀ther High crimp woven organic N/A with edge restraints. most May tear during fluctuation to high relative humidity. Includes needlepoint fixed to a stretcher. ¦ but those lacquered N/A ¦ ¦ Organic materi- als with zero stress level at rh. ¦ w oven out edge restraints. Includes basketry. Textiles such as blankets, flags, simple costumes. ¦ Includes teeth, boats tion. Crack humidity teeth below 50% rh). ¦ made from stretched leather on rigid construc- when relative drops below critical level (e.g., ¦ ¦ ¦ ¦ ¦ ⌀ther ¦ ¦ 100% objects where ratcheting mechanism may exist. material a. Vulnerability assumes to in enclosures ¦ ¦ humidity. objects can fully respond fluctuation. Objects take many days or weeks to respond. ¦ Objects where small parts continuously dislocate and block expan- sion of object. Elephant tusk positioned downwards: small parts fall down gravitationally during low relative humidity period and block expansion during rises of relative ¦ b.These objects are very rare: they break rules of craftsmanship and will have already failed unless relative humidity has never fluctuated since fabrication. Alternatively, these are objects that underwent overly interventive and inflexible restoration. Inc. ASHRAE, 2019 user. single for Licensed | {}
bc8b9393-77e5-4635-81a6-7b63c2c88b93 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Museums, Galleries, Archives, and Libraries 24.11 years. Catastrophes of mechanical damage to collections are usually caused by a system failure that causes novel conditions, compounded by a failure of rapid response (monitoring failure). Two types of observational studies of historic objects in uncon- trolled spaces are confirming these models: acoustic emission and visual evidence. Strojecki et al. (2014) applied acoustic emission to a 1785 wardrobe that was high sensitivity when new (veneer bridg- ing many seams in structural wood components, some of which have fractured). It is on permanent display in a type D (see Table 13A) controlled museum (20 to 65% rh short term, 30 to 50% 30 day av- erage), so it has been proofed to the building' s historic climate pat- tern. A year of acoustic emission established that fracture because of fatigue is growing only very slowly, on the order of 13 mm/century. Given that the existing crack is at least 100 times longer, growth is decelerating. Bratasz and Vaziri Sereshk (2018) demonstrated an up- per limit to craquelure growth as well, which they call "crack satu- ration". Ekelund et al. (2018) compared the current state of cracks in similar pieces of furniture to old photographs and established that current variations of at least ±20% rh and ±10 K did not increase vis- ible damage. Oreszczyn et al. (1994) compared visible damage dif- ferences between collections in historic houses with "improved" climate control and those without, and saw none. Highly sensitive techniques for measuring distortions are giving similar evidence (Lasyk et al. 2012). Overall, it is new (unproofed) or restored objects with erased proofed fluctuations that are more likely to be sensitive, not old (proofed) objects. The rare large fluctuations are the greatest risks, not the frequent and small ones. Very-long-term reliability and ease of rapid repair (before collections fully respond) are more important than trimming ripples in hourly climate data. The section on Tem- perature and Relative Humidity defines different levels of control of fluctuations (AA, A1, A2, B, C, and D). The most stringent level, AA control within ±5% rh, can only be justified if there are unproofed objects of very high sensitivity, ifthe small risk of fatigue fracture is unacceptable, and if all larger risks have been controlled. For many collections, either A1, A2, B, C, or D will provide suitable control of the remaining risks of fracture. 5.3 CHEMICAL DAMAGE This section is not intended to replace the use of standards avail- able for cold storage of collections, listed in Table 4. Standards con- sider not just the benefits of low temperature and low relative humidity, but also their side effects, their management, and critical procedures that are beyond the scope of this chapter. The ranges in Table 4 are not specific recommendations; rather, they only show the maximum range of conditions cited as various recommendations in each standard. Both ISO Standard 18934 and the Image Permanence Institute (IPI; Adelstein 2009) provide definitions for four temperature terms: room, cool, cold, and either subzero (ISO) or frozen (IPI). This chap- ter usesfrozen (although it unfortunately could imply that equilibrium moisture in hygroscopic materials goes through a phase transition and freezes like bulk water, which it does not.) IPI (Adelstein 2009) defines the first three terms by "anchor points" rather than ranges: 20°C, 12°C, and 4°C. These anchor points are used in Table 5. Relative Humidity The National Archives and Records Administration (NARA 2013) changed relative humidity control from a steady 45% rh to a permissible seasonal swing between 30% and 50% rh. They esti- mated a savings of $650 000 per year in utility costs as well as an increase of 20% in collection lifetime. This section enables quanti- tative answers to very common questions about sustainable varia- tions on fixed standards: how much do benefits change with adjustments in temperature and relative humidity? How much does Table 4 ISO Storage Standards for Collections that Use Cold Storage ¦ ISO Number ¦ Collections ¦ Range of Relative ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ Covered ¦ Humidity ¦ Range of T ¦ ¦ 18911:2010 ¦ Photographic films (except nitrate) ¦ 20 to 50% ¦ 0 to 7°C ¦ ¦ 18920:2011 ¦ Photographic prints ¦ 30 to 50% ¦ 2 to 16°C ¦ ¦ 18923:2000 ¦ Magnetic tape ¦ 15 to 50% ¦ 2 to 16°C ¦ ¦ 18934:2011 ¦ Multiple media ¦ 30 to 50% ¦ Room: 16 to 23°C ¦ ¦ ¦ ¦ ¦ Cool: 8 to 16°C ¦ ¦ ¦ ¦ ¦ Cold: 0 to 8°C ¦ ¦ ¦ ¦ ¦ Frozen -20 to 0°C ¦ risk climb during high temperature and high humidity? Are seasonal adjustments possible for energy saving? What are the risks during re- trieval? This section is also a reminder that not only archives, but all collections with low-stability objects listed in Table 5, can benefit from low temperature. Lower temperature reduces the rate of all forms of chemical decay. For the most rapidly decaying organic materials (right-hand columns of Table 5), the dominant mechanism is acid hydrolysis, which increases strongly with the acidity of the material, and increases with moisture content (Zou et al. 1996). Moisture content, in turn, depends on relative humidity. The consensus is that the rate of decay (or its reciprocal, lifetime) is a product of an acidity factor, a temperature factor, and a relative humidity factor (which some- times includes a correction dependent on temperature). L = f(pH)f(T) f[rh(7)] (1) where L is lifetime, in years. For our purposes, acidity is a given, and only temperature and relative humidity can be controlled. The temperature function is an Arrhenius equation: E a f(T) = C exp RT (2) where C = constant, units of time R = gas (Boltzmann) constant, 8.134E-3 kJ /mol· K Ea = activation energy, kJ /mol T = temperature, K Michalski (2002) compiled data from reviews of activation ener- gies (notably reviews by Nishimura [1996]) for paper, film, and photographic dyes, as well as further individual studies of magnetic media and the yellowing of varnish. More than three-quarters of all the studies of paper degradation, acetate film degradation, and dark fading of dyes fit within an Ea range of 80 to 120 kJ/mol. In Figure 5, this range is shown by the shaded area. Michalski (2002) further showed that this range of Ea can be derived with no consideration of a specific material, but simply by examining the kinetics of a chem- ical process that requires several decades to proceed at room tem- peratures. Thus, both data and theory suggest that this Ea range can be used to estimate the benefits of cold storage, and the risks from high temperature, for all organic materials suspected ofbeing low or very low stability (Table 5). Michalski (2000, 2002) selected a mid- dle value for mixed collections at 100 kJ/mol, shown by the heavy black line in Figure 5. For decay of polyester polyurethane (the weak link in magnetic media, and a popular material with artists in the late twentieth century) and for yellowing of natural resins, the activation energies fall slightly lower, 60 to 80 kJ/mol (between the shaded area and the dashed line in Figure 5.) Data on the influence of relative humidity are much less exten- sive than those for temperature, and insufficient to select between differing models. Some authors assume that the true variable is moisture content (Strlic et al. 2015; Zou et al. 1996) and use a Inc. ASHRAE, 2019 user. single for Licensed | {}
c238dd66-5c78-42ea-b0a3-dfb6fea02058 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 24.12 2019 ASHRAE Handbook-HVAC Applications (SI) Table 5 Classes of Chemical Stability ¦ High Stability ¦ Medium Stability ¦ Low Stability ¦ Very Low Stability ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Wood, glue, linen, cotton, leather, rag paper, parchment, oil paint, egg tempera, watercolor media, gesso. Serviceable examples up to 3 millennia old exist, from dry burial or dry enclosures at ~20°C. These examples were protected from any acid exposure (e.g., air pollu- tion from Industrial Revolution), and have never been damp. Skin, bone, and ivory of the woolly mammoth have survived intact for over 40 000 years while frozen. ¦ Current best estimate for stable photographic materials (e.g., 19th century black-and-white negatives on glass, 20th cen- tury black-and-white nega- tives on polyester film) to remain usable as images with little or no change. ¦ Acidic paper (e.g., newsprint, low-quality books, papers post-1850) and some film become brittle and brown, dif- ficult to access. Acetate film shrinks, image layer cracks. Celluloid and many early plastics become yellow, crack, distort. Natural materials acidified by pollution (textiles, leather) weaken, may disintegrate. ¦ So-called unstable materials. Typical magnetic media (e.g., video/audio/data tapes, floppy disks) begins to be unplayable. Least-stable photographic materials decay (e.g. color prints fade in the dark; poorly processed items yellow, disinte- grate; cellulose nitrate yellows, disintegrates, faster when pack- aged in large amounts). Many elastic polymers, from rubber to polyurethane foams, become brittle, or sticky, or disintegrate. Some acrylic paints on some canvas supports yellow rapidly. ¦ Lifetimes at Various Temperatures* ¦ ¦ High Stability ¦ Medium Stability ¦ Low Stability ¦ Very Low Stability ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 60°C, heat treat, sun 30°C, hot room 25°C, warm room ¦ ~4 years + ~250 years + ~500 years + ¦ ~ 1 year ~75 years ~150 years ¦ ~6 months ~25 years ~50 years ¦ 2 months ~7 years ~15 years ¦ ¦ 20°C, room ¦ Millennia ~1000 years ¦ A few centuries ~300 years ¦ One human lifetime ~100 years ¦ One human generation ~30 years ¦ ¦ 12°C, cool ¦ ~3200 years + + ¦ ~1000 years years ¦ ~320 years ¦ ~100 years ¦ ¦ 4°C, cold -20°C, frozen ¦ 11 000 years 750 000 years + ¦ ~3300 ~225 000 years ¦ ~1100 years ~75 000 years ¦ ~330 years ~22 500 years ¦ Source: Modified from the tables "Chemical sensitivity of materials to room temperature" and "Approximate lifetimes of the materials at various temperatures" (Michalski 2018) *Lifetime defined here in terms of effects or utility described for each material listed in the top row. Lifetimes expressed in each row have considerable uncertainty, but relative improvement from top to bottom rows is certain. X-Axis: Storage Temperature, °C Y-Axis: Lifetime Relative to 20°C Chart Type: line -20°C -10°C 0°C 10°C 20°C 30°C 40°C 50°C 60°C item_01 100 80 60 40 20 10 0.0 0.01 0.001 Fig. 5 Effect of Temperature on Lifetime for Various Ea complex function of relative humidity that includes a temperature correction. Three advisory tools are currently available: the preservation index (Reilly 1995), Michalski (2000), and Strlic et al. (2015). These tools can be used to derive equations for a lifetime (Lr) rela- tive to the lifetime at room conditions 20°C, 50% rh. These equa- tions have been used to plot lines of constant relative lifetime (also called isoperms) on the psychrometric chart in Figure 6. The fol- lowing equations are all arranged with the temperature and relative humidity components separated for clarity, and with R separated so that Ea becomes explicit as the numerator above RT. 1. Preservation Index, derived principally from acetate film data, but considered applicable to all organic objects as listed in Table 5 (the equation derived from Table 1 in Reilly (1995) fits within 5%); available as a wheel calculator, and as a software tool, from Image Permanence Institute (IPI 2018). 94.9 Lr = 4.69 x 10-17 [rh(0.020877 - 8.79)] exp exp RT (3) 2. Michalski (2000) derived from a review of data on paper, film, dyes; considered applicable to all organic objects. (Equation (4) was used for a similar figure in previous editions of this chapter.) 1.3 100 1 Lr = 6.17 x 10-19 exp RT rh (4) 3. Strlic et al. (2015), derived from a review of data on paper; appli- cable primarily to paper and other cellulosic materials listed in Table 5. L, = 9.468x10mm 21 119 exp RT ![image](/image/placeholder) 1 5.7688 -0.0127 ln(1-rh) exp -36.72 1.677-741.82 (5) Inc. ASHRAE, 2019 user. single for Licensed | {}
770c07ca-8c80-4fda-8cbb-c8c49f5b1aad | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Museums, Galleries, Archives, and Libraries 24.13 Chart Title: TRIPLE LINES: ACETATE FLM PRESERVATION Chart Type: line A B C D E F G H I J K L M N O P Q R S T U V W X Y Z item_01 30% 30% 30% 30% 30% 30% 30% 30% 30% 30% 30% 30% 30% 30% 30% 30% 30% 30% 30% 30% 30% 30% 30% 30% 30% 30% Fig. 6 Lines of Constant Lifetime (Isoperms) for Three Models Between 20 and 60% rh, differences in the three models are neg- ligible for practical purposes (Figure 6). Beyond this humidity range, the models diverge because of the different functions selected (exponential versus power law), but this is largely irrelevant because relative humidity extremes are usually avoided (mold risk at very high values, and mechanical risks at very low values). The small dif- ferences between models on the effect of very low temperature are not because of any differences in opinion about the function (Arrhe- nius), but on the value of Ea selected, which depends on the partic- ular data set that each author emphasized: acetate film, mixed collections, or acidic paper. The Eas ofall three models fit within the shaded area of Figure 5. Essentially, in the range of20 to 60% rh and for high and low temperatures, any of the three models can be used and will provide the same practical answers. Temperature A common technical question beyond the scope of fixed stan- dards is the impact on lifetime of out-of-spec events, or seasonal fluctuations. Estimates can assume a simple linear dependence on relative humidity: for instance, if half the year is at 30% rh and half at 60% rh, then the effective annual relative humidity is the average: 45% rh. Temperature dependence, however, is far from linear, and averages cannot be used. The derived equations are general and users can select a preferred Eas but the graphs and worked examples 20°C CONSTANT TO RELATIVE LIFETIME W, g/kg RATIO HUMIDITY ![image](/image/placeholder) 1000 700 -20°C 500 300 -15°C 200 -10°C 100 70 CIRCLES FOR 1/2LIFETIME 50 -5°C 30 ○ 20 0°C 10 5°C 7 5 3 6 12 10°C 3 4 8 18 15°C 2 HOURS PER YEAR 1 0.1 1 10 100 DAYS PER YEAR OUT OF COLD STORAGE Fig. 7 Effect of Time Out of Cold Storage (Based on Michalski [2000]) assume the middle Ea value of 100 kJ/mol (the small differences of Ea of the three models do not make practical differences). A common query concerns the effect of short periods at higher temperature. The reciprocal of Equation (2) can be used to find the average rate of decay of an object that is normally at a cooler tem- perature (T) but which is at a higher temperature (Th) for a fraction f of the time. The result for net lifetime is -1 Ea 1 1 L,(Td = f+[(1-f)] exp R Th T ⑥ where Lr (T) = lifetime relative to a lifetime of 1 at Tc f= fraction of time at hotter temperature 증 temperature in colder condition, K Th = temperature in hotter condition, K There are two situations of interest: objects in cold storage that are occasionally retrieved to room temperature, and collections at room temperature that are occasionally exposed to high tempera- ture. Figure 7 plots the relationship for retrieval from cold storage, and Table 6 provides worked examples. There is no advantage to very low temperature cold storage ifthe object is retrieved frequently to room temperatures. Cold storage does not reverse the decay that progresses during warm periods. Temperatures for cold storage should be designed considering the expected retrieval pattern. Examples in Table 6 can be considered the break-even point, where the retrieval pattern has cut the potential ofthe cold temperature by one-half. Lower-temperature storage will not significantly improve remaining lifetime, unless retrieval time also diminishes. Figure 8 plots the loss oflifetime from chemical risk during peri- ods of high temperatures as compared to room temperature (20°C). An annual accumulation of about 30 days at 40°C cuts lifetimes at 20°C in half. Using high temperatures (e.g., 60°C for pest control should not exceed a total of 6 hours per year (or 60 hours each 10 years) to maintain 90% ofnormal lifetime; this is a reasonable trade- off for reducing the risk of massive insect damage. Inc. ASHRAE, 2019 user. single for Licensed | {}
4e366545-61ec-418f-b8c2-a2b90e6da2da | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 24.14 ![image](/image/placeholder) 100% 90% 80% 20°C CONSTANT 70% 55°C 45°C 35°C 25°C 60% 60°C 50°C 40°C 30°C TO 50% RELATIVE 3 6 12 40% 4 8 18 LIFETIME HOURS PER YEAR 30% 20% 10% 0% 0.1 1 10 100 DAYS PER YEAR IN HOT CONDITIONS Fig. 8 Reduced Lifetime Caused by Occasional Hot Conditions (Based on Michalski [2000]) TEMPERATURE Chart Type: line MONTH 1 MONTH 2 MONTH 3 MONTH 4 MONTH 5 MONTH 6 MONTH 7 MONTH 8 MONTH 9 MONTH 10 MONTH 11 MONTH 12 item_01 0.5 1.0 1.5 2.0 2.5 3.0 3.5 4.0 4.5 5.0 5.5 6.0 Fig. 9 Seasonal Patterns Used for Sudden and Gradual Changes Table 6 Object Lifetime and Effects of Time Out of Storage ¦ ¦ 20°C ¦ 10°C ¦ 5°C ¦ 0°C ¦ -5°C ¦ -10°C ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Relative lifetime compared to 20°C ¦ 1 ¦ 4.4 ¦ 9.6 ¦ 21.6 ¦ 50 ¦ 120 ¦ ¦ Lifetime for very low stability objects, years ¦ 30 ¦ 132 ¦ 298 ¦ 650 ¦ 1500 ¦ 3600 ¦ ¦ Time out of storage causing 50% loss ¦ ¦ 107 days/y ¦ 42 days/y ¦ 18 days/y ¦ 7.5 days/ y ¦ 3.1 days/ y ¦ ¦ Lifetime remaining ¦ ¦ 66 y ¦ 150 y ¦ 325 y ¦ 750 y ¦ 1800 y ¦ A seasonal swing in temperature can allow energy savings, espe- cially in climates with cold winters. Its benefit to collections with low chemical stability is much more important than the smaller risks from annual temperature fluctuation. Because of the exponential dependence of lifetime on temperature, summer adjustments must be balanced by even larger winter adjustments. If one assumes a typ- ical annual schedule (Figure 9) of two winter months at the lowest temperature, two summer months at the highest temperature, and four months of adjustments through the two swing seasons, then the correction between the midpoint temperature and the effective annual temperature for calculating lifetime is given by Figure 10. 2019 ASHRAE Handbook-HVAC Applications (SI) Table 7 Examples of Corrections to Temperature Midpoint to Constant to Constant ¦ Seasonal ± ¦ Correction ¦ Equal 10°C ¦ Equal 20°C ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 5 K gradual ¦ -1 K ¦ 9 士 5°C ¦ 19 士 5°C ¦ ¦ 8 K gradual ¦ -2 K ¦ 8 + 10°C ¦ 18 + 10°C ¦ ¦ 5 K sudden ¦ - 2 K ¦ 8 + 5°C ¦ 18 + 5°C ¦ ¦ 8 K sudden ¦ 4 K ¦ 6 + 10°C ¦ 16 + 10°C ¦ Chart Type: line blue_line red_line black_line item_01 2.99°C 8.63°C 5.75°C Fig. 10 Correction to Temperature Midpoint Caused by Seasonal Adjustment The correction alters slightly with the midpoint temperature (the solid lines are for near 0°C, and the dashed lines for near 20°C), but for cautious estimates at any temperature, use the solid lines. Table 7 provides several worked scenarios. For example, when the sea- sonal adjustment reaches ±5 K or more, almost all aging occurs during the summer months, and winter simply becomes a dormant period in comparison. Retrieval from cold storage raises the question of whether to build a transition space, and what procedures to use for acclimati- zation. Two risks are mitigated by a transition space: condensation during retrieval (the major risk) and direct mechanical effects of the temperature change (usually minor). A transition space adds com- plexity to cold storage construction and operation. In smaller instal- lations, it also represents a large fraction of "lost" storage. The greatest risk of condensation is during reentry to warm conditions or during failure of the cooling system, so it is essential that objects in cold storage always be inside moisture proof packaging or bags, and that these packages not be opened until the object has reached room temperature. This packaging reduces the need for tight control of relative humidity fluctuations in cold storage, because response times are many days or weeks (see Table 8). When moving from extreme cold storage (-20°C), small amounts of condensation can still form inside packages, such as film cans (Padfield 2002) and larger wrapped plastic objects, causing irreversible blanching of some plastics (Shashoua 2004, 2005, 2008) Despite these side effects, cold storage remains the only option for preserving low- chemical-stability materials (Shashoua 2014). Detailed advice for retrieval of paper, film, and magnetic media is available in the ISO standards listed in Table 4. 5.4 CRITICAL RELA TIVE HUMIDITY At a specific critical relative humidity, minerals may hydrate, dehydrate, or deliquesce. When part of a salt-containing porous stone, a corroded metal, or a natural history specimen, these miner- als cause disintegration of the object. Distinct critical relative humidity values are known for dozens of minerals in natural history collections (Waller 1992). Pyrites, which are contaminants of most Inc. ASHRAE, 2019 user. single for Licensed | {}
69de65f1-c865-42ea-bb40-cc0d7115e45e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Museums, Galleries, Archives, and Libraries 24.15 Table 8 Hygric Half-Times (near 20°C) ¦ Time Range ¦ Objects or Enclosed Objects ¦ Design Implications ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ A year or more >108 s ¦ Wooden objects at least 12 mm thick if wrapped in heavy-gage polyethylene (200 �m), with per- fect seams. Enclosures: Paintings on canvas, paper, or photographs with several layers of matboard (or buffer) framed with glass front and impermeable backing board, perfect seals except for single pressure equalization pinhole, ~15 years. If acrylic sheet, 4 mm, ~1 1 months (Michalski 2005). ¦ Risk only emerges if annual aver- age space relative humidity is unacceptable to enclosed object. ¦ ¦ ~107 s Weeks to months ¦ Large uncoated wood objects, 100 mm across the grain, 760 mm along end grain, 100 days. Books, exposed only on fore edge, tightly compressed ~25 days, if loosely compressed ~ 11 days (Derluyn et al. 2007). Bigourdan (2012) gives ~18 days, unspecified hardcover book, exposed all sides. Enclosures: Spools of 35 mm film inside metal can, 60 days (Adelstein et al. 1997). Paintings on canvas, paper or photographs with several layers of matboard (or buffer) framed with glass front and impermeable backing board, but gaps of 0.1 mm at top and bottom, 30 days. (Michalski 2005). ¦ Hourly and daily relative humid- ity fluctuations create negligible risk. Seasonal space adjustments smoothed out. Sytem loss last- ing less than a week creates little risk. ¦ ¦ ~106 s Days to a week ¦ Old panel painting, back "waterproofed," ~15 days (Stilwell and Knight 1934). Spools of 35 mm film, no can, 4 days (Adelstein et al. 1997). Uncoated wood slab, 22 mm across grain, 160 mm along end grain. Most wooden cabinetry when empty. Ivory, uncoated, handheld ~25 mm cylindrical (Lafontaine and Wood 1982). Enclosures: Paintings on canvas, paper, or photographs with several layers of matboard (or buffer) framed with glass front and impermeable backing board, but gaps of 0.5 mm at top and bottom (Michalski 2005). Hackney (1990) measured at most 6 days with glass frame and coated backing board; gaps must have determined performance. Archive box, paperboard or polypropylene, no holes, full, ~2 days (Batterham and Wignell [2008], estimated from measured damping of external daily fluctuation of x4.) ¦ Hourly and daily relative humid- ity fluctuations create little risk. System loss lasting several days can create high risk. ¦ ¦ ~105 s A day ¦ Uncoated wood slab, 8 mm across the grain, 130 mm along end grain. Ivory, uncoated, handheld ~25 mm cylindrical (Lafontaine and Wood 1982). Partial enclosures: Paintings on canvas with continuous paint layer and impermeable backing board applied to frame (Di Pietro and Ligterink 1999). ¦ Hourly relative humidity fluctua- tions create little risk. System loss lasting all day can create high risk. ¦ ¦ ~104 s Hours ¦ Bare acrylic paint, medium-thick layer. Bare oil paint, alkyd paint, thin layers. Uncoated wood, wood fiber boards, leather, skin, 3 mm thick. ¦ Hourly relative humidity fluctua- tions or system loss can create risk. ¦ ¦ <103 s Few minutes or less ¦ Single sheet of paper, 4 min (Kupczak et al. 2018b). Includes book pages that are fanned open. Thin sheet of parchment, ivory. Thin layers of watercolor paint, gouache. Feathers, fur, hair. Lightweight textiles, costumes. Gelatin layer of photographic print or film. Sized canvas used for paintings. ¦ Relative humidity fluctuation or system loss of only a few min- utes can create risk. (Museums rarely display these objects unenclosed.) ¦ Note. All plates considered exposed both sides unless noted otherwise. Adelstein et al. (1997) and Bigourdan (2012) reported 90% response times, converted here to halftimes by x0.3 assuming exponential decay. Derluyn et al. (2007) measured a 50 mm square experimental book, closed on all sides but fore edge. Their times have been adjusted to a more realistic 100 mm depth, so x4 (square law) is applied. Estimates from Michalski (2005) based on material data plus enclosure leakage equations. Wood objects and furniture based on Figures 11 and 12. Others are based on calculations using Equation ⑦ for a plate and diffusion coefficients from the literature. fossils, disintegrate ifheld above 60% rh (Howie 1992). Bronze, one of the most important archaeological metals, has a complex chem- istry of corrosion, with several critical relative humidity values. This variety means there is no universal safe relative humidity; particular conditions should be achieved for specific artifacts with local cabi- nets or small relative-humidity-controlled packages (Waller 1992). The only generalization is that any relative humidity above 75% is dangerous. Rapid corrosion above 75% rh occurs for two reasons: increased surface adsorption of water, and contamination by salts. Water adsorption on clean metal surfaces climbs rapidly from 3 molecules or less below 75% rh to bulk liquid layers above 75% rh (Graedel 1984). This phenomenon is aggravated by most surface contami- nants, as shown in studies ofthe role of dust on clean steel corrosion. The most common contaminant of museum metals, sodium chlo- ride, dissolves and liquefies (deliquesces) above 76% rh. Glass collections, objects with glass bead decoration, and stained glass may contain a type of historic glass that is very sensitive to incorrect relative humidity because of deliquescence of unstable constituents. A stable 40% rh is recommended. See van Giffen et al. (2018) for detailed recommendations on climate control for various types of historic glass. Response Times of Artifacts Approximate thermal response times of objects are familiar from common experience, and their calculation is described in Chapter 25 of the 2017 ASHRAE Handbook-Fundamentals. This section focuses on the response time that is much less familiar to most engineers, but much more important to preservation science: hygric response times. Table 8 provides hygric half-times for common objects and enclosed objects in cultural institutions. Where direct measure- ments are available, these have been cited; other estimates are based on calculations. Lower temperatures greatly increase all these times (Adelstein et al. 1997); conversely, higher temperatures shorten Inc. ASHRAE, 2019 user. single for Licensed | {}
e7de5e00-42b0-4ae8-9b39-d94509913677 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 24.16 2019 ASHRAE Handbook- -HVAC Applications (SI) them. Response times at least double for each drop of 10 K: for example, x2 for cool conditions, x4 for cold, x8 or more for freezing storage. The hygric half time of a plate (a shape that applies to many cul- tural objects, or that provides an upper bound to cylinders, cubes, spheres, etc) is given by Crank (1979) as T1/2 = 0.049 ID (7) where TV2 = half-time of enclosure system, s L = thickness of plate (or sheet), m D = diffusion coefficient, m2/s Some estimates in Table 8 are based on Equation (7) and diffusion coefficients found in the literature on polymers. An object with a surrounding moisture barrier (coating or enclosure) can be simpli- fied as a series of two resistances to moisture flow. Figure 1 1 was generated using this approach, with wood data from Siau (2012) for medium-density wood near 50% rh. When barriers provide useful resistance (upper lines in each plot in Figure 1 1), the plots have a slope of 1 (linear). When coatings provide negligible resistance (e.g., the boundary layer of air in a calm room), the slope changes to the square law of Equation (7). There is only a slight curve as thick- ness drops to 1 mm across the grain. As Kupczak et al. (2018b) show, the contribution of the boundary layer of air, though measur- able, is far from rate determining even for a single sheet of paper. In practical terms, although thinner objects (e.g., a violin, ivory minia- ture, paper sheet) respond more quickly, they benefit greatly from even simple coatings or enclosures, whereas massive objects do not. Figure 12 was generated using the same series resistances model, but using leakage equations for an enclosure found in Michalski (1994). The horizontal plateaus are in the region where crack leak- age is insignificant, and the wood coating dominates halftime. The slopes are the region where leakage (infiltration) dominates, and the knees indicate which size cracks are worth blocking. The humidity half-time of a leaky enclosure with a hygroscopic material (objects or additional buffers) can be expressed in terms of the fraction of the enclosure volume filled with the buffering mate- rial (Michalski 1994): Vhap TV2 = 0.69 V。NC ws (8) where T1/2 = half-time of enclosure system, s, h, or days (depends on leakage units) Vh = volume of hygroscopic material, m3 Ve = volume of enclosure, m3 a = hygric capacity (slope of moisture isotherm) kg/kg P = bulk density of hygroscopic material, kg/m3 N = leakage, air changes per s, per h, or per day Cws = concentration of water in air at saturation, kg/m3 The critical role of leakage N for enclosed objects can be seen in Table 8 for paintings or works on paper in a sealed glass frame (increasingly used by major galleries, especially for loaned paint- ings.) Depending on tiny differences in crack width, performance can change by orders of magnitude. This is because of the key role of infiltration in determining N, and the fact that infiltration varies with the cube of crack width (laminar flow) (Michalski 1994). Equation (8) can be reduced to an estimate for materials such as paper, wood, leather, and dense fabrics near room temperature (20°C), where C, ws 0.0173 kg/m3. Using a conservative density of = P = 600 kg/m3 and a conservative hygric capacity of a = 0.05, then Chart Type: line ACROSS GRAIN THICKNESS, mm ALONG GRAIN LENGTH, mm item_01 100Days 100Days ing name on in ng/Pa・ m2.s. Use the graph 1000 LIGHT VARNISH that gives the fastest response. 10 000 CALM AIR LAYER Fig. 11 Calculated Humidity Response Times of Wooden Artifacts Chart Type: line 0. 1 5 item_01 10Days 100Days 1000Days ¦ Calculated for 15 mm deep crack at top and bottom drawers, average wood ¦ ······· 3 ¦ 200 �m POLYETHYLENE BAG, NO LEAKS ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ thickness 10 mm, coating exterior only, ¦ ·······30 ¦ MANY COATS OF OIL PAINT ¦ ¦ chest 1.5 mm high, 1 m wide, 0.5 m ¦ ..... 100 ¦ HEAVY VARNISH OR PAINT ¦ ¦ deep. Stack due to 40% rh or 1°C differ- ¦ ・・・・・・・ 300 ¦ MEDIUM VARNISH OR PAINT ¦ ¦ ence. Numbers preceding coating name on plots are permeance in ng/Pa · m2 · S. ¦ 1000 ¦ LIGHT VARNISH ¦ ¦ ¦ 10 000 ¦ CALM AIR LAYER ¦ Fig. 12 Interaction of Air Leakage, Wood Coating, and Textile Buffering on Response of w ooden Chest of Drawers Inc. ASHRAE, 2019 user. single for Licensed | {}
6c100a41-4bcf-48e8-8235-468b3d783c99 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Museums, Galleries, Archives, and Libraries 24.17 Vhap Tv2 ~ 0.69 V N A leakage rate of 1 air change per day (acd) is considered a suit- able design target for airtight museum display cases (Thickett et al. 2007), so an enclosure half full of wood or paper (Vh/Ve = 1/2) would give a half-time of 600 days. In practical terms, very tight enclosures are rarely very full enclosures (although wrapping large wooden objects in heavy-gage, perfectly sealed polyethylene can achieve this). Half-full enclosures are generally cabinets or crates, and they leak closer to 1 air change per hour (ach), which still pro- vides a 25 day half-time. A tight display case of 1 ach rarely has more than 10% of its volume filled with hygroscopic material, resulting in half-times up to 120 days. In practice, it is difficult but not impossible to design and maintain very low infiltration. An inevitable concern with enclosures is the humidity fluctua- tion driven by a thermal fluctuation. This worry first emerged in the 1960s for works of art in shipping crates, but Toishi (1959) showed that if a sealed crate contained hygroscopic material, it would stabi- lize its relative humidity despite drops from room temperature to freezing and back. Stolow (1966) provided complete data and equa- tions for the counter-intuitive finding that, with natural hygroscopic materials, case humidity even drops slightly when temperature drops (the opposite of empty enclosures) because of the slight downward shift of moisture isotherms at lower temperature. Thomson (1964) showed that the transition point between relative-humidity- controlled enclosures and empty-enclosure behavior for hygro- scopic materials such as wood occurred at about 1 kg/m3, and humidity control was fully in place by 10 kg/m3 (about 2% full by volume). Later authors examined further side effects such as mixed thermal/hygric dimensional response in wood (Richard 2007) and condensation in air pockets during cold storage retrieval (Padfield 2002; Shashoua, 2005, 2008) but the general consensus is that such occasional side effects do not outweigh the benefits (Richard 2007; Shashoua 2014). 5.5 AIRBORNE POLLUT ANTS/ CONT AMINANTS Sources From the outdoors, different-sized particles can infiltrate muse- ums. Gaseous outdoor pollutants such as nitrogen dioxide and ozone can also penetrate buildings, including modern HV AC-equipped construction, when gas filtration is not present to remove them. Within buildings, sources of airborne pollutants include institutional activities such as food preparation, service vehicles in the loading dock, and renovation (e.g., preparation of new exhibitions). Con- struction products such as wood, paints, adhesives, and sealants, especially by-products formed by chemical curing or solvent release, can be important sources of gaseous pollutants. Collections them- selves can be sources of pollutants that can affect other objects nearby; examples include archival materials such as cellulose nitrate and acetate films, as well as acidic papers. Collections made of nat- ural organic materials such as leathers, fur, and wood elements can also release harmful volatile compounds. The metabolism of staff and visitors further contributes to airborne pollutants, and introduces coarse particles from skin cell shedding and clothing. It is important to understand that the impact of gaseous pollutants varies according to the sensitivity of each material (i.e., acetic acid corrodes lead but is harmless to silver; silver is very sensitive to hydrogen sulfide, but lead is minimally affected). In other words, the potential damage is very specific to each pollutant/material system and the damage caused to objects by pollutants is usually cumulative, irreversible, and disfiguring. Table 9 presents a list of objects sensitive to various pollutants and pollutant sources. Impact (9) Dust deposition is a general problem for all collections. More precisely, dust deposition impacts objects' aesthetic appearance and affects conservation considerations (e.g., cleaning frequency, risk involved during treatments). Coarse dust is relatively easy to remove from robust surfaces such as flat glasses or metals, but dif- ficult to remove from fragile surfaces such as feathers. Particles gen- erated by people are not usually removed by HVAC filters. Fine particles such as black soot pose a particular challenge. This is a typ- ical problem for museums in the vicinity of high-volume diesel vehicle traffic. Special conservation skills are needed to remedy this situation, but there are cases where the soot cannot be removed (e.g., soot entrenched in the cracks of an ivory sculpture, soot in fragile textiles that may be significantly physically damaged by cleaning treatment). The deterioration process caused by airborne pollutants can be enhanced in the presence of water vapor. This has a relevant impact on objects both in a direct and indirect way. In the presence of high relative humidity, many processes of deterioration accelerate. An example of an indirect effect that is greatly affected by high relative humidity, especially above 75% rh, is the increase in corrosion rates of many metals by pollutants. For example, formaldehyde does not corrode lead at 75% rh, but corrosion can occur at higher humidities (Thickett 1997). Water vapor can directly affect some materials (e.g., cellulose papers, cellulose acetate, nitrate plastic films) by hydrolysis. With just moisture in the cellulose, deterioration is slow, but increases when acids are present. This reaction is called acid catalyzed hydrolysis. Over time, the acids present as by-products of cellulose degradation increase, which further speeds up the reac- tion (Dupont et al. 2007; Zou et al. 1996). To maximize preservation of objects affected by pollutants, it is usually better to keep relative humidity low, particularly for metal objects. However, the environ- ment must be compatible with the appropriate humidity range estab- lished for preservation of organic or composite collections. Oxygen in the indoor environment also may react with objects. Natural rub- ber is particularly known to degrade by oxidation, and many colo- rants are vulnerable to fading in the presence of oxygen and light. Some work has been done to quantify the impact of pollutants on various materials, based on the concept of the lowest observable adverse effect dose (LOAED). This dose is derived using the rec- iprocity principle: ifa critical adverse effect is observed on an object after 1 month at 1000 parts per billion (ppb) of a pollutant, the same damage could occur after 10 months at 100 ppb. When extensive data exist for a pollutant/material system, a no observable adverse effect level (NOAEL) can be determined with some confidence. After studying the effect of acetic acid on (untarnished and pure) lead at different concentrations and relative humidity levels for a year, Tetreault et al. (1998) established a NOAEL for the acetic acid/ lead system at 430 �g/m3 or 170 ppb. Extensive sets ofLOAED and some NOAEL data have been compiled by Tetreault (2003). Note that concentrations of gaseous pollutants can be reported in either volumetric units (ppb), which are temperature and pressure dependent, or in gravimetric units (ug/m3), which are temperature and pressure independent. To standardize reporting for volumetric units, the Compressed Air and Gas Institute (CAGI 2012) recom- mends using standard conditions of 20°C and 100.0 kPa. IAQ in Museums and Archives (IAQ 2016) provides an online concentra- tion converter for major pollutants. In general, there are three scenarios where objects can be at risk in museums: · Outdoor pollutant infiltration is a problem in polluted areas where unprotected objects in rooms are exposed to outdoor pol- lutants that were not adequately blocked at the building level (envelope and filtration). Soot deposition and tarnishing of silver and copper by reduced sulfur compounds are common damage Inc. ASHRAE, 2019 user. single for Licensed | {}
17e5fe3c-5f2d-4f86-83a5-2afd973de8b8 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 24.18 2019 ASHRAE Handbook-HVAC Applications (SI) Table 9 Airborne Pollutants: Sources and High- Vulnerability Materials Inc. ASHRAE, 2019 user. single for Licensed ¦ Airborne Pollutants ¦ Indoor and Outdoor Sources ¦ Effects on Materials ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Aldehydes (RCHO) ¦ Formaldehyde: formaldehyde-based resin in wood products, solid wood, paints and adhesives, natural history wet specimen collections, permanent press fabrics. Acetaldehyde: paints, adhesives, solid woods. Low-molecular-weight aldehydes can be transformed into their respective carboxylic acids in presence of strong oxidant such as peroxides released by oil-based paints or any paint films formed by oxidative polymerization. ¦ Formaldehyde: Corrosion of lead at high relative humidity (>75%). ¦ ¦ Amines (RNR) ¦ Ammonia (NH3): alkaline-type silicone sealants, concrete, emulsion adhe- Ammonia: blemishes on on cellulose sives and paints, household cleaning products, visitors, animal excrement, Other amines: thought to fertilizer and inorganic process industries, underground bacterial activi- corrosion of bronze, copper, ties. If combined with sulfate or nitrate compounds, it can form ammo- nium salts. Cyclohexylamine (CHA), diethylamino ethanol (DEAE), and octadecyl- amine (ODA): corrosion inhibitor in humidification systems, some vapor corrosion inhibitors. ¦ ebonite and efflorescence nitrate. be responsible for blemishes on paintings and and silver. ¦ ¦ Carboxylic acids (RCOOH) ¦ Acetic acid (CH3COOH): acid-type silicone sealants (acetoxy cure), deg- radation of organic materials and objects such as cellulose acetate-based objects (vinegar syndrome) and wood products, most paints, flooring adhesives, human metabolism, linoleum, microbiological contamination of air-conditioning filters, oil-based paints, photographic developing products, some "green" cleaning solutions. Formic acid (HCOOH): degradation of organic materials, oil-based paints, wood products. Fatty acids (RCOOH): burning candles, cooking, flooring adhesives, human metabolism, linoleum, lubricant in HVAC systems, microbiologi- cal activities from air-conditioning or on objects, objects made of animal parts (including skins, furs, insect collections), oil-based paints, papers, paper and wood products, vehicle exhaust. ¦ Acetic and formic acids: corrosion of copper alloys, cadmium, lead, magnesium, and zinc; efflorescence on calcareous materials (e.g., shells, corals, limestones, calcium-based fossils); fading of some colo- rants; efflorescence on soda-rich glass objects; lowering degree of polymerization of cellulose. Fatty acids: blemishes on paintings; corrosion of bronze, cadmium, and lead; ghost images on glass; yellowing of papers and photographic doc- uments. ¦ ¦ Nitrogen oxide compounds (NOx) ¦ Nitric oxide (NO): agricultural fertilizers, fuel combustion from vehicle paper, some artists' colorants, exhaust and thermal power plants, gas heaters, and photochemical smog. of Nitrogen dioxide (NO2): degradation of cellulose nitrate and same sources as for NO, but mainly from oxidation of atmospheric NO. Nitric acid (HNO3) and nitrous acid (HNO2): oxidation ofNO2 in the atmosphere or on a material's surface, and the degradation of cellulose nitrate. ¦ Deterioration of fading of enhance the deterioration effect SO2 on leather and on metals. ¦ ¦ Oxidized sulfur gases (SO2 and H2SO4) ¦ Sulfur dioxide (SO2): degradation of sulfur-containing materials and objects such as proteinaceous fibers, pure pyrite or mineral specimens containing pyrite sulfur dyes, sulfur-vulcanized rubbers, petroleum refin- eries, pulp and paper industries, combustion of sulfur-containing fossil fuels. Sulfuric acid (H2SO4): oxidation of SO2 in the atmosphere or on a mate- rial's surface. ¦ Acidification of paper, corrosion of copper, fading of some artists' colo- rants, weakening of leather. ¦ ¦ Ozone (O3) ¦ Electronic arcing, electronic air cleaners, electrostatic filtered systems, insect electrocuters, laser printers, photocopy machines, UV light sources, photochemical smog. ¦ Fading of some artists' colorants, dyes, and pigments; oxidation of organic objects with conjugated double bonds such as rubber; oxidation of volatile compounds into aldehydes and carboxylic acids. ¦ ¦ Particles and coarse) ¦ (fine General: aerosol humidifier; burning candles; concrete; cooking; laser printers; renovations; spray cans; shedding from clothing, carpets, pack- ing crates, etc. (due to abrasion, vibration, or wear); industrial activities; outdoor building construction; soil. Ammonium salts: reaction of ammonia with SO2 or NO2 in indoor or out- door environments or on solid surfaces. Biological and organic compounds: microorganisms, degradation of mate- rials and objects, visitor and animal danders, construction activities. sea salt aerosol, fossil combustion. Chlorine Soot (organic carbon): burning candles, fires, coal combustion, vehicle exhaust. ization ¦ General: abrasion of surfaces (critical for magnetic media), discoloration of objects (especially critical for those with surfaces with interstices [pores, cracks, or micro-irregularities] that entrap dust), may initiate or increase corrosion processes due to their hygroscopic nature. Ammonium salts: corrosion of copper, nickel, silver, and zinc; blemishes on varnished painting and furniture with natural resins and on ebonite; white deposit on object surface; lowering of the degree of polymeriza- tion of cellulose. Chlorides: compounds: increase of rate of metal corrosion. Soot: discoloration of porous surfaces (painting, frescoes, statues, books, textiles, etc.), increased rate of metal corrosion. Carbon and metallic elements such as iron and magnesium can lower the degree of polymer- of cellulose. Reduced ¦ ¦ sulfur (S-) ¦ Carbon disulfide (CS2): polysulfide-based sealants; fungal growth; rotting gases organic matter in oceans, soils, and marshes. graphic Carbonyl sulfide (OCS): degradation of wool, coal combustion, coastal soils, and wetlands, oxidation of carbonyl disulfide. Hydrogen sulfide (H2S): arc-welding activities, mineral specimens con- taining pyrite, sulfate-reducing bacteria in impregnated objects excavated from waterlogged sites, polysulfide sealants, vulcanized rubbers, visitors, fuel and coal combustion, marshes, ocean, petroleum and pulp industries (kraft process), vehicle exhaust, volcanoes. ¦ Corrosion of bronze, copper, and silver; discoloration of silver photo- images; darkening of lead pigments. ocean, ¦ Source: Adapted from Tetreault (2003). | {}
5fd96ccb-1103-47a4-be61-9f8546b17e58 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Museums, Galleries, Archives, and Libraries 24.19 · · observed under those conditions. An assessment must be done to decide if better control should be carried out at the building level or if some objects should be placed in enclosures such as display cases, glazed frames, or storage containers. For protection against pollution and for security reasons, many small objects are placed in display cases, and paintings can be placed in glazed frames, but not all items on exhibition or in storage can be enclosed. With pollutants generated in small enclosures, products used to build the enclosure and the objects themselves can release volatile compounds (typically carboxylic acids and reduced sulfur gases), which can react with the objects housed within. Their concentra- tions can remain high for a long period if they cannot be exfil- trated or sorbed adequately. The best preventive solution is to carefully select construction products and to evaluate objects' potential emissions. If problematic products or objects cannot be removed from the enclosure, the second-best approach is usually to reduce the pollutant concentration in the enclosure by increas- ing the air exchange rate. However, an assessment is needed to determine which degree of airtightness is most suitable. The assessment must consider the concentration of pollutants in the room and in the enclosure, as well as the nature of both the pol- lutants and objects in the enclosure. Indoor-generated pollutants are similar to off-gassing in enclo- sures, but at a room scale. Objects displayed in a room with insuf- ficient ventilation and with a high load of emissive materials can be at risk if pollutant concentrations become significant. Sources in the room can be products such as wood and paint, collections made of natural organic materials, and emissions from human activities such as cooking, renovation, or burning incense in reli- gious buildings. Indoor pollutants can also affect people in the space, and the relation between air pollution and the health and comfort of building occupants is the focus of indoor air quality (IAQ) guidance, such as ASHRAE Standard 62.1. Possible solu- tions for minimizing the impact of indoor pollutants are to increase the ventilation, and to consider gas filtration systems or enclosures. More information on the issue of pollutants in museums and his- torical buildings can be found in Anaf et al. (2015), Bellan et al. (2000), Bonacina et al. (2015), Grau-Bove and Strlic (2013), Grzy- wacz (2006), Hatchfield (2002), Lloyd et al. (2007), Mleczkowska et al. (2016, 2017), Nazaroff et al. (1993), Paterakis (2016), Pretzel (2003), and Tetreault (2003, 2017, 2018). 6. DESIGN PARAMETERS FOR PERFORMANCE TARGET SPECIFICATIONS 6.1 CLIMATE LOADS Climate loads include above- and below-grade liquid water loads from rainfall; thermal loads from conduction, convection, and radi- ation; thermal and moisture vapor loads from infiltration (especially when driven by stack effect); and vapor transport through permeable envelope assemblies. ASHRAE Standard 169-2013 provides a methodology for defin- ing climatic regions based on thermal and moisture characteristics using nine thermal zones (0 to 8: extremely hot to subarctic), based on heating and cooling degree days, and three moisture zones (A, B, or C: humid, dry, or marine) calculated using precipitation and tem- perature data. The climate zone classification is useful for differen- tiating climate regions when considering envelope performance. Table 10 and Figure 13 indicate climate zones for typical cities and geographic locations throughout the world. Figure 14 provides a higher-resolution map of climate zones in the United States. ASHRAE Standard 1 69-2013 provides an extensive list oflocations and their climate zone classification. ASHRAE Standard 169-2013 also provides comprehensive location-specific climate data for calculations of loads for system and envelope design. Engineering Weather Data, published by the National Climate Data Center of the National Oceanic and Atmo- spheric Administration (NOAA 1997), includes informative graph- ics for visualizing seasonal variations in data, but the dataset is older. When using statistical climate data for design, consider not only maximum and minimum design conditions, but also the poten- tial variability of thermal and moisture conditions in a given season; for example, in zones 3A, 4A, and 5A, thermal and moisture loads may change rapidly during spring and autumn. In some climate zones, seasonal dehumidification may not be coincident with large sensible cooling loads; thus, systems may have to be designed for dehumidification independent of cooling. Bulk moisture from precipitation, especially wind-driven rain, can be a significant moisture load on envelopes above grade. Depending on soil type and site management of stormwater runoff from roofs and at-grade surfaces, rain can also affect moisture loads on subgrade portions of the building. However, even in climate zones classified as dry (B), infrequent but high-intensity rain events can result in significant short-term moisture loads on the building and soil. The design service life and envelope durability of purpose-built museum buildings may be as long as 100 years. Design for climate loads on building envelopes should consider projections for climate change and their impact on future thermal, moisture, and bulk mois- ture loads on the building, consistent with the design service life of a building, its envelope assemblies, and environmental management systems. 6.2 BUILDING ENVELOPE The building envelope mediates exchange of thermal energy and moisture between the interior and the exterior environments, both above and below grade. Above grade, the building envelope typi- cally consists of wall assemblies, wall closure assemblies such as windows and doors, and roof assemblies. Below grade, the building envelope consists of foundation wall assemblies and floor assem- blies in contact with soils. The envelope mediates movement or transport of water, air, water vapor, and thermal energy. Flows that are not effectively mediated by the envelope result in thermal and moisture loads that must be addressed by mechanical systems; unmediated loads have implications for energy efficiency. Performance Requirements. Envelope performance needed to effectively and efficiently perform the four control functions (water [bulk moisture], air, water vapor, and thermal energy) depends on the exterior climate and desired interior conditions. Table 1 1 lists the types of climate control recommended for collections preserva- tion and identifies the envelope performance needed to achieve that control in different climate zones. For a given combination of con- trol type and climate zone, the necessary envelope performance for each function is identified as controlled, moderated, or optional. Table 12 provides examples of typical envelope features or assem- blies that correspond to these terms. Table 11 also includes con- siderations that should be addressed in design and for some combinations of exterior climate and interior type of control, and identifies whether hygrothermal analysis of the envelope is needed, recommended, or optional for the different combinations of type of control and climate zone. Hygrothermal analysis using dynamic transient modelling is preferred, but static-equilibrium analysis may be sufficient in some instances. Inc. ASHRAE, 2019 user. single for Licensed | {}
c355e39f-adb5-40ad-823c-f0dcea6eb59a | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 24.20 2019 ASHRAE Handbook-HVAC Applications (SI) ![image](/image/placeholder) Zone 0A Extremely Hot Humid Zone 0B Extremely Hot Dry Zone 1A Very Hot Humid Zone 1B Very Hot Dry Zone 2A Hot Humid Zone 2B Hot Dry Zone 3A Warm Humid Zone 3B Warm Dry Zone 3C Warm Marine Zone 4A Mixed Humid Zone 4B Mixed Dry Zone 4C Mixed Marine Zone 5A Cool Humid Zone 5B Cool Dry Zone 5C Cool Marine Zone 6A Cold Humid Zone 6B Cold Dry Zone 7 Very Cold Zone 8 Subarctic/Arctic Fig. 13 World Map of Climate Zones (ASHRAE Standard 169-2013) ![image](/image/placeholder) Dry (B) Moist (A) Marine (C) Zone 0A Extremely Hot Humid Zone 4B Mixed Dry Zone 0B Extremely Hot Dry Zone 4C Mixed Marine Zone 1A Very Hot Humid Zone 5A Cool Humid Zone 1B Very Hot Dry Zone 5B Cool Dry Zone 2A Hot Humid Zone 5C Cool Marine Zone 2B Hot Dry Zone 6A Cold Humid Zone 3A Warm Humid Zone 6B Cold Dry Zone 3B Warm Dry Zone 7 Very Cold Zone 3C Warm Marine Zone 8 Subarctic/Arctic Zone 4A Mixed Humid Fig. 14 Climate Zones in United States (ASHRAE Standard 169-2013) Inc. ASHRAE, 2019 user. single for Licensed | {}
e5554837-859f-4ecb-ae0f-6bb347aedc7c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Museums, Galleries, Archives, and Libraries 24.21 Table 10 Climate Zone Classifications for Select World Cities ¦ Climate Zone ¦ Type ¦ Location ¦ Climate Zone ¦ Type Location ¦ Climate Zone ¦ Type ¦ Location ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 0A ¦ Extremely hot, humid ¦ Recife (Brazil) Bombay (India) Manila (Philippines) ¦ 3A Warm, humid ¦ Sydney (Australia) Shanghai (China) Atlanta (United States) ¦ 5A ¦ Cool, humid ¦ Toronto (Canada) Berlin (Germany) Chicago (United States) ¦ ¦ 0B ¦ Extremely hot, dry ¦ Ahmedabad (India) Niamey (Niger) Riyadh (Saudi Arabia) ¦ 3B Warm, dry ¦ Athens (Greece) Tehran (Iran) Los Angeles (United States) ¦ 5B ¦ Cool, dry ¦ Rio Gallegos (Argentina) Taiyuan (China) Denver (United States) ¦ ¦ 1A ¦ Very hot, humid ¦ Hanoi (Vietnam) Mombasa (Kenya) Miami (United States) ¦ 3C Warm, marine ¦ Nairobi (Kenya) Cape Town (S. Africa) San Francisco (United States) ¦ 5C ¦ Cool, marine ¦ Esquel (Argentina) Corum (Turkey) Bremerton (United States) ¦ ¦ 1B ¦ Very hot, dry ¦ Luxor (Egypt) Lahore (Pakistan) Dakar (Senegal) ¦ 4A Mixed, humid ¦ Beijing (China) Paris (France) Philadelphia (United States) ¦ 6A ¦ Cold, humid ¦ Oslo (Norway) St. Petersburg (Russia) Minneapolis (United States) ¦ ¦ 2A Hot, humid 2B Hot, ¦ dry ¦ Sao Paulo (Brazil) Haifa (Israel) Dallas (United States) Cairo (Egypt) Lima (Peru) Phoenix (United States) ¦ 4B Mixed, dry 4C Mixed, marine ¦ Kabul (Afghanistan) Adelaide (Australia) Albuquerque (United States) Brussels (Belgium) Santiago (Chile) Portland (United States) ¦ 6B 7 8 ¦ Cold, dry Very cold Subarctic ¦ Chifeng (China) Bozeman (United States) Ulaanbaatar (Mongolia) (United Anchorage States) Yellowknife (Canada) Fairbanks (United States) ¦ Source: ASHRAE Standard 169-2013. Design Considerations. Interior environmental requirements for buildings containing collections are typically more stringent than those for human health and thermal comfort, particularly for relative humidity. Depending on the differences between the exterior and interior conditions, there may be large differences in temperature and moisture vapor across the building envelope. The resultant thermal, pressure, and moisture gradients between the exterior climate and the collections spaces have implications for envelope performance. In new buildings, high-performance building envelopes address thermal and moisture gradients with layered sequences of function- ally specific materials such as air barriers, thermal insulation, and vapor retarders/barriers. Older building envelopes typically used thick assemblies of fewer materials, consistent with contemporary expectations for envelope performance, building occupancy, and use. Many existing museum buildings constructed in the mid to late 20th century may have envelope assemblies similar to current high- performance envelopes, but the quality of materials, design details, or construction/installation may compromise their performance. Furthermore, many collections are housed in existing buildings that are considered significant cultural heritage in their own right; these are not limited to historic buildings, and can include architec- turally significant buildings of the late 20th century. The building envelope of historic or architecturally significant buildings is likely to be considered character defining, and changes or alterations to the envelope may be subject to preservation criteria. ASHRAE Guide- line 34-2018 provides useful information on improving the energy performance of historic building envelopes. An existing building envelope's performance possesses both strengths and liabilities for environmental management for collec- tions. It may have high thermal mass and moisture capacity that can buffer interior and exterior fluctuations of thermal energy and mois- ture; these passive, or nonmechanical, aspects of envelope perfor- mance can be beneficial during extreme weather events or when mechanical systems are disabled. Many older building envelopes have poor air control perfor- mance, especially at envelope penetrations around windows and doors, as well as the windows and doors and their operable elements. In older buildings originally designed for natural ventilation, inten- tional stack effect in large stair halls and through skylights above gal- leries may exacerbate high exchange rates through windows and doors, even when the assemblies have been upgraded. Vapor control performance of existing wall and roof assemblies is typically inadequate for the differences between exterior and interior moisture vapor that must be maintained for some collections. Steep moisture gradients across envelope assemblies can drive moisture transport, with consequential damage to the building. Examples of damage in masonry or concrete wall assemblies include migration of soluble salts, freeze-thaw cycling, coatings failures or condensation. In wall assemblies with wood, damage may occur from moisture sat- uration and microorganism activity. Vapor control performance can be difficult to incorporate in an existing building envelope. As a result, depending on the climate zone, vapor control performance of an existing envelope may define the interior relative humidity level that can be safely maintained without risk of damage to the envelope. When improved vapor control is necessary in an existing build- ing, it may be appropriate to enclose the collections space with a new vapor-controlled interior partition, separated from the interior face of the exterior wall by a substantial air space. This approach, often called box-in-box, effectively cascades the total moisture gra- dient across multiple assemblies, decreasing the moisture gradient across the exterior wall assembly, and can effectively resolve air control issues. This approach may be applied to roof and ceiling assemblies when necessary. In any case, identification of effective performance improve- ments for existing building envelopes must be based on evidence Inc. ASHRAE, 2019 user. single for Licensed | {}
5017d628-6c2a-476c-ac98-e31936fac90f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 24.22 2019 ASHRAE Handbook- -HVAC Applications (SI) Table 11 Type of Control, Climate Zone, and Typical Envelope Performance Necessary ¦ ¦ Liquid Water Loads (Table 12) ¦ Liquid Water Loads (Table 12) ¦ Hygrothermal Loads (Table 12) ¦ Necessary Envelope Performance (Table 12) ¦ Design Considerations ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Type of Control ¦ Rain Exposure (Moisture Zone) ¦ Source Moisture ¦ International Climate Zone(s) ¦ Air Leakage Thermal and Stack Moisture Hygrothermal Flows Effect Vapor Analysis ¦ Comments ¦ ¦ ¦ ¦ ¦ AA ¦ All ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Precision control A1, A2 Precision control with seasonal changes ¦ All All All ¦ All 5A, 5B, 5C colder ¦ ¦ ¦ Building envelope should be separated from interior enclosure of collections space. Building envelope should be separated from interior enclosure of collections space. Building envelope should be separated from interior enclosure of collections space. ¦ ¦ ¦ ¦ ¦ B ¦ All ¦ and 4A, 4B, 4C 3A, 3B, 3C and warmer 6A, 6B, and colder ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Limited control with seasonal changes ¦ All All All ¦ 5A, 5B, 4A, 4B, 3A, 3B 5C, 4C, 3C 2A, 2B and warmer All B ¦ ¦ ¦ Where diurnal temperature differences are large, insulation may be needed to prevent high relative humidity at night caused by cooling. ¦ ¦ ¦ ¦ ¦ Prevent relative humidity extremes ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ C ¦ All All ¦ 5C, 4C, 3C All other zones ¦ ¦ ¦ Moderated or controlled envelopes can eliminate or substantially reduce size of HVAC equipment. ¦ ¦ ¦ ¦ ¦ D ¦ All ¦ All B ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Prevent very high relative humidity ¦ ¦ ¦ ¦ ¦ Where diurnal differences are prevent ¦ ¦ ¦ ¦ ¦ ¦ All ¦ ¦ ¦ ¦ temperature large, insulation may be needed to high relative humidity at night caused by cooling. ¦ ¦ ¦ ¦ ¦ ¦ All All ¦ 5C, 4C, 3C All other zones ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ All ¦ ¦ ¦ ¦ Moderated or controlled envelopes can eliminate or substantially reduce size of HVAC equipment. ¦ ¦ ¦ ¦ ¦ Cool store ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ All ¦ ¦ ¦ Specialized collections enclosures separate from the exterior building envelope are typically used. Where cooling loads are low (e.g., climate zone 6 and colder) and in some subgrade locations, specially designed exterior envelopes can achieve this performance without a separate interior enclosure. ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Cold or "frozen" store ¦ All ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ All ¦ ¦ ¦ Specialized collections enclosures separate from the exterior building envelope are typically used. ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Relative humidity controlled below ¦ ¦ All ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ critical value ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Legend: ¦ All ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Vapor control is a priority in moisture zones A and C, and thermal control is typically needed to maintain relative humidity stability below critical values. ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Optional Optional ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Moderated ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Controlled Necessary ¦ Recommended ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Moisture and hygrothermal loads Hygrothermal analysis ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Inc. ASHRAE, 2019 user. single for Licensed | {}
90e216f5-dbb5-4f0c-8788-e7143258658f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Museums, Galleries, Archives, and Libraries 24.23 Table 12 Examples of Typical Envelope Assemblies or Features ¦ Loads ¦ Minimum Performance Examples ¦ ¦ --- ¦ --- ¦ ¦ Liquid water loads ¦ Source moisture control is typically achieved by intercepting and diverting rain and surface and subgrade water away from above- and below-grade parts of building envelope. Examples: roof drainage systems; surface water drainage systems, including swales and piped systems; drainage planes in above-grade walls; subgrade drainage systems consisting of waterproofing, drainage planes on subgrade walls and under slabs, and subgrade piping. ¦ ¦ Thermal flows ¦ Controlled thermal flows are typically achieved by building envelopes that meet current ASHRAE Standard 90.1 requirements for building envelopes. Moderated thermal flows are typically satisfied by · Climate zones 4 and higher: building envelopes with robust wall construction and thermal mass, retrofitted insulation, storm windows, or insulated glazing and insulated ceiling planes in the uppermost story attics in climates zones 4 and higher. · Climate zones 3 and lower: radiant barriers in attics or a double roof with a ventilated cavity. · Climate zones 5 and lower: summer solar gain through glazing may be moderated by low window-to-wall ratios, or by fixed or operable features such as brise soleil, roller shades, shutters, or blinds. Controlled or moderated thermal flow measures provide benefits but may not be necessary. ¦ ¦ Air leakage and stack effect ¦ Controlled air leakage is typically achieved by building envelopes that meet current ASHRAE Standard 90.1 requirements for building envelopes. Controlled stack effect is typically achieved by minimizing number of open communicating stories or by mechanical destratification among floors. Moderated air leakage is typically satisfied by limiting overall air intrusion. Examples include: air barriers in walls and in the ceiling plane of uppermost stories, weather-stripping of door and window openings, vestibules or buffer spaces at heavily used entry points. Moderated stack effect is typically limited by not more than two open communicating stories plus air leakage improvements. If building pressurization is used, interior pressure should be slightly negative during heating and humidification and slightly positive during cooling and dehumidification. Controlled or moderated measures provide benefits but may not be necessary. ¦ ¦ Moisture vapor ¦ Controlled moisture vapor flows are typically achieved by building envelopes that meet current ASHRAE Standard 90.1 requirements for building envelopes. Moderated moisture vapor flows are typically satisfied by building envelopes with robust envelope construction and limited vapor permeability, such as thick masonry walls. For less robust envelope construction, such as stud-framed walls or wood-framed ceilings in the uppermost stories and wood-framed floors over crawlspaces and basements, a vapor retarder may be needed. Any controlled or moderated measures provide benefits but may not be necessary. ¦ Note: See also Chapter 64 for moisture management in buildings. from documentary research and physical investigation of the enve- lope, and can be often informed by environmental monitoring and hygrothermal analysis. 6.3 TEMPERATURE AND RELATIVE HUMIDITY This section explains the structure and use of Tables 13A and 13B, which list a set of options (rows) and their characteristics (col- umns). The tables are not meant to be a simple recipe box. They quantify and codify many options that will be judged by the criteria in Figure 1: the preservation needs of the collection, occupants' needs, capability of the current building envelope, feasibility of a new envelope, and long-term costs and sustainability ofHVAC sys- tems. It is an iterative process, exploring and reconciling inevitable conflicts. Firstly, climate loads and envelope performance, as discussed pre- viously, must be understood. A very common error in cultural insti- tution HVAC specifications is a disconnect between the design specifications and what the envelope (and budget) can support over time. With awareness of envelope limitations, select the Type of Col- lection and Building (column 1) that most closely matches the cur- rent project. Table 13A applies to general requirements of mixed permanent collections, and Table 13B applies to specialized spaces for specific materials: loans, low-temperature storage, and collec- tions with critical relative humidity requirements. Within the Type of Collection and Building selected (column 1), examine the Collection Benefits and Risks summarized in the far- right column. For Table 13B, this is usually a straightforward deci- sion: only one option (or various degrees of cold) either is or is not feasible with the project budget in terms of high-performance enve- lope and HVAC. Table 13A concerns more common situations, but is more com- plex. For the type of collection and building selected (column 1) exam- ine the collection benefits and risks summarized in the various options of the far-right column (only one option is described for the simplest type of building, control type D). Ifthe collection contains only one type of object, or if the most important objects are of one type, then a more precise analysis of benefits and risks can be made using information in the section on the Environmental Effects on Collections. For each option considered, analyze as well as possible the (1) benefits to the collections, (2) remaining risks to the collections, and (3) costs in terms ofthe building and HV AC system required. For the latter, it is necessary to understand columns 3 to 6. There are four components to a specification: long-term outer limits, annual aver- ages, seasonal adjustments, and short-term fluctuations and space Inc. ASHRAE, 2019 user. single for Licensed | {}
a9229835-50d2-41c6-a24e-b87235957ee9 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Table 13A Temperature and Relative Humidity Specifications for Collections in Buildings or Special Rooms ¦ Type of Collection and Building ¦ Type of Control ¦ Long-Term Outer Limitsa ¦ Annual Averages ¦ Seasonal Adjustments from Annual Averageb ¦ Short-Term Fluctuations plus Space Gradientsc ¦ Collection Benefits and Risksd ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Museums, Galleries, Archives and Libraries in modern purpose-built buildings or purpose-built rooms Temperature at or near human comfort ¦ AA Precision control, no seasonal changes to rela- tive humidity A1 ¦ ≥35% rh ≤65% rh ≥10°C ≤25°C ¦ For permanent collections: historic annual average of relative humidity and temperature. In public display areas, human comfort tempera- tures can apply. ¦ No change to relative humidity Increase by 5 K; Decrease by 5 K ¦ ±5% rh, ±2 K ¦ Mold germination and growth, and rapid corrosion avoided. No risk of mechanical damage to most artifacts and paintings. Some metals, glasses, and minerals may degrade if rh exceeds a critical value. Chemically unstable objects deteriorate significantly within decades at 20°C, twice as fast each 5 K higher. Mold germination and growth, and rapid corrosion avoided. No mechanical risk to most artifacts, paintings, photographs, and books; small risk of mechanical damage to high-vulnerability arti- fact. (Current knowledge considers the specifications A1 and A2 as causing the same low risk of mechanical damage to vulnerable collections. Slow seasonal adjustment of 10% rh is estimated to cause the same mechanical risk as rapid fluctuations of 5% rh, because of significant stress relaxation occurring within three months of a slow transition.) Chemically unstable objects deteriorate significantly within decades at 20°C, twice as fast each 5 K higher. ¦ ¦ Museums, Galleries, Archives and Libraries in modern purpose-built buildings or purpose-built rooms Temperature at or near human comfort ¦ Precision control, seasonal changes in temperature and relative humidity ¦ ≥35% rh ≤65% rh ≥10°C ≤25°C ¦ For permanent collections: historic annual average of relative humidity and temperature. In public display areas, human comfort tempera- tures can apply. ¦ Increase by 10% rh. Decrease by 10% rh. Increase by 5 K; Decrease by 10 K ¦ ±5% rh, ±2 K ¦ Mold germination and growth, and rapid corrosion avoided. No risk of mechanical damage to most artifacts and paintings. Some metals, glasses, and minerals may degrade if rh exceeds a critical value. Chemically unstable objects deteriorate significantly within decades at 20°C, twice as fast each 5 K higher. Mold germination and growth, and rapid corrosion avoided. No mechanical risk to most artifacts, paintings, photographs, and books; small risk of mechanical damage to high-vulnerability arti- fact. (Current knowledge considers the specifications A1 and A2 as causing the same low risk of mechanical damage to vulnerable collections. Slow seasonal adjustment of 10% rh is estimated to cause the same mechanical risk as rapid fluctuations of 5% rh, because of significant stress relaxation occurring within three months of a slow transition.) Chemically unstable objects deteriorate significantly within decades at 20°C, twice as fast each 5 K higher. ¦ ¦ Museums, Galleries, Archives and Libraries in modern purpose-built buildings or purpose-built rooms Temperature at or near human comfort ¦ A2 Precision control, seasonal changes in temperature only ¦ ≥35% rh ≤65% rh ≥10°C ≤25°C ¦ For permanent collections: historic annual average of relative humidity and temperature. In public display areas, human comfort tempera- tures can apply. ¦ No change to relative humidity. Increase by 5 K; Decrease by 10 K ¦ ±10% rh, ±2 K ¦ Mold germination and growth, and rapid corrosion avoided. No risk of mechanical damage to most artifacts and paintings. Some metals, glasses, and minerals may degrade if rh exceeds a critical value. Chemically unstable objects deteriorate significantly within decades at 20°C, twice as fast each 5 K higher. Mold germination and growth, and rapid corrosion avoided. No mechanical risk to most artifacts, paintings, photographs, and books; small risk of mechanical damage to high-vulnerability arti- fact. (Current knowledge considers the specifications A1 and A2 as causing the same low risk of mechanical damage to vulnerable collections. Slow seasonal adjustment of 10% rh is estimated to cause the same mechanical risk as rapid fluctuations of 5% rh, because of significant stress relaxation occurring within three months of a slow transition.) Chemically unstable objects deteriorate significantly within decades at 20°C, twice as fast each 5 K higher. ¦ ¦ Museums, galleries, archives, and libraries needing to reduce stress on their building (e.g., historic house museums), depending on climate zonee ¦ B Limited control, seasonal changes in relative humidity and large seasonal changes in tem- perature. f ¦ ≥30% rh ≤70% rh ≤30°C ¦ collection: For permanent historic annual average of relative humidity and temperature. ¦ Increase by 10% rh Decrease by 10% rh Increase by 10 K Decrease by up to 20 K ¦ ±10% rh, ±5 K ¦ Mold germination and growth, and rapid corrosion avoided. Chemical deterioration halts during cool winter periods No risk of mechanical damage to many artifacts and most books. Tiny risk to most paintings, most photographs, some artifacts, some books. Moderate risk to high-vulnerability artifacts. plastics that become brittle Objects made with flexible paints and when cold, such as paintings on canvas, need special care when handling in cold temperatures. Chemically unstable objects deteriorate significantly within decades at 20°C, twice as fast each 5 K higher. Chemical deterioration halts during cool winter periods. Mold germination and growth, and rapid corrosion avoided. Tiny risk of mechanical damage to many artifacts and most books; moderate risk to most paintings, most photographs, some artifacts, some books; high risk to high-vulnerability artifacts Even greater care is needed than provided in B when handling objects made with flexible paints and plastics that become brittle when cold, such as paintings on canvas. Chemically unstable objects deteriorate significantly within decades at 20°C, twice as fast each 5 K higher. ¦ ¦ Museums, galleries, archives, and libraries needing to reduce stress on their building (e.g., historic house museums), depending on climate zonee ¦ C Prevent relative humidity extremes (damp or desiccation) and prevent high temperature extremes. ¦ ≥25% rh ≤75% rh ≤40°Cg ¦ Within 25% to 75% rh year-round. Temperature usually below 25°C ¦ ¦ Not continually above 65% rh for longer than X days.h Temperature rarely over 30°C ¦ Mold germination and growth, and rapid corrosion avoided. Chemical deterioration halts during cool winter periods No risk of mechanical damage to many artifacts and most books. Tiny risk to most paintings, most photographs, some artifacts, some books. Moderate risk to high-vulnerability artifacts. plastics that become brittle Objects made with flexible paints and when cold, such as paintings on canvas, need special care when handling in cold temperatures. Chemically unstable objects deteriorate significantly within decades at 20°C, twice as fast each 5 K higher. Chemical deterioration halts during cool winter periods. Mold germination and growth, and rapid corrosion avoided. Tiny risk of mechanical damage to many artifacts and most books; moderate risk to most paintings, most photographs, some artifacts, some books; high risk to high-vulnerability artifacts Even greater care is needed than provided in B when handling objects made with flexible paints and plastics that become brittle when cold, such as paintings on canvas. Chemically unstable objects deteriorate significantly within decades at 20°C, twice as fast each 5 K higher. ¦ ¦ Collections in open buildings, historic houses ¦ D Prevent very high relative humidity (dampness) ¦ ≤75% rh ¦ Relative humidity reliably below 75% rh ¦ ¦ Not continually above 65% rh for longer than X days.h ¦ Chemically unstable objects deteriorate significantly within decades at 20°C, and twice as fast each 5 K higher. Conversely, cool winter season can extend their life. Mold germination and growth, and rapid corrosion avoided. structured High risk of sudden or cumulative mechanical damage to most arti- facts and paintings because of low-humidity fracture; but avoids high-humidity delamination and deformations, especially in veneers, paintings, paper, and photographs. ¦ | {}
f7951479-1dd6-4a53-b3ee-d37b9c50acf2 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Museums, Galleries, Archives, and Libraries 24.25 Table 13B Temperature and Relative Humidity Specifications for Collections in Buildings or Special Rooms ¦ Type of Collection and Building ¦ Type of Control ¦ Specifications ¦ Collection Benefits and Risks ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Temporary exhibit space and unpacking space for loaned objects ¦ Conditions will be stipulated in loan agreementsi ¦ Conditions will be agreed between lender and bor- rower. Based on the historic climate to which the object is accustomed, and a risk assessment of the borrower's environment and that of the transit pro- cess. Solutions to protect objects from climate shock the creation of micro- should first be found in climates (showcases, glazing, etc., potentially using buffering). e,i 8 ¦ Benefits and risks are assessed by the lender, and con- tractual specifications based on this assessment. Often, assessment is highly risk averse, precaution- ary. For the borrowing institution, the benefits are increased access to popular objects by visitors; risks are monetary and reputational damage if climate control does not meet conditions outlined in the loan contract. ¦ ¦ Chemically unsta- ble organic mate- rials in modern purpose-built buildings or pur- pose-built roomsj ¦ Cool Cold ¦ to 16°C, 30 to 50% rh As defined in ISO Standard 18934:2011. IPI (Adel- stein 2009) uses an anchor of 12°C. 0 to 8°C, 30 to 50% rh As defined in ISO-18934:2011. IPI (Adelstein uses an anchor of 4°C. ¦ The benefit of low temperature storage is extended lifetime of objects that will be lost within a genera- tion or two at room temperature. See the section Chemical Damage for details on quantifying the benefits. Biological damage is also much reduced. The risks are the many side-effects of such systems: high humidity or condensation during malfunctions, water exposure. Objects properly packaged objects at low temperatures.e ¦ ¦ ¦ ¦ 2009) ¦ must be packaged appropri- ately to ¦ ¦ ¦ Frozen ¦ -20 to 0°C, 30 to 50% rh As defined in ISO Standard 18934:2011 and Adelstein (2009) ¦ reduce risk of condensation during retrieval, and a transition space with intermediate climate may be required. Hourly, daily, and even longer humidity fluctuations do not affect most ¦ ¦ Unstable metal or glass in modern purpose-built buildings or pur- pose-built rooms Notes for Tables 13A and 13B: ¦ Relative humidity controlled to avoid a critical relative humidity of a salt or hydrate ¦ Many different critical relative humidities for various materials. for details and sources of information. ¦ See the section on Critical Relative Humidity ¦ aLong-term limits apply to combination of selected annual average plus selected seasonal adjustments. See Figure 15 for examples on a psychrometric chart. bRate of seasonal adjustments in relative humidity set point should not exceed the short-term fluctuation limit each 30 days, and the rate for temperature adjustment should not exceed the short-term fluctuation limit each 7 days (e.g., for A1, a seasonal adjustment can be no faster than 5% rh change per 30 days and 2 K change per 30 days. cShort-term fluctuation means any fluctuation shorter than the times specified in footnote b for rate of seasonal adjustment (i.e., 30 days for relative humidity fluctuations, 7 days for temperature fluctuations). Space gradient refers to the differential in relative humidity or temperature between any two locations where objects are permitted to be placed in the controlled space (designers can specify out-of-limit locations, such as a specific distance to exterior walls and supply vents). dSee Table 3 for examples of objects in each sensitivity category, and Table 5 for lifetimes of objects at various temperatures. CMicroclimates (enclosures, packaging) can achieve the same relative humidity control as type AA or A in a much less controlled space (e.g., B, C, or D), and with much greater long-term reliability. See the section on Response Times of Artifacts. fLong-term risk (≥10 years) of mechanical damage because of relative humidity fluctuations is dominated by the probability of extreme events such as system overload or failure in winter. Control type B with high reliability is less risk to collections than AA or A with poor reliability. gAn upper temperature limit is provided for a mixed collection that may contain objects with waxy materials that deform irreversibly beginning at ~40°C. This limit is set more cau- tiously for type B control, 30°C than type C control. hFrom Figure 3, mold germination becomes very slow, but not impossible, in the range of 75 to 65% rh. iIn general, professional guidance currently refers to Bizot, which stipulates outer limits of 40 to 60% rh, and 16 to 25°C throughout the year. Ratified as of2016 by ICOM-CC, IIC, AIC, AAMD, NMD, BM, and Bizo. See Michalski (2016) for details. jSee Table 5. gradients. Rather than defining a specification and then estimating the benefits and risks, Tables 13A and 13B consider practical cate- gories ofbenefit and risk, and then define the range of specifications consistent with those benefits and risks. Column 3 (long-term outer limits) specifies the boundaries beyond which risk climbs unacceptably for many mixed collections (in broad agreement with recent guidelines such as BSI PAS Stan- dard 198:2012). The upper limit of relative humidity is based on mold risk (see the section on Biological Damage). The lower limits of relative humidity and temperature are based on mechanical risk, such as the probability of fracture of organic materials (see the sec- tion on Mechanical Deterioration). The upper limit of temperature is based on the risk of chemical decay, which climbs exponentially with increase in temperature (see the section on Chemical Deterio- ration). These generalized limits for mixed collections do not replace a thorough determination of the specific vulnerabilities of specific collections based on information in the section on the Envi- ronmental Effects on Collections, alongside consultation with con- servators and scientists. For example, a (clean) stone sculpture collection is not at risk from high summer relative humidity or high temperature (pollution and vandalism are more likely risks). Column 4 (annual averages) assumes design for permanent collec- tions, not loans. To minimize mechanical risk, and to reduce energy costs and building stress, annual averages can be set at local historic annual averages, to which the collection has mechanically acclima- tized. In public display areas, a range of human comfort temperatures can apply, but cannot be set beyond the long-term outer limits. Columns 5 (seasonal adjustments) and 6 (short-term fluctuations) are similar to older versions of this table, although some ranges are now wider. Seasonal adjustments are constrained by the long-term outer limit, although short-term fluctuations are allowed to extend beyond this limit. For a discussion of dual set-point control as a means to achieve these parameters, see the section on Controls Design. Figure 15 shows the interrelation of the four specification compo- nents and the role of long-term outer limits for an example of control type Al. The long-term outer limit (35 to 65% rh, 10 to 25°C is defined by the solid-line box. For this project, the annual average is 21°C and 42% rh, shown by the black dot; seasonal adjustments are ±10% rh, +5 K, and -10 K, although application of these seasonal adjustments is constrained by the upper temperature and lower humidity limits of the long-term outer limit. This combination of annual average and seasonal adjustment is shown by the dashed-line box. Short-term fluctuations of ±5% rh and ±2 K are added, and the Inc. ASHRAE, 2019 user. single for Licensed | {}
0fe2df25-abd6-4004-add1-b11a75335242 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 24.26 2019 ASHRAE Handbook- -HVAC Applications (SI) X-Axis: AIR TEMPERATURE, °C Y-Axis: UNIT DTOWTH Chart Type: line LONG-TERM OUTER LIMIT ANNUAL AVERAGE SEASONAL ADJUSTMENT SHORT-TERM FLUCT (OVERALL) SHORT-TERM FLUCT (AROUND MAX SEASL ADJ) item_01 20% 15% 10% 5% 0% Fig. 15 Psychrometric Depiction of Control Type A1 total range is defined by the dotted-line box. The sections of the dashed-line box that go beyond the long-term outer limits are permis- sible because they represent short-term fluctuations. To remain within the bounds of mechanical risk defined for each type of control, it is essential that the annual average be both histori- cally accurate and consistent into the indefinite future. The example in Figure 15, for example, allows short-term relative humidity to drop to 30% because the historic annual average was claimed to be an unusu- ally low 42% rh. At the same time, however, selecting this annual aver- age does not allow short-term humidity to go above 57% rh in summer. Estimates of mechanical risk for each type of control are based on the total range of relative humidity values over many years. If, next year, the annual average setting is changed to 50% rh to justify a summer high of 65% rh, A1 control can no longer be claimed. In a project where historic averages are unknown, select annual averages that are consistent with future needs (e.g., sustainability) or a known critical relative humidity for part ofthe collection. Given the fixed boundary of the long-term outer limits, the maximum seasonal adjustments are available only for annual averages near the middle of this bounded area. air( Up limited numbers of major institutions could achieve, and that were measurable with commercial monitors or with sensitive analytical methods (Mathey et al. 1983; NARA 2002; NRC 1986). In the 1980s, little information existed on the impact of some pollutants, such as ace- tic acid and nitrogen dioxide. As a precaution, "use best available tech- nology' was the stated advice for those pollutants. This expression became popular and, consequently, many institutions requested it as specification, or requested very low limits of pollutant concentrations without justification. Those low limits were often hard to achieve and maintain. Apart from the cost, it also raised the issue of sustainability. In practice, target levels for pollutants were often simply neglected or ignored. to (9 of water/kg RATIO HUMIDITY 6.4 AIRBORNE POLLUTANT CONTROL STRATEGIES In the past, recommendations for maximum pollutant concentra- tions allowed in museums and archives were based on levels that only A common analytic method for measuring specific gaseous pollut- ants uses diffusive samplers. A chemical compound in a diffusion tube absorbs a specific pollutant for a fixed amount of time, typically 3 weeks. After the sampling, collected pollutants are sent to a labora- tory for analysis. This method can detect most pollutants ofinterest for museums with good limits of detection (Grzywacz 2006). Particulate matter of different aerodynamic diameters can be measured with pre- cision using a cascade impactor (Krupinska et al. 2013). However, unlike monitoring of temperature and relative humidity, measuring different pollutants is expensive and many museums will avoid doing it unless there is serious doubt about the actual concentration of some pollutants or damage is reported on an object. Qualitative and semi- quantitative tests include pH testing, which gives an indication of the acidity level (Tetreault 1992); coarse particle deposition on glass or sticky slides (Lloyd et al. 2007); and metal corrosion electronic sensors or metal coupons, which give information on the corrosiveness of the environment (Coughlin 2011; Thickett et al. 2013). Detection limits of some of these tests can be an issue, as can the fact that they may fail to detect the most harmful compounds for the collection. Test results can- not easily be transposed to specific pollutant concentrations. Even with quantitative measurements, monitoring has some limitations. Not all rooms and enclosures are usually tested, and measurements at a spe- cific location and time may provide limited information: pollutant con- centrations can vary based on parameters such as changing seasons, crowd density, space gradients, product aging, and HVAC system adjustments. Measuring pollutant concentrations in a new building before its official opening will not give the same results as a building filled with collections, visitors, and older enclosures. It is best to con- sider a global preventive strategy before starting a monitoring cam- paign without being sure the results will provide the proper answer. · Basic level: recommended dust filter performance at least equal to that recommended for office spaces (typically minimum efficiency reporting value [MER V] 11) or as specified by an accreditation pro- gram such as the U.S. Green Building Council's (USGBC) LEED Indoor Environmental Quality credit (EQc) 5.1 (MERV 13) (ASHRAE Standard 52.2-2017). If appropriate, enclosures should be well sealed to prevent infiltration of pollutants present in the room. Consultation with conservation professionals can provide information on the global strategy for pollutant control, advise on which objects are typically at risk in museums, and provide guide- lines for proper selection of products when building enclosures. The goal of the basic level is to avoid or minimize the most common short- and medium-term damage caused by pollutants in museums and archives, at reasonably low costs. · Intermediate level: dust filtration efficiency should be higher than for the basic level (Tetreault 2003). Qualitative or semiquantitative monitoring is suitable in the new installation (rooms and enclo- sures), as well as some testing ofproducts before use. Some deeper Table 14 offers a control strategy for pollutants based on a cost benefit scale and on the reduction of uncertainties of the risk evaluation. The table has three levels of control, and makes recommendations based on the building and enclosure; additional considerations are discussed for each level of control. Inc. ASHRAE, 2019 user. single for Licensed | {}
674b8ff4-0823-4bae-a0b7-2898c936d055 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Museums, Galleries, Archives, and Libraries 24.27 Table 14 Strategies for the Control of Airborne Pollutants ¦ Level of Control ¦ Building with HVAC system ¦ Display Cases and Storage Cabinets/Boxes Considerations ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Basic Basic control of fine particles and avoiding common problems in enclosures. ¦ - Provide basic fine-particulate filtration such as that recommended for office space regulation or for LEED certification (EQc 5.1). - Locate HVAC fresh air intake away from pollutant sources and keep windows closed. ¦ - In closed spaces containing objects, - Identify objects (e.g., lead, silver, soda-rich select and use materials recommended glasses, cellulose papers, calcareous by conservation professionals. a, b objects) that may be at high or moderate risk from pollutants (see Table 9). - Ensure airtightness of enclosure (to - Address pollutants by using a systematic prevent external pollutant infiltration) approach: avoid, block, dilute, and sorb.c if there are no significant amounts of pollutants generated by objects or materials (see Table 9). ¦ ¦ Intermediate Improved control of fine parti- cles and reduced uncertainty and risk of damage in enclo- sures. Advanced and special cases Optimal control of airborne pollutants in room; better quantification of preservation performance, which allows optimal strategies for improvement. ¦ - Use medium-efficiency fine-particu- late filtration or select filter perfor- mance based on outdoor concentration provided by local authority. - Seal concrete and wooden surfaces (walls, floor, shelves, etc.). - Use high-efficiency fine-particulate filtration or select filter performance based on risk analysis result. - Use gas-phase filtration media if out- door pollutants in surrounding envi- ronment or indoor-generated pollutants are an issue. - Quantitatively monitord concentration of key pollutants - Do risk analysis of outdoor, room, and enclosure pollutant concentrations mizing impact of pollutants on specific objects or on collection in general. Adjust institutional ¦ - Test orinvestigate materials and objects - Consider adjusting relative humidity and to identify those that contain harmful temperature levels, which often affect pol- compounds. b,c lutants' reactions on objects. - Monitor enclosed environment with low-cost monitoring techniques (risk of low sensitivity). c,d - Estimate or measure airtightness of - Maximal average pollutant concentrations enclosure.e for a general collection (excluding moder- - Options for special needs: positive air ate- and high-risk objects) should stay be- pressure,c gas sorbent, c anoxia system. f low 1000 �g/m3 (400 ppb) for acetic acid; 1 �g/m3 (0.7 ppb) for hydrogen sulfide; and 10 �g/m3 for nitrogen dioxide (5 ppb), ozone (5 ppb), and fine particles. These lim- its should prevent low-level damage to ob- jects for at least 1 year. c Controlling these key pollutants makes it very likely that other pollutants will be controlled as well. and compare against suggested limits or with institutional targets. and determine most efficient solutions for mini- target if necessary. ¦ aTetreault (2017), bHatchfield (2002), Tetreault (2003), dGrzywacz (2006), eCalver et al. (2005), fMaekawa (1998). investigation can be done to identify vulnerable objects and to determine whether emissions from the collections themselves can be a risk to other objects. This will not necessarily improve con- servation of the collection from pollutants, but it reduces uncer- tainties related to the conservation strategies in place. The strategy can be adjusted, if needed, in the light of the results. · Advanced level: quantitative measurements should be taken of the airborne pollutants (gases and fine particles) outside the insti- tution as well as in some rooms and enclosures containing very significant and vulnerable objects. This can be done for a new installation, during renovations, or as needed. The maximum pol- lutant concentrations allowed can be based either on the limits in Table 14 for a general collection, or on the target for the general collection and/or for some objects established by the institution. Conservation professionals can help assign pollutant target con- centrations aligned with the institution 's preservation policy. Quantitative measurement of the air exchange rate for enclosures that need a high airtightness is also recommended. Knowing the airtightness also helps determine the quantity of silica gel or any sorbent needed for an optimal climate control in the enclosure. Measuring particle and gaseous pollutant concentrations and air- tightness of enclosures can provide better confidence on the strategy in place, and can support a proper risk analysis for the overall collec- tion or for specific objects (Krupinska et al. 2013). Local environ- mental data, obtained from different levels of government agencies, can provide useful information on the outdoor climate. This analysis can help determine the filtration performance needed for rooms and for enclosures holding specific objects or collections. If the room is well controlled, leakage from enclosures may not be an issue. How- ever, ifit is difficult to achieve adequate control in the room, then the collection can be better protected inside enclosures. Unfortunately, not all objects can be placed in enclosures (e.g., because of size or ac- cess). The length of exhibition/exposure allowed can also be ad- justed based on the results of the risk analysis. For very vulnerable or/and significant objects, some special features can be considered for optimal preservation: positive-air- pressure enclosures (preventing dust infiltration in leaky cases), en- closures with gas sorbents (to reduce the amount of undesired gases generated inside or infiltrated), and low-oxygen enclosures (to min- imize oxidative reactions, including photo oxidation). See Table 14 for references. 6.5 CONTROL STRATEGIES FOR OBJECTS WITH HIGH VULNERABILITY TO POLLUTANTS Some objects tend to be more vulnerable to inadequately con- trolled environments. Those objects need special considerations that HVAC professionals should be aware of. A conservation profes- sional can also assist with developing preservation strategies. Silver Silver is very sensitive to reduced sulfide compounds, mainly hydrogen sulfide (H2S) and, to some extent, carbonyl sulfide (COS). Sulfur sources are many: the outdoors, from people in the room, and from products and collections inside enclosures. It is usually best to keep silver objects in airtight enclosures with no sulfur-emitting products. Consult the combustion section in the safety material sheet (SMS) for specific products to see if they contain sulfur Inc. ASHRAE, 2019 user. single for Licensed | {}
82183524-29be-4d16-bef4-4d3908d16ce7 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 24.28 compounds; products that contain sulfur compounds should be avoided. It is also wise to confirm the absence of sulfur compounds in the product by running a spot test, such as the lead acetate test, Oddy test, or equivalent (Robinet and Thickett 2003; Tetreault 2003). The same strategy can be applied for the preservation of cop- per. The LOAED for H2S for silver is 0.10 �g/(m3 · yr) (0.071 ppb/ yr) and 1.0 �g/(m3.yr) (0.71 ppb/yr) for copper (Tetreault 2003). Complete dryness will not stop tarnishing, but will minimize it. Lead The most harmful vapor to lead is acetic acid. Lead is not usually at risk of corrosion in a room but may be in enclosures. Any organic- acid-emitting products or objects should be avoided. Lead may never be safe in the presence of wood, painted wood products, or freshly applied sealants or adhesives. The worst situation would be having lead present in a freshly painted enclosure with paint formed by oxidative polymerization (e.g., oil based paint). Polymerization releases aldehydes, organic acids, and peroxides. Those peroxides can convert aldehydes into organic acids (Raychaudhuri and Brim- blecombe 2000; Tetreault 201 1). Enclosing lead objects in a display case freshly sealed with acetoxy-cured silicone also puts the lead at high risk of corrosion. A relative humidity kept below 35% prevents corrosion by organic acids above the NOAEL (170 ppb). Calcareous Objects Calcareous objects (e.g., limestone, ceramics, shells) can react with organic acid vapors, especially when contaminated by chloride or nitrate salts (Halsberghe et al. 2005) in highly humid environ- ments. No data exist to quantitatively assess these objects' vulnera- bility. As a precaution, it is best to minimize the presence of acid- emitting products or objects in the enclosure as well as relative humidity and temperature fluctuations, and if possible, lower the rel- ative humidity to prevent salt dissolution, reaction, and migration. Sodium- and Potassium-Rich Glasses Inc. ASHRAE, 2019 user. single for Licensed Some historical glasses degrade slowly in the presence of water vapor, resulting in alkali leaching, which can form crystalline cor- rosion compounds on the surface or modify the structure of the glass. The presence of formic and acetic acids accelerate the leach- ing (Robinet 2006). These types of glass should be displayed or stored near 40% rh with very little fluctuation (Koob 2006). See van Giffen et al. (2018) for detailed recommendations on climate con- trol for glass. Enclosures should not contain products that can emit organic acids. Colorants Many colorants (organic pigments and dyes) are known to be sensitive to photooxidation and/or to hydrolysis (Reilly 1998). In addition, some colorants are affected by gaseous pollutants. The most sensitive colorants to nitrogen dioxide, sulfur dioxide, and ozone are curcumin, dragon 's blood, aigani, realgar, iron ink, enju, basic fuschin, Brilliant green, pararosaniline, indigo, madder lake, Persian lake, and saffron (Cass et al. 1989; Whitmore and Cass 1989; Williams et al. 1993). Yellow dyes from photographic prints have been found to be affected by acetic acid (Fenech et al. 2010). Artworks with vulnerable colorants should not be displayed long term without protective enclosures, and photograph prints should not be enclosed with products that may release organic acids. Cellulose Papers For many decades, sulfur dioxide was thought to be the most damaging pollutant for paper. As its concentration in the environ- ment decreased over the years, it was found that nitrogen dioxide was the main problem for paper. Fine particles and ozone also affect unprotected paper (Bartl et al. 2015; Gurnagul and Zou 1994). At the room level, displaying art on paper without protection (e.g., 2019 ASHRAE Handbook -HVAC Applications (SI) glazed framing, display cases) is not recommended. However, for- mic and acetic acid emitted by various organic materials can affect cellulose, but in the presence of aldehydes, the damage is found to be reduced (Tetreault et al. 2013). As a precaution, however, avoid acid-emitting products. For paper in books, most damage (yellowing, embrittlement) by outdoor and indoor pollutants tends to remain on the margins of the paper sheets, with very slow diffusion into the book. Many archi- vists will accept some limited deterioration of the pages' edges. If stack or single-sheet papers are framed or protected in airtight boxes, gas filtration in archives and libraries may not be required. The cellulose is best preserved against acid-catalyzed hydrolysis by keeping the relative humidity and temperature as low as possible. Cellulose Acetate Films Cellulose acetate films degrade by acid-catalyzed hydrolysis, and acetic acid is the by-product released (Reilly 1993). It is best to preserve films from the 1950s and 1960s in cool or cold rooms (see Table 13B). In ambient conditions, degraded films should ideally be stored in special ventilated cabinets to avoid the risk of damage to other collections. Otherwise, consider enclosing the films in airtight enclosures with moisture sorbents to prevent the ingress of high humidity in the storage area (Nishimura 2015). Cellulose Nitrate Films As with any cellulosic material, cellulose nitrate (CN) films degrade by acid-catalyzed hydrolysis, releasing nitrogen oxides. Old CN films, produced mainly from 1896 to 1952, are unstable and must be kept absolutely below 38°C, above which there is a high risk of self-ignition. CN films should be removed from the collection and properly stored according to NFPA Standard 40, which provides detailed information on the ventilation requirements. However, it is best to preserve these films in cold rooms (see Table 13B). Other CN objects (such as faux tortoise shell) do not degrade to the same magnitude as films, but to avoid the risk of damage from nitrogen oxide emissions to other collections, CN objects should be stored either in well-ventilated rooms or in special ventilated cabi- nets (Coughlin and Seeger 2008). A room with a high load of CN items must also comply with local regulations for explosive and combustible substances. Difficult-to-Clean Objects All objects are susceptible to particle deposition, but cleaning of particles is difficult or even impossible for some objects. During handling and cleaning, there is also a risk of physical damage. Example objects include those with powdery pigments or surfaces (e.g., some painted ethnographic objects, butterfly wings); physi- cally fragile objects (e.g., insect collections, filamentous mineral specimens); objects in which fine particles could become lodged in microcracks or interstices (e.g., ivories, painted objects with cracks); and objects with sticky surfaces (e.g., some deteriorated plastics, some polyethylene-glycol-treated wooden waterlogged objects). For these objects, it is best to display and store them in air- tight enclosures or in cases with a positive-pressure system. If enclosure is not an option, it is recommended to maintain a mini- mum distance between visitors and fragile objects: for example, a distance of 1.5 to 2 m reduces dust deposition by 50 to 75% (Lloyd et al. 2007). This distance prevents deposition of coarse particles on objects, but has limited effect on fine particles because of their lon- ger suspension time. 7. CONTROLS DESIGN Although control technologies for mechanical systems in cultural heritage institutions are similar to those used in the rest of the HVAC field, the control philosophies and logic that determine daily | {}
27cc1ea1-9662-49aa-a2b8-d45e6668aa21 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Museums, Galleries, Archives, and Libraries 24.29 operation of systems that condition collections areas can, and typ- ically should, be quite different. A common criticism of collections environments is the amount of energy required to maintain preserva- tion standards and narrow environmental requirements, especially in structures (historic or otherwise) not designed for that level of con- trol. Updated standards (see the section on Key Considerations) paired with an increased understanding of heritage risk (see the sec- tion on Overview ofRisks) and how collections materials respond to changes in air conditions (see the section on Environmental Effects on Collections) allow for improved approaches to control and oper- ation (see the section on Design Parameters for Performance Target Specifications) that better achieve sustainability goals while provid- ing appropriate preservation conditions for a variety of materials. Applicable standards as well as preservation and sustainability ex- pectations will have been identified during predesign (see the section on Context and Predesign); outcomes of this process may include se- lecting a nonmechanical solution to manage the collection environ- ment. Ifa mechanical solution is required or selected, the control and mechanical design must apply the predesign outcomes, including any design parameters for preservation and sustainability. As me- chanical systems move from design and construction into a commis- sioning/continuous commissioning phase, control and operation should be revisited to assess both achievement of the appropriate en- vironmental conditions as well as energy consumption at individual stages of operation; this combination of appropriate environmental preservation conditions while only using the minimum energy con- sumption necessary is key to long-term optimal, sustainable opera- tion. In any cultural heritage application, moisture management and control are almost universally the most critical, difficult, and poten- tially costly processes to achieve. Moisture's role in determining the overall psychrometric properties of any environment, as well as its central role in most forms of collection degradation, make dehumid- ification and humidification control primary aspects of the holistic building and system operation. Temperature control, though import- ant for both comfort and preservation, is generally the easier control process, and must be managed to maintain appropriate relative humidity at a given moisture content. To facilitate communication with collections professionals, designers and technicians should be prepared to discuss moisture control in the terms with which the cli- ent is most familiar and that map well with collections preservation metrics. Relative humidity is typically the best variable for analyzing risk from deterioration processes that depend on sorbed moisture in objects (see the section on Environmental Effects on Collections). Dew point can also be a useful representation of moisture content, especially for discussions of building envelope performance and deterioration (e.g., window and wall condensation), risks during retrieval of objects from cold storage, or entry of loaned objects during winter. Humidity ratio and enthalpy should be clearly defined when used in communication among the broader design team. Any controls design should clearly define both the control ranges for temperature and relative humidity and the logical process that governs the operation of the relevant equipment. The sequence of op- eration should be available as a plain-language document that serves as a master reference for institutional staff (collections and facilities) and guidance to outside contractors (designers, programmers, etc.) for controls or equipment upgrades. This master document should be updated as optimization or other changes in operation dictate. 7.1 PHILOSOPHY As noted previously, environmental tolerances for cultural heri- tage collections have largely been redefined through updated sci- ence, field observations of environmental impacts on collections, and greater awareness of sustainability considerations. Most collections environments can operate safely within a broader range of tempera- ture and relative humidity conditions than previously understood, leading to new methods and approaches for equipment control and operation to achieve preservation and sustainability goals. Certain environments (e.g., exhibitions with loaned materials governed by an agreement) may still require a narrow band of control, but many col- lections environments can safely include seasonal adjustments and allow short-term fluctuations without causing damage. The result is a more complex discussion from the controls design perspective. Information shared and developed during predesign should form the basis of the control philosophy, which should be formalized in a written sequence of operation that provides the log- ical relationships for how equipment achieves the intended opera- tion. It is critical to recognize that the design sequence of operation is only a model of what is expected to happen: it is likely, even pref- erable, that the sequence of control will be adjusted during commis- sioning and optimization. Actual energy loads in the space may be different from models, and it is difficult to predict the effects of col- lections materials, which may effectively function as heat and mois- ture sinks in the room environment. Where ratios of hygroscopic material volume to air volume are significant enough, collections may actually buffer environmental changes. Kupczak et al. (2018a) show that, at high ratios, paper collections can reduce fluctuations and energy costs. Design of temperature and relative humidity controls in cultural heritage settings have traditionally identified a single set point with a dead-band range, and the system works to achieve those set points year-round. With expanded humidity ranges and the use of seasonal temperature control in collections environments, single-point control is no longer the most efficient method. For temperature, occupied collection spaces (where human comfort needs may dictate a narrow range of temperatures throughout the year) are still appropriate can- didates for single set-point control. However, low-occupancy collec- tions spaces (e.g., storage) may see both preservation and energy benefits from seasonal temperature adjustments; designs should con- sider using dual heating/cooling set points or minimum/maximum conditions for seasonal control. Any collections environment, occu- pied or unoccupied, may benefit from dual relative humidity set points defining where humidification and dehumidification are en- abled. Controls design has two goals: · Achieving appropriate equipment operation and process manage- ment to create and maintain the collection preservation environ- ment defined during predesign · Using only as much energy as necessary to achieve the desired conditions Though many cultural heritage institutions or buildings may appear similar on the surface, individual factors such as the follow- ing usually require highly individualized controls and equipment designs to match the unique situation (see the section on Context and Predesign): · Collection type and preservation needs · Outdoor climate · Building envelope performance · Degree of mechanical intervention intended · Occupancy of collections spaces · Prioritization of preservation and energy usage · Institutional capital, operational, and utilities budgets These factors also heavily influence optimization: similarly con- structed buildings and preservation environments (e.g., many off- site library/museum storage facilities) commonly optimize differ- ently for preservation and energy based solely on geographic loca- tion and exterior environments, even when many other variables are the same. Inc. ASHRAE, 2019 user. single for Licensed | {}
0f256d39-cef2-4383-a6c0-fbed2fa826f1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 24.30 2019 ASHRAE Handbook-HVAC Applications (SI) 7.2 ZONING An air-handling zone refers to the group of spaces that an air- handling unit (AHU) serves in a building. Zoning in cultural heritage facilities can be broken down into four simple groups, each with dif- ferent requirements for control. Generally, regardless of zoning, sys- tem control should be based on some combination of sensors placed in the collection space; return air sensors can be used as a reference point, but should not be used as the control point in cultural heritage applications. The four typical zoning configurations are as follows. One AHU to One Space. Desirable for fine environmental control. Control should be based on a temperature/relative humidity (T/RH) sensor in the collection space. Control from return air sen- sors may not accurately represent what occurs in the space. One AHU to Many Spaces. Best when spaces are used for the same purpose, have similar criteria for interior space conditions, and have similar interior and exterior thermal and moisture loads. Mixed zones (i.e., collections and noncollections) generally lead to sub- optimal preservation conditions or energy use. In collections or mixed occupied collections zones, each individual space should have a T/RH sensor. Control can be based on either high/low readings from individual spaces that will enable a process, or on a zone aver- age of readings from all space sensors. Using a zone average for con- trol can lead to parts of the zone being out of the defined operational parameters, especially in rooms with an external wall or roof expo- sure. These areas may require either mitigation of the load or air re- balancing for correction. Ifhigh/low readings are used, conditions in other subzones must be monitored to ensure that they do not go out of specification. Using a blended return air sensor may lead to inac- curacy or control issues, depending on where return air is being pulled from within the zone. Many AHUs to One Space. Used in large footprints, most com- monly in storage, large galleries, or reading rooms. This strategy is especially useful if different parts of the space are exposed to differ- ent loads over a 24 h period (e.g., solar exposure). Control should be based on subzones in the space with individual T/RH sensors: con- trol from return air sensors may not accurately represent what occurs in the space. In this configuration, control and sensor placement should be considered carefully to limit the potential for units to oper- ate suboptimally; for example, the average room condition may reg- ister as acceptable, though individual units are performing dissimilar operations (e.g., one system is cooling and the other heating). Many AHUs to Many Spaces. Typically found in large, multi- level footprints (e.g., multilevel library/archives storage); especially useful if different parts of the space are exposed to different loads over a 24 h period (e.g., solar exposure). Control should be based on subzones in the spaces with individual T/RH sensors, because con- trol from return air sensors may not accurately represent what occurs in the space. For this configuration, carefully consider con- trol and sensor placement to limit the potential for units to operate suboptimally; for example, the average room condition may register as acceptable, though individual units are performing dissimilar operations (e.g., one system is cooling and the other heating). Zone design, adjacencies, and other aspects of functional orga- nization should be part of early predesign discussions to optimize design for preservation and energy usage, as well as to rightsize sys- tems for efficient initial capital investment. Table 1 describes building space types in typical cultural heritage facilities, and should inform decisions of physical zoning and con- trol. Ideally, an HVAC zone should consist of physical spaces that require similar environmental control. For many cultural heritage institutions, there are three general environmental zones to consider: · Occupied noncollection spaces where human comfort is typi- cally the priority. They require outdoor air and temperature con- trol, but little moisture control (only for human comfort). These concerns may not be as pertinent for noncollection spaces that are typically unoccupied. · Occupied collection spaces require outdoor air during occupied periods, human comfort temperatures, and moisture control for collection preservation. Systems may dehumidify and humidify based on climate zone (see Table 10 and Figures 12 and 13). Examples include galleries, reading rooms, and collection work- spaces, and may constitute a large percentage ofthe building foot- print. Note: a common issue is whether to treat certain offices as collection spaces. This should be considered carefully, not only for the added capital and operating cost, but also for risks to the collection if offices are not so treated and are nonetheless used for collections display or storage. · Storage environments (typically unoccupied collection spaces) require temperature and moisture control that is optimized for long-term preservation. Outdoor air may be reduced or eliminated entirely, based on occupancy or other requirements. Depending on the institution, examples include typical low-occupancy stor- age environments (e.g., library and archives stacks), or truly unoccupied collection spaces (e.g., cold or low-oxygen storage). Mechanical systems and buildings function best when AHUs and zones are logically divided according to purpose. System and con- trols designs should avoid mixing collection and noncollection spaces wherever possible and resist the tendency to accept down- stream sub-zone controls (e.g., VA V/reheat designs) as immediate solutions to zoning issues. Such designs will invariably be less en- ergy efficient over time, and commonly lead to problems maintain- ing conditions for the preservation environment as human comfort will take priority. 7.3 BASIC PROCESSES Cultural heritage facilities perform four basic psychrometric pro- cesses on a moving airstream to control internal environments using mechanical intervention (Figure 15): · Heating: raising sensible or dry-bulb temperature, as preheat, reheat, or heating for downstream temperature control. May be accomplished by various equipment, ranging from direct and in- direct fired heaters to electric, hot-water, or steam coils. In certain settings, heating may be by nonforced-air systems, using other convection or radiant technologies. · Cooling: decreasing sensible or dry-bulb temperature, commonly for downstream temperature control but occasionally as precool- ing ahead of some components (e.g., energy wheels) for increased efficiency. Typically accomplished either by direct-expansion (refrigerant-based) cooling or by chilled-water or glycol coils. · Dehumidification: reducing moisture content for the specific purpose of maintaining a safe range ofrelative humidity at a given temperature condition. Equipment varies from common subcool/ reheat coil designs, to various configurations of desiccant or en- ergy wheels, whether as components in a larger air handler design or as a stand-alone package unit. · Humidification: increasing moisture content to attain a mini- mum relative humidity condition in a downstream space, typi- cally in arid or seasonally dry or cold climates. Humidification can be performed by isothermal (steam) or adiabatic (evaporative) systems, and may be located at the primary unit or in downstream ductwork. The sequence of operation should clearly identify the logic of when each process occurs; for example, that humidification begins once the space drops below 35% rh, or that sensible cooling and sen- sible heating cannot be engaged at the same time. Inc. ASHRAE, 2019 user. single for Licensed | {}
53796e06-3835-428b-850c-e62aa9ae0f7a | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Museums, Galleries, Archives, and Libraries 24.31 7.4 OUTDOOR AIR AND VENTILATION Outdoor Air Introducing outdoor air into interior environments typically in- creases sensible and latent system loads and serves as the primary source of particulate and gaseous filtration loads. In collections spaces, where the primary goal is maintaining the appropriate inte- rior temperature and relative humidity conditions, outdoor air quan- tities should be restricted to the minimum necessary for occupancy based on local code. For nonoccupied collections spaces and spaces with periods of zero and nonpeak occupancy (e.g., galleries, reading rooms, workspaces during closed periods), designs should incorpo- rate means of further reducing outdoor air volumes, even to fully closed, based on actual need. CO2 sensors and modulating dampers can help automate this process, and may allow for flexibility with certain code requirements. Particular consideration of outdoor air re- quirements should be given to spaces housing materials that may emit hazardous substances (e.g., radon) or require specific outdoor air volumes because of fire code. Air-Side Economizers Economizer controls, typically intended for energy-savings/free- cooling of interior environments, should generally be avoided in cultural heritage applications. Dry-bulb temperature and enthalpy controls may allow inappropriate levels ofmoisture (either too wet or too dry) into the airstream, increasing latent loads for dehumidifica- tion and humidification compared to the return airstream. Although dry-bulb temperature and dew-point controls can be programmed to allowable conditions, they generally offer reduced energy benefit compared to other energy-reduction strategies because, generally, most outdoor environments align with both temperature and dew- point requirements only for short periods. Economizers also increase risks to interior environment maintenance: control failure or me- chanical failure of outdoor air dampers on ductwork sized to allow for 100% of the system volume can quickly create significant envi- ronmental issues. Air-side economizers should not be used unless (1) bin analysis or other study shows outdoor air moisture content to be favorable for an economical number of hours, and (2) favorable out- door air can be reliably selected by the control system by combined dry-bulb temperature and dew point comparisons. Pressurization Positive air pressurization has been frequently used in cultural heritage facilities to minimize incursion of external loads into con- trolled collections environments. However, this practice often increases energy consumption, and in some cases increases the risk to the building envelope, particularly in historic structures. With improved envelope design and appropriate zoning and adjacency design, positive air pressurization is no longer an absolute require- ment in cultural heritage settings. Neutral pressurization is typically an appropriate goal; avoid negative air pressurization. In multiple- story buildings, stack effect (discussed later) creates unavoidable pressurization in upper floors; airflow design should not exacerbate this problem. Positive pressurization is typically created through a combination of outdoor air and duct design, with supply air ducts sized for greater volumes than the return air. Designs for pressuriza- tion in cultural heritage facilities should allow for equal volumes of supply and return air to the downstream zone to facilitate recircula- tion modes (no outdoor air) without pressurization consequences because of duct sizing. Modulating dampers on the outdoor and return airstreams as well as using adjustable return and supply air grilles can allow for balancing adjustments. Natural Ventilation for Preservation In some circumstances, natural ventilation may be necessary for interior moisture control and/or inhibition of mold growth. Historic structures with limited mechanical intervention may benefit from controlled natural ventilation on a scheduled basis (e.g., diurnal or seasonal operation) or may require either mechanized or passive ventilation for emergency situations or disaster recovery. The goal of ventilation is one of the following: · Move out moisture that has originated inside the building (e.g., rising damp) · Raise temperature of spaces containing a cold surface causing high relative humidity (e.g., a slab floor) or a high-mass wall without solar exposure · Reduce stratification of spaces containing a small, localized cold surface These operations may be enabled by a high-limit relative humid- ity sensor in the space, time scheduled, or (for disaster recovery or power outages) manually activated. Air Change Rates Air change rates in cultural heritage institutions are not constant values, and should vary based on zone usage and occupancy, with other specific factors (e.g., events spaces, fabrication or paint shops, conservation labs, off-gassing collections materials) accounted for as necessary. The operational goal after optimization is to run the sys- tem with the minimum air volume/change rates necessary to main- tain the desired environmental conditions while providing for occupancy and protecting against microenvironments. Proper enve- lope, airflow design, and duct layout should minimize potential microenvironments; environmental data logging in conjunction with control sensors can alert staff to potential issues. Initial design may use air change rates recommended for particular zone types (office, laboratory, classrooms, etc.) but should include variable-frequency drives (VFDs) or variable speed drives (VSDs) that can control air volume/change rates based on occupancy patterns, established needs, and other factors. Collections storage zones generally require lower air change rates unless extenuating factors (e.g., off-gassing materi- als, issues with microenvironments) dictate otherwise. Stack Effect Stack effect can have significant implications for control in cul- tural heritage settings, particularly in multistory structures and high- ceilinged spaces (ranging from modern high-bay storage environ- ments to historic structures that may incorporate historic frescoes and murals). Differences in temperature (and, to a lesser extent, moisture) between interior and exterior environments can result in density gradients that induce air movement and exchange, drawing unconditioned outdoor air into the building and often causing issues with airflow, microenvironments, and overall system operation. Stack effect may reverse depending on the exterior and interior con- ditions: when cooling indoors, upper areas may be negatively pres- surized relative to outdoors, drawing warm air into the structure, while lower parts of the building may be positively pressurized. The reverse is true when heating indoors. This is particularly problematic in structures with limited envelope integrity and limited or poor zone design. Where this effect is noted, if envelope improvements are not an option, pay particular attention to airflow design and balancing to combat preservation risks (typically from high-temperature and high-relative-humidity microenvironments). Stratification Interior thermal stratification can occur even in buildings with excellent envelope integrity. It is caused by the displacement of warm air by more dense cool air. This can occur independently of interior/exterior pressure differentials and, like stack effect, can cre- ate issues in preservation environments because of microenviron- ments and poor environmental controls throughout multistory or high-ceilinged spaces. Common problems include high Inc. ASHRAE, 2019 user. single for Licensed | {}
b16a9417-2f02-4c75-9b49-b767aa57a129 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 24.32 temperatures (which can increase rates of chemical decay) near ceil- ings and on upper levels, and issues with high relative humidity and potential mold risk because of cooler temperatures near floor level, especially in areas with poor air circulation. Proper zoning, airflow design, duct layout, and balancing can reduce stratification. For storage and cool environments, overhead diffusers and floor-level returns generally are preferable; occupied spaces (offices, galleries, etc.) may use floor-level or overhead diffusers. Ceiling or circula- tion fans may be used as low-impact solutions for improved air mix- ing and reduced stratification. 7.5 SPECIAL CLIMA TIC CONSIDERA TION Humidistatically Controlled Heating This specialized approach has limited application and must in- clude safety controls, but is sometimes the only option that can handle envelope limitations in cold climates. In this approach, the heating system is controlled by a humidistat rather than a thermostat (LaFontaine and Michalski 1984); cold, damp air is heated until the relative humidity drops to a predetermined safe range, typically be- low mold germination conditions. Where interior temperatures drop consistently below 10°C, it solves the problem of humidity in a building that does not have an adequate envelope. Humidity- controlled heating does not provide human comfort in winter, but many small museums, historic buildings, and reserve collection buildings may be largely unoccupied during this period. A high-limit thermostat is necessary to stop overheating during warm weather, and a low-limit thermostat may be used if water pipe freezing is a concern. This approach has been used in Canada (LaFontaine 1982; Marcon 1987), the United States (Conrad 1994; Kerschner 1992, 2006), and in many historic buildings in Britain. Maekawa and To- ledo (2001) successfully applied humidistatic control in hot, humid climates to minimize mold growth. Some cautions apply. Foundations in a previously heated build- ing may heave ifthe ground is waterlogged before freezing. Improv- ing drainage, insulating the ground near the footings, and heating the basement reduce this risk. Problems have occurred in buildings with dense object storage and a very low infiltration rate, such as a specially sealed storage space (Padfield and Jensen 1996); a very slow supply of dehumidified air to the space can be helpful. This approach is cost effective in seasonal museums (especially for low-mass wood-frame buildings) in colder climates such as the northern United States and Canada, and in maritime regions. Appli- cation in hot and humid environments should be judiciously consid- ered, typically where mechanical dehumidification is impractical. Humidistatically controlled heating may be applied where the immi- nent risk of mold growth outweighs other degradation risks, and should be balanced with the increased risk of chemical decay be- cause of elevated temperatures. In many circumstances, improved air circulation or natural ventilation for air circulation may be a pre- ferred first step for mold avoidance. Note: humidistatically controlled heating may be used in place of stand-alone dehumidifiers. As described in the following section on Dehumidification, stand-alone dehumidifiers and air conditioners pose a particular threat to cultural heritage collections because of the inherent risk of flooding and electrical fire in the local collec- tions zone; their use should be judicious, and only when the build- ing/space is occupied. Hot and Humid Environments Control ofmechanical operations in hot and humid environments (whether constant or seasonal) depends largely on the level of mechanical intervention selected. From a control perspective, mois- ture management (both relative humidity and moisture content/ humidity ratio) is the critical process, and may be achieved through various mechanical means, including dehumidification, cooling 2019 ASHRAE Handbook-HVAC Applications (SI) with secondary dehumidification (as in typical direct expansion/ refrigerant-based window, residential, and package air condition- ers), ventilation, and, less commonly, humidistatically controlled heating. In most applications, the primary preservation goal is to restrict mold growth and other biological risks, with mechanical damage (particularly in seasonally humid/dry climates) and chem- ical decay typically secondary concerns. Envelope capability heavily influences both control design and equipment selection. Where the structure has a modern, purpose- built envelope that can limit sensible and latent loads, temperature control and the limitation of chemical decay may be the first design priority. For most historic, renovated, and/or repurposed structures, control design for collections zones should primarily be based on space relative humidity. Designs should consider a specific ventila- tion control (whether integrated into the primary system, or as a sep- arate system) that can also be manually enabled in the event of limited power availability or long-term power outages, where gen- erator capacity may only be capable of providing circulation with- out temperature or humidity control. In mechanical designs where redundancy or back-up power may not be available, control and sys- tem designers should also consider advocating for passive strate- gies, including single-side, cross, or stack ventilation, as a way to provide airflow and limit mold growth during equipment failures or power outages. Additional information on environmental management in hot and humid climates is presented by Harriman (2009) and Maekawa et al. (2015). 7.6 INTERIOR CONSTRUCTION Interior construction decisions in multizone buildings can signifi- cantly affect the ability to successfully control interior environments. Early during predesign and design, itis essential to share information about partitioning, solar load, and spaces in which collections will be exhibited or stored. Beyond exterior envelope performance, archi- tects and engineers must consider interior zone separations, which may include thermal and vapor barriers between collections and non- collections zones. Zone design should strive to keep spaces on the same mechanical zone contiguous to one another, with interior con- struction designed to minimize air and vapor flow between the zone and adjacent spaces. Beyond thermal and vapor barriers in interior walls, ceilings, and floors, strategies should include These practices are also commonly required for any environmen- tal zone/space using clean-agent fire suppression systems. · Insulated, fire-rated doors · Door seals, gaskets, and sweeps · Sealing any penetrations, with overall penetrations kept to a min- imum · Ducted return rather than plenum design 8. CONTROL EQUIPMENT Hardware and software choices in control design should be based on the best application for the institution/building in question, and vary from basic, direct single-point thermostat/humidistat control of a residential-style heating and air conditioning system to larger build- ing automation (BAS) or building management systems (BMSs) intended to manage multiple air and water systems throughout a building or site. Rather than detailing the structure of the control sys- tem, the following factors should be considered in the design of any controls system for a cultural heritage setting. Inc. ASHRAE, 2019 user. single for Licensed | {}
ca07cb54-89ee-424d-87db-53c91e4424b2 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Museums, Galleries, Archives, and Libraries 24.33 8.1 HARDW ARE Sensors Selection. Selection of temperature and relative humidity sen- sors (thermostats, humidistats) should consider accuracy, initial calibration, and response time. Sensors for cultural heritage appli- cations generally trend toward the more accurate, with ranges of ±0.2 K and ±2% rh or better. As a guideline, response time should be within 1 min for temperature, and less than 2 min for relative humidity (BSI 2010). Reducing project costs by reducing relative humidity sensor reliability and accuracy is a false economy that will compromise operational accuracy and place the collection at risk. Dew-point sensors, though initially expensive, are much less likely to suffer from calibration drift. Calibration. Design and initial commissioning typically assume newly purchased hardware and represent the best-case operational accuracy for the system. Institutional staff should be provided with guidance for eventual replacement or recalibration to provide con- tinued accuracy in operation. Note that field recalibration rarely achieves the same level of accuracy as factory recalibration (if avail- able) or new equipment. Location. Typical sensor placement is based on control points, with occasional reference data (e.g., discharge air conditions, space or return air conditions, outdoor air conditions). Generally, primary control sensors should be located in the collections spaces; each col- lections space should have at least one sensor associated with the control system. As environmental optimization in cultural heritage has increased in popularity, institutional staff may desire greater transparency in operation, with data available from multiple points to assess the performance of individual system components. Sensor locations may now consist of an expanded list of reference points, beyond typical control points, and may include · Outdoor air · Return air · Mixed air · Cooled air · Heated/reheat air · Humidified air · Discharge/supply air after downstream equipment Designers should work with institutional staff to understand future informational needs and determine appropriate sensor loca- tions. Stand-Alone Data Loggers. Many cultural heritage institutions use stand-alone digital data loggers to monitor a collection s environ- ment for preservation purposes. These devices have the advantage of flexible deployment throughout a mechanical zone (close to the col- lection, or in areas of suspected microenvironments) compared to hard-wired control sensors, which, because of access, location, cali- bration, etc., may not always provide an accurate representation of what the collection experiences. Stand-alone data loggers are often equally as accurate as BAS/BMS sensors and may have the advan- tage of more regular calibration. Use of data loggers and data com- parison should be discussed during predesign; ideally, data from both systems (data loggers and BAS/BMS) should be used to assess envi- ronmental performance and to identify potential issues with either set of equipment. Some institutions may still use hygrothermographs to record environmental data; however, without continuous mainte- nance and frequent calibration by trained personnel, these units are prone to large measurement errors and are generally no longer rec- ommended for use in the cultural heritage field. CO2 Sensors. Consider using CO2 sensors as a control mecha- nism in settings where there are opportunities to control outdoor air intake beyond a set volume. In storage environments and collections spaces that are only lightly occupied or that are occupied on a fixed schedule, there may be significant opportunities to reduce heat, moisture, and filtration loads by minimizing outdoor air quantities when fresh air requirements are flexible. Variable-Frequency Drives Now common for both fans and pumps, VFDs or VSDs should be included on most systems larger than residential/light commercial equipment; small drives are regularly found on rooftop and other package systems. As control equipment, their uses vary; drives may respond to differential pressure or to downstream damper control in a variable-air-volume system or, more critical in collections-centric zones, can be used for optimal part-load fan operation or soft stops/ starts as part of programmed shutdowns. 8.2 SOFTW ARE BAS/BMS systems may be proprietary or open source, and selec- tion typically depends on the institution's level of on-site expertise: some institutions do controls programming in house, whereas many use outside contractors. Engineers should work with institutional staffto determine the likely level of staffinteraction with the system, and should select a product accordingly. Other considerations may include a preexisting contractor or product at a site, and the availabil- ity of qualified controls contractors in a given geographic area. All systems should ideally allow for · Data trending: retention of historical data from multiple points, including sensor readings, damper positions, motor speeds and status, and other information. Trends should allow for a minimum of one year's worth of stored data. · Data export: export of data to open file formats (e.g., plain text, CSV) that can be imported into other programs for storage or analysis. · Alarms and notifications: contact to multiple individuals, in- cluding staff in both facilities and collections, by email, text, or other means. · Remote access: ability to manage or adjust building/system oper- ation from off site, through a virtual private network or other secure connection. · Read-only access: for nonfacilities or controls staff who use the BAS/BMS interface to monitor environmental conditions or sys- tem operation. · End-user control (as desired): most institutions with on-site facilities staff should be able to adjust space temperature and rel- ative humidity set points, create operation schedules, have access to an emergency shutdown function, and be able to set new data trends. 9. SYSTEM DESIGN AND SELECTION System and equipment selection varies greatly from institution to institution. In addition to the factors of control philosophy that influence control design discussed under the Controls Design sec- tion, system and equipment selection must consider additional input that may be determined during predesign, including · Institutional staffing and in-house mechanical expertise · Physical configurations and limitations for mechanical equip- ment · Influence or requirements of historic structures and envelopes · Maintenance (preventive and reactive) practices and budgets · Availability of qualified technicians and contractors · Availability of onsite utilities, including water, electric, natural gas, renewable power · Preexisting equipment (e.g., chillers, boilers, perimeter systems, ductwork) that may influence equipment and design choices In system upgrades or renovation projects, a combination of these factors may significantly predetermine the type of equipment Inc. ASHRAE, 2019 user. single for Licensed | {}
5b99f612-2128-4958-9bfb-865dbb307b78 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 24.34 selected, although not necessarily its capacity or control. In new con- struction, the designer may have far greater flexibility in selection. Three key principles should be considered during system design and equipment selection: Inc. ASHRAE, 2019 user. single for Licensed · Design for purpose: cultural heritage design parameters may be significantly different from standard engineering designs for oc- cupied spaces, ranging from frozen environments to narrow bands of relative humidity control for specific spaces. The first goal of any design must be to achieve the required preservation condi- tions for various building zones. These conditions are determined during predesign and may require further discussion/refinement, depending on design option. Integrated design should strive to find the most appropriate holistic design solution possible for a structure that (for new construction) may have more than five dis- tinct environments managed by multiple air or water systems, plants with multiple chillers and boilers operating to different ca- pacities, and the possibility of significant downstream equipment. · Design for operability: design of mechanical systems for cultural institutions is often an exercise in the balance of cost, capability, and, in particular, technology. Ideally, system designs should be operated, maintained, and repaired by the organizational staff or local contractors; regardless ofits efficiency or potential, technol- ogy whose repair requires two weeks of lead time from a contrac- tor many hours away will be unsustainable. In many applications, simple designs with clear roles of components and clear control logic are more favorable than the latest complex technologies and subsystems. Possibly except for the largest institutions with signif- icant facilities infrastructure, cultural heritage is rarely the best proving ground for new or untested technologies. Redundancy may be significant and affordable in certain applications (e.g., humidification), but limited by capital budgets in others; resiliency must be considered in every design, often as an understanding of the holistic building system (systems, envelope and structure, sit- ing, etc.). · Design for longevity: though all equipment has limitations on its useful lifespan, equipment selection for cultural heritage should focus on designs and equipment that provide the longest service life possible. Many cultural heritage facilities are part of nonprofit or educational institutions whose capital budget planning may be on a longer cycle than other organizations. Installing package units with a 15 year service life expectancy for an institution whose bud- get cycle will not allow additional capital investment for another 20 years creates a potential 5 year gap where operation and main- tenance of appropriate preservation conditions may be a struggle. These discussions should be included during predesign and design, and engineers should clearly communicate the potential lifespan limitations of different equipment options to the institutional staff. 9.1 ENERGY AND OPERA TING COSTS Energy and operating costs of mechanical systems are primarily a function of the amount of energy work being done for a certain number of hours, commonly analyzed on a monthly or annual basis. With large portions of buildings requiring greater moisture control than many other applications, total energy consumption by cultural institutions can appear inflated compared to noncultural applica- tions while still being comparable to similarly purposed buildings and, at least over the past 20 to 30 years, generally expected by the cultural heritage profession. Energy work related to cultural heritage should first focus on achieving the desired environmental conditions with the least energy expenditure possible. Sometimes, predesign identifies lim- itations to the potential preservation environment driven by esti- mated energy costs; these instances require some compromise to achieve the best preservation condition achievable with the pro- jected energy/utilities budget. Initial capital investments made to 2019 ASHRAE Handbook-HVAC Applications (SI) reduce recurring annual energy costs may be considered, and con- tinuous commissioning and optimization can identify opportunities for energy reduction without altering preservation quality. Energy Audits During predesign, projects for existing buildings should consider an energy audit based, at minimum, on existing systems and their typical operation. Predesign teams may also consider comprehensive energy audits for the entire building, to identify the influence of ad- ditional energy factors (e.g., lighting) not addressed in a mechanical study. Data from the audit should be analyzed for evidence of exces- sive operation, with these findings informing future system design. After construction, institutions may perform periodic energy audits to inform continuous commissioning or optimization processes. Life-Cycle Cost Analysis (LCCA) Applied to mechanical systems, LCCA is the assessment of the whole cost of the potential installed system over its estimated lifes- pan. This exercise, which can be applied on a whole-building scale, greatly assists in selecting the most appropriate design solution when several options appear viable. Typically, LCCA for systems should include estimates of · Capital costs: purchase and installation · Energy costs, whether using fossil fuels or renewables · Operation, maintenance, and repair costs · Component replacement costs, where system components (coils, motors, humidifiers, downstream equipment, etc.) may be re- placed without changing the primary cabinet or system LCCA studies should carefully identify the variables being com- pared, especially regarding differences in systems versus differ- ences in environmental conditions. For example, comparative analysis of potential system designs that achieve the same environ- mental conditions (e.g., water-based subcool/reheat versus direct expansion cooling and electric reheat) is different from comparing LCCA for a water-based subcool/reheat system designed for either 20°C/50% rh or a 18°C/40% rh. Energy Efficiency Energy efficiency may be achieved either through direct equip- ment efficiency (e.g., more efficient coils or compressors) or through operational efficiencies, such as airflow control, outdoor air control, and strategies for nonpeak operation. In general, system designs should include the most efficient equipment selections pos- sible given budget and institutional infrastructure. Potential opera- tional efficiencies, which are highly dependent on performance and use of the final populated space, should be accounted for through flexible operational design (e.g., VFDs, modulating dampers and valves, programmable thermostats in smaller applications) and tested during continuous commissioning or optimization work before adoption. Lighting and Daylighting Lighting and daylighting, as they pertain to system design and op- eration, have several components to consider. Light-emitting diodes (LEDs) are increasingly common choices for collections environ- ments in both new construction and renovation, and unlike other lights (fluorescent, incandescent, halogen) have comparatively little impact on overall system operation and design. Although LED fix- tures do produce heat, the quantities are considerably smaller. Engi- neers should consult with lighting designers regarding lighting choices, their potential heat output, and what load must be accounted for in design calculations. Renovations of systems serving existing environments using a variety ofheat sources should consider a light- ing audit to determine existing thermal loads from space or exhibit lighting. | {}
5f5a1125-6088-4f50-8758-91da185ecc15 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Museums, Galleries, Archives, and Libraries 24.35 Daylighting is often proposed, especially for noncollections areas. Generally, daylighting should be avoided for all storage envi- ronments and avoided, or severely limited, for most exhibition spaces. Preservation assessment for possible light impact on col- lections should be conducted in conjunction with any lighting design. Ayres et al. (1990) noted that daylighting is always a net energy penalty. If used, the daylighting aperture should be mini- mized, and avoided as much as possible in and over collection areas. For lower risk of leaks and better-managed lighting, clere- stories are preferred over skylights. In applications where daylight- ing is unavoidable (e.g., historic structures), light-reducing and blackout shades and UV filters can reduce exposure of collections to both visible light and ultraviolet wavelengths, as well as reduce potential heat gain. Hybrid (Load-Sharing) HVAC Systems As detailed in Chapter 6 of the 2016 ASHRAE Handbook- HVAC Systems and Equipment, hybrid HVAC systems use multiple means ofheat transfer to control a specific environment. Most com- monly, this involves collocating radiant and forced-convection sys- tems. Most of the sensible loads are assigned to radiant panel systems, whereas latent loads and the remaining sensible loads are assigned to forced-convection systems. Decoupling the HVAC functions primarily into sensible and latent heat transfer compo- nents allows the designer to select better function-oriented HVAC components and ensure higher accuracy and precision in control, potentially at lower energy expenditure. Application has been lim- ited in collections environments; where the approach is used, in- floor radiant may be the most appropriate application because of the potential for microclimates against radiant wall panels in exhibition and storage environments. One key detractor for application in cul- tural heritage is the possible higher cost of installation and mainte- nance of dual systems. Historic structures, house museums, and recent buildings can present a similar scenario from a legacy perspective when institu- tions seek to combine modern forced-air cooling and dehumidifica- tion with original hydronic systems using radiators or a perimeter heat loop for either a portion or the whole of the sensible heating load. The heat transfer mode remains the same (both systems oper- ate by convection), but the operational challenge is similar to that with other hybrid heating system designs: management and control ofa hydronic system in conjunction with forced-air control. Balance and efficient operation can be excessively difficult to achieve; new construction, with opportunities for insulated glazing and perimeter forced air zones, can generally avoid using dual hydronic and forced-air systems. Dual Fuel and Multiple Energy Sources Dual-fuel and multiple-energy-source systems are typically seen in residential or light-commercial applications, often as a package unit that incorporates both fuel and electric heat depending on demand. Application of these units in cultural heritage is relatively limited, but as new technologies develop, other multiple-energy- source systems have begun to emerge, particularly for smaller appli- cations and heating/dehumidification side. Water heating may use recovered waste heat from various applications or use solar thermal collectors, with a traditional boiler for back-up; the hot water can then be used for heating, reheat for dehumidification, or regenera- tion for a desiccant system. Variants on hybrid designs, especially with renewable energy sources, may be particularly applicable in design situations where regular utilities are limited (e.g., well-water or tank fuel-storage systems) or the cost of certain forms of energy is prohibitively high. Maintenance and Ease of Operation As discussed previously, maintenance, accessibility, and ease of operation and repair are critical components of any proposed mechanical design. System design should enable both preventive and reactive (i.e., breakdown) maintenance by either existing insti- tutional staff or an identified contractor in the local area. Specialized equipment with no local maintenance or repair support should be carefully considered for potential benefit versus risk because oflack of maintenance, and alternative options should be explored. For large projects in larger cities, code-required staffing for the plant should be considered; sometimes, smaller reciprocating chillers can be used at night to preclude the licensed engineer needed to operate larger chillers. Specific aspects to consider as part of design review may include · Accessibility of the primary unit and individual components. Package units should have adequate clearance on all sides for maintenance, repair, and cleaning. For larger air handlers, access doors should provide access to all sections, and before and after all downstream equipment; installation should be careful not to block these with piping or ductwork. Valves and dampers must be accessible for preventive maintenance and repair. Above-ceiling units should be limited if possible because of access issues, and ideally should not be located in collections areas because of leak and access risks. · Exterior equipment (rooftop, ground-level pad, etc.) versus in- terior mechanical rooms. Exterior equipment installations typi- cally suffer in longevity, especially in salt-air environments. Where possible, equipment installations should be indoors, with adequate air exchange and access. · Clear component labeling. Piping and ductwork should be clearly labeled with its purpose and direction of flow, as should primary airflow on the unit and all sections. Basic flow schematics should be available for all air handlers and hydronic systems. This practice should also be applied in construction with clear labeling of piping, ductwork, and airflow. · Identification and labeling of manual shutoffs. Primary shutoff points (electrical disconnects, manual valves) should be easy to locate and clearly labeled. · Availability of drains and fire suppression. Floor drains should be local to equipment, and fire suppression (whether a central sys- tem or handheld) should be available. Effects of maintenance activities on the collection must always be considered. For example, testing or accidental activation of a smoke removal system can radically change the collection environ- ment. Tools and ladders in gallery and storage areas are a threat to the collection, and special precautions must be taken. Contaminated air conveyance components (e.g., mold growth and other build-up) can contribute to pollution levels, lead to premature component fail- ure, and affect heat transfer efficiency, resulting in higher utility costs. Regular inspection and cleaning are an important part of pre- ventive maintenance. 9.2 DESIGN ISSUES Zoning/Functional Organization As discussed in the section on Zoning (under Controls Design), three general environmental zones must be considered not only for control but also for system layout and design: noncollections spaces, occupied collections spaces, and unoccupied collection storage envi- ronments. Efficient operation is typically best achieved when each of these zones is served by mechanical systems dedicated to that partic- ular environment; this approach avoids unnecessary energy usage (e.g., significant dehumidification for a noncollections zone) and improves the likelihood of maintaining environmental control. Inc. ASHRAE, 2019 user. single for Licensed | {}
98d72ecb-e6b2-4634-b92f-fb7a2d1c4757 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 24.36 2019 ASHRAE Handbook-HVAC Applications (SI) The design engineer should be involved from the start of project planning to ensure that space layout does not present unnecessary problems. For both functional organization and design efficiency, spaces in similar environmental zones should be kept physically con- tiguous, with the occupied collections zone and the unoccupied stor- age environments adjacent to one another. This allows not only for efficient ducting, but also for efficient interior wall (thermal and vapor barrier) construction. Appropriate zoning should minimize the necessity for downstream subzone equipment (VA V/reheat, subzone humidification) in most occupied and unoccupied collections zones. Activities that pose a potential threat to collections environments (food areas, loading docks, fabrication and rough shops, mainte- nance and housekeeping, etc.) should be kept away from collec- tions zones, with exhaust from these areas located away and downwind from any fresh air intakes for collections systems and the rest of the building. One key exception to this practice may be relative-humidity-controlled crate storage, which may share a zone with occupied collections areas. Loading docks should ideally be positively pressurized, and shared walls with collections zones should be carefully designed to mitigate any potential energy trans- fer, whether from a load perspective or to reduce risk of condensation or other issues. Where possible, a separate loading dock may be specified for cleaner transfer of collections materials and crates, with direct access to crate storage and collections intake work areas. System Design and Envelope Performance System designs that call for interior moisture control, whether humidification or dehumidification, must carefully consider the likely performance of the existing or designed envelope for both thermal insulation and vapor transfer. These issues are commonly discussed for exterior envelopes, but the same issues can exist with excessive thermal or vapor differentials across interior walls. Thermal insulation/barriers should be adequate to moderate heat transfer through the structure, with particular attention paid to ther- mal bridges (e.g., wall studs, floor/wall junctions, roof/wall junc- tions) that may be sources ofheat gain/loss or potential condensation points. V apor incursion or loss occurs by two primary paths: air leakage/ gaps and diffusion. Air leakage or gaps speed heat transfer, but may be defeated for thermal loads with positive pressurization. Vapor carried by air cannot be fully mitigated pressurization: it slows the process by slowing air transfer, but vapor flow and equilibration between interior and exterior spaces continue independently based on vapor, rather than air, pressure. The differential between interior and exterior vapor pressures also drives diffusion (movement of water vapor through permeable materials) from areas of higher vapor pressure to lower. Diffusion manifests differently depending on exterior climates and interior environments. When exterior mois- ture conditions are higher than interior conditions, whether typically or seasonally, vapor may move inward, especially during dehumid- ification, adding to system load and causing efflorescence or other damage on interior surfaces. During humidification, vapor is typi- cally forced outward through the envelope, and may limit the pos- sible control of the interior environment and damage the structure's exterior. Diffusion in either direction, combined with interior wall temperatures, can cause significant structural damage ranging from mold growth in warm environments to structural failure in situations of repetitive freeze/thaw cycles. Windows, doors, and skylights can pose risks as potential con- densation points, as well as points of heat transfer. Repetitive con- densation on doors and windows places that element at risk, and the potential transfer of that moisture to the wall or floor can lead to issues ranging from mold and wood rot to cracking and masonry damage because of freeze/thaw. Older structures, especially those with historic significance, can be particularly problematic, especially in projects that propose indoor moisture control. Where envelope performance is in ques- tion, the first step is to reassess environmental goals: considering either higher or lower relative humidity ranges to minimize differ- ences in vapor pressure or, in cold climates, lowering temperature to raise relative humidity rather than using mechanical humidification. If specific conditions are necessary for long-term preservation, alternatives for containment of preservation environments should be considered, such as · Microenvironments (cabinetry, certain housing solutions, small- scale freezing) · Offsite, purpose-built storage, which may provide better environ- mental control with better energy efficiency · Limited envelope upgrades in part of the structure, often called box-in-box solutions, where interior surfaces are built in to pro- vide room for installation of thermal and vapor barriers Reliability and Resiliency Designs should include some way to manage the interior envi- ronment during periods of interrupted operation, such as mainte- nance, equipment failure, power outages, and disasters. Redundancy and back-up equipment may be applicable in the largest of cultural heritage applications, but capital cost, load cycling for long-term operability, and limited availability of physical space are all factors against redundancy as a typical practice. Rather, dis- cussion commonly turns to reliability and resiliency as risk mitiga- tion strategies for interrupted operation. Better understanding of collection equilibration times to environmental changes and im- proved building and envelope construction often mean that collec- tions, particularly storage areas, may be able to hold appropriate environmental conditions for longer periods than previously under- stood. The design team should discuss scenarios, with designs re- flecting potential response to events to minimize downtime. Spare equipment may be kept on site to allow for timely repairs, modulat- ing outdoor air dampers may be set to fail closed to minimize infil- tration, and in certain environments architectural and systems allowances may be made to provide natural ventilation in long-term disaster or recovery scenarios. Stand-alone generators may be part of this strategy, but their design and siting should be reviewed carefully for load capacity, accessibility, weight restrictions (for rooftop applications), fuel availability, and locations of fuel storage tanks, which pose their own significant disaster risk. Loads Accounting for design capacities for both sensible and latent en- ergy is critical in cultural heritage applications and collections envi- ronments. Though common when specifying some systems types such as four-pipe subcool/reheat and desiccant designs, adequate latent capacity is often disregarded with two-pipe and standard pack- age unit designs, resulting in environments that may be able to main- tain temperature control, but commonly see relative humidity conditions rise beyond safe limits as exterior temperatures climb and cooling capacity is dedicated to the sensible load. Certain specific load characteristics of cultural heritage build- ings should be considered in system design. Occupancy patterns can vary widely among zones. Noncollections zones and occupied col- lections zones tend to have high occupancy only at certain times, which may include events outside of normal operating hours. Some gallery occupancies are as high as 1 m2 but unoccupied per person, storage zones may have 100 m2 per person or less. Systems should be designed to handle maximum loads as well as the more common part loads. Many engineers design to 2 m2 per person because part ofthe room is never occupied. In zones where spaces are extensively used for receptions, openings, and other high-traffic activities, even higher density assumptions may be justified. Continual and close Inc. ASHRAE, 2019 user. single for Licensed | {}
f4e289bd-fc60-44bb-a452-591ec20f30d3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Museums, Galleries, Archives, and Libraries 24.37 dialogue between the designer and the institution is critical. Where possible, especially in renovation projects, designers should request actual gate counts and event attendance to solidify load estimates. Lighting loads vary widely by space and by time of day. For some applications, the most common driver of cooling load in a museum is display lighting, particularly where incandescent, halo- gen, fluorescent, or metal-halide bulbs are still used. The engineer should ensure that estimated lighting loads are realistic. Lighting typically varies from 20 to 85 W/m2 for display areas; figures as high as 160 W/m2 are sometimes requested by lighting designers, but are rarely needed. With growing awareness of damage caused by light, display areas for light-sensitive objects should have low illu- mination levels and associated low lighting power densities. The proliferation of LEDs has minimized many of the heat load con- cerns. Shelving, Storage Cabinetry, and Compact Storage Designers should be actively involved in discussions about col- lections storage designs, which can have significant impact on space airflow and the potential for microclimates. As a general rule, stor- age solutions fall into four categories for their interaction with the overall room environment: · Stationary library or museum shelving: aisle widths and vary- ing shelf heights generally allow for adequate airflow throughout the footprint. High-density storage environments with standard shelfheights spaced for storage efficiency may greatly restrict air- flow between stacks while still allowing airflow through the aisle. - Airflow should be parallel to or above the stack orientation; per- pendicular airflow will be blocked by the first stack, risking mi- croenvironments and poor circulation throughout the stack. - Proximity of diffusers: diffusers less than 1 m from shelving may expose collections to dangerously high relative humidity microen- vironments that can induce mold germination, particularly during dehumidification operations. · Compact library and museum storage (including sliding art racks): minimized footprints, minimal gaps when closed, and narrow spaces between racks can greatly reduce airflow through the assembly. Compact shelving often contains a mix of storage assemblies, including shelving, open bins, flat-files, and cabinets. - Diffusers must be above the compact assembly and configured for side supply to throw air across the top ofthe assembly to ensure adequate dispersal. - Carriages should be designed with spacers to allow a 40 to 60 mm gap between carriages when closed, to allow air movement within the assembly. - Density of materials and tightly closed carriages can behave as a sealed package that tends toward developing microenvironments. - For large art rack installations, airflow should be parallel to rack orientation. Perpendicular airflow will be blocked by the first rack, risking microenvironments and poor circulation throughout the in- stallation. - Proximity of diffusers: diffusers less than 1 m from shelving may expose collections to dangerously high relative humidity microen- vironments that can induce mold germination, particularly during dehumidification. · Storage cabinetry (standard): comes in various configurations, including flat file storage. These generally restrict airflow, but may include vent ports to allow for minimal air exchange, vapor equil- ibration, and off-gassing; · Storage cabinetry (gasketed): comes in various configurations but is specifically gasketed to minimize air exchange and provide microenvironments or buffering for relative humidity conditions; may be maintained with silica desiccant. In all applications, designers must advocate for sufficient spac- ing for airflow between storage furniture and exterior walls. Poor airflow can lead to high temperature or high relative humidity microenvironments, particularly near exterior walls with inadequate thermal resistance. Integrating HVAC with Design of Exhibit Cases, Closed Cabinets, and Packaging As discussed in the section on Response Times of Artifacts, the hygric response time of an enclosure containing hygroscopic mate- rials will almost always exceed 24 h and can reach many months. This is analogous to the thermal mass (flywheel) effect of a build- ing, but with hygric response times typically an order of magnitude longer. Design of sustainable and reliable building humidity control should take advantage of the hygric flywheels filling the building, not fight them. Feeding HVAC supply air into cases, though often proposed, usually results in very erratic conditions inside the cases since the moisture and thermal loads of the cases are a tiny fraction of the room loads. Barrette (1985) describes the failure of a system using AHUs attached to very large display cases at the Metropolitan Museum, and their (successful) decision to adopt "passive" relative humidity control instead. When the annual average relative humidity ofthe space is suitable for the object or collection, a completely passive approach is best. Many objects can adapt to a stable relative humidity somewhere be- tween 35 and 60%, and the annual average relative humidity inside many buildings (with HVAC) in many climates is also in this range. The role of the enclosure is to smooth out relative humidity fluctua- tions. If the only fluctuations are hourly or daily, and the enclosures are more than half full of hygroscopic materials, then ordinary en- closures (e.g., metal storage cabinet full of paper files, photographic materials in impermeable packaging) can perform well enough. If the fluctuations are seasonal, or the enclosure has only a small frac- tion of its volume filled, then achieving an adequate response time requires special attention to seal details and probably additional hu- midity buffers (Tetreault and Begin 2018). The key to achieving long response times is reducing enclosure leakage (Michalski 1994; Thickett et al. 2007). Measuring and specifying acceptable case leak- age is well established in museums (Thickett et al. 2007). When the annual average relative humidity is not acceptable for the object or collection, routine intervention becomes necessary. The most reliable intervention is using a removable humidity buffer, typically silica gel. When the enclosure drifts to an unacceptable relative humidity, the (reusable) buffer is removed and replaced with one that has been equilibrated (reconditioned) to the desired relative humidity. This technique has been used to maintain middle, very low, or very specific relative humidity conditions in display cases (Thomson 1986), shipping crates (Richard et al. 1991), boxes with mineral specimens (W aller 1992), and film packages in cold storage (McCormick-Goodhart 2003). This method provides resilience: if the reconditioning process is abandoned (not unusual), all high risks from incorrect relative humidity are still mitigated as long as the annual average does not exceed 65% rh. Tetreault and Begin (2018) provide a recent manual on the application of silica gel buffers for museums. Active mechanical control systems for relative humidity alone have been made for museum enclosures, especially display cases. These can be very small commercial units hidden in a single case, or designs for a larger package that feeds many cases via small- diameter tubes (Shiner 2007). Often these are used as short-term solutions to a loan requirement. For permanent collections, experi- ence shows that the key factor for long-term success is that the units have a known parts and maintenance provider, and that they are ad- opted and maintained by facilities staff, not by the conservation or exhibits staff alone. Inc. ASHRAE, 2019 user. single for Licensed | {}
0b8c8f7a-8851-4ee6-a605-3e3f841cdf62 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 24.38 2019 ASHRAE Handbook-HVAC Applications (SI) 9.3 SPECIALIZED SPACES Cold/Frozen Storage Vaults Cold or frozen storage vaults extend the life of materials particu- larly sensitive to chemical deterioration (e.g., cellulose acetate, color photographic materials), or those that require cold/frozen conditions for their own stability as well as the potential threat they pose to other collections materials (e.g., cellulose nitrate). Design environmental conditions (see Table 13B) for cold/frozen environments typically require dehumidification beyond what can be achieved by chilled- water or glycol-mix systems. Direct expansion (DX) systems, though common as the primary equipment for cold/frozen environ- ments in other industries, are typically only used for sensible cooling in these environments for cultural heritage. Dehumidification is han- dled as a separate process, typically via desiccant equipment, which achieves the preservation requirement for cold temperatures at con- trolled relative humidity conditions. Design and construction of frozen vaults, in particular, should be carefully considered from a space need perspective: many cultural heritage institutions have only limited quantities of media that re- quire frozen storage. For smaller collections, storage needs may be met with stand-alone solutions such as frost-free freezers. Depend- ing on intended usage patterns, frozen storage may not be the best solution (see Table 6). Cellulose nitrate is classified as a hazardous material; beyond preservation requirements, consult NFPA Standard 40-2019 and lo- cal fire codes for safe storage and disposal requirements. Smaller quantities can potentially be safely managed with approved cabine- try; vaults that hold larger quantities have specific construction re- quirements, including fire-rated walls and explosion venting. Antechambers may be necessary in certain applications, espe- cially where vault temperatures are colder than the typical ambient dew point (whether seasonal or year-round). The antechamber mi- croenvironment should allow the object to fully equilibrate to a tem- perature higher than the final environment's dew point, with relative humidity in the safe range for the media. Some collection packaging practices may eliminate the necessity of the antechamber; applica- tion varies by institution and should be discussed during predesign. Conservation Laboratories Detailed discussion of HVAC design for laboratories can be found in Chapter 17. Further details on containment, collection, and removal of airborne contaminants such as particulates, vapors, and hazardous gases can be found in Chapter 33. 9.4 PRIMARY ELEMENTS AND FEATURES Figure 16 shows the basic components of a cultural heritage HVAC system, and their typical order along the airstream. A few aspects of this order are different from many other applications: the cooling coil precedes the heating coil, to allow dehumidification fol- lowed by reheat; and the fine filter is last in line, to capture particu- lates created by any of the preceding components. A desiccant dehumidifier is common in cool and cold storage systems that need relative humidity control. The following sections outline details, as well as the many variations on this system. Air Volumes Air volume design in most cultural heritage applications should account for varying needs; individual functional zones may have volume requirements that change based on occupancy, space usage, loads, and other factors. In all cases, the design goal should be to provide the appropriate volume required to meet the need, without expending energy on work applied to volumes that are unnecessary. Collections zones should have supply and return air ductwork designed to equal volumes to allow for recirculation without risk of RELIEF AIR MAY BE REQUIRED FOR VENTING OFFGASSING COLLECTION ![image](/image/placeholder) RELIEF AIR NEUTRAL OR POSITIVE PRESSURE DAMPER RETURN AIR SUPPLY AIR CO2 H T RETURN AIR DAMPER OUTDOOR IVA FINE FILTER AIR DAMPER HUMIDIFIER PREFILTER SUPPLY AIR FAN HEATING COIL PREHEAT COIL COOLING COIL GAS-PHASE FILTER PREFILTER DESICCANT DEHUMIDIFIER IN POSITION 1 OR 2, IF USED FILTER REACTIVATION REACTIVATION HOT, HEATER FAN HUMID DESICCANT EXHAUST WHEEL Fig. 16 Basic Components of HVAC System for Museums, Galleries, Archives, and Libraries negative pressurization during low-occupancy, minimal outdoor air operation. Diffusers with adjustable outlets should be selected to allow appropriate zone balancing. The specific application of con- stant-volume and variable-air-volume designs is discussed in the section on System Types. Fans Every forced-air convection system, ranging from air-handling units to computer room air-conditioning (CRAC) systems and fan- coil units (FCUs), has at least a supply fan; depending on total air volumes, physical extent of the zone, outdoor air and exhaust design, etc., return fans may also be required. For institutions with the appro- priate infrastructure, fan-wall/fan-array designs have distinct advan- tages over single-fan designs, including ease of motor maintenance/ replacement and improved redundancy/resiliency. In either single- fan or fan-wall solutions, each motor should typically be equipped with a VFD; for systems with both supply and return fans, designers should ensure that VFDs are installed on both motors. Fans may also be required for processes separate from the pri- mary mechanical design. Ceiling and other circulation fans can be very effective for mitigating stratification and microenvironments, and some designs, especially in historic structures, should include fans for natural ventilation or other purposes. Heating Equipment Equipment for sensible heating in cultural heritage applications varies widely; direct-fire solutions are occasionally applied to stor- age warehouses and as components in desiccant regeneration, and indirect-fire systems, ranging from residential-type systems used in many historic structures to roof-top package systems, are common in smaller applications. Heat pumps may appear in smaller struc- tures in hot environments, and electric heat can be applied in various Inc. ASHRAE, 2019 user. single for Licensed | {}
c66afc05-6508-4ae3-9309-fb8b08028d02 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Museums, Galleries, Archives, and Libraries 24.39 settings, as the primary heat source or as a downstream component. Coil-based designs are most common in larger cultural heritage applications, and may be served with hot water or steam from boil- ers or a central plant. Heat generation systems can vary, including steam and oil with converter, modular boilers, and scotch marine boilers. Downstream reheat coils (common in VAV systems, but may exist without) most commonly use hot water or electricity. Locations ofheat application can vary; preheat may be required to protect downstream coils from freezing. For cultural heritage insti- tutions, heat should typically be applied downstream of a cooling coil to allow for dehumidification. Reheat coils as part of down- stream VAV configurations are typically best used for increased sen- sible temperature control. If used as the sole source of reheat, the capacity of downstream in-duct coils should be carefully considered and sized appropriately. Cooling Equipment The most common equipment for sensible cooling is coil based, including DX (refrigerant) systems, chilled water, and glycol. Evap- orative cooling, common in arid regions, can be difficult to apply in cultural heritage settings because of reduced sensible temperature and moisture control. Designs using evaporative systems should carefully consider performance during any wet/rainy seasons; alter- native design or additional equipment may be required for dehumid- ification. Ice storage systems with glycol may be an option in larger applications with appropriate infrastructure. Cooling coils are commonly used for both sensible cooling and dehumidification in a subcool/reheat configuration. Location of cooling should typically allow for both sensible temperature control and dehumidification, with the cooling coil located upstream of the heating coil. Screw compressors are recommended to generate chilled water at 2°C for use in chilled-water coils, which generally have copper fins and tubes. Humidification Humidification should be provided by clean steam or deionized water introduced in the air system. Evaluate the moisture source for risks of pollutants; building/plant steam should typically be avoided as a source for humidification, unless used to generate clean steam via a steam-to-steam heat exchanger. Often, steam used in closed loops to heat is treated with compounds (especially amines) that can pose a risk to the collection (V olent and Baer 1985). Systems should be selected and designed to prevent standing pools of water, and should follow good humidification design (see Chapters 1 and 22 of the 2016 ASHRAE Handbook- -HVAC Systems and Equipment). Humidification equipment varies based on the application. In all applications, deionized or reverse osmosis water (based on institu- tional needs and availability) are preferred, whether for isothermal or adiabatic systems. Isothermal is generally more common, especially in year-round or seasonally cold environments, and steam is com- monly generated via steam-to-steam heat exchangers or electronic steam humidifiers. Adiabatic systems (i.e., evaporative pan humidifi- ers, spray-coil wetted-element systems, pressurized-water atomizers, ultrasonic humidification) are more common in warmer climates. All materials in humidification equipment should be selected to minimize mold growth and degradation of system components. Humidification should typically be located downstream of cool- ing and heating coils, and preferably in the primary air-handling unit. Mechanical design for cultural heritage is often more concerned with controlling humidity than temperature. The averaging effect of a common mixed-return air and common humidifier on a central sys- tem is preferred, but downstream zone humidifiers may be necessary to boost relative humidity because of specific environmental require- ments or loads. Iflocal low humidity conditions exist, try to identify and correct the cause of the condition before applying further me- chanical solutions. Duct installations, whether on a common supply or in downstream subzone applications, should follow design re- quirements for absorption and be provided with drainage from the ductwork. Downstream humidifiers should not be located above col- lections areas; ifit cannot be avoided, the ductwork approaching and downstream of the humidifier should be fitted with an additional catch pan with a drain and water alarm beneath the duct to provide protection for the collection. Widely different conditions in zones using the same air handler can be difficult to maintain and inefficient. If possible, different zone conditions should have the same absolute moisture content, using zone reheat to modify space humidity for different relative humidity requirements. Designers should review maintenance requirements for humidi- fiers with institutional staff or contractors; electronic steam humid- ifiers and systems using building water can require particularly intensive maintenance to maintain design conditions and remain operable. Humidification in structures with limited envelope capac- ity should be carefully considered, and typically avoided. Dehumidification Dehumidification is the single most critical mechanical process for many cultural heritage institutions, and should be a central focus of most system designs. The required environmental conditions often determine the means of dehumidification. Sebor (1995) sug- gests the following typical approaches to more aggressive dehumid- ification: · Low-temperature chilled water, usually based on a glycol solu- tion, offers familiar operation and stable control but requires gly- col management. · DX refrigeration tends to be better for small systems and has low- er capital costs, but generally is less reliable, requires more energy, and may require a defrost cycle. · Desiccant dehumidifiers can be effective if properly designed, installed, and maintained. Economy of operation is very sensitive to the cost of the regeneration heat source. Active desiccants are typically preferred in collections settings and have become com- mon features in cool/cold environment designs. Liquid desiccant systems eliminate (1) the need to cool the air below the dew point, and (2) reheat, both of which are very important cost factors for sustainability. Note that the possible application of liquid desic- cant systems to collection environments should be carefully dis- cussed with collections/preservation staff because of the potential risk of any aerosolized desiccant media coming in contact with collection materials. Subcool/reheat designs, typically using cooling and heating coils, can generally achieve dew-point conditions as low as 2 to 3°C, depending on the chilled water/glycol temperature. Lack of dehu- midification capacity may originate with design assumptions or equipment selection, or may be caused by issues including compro- mises in the cooling medium temperature, inadequate reheat, dirty or blocked coils, and poor flow or valve control. Desiccant dehumidification, most commonly used for low dew points necessary in cold/frozen environments, is now being applied for dew-point control in some applications at 4°C and higher. Des- iccant technology (typically a silica-gel rotary wheel design) can be installed as part of the primary system or as a separate component that feeds into the main air handler. For zones with minimal latent loads, or in designs using a high volume/percentage of outdoor air, designers may choose to focus on dehumidification of the outdoor airstream, rather than on the mixed air. For smaller applications and systems, package desiccant systems may be put in line with outdoor or return air. Dehumidification systems should be additions to a typ- ical cooling system; they cannot maintain comfort conditions by themselves. For collections requiring cool, dry conditions, a Inc. ASHRAE, 2019 user. single for Licensed | {}
71566c5b-3685-4f9f-bc10-b57769d44f55 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 24.40 2019 ASHRAE Handbook-HVAC Applications (SI) desiccant system may be required. Chapter 24 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment has further information on desiccants. Note: stand-alone dehumidifiers, common in residential and smaller applications, are not recommended for use in cultural heri- tage settings except in emergency scenarios. Risks to collections (e.g., electrical fires, flooding from basin overflow) generally out- weigh benefits. If stand-alone dehumidifiers are used in collections environments, it should only be during occupied hours, with units emptied and unplugged before staff leave. Outdoor Air Outdoor air should typically be limited to the minimum neces- sary in cultural heritage applications. Intakes should have modulat- ing dampers balanced with return air dampers on the system. Siting of the physical intake is critical; potential locations should be eval- uated for various factors, including pollutants (e.g., vehicles, equip- ment, kitchen exhaust), prevailing wind directions, and sources of moisture/particulates (e.g., sprinklers, landscaping). In most appli- cations, outdoor air intakes should fail closed on a shutdown or power outage, with the ability to manually adjust the damper if nat- ural ventilation is required. Preheat, precooling, or dehumidification may be best applied to the incoming outdoor airstream, increasing operational efficiency. Ductwork Ductwork selection varies by application; sheet metal, flexible fi- berglass (flex duct), cloth, and others can be appropriate duct choices. Fiberboard is typically not recommended for cultural heri- tage institutions because of the potential for media breakdown over time. All supply air ductwork should be insulated on the exterior, but return air ductwork should be insulated on the exterior if the differ- ence between the duct condition and the ambient space is enough to make condensation possible. All duct joints, both in the duct itself and in the insulation, should be sealed against air leaks. Interior ductwork insulation/lining is not recommended in cultural heritage applications because of the potential for trapping moisture and the eventual breakdown into particulates that can deposit in collections areas. Where external insulation is not possible, or there are signif- icant sound attenuation needs, interior duct lining may be consid- ered ifit meets hospital and health care facility standards: fiber free, closed cell, antimicrobial coated, low- VOC certified, and moisture and mold resistant. These sections must be clearly labeled on design drawings and should be discussed with institutional staff regarding ongoing maintenance and eventual replacement. Inc. ASHRAE, 2019 user. single for Licensed Design 9.5 FILTRATION Particulate filtration is essential for removal of contaminants that could foul the HVAC system, as well as particles that might degrade or deface collections being preserved. For this reason, particulate filtration is addressed here in two steps: prefiltration and fine-par- ticulate filtration. Physical location of the filtration stages affects HVAC system performance, energy use, and ultimately protection of collections. In upstream filtration, all filtration is placed upstream of the cool- ing/heating and fans in system. All filters are essentially prefilters, even though fine-particle filtration may be present in the HVAC sys- tem. When all filters are upstream, itis common practice to stack fil- ters, with a MER V 7 or 8 prefilter on a MERV 14 or 15 fine particle filter in the same section. This is done to preserve the life of the fine- particle filter. However, evaluate whether the cost of energy out- weighs the savings of the fine-filter life: most collection areas are fairly clean environments. Eliminating the prefilter can be a very effective improvement to airflow and energy savings. In upstream/downstream filtration, prefiltration is installed up- stream of the cooling/heating and fan components and final filters downstream of all mechanical equipment. This more effective ap- proach prevents a failure of HVAC components from fouling the ductwork and preservation areas downstream. In this case, it is im- portant to filter at a minimum ofMERV 11 for any chilled-water sys- tems to prevent microbial fouling of the coils. MERV 7 or 8 is at best only 50% effective in this particle size category, and does not provide the protection needed against biofilm growth. Performance In some cases, prefiltration for HVAC system protection is the only filtration in a collection area. Ifthis is the case, MERV 13 is rec- ommended. Prefiltration is required to prevent fouling in cooling coils and dust build-up in the fan, ductwork, or other HVAC components. It also protects and prolongs the functional service life of gas-phase fil- ters and fine-particle filters. These fouling-size particles and mi- crobes tend to be between 2 and 6 �m and accumulate into biofilms on coils and other wet areas in HVAC systems. MERV 7 or 8 filters by definition will not protect HVAC systems from this particle chal- lenge and should be replaced by a minimum of MERV 11. Fine-particulate filtration protects artifacts and collections in the facility. These accumulation-size particles fall in the MERV E- 1 range of particles (0.3 to 1 �m). Removal efficiencies of a mini- mum of 85% of the E-1 range are sufficient for preservation of most collections. MERV 15 filters by definition are minimum 85% in the E-1 range, and minimum 90% in both the E-2 (1 to 3 �m) and E-3 (3 to 10 um) ranges. Some collections may require efficiencies higher than MERV 15 for long-term preservation. Options include microenclosures with minimal airflow and separate filtration, or HEPA (99.97% at 0.3 um) filtration for the entire common area. Whenever HEPA filtra- tion is used as the final filtration, seriously consider upgrading the prefiltration to protect the life of the HEPA filters. Framing systems should be able to seal the air filters without bypass air leakage in housings and unit access doors. System designs with positive locking mechanisms for filters are beneficial, as is using gaskets rather than framing components on filters. High-voltage electrostatic air cleaners should be used with cau- tion because of their potential to generate ozone, which can damage collections (see Table 9). Outdoor air infiltration of gaseous pollutants, materials off-gas- sing in new construction, and similar off-gassing of furnishings may put some collections at risk. Sensitive collections, such as those containing some metals and alloys, film, various papers and low- fired ceramics, should be carefully enclosed or controlled by an active gas-phase filtration system, depending on which method is most appropriate for reaching the desired preservation target (see the section on Control Strategies for Objects with High Vulnerabil- ity to Pollutants). The primary compounds of concern include hydrogen sulfide, nitrogen dioxide, ozone, sulfur dioxide, and undesired volatile organic compounds, all of which are removable with molecular fil- tration. The specific sorbent must be chosen for the various gaseous contaminants indigenous to the facility, because removal and reten- tion properties are not all the same. Some gases are easily removed with activated carbon, whereas others may require treated sorbents or beds. Using potassium-permanganate-treated media is not rec- ommended because of the risk from the highly oxidative dust to col- lections and space surfaces. Service life of molecular filtration media should be carefully evaluated. Much service life testing has focused on the potential mass removal capacity of the sorbent when immersed in a challenge | {}
ff87a829-0894-44ec-b12d-470b3bed8722 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Museums, Galleries, Archives, and Libraries 24.41 chemical; although this information may be useful, its ability to remove pollutants from an airstream may not be achievable even though the sorbent is not spent. If a molecular filtration system is used, some gas-filter designs require dusting filters downstream, because the aging gas filters can release dust that can affect the HVAC system and collection. Gas-phase filtration system design should also consider institu- tional staffing and preventive maintenance practices; infrastructure must be able to support timely media replacement, in both labor and material cost. Consider gaseous contaminant monitoring and anal- ysis before fully adopting gas-phase filtration; designers may choose to include the gaseous filter section in the design, but wait to install media until need has been determined. 9.6 SYSTEM TYPES The type of HV AC system used is critical to achieving environ- mental goals; appropriate types may vary by zone based on use. In any cultural heritage application, proper airflow filters the air, con- trols moisture and relative humidity, adjusts temperature for either collection needs or human comfort, and inhibits mold growth and oxidation. For any design, maintenance access and minimizing risk to the collection from disruptions and leaks from overhead or decentral- ized equipment are primary considerations. Water or steam pipes over and in collection areas present the possibility ofleaks, as do air- handling units. Some systems can provide full control without run- ning any pipes to the zones, but others require two to six pipes to each zone, which often must be run over or in collection areas and are, unfortunately, the pipes most likely to leak. Leaks and mainte- nance can prevent effective use of spaces and result in lost space efficiency. Central air-handling stations keep filtration, dehumidification, humidification, maintenance, and monitoring away from the collec- tion. The investment in added space and expense of the more elab- orate duct system provide major returns in reduced disruption to the collection spaces and a dramatically extended service life for the distribution system. Where existing duct systems can be reused, ren- ovating the existing system is economical, with most renovations confined entirely to the mechanical rooms. Duct distribution sys- tems that are heavy on downstream equipment (e.g., terminal reheat, dual-duct, variable-air-volume) may require a new duct system and terminal equipment as part of a renovation, incurring major expense from demolishing the old ducts, installing the new duct system, and reinstalling architectural finishes. Variable-Air- v olume and Constant- v olume Air volume design can depend on several factors, including · Sensible and latent loads in a space · Collection degradation · Practical airflow based on system design In most cultural heritage applications, variable-air-volume (VA V) systems, in single-zone or multizone configurations, are appropriate. Note: multizone VA v systems should not be used to serve multi- ple functional zones. Rather, the approach should be to account for varying loads within the same functional zone. (See the sections on Zoning and on Zoning/Functional Organization) Multizone VA V has the distinct advantage of providing better temperature and relative humidity control to individual subzones with different sensible loads; both multi- and single-zone VAV design can achieve significant energy-savings in climates with diur- nally or seasonally variable sensible and latent loads. Single-zone VAV designs in cultural heritage typically vary air volumes and occasionally sensible reheat temperatures; cooling coils, if used for dehumidification, most often have a single leaving air set point. Constant-volume system designs may be necessary in certain sce- narios. Some geological collections can emit radon, and may require constant volume and increased air change rates. Interior zones (e.g., storage rooms surrounded by a perimeter zone and with limited out- door air) and some climates may experience essentially the same la- tent and sensible loads constantly, limiting the effectiveness of VAV designs. Even in these cases, initial designs should consider the in- clusion of at least a VFD: actual air volume requirements may be dif- ferent than design modeling, and the VFD allows adjustment of the optimal volume, even if the system operates at a constant volume moving forward. For small volumes and applications, such as some cold/frozen storage vaults, constant volume (CV) may be the most practical design, whether based on equipment airflow requirements or simply because a VA v design offers no noticeable preservation or energy advantage. Institutional capabilities and infrastructure must inform air vol- ume and airflow designs. VAV control and equipment can quickly add to control/operational complexity and maintenance require- ments; consider staff capabilities and/or the availability of qualified contractors before finalizing the design. VAV or CV Reheat A reheat system can present problems if improperly applied. In many institutions, terminal reheat with steam or hot-water coils located near or over collection spaces causes chronic problems from steam and water leaks. Subzone humidification control guidance often suggests placing the humidifier downstream from the terminal reheat coil; if the reheat coil is located near or over collection spaces, preventive maintenance on humidifiers further complicates the maintenance requirements. Reheat systems for collections zones are most effective when reheat coils and humidifiers are installed entirely within the mechanical space, instead of at the terminal end, feeding through what is effectively a multizone distribution system. Multizone Systems A multizone air handler with sufficient dehumidification capac- ity at the primary unit, zone reheat, and zone humidification can be a stable and relatively energy-efficient solution. However, multi- zone systems without individual zone reheat and zone humidifica- tion have proved problematic for many institutions, requiring retrofit of zone equipment for stable humidity control. With proper layout and complementary equipment, a multizone system can reduce the amount ofreheat and be very energy efficient. Multizone systems should consider dehumidification in the outdoor airstream or upstream of the heating coil to ensure that sufficient dehumidifi- cation is available to the entire airstream. Note that multizone designs are still best applied to spaces with similar dehumidification requirements; mixing collections and noncollections spaces in the same multizone design typically leads to inefficiency and difficulty maintaining space conditions. Future renovation or changes in space usage can significantly impact design viability, again leading to issues with efficiency and management of the preservation envi- ronment. Dual-Duct Systems Inc. ASHRAE, 2019 user. single for Licensed As with multizone systems, dual-duct designs can work well in cultural heritage if zoning is carefully considered. Downstream mixing boxes must be controlled and maintained to guard against overcooling and the resultant high-relative-humidity conditions. A critical consideration for dual-duct designs is a separate dehumidi- fication coil upstream of both the hot and cold decks. This separate cooling coil, distinct from the one in the cold deck, is used during dehumidification demand. Air can be cooled to dew point even ifit eventually flows through the hot deck. Without this feature, moist return air or outdoor air could be warmed in the hot deck and | {}
3da0cc5f-9343-4d62-a93b-5149fd6acf39 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 24.42 2019 ASHRAE Handbook- -HVAC Applications (SI) delivered back to the room without being dehumidified. An alterna- tive is to locate a single cooling coil upstream of both decks, or in the outdoor air. Fan-Coil Units Fan-coil units have been problematic when placed in and above collection areas. Fan-coil units expand and decentralize mainte- nance, requiring maintenance in collection areas and a net increase in overall facility maintenance. Because they cool locally, they need condensate drains, which can leak or back up over time. As all- water systems, they require four pressurized-water pipes to each unit, increasing the chance of piping leaks in collection areas. Fan-Powered Mixing Boxes Fan-powered mixing boxes are usually inappropriate for cultural heritage facilities. Although fan-powered mixing boxes can help ensure air circulation to suppress mold growth, they do not allow effective air filtration for particles and gases. These fans also increase local maintenance requirements and present an added fire risk. If they include reheat, there is an added risk from leaks (with water or steam reheat) or fire (with electric reheat). 10. CONSTRUCTION (This section is based, with permission, on Maekawa et al. [2015].) The system design is physically realized through the procure- ment, construction and installation of equipment. Conformance with the design intent and the owner's project requirements (OPR) is confirmed through various methods, including review and accep- tance of the contractor's technical submittals for materials and equipment to be supplied; in-factory acceptance of complex equip- ment before shipment; qualification and certification of tradesper- sons for certain critical installation activities such as welding; and field observation and inspection of equipment and systems during installation. Construction quality, including cleanliness of systems during construction, is critical; all incomplete piping and ductwork should be kept closed or sealed during installation to prevent introducing dust and debris. 11. COMMISSIONING (This section is based, with permission, on Maekawa et al. [2015].) Start-up, testing, and balancing are performed once an environ- mental management system is installed. Preparation includes the following: · Design conformance: The installed system must be checked for conformance with the design intent and the owner's project requirements. Specifically, the leaktightness of air and hydraulic systems must be verified by pressure testing; pump and fans checked for proper rotation; valves and control devices checked for correct actuation/response; and the electrical continuity and proper polarity of electrical wiring and connections must be con- firmed. Sensors, instrumentation, and control devices must be checked for correct calibration and signal/response. · Cleaning: Hydraulic systems must be flushed clean using start- up strainers, and air systems operated with construction filters; both operations must continue until cleanliness requirements are met, as indicated by the amount of construction-related debris and particulates captured in the strainers and filters. · Start-up: Operation of each piece of equipment must be initiated in accordance with a start-up procedure provided by the equip- ment manufacturer. Itis essential to adhere to the manufacturer's start-up procedures, because the manufacturer's warranty period begins with the initial power-up of equipment; failure to follow start-up instructions can void the warranty. On completion of preliminary testing, cleaning, and start-up of individual components, equipment, and assemblies, the start-up sequence and shut-down sequences for the entire system must be verified before the system can be operated. After successful system start-up and shut-down, the system can be balanced for operation and construction commissioning can occur, as follows: · Balancing: The balancing phase consists of measuring system air and fluid flows, making adjustments, and balancing the flows to match design flow rates. This may require adjusting airflow using dampers in ducts and/or pulleys or belts at the fans. Similarly, water flow rates in hot- or chilled-water systems must be mea- sured, adjusted, and balanced. Both cooling and reheating capac- ities may also need to be adjusted by refrigerant compression or by regulation of cooling or heating fluid flow rates, to produce design heating, cooling, or dehumidification. Electrical loads from equipment must also be verified. · Construction commissioning: After testing and balancing, con- struction commissioning occurs, during which system perfor- mance is checked against the owner's performance requirements and verified. In climates with wide ranges of thermal and mois- ture loads over four seasons, performance verification may take up to 12 months; in climates with more consistent thermal and moisture loads throughout the year, performance verification might be accomplished in 6 months. 12. TRAINING AND DOCUMENTATION (This section is based, with permission, on Maekawa et al. [2015].) The facilities staff at the building where the environmental man- agement system is installed should be familiar with the owner' s per- formance requirements and knowledgeable about design intent, operation, maintenance, and basic troubleshooting of the system. In-house knowledge of the OPR helps protect the collections, min- imize unnecessary service calls, maintain system operation within performance specifications, and avoid premature failures. After sys- tem start-up, testing, and full commissioning, the facilities staff and building maintenance personnel must be trained in the operation and maintenance of the environmental management system. Train- ing should start with the fundamentals of the system , s design intent, followed by explanation of the contents of the operations and main- tenance manual prepared for the system. Training should also in- clude · Hands-on practice by facilities staff with each of the necessary service/maintenance operations and control systems adjustments · Basic trouble-shooting procedures for the system · Operation of the monitoring features of the environmental man- agement system and early identification of performance issues Complete documentation of the environmental management from inception through start-up is a product of the commissioning process and is provided to the facility owner. The system documen- tation should include the OPR, design intent of the environmental control system, design documents, performance specifications, technical submittals, inspection reports, calibration records, testing and balancing reports, a detailed sequence of operation, start-up and shut-down procedures, a maintenance schedule for each of the sys- tem 's components, and simple diagnostic and/or troubleshooting procedures. Inc. ASHRAE, 2019 user. single for Licensed | {}
630492b5-700f-4db8-87d4-8480093cbf2d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Museums, Galleries, Archives, and Libraries 24.43 13. OPTIMIZATION (This section is based, with permission, on Maekawa et al. [2015].) Operation of any environmental management system requires a program of preventive maintenance, ongoing performance monitor- ing, and periodic performance assessment and evaluation for overall effectiveness in collections conservation and in energy use. If changes in operational parameters, collections conditions, or energy efficiency are noted, the current system 's performance should be revisited as per the steps described in the Context and Predesign section, including · Define realistic and achievable objectives and criteria; resolve competing objectives · Identify possible environmental management strategies · Evaluate and select the preferred strategy or strategies REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. Adelstein, P.Z. 2009. IPI media storage quick reference, 2nd ed. Image Permanence Institute, Rochester. www.imagepermanenceinsitute.org/ webfm_send/301. Adelstein, P.Z., J.L. Bigourdan, and J.M. Reilly. 1997. Moisture relation- ships ofphotographic film. Journal ofthe American Institute for Conser- vation 36(3):193-206. AIC. 2018. Definitions of conservation terminology. American Institute for Conservation of Historic and Artistic Works, Washington, D.C. www. comeevation-us.org/about-comervation/onifitions# W2BoptIzY2w. Anaf, W., L. Bencs, R. Van Grieken, K. Janssens, and K. DeWael. 2015. Indoor particulate matter in four Belgian heritage sites: Case studies on the deposition of dark-colored and hygroscopic particles. Science of the Total Environment 506:361-368. ASHRAE. 2017. Method of testing general ventilation air-cleaning devices for removal efficiency by particle size. Standard 52.2-2017 ASHRAE. 2017. Thermal environmental conditions for human occupancy. Standard 55-2017. ASHRAE. 2016. Ventilation for acceptable indoor air quality. ANSI/ ASHRAE Standard 62. 1-2016. ASHRAE. 2013. Climatic data for building design standards. ANSI/ ASHRAE Standard 169-2013. ASHRAE. 2018. Energy guideline for historic buildings. Guideline 34-2018. Ayerst, G. 1968. Prevention of biodeterioration by control environmental conditions. In Biodeterioration of Materials, pp. 223-241. A.H. Walters and J.J. Elphick, eds. Elsevier, Amsterdam. Ayres, J.M., H. Lau, and J.C. Haiad. 1990. Energy impact of various inside air temperatures and humidities in a museum when located in five U.S. cities. ASHRAE Transactions 96(2):100-111. Barrette, B. 1985. The Egyptian galleries at the Metropolitan Museum of Art. Museum International 37(2):81-84. Bartl, B., L. Maskova, H. Paulusova, J. Smolik, L. Bartlova, and P. Vodicka. 2015. The effect of dust particles on cellulose degradation. Studies in Conservation 61(4):203-208. Batterham, I., and J. Wignell. 2008. The mitigating effects of packaging on temperature and humidity fluctuations. AICCM Book, Paper and Photo- graphic Materials Symposium. Australian Institute for the Conservation of Cultural Material, Moonah. Bellan, L.M., L.G. Salmon, and G.R. Cass. 2000. A study on the human abil- ity to detect soot deposition onto works of art. Environmental Science & Technology 34(10):1946-1952. Beuchat, L.R. 1987. Influence of water activity on sporulation, germination, outgrowth, and toxin production. In Water activity: Theory and applica- tions to food, pp. 137-152. L.B. Beuchat, and L.R. Rockland, eds. Marcel Dekker, New York. Bigourdan, J. 2012. Understanding temperature and moisture equilibration: A path towards sustainable preservation strategies. Presentation at IAQ 2012, London, UK. www.imagerpermanceineinsitte.mg/weiofofn_send /605. Bizot Group. 2015. Bizot green protocol. In Environmental sustainability: Reducing museums carbon footprint. London: National Museum Di- rectors , Council, London. www.nationalmuseums.org.uk/what-we-do (contributing-sector'environmental-conditions/) Bonacina, C., P. Baggio, F. Cappelletti, P. Romagnoni, and A.G. Stevan. 2015. The Scrovegni chapel: The results of over 20 years of indoor cli- mate monitoring. Energy and Buildings 95:144-152. Bratasz, L., and M.R. Vaziri Sereshk. 2018. Crack saturation as a mechanism of acclimatization of panel paintings to unstable environments. Studies in Conservation 63(sup. 1):22-27. dx.doi.org/10.1080/00393630.2018 1504433. Bratasz, L., M. Lukomski, A. Klisinska-Kopacz, W. Zawadzki, K. Dzier- zega, M. Bartosik, J. Sobczyk, F.J. Lennard, and R. Kozlowski. 2015. Risk of climate-induced damage in historic textiles. Strain 51(1):78-88. Brimblecombe, P., and P. Lankester. 2013. Long-term changes in climate and insect damage in historic houses. Studies in Conservation 58:13-22. BSI. 2010. Conservation of cultural property- Procedures and instruments for measuring temperatures of the air and the surfaces of objects. BSI EN Standard 15758:2010. British Standards Institution, London. BSI. 2012. Specification for managing environmental conditions for cultural collections. PAS Standard 198:2012. British Standards Institution, Lon- don. CAGI. 2012. Standard air defined as in ISO standards. Compressed Air and Gas Institute, Cleveland. www.cagi.org/education/glosary aspat/char_s. Calver, A., A. Holbrook, D. Thickett, and S. Weintraub. 2005. Simple meth- ods to measure air exchange rates and detect leaks in display and storage enclosures. 14th Triennial Meeting, ICOM Committee for Conservation, The Hague, pp. 597-609. I. Verger, ed. James & James, London. Cass, G.R., J.R. Druzik, D. Grosjean, W. W. Nazaroff, P.M. Whitemore, and C.L. Wittman. 1989. Protection of works of art from atmospheric ozone. Research in Conservation Series 5. Getty Conservation Institute, Los Angeles. www.gotty.ai.vionervation/pibtuaims_res/pot_ publications/protection_amospheric_osme.html Cassar, M. 1995. Cost/benefits appraisals for collection care: A practical guide. Museum and Galleries Commission, London. www.ucl.ac.uk/ sustainableheritage-save/cost_ benefits.pdf. CCI. 2018. Agents ofdeterioration. Canadian Conservation Institute, Ottawa. www.umak.comencomenvin-intervier.com/dedation .html. Child, R.E. 2007. Insect damage as a function of climate. In Museum micro- climates. T. Padfield and K. Borchersen, eds. National Museum of Den- mark, Copenhagen. Conrad, E. 1994. Balancing environmental needs of the building, the collec- tion, and the user. In Preventive Conservation Practice, Theory and Research: Preprints ofthe Contributions to the Ottawa Congress, A. Roy and P. Smith, eds. International Institute for Conservation ofHistoric and Artistic Works (IIC), London. Coughlin, M. 2011. Monitoring acidic off-gassing of plastics. Conserve 0 Gram no. 8/5. National Park Service, Washington, D.C. www .nps.gov /museum/pubficaions/conserserveogran/08-05.pdf Coughlin, M., and A.M. Seeger. 2008. You collected what?! The risks and rewards of acquiring cellulose nitrate. Plastics-Looking at the future and learningfrom the past: Papers from the conference held at the Vic- toria and Albert Museum, pp. 119-124. B. Keneghan and L. Betts, eds. Archetype, London. Crank, J. 1979. The mathematics of diffusion. Oxford University Press, Oxford. Daly Hartin, D., S. Michalski, E. Hagan, and M. Choquette. 2018. Overview of the CCI lining project: Do linings prevent cracking and cupping in paintings? Paintings Group Postprints 28, 2015. American Institute for Conservation, Washington, D.C. 137-150. Derluyn, H., H. Janssen, J. Diepens, D. Derome, and J. Carmeliet. 2007. Hygroscopic behavior of paper and books. Journal of Building Physics 31(1):9-35. Di Pietro, G., and F.J. Ligterink. 1999. Prediction of the relative humidity response of backboard-protected canvas paintings. Studies in Conserva- tion 44(4):269-277. Inc. ASHRAE, 2019 user. single for Licensed | {}
56fbef56-6a84-41ac-81f2-6d49fd41b6bd | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 24.44 Dupont, A.-L, C. Egasse, A. Morin, and F. Vasseur. 2007. Comprehensive characterisation of cellulose and lignocellulose degradation products in aged papers: Capillary zone electrophoresis of low-molar mass organic acids, carbohydrates, and aromatic lignin derivatives. Carbohydrate Poly- mers 68(1):1-16. Ekelund, S., P. Van Duin, A. Jorissen, B. Ankersmit, and R.M. Groves. 2018. A method for studying climate-related changes in the condition of deco- rated wooden panels. Studies in Conservation 63(2):62-71. Erhardt, D., and M. Mecklenburg. 1994. Relative humidity re-examined. Pre- ventive Conservation Practice, Theory and Research: Preprints of the Contributions to the Ottawa Congress, pp. 32-38. International Institute for Conservation of Historic and Artistic Works, London. Erlebacher, J.D., E. Brown, M.F. Mecklenburg, and C.S. Tumosa. 1992. The effects of temperature and relative humidity on the mechanical properties of modern painting materials. In MRS Proceedings, vol. 267. Fenech, A. M. Strlic, I. Degano, and M. Cassar. 2010. Stability of chromo- genic colour prints in polluted indoor environments. Polymer Degrada- tion Stability 95:2481-2485. Graedel, T.E. 1984. Concentrations and metal interactions of atmospheric trace gases involved in corrosion. Proceedings of Metallic Corrosion, Toronto, pp. 396-401. Grau-Bove, J., and M. Strlic. 2013. Fine particulate matter in indoor cultural heritage: A literature review. Heritage Science 1:8. dx.doi.org/10.1 186 /2050-7445-1-8. Groom, P., and T. Panisset. 1933. Studies in Penicillium chrysogenum thom in relation to temperature and relative humidity of the air. Annals of Applied Biology 20:633-660. Grzywacz, C.M. 2006. Monitoring for gaseous pollutants in museum envi- ronments. In Tools in Conservation, E. Maggio, ed. Getty Conservation Institute, Los Angeles. Gurnagul, N., and X. Zou. 1994. The effect of atmospheric pollutants on paper permanence: A literature review. Tappi Journal 77:199-204. Hackney, S. 1990. Framing for conservation at the Tate Gallery. The Con- servator 14(1):44-52. Hagan, E. W. S. 2017. Thermo-mechanical properties of white oil and acrylic artist paints. Progress in Organic Coatings 104:28-33. Halsberghe, L., L.T. Gibson, and D. Erhardt. 2005. A collection of ceramics damaged by acetate salts: conservation and investigation into the causes. 14th Triennial Meeting, ICOM Committeefor Conservation, The Hague, pp. 131-138. I. Verger, ed. James & James, London. Harriman, L.G. 2009. The ASHRAE guidefor buildings in hot and humid cli- mates. ASHRAE. Hatchfield, P.B. 2002. Pollutants in the museum environment: Practical strategies for problem solving in design, exhibition, and storage. Arche- type Publications, London. Hens, H.L.S.C. 1993. Mold risk: Guidelines and practice, commenting the results of the International Energy Agency EXCO on energy conserva- tion in buildings and community systems, Annex 14: Condensation en- ergy. In Bugs, Mold and Rot III: Moisture Specifications and Control in Buildings, pp. 19-28. W. Rose and A. Tenwolde, eds. National Institute of Building Sciences, Washington, D.C. Howie, F.M. 1992. Pyrite and marcasite. In The care and conservation of geological material: Minerals, rocks, meteorites, and lunarfinds, pp. 70- 84. Butterworth-Heinemann, London. IAQ. 2016. Concentration converter. IAQ in Museums and Archives, Den- mark. iaq.dk/papers/conc_calc.htm. IIC/ICOM-CC. 2014. Environmental guidelines-IIC and ICOM-CC dec- laration. International Institute for Conservation of Historic and Artis- tic Works, and ICOM-CC International Council of Museums Committee for Conservation. www.iiconservation.org/sites/default/ fileshow.krajimate1588-004_Bellandeo_portdonntal_ guidelines.pdf. IPI. 2018. Preservation metrics. Image Permanence Institute, Rochester, NY. www.imagepementencehainter.com/entionmenteenahl preservation-metrics. ISO. 2010. Imaging materials Processed safety photographic films Stor- age practices. ISO Standard 18911:2010. International Organization for Standardization, Geneva. ISO. 2011. Imaging materials- -Reflection prints- Storage practices. ISO Standard 18920:2011. International Organization for Standardization, Geneva. 2019 ASHRAE Handbook-HVAC Applications (SI) ISO. 2000. Imaging materials- Polyester-base magnetic tape Storage practices. ISO Standard 18923:2000. International Organization for Stan- dardization, Geneva. ISO. 2011. Imaging materials-Multiple media archives- Storage environ- ment. ISO Standard 18934:2011. International Organization for Stan- dardization, Geneva. Jakiela, S., L. Bratasz, and R. Kozlowski. 2008. Numerical modelling of moisture movement and related stress field in lime wood subjected to changing climate conditions. Wood Science and Technology 42(1):21- 37. Karpowicz, A. 1989. In-plane deformations of films of size on paintings in the glass transition region. Studies in Conservation 34(2):67-74. Kerschner, R.L. 1992. A practical approach to environmental requirements for collections in historic buildings. Journal of the American Institute for Conservation 31:65-76. Kerschner, R.L. 2006. Providing safe and practical environments for cultural properties in historic buildings. and beyond. Presented at 20th Annual Preservation Conference: Beyond the Numbers: Specifying and Achiev- ing an Efficient Preservation Environment. National Archives, Washing- ton, D.C. www.anhivs.govipasenationionsionce.Cokinessative .html. Koob, S.P. 2006. Conservation and care of glass objects. Archetype, Lon- don. Krupinska, B., R. Van Grieken, and K. De Wael. 2013. Air quality monitor- ing in a museum for preventive conservation: Results of a three-year study in the Plantin-Moretus Museum in Antwerp, Belgium. Microchem- ical Journal 110:350-360. Krzemien, L., M. Lukomski, L. Bratasz, R. Kozlowski, and M.F. Mecklen- burg. 2016. Mechanism of craquelure pattern formation on panel paint- ings. Studies in Conservation 61(6):324-330. Kupczak, A. A. Sadlowska-Salegab, L. Krzemiena, J. Sobczyk, J. Radon, and R. Kozlowski. 2018a. Impact of paper and wooden collections on humidity stability and energy consumption in museums and libraries. Energy and Buildings 158:77-85. Kupczak, A., L. Bratasz, J. Krysciak-Czerwenka, and R. Kozlowski. 2018b. Moisture sorption and diffusion in historical cellulose-based materials. Cellulose 1-12. LaFontaine, R.H. 1979. Environmental norms for Canadian museums, art galleries, and archives. CCI Technical Bulletin 5, Canadian Conservation Institute, Ottawa. LaFontaine, R.H. 1982. Hurmidistically-controlled heating: A new approach to relative humidity control in museum closed for the winter season. Journal of the International Institutefor Conservation: Canadian Group 7(1,2):35-41. LaFontaine, R.H., and S. Michalski. 1984. The control of relative humid- ity- Recent developments. ICOM Conservation 7th Triennial Meeting, Copenhagen, pp. 33-37. Lafontaine, R.H. and P.A. Wood. 1982. The stabilization ofivory against rel- ative humidity fluctuations. Studies in Conservation 27(3), 109-17. Lasyk, L., M. Lukomski, T.M. Olstad, and A. Haugen. 2012. Digital speckle pattern interferometry for the condition surveys of painted wood: Moni- toring the altarpiece in the church in Hedalen, Norway. Journal of Cul- tural Heritage 13(3, Supplement):S102-108. Lloyd, H., C. Bendix, P. Brimblecombe, and D. Thickett. 2007. Dust in his- toric libraries. Museum Microclimates, pp. 135-144. T. Padfield and K. Borchersen, eds. The National Museum of Denmark, Copenhagen Luciani, A. 2013. Historical climates and conservation environments. His- torical perspectives on climate control strategies within museums and heritage buildings. Ph.D. dissertation. Milan, Politecnico di Milano. www.politesi.polimi.ithandle/10589/74423. Madsen, B. 1975. Duration of load tests for wood in tension perpendicular to the grain. Forest Products Journal 25(8):48-53. Maekawa, S. 1998. Oxygen-free museum cases. Research in Conservation. Getty Conservation Institute, Los Angeles. Maekawa, S., and F. Toledo. 2001. Sustainable climate control for historic buildings in hot and humid regions. Renewable Energyfor a Sustainable Development ofthe Built Environment: Proceedings of the 18th Interna- tional Conference on Passive and Low Energy Architecture, F.O.R. Pereira, R. R�ther, R. V.G. Souza, S. Afonso, and J.A.B. da Cunha Neto, eds. Maekawa, S., V. Beltran, and M. Henry. 2015. Environmental management for collections: Alternative preservation strategiesfor hot and humid cli- mates. Getty Publications, Los Angeles. Inc. ASHRAE, 2019 user. single for Licensed | {}
2d497a71-411b-4d76-a177-9563b3f0c027 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Museums, Galleries, Archives, and Libraries 24.45 Marcon, P.J. 1987. Controlling the environment within a new storage and display facility for the governor general's carriage. Journal of the Inter- national Institute for Conservation: Canadian Group 12:37-42. Mathey, R.G., T.K. Faison, S. Silberstein, J.E. Woods, W.B. Johnson, W.P. Lull, C.A. Madson, A. Turk, K.L. Westlin, and P.N. Banks. 1983. Air quality criteria for storage of paper-based archival records. NBSIR Tech- nical Report 83-2795. U.S. Department of Commerce National Bureau of Standards, Washington, D.C. McCormick-Goodhart, M.H. 2003. On the cold storage of photographic materials in a conventional freezer using the critical moisture indicator (CMI) packaging method. www.wilhelm-cesearch.com/subzero/CMI - Paper_2003_07_31.pdf. Mecklenburg, M.F. 1991. Some mechanical and physical properties of gild- ing gesso. In Gilded wood: Conservation and history, pp. 163-170. D. Bigelow, E. Come, G. J. Landrey, and C. van Horne, eds. Sound View Press, Madison, WI. Mecklenburg, M.F., and C.S. Tumosa. 1991. An introduction into the mechanical behavior of paintings under rapid loading conditions. In Art in transit: Studies in the transport ofpaintings, pp. 137-172. National Gallery of Art, Washington, D.C. Mecklenburg, M.F., and C.S. Tumosa. 2005. The structure of canvas sup- ported paintings. In Preprints ofthe international conference on painting conservation, canvases: Behavior, deterioration and treatment, pp. 119- 155. M. Castell Agusti and M.Y. Otros, eds. Editorial Universidad Politecnica de Valencia, Valencia, Spain. Mecklenburg, M.F., C.S. Tumosa, and D. Erhardt. 1998. Structural response of painted wood surfaces to changes in ambient relative humidity. In Painted wood: History and conservation. The Getty Conservation Insti- tute, Los Angeles. Michalski, S. 1991. Paintings, their response to temperature, relative humid- ity, shock and vibration. In Works of Art in Transit, pp. 223-248. M.F. Mecklenburg, ed. National Gallery, Washington, D.C. Michalski, S. 1993. Relative humidity: a discussion of correct/incorrect values. In ICOM Committee for Conservation 10th Triennial Meeting Preprints, pp. 624-629. J. Bridgland, ed. International Council of Muse- ums Committee for Conservation, Paris. Michalski, S. 1994. Leakage prediction for buildings, cases, bags and bot- tles. Studies in Conservation 39(3):169-186. Michalski, S. 2000. Guidelines for humidity and temperature for Canadian archives. CCI Technical Bulletin 23. Canadian Conservation Institute, Ottawa. Michalski, S. 2002. Double the life for each five-degree drop, more than double the life for each halving ofrelative humidity. In ICOM Committee for Conservation 13th Triennial Meeting, Rio de Janeiro, Preprints, pp. 66-72. James & James, London. Michalski, S. 2005. Risk analysis of backing boards for paintings: damp cli- mates vs cold climates. In Minimo intervento conservativo nel restauro dei dipinti, pp. 21-27. II Prato, Saonara Italy. Michalski, S. 2014. The power of history in the analysis of collection risks from climate fluctuations and light. In ICOM Committee for Conserva- tion 17th Triennial Meeting, Melbourne, 15-19 September 2014 Pre- prints, pp. 1-8. J. Bridgland, ed. International Council of Museums- Committee for Conservation, Paris. Michalski, S. 2016. Climate guidelines for heritage collections: Where we are in 2014 and how we got here. In Summit on the Museum Preservation Environment, pp. 7-32. Smithsonian Institution Scholarly Press, Wash- ington, D.C. Michalski, S. 2018. Agent of deterioration: Incorrect temperature. Ottawa. Canadian Conservation Institute. www.canada.ca/en/conservation -inabite/erviceslagent-deviotionion Deranperatiol Mleczkowska, A., M. Strojecki, L. Bratasz, and R. Kozlowski. 2016. Parti- cle penetration and deposition in historic churches. Buildings and Envi- ronment 95:291-298. Mleczkowska, A., M. Strojecki, L. Bratasz, and R. Kozlowski. 2017. The effect of ventilation on soiling by particles of outdoor and indoor origin in historical churches, Building Simulation 10(3):383-393. NARA. 2002. Archival storage standards. NARA Directive 1571. National Archives and Records Administration, Washington, D.C. www.archives gov/files/fria/directives/nara1571.pdf. NARA. 2013. National Archives extends life expectancy ⌀fits textual records at its College Park facility AND saves energy at the same time. National Archives/Environmental Monitoring. National Archives and Records Administration, Washington, D.C. www.archives.gov/preservation/ carion-andecomi/imporchavionmation-mogy-andspiti Nazaroff, W. W., M.P. Ligocki, L.G. Salmon, G.R. Cass, T. Fall, M.C. Jones, H.I.H. Liu, and T. Ma. 1993. Airborne particles in museums. Research in Conservation vol. 6. Getty Conservation Institute, Marina del Rey. www getty.com/pukications/vimuallbmry/0392361875.hml NFPA. 2019. Standard for the storage and handling of cellulose nitrate film. NFPA Standard 40-2019. National Fire Protection Association, Quincy. Nishimura, D.W. 1996. The practical presentation of research studies on film stability. In Research Techniques in Photographic Conservation: Proceedings of the Conference in Copenhagen, pp. 85-92. The Royal Danish Academy of Fine Arts, Copenhagen. Nishimura, D.W. 2015. Strategies for the storage of cellulose acetate film. AIC News 40:1-5. NMDC. 2008. Guiding principles for reducing museums carbon footprint. National Museum Directors' Council, London. www.nationalmuseums .org.uk/media/documents/what_ we_do_documents/guiding_principles _reducing_ carbon_footprint.pdf. NOAA. 1997. Engineering weather data. National Oceanic and Atmo- spheric Administration, Washington, D.C. NRC. 1986. Preservation ofhistorical records. National Research Council. National Academy Press, Washington, DC. Ohtsuki, T. 1990. Studies on Eurotium tonophilum Ohtsuki: Minimum humidity for germination and characterization of yellow pigments pro- duced by this fungus. Scientific Papers on Japanese Antiquities and Art Crafts 35:28-34. Oreszczyn, T., M. Cassar, and K. Fernandez. 1994. Comparative study of air-conditioned and non air-conditioned museums. Studies in Conserva- tion 39(sup. 2):144-148. Padfield, T. 2002. Condensation in film containers during cooling and warming. In Preserve then show, pp. 67-77. D. Nissen, ed. The Danish Film Institute, Copenhagen. www.conservationphysics.org/coolfilm /coolingfilm.pdf. Padfield, T., and P. Jensen. 1996. Low energy climate control in stores: A postscript. ICOM Conservation Committee, 9th Triennial Meeting, Dres- den, pp. 596-601. Paterakis, A.B. 2016. Volatile organic compounds and the conservation of inorganic materials, Archetype Publications, London. Pinniger, D.B. 2001. Pest management in museums, archives and historic houses. Archetype Publications, London. Pretzel, B. 2003. Materials and their interaction with museum objects. Con- servation Journal 44. www. vam.ac.uk/content/journals/conservation -jomai/Seas4/mandiesmanchandecantramenthemn/i Raychaudhuri, M.R., and P. Brimblecombe. 2000. Formaldehyde oxidation and lead corrosion. Studies in Conservation 45(4):226-232. Reilly, J.M. 1993. IPI storage guide for acetate film: Instructions for using the wheel, graphs, and table: Basic strategyforfilm preservation. Roch- ester Institute ofTechnology. Image Permanence Institute, Rochester. Reilly, J.M. 1995. New tools for preservation: Assessing long-term environ- mental effects on library and archives collections. Commission on Pres- ervation and Access, Washington, D.C. Reilly, J.M. 1998. Storage guide for color photographic materials: Caring for color slides, prints, negatives, and movie films. The University of the State of New York, Albany. www.imagepermanenceinstitute.org /webfm_send/517. Richard, M. 2007. The benefits and disadvantages of adding silica gel to microclimate packages for panel paintings. In Museum Microclimates Conference, pp. 237-243. National Museum of Denmark, Copenhagen. Richard, M., M.F. Mecklenburg, and R.M. Merrill. 1991. Art in transit: hand- book for packing and transporting paintings. National Gallery of Art, Washington, D.C. Robinet, L. 2006. The role of organic pollutants in the alteration of his- toric soda silicate glasses. Ph.D. dissertation. Edinburgh University. tel .archives-ouvertes.fr/tel-00088408. Robinet, L., and D. Thickett. 2003. A new methodology for accelerated cor- rosion testing. Studies in Conservation 48(4):263-268. Sebor, A.J. 1995. Heating, ventilating, and air-conditioning systems. In Storage of natural history collections: Ideas and practical solutions. C.L. Rose, C.A. Hawks, and H.H. Genoways, eds. Society for the Pres- ervation of Natural History Collections, Washington, D.C. Inc. ASHRAE, 2019 user. single for Licensed | {}
213871a1-589f-4b74-8c5f-ac9043503d5c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 24.46 2019 ASHRAE Handbook-HVAC Applications (SI) Sedlbauer. K. 2001. Prediction ofmouldfungusformation on the surface of and inside building components. Ph.D. dissertation. Fraunhofer Insti- tute for Building Physics, Munich, Germany. www.ibp.fraunhofer.de (coment/anditylembounchaviflianoran Deartat dissertation_etcm45-30729.pdf. Shashoua, Y. 2004. Modern plastics: Do they suffer from the cold? Studies in Conservation, 49(sup. 2):91-95. Shashoua, Y. 2005. Storing plastics in the cold: More harm than good? In ICOM Committeefor Conservation 14th Triennial meeting, pp. 358-364. James & James, London. Shashoua, Y. 2008. Conservation of plastics: Materials science, degrada- tion and preservation. Butterworth-Heinemann Elsevier, Oxford. Shashoua, Y. 2014. A safe place: Storage strategies for plastics. Con- servation Perspectives (Spring):13-15. www.getty. edu/conservation /publications_resources/newsletters/29] _1/storage.html. Shiner, J. 2007. Trends in microclimate control of museum display cases. In Museum Microclimates Conference, pp. 19-23. T. Padfield and K. Borch- ersen, eds. National Museum of Denmark, Copenhagen. Siau, J.F. 2012. Transport processes in wood. Springer Science & Business Media, Berlin. Snow, D., M.H.G. Crichton, and N.C. Wright. 1944. Mould deterioration of feeding stuff in relation to humidity of storage. Annals of Applied Biol- ogy 31:102-110. Stilwell, S.T.O., and R.A.G. Knight. 1934. Appendix I. Investigation into the effect of humidity variations on old panel paintings on wood. In Some notes on atmospheric humidity in relation to works of art, pp. 17-33. Courtauld Institute of Art, London. Stolow, N. 1966. Controlled environment for works of art in transit. Butter- worths, London. Strang, T. 2012. Studies in pest control for cultural properties. Ph.D. dis- sertation. University of Goteborg, Sweden. gupea.ub.gu.se/bitstream /2077/31500/7/gupea_2077 _31500_ 7.pdf. Strlic, M., C. M. Grossi, C. Dillon, N. Bell, K. Fouseki, P. Brimblecombe, E. Menart, K. Ntanos, W. Lindsay, D. Thickett, F. France, and G. D. Bruin. 2015. Damage function for historic paper. Part III: Isochrones and demography of collections. Heritage Science 3(1):1-11. Strojecki, M., M. Lukomski, L. Krzemien, J. Sobczyk, and L. Bratasz. 2014. Acoustic emission monitoring of an eighteenth-century wardrobe to sup- port a strategy for indoor climate management. Studies in Conservation 59(4):225-232. Tantideeravit, S., M.N. Charalambides, D.S. Balint, and C.R.T. Young. 2013. Prediction of delamination in multilayer artist paints under low amplitude fatigue loading. Engineering Fracture Mechanics 112-113: 41-57. Taylor, J. Forthcoming. Technical note: Considerations for the process of managing collection environments. Getty Conservation Institute, CA. Tetreault, J. 1992. La mesure de l'acidite des produits volatils. Journal ofthe International Institute for Conservation- Canadian Group 17:7-25. English translation available at www .researchgate.net/publication /281296057 _Measuring_ the_acidity_ of_ volatile_products. Tetreault, J. 2003. Airborne pollutants in museums, galleries and archives: Risk assessment, control strategies andpreservation management. Cana- dian Conservation Institute, Ottawa. Tetreault, J. 2011. Sustainable use of coatings in museums and archives Some critical observations. e-Preservation Science 8:39-48. www.morana -rtd.com/e-preservationscience/2011/T etreault-05-01-201 1 .pdf. Tetreault, J. 2017. Products used in preventive conservation. Technical Bul- letin 32. Canadian Conservation Institute, Ottawa. www.canada.ca/ eniomar-minaviatudevice-cestonsing-posserain-puf- cationas/imical-holadis/polucee/recent/contra-co- tion.html Tetreault, J. 2018. Agent of deterioration: Pollutants. Canadian Conserva- tion Institute, Ottawa. www.camada.ca/er/conservation-instituservices /agents-deterioration/pollutants.html. Tetreault, J., and P. Begin. 2018. Silica gel: Passive control of relative hu- midity. Technical Bulletin 33. Canadian Conservation Institute, Ottawa. comatuatofoservioolinsinewevizensionsitograin -podicatumelechnical Remicallosgrveaingehumedingllp Tetreault, J., J. Sirois, and E. Stamatopoulou. 1998. Study oflead corrosion in acetic acid environment, Studies in Conservation 43:17-32. Tetreault, J., A.-L. Dupont, P. Begin, and S. Paris. 2013. The impact of vol- atile compounds released by paper on cellulose degradation in ambient hygrothermal conditions. Polymer Degradation and Stability 98:1827- 1837. Thickett, D. 1997. Relative effect of formaldehyde, formic and acetic acids on lead, copper and silver. Report 1997/12. British Museum, London. Thickett, D., P. Fletcher, A. Calver, and S. Lambarth. 2007. The effect of air tightness on RH buffering and control. In Museum Microclimates Con- ference, pp. 245-251. T. Padfield and K. Borchersen, eds. National Museum of Denmark, Copenhagen. Thickett, D., R. Chisholm, and P. Lankester. 2013. Reactivity monitoring of atmospheres. Metal 2013: Proceedings of the International Conference on Metals Conservation, pp. 129-135. E. Hyslop, V. Gonzalez, L. Troalen, and L. Wilson, eds. Lulu Enterprises, Inc., Edinburgh. Thomson, G. 1964. Relative humidity- Variation with temperature in a case containing wood. Studies in Conservation 9(4):153-169. Thomson, G. 1986. The museum environment, 2nd ed. London, Elsevier. Toishi, K. 1959. Humidity control in a closed package. Studies in Conser- vation 4(3):81-87. UNESCO. 2017a. Tangible cultural heritage. United Nations Educational, Scientific and Cultural Organization, Cairo. www.unesco.org/new/en /cairo/culture/tangible-cultural-heritage/. UNESCO. 2017b. Communication and information. United Nations Educa- tional, Scientific and Cultural Organization, Paris. www.unesco.org/new beformentaibankamentomationacesen-Mixingravedo -14commentry-hotoginglikeringscoupp-o-p-denidep/ UNESCO. 2018. World heritage. United Nations Educational, Scientific and Cultural Organization, Paris. whc.unesco.org/en/about/. UNI. 2002. 2002 cultural heritage- General principles for the choice and the control ofthe climate to preserve cultural heritage in indoor environ- ments. UNI Standard 10969:2002. Italian Standards, Milan. van Giffen, N.A.R., S.P. Koob, J.J. Kunicki-Goldfinger, and R.H. Brill. 2018. Caring for glass collections: the importance of maintaining envi- ronmental controls. Studies in Conservation 63(sup. 1). Volent, P., and N.S. Baer. 1985. Volatile amines used as corrosion inhibitors in museum humidification systems. International Journal of Museum Management and Curatorship 4:359-364. Waller, R. 1992. Temperature and humidity-sensitive mineralogical and petrological specimens. In The care and conservation ofgeological mate- rial: Minerals, rocks, meteorites, and lunarfinds, pp. 25-50. F. Howie, ed. Butterworth-Heinemann Publishers, Boston. Whitmore P.M., and G.R. Cass. 1989. The fading of artists' colorants by exposure to atmospheric nitrogen dioxide. Studies in Conservation 34(2): 85-97 Williams, E.L., E. Grosjean, and D. Grosjean. 1993. Exposure of artists' col- orants to sulfur dioxide. Journal of the American Institute for Conserva- tion 32(3):291-310. Zou, X., T. Uesaka, and N. Gurnagul. 1996. Prediction of paper permanence by accelerated aging I: Kinetic analysis of the aging process. Cellulose 3(1):243-267. BIBLIOGRAPHY AIC. 2013. Environmental guidelines: Museum climate in a changing world. American Institute for Conservation of Historic & Artistic Works, Washington, D.C. www.conservation-wiki. com/wiki/Environmental Guidelines. Michalski, S. 2018a. Agent ofdeterioration: Incorrect relative humidity. Ca- nadian Conservation Institute, Ottawa. www.canada. ca/en/conservation -inationtervicessiggents-Jectionation humility. Padfield, T., M. Ryhl-Svendsen, P.K Larsen, and L.A. Jensen. 2018. A review of the physics and the building science which underpins methods of low energy storage of museum and archive collections. Studies in Conserva- tion 63(sup. 1):209-215. dx.doi.org/10.1080009999630.2018.1504456. Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
2515a6ff-deb5-4478-bd69-c57eb6da23f4 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 25 ENVIRONMENTAL CONTROL FOR ANIMALS AND PLANTS ¦ DESIGN FOR ANIMAL ENVIRONMENTS ¦ 25.1 ¦ DESIGN FOR PLANT FACILITIES ¦ 25.10 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Cooling and Heating ¦ 25.4 ¦ Greenhouses ¦ 25.10 ¦ ¦ Ventilation ¦ 4+ 25.5 ¦ Plant Growth Environmental ¦ ¦ ¦ Ventilation Management ¦ 25.5 ¦ Facilities ¦ 25.16 ¦ ¦ Recommended Practices by Species ¦ 25.7 ¦ Other Plant Environmental Facilities ¦ 25.21 ¦ T HE design of plant and animal housing is complicated because many environmental factors affect the production and well- being ofliving organisms. Designers should consider that equipment must repay costs through improved economic productivity. Engi- neers, likewise, must balance costs of modifying the environment against potential economic losses incurred through plants or animals kept in a less than ideal environment. Thus, design of plant and animal housing is affect by financial considerations, in addition to concern for the well-being of workers and animals, and regulations on pollution, sanitation, and health assurance. 1. DESIGN FOR ANIMAL ENVIRONMENTS Typical animal production plants modify the environment, to some degree, by housing or sheltering animals year-round or for parts of a year. The degree of modification is generally based on the expected increase in production. Animal sensible heat and moisture production data, combined with information on the effects of envi- ronment on growth, productivity, and reproduction, help designers select optimal equipment. Detailed information is available in a series of handbooks published by the MidWest Plan Service. These include Mechanical Ventilating Systems for Livestock Housing (MWPS 1990a), Natural Ventilating Systems for Livestock Housing and Heating (MWPS 1989), and Cooling and Tempering Air for Livestock Housing (MWPS 1990b). ASAE Monograph 6, Ventila- tion of Agricultural Structures (Hellickson and Walter 1983), also gives more detailed information. Design Approach Environmental control systems are typically designed to maintain thermal and air quality conditions within an acceptable range and as near the ideal show as is practicable. Equipment is usually sized as- suming steady-state energy and mass conservation equations. Ex- perimental measurements that heat and moisture production by animals is not constant and that there may be important thermal capacitance effects in livestock buildings. Nevertheless, for most design situations, the steady-state equations are acceptable. Achieving the appropriate fresh air exchange rate and establish- ing the proper distribution within the room are generally the two most important design considerations. The optimal ventilation rate is selected according to the ventilation rate logic curve (Figure 1). During the coldest weather, the ideal ventilation rate is that required to maintain indoor relative humidity at or below the maximum desired, and air contaminant concentrations within The preparation of this chapter is assigned to TC 2.2, Plant and Animal Environment. RATE VENTILATION ![image](/image/placeholder) Maximum practical ventilation rate for maintaining comfort C Ventilation rate for IDEAL moisture removal VENTILATION RATE B A Ventilation rate to maintain indoor air quality Ventilation rate to maintain inside design temperature AMBIENT TEMPERATURE Fig. 1 Logic for Selecting Appropriate Ventilation Rate in Livestock Buildings (Adapted from Christianson and Fehr 1983) acceptable ranges (Rates A and B in Figure 1). Supplemental heating is often required to prevent the temperature from drop- ping below optimal levels. In milder weather, the ventilation rate required for maintaining optimal room air temperature is greater than that required for mois- ture and air quality control (Rates C and D in Figure 1). In hot weather, the ventilation rate is chosen to minimize the temperature rise above ambient and to provide optimal air movement over ani- mals. Cooling is sometimes used in hot weather. The maximum rate (D) is often set at 60 air changes per hour (ach) as a practical maxi- mum. Temperature Control The temperature in an animal structure is computed from the sensible heat balance of the system, usually disregarding transient effects. Nonstandard buildings with low airflow rates and/or large thermal mass may require transient analysis. Steady-state heat transfer through walls, ceiling or roof, and ground is calculated as presented in Chapters 25 to 27 of the 2017 ASHRAE Handbook- - Fundamentals. 25.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
4a685991-b728-46f3-b4c3-a8d0cb5e2fe7 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 25.2 Mature animals typically produce more heat per of unit floor area than do young stock. Chapter 10 of the 2005 ASHRAE Handbook- Fundamentals presents estimates of animal heat loads. Lighting and equipment heat loads are estimated from power ratings and operat- ing times. Typically, the designer selects indoor and outdoor design temperatures and calculates the ventilation rate to maintain the tem- perature difference. Outdoor design temperatures are given in Chap- ter 14 of the 2017 ASHRAE Handbook-Fundamentals. The section on Recommended Practices by Species in this chapter presents indoor design temperature values for various livestock. Moisture Control Moisture loads produced in an animal building may be calculated from data in Chapter 10 of the 2005 ASHRAE Handbook-Funda- mentals. The mass of water vapor produced is estimated by dividing the animal latent heat production by the latent heat of vaporization of water at animal body temperature. Spilled water and evaporation of fecal water must be included in the estimates of latent heat pro- duction within the building. The amount of water vapor removed by ventilation from a totally slatted (manure storage beneath floor) swine facility may be up to 40% less than the amount removed from a solid concrete floor. If the floor is partially slatted, the 40% max- imum reduction is decreased in proportion to the percentage of the floor that is slatted. Ventilation should remove enough moisture to prevent conden- sation but should not render the relative humidity so low (less than 40%) as to create dusty conditions. Indoor relative humidity for winter ventilation is usually designed to be between 70 and 80%. The walls should have sufficient insulation to prevent surface con- densation at 80% rh inside. During cold weather, ventilation needed for moisture control usually exceeds that needed to control temperature. Minimum ven- tilation must always be provided to remove animal moisture. Up to a full day of high humidity may be allowed during extremely cold periods when normal ventilation rates could cause an excessive heating demand. Humidity level is not normally the controlling fac- tor in mild or hot weather. Air Quality Control Contaminants. High moisture levels can also aggravate contam- inant problems. The most common air contaminants in animal buildings are particulate matter (PM) and gases. In animal build- ings, particulate matter originates mainly from feed, litter, fecal materials, and other animal substances. Particulates include solid particles (or dust), liquid droplets, and microorganisms, can be deposited deep within the respiratory system. Particulates carry allergens that cause discomfort and health problems for workers in animal housing facilities. They also carry much of the odors in ani- mal housing facilities, for potentially long distances from the facil- ities. Consequently, particulates pose major problems for animals, workers, and neighbors. Particulate levels in swine buildings have been measured to range from 1 to 15 mg/m3. Dust has not been a major problem in dairy buildings; one two-year study found an aver- age of only 0.5 mg/m3 in a naturally ventilated dairy barn. Poultry building dust levels average around 2 to 7 mg/m3, but levels up to 18 to 29 mg/m3 have been measured during high activity. The most common gas contaminants are ammonia, hydrogen sulfide, other odorous compounds, carbon dioxide, and carbon monoxide. Ammonia, which results from decomposition of manure, is the most important chronically present contaminant gas. Typical ammonia levels measured have been 7 to 37 mg/m3 in poultry units, 0 to 15 mg/m3 in cattle buildings, 4 to 22 mg/m3 in swine units with liquid manure systems, and 7 to 37 mg/m3 in swine units with solid floors (Ni et al. 1998a). Up to 150 mg/m3 have been measured in 2019 ASHRAE Handbook-HVAC Applications (SI) swine units in winter. Ammonia should be maintained below 18 mg/ m3 and, ideally, below 7 mg/m3. Maghirang et al. (1995) and Zhang et al. (1992) found ammonia levels in laboratory animal rooms to be negligible, but concentra- tions could reach 45 mg/m3 in cages. Weiss et al. (1991) found ammonia levels in rat cages of up to 260 mg/m3 with four male rats per cage and 50 mg/m3 with four female rats per cage. Hasenau et al. (1993) found that ammonia levels varied widely among various mouse microisolation cages; ammonia ranged from negligible to 380 mg/m3 nine days after cleaning the cage. Hydrogen sulfide, a by-product of microbial decomposition of stored manure, is the most important acute gas contaminant. During normal operation, hydrogen sulfide concentration is usually insig- nificant (i.e., below 1 mg/m3). A typical level ofhydrogen sulfide in swine buildings is around 200 to 500 �g/m3 (Ni et al. 1998b). How- ever, levels can reach 280 to 460 mg/m3, and possibly up to 1.4 to 11 g/m3 during in-building manure agitation. Odors from animal facilities are an increasing concern, both in the facilities and surrounding areas. Odors result from both gases and particulates; particulates are of primary concern because odor- ous gases can be quickly diluted below odor threshold concentra- tions in typical weather conditions, whereas particulates can retain odor for long periods. Methods that control particulate and odorous gas concentrations in the air also reduce odors, but controlling odor generation at the source appears to be the most promising method of odor control. Barber et al. (1993), reporting on 173 pig buildings, found that carbon dioxide concentrations were below 5400 mg/m3 in nearly all instances when the external temperature was above 0°C but almost always above 5400 mg/m3 when the temperature was below 0°C. The report indicated that there was a very high penalty in heat- ing cost in cold climates if the maximum allowed carbon dioxide concentration was less than 9000 mg/m3. Air quality control based on carbon dioxide concentrations was suggested by Donham et al. (1989). They suggested a carbon dioxide concentration of 2770 mg/m3 as a threshold level, above which symptoms of respi- ratory disorders occurred in a population of swine building work- ers. For other industries, a carbon dioxide concentration of 9000 mg/m3 is suggested as the time-weighted threshold limit value for 8 h of exposure (ACGIH 1998). Other gas contaminants can also be important. Carbon monoxide from improperly operating unvented space heaters sometimes reaches problem levels. Methane is another occasional concern. Control Methods. Three standard methods used to control air contaminant levels in animal facilities are 1. Reduce contaminant production at the sources 2. Remove contaminants from the air by air cleaning 3. Reduce contaminant concentration by dilution (ventilation) The first line of defense is to reduce release of contaminants from the source, or at least to intercept and remove them before they reach workers and animals. Animal feces and urine are the largest sources of contaminants, but feed, litter, and animal bodies are also a major source of contaminants, especially particulates. Successful opera- tions effectively collect and remove all manure from the building within three days, before it decomposes enough to produce large quantities of contaminants. Removing ventilation air uniformly from manure storage or collection areas helps remove contaminants before they reach animal or worker areas. Ammonia production can be minimized by removing wastes from the room and keeping floor surfaces or bedding dry. Immediately covering manure solids in gutters and pits with water also reduces ammonia, which is highly soluble in water. Because adverse effects of hydrogen sulfide on production begin to occur at 30 mg/m3, ven- tilation systems should be designed to maintain hydrogen sulfide levels below 30 mg/m3 during agitation. When manure is agitated Inc. ASHRAE, 2019 user. single for Licensed | {}
bbbd7851-1709-467a-9cbf-196d72d854a8 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Environmental Control for Animals and Plants 25.3 and removed from the storage, the building should be well ventilated and all animals and occupants evacuated to avoid potentially fatal concentrations of gases. For laboratory animals, changing the bedding frequently and keeping the bedding dry with lower relative humidities and appro- priate cage ventilation can reduce ammonia release. Individually ventilated laboratory animal cages or placing cages in mass air dis- placement units reduce contaminant production by keeping litter drier. Using localized contaminant work stations for dust-producing tasks such as cage changing may also help. For poultry or laboratory animals, the relative humidity of air surrounding the litter should be kept between 50 and 75% to reduce particulate and gas contaminant release. Relative humidities between 40 and 75% also reduce the vi- ability of pathogens in the air. A moisture content of25 to 30% (wet basis) in the litter or bedding keeps dust to a minimum. Adding 0.5 to 2% of edible oil or fat can significantly reduce dust emission from the feed. Respirable dust (smaller than 10 �m), which is most harm- ful to the health and comfort of personnel and animals, is primarily from feces, animal skins, and dead microorganisms. Respirable dust concentration should be kept below 0.23 mg/m3. Some dust control technologies are available. For example, sprinkling oil at 5 mL/m2 of floor area per day can reduce dust concentration by more that 80%. High animal activity levels release large quantities of particu- lates into the air, so management strategies to reduce agitation of an- imals are helpful. Methods of removing contaminants from the air are essentially limited to particulate removal, because gas removal methods are often too costly for animal facilities. Some animal workers wear per- sonal protection devices (appropriate masks) to reduce inhaled par- ticulates. Room air filters reduce animal disease problems, but they have not proven practical for large animal facilities because of the large quantity of particulates and the difficulty in drawing particu- lates from the room and through a filter. Air scrubbers can remove gases and particulates, but the initial cost and maintenance make them impractical. Aerodynamic centrifugation is showing promise for removing the small particulates found in animal buildings. Ventilation is the most prevalent method used to control gas contaminant levels in animal facilities. It is reasonably effective in removing gases, but not as effective in removing particulates. Pock- ets in a room with high concentrations of particulate contaminants are common. These polluted pockets occur in dead air spots or near large contaminant sources. Providing high levels of ventilation can be costly in winter, can create drafts on the animals, and can in- crease the release of gas contaminants by increasing air velocity across the source. Disease Control Airborne microbes can transfer disease-causing organisms among animals. For some situations, typically with young animals where there are low-level infections, it is important to minimize air mixing among animal groups. It is especially important to minimize air ex- change between different animal rooms, so buildings need to be fairly airtight. Poor thermal environments and air contaminants can increase stress on the animals, which can make them more susceptible to dis- ease. Therefore, a good environmental control system is important for disease prevention. Air Distribution Air speed should be maintained below 0.25 m/s for most animal species in both cold and mild weather. Animal sensitivities to draft are comparable to those of humans, although some animals are more sensitive at different stages. Riskowski and Bundy (1988) documented that air velocities for optimal rates of gain and feed Chart Type: line 27°C (other) item_01 23% 1% Fig. 2 Response of Swine to Air Velocity efficiencies can be below 0.13 m/s for young pigs at thermoneutral conditions. Increased air movement during hot weather increases growth rates and improves heat tolerance. There are conflicting and lim- ited data defining optimal air velocity in hot weather. Bond et al. (1965) and Riskowski and Bundy (1988) determined that both young and mature swine perform best when air speed is less than 1 m/s (Figure 2). Mount and Start (1980) did not observe performance penalties at air speeds increased to a maximum of 0.76 m/s. Degree of Shelter Livestock, especially young animals, need some protection from adverse climates. On the open range, mature cattle and sheep need protection during severe winter conditions. In winter, dairy cattle and swine may be protected from precipitation and wind with a three-sided, roofed shelter open on the leeward side. The wind- ward side should also have approximately 10% of the wall surface area open to prevent negative pressure inside the shelter, which could cause rain and snow to be drawn into the building on the lee- ward side. These shelters do not protect against high temperature or high humidity. In warmer climates, shades often provide adequate shelter, especially for large, mature animals such as dairy cows. Shades are commonly used in Arizona; research in Florida has shown an approximate 10% increase in milk production and a 75% increase in conception efficiency for shaded versus unshaded cows. The benefit of shades has not been documented for areas with less severe sum- mer temperatures. Although shades for beef cattle are also common practice in the southwestern United States, beef cattle are somewhat less susceptible to heat stress, and extensive comparisons of various shade types in Florida have detected little or no differences in daily mass gain or feed conversion. The energy exchange between an animal and various areas of the environment is illustrated in Figure 3. A well-designed shade makes maximum use of radiant heat sinks, such as the cold sky, and gives maximum protection from direct solar radiation and high surface temperature under the shade. Good design considers geometric ori- entation and material selection, including roof surface treatment and insulation material on the lower surface. An ideal shade has a top surface that is highly reflective to solar energy and a lower surface that is highly absorptive to solar radiation reflected from the ground. A white-painted upper surface reflects solar radiation, yet emits infrared energy better than aluminum. The undersurface should be painted a dark color to prevent multiple reflection of shortwave energy onto animals under the shade. Inc. ASHRAE, 2019 user. single for Licensed | {}
ca21b048-c11b-4081-ac8a-cccc4d7d8254 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 25.4 ![image](/image/placeholder) SKY TEMPERATURE 6000°C 13°C SUN DIRECT INFRARED SOLAR 27°C REFLECTED RADIATION RADIATION SOLAR FROM 40°C RADIATION ATMOS. INFRARED RADIATION V 50°C INFRARED RADIATION EVAP. CONVECTION INFRARED MZ INFRARED SOIL RADIATIONI EVAP? RADIATION 20°C REFLECTED SOLAR RADIATION 25°C CONDUCTION Fig. 3 Energy Exchange Between Farm Animal and Surroundings in Hot Environment 1.1 COOLING AND HEATING Air Velocity Increasing air velocity helps to facilitate the cooling of mature animals. Itis especially beneficial when combined with skin wetting evaporative cooling. Mature swine benefit most with air velocities up to 1 m/s; cattle around 1.5 m/s; and poultry around 3 m/s. Air velocity can be increased with air circulation fans that blow air hor- izontally in circular patterns around the room, paddle fans that blow air downward, or tunnel cooling that moves air horizontally along the length of the building. Evaporative Cooling Supplemental cooling of animals in intensive housing conditions may be necessary during heat waves to prevent heat prostration, mortality, or serious losses in production and reproduction. Evapo- rative cooling, which may reduce ventilation air to 27°C or lower in most of the United States, is popular for poultry houses, and is sometimes used for swine and dairy housing. Evaporative cooling is well suited to animal housing because the high air exchange rates effectively remove odors and ammonia, and increase air movement for convective heat relief. Initial cost, oper- ating expense, and maintenance problems are all relatively low compared to other types of cooling systems. Evaporative cooling works best in areas with low relative humidity, but significant ben- efits can be obtained even in the humid southeastern United States. The building and pad system must be airtight because air leaks caused by the negative-pressure ventilation reduce airflow through the pads, and hence reduce cooling effectiveness. Design. The pad area should be sized to maintain air velocities between 1.0 and 1.4 m/s through the pads. For most pad systems, these velocities produce evaporative efficiencies between 75 and 85%; they also increase pressures against the ventilating fans from 10 to 30 Pa, depending on pad design. The most serious problem encountered with evaporative pads for agricultural applications is clogging by dust and other airborne particles. Whenever possible, fans should exhaust away from pads on adjacent buildings. Regular preventive maintenance is essential. Water bleed-off and the addition of algaecides to the water are rec- ommended. When pads are not used in cool weather, they should be sealed to prevent dusty inside air from exhausting through them. High-pressure fogging with water pressure of 3.5 MPa is pre- ferred to pad coolers for cooling air in broiler houses with built-up litter. The high pressure creates a fine aerosol, causing minimal litter wetting. Timers and/or thermostats control the cooling. Evaporative efficiency and installation cost are about one-half those of a well- designed evaporative pad. Foggers can also be used with naturally 2019 ASHRAE Handbook- -HVAC Applications (SI) ventilated, open-sided housing. Low-pressure systems are not rec- ommended for poultry, but may be used during emergencies. Nozzles that produce water mist or spray droplets to wet animals directly are used extensively during hot weather in swine confine- ment facilities with solid concrete or slatted floors. Currently, mist- ing or sprinkling systems with larger droplets that directly wet the skin surface of the animals (not merely the outer portion of the hair coat) are preferred. Timers that operate periodically, (e.g., 2 to 3 min on a 15 to 20 min cycle) help to conserve water. Mechanical Refrigeration Mechanical refrigeration can be designed for effective animal cooling, but it is considered uneconomical for most production animals. Air-conditioning loads for dairy housing may require 2.5 kW or more per cow. Recirculation of refrigeration air is usu- ally not feasible because of high contaminant loads in the air in the animal housing. Sometimes, zone cooling of individual ani- mals is used instead of whole-room cooling, particularly in swine farrowing houses, where a lower air temperature is needed for sows than for unweaned piglets. It is also beneficial for swine boars and gestating sows. Refrigerated air, 10 to 20 K below ambient temperature, is supplied through insulated ducts directly to the head and face of the animal. Air delivery rates are typically 10 to 20 L/s per animal for snout cooling, and 30 to 40 L/s per SOW for zone cooling. Earth Tubes Some livestock facilities obtain cooling in summer and heating in winter by drawing ventilation air through tubing buried 2 to 4 m below grade. These systems are most practical in the north central United States for animals that benefit from both cooling in summer and heating in winter. MWPS (1990b) details design procedures for this method. A typ- ical design uses 15 to 50 m of 200 mm diameter pipe to provide 150 L/s of tempered air. Soil type and moisture, pipe depth, airflow, cli- mate, and other factors affect the efficiency of buried pipe heat exchangers. The pipes must slope to drain condensation, and must not have dips that could plug with condensation. Heat Exchangers Ventilation accounts for 70 to 90% of the heat losses in typical livestock facilities during winter. Heat exchangers can reclaim some of the heat lost with the exhaust ventilating air. However, predicting fuel savings based on savings obtained during the coldest periods overestimates yearly savings from a heat exchanger. Estimates of energy savings based on air enthalpy can improve the accuracy of the predictions. Heat exchanger design must address the problems of condensate freezing and/or dust accumulation on the heat-exchanging surfaces. If unresolved, these problems result in either reduced efficiency and/or the inconvenience of frequent cleaning. Supplemental Heating For poultry with a mass of 1.5 kg or more, for pigs heavier than 23 kg, and for other large animals such as dairy cows, body heat of animals at recommended space allocations is usually sufficient to maintain moderate temperatures (i.e., above 10°C) in a well-insu- lated structure. Combustion-type heaters are used to supplement heat for baby chicks and pigs. Supplemental heating also increases the moisture-holding capacity of the air, which reduces the quantity ofair required for moisture removal. Various types ofheating equip- ment may be included in ventilation, but they need to perform well in dusty and corrosive atmospheres. Inc. ASHRAE, 2019 user. single for Licensed | {}
746ae21e-a779-423f-975b-c781ee311f4c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Environmental Control for Animals and Plants 25.5 ![image](/image/placeholder) 3 2 Fig. 4 Climatic Zones (Reprinted with permission from ASAE Standard S401.2) Table 1 Minimum Recommended Overall Coefficients of Heat Transmission U for Insulated Assembliesa,b ¦ ¦ Recommended Minimum U, W/(m2. K)c ¦ Recommended Minimum U, W/(m2. K)c ¦ Recommended Minimum U, W/(m2. K)c ¦ Recommended Minimum U, W/(m2. K)c ¦ Recommended Minimum U, W/(m2. K)c ¦ Recommended Minimum U, W/(m2. K)c ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ Cold ¦ Cold ¦ Modified Environment ¦ Modified Environment ¦ Supplementally Heated ¦ Supplementally Heated ¦ ¦ Climatic Zoned ¦ Walls ¦ Ceiling ¦ Walls ¦ Ceiling ¦ Walls ¦ Ceiling ¦ ¦ 1 ¦ ¦ 0.91e ¦ 0.91e ¦ 0.40 ¦ 0.40 ¦ 0.26 ¦ ¦ 2 ¦ - ¦ 0.91 ¦ 0.91 ¦ 0.33 ¦ 0.40 ¦ 0.23 ¦ ¦ 3 ¦ ¦ 0.91 ¦ 0.48 ¦ 0.23 ¦ 0.29 ¦ 0.17 ¦ aUse assembly U-factors that include framing effects, air spaces, air films, linings, and sidings. Determine assembly U-factors by testing the full assembly in accordance with ASTM Standard C236 or C976 or calculate by the procedures presented in the 2017 ASHRAE Handbook-Fundamentals. bValues shown do not represent the values necessary to provide a heat balance between heat produced by products or animals and heat transferred through the building. Current practice for poultry grow-out buildings uses a U of 0.63 to 0.81 W/(m2.K) in the roof and walls. dRefer to Figure 4. eWhere ambient temperature and radiant heat load are severe, use U = 0.48 W/(m2.K). Insulation Requirements The amount of building insulation required depends on climate, animal space allocations, and animal heat and moisture production. Refer to Figure 4 and Table 1 for selecting insulation levels. In warm weather, ventilation between the roof and insulation helps reduce the radiant heat load from the ceiling. Insulation in warm climates can be more important for reducing radiant heat loads in summer than reducing building heat loss in winter. Cold buildings have indoor conditions about the same as out- door conditions. Examples are free-stall barns and open-front live- stock buildings. Minimum insulation is frequently recommended in the roofs of these buildings to reduce solar heat gain in summer and to reduce condensation in winter. Modified environment buildings rely on insulation, natural ven- tilation, and animal heat to remove moisture and to maintain the inside within a specified temperature range. Examples are warm free- stall barns, poultry production buildings, and swine finishing units. Supplementary heated buildings require insulation, ventila- tion, and extra heat to maintain the desired inside temperature and humidity. Examples are swine farrowing and nursery buildings. 1.2 VENTILA TION Mechanical Ventilation Mechanical ventilation uses fans to create a static pressure dif- ference between the inside and outside ofa building. Farm buildings use either positive pressure, with fans forcing air into a building, or negative pressure, with exhaust fans. Some ventilation systems use a combination of positive pressure to introduce air into a building and separate fans to remove air. These zero-pressure systems are particularly appropriate for heat exchangers. Positive-Pressure Ventilation. Fans blow outdoor air into the ventilated space, forcing humid air out through any planned outlets and through leaks in walls and ceilings. If vapor barriers are not complete, moisture can condense within the walls and ceiling during cold weather. Condensation causes deterioration of building materials and reduces insulation effectiveness. The energy used by fan motors and rejected as heat is added to the building (an advan- tage in winter, but a disadvantage in summer). Negative-Pressure Ventilation. Fans exhaust air from the venti- lated space while drawing outdoor air in through planned inlets and leaks in walls, in ceilings, and around doors and windows. Air dis- tribution in negative-pressure ventilation is often less complex and costly than positive- or neutral-pressure systems. Simple openings and baffled slots in walls control and distribute air in the building. However, at low airflow rates, negative pressure ventilation may not distribute air uniformly because of air leaks and wind pressure effects. Supplemental air mixing may be necessary. Allowances should be made for reduced fan performance caused by dust, guards, and corrosion of louver joints (Person et al. 1979). Totally enclosed fan motors are protected from exhaust air con- taminants and humidity. Periodic cleaning helps prevent overheat- ing. Negative-pressure ventilation is more commonly used than positive-pressure ventilation. Ventilation should always be designed so that manure gases are not drawn into the building from manure storages connected to the building by underground pipes or channels. Neutral-Pressure v entilation. Neutral-pressure (push/pull) ven- tilation typically uses supply fans to distribute air down a distribution duct to room inlets, and exhaust fans to remove air from the room. Supply and exhaust fan capacities should be matched. Neutral-pressure systems are often more expensive, but they achieve better control of the air. They are less susceptible to wind effects and to building leakage than positive- or negative-pressure systems. Neutral-pressure systems are most frequently used for young stock and for animals most sensitive to environmental condi- tions, primarily where cold weather is a concern. Natural Ventilation Either natural or mechanical ventilation is used to modify envi- ronments in livestock shelters. Natural ventilation is most common for mature animal housing, such as free-stall dairy, poultry growing, and swine finishing houses. Natural ventilation depends on pressure differences caused by wind and temperature differences. Well- designed natural ventilation keeps temperatures reasonably stable, if automatic controls regulate ventilation openings. Usually, a design includes an open ridge (with or without a rain cover) and openable sidewalls, which should cover at least 50% of the wall for summer operation. Ridge openings are about 17 mm wide for each metre of house width, with a minimum ridge width of 150 mm to avoid freezing problems in cold climates. Upstand baffles on each side of the ridge opening greatly increase airflow (Riskowski et al. 1998). Small screens and square edges around sidewall openings can significantly reduce airflow through vents. Openings can be adjusted automatically, with control based on air temperature. Some designs, referred to as flex housing, include a combination of mechanical and natural ventilation usually dictated by outdoor air temperature and/or the amount of ventilation required. Inc. ASHRAE, 2019 user. single for Licensed | {}
2e6bc076-370f-4890-be25-be02bca55b5b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 25.6 2019 ASHRAE Handbook-HVAC Applications (SI) 1.3 VENTILATION MANAGEMENT Air Distribution Pressure differences across walls and inlet or fan openings are usually maintained between 10 and 15 Pa. (The exhaust fans are usually sized to provide proper ventilation at pressures up to 30 Pa to compensate for wind effects.) This pressure difference creates inlet velocities of 3 to 5 m/s, sufficient for effective air mixing, but low enough to cause only a small reduction in fan capacity. A prop- erly planned inlet system distributes fresh air equally throughout the building. Negative pressure ventilation that relies on cracks around doors and windows does not distribute fresh air effectively. Inlets require adjustment, since winter airflow rates are typically less than 10% of summer rates. Automatic controllers and inlets are available to regulate inlet areas. Positive pressure ventilation, with fans connected directly to per- forated air distribution tubes, may combine heating, circulation, and ventilation in one system. Air distribution tubes or ducts connected to circulating fans are sometimes used to mix the air in negative pressure ventilation. Zhang (1994) describes detailed design proce- dures for perforated ventilation tubes. However, dust in the ducts is of concern when air is recirculated, particularly when cold incom- ing air condenses moisture in the tubes. Inlet Design. Inlet location and size most critically affect air dis- tribution within a building. Continuous or intermittent inlets can be placed along the entire length of one or both outer walls. Building widths narrower than 6 m may need only a single inlet along one wall. The total inlet area may be calculated by the system character- istic technique, which follows. Because the distribution of the inlet area is based on the geometry and size of the building, specific rec- ommendations are difficult. System Characteristic Technique. This technique determines the operating points for the ventilation rate and pressure difference across inlets. Fan airflow rate as a function of pressure difference across the fan should be available from the manufacturer. Allow- ances must be made for additional pressure losses from fan shutters or other devices such as light restriction systems or cooling pads. Inlet flow characteristics are available for hinged baffle and center-ceiling flat baffle slotted inlets (Figure 5). Airflow rates can be calculated for the baffles in Figure 5 by the following: For Case A: Inc. ASHRAE, 2019 user. single for Licensed 0 = 1. 1 Wp 0.5 For Case B: 0 = 0.71 Wp0.5 (2) (1) For Case C (total airflow from sum of both sides): 0 = 1.3Wp 0.5(D/T)0.08 e(-0.867 W/T) where Q = airflow rate, L/s per metre length of slot opening W = slot width, mm p pressure difference across the inlet, Pa D = baffle width, mm T = width of slot in ceiling, mm Zhang and Barber (1995) measured infiltration rates of five rooms in a newly built swine building at 0.6 L/s per square metre of surface area at 20 Pa. Surface area included the area of walls and ceiling enclosing the room. Itis important to include this infiltration rate into the ventilation design and management. For example, at 0.6 L/s per square metre of surface area, the infiltration represents 1.4 ach. In the heating season, the minimum ventilation is usually about 3 ach. Thus, large infiltration rates greatly reduce the airflow from the controlled inlet and adversely affect the air distribution. (3) Room Air Velocity. The average air velocity inside a slot- ventilated structure relates to the inlet air velocity, inlet slot width ![image](/image/placeholder) CASE A WARM INSIDE AIR HINGED FRESH BAFFLE OUTSIDE AIR MIXTURE OF INSIDE AND OUTSIDE AIR CASE B MIXTURE OF INSIDE AND FRESH OUTSIDE AIR OUTSIDE HINGED AIR BAFFLE WARM INSIDE AIR ATTIC SPACE OR PLENUM ![image](/image/placeholder) CASE C THROAT RISER W MIXTURE MIXTURE D WARM INSIDE AIR Fig. 5 Typical Livestock Building Inlet Configurations (or equivalent continuous length for boxed inlets), building width, and ceiling height. Estimates of air velocity within a barn, based on air exchange rates, may be very low because of the effects of jet velocity and recirculation. Conditions are usually partially tur- bulent, and there is no reliable way to predict room air velocity at animal level. General design guidelines keep the throw distance less than 6 m from slots and less than 3 m from perforated tubes. Fans Fans should not exhaust against prevailing winds, especially for cold-weather ventilation. If structural or other factors require installing fans on the windward side, fans rated to deliver the required capacity against at least 30 Pa static pressure and with a relatively flat power curve should be selected. The fan motor should withstand a wind velocity of 50 km/h, equivalent to a static pressure of 100 Pa, without overloading beyond its service factor. Wind hoods on the fans or windbreak fences reduce the effects of wind. Third-party test data should be used to obtain fan performance and energy efficiencies for fan selection (BESS Lab 1997). Fans should be tested with all accessories (e.g., louvers, guards, hoods) in | {}
9ef911de-c608-4287-bfe5-18c401ababe3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Environmental Control for Animals and Plants 25.7 place, just as they will be installed in the building. The accessories have a major effect on fan performance. Flow Control. Because the numbers and size of livestock and climatic conditions vary, means to modulate ventilation rates are often required beyond the conventional off/on thermostat switch. The minimum ventilation rate to remove moisture, reduce air contaminant concentrations, and keep water from freezing should always be provided. Methods of modulating ventilation rates in- clude (1) intermittent fan operation (fans operate for a percentage of the time controlled by a percentage timer with a 10 min cycle); (2) staging of fans using multiple units or fans with high/low- exhaust capability; (3) using multispeed fans [larger fans (400 W and up) with two flow rates, the lower being about 60% of the max- imum rate]; and (4) using variable-speed fans [split-capacitor motors designed to modulate fan speed smoothly from maximum down to 10 to 20% of the maximum rate (the controller is usually thermostatically adjusted)]. Generally, fans are spaced uniformly along the winter leeward side of a building. Maximum distance between fans is 35 to 40 m. Fans may be grouped in a bank ifthis range is not exceeded. In hous- ing with side curtains, exhaust fans that can be reversed or removed and placed inside the building in the summer are sometimes installed to increase air movement in combination with doors, walls, or windows being opened for natural ventilation. Thermostats Thermostats should be placed where they respond to a represen- tative temperature as sensed by the animals. Thermostats need pro- tection and should be placed to prevent potential physical or moisture damage (i.e., away from animals, ventilation inlets, water pipes, lights, heater exhausts, outer walls, or any other objects that will unduly affect performance). Thermostats also require periodic adjustment based on accurate thermometer readings taken in the immediate proximity of the animal. Emergency Warning Animals housed in a high-density, mechanically controlled envi- ronment are subject to considerable risk of heat prostration if a fail- ure of power or ventilation equipment occurs. To reduce this danger, an alarm and an automatic standby electric generator are highly rec- ommended. Many alarms detect failure of the ventilation. These alarms range from inexpensive power-off alarms to ones that sense temperature extremes and certain gases. Automatic telephone- dialing systems are effective as alarms and are relatively inexpensive. Building designs that allow some side wall panels (e.g., 25% of wall area) to be removed for emergency situations are also recommended. 1.4 RECOMMENDED PRACTICES BY SPECIES Mature animals readily adapt to a broad range of temperatures, but efficiency of production varies. Y ounger animals are more tem- perature sensitive. Figure 6 illustrates animal production response to temperature. Relative humidity has not been shown to influence animal per- formance, except when accompanied by thermal stress. Relative humidity consistently below 40% may contribute to excessive dust- iness; above 80%, it may increase building and equipment deterio- ration. Disease pathogens also appear to be more viable at either low or high humidity. Relative humidity has a major influence on the effectiveness of skin-wetting cooling methods. Dairy Cattle Dairy cattle shelters include confinement stall barns, free stalls, and loose housing. In a stall barn, cattle are usually confined to stalls approximately 1.2 m wide, where all chores, including milk- ing and feeding, are conducted. Such a structure requires environ- mental modification, primarily through ventilation. Total space requirements are 5 to 7 m2 per COW. In free-stall housing, cattle are not confined to stalls but can move freely. Space requirements per COW are 7 to 9 m2. In loose housing, cattle are free to move within a fenced lot containing resting and feeding areas. Space required in sheltered loose housing is similar to that in free-stall housing. Shelters for resting and feeding areas are generally open-sided and require no air conditioning or mechanical ventilation, but supple- mental air mixing is often beneficial during warm weather. The milking area is in a separate area or facility and may be fully or par- tially enclosed, thus requiring some ventilation. For dairy cattle, climate requirements for minimal economic loss are broad, and range from 2 to 24°C with 40 to 80% rh. Below 2°C, production efficiency declines and management problems increase. However, the effect oflow temperature on milk production is not as extreme as are high temperatures, where evaporative coolers or other cooling methods may be warranted. Ventilation Rates for Each 500 kg Cow ¦ Winter ¦ Spring/Fall ¦ Summer ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 17 to 22 L/s ¦ 67 to 90 L/s ¦ 110 to 220 L/s ¦ Required ventilation rates depend on specific thermal character- istics of individual buildings and internal heating load. The relative humidity should be maintained between 50 and 80%. Both loose housing and stall barns require an additional milk room to cool and hold the milk. Sanitation codes for milk produc- tion contain minimum ventilation requirements. The market being supplied should be consulted for all applicable codes. Some state codes require positive-pressure ventilation of milk rooms. Milk rooms are usually ventilated with fans at rates of 4 to 10 ach to sat- isfy requirements of local milk codes and to remove heat from milk coolers. Most milk codes require ventilation in the passageway (if any) between the milking area and the milk room. Beef Cattle Beef cattle ventilation requirements are similar to those of dairy cattle on a unit mass basis. Beef production facilities often provide only shade and wind breaks. Swine Swine housing can be grouped into four general classifications: 1. Farrowing pigs, from birth to 14 kg, and sows 2. Nursery pigs, from 14 to 34 kg 3. Growing/finishing pigs, from 34 kg to market size 4. Breeding and gestation In farrowing barns, two environments must be provided: one for sows and one for piglets. Because each requires a different tempera- ture, zone heating and/or cooling is used. The environment within the nursery is similar to that within the farrowing barn for piglets. The requirements for growing barns and breeding stock housing are similar. Currently recommended practices for farrowing houses: · Temperature: 10 to 20°C, with small areas for piglets warmed to 28 to 32°C by brooders, heat lamps, or floor heat. Avoid cold drafts and extreme temperatures. Hovers are sometimes used. Provide supplemental cooling for sows (usually drippers or zone cooling) in extreme heat. · Relative humidity: Up to 70% maximum · Ventilation rate: 10 to 240 L/s per SOW and litter (about 180 kg total mass). The low rate is for winter; the high rate is for summer temperature control. · Space: 3.25 m2 per SOW and litter (stall); 6.0 m2 per SOW and litter (pens) Inc. ASHRAE, 2019 user. single for Licensed | {}
cf80221c-3c65-4b1a-9b6d-8429817e856b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 25.8 2019 ASHRAE Handbook-HVAC Applications (SI) Chart Type: bar SWENE SWE_100 SWE_200 SWE_300 SWE_400 SWE_500 SWE_600 SWE_700 SWE_800 SWE_900 SPE_1000 SPE_910 SPE_2000 SWE_310 SWE_920 SWE_930 item_01 0.8Temperature (°C) 0.8Temperature (°C) 1.5Temperature (°C) 0.6Temperature (°C) 0.4Temperature (°C) 0.3Temperature (°C) 0.2Temperature (°C) 0.0Temperature (°C) 0.0Temperature (°C) 0.0Temperature (°C) 0.0Temperature (°C) 0.0Temperature (°C) 0.0Temperature (°C) 0.0Temperature (°C) 0.0Temperature (°C) 0.0Temperature (°C) Optimal Performance Nominal Performance Losses Fig. 6 Critical Ambient Temperatures and Temperature Zone for Optimum Performance and Nominal Performance Loss in Farm Animals (Adapted from Hahn 1985, in Stress Physiology in Livestock, Vol. II, CRC Press) ト Lower Critical Temperature - Upper Critical Temperature Recommendations for nursery barns: · Temperature: 27°C for first week after weaning. Lower room temperature 1.5 K per week to 21°C. Provide warm, draft-free floors. Provide supplemental cooling for extreme heat (temperatures 30°C and above). · Ventilation rate: 1 to 12 L/s per pig, 5.5 to 14 kg each 1.5 to 18 L/s per pig, 6 to 36 kg each · Space: 0.19 to 0.23 m2 per pig, 5.5 to 14 kg each 0.28 to 0.37 m2 pig, 6 to 14 kg each per Recommendations for growing and gestation barns: · Temperature: 13 to 22°C preferred. Provide supplemental cooling (sprinklers or evaporative coolers) for extreme heat. · Relative humidity: · Ventilation rate: Growing pig (34 to 68 kg), 3 to 35 L/s Finishing pig (68 to 100 kg), 5 to 60 L/s Gestating SOW (150 kg), 6 to 70 L/s Boar/breeding SOW (180 kg), 7 to 140 L/s · Space: 0.55 m2 per pig, 34 to 68 kg each 0.75 m2 68 to 100 kg each per pig, 1.3 to 2.2 m2 per pig, 110 to 130 kg each Poultry 75% maximum in winter; no established limit in summer In broiler and brooder houses, growing chicks require changing environmental conditions, and heat and moisture dissipation rates increase as the chicks grow older. Supplemental heat, usually from brooders, is used until sensible heat produced by the birds is ade- quate to maintain an acceptable air temperature. At early stages of growth, moisture dissipation per bird is low. Consequently, low ventilation rates are recommended to prevent excessive heat loss. Inc. ASHRAE, 2019 user. single for Licensed | {}
01e2ceb3-e7a8-43c6-8df4-883b9a1968be | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Environmental Control for Animals and Plants 25.9 Litter is allowed to accumulate over 3 to 5 flock placements. Lack of low-cost litter material may justify the use of concrete floors. After each flock, caked litter is removed and fresh litter is added. Housing for poultry may be open, curtain-sided or totally en- closed. Mechanical ventilation depends on the type ofhousing used. For open-sided housing, ventilation is generally natural airflow in warm weather, supplemented with stirring fans, and by fans with closed curtains in cold weather or during the brooding period. Mechanical ventilation is used in totally enclosed housing. Newer houses have smaller curtains and well-insulated construction to accommodate both natural and mechanical ventilation operation. Recommendations for broiler houses: · Room temperature: 15 to 27°C · Temperature under brooder hover: 30 to 33°C, reducing 3 K per week until room temperature is reached · Relative humidity: 50 to 80% · Ventilation rate: Sufficient to maintain house within 1 to 2 K of outdoor air conditions during summer. Generally, rates are about 0.1 L/s per kilogram live mass during winter and 1 to 2 L/s per kilogram for summer conditions. · Space: 0.06 to 0.1 m2 per bird (for the first 21 days of brooding, only 50% of floor space is used) · Light: Minimum of 10 lx to 28 days of age; 1 to 20 lx for growout (in enclosed housing). Recommendations for breeder houses with birds on litter and slatted floors: · Temperature: 10 to 30°C maximum; consider evaporative cooling if higher temperatures are expected. · Relative humidity: 50 to 75% · Ventilation rate: Same as for broilers on live mass basis. · Space: 0.2 to 0.3 m2 per bird Recommendations for laying houses with birds in cages: · Temperature, relative humidity, and ventilation rate: Same as for breeders. · Space: 0.032 to 0.042 m2 per hen minimum · Light: Controlled day length using light-controlled housing is generally practiced (January through June). Laboratory Animals The well-being and experimental response of laboratory animals depend greatly on the design of the facilities. Cage type, noise lev- els, light levels, air quality, and thermal environment can affect animal well-being and, in many cases, affect how the animal responds to experimental treatments (Clough 1982; Lindsey et al. 1978; McPherson 1975; Moreland 1975). If any of these factors vary across treatments or even within treatments, it can affect the validity of experimental results, or at least increase experimental error. Consequently, laboratory animal facilities must be designed and maintained to expose the animals to appropriate levels of these environmental conditions and to ensure that all animals in an exper- iment are in a uniform environment. See Chapter 16 for additional information on laboratory animal facilities. In the United States, recommended environmental conditions within laboratory animal facilities are usually dictated by Institute for Laboratory Animal Research (ILAR 1996). Temperature rec- ommendations vary from 16 to 29°C, depending on the species being housed. The acceptable range for relative humidity is 30 to 70%. For animals in confined spaces, daily temperature fluctua- tions should be minimized. Relative humidity must also be con- trolled, but not as precisely as temperature. Ventilation recommendations are based on room air changes; however, cage ventilation rates may be inadequate in some cages and excessive in other cages, depending on cage and facility design. ILAR (1996) recommendations for room ventilation rates of 10 to 15 ach are an attempt to provide adequate ventilation for the room and cages. This recommendation is based on the assumption that adequate ventilation in the macroenvironment (room) provides suf- ficient ventilation to the microenvironment (cage). This may be a reasonable assumption when cages have a top of wire rods or mesh. However, several studies have shown that covering cages with filter tops, which provide a protective barrier for rodents and reduce air- borne infections and diseases, especially neonatal diarrhea, can cre- ate significant differences in microenvironmental conditions. Maghirang et al. (1995) and Riskowski et al. (1996) surveyed room and cage environmental conditions in several laboratory ani- mal facilities and found that the animal's environmental needs may not be met even though the facilities were designed and operated according to ILAR (1996). The microenvironments were often con- siderably poorer than the room conditions, especially in micro- isolator cages. For example, ammonia levels in cages were up to 45 mg/m3 even though no ammonia was detected in a room. Cage temperatures were up to 4 K higher than room temperature and rel- ative humidities up to 41% higher. Furthermore, cage microenvironments in the same room were found to have significant variation (Riskowski et al. 1996): ammo- nia levels varied from 0 to 45 mg/m3, air temperature varied from 0.5 to 4 K higher than room temperature, relative humidity varied from 1 to 30% higher than room humidity, and average light levels varied from 2 to 337 lx. This survey found three identical rooms that had room ventilation rates from 4.4 to 12.5 ach but had no differ- ences in room or cage environmental parameters. A survey oflaboratory animal environmental conditions in seven laboratory rat rooms was conducted by Zhang et al. (1992). They found that room air ammonia levels were under 0.37 mg/m3 for all rooms, even though room airflow varied from 11 to 24 ach. Air exchange rates in the cages varied from less than 0.05 L/s to 1.2 L/ s per rat, and ammonia levels ranged from negligible to 45 mg/m3. Riskowski et al. (1996) measured several environmental parameters in rat shoebox cages in full-scale room mockups with various room and ventilation configurations. Significant variations in cage tem- perature and ventilation rates within a room were also found. Vary- ing room ventilation rate from 5 to 15 ach did not have large effects on cage environmental conditions. These studies verify that designs based only on room air changes do not guarantee desired conditions in the animal cages. In order to analyze the ventilation performance of different laboratory animal research facilities, Memarzadeh (1998) used computational fluid dynamics (CFD) to undertake computer simulation of over 100 different room configurations. CFD is a three-dimensional mathematical technique used to compute the motion of air, water, or any other gas or liquid. However, all con- ditions must be correctly specified in the simulation to produce accurate results. Empirical work defined inputs for such parame- ters as heat dissipation and surface temperature as well as the moisture, CO2, and NH3 mass generation rates for mice. This approach compared favorably with experimentally mea- sured temperatures and gas concentrations in a typical animal research facility. To investigate the relationships between room con- figuration parameters and the room and cage environments in labo- ratory animal research facilities, the following parameters were varied: · Supply air diffuser type and orientation, air temperature, and air moisture content · Room ventilation rate · Exhaust location and number · Room pressurization · Rack layout and cage density · Change station location, design, and status Inc. ASHRAE, 2019 user. single for Licensed | {}
12a002d3-74ea-4de7-9c00-8d5b3240b01d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 25.10 2019 ASHRAE Handbook- -HVAC Applications (SI) · Leakage between the cage lower and upper moldings · Room width Room pressurization, change station design, and room width had little effect on ventilation performance. However, other factors found to affect the macroenvironment, microenvironment, or both led to the following observations: · Ammonia production depends on relative humidity. Ten days after the last change of bedding, a high-humidity environment produced ammonia at about three times the rate of cages in a low- humidity environment. · Acceptable room and cage ammonia concentrations after 5 days without changing cage bedding are produced by room supply air- flow rates of around 4 L/s per kilogram of body mass of mice. This is equivalent to 5 ach for the room with single-density racks considered in this study, and 10 ach for the room with double- density racks. The temperature of the supply air must be set appropriately for the heat load in the room. The room with single- density racks contained 1050 mice with a total mass of21 kg and the room with double-density racks contained 2100 mice with a total mass of 42 kg. · Increasing the room ventilation rate does not have a large effect on the cage ventilation. Increasing the supply airflow from 5 to 20 ach around single-density racks parallel to the walls reduces the CO2 concentration from 3175 to 3000 mg/m3, a reduction of only 6%. For the double-density racks perpendicular to the walls, the reduction is larger, but still only from about 4140 to 3240 mg/ m3 (around 20%) · Both the cage and the room ammonia concentrations can be reduced by increasing the supply air temperatures. This reduces the relative humidity for a given constant moisture content in the air, and the lower relative humidity leads to lower ammonia gen- eration. Raising the supply discharge temperature from 19 to 22°C at 15 ach raises the room temperature by 3 K to around 23°C and the cages by 2 K to around 25°C. This can reduce ammonia concentrations by up to 50%. · Using 22°C as the supply discharge temperature at 5 ach (the low- est flow rate considered) for double-density racks produces a room temperature around 26°C, with cage temperatures only slightly higher. Although this higher temperature provides a more comfortable environment for the mice (Gordon et al. 1997), the high room temperature may be unacceptable to the scientists working in the room. · Ceiling or high-level exhausts tend to produce lower room tem- peratures (for a given supply air temperature, all CFD models were designed to have 22°C at the room exhaust) when compared to low-level exhausts. This indicates that low-level exhausts are less efficient at cooling the room. · Low-level exhausts appear to ventilate the cages slightly better (up to 27% for the radial diffuser; much less for the slot diffuser) than ceiling or high-level exhausts when the cages are placed parallel to the walls, near the exhausts. Ammonia concentration in the cages decreased even further, although this is because of the higher temperatures in the low-level exhaust cases when com- pared to the ceiling and high-level exhausts. The room concentra- tions of CO2 and ammonia do not show that any type of supply or exhaust is significantly better or worse than the other type. 2. DESIGN FOR PLANT FACILITIES Greenhouses, plant growth chambers, and other facilities for in- door crop production overcome adverse outdoor environments and provide conditions conducive to economical crop production. The basic requirements of indoor crop production are (1) adequate light; (2) favorable temperatures; (3) favorable air or gas content; (4) protection from insects and disease; and (5) suitable growing ![image](/image/placeholder) Fig. 7 Structural Shapes of Commercial Greenhouses media, substrate, and moisture. Because of their lower cost per unit of usable space, greenhouses are preferred over plant growth cham- bers for protected crop production. This section covers green- houses and plant growth facilities. 2.1 GREENHOUSES Figure 7 shows the structural shapes of typical commercial greenhouses. Other greenhouses may have Gothic arches, curved glazing, or simple lean-to shapes. Glazing, in addition to traditional glass, now includes both film and rigid plastics. High light transmis- sion by the glazing is usually important; good location and orienta- tion of the house are also important in providing desired light conditions. Location affects heating and labor costs, exposure to plant disease and air pollution, and material handling requirements. As a general rule in the northern hemisphere, a greenhouse should be placed at a distance of at least 2.5 times the height of the object closest to it in the eastern, western, and southern directions. Site Selection Sunlight. Sunlight provides energy for plant growth and is often the limiting growth factor in greenhouses of the central and northern areas of North America during the winter. When planning green- houses that are to be operated year-round, a designer should design for the greatest sunlight exposure during the short days of midwin- ter. The building site should have an open southern exposure, and if the land slopes, it should slope to the south. Soil and Drainage. When plants are to be grown in the soil covered by the greenhouse, a growing site with deep, well-drained, fertile soil, preferably sandy loam or silt loam, should be chosen. Even though organic soil amendments can be added to poor soil, fewer problems occur with good natural soil. However, when good soil is not available, growing in artificial media should be consid- ered. The greenhouse should be level, but the site can and often should be sloped and well-drained to reduce salt build-up and in- sufficient soil aeration. A high water table or a hardpan may pro- duce water-saturated soil, increase greenhouse humidity, promote diseases, and prevent effective use of the greenhouse. If present, these problems can be alleviated by tile drains under and around the greenhouse. Ground beds should be level to prevent water from concentrating in low areas. Slopes within greenhouses also in- crease temperature and humidity stratification and create addi- tional environmental problems. Sheltered Areas. Provided they do not shade the greenhouse, surrounding trees act as wind barriers and help prevent winter heat loss. Deciduous trees are less effective than coniferous trees in mid- winter, when the heat loss potential is greatest. In areas where snow- drifts occur, windbreaks and snowbreaks should be 30 m or more from the greenhouse to prevent damage. Orientation. Generally, in the northern hemisphere, for single- span greenhouses located north of 35° latitude, maximum trans- mission during winter is attained by an east-west orientation. South of 35° latitude, orientation is not important, provided headhouse structures do not shade the greenhouse. North-south orientation provides more light on an annual basis. Inc. ASHRAE, 2019 user. single for Licensed | {}
71557f00-5ce0-4fd2-ba68-92b356aad849 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Environmental Control for Animals and Plants 25.11 Chart Type: line POLYETHYLENE MYLAR GLASS FIBERGLASS item_01 0.9 0.8 0.6 0.3 Fig. 8 Transmittance of Solar Radiation Through Glazing Materials for Various Angles of Incidence Gutter-connected or ridge-and-furrow greenhouses are oriented preferably with the ridge line north-south regardless oflatitude. This orientation allows the shadow pattern caused by the gutter super- structure to move from the west to the east side of the gutter during the day. With an east-west orientation, the shadow pattern would remain north of the gutter, and the shadow would be widest and cre- ate the most shade during winter when light levels are already low. Also, the north-south orientation allows rows of tall crops, such as roses and staked tomatoes, to align with the long dimension of the house (an alignment that is generally more suitable to long rows and the plant support methods preferred by many growers). The slope of the greenhouse roofis a critical part of greenhouse design. If the slope is too flat, a greater percentage of sunlight is reflected from the roof surface (Figure 8). A slope with a 1:2 rise-to- run ratio is the usual inclination for a gable roof. Heating Structural Heat Loss. Estimates for heating and cooling a greenhouse consider conduction, infiltration, and ventilation energy exchange. In addition, the calculations must consider solar energy load and electrical input, such as light sources, which are usually much greater for greenhouses than for conventional buildings. Gen- erally, conduction qc plus infiltration qi are used to determine the peak requirements It for heating. It = qc + qi qc = UA(ti-to) qi = 0.5VN(ti-to) where U = overall heat loss coefficient, W/(m2 - K) (Tables 2 and 3) A = exposed surface area, m2 ti = inside temperature, °C to = outdoor temperature, °C V = greenhouse internal volume, m3 N = number of air exchanges per hour (Table 4) (4) (5) ⑥ Table 2 Suggested Heat Transmission Coefficients ¦ ¦ ¦ U, W/(m2.K) ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Glass ¦ Glass ¦ Glass ¦ ¦ ¦ Single-glazing ¦ 6.4 ¦ ¦ ¦ Double-glazing ¦ 4.0 ¦ ¦ ¦ Insulating ¦ Manufacturers' data ¦ ¦ Plastic film ¦ Plastic film ¦ Plastic film ¦ ¦ ¦ Single filma ¦ 6.8 ¦ ¦ ¦ Double film, inflated ¦ 4.0 ¦ ¦ ¦ Single film over glass ¦ 4.8 ¦ ¦ ¦ Double film over glass ¦ 3.4 ¦ ¦ Corrugated glass fiber ¦ Corrugated glass fiber ¦ Corrugated glass fiber ¦ ¦ ¦ Reinforced panels ¦ 6.8 ¦ ¦ Plastic structured sheetb ¦ Plastic structured sheetb ¦ Plastic structured sheetb ¦ ¦ ¦ 16 mm thick ¦ 3.3 ¦ ¦ ¦ 8 mm thick ¦ 3.7 ¦ ¦ ¦ 6 mm thick ¦ 4.1 ¦ aInfrared barrier polyethylene films reduce heat loss; however, use this coefficient when designing heating systems because the structure could occasionally be covered with non-IR materials. bPlastic structured sheets are double-walled, rigid plastic panels. Table 3 Construction U-Factor Multipliers ¦ Metal frame and glazing system, 400 to 600 mm spacing ¦ 1.08 ¦ ¦ --- ¦ --- ¦ ¦ Metal frame and glazing system, 1200 mm spacing ¦ 1.05 ¦ ¦ Fiberglass on metal frame ¦ 1.03 ¦ ¦ Film plastic on metal frame ¦ 1.02 ¦ ¦ Film or fiberglass on wood ¦ 1.00 ¦ Table 4 Suggested Design Air Changes (N) ¦ New Construction ¦ New Construction ¦ ¦ --- ¦ --- ¦ ¦ Single glass lapped (unsealed) ¦ 1.25 ¦ ¦ Single glass lapped (laps sealed) ¦ 1.0 ¦ ¦ Plastic film covered ¦ 0.6 to 1.0 ¦ ¦ Structured sheet ¦ 1.0 ¦ ¦ Film plastic over glass ¦ 0.9 ¦ ¦ Old Construction ¦ Old Construction ¦ ¦ Good maintenance ¦ 1.5 ¦ ¦ Poor maintenance ¦ 2 to 4 ¦ Type of Framing. The type of framing should be considered in determining overall heat loss. Aluminum framing and glazing sys- tems may have the metal exposed to the exterior to a greater or lesser degree, and the heat transmission of this metal is higher than that of the glazing material. To allow for such a condition, the U-factor of the glazing material should be multiplied by the factors shown in Table 3. Infiltration. Equation ⑥ may be used to calculate heat loss by infiltration. Table 4 suggests values for air changes N. Radiation Energy Exchange. Solar gain can be estimated using the procedures outlined in Chapter 18 of the 2017 ASHRAE Hand- book-Fundamentals. As a guide, when a greenhouse is filled with a mature crop of plants, one-half the incoming solar energy is con- verted to latent heat, and one-quarter to one-third, to sensible heat. The rest is either reflected out of the greenhouse or absorbed by the plants and used in photosynthesis. Radiation from a greenhouse to a cold sky is more complex. Glass admits a large portion of solar radiation but does not transmit long-wave thermal radiation in excess of approximately 5000 nm. Plastic films transmit more of the thermal radiation but, in general, the total heat gains and losses are similar to those of glass. Newer plastic films containing infrared (IR) inhibitors reduce the thermal radiation loss. Plastic films and glass with improved radiation reflection are available at a somewhat higher cost. Some research greenhouses use a retractable horizontal heat curtain to reduce the Inc. ASHRAE, 2019 user. single for Licensed | {}
c6efb17f-9c2e-45c1-a8f7-121cf4754082 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 25.12 ![image](/image/placeholder) 22 20 21 20 20 21 19°C 22 23 18 17 Fig. 9 Temperature Profiles in a Greenhouse Heated with Radiation Piping along the Sidewalls effect of night sky losses. Normally, radiation energy exchange is not considered in calculating the design heat load. Heating Systems. Greenhouses may have a variety of heaters. One is a convection heater that circulates hot water or steam through plain or finned pipe. The pipe is most commonly placed along walls and occasionally beneath plant benches to create desirable convec- tion currents. A typical temperature distribution pattern created by perimeter heating is shown in Figure 9. More uniform temperatures can be achieved when about one-third the total heat comes from pipes spaced uniformly across the house. These pipes can be placed above or below the crop, but temperature stratification and shading are avoided when they are placed below. Outdoor weather condi- tions affect temperature distribution, especially on windy days in loosely constructed greenhouses. Manual or automatic overhead pipes are also used for supplemental heating to prevent snow build- up on the roof. In a gutter-connected greenhouse in a cold climate, a heat pipe should be placed under each gutter to prevent snow accu- mulation. An overhead tube heater consists of a unit heater that discharges into 300 to 750 mm diameter plastic film tubing perforated to pro- vide uniform air distribution. The tube is suspended at 2 to 3 m inter- vals and extends the length of the greenhouse. Variations include a tube and fan receiving the discharge of several unit heaters. The fan and tube system is used without heat to recirculate the air and, during cold weather, to introduce ventilation air. However, tubes sized for heat distribution may not be large enough for effective ven- tilation during warm weather. Perforated tubing, 150 to 250 mm in diameter, placed at ground- level (underbench) heaters can also improve heat distribution. Ide- ally, the ground-level tubing should draw air from the top of the greenhouse for recirculation or heating. Tubes on or near the floor have the disadvantage of being obstacles to workers and reducing usable floor space. Underfloor heating can supply up to 25% or more of the peak heat- ing requirements in cold climates. A typical underfloor system uses 100 mm plastic pipe spaced 300 to 400 mm on center, and covered with 20 mm of gravel or porous concrete. Hot water, not exceeding 40°C, circulates at a rate of0.5 to 1.0 L/s per loop. Pipe loops should generally not exceed 130 m in length. This can provide 50 to 65 W/ m2 from a bare floor, and about 75% as much when potted plants or seedling flats cover most of the floor. Similar systems can heat soil directly, but root temperature must not exceed 25°C. When used with water from solar collectors or other heat sources, the underfloor area can store heat. This storage consists of a vinyl swimming pool liner placed on top of insulation and a moisture barrier at a depth of200 to 300 mm below grade, and filled with 50% void gravel. Hot water from solar collectors or other clean sources enters and is pumped out on demand. Some heat sources, such as cooling water from power plants, cannot be used 2019 ASHRAE Handbook- -HVAC Applications (SI) directly but require closed-loop heat transfer to avoid fouling the storage and the power plant cooling water. Greenhouses can also be bottom-heated with 6 mm diameter EPDM tubing (or variations of that method) in a closed loop. The tubes can be placed directly in the growing medium of ground beds or under plant containers on raised benches. The best tem- perature uniformity is obtained by flow in alternate tubes in oppo- site directions. This method can supply all the greenhouse heat needed in mild climates. Bottom heat, underfloor heating, and underbench heating are, because of the location of the heat source, more effective than overhead or peripheral heating, and can reduce energy loss by 20 to 30%. Unless properly located and aimed, overhead unit heaters, whether hydronic or direct fired, do not give uniform temperature at the plant level and throughout the greenhouse. Horizontal blow heaters positioned so that they establish a horizontal airflow around the outside of the greenhouse offer the best distribution. The airflow pattern can be supplemented with the use ofhorizontal blow fans or circulators. When direct combustion heaters are used in the greenhouse, combustion gases must be adequately vented to the outdoors to minimize danger to plants and humans from products of combus- tion. One manufacturer recommends that combustion air must have access to the space through a minimum of two permanent openings in the enclosure, one near the bottom. A minimum of 2200 mm2 of free area per kilowatt input rating of the unit, with a minimum of0.65 m2 for each opening, whichever is greater, is rec- ommended. Unvented direct-combustion units should not be used inside the greenhouse. Many greenhouses combine overhead and perimeter heating. Regardless of the type ofheating, it is common practice to calculate overall heat loss first, and then to calculate the individual elements such as the roof, sidewalls, and gables. It is then simple to allocate the overhead portion to the roof loss and the perimeter portions to the sides and gables, respectively. The annual heat loss can be approximated by calculating the design heat loss and then, in combination with the annual degree- day tables using the 18.3°C base, estimating an annual heat loss and computing fuel usage on the basis of the rating of the particular fuel used. If a 10°C base is used, it can be prorated. Heat curtains for energy conservation are becoming more important in greenhouse construction. Although this energy savings may be considered in the annual energy use, it should not be used when calculating design heat load; the practice is to open the heat curtains during snowstorms to facilitate snow melting, thereby nul- lifying its contribution to the design heat loss value. Air-to-air and water-to-air heat pumps have been used experi- mentally on small-scale installations. Their usefulness is especially sensitive to the availability of a low-cost heat source. Radiant (Infrared) Heating. Radiant heating is used in some lim- ited applications for greenhouse heating. Steel pipes spaced at inter- vals and heated to a relatively high temperature by special gas heaters serve as the source of radiation. Because the energy is trans- mitted by radiation from a source of limited size, proper spacing is important to completely cover the heated area. Further, heavy- foliage crops can shade the lower parts of the plants and the soil, thus restricting the radiation from warming the root zone, which is important to plant growth. Cogenerated Sources of Heat. Greenhouses have been built near or adjacent to power plants to use the heat and electricity gen- erated by the facility. Although this energy may cost very little, an adequate standby energy source must be provided, unless the power supplier can assure that it will supply a reliable, continuous source of energy. Inc. ASHRAE, 2019 user. single for Licensed | {}
58bc5efd-79ca-4956-8f4e-2d6dcdcf449e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Environmental Control for Animals and Plants 25.13 Cooling Solar radiation is a considerable source of sensible heat gain; even though some of this energy is reflected from the greenhouse, some of it is converted into latent heat as the plants transpire moisture, and some is converted to plant material by photosynthesis. Natural ven- tilation, mechanical ventilation, shading, and evaporative cooling are common methods used to remove this heat. Mechanical refrigeration is seldom used to air-condition greenhouses because the cooling load and resulting cost is so high. Natural Ventilation. Most older greenhouses and many new ones rely on natural ventilation with continuous roof sashes on each side of the ridge and continuous sashes in the sidewalls. The roof sashes are hinged at the ridge, and the wall sashes are hinged at the top ofthe sash. During much of the year, vents admit enough venti- lating air for cooling without the added cost of running fans. The principles of natural ventilation are explained in Chapter 16 of the 2017 ASHRAE Handbook-Fundamentals. Ventilation air is driven by wind and thermal buoyancy forces. Proper vent openings take advantage of pressure differences created by wind. Thermal buoyancy caused by the temperature difference between the inside and the outside of the greenhouse is enhanced by the area of the vent opening and the stack height (vertical distance between the center of the lower and upper opening). Within the limits of typical construc- tion, the larger the vents, the greater the ventilating air exchanged. For a single greenhouse, the combined area of the sidewall vents should equal that of the roof vents. In ranges of several gutter- connected greenhouses, the sidewall area cannot equal the roof vent area. Mechanical (Forced) Ventilation. Exhaust fans provide posi- tive ventilation without depending on wind or thermal buoyancy forces. The fans are installed in the side or end walls of the green- house and draw air through vents on the opposite side or end walls. Air velocity through the inlets should not exceed 2 m/s. ![image](/image/placeholder) 35 30 + DOUBLE COVERING DIFFERENCE, 25 20 SINGLE COVERING TEMPERATURE 15 10 5 0 0 1/4 1/2 1 2 3 4 AIR CHANGE RATE, VOLUMES/MIN Fig. 10 Influence of Air Exchange Rate on Temperature Rise in Single- and Double-Covered Greenhouses Air exchange rates between 0.75 and 1 change per minute effec- tively control the temperature rise in a greenhouse. As shown in Fig- ure 10, the temperature inside the greenhouse rises rapidly at lower airflow rates. At higher airflow rates, the reduction of the tempera- ture rise is small, fan power requirements are increased, and plants may be damaged by the high air speed. Shading. Shading compounds can be applied in varying amounts to the exterior of the roof of the greenhouse to achieve up to 50% shading. Durability of these compounds varies; ideally, the compound wears away during the summer and leaves the glazing clean in the fall, when shading is no longer needed. In practice, some physical cleaning is needed. Compounds used formerly usu- ally contained lime, which corrodes aluminum and attacks some caulking. Most compounds used currently are formulated to avoid this problem. Mechanically orated shade cloth systems with a wide range of shade levels are also available. They are mounted inside the green- house to protect them from the weather. Not all shading compounds or shade cloths are compatible with all plastic glazings, so the man- ufacturers' instructions and precautions should be followed. Evaporative Cooling. Fan-and-Pad Systems. Fans for fan-and-pad evaporative cool- ing are installed in the same manner as fans used for mechanical ventilation. Pads of cellulose material in a honeycomb form are installed on the inlet side. The pads are kept wet continuously when evaporative cooling is needed. As air is drawn through the pads, the water evaporates and cools the air. New pads cool the air by about 80% of the difference between the outdoor dry- and wet-bulb temperatures, or to 1.5 to 2 K above the wet-bulb tem- perature. The principles of applying evaporative cooling are explained in Chapter 41 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment and in Chapter 52 of this volume. The empirical base rate of airflow is 40 L/s per square metre of floor area. This flow rate is modified by multiplying it by factors for elevation (Fe), maximum interior light intensity (Fi), and allowable temperature rise between the pad and fans (Ft). These factors are listed in Table 5. The overall factor for the house is given by the fol- lowing equation: Fh = FeFlFt (7) The maximum fan-to-pad distance should be kept to 53 m, although some greenhouses with distances of 68 m have shown no serious reduction in effectiveness. With short distances, the air velocity becomes so low that the air feels clammy and stuffy, even though the airflow is sufficient for cooling. Therefore, a velocity factor Fv listed in Table 6 is used for distances less than 30 m. For distance less than 30 m, Fv is compared to Fh. The factor that gives the greatest airflow is used to modify the empirical base rate. For Fv can be ignored. fan-to-pad distances greater than 30 m, For best performance, pads should be installed on the windward side, and fans spaced within 7.5 m of each other. Fans should not blow toward pads of an adjacent house unless it is at least 15 m away. Fans in adjacent houses should be offset if they blow toward each other and are within 4.5 m of each other. Recommended air velocities through commonly used pads are listed in Table 7. Water flow and sump capacities are shown in Table 8. The system should also include a small, continuous bleed-off of water to reduce the build-up of dirt and other impurities. Unit Evaporative Coolers. This equipment contains the pads, water pump, sump, and fan in one unit. Unit coolers are primarily used for small compartments. They are mounted 4.5 to 6 m apart on the sidewall and blow directly into the greenhouse. They cool a dis- tance of up to 15 m from the unit. A side sash on the outside opposite wall is the best outlet, but roof vents may also work. The roof vent on the same side as the unit should be slightly open for better air dis- tribution. If the roof vent on the opposite side is opened instead, air Inc. ASHRAE, 2019 user. single for Licensed | {}
9b37183d-03f6-4171-b48a-bad0bd4e9529 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 25.14 ¦ Elevation (Above Sea Level) ¦ Elevation (Above Sea Level) ¦ Max. Interior Light Intensity ¦ Max. Interior Light Intensity ¦ Fan-to-Pad Temp. Difference ¦ Fan-to-Pad Temp. Difference ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ m ¦ Fe ¦ klx ¦ Fl ¦ K ¦ Ft ¦ ¦ <300 ¦ 1.00 ¦ 40 ¦ 0.74 ¦ 5.5 ¦ 0.71 ¦ ¦ 300 ¦ 1.03 ¦ 45 ¦ 0.84 ¦ 5.0 ¦ 0.78 ¦ ¦ 600 ¦ 1.08 ¦ 50 ¦ 0.93 ¦ 4.5 ¦ 0.87 ¦ ¦ 900 ¦ 1.12 ¦ 55 ¦ 1.02 ¦ 4.0 ¦ 0.98 ¦ ¦ 1200 ¦ 1.16 ¦ 60 ¦ 1.12 ¦ 3.5 ¦ 1.12 ¦ ¦ 1500 ¦ 1.20 ¦ 65 ¦ 1.21 ¦ 3.0 ¦ 1.31 ¦ ¦ 1800 ¦ 1.25 ¦ 70 ¦ 1.30 ¦ 2.5 ¦ 1.58 ¦ ¦ 2100 ¦ 1.29 ¦ 75 ¦ 1.39 ¦ ¦ ¦ ¦ 2400 ¦ 1.33 ¦ 80 ¦ 1.49 ¦ ¦ ¦ ¦ 2700 ¦ 1.37 ¦ 85 ¦ 1.58 ¦ ¦ ¦ Table 5 Multipliers for Calculating Airflow for Fan-and-Pad Cooling Table 6 Velocity Factors for Calculating Airflow for Fan-to-Pad Cooling ¦ Fan-to-Pad Distance, m ¦ Fv ¦ Fan-to-Pad Distance, m ¦ Fv ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 6 ¦ 2.26 ¦ 20 ¦ 1.23 ¦ ¦ 8 ¦ 1.96 ¦ 22 ¦ 1.17 ¦ ¦ 10 ¦ 1.75 ¦ 24 ¦ 1.13 ¦ ¦ 12 ¦ 1.60 ¦ 26 ¦ 1.08 ¦ ¦ 14 ¦ 1.48 ¦ 28 ¦ 1.04 ¦ ¦ 16 ¦ 1.38 ¦ 30 ¦ 1.00 ¦ ¦ 18 ¦ 1.30 ¦ ¦ ¦ ¦ Pad Type and Thickness ¦ Air Face Velocity Through Pad,* m/s ¦ ¦ --- ¦ --- ¦ ¦ Corrugated cellulose, 100 mm thick ¦ 1.25 ¦ ¦ Corrugated cellulose, 150 mm thick ¦ 1.75 ¦ Table 7 Recommended Air Velocity Through Various Pad Materials *Speed may be increased by 25% where construction is limiting. Table 8 Recommended Water Flow and Sump Capacity for Vertically Mounted Cooling Pad Materials ¦ Pad Type and Thickness ¦ Minimum Water Rate per Linear Metre of Pad, L/s ¦ Minimum Sump Capacity per Unit Pad Area, L/m2 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Corrugated cellulose, 100 mm thick ¦ 0.10 ¦ 30 ¦ ¦ Corrugated cellulose, 150 mm thick ¦ 0.16 ¦ 40 ¦ may flow directly out the vent and not cool the opposite side of the greenhouse. Fog. In a direct-pressure atomizer, a high-pressure pump forces water at 5.5 to 7 MPa through a special fog nozzle. Fog is considered to be a water droplet smaller than 40 um in diameter. The direct- pressure atomizer generates droplets of35 �m or less. This requires a superior filter to minimize clogging of the very small nozzle orifices. A line of nozzles placed along the top of the vent opening can cool the entering air nearly to its wet-bulb temperature. Additional lines in the greenhouse continue to cool the air as it absorbs heat in the space. Fogging cools satisfactorily with less airflow than fan-and-pad systems, but the fan capacity must still be based on one air change per minute to ventilate the greenhouse when the cooler will be used without fog. 2019 ASHRAE Handbook- -HVAC Applications (SI) Other Environmental Controls Humidity Control. At various times during the year, humidity may need to be controlled in the greenhouse. When the humidity is too high at night, it can be reduced by adding heat and ventilating simultaneously. When the humidity is too low during the day, it can be increased by turning on a fog or mist nozzle. Winter Ventilation. During the winter, houses are normally closed tightly to conserve heat, but photosynthesis by the plants may lower the carbon dioxide level to such a point that it slows plant growth. Some ventilation helps maintain inside carbon dioxide lev- els. A normal rate of airflow for winter ventilation is 10 to 15 L/s per square metre of floor area. Air Circulation. Continuous air circulation within the green- house reduces still-air conditions that favor plant diseases. Recir- culating fans, heaters that blow air horizontally, and fans attached to polyethylene tubes are used to circulate air. The amount of recirculation has not been well defined, except that some studies have shown high air velocities (greater than 1.0 m/s) can harm plants or reduce growth. Insect Screening. Insect screening is used to cover vent inlets and outlets. These fine-mesh screens increase resistance to airflow, which must be considered when selecting ventilation fans. The screen manufacturer should provide static pressure data for its screens. The pressure drop through the screen can be reduced by framing out from the vent opening to increase the area ofthe screen. Carbon Dioxide Enrichment. Carbon dioxide is added in some greenhouse operations to increase growth and enhance yields. How- ever, CO2 enrichment is practical only when little or no ventilation is required for temperature control. Carbon dioxide can be gener- ated from solid CO2 (dry ice), bottled CO2, and misting carbonated water. Bulk or bottled CO2 gas is usually distributed through perfo- rated tubing placed near the plant canopy. Carbon dioxide from dry ice is distributed by passing greenhouse air through an enclosure containing dry ice. Air movement around the plant leafincreases the efficiency with which the plant absorbs available CO2. One study found an air speed of 0.5 m/s to be equivalent to a 50% enrichment in CO2 without forced air movement. Radiant Energy. Light is normally the limiting factor in green- house crop production during the winter. North of the 35th parallel (in the northern hemisphere), light levels are especially inadequate or marginal in fall, winter, and early spring. Artificial light sources, usually high-intensity discharge (HID) lamps, may be added to greenhouses to supplement low natural light levels. High-pressure sodium (HPS), metal halide (MH), low-pressure sodium (LPS), and, occasionally, mercury lamps coated with a color-improving phosphor are currently used. Because differing irradiance or illumi- nance ratios are emitted by the various lamp types, the incident radi- ation is best described as radiant flux density (W/m2) between 400 and 850 nm, or as photon flux density between 400 and 700 nm, rather than in photometric terms of lux. To assist in relating irradiance to more familiar illuminance val- ues, Table 9 shows constants for converting illuminance (lux) and photon flux density [�mol/(s · m2)] of HPS, MH, LPS, and other lamps to the irradiance (W/m2). Table 10 gives suggested values for irradiance at the top of the plant canopy, duration, and time of day for supplementing natural light levels for specific plants. HID lamps in luminaires developed specifically for greenhouse use are often placed in a horizontal position, which may decrease both the light output and the life of the lamp. These drawbacks may be balanced by improved horizontal and vertical uniformity as com- pared to industrial parabolic reflectors. Photoperiod Control. Artificial light sources are also used to lengthen the photoperiod during the short days of winter. Photope- riod control requires much lower light levels than those needed for Inc. ASHRAE, 2019 user. single for Licensed | {}
377ef46c-4d95-46b8-a964-cbf06d111cc3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Environmental Control for Animals and Plants 25.15 Table 9 Constants to Convert to W/m2 ¦ Light Source ¦ klx ¦ mol/(s·m2) ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 400 to 700 nm ¦ ¦ ¦ ¦ Incandescent (INC) ¦ 3.99 ¦ 0.20 ¦ ¦ Fluorescent cool white (FCW) ¦ 2.93 ¦ 0.22 ¦ ¦ Fluorescent warm white (FWW) ¦ 2.81 ¦ 0.21 ¦ ¦ Discharge clear mercury (HG) ¦ 2.62 ¦ 0.22 ¦ ¦ Metal halide (MH) ¦ 3.05 ¦ 0.22 ¦ ¦ High-pressure sodium (HPS) ¦ 2.45 ¦ 0.20 ¦ ¦ Low-pressure sodium (LPS) ¦ 1.92 ¦ 0.20 ¦ ¦ Daylight ¦ 4.02 ¦ 0.22 ¦ photosynthesis and growth. Photoperiod illuminance needs to be only 6 to 12 W/m2. The incandescent lamp is the most effective light source for this purpose because of its higher far-red component. Lamps such as 150 W (PS-30) silverneck lamps spaced 3 to 4 m on centers and 4 m above the plants provide a cost-effective system. Where a 4 m height is not practical, 60 W extended service lamps on 2 m centers are satisfactory. One method of photoperiod control is to interrupt the dark period by turning the lamps on at 2200 and off at 0200. The 4 h interruption, initially based on chrysanthemum response, induces a satisfactory long-day response in all photoperi- odically sensitive species. Many species, however, respond to inter- ruptions of 1 h or less. Demand charges can be reduced in large installations by operating some sections from 2000 to 2400 and oth- ers from 2400 to 0400. The biological response to these schedules, however, is much weaker than with the 2200 to 0200 schedule, so some varieties may flower prematurely. If the 4 h interruption period is used, it is not necessary to keep the light on throughout the interruption period. Photoperiod control of most plants can be accomplished by operating the lamps on light and dark cycles with 20% on times; for example, 12 s/min. The length ofthe dark period in the cycle is critical, and the system may fail if the dark period exceeds about 30 min. Demand charges can be reduced by alternate scheduling of the on times between houses or benches without reducing the biological effectiveness of the interruption. Plant displays in places such as showrooms or shopping malls require enough light for plant maintenance and a spectral distribu- tion that best shows the plants. Metal halide lamps, with or without incandescent highlighting, are often used for this purpose. Fluores- cent lamps, frequently of the special phosphor plant-growth type, enhance color rendition, but are more difficult to install in aestheti- cally pleasing designs. Design Conditions Plant requirements vary from season to season and during differ- ent stages of growth. Even different varieties of the same species of plant may vary in their requirements. State and local cooperative extension offices are a good source of specific information on design conditions affecting plants. These offices also provide cur- rent, area-specific information on greenhouse operations. Alternative Energy Sources and Energy Conservation Limited progress has been achieved in heating commercial greenhouses with solar energy. Collecting and storing the heat requires a volume at least one-half the volume of the entire green- house. Passive solar units work at certain times of the year and, in a few localities, year-round. If available, reject heat is a possible source of winter heat. Winter energy and solar (photovoltaic) sources are possible future energy sources for greenhouses, but the development of such systems is still in the research stage. Energy Conservation. A number of energy-saving measures (e.g., thermal curtains, double glazing, and perimeter insulation) Table 10 Suggested Radiant Energy, Duration, and Time of Day for Supplemental Lighting in Greenhouses ¦ ¦ ¦ Duration ¦ Duration ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Plant and Stage of Growth ¦ W/m2 ¦ Hours ¦ Time ¦ ¦ African violets early-flowering ¦ 12 to 24 ¦ 12 to 16 ¦ 0600-1800 0600-2200 ¦ ¦ Ageratum early-flowering ¦ 12 to 48 ¦ 24 ¦ ¦ ¦ Begonias- fibrous rooted branching and early-flowering ¦ 12 to 24 ¦ 24 ¦ ¦ ¦ Carnation branching and early-flowering ¦ 12 to 24 ¦ 16 ¦ 0800-2400 ¦ ¦ Chrysanthemums vegetable growth branching ¦ 12 to 24 ¦ 16 ¦ 0800-2400 ¦ ¦ and multiflowering ¦ 12 to 24 ¦ 8 ¦ 0800-1600 ¦ ¦ Cineraria seedling growth (four weeks) ¦ 6 to 12 ¦ 24 ¦ ¦ ¦ Cucumber rapid growth and early-flowering ¦ 12 to 24 ¦ 24 ¦ ¦ ¦ Eggplant early-fruiting ¦ 12 to 48 ¦ 24 ¦ ¦ ¦ Foliage plants (Philodendron, Schefflera) rapid growth ¦ 6 to 12 ¦ 24 ¦ ¦ ¦ Geranium branching and early-flowering ¦ 12 to 48 ¦ 24 ¦ ¦ ¦ Gloxinia ¦ 12 to 48 ¦ 16 ¦ 0800-2400 ¦ ¦ early-flowering ¦ 6 to 12 ¦ 24 ¦ ¦ ¦ Lettuce rapid growth ¦ 12 to 48 ¦ 24 ¦ ¦ ¦ Marigold early-flowering ¦ 12 to 48 ¦ 24 ¦ ¦ ¦ Impatiens-New Guinea branching and early-flowering ¦ 12 ¦ 16 ¦ 0800-2400 ¦ ¦ Impatiens-Sultana branching and early-flowering ¦ 12 to 24 ¦ 24 ¦ ¦ ¦ Juniper vegetative growth ¦ 12 to 48 ¦ 24 ¦ ¦ ¦ Pepper early-fruiting, compact growth ¦ 12 to 24 ¦ 24 ¦ ¦ ¦ Petunia branching and early-flowering ¦ 12 to 48 ¦ 24 ¦ ¦ ¦ Poinsettia- vegetative growth ¦ 12 ¦ 24 ¦ ¦ ¦ branching and multiflowering ¦ 12 to 24 ¦ 8 ¦ 0800-1600 ¦ ¦ Rhododendron vegetative growth (shearing tips) ¦ 12 ¦ 16 ¦ 0800-2400 ¦ ¦ Roses (hybrid teas, miniatures) early-flowering and rapid regrowth ¦ 12 to 48 ¦ 24 ¦ ¦ ¦ Salvia early-flowering ¦ 12 to 48 ¦ 24 ¦ ¦ ¦ Snapdragon early-flowering ¦ 12 to 48 ¦ 24 ¦ ¦ ¦ Streptocarpus early-flowering ¦ 12 ¦ 16 ¦ 0800-2400 ¦ ¦ Tomato rapid growth and early-flowering ¦ 12 to 24 ¦ 16 ¦ 0800-2400 ¦ ¦ Trees (deciduous) vegetative growth ¦ 6 ¦ 16 ¦ 1600-0800 ¦ ¦ Zinnia early-flowering ¦ 12 to 48 ¦ 24 ¦ ¦ Inc. ASHRAE, 2019 user. single for Licensed | {}
5c54243d-9128-483b-96e3-1ae9231465cf | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 25.16 2019 ASHRAE Handbook- -HVAC Applications (SI) have been retrofitted to existing greenhouses and incorporated into new construction. Sound maintenance is necessary to keep heating system efficiency at a maximum level. Automatic controls, such as thermostats, should be calibrated and cleaned at regular intervals, and heating-ventilation controls should interlock to avoid simultaneous operation. Boilers that can burn more than one type of fuel allow use of the most inexpensive fuel available. Modifications to Reduce Heat Loss Film covers that reduce heat loss are used widely in commercial greenhouses, particularly for growing foliage plants and other spe- cies that grow under low light levels. Irradiance (intensity) is reduced 10 to 15% per layer of plastic film. One or two layers of transparent 0.10 or 0.15 mm continuous- sheet plastic is stretched over the entire greenhouse (leaving some vents uncovered), or from the ridge to the sidewall ventilation open- ing. When two layers are used, (outdoor) air at a pressure of 50 to 60 Pa is introduced continuously between the layers offilm to main- tain the air space between them. When a single layer is used, an air space can be established by stretching the plastic over the glazing bars and fastening it around the edges, or a length of polyethylene tubing can be placed between the glass and the plastic and inflated (using outdoor air) to stretch the plastic sheet. Double-Glazing Rigid Plastic. Double-wall panels are manu- factured from acrylic and polycarbonate plastics, with walls sep- arated by about 10 mm. Panels are usually 1.2 m wide and 2.4 m or longer. Nearly all types of plastic panels have a high thermal expansion coefficient and require about 1% expansion space (10 mm/m). When a panel is new, light reduction is roughly 10 to 20%. Moisture accumulation between the walls of the panels must be avoided. Double-Glazing Glass. The framing of most older greenhouses must be modified or replaced to accept double glazing with glass. Light reduction is 10% more than with single glazing. Moisture and dust accumulation between glazings increases light loss. As with all types of double glazing, snow on the roof melts slowly and increases light loss. Snow may even accumulate enough to cause structural damage, especially in gutter-connected greenhouses. Silicone Sealants. Transparent silicone sealant in the glass over- laps of conventional greenhouses reduces infiltration and may produce heat savings of 5 to 10% in older structures. There is little change in light transmission. Precautions. The preceding methods reduce heat loss by reducing conduction and infiltration. They may also cause more condensation, higher relative humidity, lower carbon dioxide concentration, and an increase in ethylene and other pollutants. Combined with the reduced light levels, these factors may cause delayed crop production, elongated plants, soft plants, and vari- ous deformities and diseases, all of which reduce the marketable crop. Thermal Blankets. Thermal blankets are any flexible material that is pulled from gutter to gutter and end to end in a greenhouse, or around and over each bench, at night. Materials ranging from plastic film to heavy cloth, or laminated combinations, have suc- cessfully reduced heat losses by 25 to 35% overall. Tightness offit around edges and other obstruction are more important than the kind of material used. Some films are vaportight and retain mois- ture and gases. Others are porous and allow some gas exchange between the plants and the air outside the blanket. Opaque mate- rials can control crop day length when short days are part of the requirement for that crop. Condensation may drip onto and collect on the upper sides of some blanket materials to such an extent that they collapse. Inc. ASHRAE, 2019 user. single for Licensed Multiple-layer blankets, with two or more layers separated by air spaces, have been developed. One such design combines a porous- material blanket and a transparent film blanket; this design is used for summer shading. Another design has four layers of porous, alu- minum foil-covered cloths, with the layers separated by air. Thermal blankets may be opened and closed manually as well as automatically. The decision to open or close should be based on irra- diance level and whether it is snowing, rather than on time of day. Two difficulties with thermal blankets are the physical problems of installation and use in greenhouses with interior supporting col- umns, and the loss of space from shading by the blanket when it is not in use during the day. Other Recommendations. Although the foundation can be insulated, the insulating materials must be protected from moisture, and the foundation wall should be protected from freezing. All or most of the north wall can be insulated with opaque or reflective- surface materials. The insulation reduces the amount of diffuse light entering the greenhouse and, in cloudy climates, causes reduced crop growth near the north wall. Ventilation fan cabinets should be insulated, and fans not needed in winter should be sealed against air leaks. Efficient management and operation of existing facilities are the most cost-effective ways to reduce energy use. 2.2 PLANT GROWTH ENVIRONMENTAL FACILITIES Controlled-environment rooms (CERs), also called plant growth chambers, include all controlled or partially controlled environmental facilities for growing plants, except greenhouses. CERs are indoor facilities. Units with floor areas less than 5 m2 may be moveable with self-contained or attached refrigeration units. CERs usually have artificial light sources, provide control of temperature and, in some cases, control relative humidity and CO2 level. CERs are used to study all aspects of botany. Some growers use growing rooms to increase seedling growth rate, produce more uniform seedlings, and grow specialized, high-value crops. The main components of the CER are (1) an insulated room or an insu- lated box with an access door; (2) a heating and cooling mechanism with associated air-moving devices and controls; and (3) a lamp module at the top of the insulated box or room. CERs are similar to walk-in cold storage rooms, except for the lighting and larger refrig- eration system needed to handle heat produced by the lighting. Location The location for a CER must have space for the outer dimensions of the chamber, refrigeration equipment, ballast rack, and control panels. Additional space around the unit is necessary for servicing the various components of the system and, in some cases, for substrate, pots, nutrient solutions, and other paraphernalia associated with plant research. The location requires electricity, water, compressed air, and ventilation and exhaust air systems. For planning purposes, electrical densities of up to 1500 W/m2 of controlled environment space) are possible, or 1000 W/m2 of total space housing CERs. Construction and Materials Wall insulation should have a thermal conductance of less than 0.15 W/(m2 · K). Materials should resist corrosion and moisture. The interior wall covering should be metal, with a high-reflectance white paint, or specular aluminum with a reflectivity of at least 80%. Reflective films or similar materials can be used, but require peri- odic replacement. Floors and Drains Floors that are part of the CER should be corrosion-resistant. Tar or asphalt waterproofing materials and volatile caulking compounds should not be used because they are likely to release phytotoxic gases | {}
83dd2c3c-3bf7-4744-9253-89738994113d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Environmental Control for Animals and Plants 25.17 into the chamber atmosphere. The floor must have a drain to remove spilled water and nutrient solutions. The drains should be trapped and equipped with screens to catch plant and substrate debris. Plant Benches Three bench styles for supporting the pots and other plant containers are normally encountered in plant growth chambers: (1) stationary benches; (2) benches or shelves built in sections that are adjustable in height; and (3) plant trucks, carts, or dollies on casters, which are used to move plants between chambers, green- houses, and darkrooms. The bench supports containers filled with moist sand, soil, or other substrate, and is usually rated for loads of at least 240 kg/m2. The bench or truck top should be constructed of nonferrous, perforated metal, wire, or metal mesh to allow free passage of air around the plants and to let excess water drain from the containers to the floor and subsequently to the floor drain. Normally, benches, shelves, or truck tops are adjustable in height so that small plants can be placed close to the lamps and thus receive a greater amount of light. As the plants grow, the shelf or bench is lowered so that the tops of the plants continue to receive the original radiant flux density. Control Environmental chambers require complex controls to provide the following: · Automatic transfer from heating to cooling with 1 K or less dead zone and adjustable time delay. · Automatic daily switching of the temperature set point for differ- ent day and night temperatures (setback may be as much as 5 K). · Protection of sensors from radiation. Ideally, the sensors are located in a shielded, aspirated housing, but satisfactory perform- ance can be attained by placing them in the return air duct. · Control of the daily duration oflight and dark periods. Ideally, this control should be programmable to change the light period each day to simulate the natural progression of day length. Photoperiod control, however, is normally accomplished with mechanical time clocks, which must have a control interval of 5 min or less for sat- isfactory timing. · Protective control to prevent the chamber temperature from going more than a few degrees above or below the set point. Control should also prevent short-cycling of the refrigeration system, especially when condensers are remotely located. · Control of the CO2 level in enriched environment chambers. · Audible and visual alarms to alert personnel of malfunctions. · Maintenance of relative humidity to prescribed limits. Data loggers, recorders, or recording controllers are recom- mended for monitoring daily operation. Solid-state, microprocessor- based controls are widely used for programming, controlling, and monitoring the CER conditions. Host systems are also used to pro- gram and monitor larger numbers of units in a common facility, and most offer remote access functions. Host systems tend to be vendor- specific in their use and application. Heating, Air Conditioning, and Airflow When the lights are on, cooling will normally be required, and the heater will rarely be called on to operate. When the lights are off, however, both heating and cooling may be needed. Conventional refrigeration is generally used with some modification. Direct- expansion units usually operate with a hot-gas bypass to prevent numerous on/off cycles, and secondary coolant may use aqueous ethylene glycol rather than chilled water. Heat is usually provided by electric heaters, but other energy sources can be used, including hot gas from the refrigeration. The plant compartment is the heart of the growth chamber. The primary design objective, therefore, is to provide the most uniform, consistent, and regulated environmental conditions possible. Thus, airflow must be adequate to meet specified psychrometric condi- tions, but it is limited by the effects of high air speed on plant growth. As a rule, the average air speed in CERs is restricted to about 0.5 m/s. To meet the uniform conditions required by a CER, conditioned air is normally moved through the space from bottom to top, although some CERs use top-to-bottom airflow. There is no appar- ent difference in plant growth between horizontal, upward, or down- ward airflow when the speed is less than 0.9 m/s. Regardless of the method, a temperature gradient is certain to exist, and should be kept as small as possible. Uniform airflow is more important than the direction of flow; thus, selection of properly designed diffusers or plenums with perforations is essential for achieving it. The ducts or false sidewalls that direct air from the evaporator to the growing area should be small, but not so small that the noise increases appreciably more than acceptable building air duct noise. CER design should include some provision for cleaning the interior of the air ducts. Air-conditioning equipment for relatively standard chambers pro- vides temperatures that range from 7 to 35°C. Specialized CERs that require temperatures as low as -20°C need low-temperature refrig- eration equipment and devices to defrost the evaporator without increasing the growing area temperature. Other chambers that require temperatures as high as 45°C need high-temperature compo- nents. The air temperature in the growing area must be controlled with the least possible variation about the set point. Temperature variation about the set point can be held to 0.3 K using solid-state controls, but in older facilities, the variation is 0.5 to 1 K. The relative humidity in many CERs is simply an indicator of the existing psychrometric conditions and is usually between 50 and 80%, depending on the temperature. Relative humidity in the cham- ber can be increased by steam injection, misting, hot-water evapo- rators, and other conventional humidification methods. Steam injection causes the least temperature disturbance, and sprays or misting cause the greatest disturbance. Complete control of relative humidity requires dehumidification as well as humidification. A typical humidity control includes a cold evaporator or steam injection to adjust the chamber air dew point. The air is then condi- tioned to the desired dry-bulb temperature by electric heaters, a hot- gas bypass evaporator, or a temperature-controlled evaporator. A dew point lower than about 5°C cannot be obtained with a cold-plate dehumidifier because of icing. Dew points lower than 5°C usually require a chemical dehumidifier in addition to the cold evaporator. Lighting Environmental Chambers The type of light source and number of lamps used in CERs are determined by the desired plant response. Traditionally, cool-white fluorescent plus incandescent lamps that produce 10% of the fluo- rescent illuminance are used. Nearly all illumination data are based on either cool-white or warm-white fluorescent, plus incandescent lamps. A number of fluorescent lamps have special phosphors hypothesized to be the spectral requirements of the plant. Some of these lamps are used in CERs, but there is little data to suggest that they are superior to cool-white and warm-white lamps. In recent years, high-intensity discharge lamps have been installed in CERs, either to obtain very high radiant flux densities, or to reduce the electrical load while maintaining a light level equal to that produced by the less efficient fluorescent-incandescent systems. One method to design lighting for biological environments is to base light source output recommendations on photon flux density mol/(s· m2) between 400 and 700 nm, or, less frequently, as radi- ant flux density between 400 and 700 nm, or 400 and 850 nm. Rather than basing illuminance measurements on human vision, this allows comparisons between light sources as a function of plant Inc. ASHRAE, 2019 user. single for Licensed | {}
1dcd20da-e3a5-48e5-a780-513efb2e1739 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 25.18 2019 ASHRAE Handbook-HVAC Applications (SI) Table 11 Input Power Conversion of Light Sources ¦ Lamp Identification ¦ ¦ Total Input Power, W ¦ Radiation (400-700 nm), % ¦ Radiation (400-850 nm), % ¦ Other Radiation, % ¦ Conduction and Convection, % ¦ Ballast Loss, % ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Incandescent ¦ INC, 100A ¦ 100 ¦ 7 ¦ 15 ¦ 75 ¦ 10 ¦ 0 ¦ ¦ Fluorescent ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Cool white ¦ FCW ¦ 46 ¦ 21 ¦ 21 ¦ 32 ¦ 34 ¦ 13 ¦ ¦ Cool white ¦ FCW ¦ 225 ¦ 19 ¦ 19 ¦ 34 ¦ 35 ¦ 12 ¦ ¦ Warm white ¦ FWW ¦ 46 ¦ 20 ¦ 20 ¦ 32 ¦ 35 ¦ 13 ¦ ¦ Plant growth A ¦ PGA ¦ 46 ¦ 13 ¦ 13 ¦ 35 ¦ 39 ¦ 13 ¦ ¦ Plant growth B ¦ PGB ¦ 46 ¦ 15 ¦ 16 ¦ 34 ¦ 37 ¦ 13 ¦ ¦ Infrared ¦ FIR ¦ 46 ¦ 2 ¦ 9 ¦ 39 ¦ 39 ¦ 13 ¦ ¦ Discharge ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Clear mercury ¦ HG ¦ 440 ¦ 12 ¦ 13 ¦ 61 ¦ 17 ¦ 9 ¦ ¦ Mercury deluxe ¦ HG/DX ¦ 440 ¦ 13 ¦ 14 ¦ 59 ¦ 18 ¦ 9 ¦ ¦ Metal halide ¦ MH ¦ 460 ¦ 27 ¦ 30 ¦ 42 ¦ 15 ¦ 13 ¦ ¦ High-pressure sodium ¦ HPS ¦ 470 ¦ 26 ¦ 36 ¦ 36 ¦ 13 ¦ 15 ¦ ¦ Low-pressure sodium ¦ LPS ¦ 230 ¦ 27 ¦ 31 ¦ 25 ¦ 22 ¦ 22 ¦ Note: Conversion efficiency is for lamps without luminaires. Values compiled from manufacturers' data, published information, and unpublished test data by R. W. Thimijan. Table 12 Approximate Mounting Height and Spacing of Luminaires in Greenhouses ¦ ¦ Irradiation, W/m2 ¦ Irradiation, W/m2 ¦ Irradiation, W/m2 ¦ Irradiation, W/m2 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Lamp and Wattage ¦ 6 ¦ 12 ¦ 24 ¦ 48 ¦ ¦ ¦ Height and Spacing, m ¦ Height and Spacing, m ¦ Height and Spacing, m ¦ Height and Spacing, m ¦ ¦ HPS (400 W) ¦ 3.0 ¦ 2.3 ¦ 1.6 ¦ 1.0 ¦ ¦ LPS (180 W) ¦ 2.4 ¦ 1.7 ¦ 1.2 ¦ 0.8 ¦ ¦ MH (400 W) ¦ 2.7 ¦ 2.0 ¦ 1.4 ¦ 0.9 ¦ photosynthetic potential. Table 9 shows constants for converting various measurement units to W/m2. However, instruments that measure the 400 to 850 nm spectral range are generally not avail- able, and some controversy exists about the effectiveness of 400 to 850 nm as compared to the 400 to 700 nm range in photosynthesis. The power conversion of various light sources is listed in Table 11. The design requirements for plant growth lighting differ greatly from those for vision lighting. Plant growth lighting requires a greater degree of horizontal uniformity and, usually, higher light levels than vision lighting. In addition, plant growth lighting should have as much vertical uniformity as possible (a factor rarely import- ant in vision lighting). Horizontal and vertical uniformity are much easier to attain with linear or broad sources, such as fluorescent lamps, than with point sources, such as HID lamps. Tables 12 and 13 show the type and number of lamps, mounting height, and spacing required to obtain several levels ofincident energy. Because the data were taken directly under lamps with no reflecting wall surfaces nearby, the incident energy is perhaps one-half of what the plants would receive if the lamps had been placed in a small chamber with highly reflective walls. Extended-life incandescents lower lamp replacement require- ments. These lamps have lower lumen output, but are nearly equiv- alent in the red portion of the spectrum. For safety, porcelain lamp holders and heat-resistant lamp wiring should be used. Lamps used for CER lighting include fluorescent lamps (usually 1500 mA), 250, 400, and occasionally 1000 W HPS and MH lamps, 180 W LPS lamps, and various sizes of incandescent lamps. In many installations, the abnormally short life of incandescent lamps is caused by vibration from the lamp loft ventilation or from cooling fans. Increased incandescent lamp life under these conditions can be attained by using lamps constructed with a C9 filament. Energy-saving lamps have approximately equal or slightly lower irradiance per input watt. Because the irradiance per lamp is lower, there is no advantage to using these lamps, except in tasks that can be accomplished with low light levels. Light output of all lamps declines with use, except perhaps for low-pressure sodium (LPS) lamps, which appear to maintain approximately constant output but require an increase in input power during use. Fluorescent and metal halide designs should be based on 80% of the initial light level. Most CER lighting systems have difficulty maintaining a relatively constant light level over considerable peri- ods of time. Combinations of MH and HPS lamps compound the problem, because the lumen depreciation of the two light sources is significantly different. Thus, over time, the spectral energy distribu- tion at plant level shifts toward the HPS. Lumen output can be main- tained in two ways: (1) individual lamps, or a combination of lamps, can be switched off initially and activated as the lumen output decreases; and (2) the oldest 25 to 33% of the lamps can be replaced periodically. Solid-state dimmer systems are commercially available only for low-wattage fluorescent lamps and for mercury lamps. To maintain a constant distance from plant to light source, light fixtures in many CERs are mounted on movable, counterbalanced light banks. This design requirement precludes separation of the lamps from the plant chamber. Large rooms, especially those constructed as an integral part of the building and retrofitted as CERs, rarely separate the lamps from the growing area with a transparent barrier. Rooms designed as CERs (at the time a building is constructed) and freestanding rooms or chambers usually separate the lamp from the growing area with a barrier of glass or rigid plastic. Light output from fluorescent lamps is a function of the temperature of the lamp. Thus, the barrier serves a twofold purpose: (1) to maintain optimum lamp tempera- ture when the growing area temperature is higher or lower than opti- mum, and (2) to reduce the thermal radiation entering the growing area. Fluorescent lamps should operate in an ambient temperature and airflow environment that maintains the tube wall temperature at 40°C. Under most conditions, the light output of HID lamps is not affected by ambient temperature. The heat must be removed, how- ever, to prevent high thermal radiation from causing adverse biolog- ical effects (Figure 1 1). Transparent glass barriers remove nearly all radiation from about 350 to 2500 nm. Rigid plastic is less effective than glass; however, the lower mass and lower breakage risk of plastic makes it a popular barrier material. Ultraviolet is also screened by both glass and plastic (more by plastic). Special UV -transmitting plastic (which degrades rapidly) can be obtained if the biological process requires UV light. When irradiance is very high, especially from HID lamps or large numbers of incandescent lamps or both, rigid plastic can soften from the heat and fall from the supports. Furthermore, very high irradiance and the resulting high temperatures can darken plas- tic, which can increase the absorptivity and temperature enough to Inc. ASHRAE, 2019 user. single for Licensed | {}
f9d4f98b-04d5-4ca1-a7ad-c27de29c383d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Environmental Control for Animals and Plants 25.19 Table 13 Height and Spacing of Luminaires ¦ ¦ Radiant Flux Density, W/m2 ¦ Radiant Flux Density, W/m2 ¦ Radiant Flux Density, W/m2 ¦ Radiant Flux Density, W/m2 ¦ Radiant Flux Density, W/m2 ¦ Radiant Flux Density, W/m2 ¦ Radiant Flux Density, W/m2 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Light Source ¦ 0.3 ¦ 0.9 ¦ 3 ¦ 9 ¦ 18 ¦ 24 ¦ 50 ¦ ¦ Fluorescent: Cool White ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 40 W single 1.2 m lamp, 3.2 klm ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Radiant power, W/m2, 400 to 700 nm ¦ 0.3 ¦ 0.9 ¦ 2.9 ¦ 8.8 ¦ ¦ ¦ ¦ ¦ Illumination, klx ¦ 0.10 ¦ 0.30 ¦ 1.0 ¦ 3.0 ¦ ¦ ¦ ¦ ¦ Lamps per 10 m2 ¦ 1.1 ¦ 3.3 ¦ 11 ¦ 33 ¦ ¦ ¦ ¦ ¦ Distance from plants, m ¦ 2.9 ¦ 1.7 ¦ 0.92 ¦ 0.53 ¦ ¦ ¦ ¦ ¦ 40 W 2-lamp fixtures (1.2 m), 6.4 klm ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Radiant power, W/m2, 400 to 700 nm ¦ 0.3 ¦ 0.9 ¦ 2.9 ¦ 8.8 ¦ ¦ ¦ ¦ ¦ Illumination, klx ¦ 0.10 ¦ 0.30 ¦ 1.0 ¦ 3.0 ¦ ¦ ¦ ¦ ¦ Fixtures per 10 m2 ¦ 0.6 ¦ 1.7 ¦ 5.5 ¦ 16.7 ¦ ¦ ¦ ¦ ¦ Distance from plants, m ¦ 4.1 ¦ 2.4 ¦ 1.3 ¦ 0.75 ¦ ¦ ¦ ¦ ¦ 215 W, 2-2.4 m lamps, 31.4 klm ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Radiant power, W/m2, 400 to 700 nm ¦ 0.3 ¦ 0.9 ¦ 2.9 ¦ 8.8 ¦ 17.6 ¦ 23.5 ¦ 49.0 ¦ ¦ Illumination, klx ¦ 0.10 ¦ 0.30 ¦ 1.0 ¦ 3.0 ¦ 6.0 ¦ 8.0 ¦ 16.7 ¦ ¦ Lamps per 10 m2 ¦ 0.1+ ¦ 0.4 ¦ 1.2 ¦ 3.6 ¦ 7.1 ¦ 9.3 ¦ 20 ¦ ¦ Distance from plants, m ¦ 8.8 ¦ 5.1 ¦ 2.8 ¦ 1.6 ¦ 1.1 ¦ 1.0 ¦ 0.7 ¦ ¦ High-Intensity Discharge ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Mercury-1 400 W parabolic reflector ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Radiant power, W/m2, 400 to 700 nm ¦ 0.28 ¦ 0.84 ¦ 2.80 ¦ 8.39 ¦ 16.8 ¦ 22.4 ¦ 46.6 ¦ ¦ Illumination, klx ¦ 0.1 ¦ 0.32 ¦ 1.1 ¦ 3.2 ¦ 6.4 ¦ 8.6 ¦ 18.0 ¦ ¦ Lamps per 10 m2 ¦ 0.2 ¦ 0.5 ¦ 1.6 ¦ 4.8 ¦ 9.3 ¦ 13.0 ¦ 27 ¦ ¦ Distance from plants, m ¦ 7.6 ¦ 4.4 ¦ 2.4 ¦ 1.4 ¦ 1.0 ¦ 0.8 ¦ 0.6 ¦ ¦ Metal halide-1 400 W ¦ ¦ ¦ ¦ 8.03 ¦ ¦ ¦ ¦ ¦ Radiant power, W/m2, 400 to 700 nm ¦ 0.77 ¦ 0.80 ¦ 2.68 ¦ ¦ 16.1 ¦ 21.4 ¦ 44.6 ¦ ¦ Illumination, klx ¦ 0.09 ¦ 0.26 ¦ 0.88 ¦ 2.6 ¦ 5.3 ¦ 7.0 ¦ 15.0 ¦ ¦ Lamps per 10 m2 ¦ 0.09 ¦ 0.2 ¦ 0.7 ¦ 2.2 ¦ 4.4 ¦ 5.8 ¦ 12.0 ¦ ¦ Distance from plants, m ¦ 11.3 ¦ 6.5 ¦ 3.6 ¦ 2.1 ¦ 1.5 ¦ 1.3 ¦ 0.87 ¦ ¦ High-pressure sodium 400 W ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Radiant power, W/m2, 400 to 700 nm ¦ 0.22 ¦ 0.65 ¦ 2.18 ¦ 6.52 ¦ 13.0 ¦ 17.4 ¦ 36.2 ¦ ¦ Illumination, klx ¦ 0.09 ¦ 0.27 ¦ 0.89 ¦ 2.7 ¦ 5.3 ¦ 7.1 ¦ 15.0 ¦ ¦ Lamps per 10 m2 ¦ 0.05 ¦ 0.14 ¦ 0.5 ¦ 1.4 ¦ 2.8 ¦ 3.6 ¦ 7.6 ¦ ¦ Distance from plants, m ¦ 14.2 ¦ 8.2 ¦ 4.5 ¦ 2.6 ¦ 1.8 ¦ 1.6 ¦ 1.1 ¦ ¦ Low-pressure sodium 180 W ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Radiant power, W/m2, 400 to 700 nm ¦ 0.26 ¦ 0.79 ¦ 2.64 ¦ 7.93 ¦ 15.9 ¦ 21.1 ¦ 44.0 ¦ ¦ Illumination, klx ¦ 0.14 ¦ 0.41 ¦ 1.4 ¦ 4.1 ¦ 8.3 ¦ 11.0 ¦ 23.0 ¦ ¦ Lamps per 10 m2 ¦ 0.08 ¦ 0.24 ¦ 0.8 ¦ 2.4 ¦ 4.9 ¦ 6.5 ¦ 13.6 ¦ ¦ Distance from plants, m ¦ 10.7 ¦ 6.2 ¦ 3.4 ¦ 2.0 ¦ 1.4 ¦ 1.2 ¦ 0.83 ¦ ¦ Incandescent ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Incandescent 100 W Radiant power, W/m2, 400 to 700 nm ¦ 0.14 ¦ 0.41 ¦ ¦ ¦ ¦ 11.0 ¦ 23.0 ¦ ¦ Illumination, klx ¦ 0.033 ¦ 0.10 ¦ 1.38 ¦ 4.14 ¦ 8.28 2.0 ¦ 2.7 ¦ 5.6 ¦ ¦ ¦ ¦ ¦ 0.33 ¦ 1.0 ¦ ¦ ¦ ¦ ¦ Lamps per 10 m2 ¦ 0.5 ¦ 1.6 ¦ 5.2 ¦ 15.8 ¦ 32 ¦ 42 ¦ 87 ¦ ¦ Distance from plants, m ¦ 4.2 ¦ 4.2 ¦ 1.3 ¦ 0.77 ¦ 0.54 ¦ 0.47 ¦ 0.33 ¦ ¦ Incandescent 150 W flood ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Radiant power, W/m2, 400 to 700 nm ¦ ¦ ¦ ¦ 4.14 ¦ 8.28 ¦ 11.0 ¦ 23.0 ¦ ¦ ¦ 0.14 0.033 ¦ 0.41 ¦ 1.38 ¦ ¦ 2.0 ¦ 2.6 ¦ 5.5 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Illumination, klx ¦ ¦ 0.098 ¦ 0.33 ¦ 1.0 ¦ ¦ 26 ¦ 54 ¦ ¦ Lamps per 10 m2 Distance from plants, m ¦ 0.3 5.4 ¦ 0.9 3.1 ¦ 3.3 1.7 ¦ 9.3 1.0 ¦ 19.5 0.7 ¦ 0.6 ¦ 0.4 ¦ ¦ Incandescent-Hg 160 W Radiant power, W/m2, 400 to 700 nm ¦ 0.14 ¦ 0.41 ¦ 1.38 ¦ 4.14 ¦ 8.28 ¦ 11.0 ¦ 23.0 ¦ ¦ Illumination, klx Lamps per 10 m2 ¦ 0.050 0.7 ¦ 0.15 2.0 ¦ 0.50 6.9 ¦ 1.5 20.4 ¦ 3.0 42 ¦ 4.0 56 ¦ 8.3 111 ¦ ¦ Distance from plants, m Sunlight ¦ 3.7 ¦ 2.1 ¦ 1.2 ¦ 0.67 ¦ 0.47 ¦ 0.41 ¦ 0.28 ¦ ¦ Radiant power, W/10 m2 ¦ 0.22 ¦ 0.66 ¦ 2.21 0.54 ¦ 6.65 1.6 ¦ 13.3 3.2 ¦ 17.7 4.3 ¦ 76.9 8.9 ¦ ¦ Illumination, klx ¦ 0.054 ¦ 0.16 ¦ ¦ ¦ ¦ ¦ ¦ Inc. ASHRAE, 2019 user. single for Licensed | {}
a2f10f10-32e9-4846-bb4f-7c919ab854cc | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 25.20 ![image](/image/placeholder) LAMPS GLASS OR PLASTIC TUBES TO BE ACCESSIBLE PLANT RACK GROWTH CABINET - LIGHTS AIR-COOLED ![image](/image/placeholder) REFRIG. COILS DRIP TRAY 」 THERMOSTAT FOR OVERHEAT THERMOSTAT REFRIG. UNIT PLANT RACK GROWTH CHAMBER - LIGHTS COOLED BY REFRIGERATION Fig. 11 Cooling Lamps in Growth Chambers destroy it. Under these conditions, heat-resistant glass may be nec- essary. The lamp compartment and barrier absolutely require posi- tive ventilation regardless of the light source, and the lamp loft should have limit switches to shut down the lamps ifthe temperature rises to a critical level. Phytotrons A phytotron is a botanical laboratory comprising a series of chambers reproducing any condition of temperature, humidity, illumination, or other plant growth factor. They are typically found in plant-based research buildings. These facilities require substan- tial electrical and mechanical systems to generate light required for plant growth as well as to remove heat generated by lights and CER cooling systems. Electrical Requirements. If the exact number and size of units is unknown, an electrical consumption of2 kW/m2 may be assumed for lighting input to the CERs. If the CERs have a built-in refrigeration system, the compressor input is typically 80% oflight- ing input, because the units are designed to maintain the chamber at 10°C with lights on, creating a high latent load on the compressor at an inefficient operating point. Remote condensing units and remote 2019 ASHRAE Handbook- -HVAC Applications (SI) air-cooled condensers require a separate electrical feed and inter- connecting control wiring. Heat Rejection. Most of the electrical input to the CERs is con- verted to heat. The heat rejection system must be able to remove that heat from the phytotron; this can be done in a number of ways. If the CERs are primarily self-contained air-cooled units, the room can be ventilated at a rate that maintains acceptable working conditions in the space (see Chapter 14). Because of the high venti- lation rates needed, ensure that air returned to the space is properly filtered to limit the introduction of dust, pollen, insects, and bacteria from the outdoors. Self-contained CERs with water-cooled condensing units typi- cally use a condenser water loop connected to a cooling tower or fluid cooler to reject heat. Chapter 13 of the 2016 ASHRAE Hand- book-HVAC Systems and Equipment describes selection and design of these systems. Because phytotron facilities operate all year, operation of fluid coolers and cooling towers at ambient tem- peratures below freezing in cold climates must be considered. Sed- iment must also be removed from the condenser water, because the condenser on the CER is a relatively low-velocity point in the loop and will plug up with these solids. Locations of remote condensing units or remote air-cooled con- densers should be easily accessible, because they require servicing at all times of the year. Ensure good airflow around all air-cooled condensers so that discharge air from one unit is not reentrained into adjacent units. Locate equipment away from laboratory exhaust sys- tems that could accelerate corrosion of metal on the units. Refriger- ant piping must be carefully designed, sized, and installed to ensure proper oil return and long-term operation of the compressors. Chap- ter 1 of the 2018 ASHRAE Handbook-Refrigeration details these requirements. Central chilled water can be used for the CERs. The primary consideration is the chilled-water temperature to be provided to each unit. In practice, most CERs operate at internal temperatures between 20 and 25°C when lights are on. As a result, standard chilled-water supply temperatures of 7°C can be used successfully. When lights are off, temperatures of 10°C can be achieved using the same chilled-water temperature. Chambers that require cooler daytime temperatures can use water-cooled condensing units and reject their heat to the chilled-water loop. Some phytotrons use chilled-water supply temperatures of-10°C, but with a high failure rate on the compressors because of low suction temperatures and poor oil return. Energy Conservation. Because of CERs' very high energy con- sumption and the predictable day/night cycle of the lighting load, consider balancing the units' schedule to limit electrical demand. Most plants require a 12 to 16 h daily photoperiod. By adjusting the day/night schedule, it is possible to reduce the phytotron' s electrical demand by up to 25%. Chilled-water CERs can have the lowest total energy consumption because of the economy of scale available by using large-capacity chillers versus small compressors. Large laboratory facilities can reject heat from the phytotron to preheat laboratory makeup air. In cold climates, chilled water can be produced without mechanical cooling at ambient temperatures below -2°C. If exposing chilled water to ambient air that could be below freezing, use an appropriate concentration of suitable antifreeze. Condenser water can also be used to preheat fresh air or, because of its higher temperature, other process loads, such as domestic hot water. Operating Considerations. CERs with self-contained com- pressors generate noise. When a large number of units are placed in a room, consideration should be given to attenuating this sound. Chilled-water and remote-condensing-unit CERs provide the quietest environment for workers, because the compressors are remotely located. The total installed cost of these systems may be Inc. ASHRAE, 2019 user. single for Licensed | {}
b2694214-4d4d-4b89-ae0d-7c5c0987dcc8 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Environmental Control for Animals and Plants 25.21 higher because of the extra cost to remotely locate and energize the cooling systems. Plants require CO2 to grow. Many CERs in phytotrons have a central exhaust system to exhaust any chemicals used inside the chambers and to pull in a constant supply of air. Because the units are under a slight negative pressure, makeup air entering the unit must be filtered to limit uncontrolled spread of pollen, insect pests, and bacteria. The flow rate from units depends on the type of crop being grown. A normal rate of ventilation is 10 to 15 L/s per square metre of plant growth area. Water is required for humidification, plant watering, and clean- ing. This often means that three totally separate systems are used. High-purity water is often available in laboratory buildings, and can be used to directly humidify the chambers without introducing waterborne minerals into the chamber. Water for plants should be tempered to avoid root shock. A tempered-water loop with provi- sion for introducing chemical fertilizer, supplied to designated hose stations in the phytotron, is common in larger installations, but nor- mal municipal water supplies are all that is required. Cleaning of these areas is important. CERs require drainage of cooling coil condensate and plant over- watering. It is important to provide good drainage near the units without excess use of drain lines running exposed across the floor. Similarly, any piping or ducts that operate below the room design dew-point temperature should be insulated to prevent condensation on those lines. These puddles of water are prime breeding grounds for plant pests, and could cause slip hazards for staff. Keeping the phytotron clean is important for plants' health. Phy- totrons typically have separate potting areas and harvest rooms, both of which generate a lot of dust and dirt. Potting areas must remain sanitary to minimize contamination of seedlings and plantlets. In harvest rooms, mature plants may host insects that can damage young plants. Ventilation systems should keep harvest rooms at neg- ative pressure relative to the cleaner potting areas and phytotron. Genetically modified plants must be autoclaved once the plant is harvested. Provision should be made for an autoclave next to the harvest room, with a supply of steam or electricity. Odors and steam from the autoclave should be exhausted out of the building. 2.3 OTHER PLANT ENVIRONMENTAL FACILITIES Plants may be held or processed in warehouse-type structures prior to sale or use in interior landscaping. Required temperatures range from slightly above freezing for cold storage ofroot stock and cut flowers, to 20 to 25°C for maintaining growing plants, usually in pots or containers. Provision must be made for venting fresh air to avoid CO2 depletion. Light duration must be controlled by a time clock. When they are in use, lamps and ballasts produce almost all the heat required in an insulated building. Ventilation and cooling may be required. Illumination levels depend on plant requirements. Table 14 shows approximate mounting heights for two levels of illumination. Luminaires mounted on chains permit lamp height to be adjusted to compensate for varying plant height. The main concerns for interior landscape lighting are how it renders the color of plants, people, and furnishings, as well as how it meets the minimum irradiation requirements of plants. The temperature required for human occupancy is normally acceptable for plants. Light level and duration determine the types of plants that can be grown or maintained. Plants grow when exposed to higher levels, but do not survive below the suggested minimum. Plants may be grouped into three levels based on the following of irradiances: Low (survival): A minimum light level of0.75 W/m2 and a pre- ferred level of 3 W/m2 irradiance for 8 to 12 h daily. Table 14 Mounting Height for Luminaires in Storage Areas ¦ ¦ Survival = 3 W/m2 ¦ Survival = 3 W/m2 ¦ Maintenance = 9 W/m2 ¦ Maintenance = 9 W/m2 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ Distance, m ¦ lux ¦ Distance, m ¦ lux ¦ ¦ Fluorescent (F) ¦ ¦ ¦ ¦ ¦ ¦ FCW two 40 W ¦ 0.9 ¦ 1000 ¦ 0.75 ¦ 3000 ¦ ¦ FWW ¦ 0.9 ¦ 1000 ¦ 0.75 ¦ 3000 ¦ ¦ FCW two 215 W ¦ 2.8 ¦ 1000 ¦ 1.6 ¦ 3000 ¦ ¦ Discharge (HID) ¦ ¦ ¦ ¦ ¦ ¦ MH 400 W ¦ 3.3 ¦ 800 ¦ 2.0 ¦ 2400 ¦ ¦ HPS 400 W ¦ 4.5 ¦ 800 ¦ 2.5 ¦ 2400 ¦ ¦ LPS 180 W ¦ 3.4 ¦ 1300 ¦ 1.2 ¦ 4000 ¦ ¦ Incandescent (INC) ¦ ¦ ¦ ¦ ¦ ¦ INC 160 W ¦ 1.3 ¦ 350 ¦ 0.3 ¦ 1000 ¦ ¦ INC-HG 160 W ¦ 1.2 ¦ 500 ¦ 1.6 ¦ 1500 ¦ ¦ DL ¦ ¦ 500 ¦ ¦ 1500 ¦ Medium (maintenance): A minimum of3 W/m2 and a preferred level of9 W/m2 irradiance for 8 to 12 h daily. High (propagation): A minimum of 9 W/m2 and a preferred level of 24 W/m2 irradiance for 8 to 12 h daily. Fluorescent (warm-white), metal halide, or incandescent lighting is usually chosen for public places. Table 13 lists the irradiance of various light sources. REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. AGCIH. 1998. Industrial ventilation: A manual of recommended practice, 23rd ed. American Conference of Governmental Industrial Hygienists, Cincinnati, OH. ASAE. 2003. Guidelines for use of thermal insulation in agricultural build- ings. ANSI/ASAE Standard S401.2. American Society of Agricultural Engineers (now American Society of Agricultural and Biological Engi- neers), St. Joseph, MI. ASTM. 2005. Test method for thermal performance of building materials and envelope assemblies by means of a hot box apparatus. Standard C1363-05. American Society for Testing and Materials, West Consho- hocken, PA. Barber, E.M., J.A. Dosman, C.S. Rhodes, G.I. Christison, and T.S. Hurst. 1993. Carbon dioxide as an indicator of air quality in swine buildings. Proceedings of Third International Livestock Environment Symposium. American Society of Agricultural Engineers (now American Society of Agricultural and Biological Engineers), St. Joseph, MI. BESS Lab. 1997. Agricultural ventilation fans-Performance and efficien- cies. Bioenvironmental and Structural Systems Laboratory, Department of Agricultural Engineering, University ofIllinois at Urbana-Champaign. Bond, T.E., H.H. Heitman, Jr., and C.F. Kelly. 1965. Effect of increased air velocities on heat and moisture loss and growth of swine. Transactions of ASAE 8(2):167-169, 174. Christianson, L.L., and R.L. Fehr. 1983. Ventilation- Energy and econom- ics. In Ventilation of agricultural structures, pp. 335-349. American Society of Agricultural Engineers (now American Society of Agricul- tural and Biological Engineers), St. Joseph, MI. Clough, G. 1982. Environmental effects on animals used in biomedical research. Biological Reviews 57:487-523. Donham, J.K., P. Haglind, Y. Peterson, R. Rylander, and L. Belin. 1989. Environmental and health studies of workers in Swedish swine confine- ment buildings. British Journal ofIndustrial Medicine 40:31-37. Gordon, C.J., P. Becker, and J.S. Ali. 1997. Behavioural thermoregulatory responses ofsingle- and group-housed mice. Neurotoxicology Division, National Health and Environmental Effects Research Laboratory, U.S. Environmental Protection Agency, Research Triangle Park, NC. Inc. ASHRAE, 2019 user. single for Licensed | {}
42a948f3-d15f-4963-b8c1-ccf5aab48204 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 25.22 2019 ASHRAE Handbook- -HVAC Applications (SI) Hahn, G.L. 1985. Management and housing of farm animals in hot environ- ments. In Stress physiology in livestock, vol. II, pp. 151-176. M. Yousef, ed. CRC Press, Boca Raton, FL. Hasenau, J.J., R.B. Baggs, and A.L. Kraus. 1993. Microenvironments in cages using BALB/c and CD-1 mice. Contemporary Topics 32(1):11-16. Hellickson, M.A., and J.N. Walker, eds. 1983. Ventilation of agricultural structures. ASAE Monograph 6. American Society of Agricultural Engi- neers (now American Society of Agricultural and Biological Engineers), St. Joseph, MI. ILAR. 1996. Guide for the care and use of laboratory animals. National Institutes of Health, Bethesda, MD. Lindsey, J.R., M. W. Conner, and H.J. Baker. 1978. Physical, chemical and microbial factors affecting biologic response. In Laboratory Animal Housing, pp. 31-43. Institute of Laboratory Animal Resources, National Academy of Sciences, Washington, D.C. Maghirang, R.G., G.L. Riskowski, L.L. Christianson, and P.C. Harrison. 1995. Development of ventilation rates and design information for labo- ratory animal facilities Part 1 field study. ASHRAE Transactions 101 (2):208-218. McPherson, C. 1975. Why be concerned about the ventilation requirements of experimental animals. ASHRAE Transactions 81(2):539-541. Memarzadeh, F. 1998. Design handbook on animal researchfacilities using static microisolators, vols. I and II. National Institutes of Health. Bethesda, MD. Moreland, A.F. 1975. Characteristics of the research animal bioenviron- ment. ASHRAE Transactions 81(2):542-548. Mount, L.E., and I.B. Start. 1980. A note on the effects of forced air move- ment and environmental temperature on weight gain in the pig after weaning. Animal Production 30(2):295. MWPS. 1989. Natural ventilating systemsfor livestock housing and heating. MidWest Plan Service, Ames, IA. MWPS. 1990a. Cooling and tempering air for livestock housing. MidWest Plan Service, Ames, IA. MWPS. 1990b. Mechanical ventilating systems for livestock housing. MidWest Plan Service, Ames, IA. Ni, J., A.J. Heber, T.T. Lim, R.K. Duggirala, B.L. Haymore, and C.A. Diehl. 1998a. Ammonia emission from a tunnel-ventilated swine finishing building. ASAE Paper 984051. American Society of Agricultural Engineers (now American Society of Agricultural and Biological Engi- neers), St. Joseph, MI. Ni, J., A.J. Heber, T.T. Lim, R.K. Duggirala, B.L. Haymore, and C.A. Diehl. 1998b. Emissions of hydrogen sulfide from a mechanically-ventilated swine grow-finish unit. ASAE Paper 984050. American Society of Agricultural Engineers (now American Society of Agricultural and Bio- logical Engineers), St. Joseph, MI. Person, H.L., L.D. Jacobson, and K.A. Jordan. 1979. Effect of dirt, louvers and other attachments on fan performance. Transactions ofASAE 22(3): 612-616. Riskowski, G.L., and D.S. Bundy. 1988. Effects of air velocity and tempera- ture on weanling pigs. Livestock environment III: Proceedings of the Third International Livestock Environment Symposium. American Soci- ety of Agricultural Engineers (now American Society ofAgricultural and Biological Engineers), St. Joseph, MI. Riskowski, G.L., S.E. Ford, and K.O. Mankell. 1998. Laboratory measure- ments of wind effects on ridge vent performance. ASHRAE Transactions 104(1). Riskowski, G.L., R.G. Maghirang, and W. Wang. 1996. Development of ventilation rates and design information for laboratory animal facili- ties-Part 2 laboratory tests. ASHRAE Transactions 102(2):195-209. Weiss, J., G.T. Taylor, and W. Nicklas. 1991. Ammonia concentrations in laboratory rat cages under various housing conditions. American Asso- ciation for Laboratory Animal Science, Cordova, TN. Zhang, Y. 1994. Swine building ventilation. Prairie Swine Centre, Saska- toon, Saskatchewan, Canada. Zhang, Y., and E.M. Barber. 1995. Air leakage and ventilation effectiveness for confinement livestock housing. Transactions of ASAE 38(5):1501- 1504. Zhang, Y., L.L. Christianson, G.L. Riskowski, B. Zhang, G. Taylor, H. W. Gonyou, and P.C. Harrison. 1992. A survey on laboratory rat environ- ments. ASHRAE Transactions 98(2):247-253. BIBLIOGRAPHY ANIMALS Handbooks and Proceedings Albright, L.D. 1990. Environment control for animals and plants, with computer applications. American Society of Agricultural Engineers (now American Society of Agricultural and Biological Engineers), St. Joseph, MI. ASAE. 1982. Dairy housing II: Second National Dairy Housing Conference Proceedings. American Society of Agricultural Engineers (now Ameri- can Society of Agricultural and Biological Engineers), St. Joseph, MI. ASAE. 1982. Livestock environment II: Second International Livestock Environment Symposium. American Society of Agricultural Engineers (now American Society of Agricultural and Biological Engineers), St. Joseph, MI. ASAE. 1988. Livestock environment III: Proceedings of the Third Inter- national Livestock Environment Symposium. American Society of Agri- cultural Engineers (now American Society of Agricultural and Biological Engineers), St. Joseph, MI. ASAE. 1993. Livestock environment IV: Proceedings ofthe Fourth Interna- tional Livestock Environment Symposium. American Society of Agricul- tural Engineers (now American Society of Agricultural and Biological Engineers), St. Joseph, MI. ASAE. 1993. Design of ventilation systems for livestock and poultry shel- ters. Standard EP270.5. American Society of Agricultural Engineers (now American Society of Agricultural and Biological Engineers), St. Joseph, MI. Curtis, S.E. 1983. Environmental management in animal agriculture. Iowa State University Press, Ames. Curtis, S.E., ed. 1988. Guide for the care and use of agricultural animals in agricultural research and teaching. Consortium for Developing a Guide for the Care and Use of Agricultural Animals in Agricultural Research and Teaching, Champaign, IL. HEW. 1978. Guide for the care and use of laboratory animals. Publication (NIH)78-23. U.S. Department of Health, Education and Welfare, Wash- ington, D.C. Rechcigl, M., Jr., ed. 1982. Handbook of agricultural productivity, vol. II, Animal productivity. CRC Press, Boca Raton, FL. Straub, H.E. 1989. Building systems: Room air and air contaminant distri- bution. ASHRAE. Air Cooling Canton, G.H., D.E. Buffington, and R.J. Collier. 1982. Inspired-air cooling for dairy cows. Transactions ofASAE 25(3):730-734. Hahn, G.L., and D.D. Osburn. 1969. Feasibility of summer environmental control for dairy cattle based on expected production losses. Trans- actions of ASAE 12(4):448-451. Hahn, G.L., and D.D. Osburn. 1970. Feasibility of evaporative cooling for dairy cattle based on expected production losses. Transactions ofASAE 12(3):289-291. Heard, L., D. Froelich, L. Christianson, R. Woerman, and R. Witmer. 1986. Snout cooling effects on sows and litters. Transactions of ASAE 29(4): 1097-1101. Morrison, S.R., M. Prokop, and G.P. Lofgreen. 1981. Sprinkling cattle for heat stress relief: Activation, temperature, duration of sprinkling, and pen area sprinkled. Transactions ofASAE 24(5):1299-1300. Timmons, M.B., and G.R. Baughman. 1983. Experimental evaluation of poultry mist-fog systems. Transactions ofASAE 26(1):207-210. Wilson, J.L., H.A. Hughes, and W.D. Weaver, Jr. 1983. Evaporative cooling with fogging nozzles in broiler houses. Transactions of ASAE 26(2): 557-561. Air Pollution in Buildings ACGIH. 2011. TLVsⓇ and BEIsⓇ. American Conference of Governmental Industrial Hygienists, Cincinnati. Avery, G.L., G.E. Merva, and J.B. Gerrish. 1975. Hydrogen sulfide produc- tion in swine confinement units. Transactions ofASAE 18(1):149. Bundy, D.S., and T.E. Hazen. 1975. Dust levels in swine confinement sys- tems associated with different feeding methods. Transactions of ASAE 18(1):137. Inc. ASHRAE, 2019 user. single for Licensed | {}
74f1d288-f3d8-4324-a9f5-db017990f351 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Environmental Control for Animals and Plants 25.23 Deboer, S., and W.D. Morrison. 1988. The effects of the quality of the envi- ronment in livestock buildings on the productivity of swine and safety of humans-A literature review. Department of Animal and Poultry Sci- ence, University of Guelph, Ontario. Grub, W., C.A. Rollo, and J.R. Howes. 1965. Dust problems in poultry envi- ronment. Transactions ofASAE 8(3):338. Effects of Environment on Production and Growth of Animals Cattle Anderson, J.F., D.W. Bates, and K.A. Jordan. 1978. Medical and engineer- ing factors relating to calf health as influenced by the environment. Transactions ofASAE 21(6):1169. Garrett, W.N. 1980. Factors influencing energetic efficiency ofbeef produc- tion. Journal of Animal Science 51(6):1434. Gebremedhin, K.G., C.O. Cramer, and W.P. Porter. 1981. Predictions and measurements ofheat production and food and water requirements of Hol- stein calves in different environments. Transactions ofASAE 24(3): 715. Holmes, C.' W., and N.A. McLean. 1975. Effects of air temperature and air movement on the heat produced by young Friesian and Jersey calves, with some measurements of the effects of artificial rain. New Zealand Journal ofAgricultural Research 18(3):277. Morrison, S.R., G.P. Lofgreen, and R.L. Givens. 1976. Effect of ventilation rate on beef cattle performance. Transactions ofASAE 19(3):530. General Hahn, G.L. 1982. Compensatory performance in livestock: Influences on environmental criteria. Proceedings of the Second International Live- stock Environment Symposium. American Society of Agricultural Engi- neers (now American Society of Agricultural and Biological Engineers), St. Joseph, MI. Hahn, G.L. 1981. Housing and management to reduce climatic impacts on livestock. Journal of Animal Science 52(1):175-186. Pigs Boon, C.R. 1982. The effect of air speed changes on the group postural behaviour of pigs. Journal of Agricultural Engineering Research 27(1): 71-79. Christianson, L.L., D.P. Bane, S.E. Curtis, W.F. Hall, A.J. Muehling, and G.L. Riskowski. 1989. Swine care guidelines for pork producers using environmentally controlled housing. National Pork Producers Council, Des Moines, IA. Close, W.H., L.E. Mount, and I.B. Start. 1971. The influence of environmental temperature and plane of nutrition on heat losses from groups of growing pigs. Animal Production 13(2):285. Driggers, L.B., C.M. Stanislaw, and C.R. Weathers. 1976. Breeding facility design to eliminate effects of high environmental temperatures. Trans- actions ofASAE 19(5):903. McCracken, K.J., and R. Gray. 1984. Further studies on the heat production and affective lower critical temperature of early-weaned pigs under com- mercial conditions of feeding and management. Animal Production 39:283-290. Nienaber, J.A., and G.L. Hahn. 1988. Environmental temperature influences on heat production of ad-lib-fed nursery and growing-finishing swine. Livestock Environment III: Proceedings of the Third International Live- stock Environment Symposium. American Society of Agricultural Engi- neers (now American Society of Agricultural and Biological Engineers), St. Joseph, MI. Phillips, P.A., B.A. Young, and J.B. McQuitty. 1982. Liveweight, protein deposition and digestibility responses in growing pigs exposed to low tem- perature. Canadian Journal ofAnimal Science 62:95-108. Poultry Buffington, D.E., K.A. Jordan, W.A. Junnila, and L.L. Boyd. 1974. Heat pro- duction of active, growing turkeys. Transactions ofASAE 17(3):542. Carr, L.E., T.A. Carter, and K.E. Felton. 1976. Low temperature brooding of broilers. Transactions ofASAE 19(3):553. Riskowski, G.L., J.A. DeShazer, and F.B. Mather. 1977. Heat losses of white leghorn laying hens as affected by intermittent lighting schedules. Trans- actions ofASAE 20(4):727-731. Siopes, T.D., M.B. Timmons, G.R. Baughman, and C.R. Parkhurst. 1983. The effect oflight intensity on the growth performance ofmale turkeys. Poultry Science 62:2336-2342. Sheep Schanbacher, B.D., G.L. Hahn, and J.A. Nienaber. 1982. Photoperiodic influ- ences on performance of market lambs. Proceedings of the Second Inter- national Livestock Environment Symposium. American Society of Agricultural Engineers (now American Society of Agricultural and Bio- logical Engineers), St. Joseph, MI. Vesely, J.A. 1978. Application oflight control to shorten the production cycle in two breeds of sheep. Animal Production 26(2):169. Modeling and Analysis Albright, L.D., and N.R. Scott. 1974. An analysis of steady periodic building temperature variations in warm weather- Part I: A mathematical model. Transactions ofASAE 17(1):88-92, 98. Albright, L.D., and N.R. Scott. 1974. An analysis of steady periodic building temperature variations in warm weather-Part II: Experimental verifica- tion and simulation. Transactions ofASAE 17(1):93-98. Albright, L.D., and N.R. Scott. 1977. Diurnal temperature fluctuations in multi-air spaced buildings. Transactions ofASAE 20(2):319-326. Bruce, J.M., and J.J. Clark. 1979. Models of heat production and critical tem- perature for growing pigs. Animal Production 28:353-369. Christianson, L.L., and H.A. Hellickson. 1977. Simulation and optimization of energy requirements for livestock housing. Transactions of ASAE 20(2):327-335. Ewan, R.C., and J.A. DeShazer. 1988. Mathematical modeling the growth of swine. Livestock environment III. Proceedings of the Third International Livestock Environment Symposium. American Society of Agricultural Engineers (now American Society of Agricultural and Biological Engi- neers), St. Joseph, MI. Hellickson, M.L., K.A. Jordan, and R.D. Goodrich. 1978. Predicting beef ani- mal performance with a mathematical model. Transactions of ASAE 21(5):938-943. Teter, N.C., J.A. DeShazer, and T.L. Thompson. 1973. Operational character- istics of meat animals-Part I: Swine; Part II: Beef; Part III: Broilers. Transactions ofASAE 16:157-159, 740-742, 1165-1167. Timmons, M.B. 1984. Use of physical models to predict the fluid motion in slot-ventilated livestock structures. Transactions ofASAE 27(2):502-507. Timmons, M.B., L.D. Albright, R.B. Furry, and K.E. Torrance. 1980. Experi- mental and numerical study of air movement in slot-ventilated enclosures. ASHRAE Transactions 86(1):221-240. Shades for Livestock Bedwell, R.L., and M.D. Shanklin. 1962. Influence of radiant heat sink on thermally-induced stress in dairy cattle. Missouri Agricultural Experiment Station Research Bulletin 808. Bond, T.E., L. W. Neubauer, and R.L. Givens. 1976. The influence of slope and orientation of effectiveness of livestock shades. Transactions of ASAE 19(1):134-137. Roman-Ponce, H., W.W. Thatcher, D.E. Buffington, C.J. Wilcox, and H.H. VanHorn. 1977. Physiological and production responses of dairy cattle to a shade structure in a subtropical environment. Journal of Dairy Science 60(3):424. Transport of Animals Ashby, B.H., D.G. Stevens, W.A. Bailey, K.E. Hoke, and W.G. Kindya. 1979. Environmental conditions on air shipment oflivestock. U.S. Department of Agriculture, SEA, Advances in Agricultural Technology, Northeastern Series 5. Ashby, B.H., A.J. Sharp, T.H. Friend, W.A. Bailey, and M.R. Irwin. 1981. Experimental railcar for cattle transport. Transactions ofASAE 24(2): 452. Ashby, B.H., H. Ota, W.A. Bailey, J.A. Whitehead, and W.G. Kindya. 1980. Heat and weight loss of rabbits during simulated air transport. Trans- actions ofASAE 23(1):162. Grandin, R. 1988. Livestock trucking guide. Livestock Conservation Institute, Madison, WI. Scher, S. 1980. Lab animal transportation receiving and quarantine. Lab Ani- mal 9(3):53. Stermer, R.A., T.H. Camp, and D.G. Stevens. 1982. Feeder cattle stress during handling and transportation. Transactions ofASAE 25(1):246-248. Stevens, D.G., G.L. Hahn, T.E. Bond, and J.H. Langridge. 1974. Environmen- tal considerationsfor shipment oflivestock by airfreight. U.S. Department of Agriculture, Animal and Plant Health Inspection Service. Stevens, D.G., and G.L. Hahn. 1981. Minimum ventilation requirement for the air transportation of sheep. Transactions of ASAE 24(1):180. Inc. ASHRAE, 2019 user. single for Licensed | {}
4df7fc02-ac7d-44c3-96b3-74b0122ce741 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 25.24 Laboratory Animals NIH. 1978. Laboratory animal housing. Proceedings ⌀fa symposium held at Hunt Valley, MD, September 1976. National Academy of Sciences, Wash- ington, D.C. McSheehy, T. 1976. Laboratory animal handbook 7-Control of the animal house environment. Laboratory Animals, Ltd. Soave, O., W. Hoag, F. Gluckstein, and R. Adams. 1980. The laboratory ani- mal data bank. Lab Animal 9(5):46-49. Ventilation Systems Albright, L.D. 1976. Air flows through hinged-baffle, slotted inlets. Trans- actions ofASAE 19(4):728, 732, 735. Albright, L.D. 1978. Air flow through baffled, center-ceiling, slotted inlets. Transactions ofASAE 21(5):944-947, 952. Albright, L.D. 1979. Designing slotted inlet ventilation by the systems char- acteristic technique. Transactions ofASAE 22(1):158. Pohl, S.H., and M.A. Hellickson. 1978. Model study of five types of manure pit ventilation systems. Transactions ofASAE 21(3):542. Randall, J.M. 1980. Selection of piggery ventilation systems and penning lay- outs based on the cooling effects of air speed and temperature. Journal of Agricultural Engineering Research 25(2):169-187. Randall, J.M., and V.A. Battams. 1979. Stability criteria for air flow patterns in livestock buildings. Journal of Agricultural Engineering Research 24(4):361-374. Timmons, M.B. 1984. Internal air velocities as affected by the size and loca- tion of continuous inlet slots. Transactions of ASAE 27(5):1514-1517. Natural Ventilation Bruce, J.M. 1982. Ventilation of a model livestock building by thermal buoy- ancy. Transactions ofASAE 25(6):1724-1726. Jedele, D.G. 1979. Cold weather natural ventilation of buildings for swine fin- ishing and gestation. Transactions ofASAE 22(3):598-601. Timmons, M.B., R. W. Bottcher, and G.R. Baughman. 1984. Nomographs for predicting ventilation by thermal buoyancy. Transactions of ASAE 27(6): 1891-1893. PLANTS Greenhouse and Plant Environment Aldrich, R.A., and J.W. Bartok. 1984. Greenhouse engineering. Department of Agricultural Engineering, University of Connecticut, Storrs. ASAE. 2002. Guidelines for measuring and reporting environmental param- eters for plant experiments in growth chambers. ANSI/ASAE Engineer- ing Practice EP411.2. American Society of Agricultural Engineers (now American Society of Agricultural and Biological Engineers), St. Joseph, MI. Clegg, P., and D. Watkins. 1978. The complete greenhouse book. Garden Way Publishing, Charlotte, VT. Downs, R.J. 1975. Controlled environments for plant research. Columbia University Press, New York. Langhans, R. W. 1985. Greenhouse management. Halcyon Press, Ithaca, NY. Mastalerz, J.W. 1977. The greenhouse environment. John Wiley & Sons, New York. Nelson, P. V. 1978. Greenhouse operation and management. Reston Publish- ing, VA. Pierce, J.H. 1977. Greenhouse grow how. Plants Alive Books, Seattle. Riekels, J.W. 1977. Hydroponics. Ontario Ministry ofAgriculture and Food, Fact Sheet 200-24, Toronto. Riekels, J. W. 1975. Nutrient solutions for hydroponics. Ontario Ministry of Agriculture and Food, Fact Sheet 200-532, Toronto. Sheldrake, R., Jr., and J. W. Boodley. Commercial production of vegetable and flower plants. Research Park, IB-82, Cornell University, Ithaca, NY. Tibbitts, T. W., and T.T. Kozlowski, eds. 1979. Controlled environment guidelines for plant research. Academic Press, New York. Light and Radiation Bickford, E.D., and S. Dunn. 1972. Lighting for plant growth. Kent State University Press, OH. Carpenter, G.C., and L.J. Mousley. 1960. The artificial illumination of envi- ronmental control chambers for plant growth. Journal of Agricultural Engineering Research [U.K.] 5:283. Campbell, L.E., R. W. Thimijan, and H.M. Cathey. 1975. Special radiant power of lamps used in horticulture. Transactions ofASAE 18(5):952. 2019 ASHRAE Handbook-HVAC Applications (SI) Cathey, H.M., and L.E. Campbell. 1974. Lamps and lighting: A horticultural view. Lighting Design & Application 4:41. Cathey, H.M., and L.E. Campbell. 1979. Relative efficiency of high- and low-pressure sodium and incandescent filament lamps used to supple- ment natural winter light in greenhouses. Journal of the American Soci- ety for Horticultural Science 104(6):812. Cathey, H.M., and L.E. Campbell. 1980. Light and lighting systems for horticultural plants. Horticultural Reviews 11:491. AVI Publishing, Westport, CT. Cathey, H.M., L.E. Campbell, and R. W. Thimijan. 1978. Comparative devel- opment of 1 1 plants grown under various fluorescent lamps and different duration ofirradiation with and without additional incandescent lighting. Journal of the American Societyfor Horticultural Science 103:781. Hughes, J., M.J. Tsujita, and D.P. Ormrod. 1979. Commercial applications of supplementary lighting in greenhouses. Ontario Ministry of Agricul- ture and Food, Fact Sheet 290-717, Toronto. Kaufman, J.E., ed. 1981. IES Lighting handbook: Application volume. IES, New York. Kaufman, J.E., ed. 1981. IES Lighting handbook: Reference volume. IES, New York. Robbins, F. V. , and C.K. Spillman. 1980. Solar energy transmission through two transparent covers. Transactions ofASAE 23(5). Sager, J.C., J.L. Edwards, and W.H. Klein. 1982. Light energy utilization efficiency for photosynthesis. Transactions ofASAE 25(6):1 737-1746. Photoperiod Heins, R.D., W.H. Healy, and H.F. Wilkens. 1980. Influence ofnight lighting with red, far red, and incandescent light on rooting of chrysanthemum cuttings. HortScience 15:84. Carbon Dioxide Bailey, W .A., et al. 1970. CO2 systems for growing plants. Transactions of ASAE 13(2):63. Gates, D.M. 1968. Transpiration and leaf temperature. Annual Review of Plant Physiology 19:211. Holley, W.D. 1970. CO2 enrichment for flower production. Transactions of ASAE 13(3):257. Kretchman, J., and F.S. Howlett. 1970. Enrichment for vegetable produc- tion. Transactions of ASAE 13(2):252. Tibbitts, T. W J.C. McFarlane, D.T. Krizek, W.L. Berry, P.A. Hammer, R.H. Hodgsen, and R. W. Langhans. 1977. Contaminants in plant growth chambers. Horticulture Science 12:310. Wittwer, S.H. 1970. Aspects of CO2 enrichment for crop production. Trans- actions ofASAE 13(2):249. Heating, Cooling, and Ventilation ASAE. 2003. Heating, ventilating and cooling greenhouses. ANSI/ASAE Engineering Practice EP406.1. American Society of Agricultural Engineers (now American Society of Agricultural and Biological Engi- neers), St. Joseph, MI. Albright, L.D., I. Seginer, L.S. Marsh, and A. Oko. 1985. In situ thermal cal- ibration of unventilated greenhouses. Journal ofAgricultural Engineer- ing Research 31(3):265-281. Buffington, D.E., and T.C. Skinner. 1979. Maintenance guide for green- house ventilation, evaporative cooling, and heating systems. Publication AE-17. Department of Agricultural Engineering, University of Florida, Gainesville. Duncan, G.A., and J.N. Walker. 1979. Poly-tube heating ventilation systems and equipment. Publication AEN-7. Agricultural Engineering Depart- ment, University of Kentucky, Lexington. Elwell, D.L., M.Y. Hamdy, W.L. Roller, A.E. Ahmed, H.N. Shapiro, J.J. Parker, and S.E. Johnson. 1985. Soil heating using subsurface pipes. Department of Agricultural Engineering, Ohio State University, Columbus. Heins, R., and A. Rotz. 1980. Plant growth and energy savings with infrared heating. Florists , Review (October):20. NGMA. 1989. Greenhouse heat loss. National Greenhouse Manufacturers' Association, Taylors, SC. NGMA. 1989. Standards for ventilating and cooling greenhouses. National Greenhouse Manufacturers' Association, Taylors, SC. NGMA. 1993. Recommendationfor using insect screens in greenhouse struc- tures. National Greenhouse Manufacturers' Association, Taylors, SC. Inc. ASHRAE, 2019 user. single for Licensed | {}
c370235e-ff03-4402-8d1f-3f3db63f5edb | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Environmental Control for Animals and Plants 25.25 Roberts, W.J., and D. Mears. 1984. Floor heating and bench heating extension bulletin for greenhouses. Department of Agricultural and Biological Engineering, Cook College, Rutgers University, New Brunswick, NJ. Roberts, W.J., and D. Mears. 1984. Heating and ventilating greenhouses. Department of Agricultural and Biological Engineering, Cook College, Rutgers University, New Brunswick, NJ. Roberts, W J., and D.R. Mears. 1979. Floor heating ofgreenhouses. Miscel- laneous Publication, Rutgers University, New Brunswick, NJ. Silverstein, S.D. 1976. Effect of infrared transparency on heat transfer through windows: A clarification of the greenhouse effect. Science 193:229. Walker, J.N., and G.A. Duncan. 1975. Greenhouse heating systems. Publi- cation AEN-31. Agricultural Engineering Department, University of Kentucky, Lexington. Walker, J.N., and G.A. Duncan. 1979. Greenhouse ventilation systems. Publication AEN-30. Agricultural Engineering Department, University of Kentucky, Lexington. Energy Conservation Roberts, W.J., J.W. Bartok, Jr., E.E. Fabian, and J. Simpkins. 1985. Energy conservation for commercial greenhouses. NRAES-3. Department of Agricultural Engineering, Cornell University, Ithaca, NY. Solar Energy Use Albright, L.D., R. W. Langhans, and G.B. White. 1980. Passive solar heating applied to commercial greenhouses. Publication 115, Energy in Pro- tected Civilization. Acta Horticultura. Cathey, H.M. 1980. Energy-efficient crop production in greenhouses. ASHRAE Transactions 86(2):455. Duncan, G.A., J.N. Walker, and L. W. Turner. 1979. Energyfor greenhouses, Part I: Energy Conservation. Publication No. AEES-16. College of Agri- culture, University of Kentucky, Lexington. Duncan, G.A., J.N. Walker, and L. W. Turner. 1980. Energyfor greenhouses, PartII: Alternative Sources ofEnergy. College of Agriculture, University of Kentucky, Lexington. Gray, H.E. 1980. Energy management and conservation in greenhouses: A manufacturer's view. ASHRAE Transactions 86(2):443. Roberts, W.J., and D.R. Mears. 1980. Research conservation and solar energy utilization in greenhouses. ASHRAE Transactions 86(2):433. Short, T.H., M.F. Brugger, and W.L. Bauerle. 1980. Energy conservation ideas for new and existing commercial greenhouses. ASHRAE Trans- actions 86(2):448. Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
4e97eebf-ae16-4225-8d85-fa990b14e79d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 26 DRYING AND STORING SELECTED FARM CROPS ¦ DRYING ¦ 26.2 ¦ Cotton ¦ 26.8 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Drying Equipment and Practices ¦ 26.2 ¦ Peanuts ¦ 26.9 ¦ ¦ Shallow-Layer Drying ¦ 26.3 ¦ Rice ¦ 26.9 ¦ ¦ Deep-Bed Drying ¦ 26.4 ¦ STORAGE PROBLEMS AND PRACTICES ¦ 26.9 ¦ ¦ DRYING SPECIFIC CROPS ¦ · 26.7 ¦ Moisture Migration ¦ 26.9 ¦ ¦ Soybeans ¦ 26.7 ¦ Grain Aeration ¦ 26.9 ¦ ¦ Hay ¦ ·· 26.8 ¦ SEED STORAGE ¦ 26.12 ¦ CONTROL of moisture content and temperature during storage critical to preserving the nutritional and economic value of farm crops as they move from the field to the market. Fungi (mold) and insects feed on poorly stored crops and reduce crop quality. Relative humidity and temperature affect mold and insect growth, which is reduced to a minimum if the crop is kept cooler than 10°C and if the relative humidity of the air in equilibrium with the stored crop is less than 60%. Mold growth and spoilage are a function of elapsed storage time, temperature, and moisture content above critical values. Approxi- mate allowable storage life for cereal grains is shown in Table 1. For example, corn at 16°C and 20% wet basis (w.b.) moisture has a stor- age life of about 25 days. Ifit is dried to 18% w.b. after 12 days, half of its storage life has elapsed. Thus, the remaining storage life at 16°C and 18% w.b. moisture content is 25 days, not 50 days. Insects thrive in stored grain ifthe moisture content and tempera- ture are not properly controlled. At low moisture contents and tem- peratures below 10°C, insects remain dormant or die. Most farm crops must be dried to, and maintained at, a suitable moisture content. For most grains, a suitable moisture content is in the range of 12 to 15% w.b., depending on the specific crop, storage temperature, and length of storage. Oilseeds such as peanuts, sun- flower seeds, and flaxseeds must be dried to a moisture content of 8 to 9% w.b. Grain stored for more than a year, grain that is damaged, Table 1 Approximate Allowable Storage Time (Days) for Cereal Grains ¦ Moisture Content, % w.b.a ¦ Temperature, °C ¦ Temperature, °C ¦ Temperature, °C ¦ Temperature, °C ¦ Temperature, °C ¦ Temperature, °C ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Moisture Content, % w.b.a ¦ -1 ¦ 4 ¦ 10 ¦ 16 ¦ 22 ¦ 27 ¦ ¦ 14 ¦ * ¦ * ¦ * ¦ * ¦ 200 ¦ 140 ¦ ¦ 15 ¦ * ¦ * ¦ * ¦ 240 ¦ 125 ¦ 70 ¦ ¦ 16 ¦ * ¦ * ¦ 230 ¦ 120 ¦ 70 ¦ 40 ¦ ¦ 17 ¦ * ¦ 280 ¦ 130 ¦ 75 ¦ 45 ¦ 20 ¦ ¦ 18 ¦ * ¦ 200 ¦ 90 ¦ 50 ¦ 30 ¦ 15 ¦ ¦ 19 ¦ * ¦ 140 ¦ 70 ¦ 35 ¦ 20 ¦ 10 ¦ ¦ 20 ¦ * ¦ 90 ¦ 50 ¦ 25 ¦ 14 ¦ 7 ¦ ¦ 22 ¦ 190 ¦ 60 ¦ 30 ¦ 15 ¦ 8 ¦ 3 ¦ ¦ 24 ¦ 130 ¦ 40 ¦ 15 ¦ 10 ¦ 6 ¦ 2 ¦ ¦ 26 ¦ 90 ¦ 35 ¦ 12 ¦ 8 ¦ 5 ¦ 2 ¦ ¦ 28 ¦ 70 ¦ 30 ¦ 10 ¦ 7 ¦ 4 ¦ 2 ¦ ¦ 30 ¦ 60 ¦ 25 ¦ 5 ¦ 5 ¦ 3 ¦ 1 ¦ Based on composite of 0.5% maximum dry matter loss calculated on the basis of USDA research; Transactions of ASAE 333-337, 1972; and "Unheated Air Drying,' Manitoba Agriculture Agdex 732-1, rev. 1986. aGrain moisture content calculated as percent wet basis: (mass of water in a given amount of wet grain + mass of the wet grain) x 100. * Approximate allowable storage time exceeds 300 days. The preparation of this chapter is assigned to TC 2.2, Plant and Animal Environment. and seed stock should be dried to a lower moisture content. Moisture levels above these critical values lead to the growth of fungi, which may produce toxic compounds such as aflatoxin. The maximum yield of dry matter can be obtained by harvesting when the corn has dried in the field to an average moisture content of 26% w.b. However, for quality-conscious markets, the minimum damage occurs when corn is harvested at 21 to 22% w.b. Wheat can be harvested when it has dried to 20% w.b., but harvesting at these moisture contents requires expensive mechanical drying. Although field drying requires less expense than operating drying equipment, total cost may be greater because field losses generally increase as the moisture content decreases. The price of grain to be sold through commercial market channels is based on a specified moisture content, with price discounts for moisture levels above the specified amount. These discounts com- pensate for the mass of excess water, cover the cost of water removal, and control the supply of wet grain delivered to market. Grain dried to below the base moisture content set by the market (15.0% w.b. for corn, 13.0% w.b. for soybeans, and 13.5% w.b. for wheat) is not gen- erally sold at a premium; thus, the seller loses the opportunity to sell water for the price of grain. Grain Quantity The bushel is a volume measure (0.03524 m3) that is the common measure used for marketing grain in the United States, while the tonne (Mg) is the more common international measure. The legal mass for the bushel in the United States is set at 25.40 kg for corn and 27.22 kg for wheat. The densities of some crops are listed in Table 2. The percent of mass lost due to water removed may be calculated by the following equation: M。 - Mf Moisture shrink, % = x 100 100 - Mf where M0 = original or initial moisture content, wet basis Mf = final moisture content, wet basis Applying the formula to drying a crop from 25% to 15%, 25 - 15 Moisture shrink = x 100 = 11.76% 100 - 15 In this case, the moisture shrink is 11.76%, or an average 1.176% mass reduction for each percentage point of moisture reduction. The moisture shrink varies depending on the final moisture content. For example, the average shrink per point of moisture when drying from 20% to 10% is 1.111. Economics Inc. ASHRAE, 2019 user. single for Licensed Producers generally have the choice of drying their grain on the farm before delivering it to market, or delivering wet grain with a price discount for excess moisture. The expense of drying on the farm 26.1 | {}
29a7d825-a755-451d-abf3-f3a03ff60ab0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 26.2 2019 ASHRAE Handbook- -HVAC Applications (SI) Table2 Calculated Densities of Grains and Seeds Based on U.S. Department of Agriculture Data ¦ ¦ Bulk Density, kg/m3 ¦ ¦ --- ¦ --- ¦ ¦ Alfalfa ¦ 768 ¦ ¦ Barley ¦ 614 ¦ ¦ Beans, dry ¦ 768 ¦ ¦ Bluegrass ¦ 180 to 384 ¦ ¦ Canola ¦ 643 to 770 ¦ ¦ Clover ¦ 768 ¦ ¦ Corn ¦ ¦ ¦ Ear, husked ¦ 448 ¦ ¦ Shelled ¦ 717 ¦ ¦ Cottonseed ¦ 410 ¦ ¦ Oats ¦ 410 ¦ ¦ Peanuts, unshelled ¦ ¦ ¦ Virginia type ¦ 218 ¦ ¦ Runner, Southeastern ¦ 269 ¦ ¦ Spanish ¦ 317 ¦ ¦ Rice, rough ¦ 576 ¦ ¦ Rye ¦ 717 ¦ ¦ Sorghum ¦ 640 ¦ ¦ Soybeans ¦ 768 ¦ ¦ Sudan grass ¦ 768 ¦ ¦ Sunflower ¦ ¦ ¦ Nonoil ¦ 307 ¦ ¦ Oilseed ¦ 410 ¦ ¦ Wheat ¦ 768 ¦ Table 3 Estimated Corn Drying Energy Requirement ¦ Dryer Type ¦ kJ/kg of Water Removed ¦ ¦ --- ¦ --- ¦ ¦ Unheated air ¦ 2300 to 2800 ¦ ¦ Low temperature ¦ 2800 to 3500 ¦ ¦ Batch-in-bin, continuous-flow in-bin ¦ 3500 to 4700 ¦ ¦ High temperature ¦ ¦ ¦ Air recirculating ¦ 4200 to 5100 ¦ ¦ Without air recirculating ¦ 4700 to 7000 ¦ ¦ Combination drying, dryeration ¦ 3300 to 4200 ¦ Note: Includes all energy requirements for fans and heat. includes both fixed and variable costs. Once a dryer is purchased, the costs of depreciation, interest, taxes, and repairs are fixed and mini- mally affected by volume of crops dried. The costs oflabor, fuel, and electricity vary directly with the volume dried. Total drying costs vary widely, depending on the volume dried, the drying equipment, and fuel and equipment prices. Energy consumption depends primar- ily on dryer type. Generally, the faster the drying speed, the greater the energy consumption (Table 3). 1. DRYING 1.1 DRYING EQUIPMENT AND PRACTICES Contemporary crop-drying equipment depends on mass and energy transfer between the drying air and the product to be dried. The drying rate is a function of the initial temperature and moisture content of the crop, the air-circulation rate, the entering condition of the circulated air, the length of flow path through the products, and the time elapsed since the beginning of the drying operation. Out- door air is frequently heated before it is circulated through the prod- uct. Heating increases the rate of heat transfer to the product, increases its temperature, and increases the vapor pressure of the product moisture. For more information on crop responses to drying, see Chapter 11 of the 2005 ASHRAE Handbook-Fundamentals. Most crop-drying equipment consists of (1) a fan to move the air through the product, (2) a controlled heater to increase the ambient air temperature to the desired level, and (3) a container to distribute the drying air uniformly through the product. The exhaust air is vented to the atmosphere. Where climate and other factors are favorable, unheated air is used for drying, and the heater is omitted. Fans The fan selected for a given drying application should meet the same requirements important in any air-moving application. It must deliver the desired amount of air against the static resistance of the product in the bin or column, the resistance of the delivery system, and the resistance of the air inlet and outlet. Foreign material in the grain can significantly change the re- quired air pressure in the following ways: · Foreign particles larger than the grain (straw, plant parts, and larger seeds) reduce airflow resistance. The airflow rate may be increased by 60% or more. · Foreign particles smaller than the grain (broken grain, dust, and small seeds) increase the airflow resistance. The effect may be dramatic, decreasing the airflow rate by 50% or more. · The method used to fill the dryer or the agitation or stirring of the grain after it is placed in the dryer can increase pressure require- ments by up to 100%. In some grain, high moisture causes less pressure drop than does low moisture. v aneaxial fans are normally recommended when static pres- sures are less than 0.75 kPa. Backward-curved centrifugal fans are commonly recommended when static pressures are higher than 1.0 kPa. Low-speed centrifugal fans operating at 1750 rpm per- form well up to about 1.75 kPa, and high-speed centrifugal fans operating at about 3500 rpm have the ability to develop static pres- sure up to about 2.5 kPa. The in-line centrifugal fan consists of a centrifugal fan impeller mounted in the housing of an axial flow fan. A bell-shaped inlet funnels the air into the impeller. The in- line centrifugal fan operates at about 3450 rpm and has the ability to develop pressures up to 2.5 kPa on 6 kW or larger fans. After functional considerations are made, the initial cost of the dryer fan should be taken into account. Drying equipment has a low percentage of annual use in many applications, so the cost of dryer ownership per unit of material dried is sometimes greater than the energy cost of operation. The same considerations apply to other components of the dryer. Heaters Most crop dryer heaters are fueled by either natural gas, liquefied petroleum gas, or fuel oil, though some electric heaters are used. Dryers using coal, biomass (e.g., corn cobs, stubble, or wood), and solar energy have also been built. Fuel combustion in crop dryers is similar to combustion in domestic and industrial furnaces. Heat is transferred to the drying air either indirectly, by means of a heat exchanger, or directly, by combining the combustion gases with the drying air. Direct combus- tion heating is generally limited to natural gas or liquefied petro- leum (LP) gas heaters. Most grain dryers use direct combustion. Indirect heating is sometimes used in drying products such as hay because of its greater fire hazard. Controls In addition to the usual temperature controls for drying air, all heated air units must have safety controls similar to those found on space-heating equipment. These safety controls shut off the fuel in case of flame failure and stop the burner in case of overheating or excessive drying air temperatures. All controls should be set up to operate the machinery safely in the event of power failure. Inc. ASHRAE, 2019 user. single for Licensed | {}
8681e9be-a42a-4569-a077-d86c4e165a39 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Drying and Storing Selected Farm Crops 26.3 1.2 SHALLOW-LA YER DRYING Batch Dryers The batch dryer cycles through the loading, drying, cooling, and unloading ofthe grain. Fans force hot air through columns (typically 300 mm wide) or layers (600 to 1500 mm thick) of grain. Drying time depends on the type of grain and the amount of moisture to be removed. Some dryers circulate and mix the grain to prevent signif- icant moisture content gradients from forming across the column. A circulation rate that is too fast or a poor selection of handling equip- ment may cause undue damage and loss ofmarket quality. Batch dry- ers are suitable for farm operations and are often portable. Continuous-Flow Dryers This type of self-contained dryer passes a continuous stream of grain through the drying chamber. Some dryers use a second cham- ber to cool the hot, dry grain before storage. Handling and storage equipment must be available at all times to move grain to and from the dryers. These dryers have cross-flow, concurrent flow, or coun- terflow designs. Cross-Flow Dryers. A cross-flow dryer is a column dryer that moves air perpendicular to the grain movement. These dryers commonly consist of two or more vertical columns surrounding the drying and cooling air plenums. The columns range in thickness from 200 to 400 mm. Airflow rates range from 0.7 to 2. 7 m3/s per cubic metre of grain. The thermal efficiency of the drying process increases as column width increases and decreases as airflow rate increases. However, moisture uniformity and drying capacity increase as airflow rate increases and as column width decreases. Dryers are designed to obtain a desirable balance of airflow rate and column width for the expected moisture content levels and drying air temperatures. Performance is evaluated in terms of drying capac- ity, thermal efficiency, and dried product moisture uniformity. As with the batch dryer, a moisture gradient forms across the col- umn because the grain nearest the inside ofthe column is exposed to the driest air during the complete cycle. Several methods minimize the problem of uneven drying. One method uses turnflow devices that split the grain stream and move the inside half ofthe column to the outside and the outside half to the inside. Although effective, turnflow devices tend to plug ifthe grain is trashy. Under these conditions, a scalper/cleaner should be used to clean the grain before it enters the dryer. Another method is to divide the drying chamber into sections and duct the hot air so that its direction through the grain is reversed in alternate sections. This method produces about the same effect as the turnflow method. A third method is to divide the drying chamber into sections and reduce the drying air temperature in each section consecutively. This method is the least effective. Rack-Type Dryers. In this special type of cross-flow dryer, grain flows over alternating rows of heated air supply ducts and air exhaust ducts (Figure 1). This action mixes the grain and alternates exposure to relatively hot drying air and air cooled by previous con- tact with the grain, promoting moisture uniformity and equal expo- sure of the product to the drying air. Concurrent-Flow Dryers. In the concurrent-flow dryer, grain and drying air move in the same direction in the drying chamber. The drying chamber is coupled to a counterflow cooling section. Thus, the hottest air is in contact with the wettest grain, allowing the use of higher drying air temperatures (up to 230°C). Rapid evaporative cooling in the wettest grain prevents the grain tem- perature from reaching excessive levels. Because higher drying air temperatures are used, the energy efficiency is better than that obtained with a conventional cross-flow dryer. In the cooling ![image](/image/placeholder) GRAIN IN GARNER D ○ ○ ○ ( D ○ ○ ○ HEATER SECTION D ○ ○ ) AIR OUT 5 AIR IN HEATED AIR FRONT VIEW SIDE VIEW Fig. 1 Rack-Type Continuous-Flow Grain Dryer with Alternate Rows of Air Inlet and Outlet Ducts section, the coolest air initially contacts the coolest grain. The combination of drying and cooling chambers results in lower thermal stresses in the grain kernels during drying and cooling and, thus, a higher-quality product. Counterflow Dryers. The grain and drying air move in opposite directions in the drying chamber of this dryer. Counterflow is com- mon for in-bin dryers. Drying air enters from the bottom of the bin and exits from the top. The wet grain is loaded from overhead, and floor sweep augers can be used to bring the hot, dry grain to a center sump, where it is removed by another auger. The travel of the sweep is normally controlled by moisture- or temperature-sensing elements. A drying zone exists only in the lower layers of the grain mass and is truncated at its lower edge so that the grain being removed is not overdried. As a part of the counterflow process, the warm, sat- urated or near-saturated air leaving the drying zone passes through the cool incoming grain. Some energy is used to heat the cool grain, but some moisture may condense on the cool grain if the bed is deep and the initial grain temperature is low. Reducing Energy Costs Recirculation. In most commercially available continuous-flow dryers, optional ducting systems recycle some ofthe exhaust air from the drying and cooling chambers back to the inlet of the drying chamber (Figure 2). Systems vary, but most make it possible to recir- culate all of the air from the cooling chamber and from the lower two-thirds ofthe drying chamber. The relative humidity of this recir- culated air for most cross-flow dryers is less than 50%. Energy sav- ings of up to 30% can be obtained from a well-designed system. Dryeration. This is another means ofreducing energy consump- tion and improving grain quality. In this process, hot grain with a moisture content one or two percentage points above that desired for storage is removed from the dryer (Figure 3). The hot grain is placed in a dryeration bin, where it tempers without airflow for at least 4 to 6 h. After the first grain delivered to the bin has tempered, the cool- ing fan is turned on as additional hot grain is delivered to the bin. The air cools the grain and removes 1 to 2% of its moisture before the grain is moved to final storage. Ifthe cooling rate equals the fill- ing rate, cooling is normally completed about 6 h after the last hot grain is added. The crop cooling rate should equal the filling rate of the dryeration bin. A faster cooling rate cools the grain before it has tempered. A slower rate may result in spoilage, since the allowable storage time for hot, damp grain may be only a few days. The re- quired airflow rate is based on dryer capacity and crop density. An airflow rate of 0.2 m3/s for each cubic metre per hour of grain ca- pacity provides cooling capacity to keep up with the dryer when Inc. ASHRAE, 2019 user. single for Licensed | {}
dc18b679-91bc-43d2-8c4e-5fac0956a49e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 26.4 2019 ASHRAE Handbook- -HVAC Applications (SI) Table 4 Recommended Airflow Rates for Dryeration ¦ Crop ¦ Density, kg/m3 ¦ Recommended Dryeration Airflow Rate, m3/s per cubic metre per hour dryer capacity ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Barley ¦ 768 ¦ 0.17 ¦ ¦ Corn ¦ 896 ¦ 0.20 ¦ ¦ Durum ¦ 960 ¦ 0.21 ¦ ¦ Edible beans ¦ 960 ¦ 0.21 ¦ ¦ Flaxseeds ¦ 896 ¦ 0.20 ¦ ¦ Millet ¦ 800 ¦ 0.18 ¦ ¦ Oats ¦ 512 ¦ 0.11 ¦ ¦ Rye ¦ 896 ¦ 0.20 ¦ ¦ Sorghum ¦ 896 ¦ 0.20 ¦ ¦ Soybeans ¦ 960 ¦ 0.21 ¦ ¦ Nonoil sunflower seeds ¦ 384 ¦ 0.09 ¦ ¦ Oil sunflower seeds ¦ 512 ¦ 0.11 ¦ ¦ Hard red spring wheat ¦ 960 ¦ 0.21 ¦ Note: Basic air volume is 0.80 m3/kg, ![image](/image/placeholder) h Fig. 2 Crop Dryer Recirculation Unit (Courtesy Farm Fans, Inc., a division of The GSI Group) drying corn that has a density of 900 kg/m3. Recommended airflow rates for some crops are listed in Table 4. Combination Drying. This method was developed to improve drying thermal efficiency and corn quality. First, a high-temperature dryer dries the corn to 18 to 20% moisture content. Then it is trans- ferred to a bin, where the full-bin drying system brings the moisture down to a safe storage level. Dryer Temperature. For energy savings, operating tempera- tures ofbatch and continuous-flow dryers are usually set at the high- est level that will not damage the product for its end use. 1.3 DEEP-BED DRYING A deep-bed drying system can be installed in any structure that holds grain. Most grain storage structures can be designed or adapted for drying if a means of distributing the drying air uni- formly through the grain is provided. A perforated floor (Figure 4) and duct systems placed on the floor of the bin (Figure 5) are the two most common means. Perforations in the floor should have a total area of at least 10% of the floor area. A perforated floor distributes air more uniformly and offers less resistance to airflow than do ducts, but a duct sys- tem is less expensive for larger floor area systems. Ducts can be removed after the grain is removed, and the structure can be cleaned and used for other purposes. Ducts should not be spaced farther apart than one-half times the depth of the grain. The amount of perforated area or the duct length will affect airflow dis- tribution uniformity. Air ducts and tunnels that disperse air into the grain should be large enough to prevent the air velocity from exceeding 10 m/s; slower speeds are desirable. Sharp turns, obstructions, or abrupt changes in duct size should be eliminated, as they cause pressure loss. Operating methods for drying grain in storage bins are (1) full-bin drying, (2) layer drying, (3) batch-in-bin drying, and (4) recirculat- ing/continuous-flow bin drying. Full-Bin Drying Full-bin drying is generally performed with unheated air or air heated up to 11 °C above ambient. A humidistat is frequently used to sense the humidity of the drying air and turn off the heater if the weather conditions are such that heated air would cause overdrying. A humidistat setting of 55% stops drying at approximately the 12% moisture level for most farm grains, assuming that the ambient rel- ative humidity does not go below this point. Airflow rate requirements for full-bin drying are generally cal- culated on the basis of cubic metre per second of air required per cubic metre of grain. The airflow rate recommendations depend on Fig.3 Dryeration System Schematic ![image](/image/placeholder) TRANSFER HOT AT DRYERATION MOISTURE HARVEST CONTENT MOISTURE TRANSFER COOL CONTENT AND DRY TEMPER 46 HOURS, STORAGE THEN COOL HIGH- SPEED DRYER COOLING FAN AERATION FAN Inc. ASHRAE, 2019 Ⓒ user. single for Licensed | {}
8ff0e944-4b86-4d58-8956-35af9fb087f0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Drying and Storing Selected Farm Crops 26.5 Table 5 Maximum Corn Moisture Contents, Wet Mass Basis, for Single-Fill Unheated Air Drying ¦ Zone ¦ Full-Bin Airflow Rate, m3/s per cubic metre of grain ¦ Harvest Date ¦ Harvest Date ¦ Harvest Date ¦ Harvest Date ¦ Harvest Date ¦ Harvest Date ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Zone ¦ Full-Bin Airflow Rate, m3/s per cubic metre of grain ¦ 9-1 ¦ 9-15 ¦ 10-1 ¦ 10-15 ¦ 11-1 11-15 ¦ 12-1 ¦ ¦ ¦ Zone ¦ Full-Bin Airflow Rate, m3/s per cubic metre of grain ¦ Initial Moisture Content, % ¦ Initial Moisture Content, % ¦ Initial Moisture Content, % ¦ Initial Moisture Content, % ¦ Initial Moisture Content, % ¦ Initial Moisture Content, % ¦ ¦ ¦ A ¦ 0.013 ¦ 18 ¦ 19.5 ¦ 21 ¦ 22 ¦ 24 20 ¦ 18 ¦ A ¦ ¦ A ¦ 0.017 ¦ 20 ¦ 20.5 ¦ 21.5 ¦ 23 ¦ 24.5 20.5 ¦ 18 ¦ A ¦ ¦ A ¦ 0.020 ¦ 20 ¦ 20.5 ¦ 22.5 ¦ 23 ¦ 25 21 ¦ 18 ¦ A ¦ ¦ A ¦ 0.027 ¦ 20.5 ¦ 21 ¦ 23 ¦ 24 ¦ 25.5 21.5 ¦ 18 ¦ A ¦ ¦ A ¦ 0.040 ¦ 22 ¦ 22.5 ¦ 24 ¦ 25.5 ¦ 27 22 ¦ 18 ¦ A ¦ ¦ B ¦ 0.013} ¦ 19 ¦ 20 ¦ 20 ¦ 21 ¦ 23 20 ¦ ¦ 18 ¦ ¦ B ¦ 0.017 ¦ 19 ¦ 20 ¦ 20.5 ¦ 21.5 ¦ 24 20.5 ¦ 18 ¦ 18 ¦ ¦ B ¦ 0.020 ¦ 19.5 ¦ 20.5 ¦ 21 ¦ 22.5 ¦ 24 21 ¦ 18 ¦ 18 ¦ ¦ B ¦ 0.027 ¦ 20 ¦ 21 ¦ 22.5 ¦ 23.5 ¦ 25 21.5 ¦ 18 B ¦ 18 ¦ ¦ B ¦ 0.040 ¦ 21 ¦ 22.5 ¦ 23.5 ¦ 24.5 ¦ 26 ¦ 22 18 ¦ 18 ¦ ¦ C ¦ 0.013 ¦ 19 ¦ 19.5 ¦ 20 ¦ 21 ¦ 22 20 ¦ ¦ 18 ¦ ¦ C ¦ 0.017 ¦ 19 ¦ 20 ¦ 20.5 ¦ 21.5 ¦ 22.5 20.5 ¦ 18 ¦ 18 ¦ ¦ C ¦ 0.020 ¦ 19.5 ¦ 20 ¦ 21 ¦ 22 ¦ 23.5 21.5 ¦ 18 ¦ 18 ¦ ¦ C ¦ 0.027 ¦ 20 ¦ 21 ¦ 22 ¦ 23 ¦ 24.5 21.5 ¦ 18 ¦ 18 ¦ ¦ C ¦ 0.040 ¦ 21 ¦ 22 ¦ 23.5 ¦ 24.5 ¦ 25.5 22 ¦ 18 ¦ 18 ¦ ¦ C ¦ D 0.013} ¦ 19 ¦ 19.5 ¦ 20 ¦ 21 ¦ 22 20 ¦ 18 ¦ 18 ¦ ¦ C ¦ 0.017 ¦ 19 ¦ 19.5 ¦ 20.5 ¦ 21 ¦ 22.5 20.5 ¦ 18 D ¦ 18 ¦ ¦ C ¦ 0.020 ¦ 19 ¦ 19.5 ¦ 21 ¦ 22 ¦ 23 21 ¦ 18 ¦ 18 ¦ ¦ C ¦ 0.027 ¦ 19.5 ¦ 21 ¦ 21.5 ¦ 23 ¦ 24 21.5 ¦ 18 ¦ 18 ¦ ¦ C ¦ 0.040 ¦ 20.5 ¦ 21.5 ¦ 23 ¦ 24 ¦ 25 22 ¦ 18 ¦ 18 ¦ Source: Midwest Plan Service, 1980. Reprinted with permission. ![image](/image/placeholder) AIR OUTLET GRAIN SPREADER BIN ROOF BIN WALL GRAIN LEVEL TRANSITION DUCT HEATER FAN CONCRETE PERFORATED FLOOR FLOOR Fig. 4 Perforated Floor System for Bin Drying of Grain the weather conditions and on the type of grain and its moisture con- tent. Airflow rate is important for successful drying. Because faster drying results from higher airflow rates, the highest economical air- flow rate should be used. However, the cost offull-bin drying at high airflow rates may exceed the cost of using column dryers, or the electric power requirement may exceed the available capacity. Recommendations for full-bin drying with unheated air are shown in Tables 5, 6, and 7. These recommendations apply to the principal production areas of the continental United States and are based on experience under average conditions; they may not be applicable under unusual weather conditions or even usual weather conditions in the case of late-maturing crops. Full-bin drying may not be feasible in some geographical areas. ![image](/image/placeholder) AIR FLOWS OUT FROM DUCT Fig. 5 Tunnel or Duct Air Distribution System Table 6 Minimum Airflow Rate for Unheated Air Low-Temperature Drying of Small Grains and Sunflower in the Northern Plains of the United States ¦ Airflow Rate m3/s per cubic metre of grain ¦ Maximum Initial Moisture Content, % Wet Basis ¦ Maximum Initial Moisture Content, % Wet Basis ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Airflow Rate m3/s per cubic metre of grain ¦ Small Grains ¦ Sunflower ¦ ¦ 0.007 ¦ 16 ¦ 15 ¦ ¦ 0.013 ¦ 18 ¦ 17 ¦ ¦ 0.027 ¦ 20 ¦ 21 ¦ The maximum practical depth of grain to be dried (distance of air travel) is limited by the cost of the fan, motor, air distribution sys- tem, and power required. This depth seems to be 6 m for corn and soybeans, and about 4.5 m for wheat. To ensure satisfactory drying, heated air may be used during periods of prolonged fog or rain. Burners should be sized to raise Inc. ASHRAE, 2019 Ⓒ user. single for Licensed | {}
628e6028-b7d4-4e31-867d-20389598bf10 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 26.6 Table 7 Recommended Unheated Air Airflow Rate for Different Grains and Moisture Contents in the Southern United States ¦ Type of Grain ¦ Grain Moisture Content, % ¦ Recommended Airflow Rate, m3/s per cubic metre of grain ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Wheat ¦ 25 ¦ 0.080 ¦ ¦ Wheat ¦ 22 ¦ 0.067 ¦ ¦ Wheat ¦ 20 ¦ 0.040 ¦ ¦ Wheat ¦ 18 ¦ 0.027 ¦ ¦ Wheat ¦ 16 ¦ 0.013 ¦ ¦ Oats ¦ 25 ¦ 0.040 ¦ ¦ Oats ¦ 20 ¦ 0.027 ¦ ¦ Oats ¦ 18 ¦ 0.020 ¦ ¦ Oats ¦ 16 ¦ 0.013 ¦ ¦ Shelled Corn ¦ 25 ¦ 0.067 ¦ ¦ Shelled Corn ¦ 20 ¦ 0.040 ¦ ¦ Shelled Corn ¦ 18 ¦ 0.027 ¦ ¦ Shelled Corn ¦ 16 ¦ 0.013 ¦ ¦ Ear Corn ¦ 25 ¦ 0.107 ¦ ¦ Ear Corn ¦ 18 ¦ 0.053 ¦ ¦ Grain Sorghum ¦ 25 ¦ 0.080 ¦ ¦ Grain Sorghum ¦ 22 ¦ 0.067 ¦ ¦ Grain Sorghum ¦ 18 ¦ 0.040 ¦ ¦ Grain Sorghum ¦ 15 ¦ 0.027 ¦ ¦ Soybeans ¦ 25 ¦ 0.080 ¦ ¦ Soybeans ¦ 22 ¦ 0.067 ¦ ¦ Soybeans ¦ 18 ¦ 0.040 ¦ ¦ Soybeans ¦ 15 ¦ 0.027 ¦ Compiled from USDA Leaflet 332 (1952) and Univ. of Georgia Bulletin NS 33 (1958). ![image](/image/placeholder) ROOF CAP HATCH ROOF DISTRIBUTOR VENT WET GRAIN PRIMARY DRYING ZONE ↕0.3 to 0.6 m DRY GRAIN TRANSITION DUCT HEATER PERFORATED FLOOR AIR PLENUM FAN Fig. 6 Three Zones Within Grain During Full-Bin Drying the temperature of the drying air by no more than 6 K above ambi- ent. The temperature should not exceed about 27°C after heating. Overheating the drying air causes the grain to overdry and dry non- uniformly; heat is recommended only to counteract adverse weather conditions. Electric controllers can be applied to fan and heater operation to achieve the final desired grain moisture content. Drying takes place in a drying zone, which advances upward through the grain (Figure 6). Grain above this drying zone remains at or slightly above the initial moisture content, while grain below the drying zone is at a moisture content in equilibrium with the drying air. As the direction of air movement does not affect the rate of dry- ing, other factors must be considered in choosing the direction. A pressure system moves the moisture-laden air up through the grain, and it is discharged under the roof. If there are insufficient roof outlets, moisture may condense on the underside of metal roofs. During pressure system ventilation, the wettest grain is near the top 2019 ASHRAE Handbook-HVAC Applications (SI) ![image](/image/placeholder) FULL-BIN AIRFLOW 0.013 m3/s OCTOBER 22 15 to 17% HARVEST MOISTURE CONTENT per cubic metre OCTOBER 15 18% HARVEST MOISTURE CONTENT HALF-BIN AIRFLOW OCTOBER 8 AT LEAST 0.027 m3/s 21% HARVEST MOISTURE CONTENT per cubic metre QUARTER-BIN AIRFLOW AT LEAST 0.054 m3/s OCTOBER 1 24% HARVEST MOISTURE CONTENT per cubic metre □ Fig. 7 Example of Layer Filling of Corn surface and is easy to monitor. Fan and motor waste heat enter into the airstream and contribute to drying. A negative-pressure system moves air down through the grain. Moisture-laden air discharges from the fan to the outdoors; thus, roof condensation is not a problem. Also, the air picks up some solar heat from the roof. However, the wettest grain is near the bottom of the mass and is difficult to sample. Of the two systems, the pressure system is recommended because it is easier to manage. The following management practices must be observed to ensure the best performance of the dryer: 1. Minimize foreign material. A scalper-cleaner is recommended for cleaning the grain to reduce air pressure and energy requirements and to help provide uniform airflow for elimination of wet spots. 2. Distribute the remaining foreign material uniformly by installing a grain distributor. 3. Place the grain in layers and keep it leveled. 4. Start the fan as soon as the floor or ducts are covered with grain. 5. Operate the fan continuously with unheated air unless it is rain- ing heavily or there is a dense ground fog. Once all the grain is within 1% of desired storage moisture content, run the fans only when the relative humidity is below 70%. Layer Drying In layer drying, successive layers of wet grain are placed on top of dry grain. When the top 150 mm has dried to within 1% ofthe desired moisture content, another layer is added (Figure 7). Compared to full- bin drying, layering reduces the time that the top layers of grain remain wet. Because the effective airflow rate is greater for lower lay- ers, allowable harvest moisture content of grain in these levels can be greater than that in the upper layers. Either unheated air or air heated 6 to 11°C above ambient may be used, but using heated air controlled with a humidistat to prevent overdrying is most common. The first layer may be about 2 m deep, with successive layers of about 1 m. Batch-in-Bin Drying A storage bin adapted for drying may be used to dry several batches of grain during a harvest season, ifthe grain is kept to a shal- low layer so that higher airflow rates and temperatures can be used. After the batch is dry, the bin is emptied, and the cycle is repeated. The drying capacity of the batch system is greater than that of other in-storage drying systems. In a typical operation, batches of corn in 1 m depths are dried from an initial moisture content of 25% with 54°C air at the rate of about 0.33 m3/s per cubic metre. Considerable nonuniformity of moisture content may be present in the batch after drying is stopped; therefore, the grain should be well mixed as it is Inc. ASHRAE, 2019 user. single for Licensed | {}
664da8bc-ba31-440a-9379-0d35f3644277 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Drying and Storing Selected Farm Crops 26.7 ![image](/image/placeholder) DRYING FAN RECIRCULATING BATCH DRYER COOLING BIN DRYING FAN COOLING FAN CONTINUOUS-FLOW DRYER Fig. 8 Grain Recirculators Convert Bin Dryer to High-Speed Continuous-Flow Dryer placed into storage. If the mixing is done well, grain that is too wet equalizes in moisture with grain that is too dry before spoilage can occur. Aeration ofthe grain in storage will facilitate the equalization of moisture. Grain may be cooled in the dryer to ambient temperature before it is stored. Cooling is accomplished by operating the fan without the heater for about 1 h. Some additional drying occurs during the cooling process, particularly in the wetter portions of the batch. Grain stirring devices are used with both full-bin and batch-in- bin drying systems. Typically, these devices consist of one or more open, 50 mm diameter, standard pitch augers suspended from the bin roof and extending to near the bin floor. The augers rotate and simultaneously travel horizontally around the bin, mixing the dry- ing grain to reduce moisture gradients and prevent overdrying of the bottom grain. The augers also loosen the grain, allowing a higher airflow rate for a given fan. Stirring equipment reduces bin capacity by about 10%. Furthermore, commercial stirring devices are avail- able only for round storage enclosures. Recirculating/Continuous-Flow Bin Drying This type of drying incorporates a tapered sweep auger that re- moves uniform layers of grain from the bottom of the bin as it dries (Figure 8). The dry grain is then redistributed on top of the pile of grain or moved to a second bin for cooling. The sweep auger may be controlled by temperature or moisture sensors. When the desired condition is reached, the sensor starts the sweep auger, which re- moves a layer of grain. After a complete circuit ofthe bin, the sweep auger stops until the sensor determines that another layer is dry. Some drying takes place in the cooling bin. Up to two percentage points of moisture may be removed, depending on the management of the cooling bin. 2. DRYING SPECIFIC CROPS 2.1 SOYBEANS Soybeans usually need drying only when there is inclement weather during the harvest season. Mature soybeans left exposed to rain or damp weather develop a dark brown color and a mealy or chalky texture. Seed quality deteriorates rapidly. Oil from weather- damaged beans costs more to refine and is often not of edible grade. In addition to preventing deterioration, the artificial drying of soy- beans offers the advantage of early harvest, which reduces the chance of loss from bad weather and reduces natural and combine shatter loss. Soybeans harvested with a wet basis moisture content greater than 13.5% exhibit less damage. Drying Soybeans for Commercial Use Conventional corn-drying equipment can be used for soybeans, with some limitations on heat input. Soybeans for commercial use can be dried at 55 to 60°C; drying temperatures of 90°C reduce the oil yield. If the relative humidity of the drying air is below 40%, excessive seedcoat cracking occurs, causing many split beans in subsequent handling. Physical damage can cause fungal growth on the beans, storage problems, and a slight reduction in oil yield and quality. Flow-retarding devices should be used during handling, and beans should not be dropped more than 6 m onto concrete floors. Drying Soybeans for Seed and Food The relative humidity of the drying air should be kept above 40%, regardless of the amount of heat used. The maximum drying temperature to avoid germination loss is 43°C. Natural air drying at a flow rate of 0.0267 m3/s per cubic metre is adequate for drying seed with an initial moisture content of up to 16% w.b. If adding heat, raise the drying air temperature no more than 3 K above ambient. This drying method is slow, but it results in excellent quality and avoids overdrying. However, drying must be completed before spoilage occurs. At higher moisture contents, good results have been obtained using an airflow rate of 0.0534 m3/s per cubic metre with humidity control. Data on allowable drying time for soy- beans are unavailable. Without better information, an estimate of storage life for oil crops can be made based on the values for corn, using an adjusted moisture content calculated by the following equation: Oilseed moisture content Comparable moisture = x 100 content 100 - Seed oil content A corn moisture content 2% greater than that of the soybeans should generally be used to estimate allowable drying time (e.g., 12% soybeans are comparable to 14% corn). Soybeans are dried from a lower initial moisture content than corn. Dry high-moisture soybeans in a bin with the air temperature controlled to keep the relative humidity at 40% or higher. Airflow rates of 0.130 m3/s per cubic metre are recommended, with the depth of the beans not to exceed 1.2 m. 2.2 HAY Hay normally contains 65 to 80% wet basis moisture at cutting. Field drying to 20% may result in a large loss of leaves. Alfalfa hay leaves average about 50% of the crop by mass, but they contain 70% of the protein and 90% of the carotene. The quality of hay can be increased and the risk of loss due to bad weather reduced if the hay is put under shelter when partially field dried (35% moisture content) and then artificially dried to a safe storage moisture content. In good drying weather, hay conditioned by mechanical means can be dried sufficiently in one day and placed in the dryer. Hay may be long, chopped, or baled for this operation; unheated or heated air can be used. Inc. ASHRAE, 2019 user. single for Licensed | {}
e7a8d4c6-f80e-4b8a-8263-842df185e3da | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 26.8 2019 ASHRAE Handbook - HVAC Applications (SI) In-Storage Drying Unheated air is normally used for in-storage or mow drying. Hay is dried in the field to 30 to 40% moisture content before being placed in the dryer. For unheated air drying, airflow should be at least 0.10 m3/s per megagram. The fan should be able to deliver required airflow against static pressure of 250 to 500 Pa. Slotted floors, with at least 50% of the area open, are generally used for drying baled hay. For long or chopped hay in mows nar- rower than 1 1 m wide, the center duct system is the most popular. A slotted floor should be placed on each side of the duct to within 1.5 m ofits ends and the outer walls (Figure 9). Ifthe mow is wider than 11 m, it should be divided crosswise into units of 8.5 m or narrower. These should then be treated as individual dryers. If the storage depth exceeds about 4 m, vertical flues and/or additional levels of ducts may be used. If tiered ducts are used, a vertical air chamber, about 75% of the probable hay depth, should be used. The supply ducts are then connected at 2 to 3 m vertical intervals as the mow is filled. With either of these methods, hay in total depths up to 9 m can be dried. The duct size should be such that the air velocity is less than 5 m/s. The maximum depth of wet hay that should be placed on a hay- drying system at any time depends on hay moisture content, weather conditions, the physical form of the hay, and the airflow rate. The maximum drying depth is about 5 m for long hay, 4 m for chopped hay, and 7 small rectangular bales deep for baled hay. Baled hay should have a density of about 130 kg/m3. For best results, bales should be stacked tightly together on edge (parallel to the stems) to ensure that no openings exist between them. For mow drying, the fan should run continuously during the first few days. Afterward, it should be operated only during low relative humidity weather. During prolonged wet periods, the fan should be operated only enough to keep the hay cool. Batch w agon Drying Batch drying can be done on a slotted floor platform; however, because this method is labor-intensive, wagon dryers are more commonly used. With a wagon dryer system, hay is baled at about 45% moisture content to a density of about 180 kg/m3. The hay is then stacked onto a wagon with tight, high sides and a slotted or expanded metal floor. Drying is accomplished most efficiently by forcing the heated air (up to 70°C) down the canvas duct of a plenum chamber secured to the top of the wagon. After 4 or 5 h of drying, the exhaust air is no longer saturated with moisture, and about 75% of it may be recirculated or passed through a second wagon of wet hay for greater drying efficiency. In this method, the amount of hay harvested each day is limited by the capacity of the drying wagons. In this 24 h process, the hay cut one day is stored the following day; only enough hay to load the drying wagons should be harvested each day. ![image](/image/placeholder) CONCRETE BLOCKS 900 mm ON CENTER OR 38 by 184 mm ON EDGE MAIN DUCT 1500 mm 0 1200 mm mm 10 m 1200 38 by 140 mm 1500 mm 900 mm ON CENTER 250 mm 6 m AIR INTAKE OPENING 19 by 38 mm WOOD SLATS Fig. 9 Central Duct Hay-Drying System with Lateral Slatted Floor for Wide Mows The airflow rate in this method is normally much higher than when unheated air is used. About 0.2 m3/s per square metre of wagon floor space is required. As with mow drying, the duct size should be such that the air velocity is less than 5 m/s. 2.3 COTTON Producers normally allow cotton to dry naturally in the field to 12% moisture content or less before harvest. Cotton harvested in this manner can be stored in trailers, baskets, or compacted stacks for extended periods with little loss in fiber or seed quality. Thus, cotton is not normally aerated or artificially dried before ginning. Cotton harvested during inclement weather and stored cotton exposed to precipitation must be dried at the cotton gin within a few days to prevent self heating and deterioration of the fiber and seed. Though cotton may be safely stored at moisture contents as high as 12%, moisture levels near the upper limit are too high for efficient ginning and for obtaining optimum fiber grade. The cleaning effi- ciency of cotton is inversely proportional to its moisture content, with the most efficient level being 5% fiber moisture content. How- ever, fiber quality is best preserved when the fiber is separated from the seed at moisture contents between 6.5 and 8%. Therefore, if cot- ton comes into the system below this level, it can be cleaned, but moisture should be added before separating the fiber from the seed to improve the ginning quality. Dryers in the cotton gins are capable of drying the cotton to the desired moisture level. The tower dryer is the most commonly used among several types of commercially available dryers. This device operates on a parallel flow principle: 0.015 to 0.025 m3/s of drying air per kilo- gram of cotton also serves as the conveying medium. As it moves through the dryer's serpentine passages, cotton impacts on the walls. This action agitates the cotton for improved drying and lengthens its exposure time. Drying time depends on many vari- ables, but total exposure seldom exceeds 15 s. For extremely wet cotton, two stages of drying are needed for adequate moisture con- trol. Wide variations in initial moisture content dictate different drying amounts for each load of cotton. Rapid changes in drying require- ments are accommodated by automatically controlling drying air temperature in response to moisture measurements taken before or after drying. These control systems prevent overdrying and reduce energy requirements. For safety and to preserve fiber quality, drying air temperature should not exceed 177°C in any portion of the dry- ing system. If the internal cottonseed temperature does not exceed 60° C, germination is unimpaired by drying. This temperature is not exceeded in a tower dryer; however, the moisture content of the seed after drying may be above the 12% level recommended for safe long-term storage. Wet cottonseed is normally processed immediately at a cottonseed oil mill. Cottonseed under the 12% level is frequently stored for several months before milling or delinting and treatment at a seed processing plant. The aeration that cools deep beds of stored cottonseed effectively maintains viability and prevents an increase in free fatty acid content. For aeration, ambient air is normally drawn downward through the bed at a rate of at least 0.0004 m3/s per cubic metre of oil mill seed and 0.0021 m3/s per cubic metre of planting seed. 2.4 PEANUTS Peanuts normally have a moisture content of about 50% at the time of digging. Allowing the peanuts to dry on the vines in the windrow for a few days removes much of this water. However, pea- nuts usually contain 20 to 30% moisture when removed from the vines, and some artificial drying is necessary. Drying should begin within 6 h after harvesting to keep the peanuts from self heating. Inc. ASHRAE, 2019 user. single for Licensed | {}
bc8a409f-8a2a-4b52-8201-394c80a9d4a4 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Drying and Storing Selected Farm Crops 26.9 Both the maximum temperature and the rate of drying must be care- fully controlled to maintain quality. High temperatures result in an off flavor or bitterness. Drying too rapidly without high temperatures results in blandness or nuts that do not develop flavor during roasting. High temperatures, rapid drying, or excessive drying cause the skin to slip easily and the ker- nels to become brittle. These conditions result in high damage rates in the shelling operation but can be avoided if the moisture removal rate does not exceed 0.5% per hour. Because of these limitations, continuous-flow drying is not usually recommended for peanuts. Peanuts can be dried in bulk bins using unheated air or air with supplemental heat. Under poor drying conditions, unheated air may cause spoilage, so supplemental heat is preferred. Air should be heated no more than 7 to 8°C to a maximum temperature of 35°C. An airflow rate of 0.050 to 0.130 m3/s per cubic metre of peanuts should be used, depending on the initial moisture content. The most common method of drying peanuts is bulk wagon dry- ing. Peanuts are dried in depths of 1.5 to 1.8 m, using airflow rates of0.05 to 0.08 m3/s per cubic metre of peanuts and air heated 6 to 8 K above ambient. This method retains quality and usually dries the peanuts in three to four days. Wagon drying reduces handling labor but may require additional investment in equipment. 2.5 RICE Of all grains, rice is probably the most difficult to process with- out quality loss. Rice containing more than 13.5% moisture cannot be safely stored for long periods, yet the recommended harvest moisture content for best milling and germination ranges from 20 to 26%. When rice is harvested at this moisture content, drying must be started promptly to prevent souring. Normally, heated air is used in continuous-flow dryers, where large volumes of air are forced through 100 to 250 mm layers of rice. Temperatures as high as 55°C may be used, if (1) the temperature drop across the rice does not exceed 11 to 17 K, (2) the moisture reduction does not exceed two percentage points in a 0.5 h exposure, and (3) the rice temperature does not exceed 38°C. During the tempering period following dry- ing, the rice should be aerated to ambient temperature before the next pass through the dryer. This removes additional moisture and eliminates one to two dryer passes. It is estimated that full use of aeration following dryer passes could increase the maximum daily drying capacity by about 14%. Unheated air or air with a small amount of added heat (7 K above ambient, but not exceeding 35°C) should be used for deep-bed rice drying. Too much heat overdries the bottom, resulting in checking (cracking), reduced milling qualities, and possible spoilage in the top. Because unheated air drying requires less investment and attention than supplemental heat drying, it is preferred when conditions permit. In the more humid rice-growing areas, supplemental heat is desirable to ensure that the rice dries. The time required for drying varies with weather conditions, moisture content, and airflow rate. In California, the recommended airflow rate is 0.001 to 0.012 m3/s per cubic metre. Because of less favorable drying conditions in Arkan- sas, Louisiana, and Texas, greater airflow rates are recommended (e.g., a minimum of 0.01 m3/s per cubic metre is recommended in Texas). Whether unheated air or supplemental heat is used, the fan should be turned on as soon as rice uniformly covers the air distribu- tion system. The fan should then run continuously until the moisture content in the top 300 mm of rice is reduced to about 15%. At this point, the supplemental heat should be turned off. The rice can then be dried to a safe storage level by operating the fan only when the rel- ative humidity is below 75%. 3. STORAGE PROBLEMS AND PRACTICES 3.1 MOISTURE MIGRATION Redistribution of moisture generally occurs in stored grain when grain temperature is not controlled (Figure 10). Localized spoilage can occur even when the grain is stored at a safe moisture level. Grain placed in storage in the fall at relatively high temperatures cools nonuniformly through contact with the outer surfaces of the storage bin as winter approaches. Thus, the grain near the outer walls and roof may be at cool outdoor temperatures while the grain nearer the center is still nearly the same temperature it was at har- vest. These temperature differentials induce air convection currents that flow downward along the outer boundaries of the porous grain mass and upward through the center. When the cool air from the outer regions contacts the warm grain in the interior, the air is heated and its relative humidity is lowered, increasing its capacity to absorb moisture from the grain. When the warm, humid air reaches the cool grain near the top of the bin, it cools again and transfers vapor to the grain. Under extreme conditions, water condenses on the grain. The moisture concentration near the center of the grain surface causes significant spoilage if moisture migration is uncontrolled. During spring and summer, the temperature gradients are reversed. The grain moisture content increases most at depths of 600 to 1200 mm below the surface. Daily variations in temperature do not cause sig- nificant moisture migration. Aside from seasonal temperature vari- ations, the size of the grain mass is the most important factor in fall and winter moisture migration. In storages containing less than 35 m3, there is less trouble with moisture migration. The problem becomes critical in large storages and is aggravated by incomplete cooling of artificially dried grain. Artificially dried grain should be cooled to near ambient temperature soon after drying. 10°C 3.2 GRAIN AERATION Aeration by mechanically moving ambient air through the grain mass is the best way to control moisture migration. Aeration systems are also used to cool grain after harvest, particularly in warmer cli- mates where grain may be placed in storage at temperatures exceed- ing 38°C. After the harvest heat is removed, aeration may be continued in cooler weather to bring the grain to a temperature within 11 K of the coldest average monthly temperature. The temperature must be maintained below 10°C. Aeration systems are not a means of drying because airflow rates are too low. However, in areas where the climate is favorable, care- fully controlled aeration may be used to remove small amounts of moisture. Commercial storages may have pockets of higher- moisture grain if, for example, some batches of grain are delivered after a rain shower or early in the morning. Aeration can control heating damage in the higher-moisture pockets. ![image](/image/placeholder) HIGH MOISTURE CONTENT COC WARM LOW MOISTURE CONTENT AIRFLOW Fig. 10 Grain Storage Conditions Associated with Moisture Migration During Fall and Early Winter Inc. ASHRAE, 2019 user. single for Licensed | {}
01b07532-d31a-4134-bee2-9b90f778fe2d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 26.10 Aeration Systems Design Aeration systems include fans capable of delivering the required amount of air at the required static pressure, suitable ducts or floors to distribute the air into the grain, and controls to regulate the oper- ation of the fan. The airflow rate determines how many hours are required to cool the crop (Table 8). Most aeration systems are designed with airflow rates between 0.0007 to 0.0027 m3/s per cubic metre of grain. Stored grain is aerated by forcing air up or down through the grain. Upward airflow is more common because it is easier to ob- serve when the cooling front has moved through the entire grain mass. In large, flat storages with long ducts, upward airflow re- sults in more uniform air distribution than downdraft systems. During aeration, a warming or cooling front moves through the crop (Figure 1 1); it is important to run the fan long enough to move the front completely through the crop. Static pressure for an aeration system can be determined using the airflow resistance information in Chapter 11 of the 2005 ASHRAE Handbook- -Fundamentals. All common types of fans are used in aeration systems. Attention should be given to noise levels with fans that are operated near residential areas or where people work for extended periods. The supply ducts connecting the fan to the distribution ducts in the grain should be designed and constructed according to the standards of good practice for any air-moving application. A maximum air velocity of 13 m/s may be used, but 8 to 10 m/s is preferred. In large systems, one large fan may be attached to a manifold duct leading to several distribution ducts in one or more storages, or smaller individual fans may serve individual distribution ducts. Where a manifold is used, valves or dampers should be installed at each takeoff to allow adjustment or closure of airflow when part of the aerator is not needed. Table 8 Airflow Rates Corresponding to Approximate Grain Cooling Time ¦ Airflow Rate, m3/s per cubic metre of grain ¦ Cooling Time, h ¦ ¦ --- ¦ --- ¦ ¦ 0.0007 ¦ 240 ¦ ¦ 0.0013 ¦ 120 ¦ ¦ 0.0027 ¦ 60 ¦ ¦ 0.0040 ¦ 40 ¦ ¦ 0.0054 ¦ 30 ¦ ¦ 0.0067 ¦ 24 ¦ ¦ 0.0080 ¦ 20 ¦ ¦ 0.0107 ¦ 15 ¦ ¦ 0.0134 ¦ 12 ¦ 2019 ASHRAE Handbook-HVAC Applications (SI) Distribution ducts are usually perforated sheet metal with a cir- cular or inverted U-shaped cross section, although many func- tional arrangements are possible. The area of the perforations should be at least 10% of the total duct surface. The holes should be uniformly spaced and small enough to prevent the passage of the grain into the duct (e.g., 2.5 mm holes or 2 mm wide slots do not pass wheat). Since most problems develop in the center of the storage, and the crop cools naturally near the wall, the aeration system must provide good airflow in the center. Flush floor systems work well in storages with sweep augers and unloading equipment. Ducts should be easily removable for cleaning. Duct spacing should not exceed the depth of the crop; the distance between the duct and storage structure wall should not exceed one-half the depth of the crop for bins and flat storages. Common duct patterns for round bins are shown in Figure 12. Duct spacing for flat storages is shown in Figure 13. When designing the distribution duct system for any type of stor- age, the following should be considered: (1) the cross-sectional area and length of the duct, which influences both the air velocity within the duct and the uniformity of air distribution; (2) the duct surface area, which affects the static pressure losses in the grain surrounding the duct; and (3) the distance between ducts, which influences the uniformity of airflow. For upright storages where distribution ducts are relatively short, duct velocities up to 10 m/s are permissible. Maximum rec- ommended air velocities in ducts for flat storages are shown in Table 9. Furthermore, these velocities should not be exceeded in the air outlets from the storage; therefore, an air outlet area at least equal to the duct cross-sectional area should be provided. The duct surface area that is perforated or otherwise open for air distribution must be great enough that the air velocity through the Table 9 Maximum Recommended Air Velocities Within Ducts for Flat Storages ¦ Grain ¦ Airflow Rate, m3/s per cubic metre (grain) ¦ Air Velocity (m/s) within Ducts for Grain Depths of: ¦ Air Velocity (m/s) within Ducts for Grain Depths of: ¦ Air Velocity (m/s) within Ducts for Grain Depths of: ¦ Air Velocity (m/s) within Ducts for Grain Depths of: ¦ Air Velocity (m/s) within Ducts for Grain Depths of: ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Grain ¦ Airflow Rate, m3/s per cubic metre (grain) ¦ 3 m ¦ 6 m ¦ 9 m ¦ 12 m ¦ 15 m ¦ ¦ Corn, soybeans, and other large grains ¦ 0.0007 ¦ ¦ 3.8 ¦ 5.0 ¦ 6.3 ¦ 6.3 ¦ ¦ Corn, soybeans, and other large grains ¦ 0.0013 ¦ 3.8 ¦ 5.0 ¦ 6.3 ¦ 7.6 ¦ 8.8 ¦ ¦ Corn, soybeans, and other large grains ¦ 0.0027 ¦ 5.0 ¦ 6.3 ¦ - ¦ ¦ ¦ ¦ Wheat, grain sorghum, and other small grains ¦ 0.0007 ¦ ¦ 5.0 ¦ 7.6 ¦ 8.8 ¦ 10.0 ¦ ¦ Wheat, grain sorghum, and other small grains ¦ 0.0013 ¦ 3.8 ¦ 7.6 ¦ 10.0 ¦ ¦ ¦ ¦ Wheat, grain sorghum, and other small grains ¦ 0.0027 ¦ 5.0 ¦ 10.0 ¦ ¦ ¦ ¦ ![image](/image/placeholder) TEMPERED GRAIN COOLING OR WARMING ZONE MOVES DOWN THROUGH GRAIN GRAIN TO BE TEMPERED NEGATIVE-PRESSURE AERATION Fig. 11 Aerating to Change Grain Temperature ![image](/image/placeholder) GRAIN TO BE TEMPERED COOLING OR WARMING ZONE MOVES UP THROUGH GRAIN TEMPERED GRAIN POSITIVE-PRESSURE AERATION Inc. ASHRAE, 2019 user. single for Licensed | {}
ebbba884-88c5-44b0-a8dd-661f206eea70 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Drying and Storing Selected Farm Crops 26.11 grain surrounding the duct is low enough to avoid excessive pres- sure loss. When a semicircular perforated duct is used, the entire surface area is effective; only 80% of the area of a circular duct rest- ing on the floor is effective. For upright storages, the air velocity through the grain near the duct (duct face velocity) should be limited to 0.15 m/s or less; in flat storages, to 0.10 m/s or less. Duct strength and anchoring are important. If ducts placed directly on the floor are to be held in place by the crop, the crop flow should be directly on top ofthe ducts to prevent movement and dam- age. Distribution ducts buried in the grain must be strong enough to withstand the pressure the grain exerts on them. In tall, upright stor- ages, static grain pressures may reach 70 kPa. When ducts are located in the path of the grain flow, as in a hopper, they may be sub- jected to many times this pressure during grain unloading. Operating Aeration Systems The operation of aeration systems depends largely on the objec- tives to be attained and the locality. In general, cooling should be ![image](/image/placeholder) UNLOADING H AUGER FAN FOR BIN UP TO . 18 ft DIAMETER FOR BIN UP TO 24 ft DIAMETER MINIMUM 1/2 BIN DIAMETER FOR BIN UP TO 30 ft DIAMETER carried out any time the outdoor air temperature is about 8 K cooler than the grain. Stored grain should not be aerated when the air humidity is much above the equilibrium humidity of the grain because moisture will be added. The fan should be operated long enough to cool the crop completely, but it should then be shut off and covered, thus limiting the amount of grain that is rewetted. Aeration to cool the grain should be started as soon as the storage is filled, and cooling air temperatures are available. Aeration to pre- vent moisture migration should be started whenever the average air temperature is 6 to 8 K below the highest grain temperature. Aeration is usually continued as weather permits until the grain is uniformly cooled to within 11 K of the average temperature of the coldest month, or to 0 to 5°C. Grain temperatures of about 0 to 10°C are desirable. In the northern corn belt, aeration may be resumed in the spring to equal- ize the grain temperature and raise it to between 5 to 10°C This reduces the risk of localized heating from moisture migration. Storage problems are the only reason to aerate when air tempera- tures are above 15°C. Aeration fans and ducts should be covered when not in use. In storages where fans are operated daily in fall and winter months, automatic controls work well when air is not too warm or humid. One thermostat usually prevents fan operation when the air temperature is too high, and another prevents operation when the air is too cold. A humidistat allows operation when the air is not too humid. Fan controllers that determine the equilib- rium moisture content of the crop based on existing air condi- tions can regulate the fan based on entered information. 4. SEED STORAGE Seed must be stored in a cool, dry environment to maintain via- bility. Most seed storages have refrigeration equipment to main- tain a storage environment of 7 to 12°C. Seed storage conditions must be achieved before mold and insect damage occur. Fig. 12 Common Duct Patterns for Round Grain Bins ![image](/image/placeholder) BUILDINGS UP TO 18 m TO 36 m WIDE BUILDINGS UP TO 12 m WIDE AND 30 m LONG FAN AERATION DUCT X BUILDINGS UP TO 12 m WIDE AND 48 m LONG UP TO 18 m UP TO 36 m AERATION DUCT FAN PERFORATED DUCTS FAN- GRAIN PEAKED WITH SHALLOW DEPTH NEAR WALL FANS SPACING EQUAL TO LEAST GRAIN DEPTH AERATION DUCT (A) IS SHORTEST AIR PATH MAKE (B) OR (C) NO MORE THAN 1.5 TIMES (A) Fig. 13 Duct Arrangements for Large Flat Storages Inc. ASHRAE, 2019 user. single for Licensed | {}
5762465a-8a25-4cc3-9e23-c1cd27ff34c1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 26.12 2019 ASHRAE Handbook- - HVAC Applications (SI) BIBLIOGRAPHY ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. ASAE. 1993. Density, specific gravity, and mass-moisture relationships of grain for storage. ANSI/ASAE Standard D241.4. American Society of Agricultural Engineers (now American Society of Agricultural and Bio- logical Engineers), St. Joseph, MI. ASAE. 1995. Moisture relationship of plant-based agricultural products. ASAE Standard D245.5. American Society of Agricultural Engineers (now American Society of Agricultural and Biological Engineers), St. Joseph, MI. ASAE. 1996. Resistance of airflow of grains, seeds, other agricultural prod- ucts, and perforated metal sheets. ASAE Standard D272.2. American Society of Agricultural Engineers (now American Society of Agricul- tural and Biological Engineers), St. Joseph, MI. Brooker, D.B., F. Bakker-Arkema, and C.W. Hall. 1992. Drying and storage of grains and oilseeds. Van Nostrand, Reinhold, NY. MidWest Plan Service. 1988. Grain drying, handling and storage handbook. MWPS-13. Iowa State University, Ames. MidWest Plan Service. 1980. Low temperature and solar grain drying hand- book. MWPS-22. Iowa State University, Ames. MidWest Plan Service. 1980. Managing dry grain in storage. AED-20. Iowa State University, Ames. Hall, C.A. 1980. Drying and storage of agricultural crops. AVI Publishing, Westport, CT. Hellevang, K.J. 1989. Crop storage management. AE-791. NDSU Exten- sion Service, North Dakota State University, Fargo. Hellevang, K.J. 1987. Grain drying. AE-701. NDSU Extension Service, North Dakota State University, Fargo. Hellevang, K.J. 1983. Natural air/low temperature crop drying. EB-35. NDSU Extension Service, North Dakota State University, Fargo. Saver, D.B. (ed.) 1992. Storage of cereal grains and their products. Ameri- can Association of Cereal Chemists, St. Paul, MN. Schuler, R.T, B.J. Holmes, R.J. Straub, and D.A. Rohweder. 1986. Hay dry- ing. A3380. University of Wisconsin-Extension, Madison. Inc. ASHRAE, 2019 user. single for Licensed Related Commercial Resources | {}
46b7e677-3653-4d68-9639-32da78968551 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 27 AIR CONDITIONING OF WOOD AND PAPER PRODUCT FACILITIES General Wood Product Operations 27.1 Pulp and Paper Operations 27.2 T HIS chapter covers some of the standard requirements for air conditioning of facilities that manufacture finished wood prod- ucts as well as for pulp and paper product process operations. Special Warning: Certain industrial spaces may contain flam- mable, combustible, and/or toxic concentrations of vapors or dusts under either normal or abnormal conditions. In spaces such as these, there are life-safety issues that this chapter may not completely address. Special precautions must be taken in accordance with requirements ofrecognized authorities such as the National Fire Pro- tection Association (NFPA), the Occupational Safety and Health Administration (OSHA), and the American National Standards Institute (ANSI). In all situations, engineers, designers, and install- ers who encounter conflicting codes and standards must defer to the code or standard that best addresses and safeguards life safety. 1. GENERAL WOOD PRODUCT OPERATIONS In wood product manufacturing facilities, ventilation can be con- sidered a part of the process. Metal ductwork should be used and grounded to prevent a buildup of static electricity. Hoods should be made of spark-free, noncombustible material. A pneumatic conveying system should be furnished to reduce the accumulation of wood dust in the collecting duct system. The airflow rate and velocity should be able to maintain the air-dust mixture below the minimum explosive The preparation of this chapter is assigned to TC 9.2, Industrial Air Conditioning. X-Axis: Temperature, °C Y-Axis: Relative Humidity % Chart Type: line -20°C 0°C 40°C 50°C 60°C 70°C 80°C 90°C 100°C item_01 90% 80% 70% 60% 50% 40% 30% 20% 10% concentration level. If dampers are unavoidable in the system, they should be firmly fastened after balancing work. Dust collectors should be located outside the building. Fans or blowers should be placed downstream of the dust collector and air-cleaning equipment, and should be interlocked with the wood-processing equipment. When the fan or blower stops, the wood process should stop immediately and forward a signal to the alarm system. Deflagration venting and suppression should be furnished for wood-processing workshops and wood-processing equipment such as vessels, reactors, mixers, blenders, mills, dryers, ovens, filters, dust collectors, storage equipment, material-handling equipment, and aerosol areas. The deflagration suppression system must be dis- armed before performing any maintenance work to avoid possible injury from discharging the suppressant. Warning signs should be displayed prominently at all maintenance access points. Finished lumber products to be used in heated buildings should be stored in areas that are heated 6 to 11 K above ambient. This pro- vides sufficient protection for furniture stock, interior trim, cabinet material, and stock for products such as ax handles and glue-lami- nated beams. Air should be circulated within the storage areas. Lumber that is kiln-dried to a moisture content of 12% or less can be kept within a given moisture content range through storage in a heated shed. The moisture content can be regulated either manually or automatically by altering the dry-bulb temperature (Figure 1). Some special materials require close control of moisture content. For example, musical instrument stock must be dried to a given moisture level and maintained there because the moisture content of % CONTENT, MOISTURE EQUILIBRIUM Fig. 1 Relationship of Temperature, Relative Humidity, and Vapor Pressure of Air and Equilibrium Moisture Content of Wood 27.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
d4a3181b-aff6-4561-ab28-e85b0b5fc0ed | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 27.2 2019 ASHRAE Handbook-HVAC Applications (SI) the wood affects the harmonics of most stringed wooden instru- ments. This control may require air conditioning, heating, and/or humidification, with or without reheating. Process Area Air Conditioning Temperature and humidity requirements in wood product pro- cess areas vary according to product, manufacturer, and governing code. For example, in match manufacturing, the match head must be cured (i.e., dried) after dipping. This requires careful control of humidity and temperature to avoid a temperature near the ignition point. Any process involving application of flammable substances should follow the ventilation recommendations of the National Fire Protection Association, the National Fire Code, and the U.S. Occu- pational Safety and Health Act. Finished Product Storage Finished lumber to be made into furniture, equipment parts, musical instruments, architectural woodwork, or other wood prod- ucts of value is stored and/or manufactured under controlled tem- perature and humidity to maintain proper wood dryness. Improper drying can cause laminated or glued joints to fail. Finished wood that has changed dimension because of excess moisture gain or loss can cause fitting problems. Cracking, splitting, checking, warping, and discoloration can also occur in improperly dried and/or stored wood. Green, rough, cut lumber is stacked end to end in layers, each layer being separated by wood strips to allow air circulation. Lum- ber can be stacked and left to dry naturally in open-sided sheds. Enclosed, heated kilns with steam coils and/or direct steam injec- tion, forced air circulation, makeup air, and exhaust air vents could be used where faster, controlled drying is preferred. Drying (or addi- tion of moisture) can be accomplished by HVAC systems using dehumidifying coils and/or desiccants, heating/reheat coils, humid- ifiers, makeup and exhaust air, distribution air ducts, and automatic controls. An insulated dehumidifying/humidifying room could be constructed and finished to minimize moisture migration from higher-humidity areas. Lumber can also be dried by solar kilns, microwaves, dielectric heating, superheated steam, and vacuum. Inc. ASHRAE, 2019 user. single for Licensed W ood is composed of natural fibers and moisture content varies according to the environment. Samples from the wood being dried must be tested for moisture content at predetermined time intervals to prevent overdrying and defects. Drying rates are determined by the wood species. Final moisture content depends upon the wood's ultimate use. The formula for determining moisture content is Mass of sample - x 100 Mass of oven- when cut dried sample Moisture Mass of oven-dried sample content, % Lumber/wood drying using HVAC systems can be accomplished with factory- or field-assembled systems. The quantity of lumber/ wood to be dried, wood species, rate of drying, total moisture removal, drying room construction, economics (cost and rate of return on investment), fire and safety codes, maintenance, and ease of use influence the type ofHVAC system to be installed. 2. PULP AND PAPER OPERA TIONS The papermaking process comprises two basic steps: (1) wood is reduced to pulp (i.e., wood fibers), and (2) the pulp is converted to paper. W ood can be pulped by either mechanical action (e.g., grind- ing in a groundwood mill), chemical action (e.g., kraft pulping), or a combination of both. Many different types of paper can be produced from pulp, rang- ing from the finest glossy finish to newsprint to bleached board to fluff pulp for disposable diapers. To make newsprint, a mixture of mechanical and chemical pulps is fed into the paper machine. To make kraft paper (e.g., grocery bags, corrugated containers), how- ever, only unbleached chemical pulp is used. Disposable diaper material and photographic paper require bleached chemical pulp with a very low moisture content of 6 to 9%. Paper Machine Area In papermaking, extensive air systems are required to support and enhance the process (e.g., by preventing condensation) and to provide reasonable comfort for operating personnel. Radiant heat from steam and hot-water sources and mechanical energy dissipated as heat can result in summer temperatures as high as 50°Cin the machine room. In addition, high paper machine operating speeds of 10 to 23 m/s and a stock temperature near 50°C produce warm vapor in the machine room. Outdoor air makeup units and process exhausts absorb and remove room heat and water vapor released from the paper as it is dried (Figure 2). Makeup air is distributed to working areas above and below the operating floor. Part of the air delivered to the base- ment migrates to the operating floor through hatches and stairwells. Motor-cooling equipment distributes cooler basement air to the paper machine drive motors. Wet and basement exhaust should be installed inside the room. Outdoor air intakes with insulated adjustable louvers should be installed on the outside wall to supplement the mechanical air sup- ply. In facilities with no basement exterior wall, sufficient mechan- ical air intake should be provided. The exhaust, adjustable louver, or mechanical air intake should be furnished with modulating control. When the ambient temperature drops to near freezing, outdoor air- flow must be reduced to a minimum and the appropriate heater started to prevent freezing. The most severe ventilation demand occurs in the area between the wet-end forming and press sections and the dryer section. In the forming section, the pulp slurry, which contains about 90% water, is deposited on a traveling screen. Gravity, rolls, foils, vacuum, steam boxes, and three or more press roll nips are sequentially used to remove up to 50% of the water in the forming and press sections. The wet end is very humid because of evaporation of moisture and mechanical generation of vapor by turning rolls and cleaning show- ers. Baffles and a custom-designed exhaust in the forming section help control the vapor. A drive-side exhaust in the wet end removes heat from the motor vent air and removes the process generated vapor. To prevent condensation or accumulated fiber from falling on the traveling web, a false ceiling is used with ducts connected to roof ![image](/image/placeholder) ROOF FALSE CEILING ROOF HEATING EXHAUST EXHAUST SUPPLY FAN FAN UNIT ROOM FALSE CEILING AIR HEAT RECOVERY HOOD PAPER EXHAUST MACHINE EXHAUST FAN HOOD PLENUM ROOM ○ AIR POCKET VENT DRYER SUPPLY UNIT · ▲ ▲ POCKET INFILTRATION VENTILATION DRYER INFILTRATION BASEMENT OUTSIDE OUTSIDE AIR ENCLOSURE AIR Fig. 2 Paper Machine Area | {}
b271b9df-82e5-467e-a015-62d82e66a38c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Air Conditioning of w ood and Paper Product Facilities 27.3 exhausters that remove humid air not captured at a lower point. At the wet end, heated inside air is usually circulated to scrub the underside of the roof to prevent condensation in cold weather. Addi- tional roof exhaust may also remove accumulated heat from the dryer section and the dry end during warmer periods. Ventilation in the wet end should be predominantly accomplished by roof exhaust. The large volume of moisture and vapor generated from the wet-end process rises and accumulates under the roof. To keep condensation from forming in winter, the roofis normally exhaust- ed and hot air is distributed under the roof. Sufficient roof insula- tion should be installed to keep the inside surface temperature above the dew point. Heat transfer from the room to the interior surface is tr tis tis to R R is-o r-is where tr = room air temperature, °C tis roof interior surface temperature, °C to outdoor air temperature, °C Rr-is heat transfer resistance from room air to roof interior surface. In winter, Rr-is = 0.11 (m2. K)/W Ris-o = required total R-value from roof interior surface to outdoor air, (m2.K)/W For a given project, to and tr have been determined and only tis needs to be selected. For wet-end roof insulation and assuming 96% relative humidity, tis can be shown on a psychrometric chart to be tis = tr-0.7°C Then Equation (1) can be simplified to find the required roof R-value as 0.11 Ris-o = (tr - to - 0.7) 0.7 In the dryer section, the paper web is dried as it travels in a ser- pentine path around rotating steam-heated drums. Exhaust hoods remove heat from the dryers and moisture evaporated from the paper web. Most modern machines have enclosed hoods, which reduce the airflow required to less than 50% of that required for an open-hood exhaust. The temperature inside an enclosed hood ranges from 50 to 60°C at the operating floor to 80 to 95°C in the hood exhaust plenum at 70 to 90% rh, with an exhaust rate generally ranging from 140 to 190 m3/s per machine. Where possible, pocket ventilation air (see Figure 3) and hood supply air are drawn from the upper level of the machine room to take advantage of the preheating of makeup air by process heat as it rises. The basement of the dryer section is also enclosed to control infiltration of machine room air to the enclosed hood. The hood supply and the pocket ventilation air typically operate at 95°C; how- ![image](/image/placeholder) POCKET DRYER VENTILATOR PAPER WEB DRYER Fig. 3 Pocket Ventilation (1) (2) ever, some systems run as high as 120°C. Enclosed hood exhaust is typically 0.16 m3/s per megagram of machine capacity. The pocket ventilation and hood supply are designed for 75 to 80% of the ex- haust, with the balance infiltrated from the basement and machine room. Large volumes of air (240 to 380 m3/s) are required to balance the paper machine's exhaust with the building air balance. (3) The potential for heat recovery from hood exhaust air should be evaluated. Most of the energy in steam supplied to the paper dryers is converted to latent heat in the hood exhaust as water evaporates from the paper web. Air-to-air heat exchangers are used where the air supply is located close to the exhaust. Air-to-liquid heat exchangers that recirculate water/glycol to heat remote makeup air units can also be used. Air-to-liquid systems provide more latent heat recovery, resulting in three to four times more total heat recov- ery than air-to-air units. Some machines use heat recovered from the exhaust air to heat process water. Ventilation in paper machine buildings in the United States ranges from 10 to 25 air changes per hour in northern mills to 20 to 50 in southern mills. In some plants, computers monitor the production rate and outdoor air temperature to optimize operation and conserve energy. After fine, bond, and cut papers have been bundled and/or pack- aged, they should be wrapped in a nonpermeable material. Most papers are produced with less than 10% moisture by mass, the aver- age being 7%. Dry paper and pulp are hygroscopic and begin to swell noticeably and deform permanently when the relative humid- ity exceeds 38%. Therefore, finished products should be stored under controlled conditions to maintain their uniform moisture con- tent. Finishing Area To produce a precisely cut paper that stabilizes at a desirable equilibrium moisture content, the finishing areas require tempera- ture and humidity control. Further converting operations such as printing and die cutting require optimum sheet moisture content for efficient processing. Finishing room conditions range from 21 to 24°C db and from 40 to 45% rh. Rooms should be maintained within reasonably close limits of the selected conditions. Without precise environmental control, the paper equilibrium moisture content var- ies, influencing dimensional stability, the tendency to curl, and fur- ther processing. Process and Motor Control Rooms In most pulp and paper applications, process control, motor con- trol, and switchgear rooms are separate from the process environ- ment. Air conditioning removes heat generated by equipment, lights, etc., and reduces the air-cleaning requirement. (See Chapter 20 for air conditioning in control rooms that include a computer, a com- puter terminal, or data processing equipment.) Ceiling grilles or dif- fusers should be located above access aisles to avoid the risk of condensation on control consoles or electrical equipment during start-up and recovery after an air-conditioning shutdown. Electrical rooms are usually maintained in the range of24 to 27°C, with control rooms at 23°C; the humidity is maintained in the range of 45 to 55% in process control rooms and is not normally controlled in electrical equipment rooms. Motor and electrical control rooms for process and electrical dis- tribution control contain electronic equipment that is susceptible to corrosion. The typical pulp and paper mill environment contains both particulate and vapor-phase contaminants with sulfur- and chloride-based compounds. To protect equipment, multistage partic- ulate and adsorbent filters should be used. They should have treated activated charcoal and potassium permanganate-impregnated alu- mina sections for vapor-phase contaminants, as well as fiberglass and cloth media for particulates. To ensure normal operation of air-conditioning systems, re- dundancy of supply fans, fan motors, and fan power supply in air- Inc. ASHRAE, 2019 user. single for Licensed | {}
2e7ff9c1-6ba4-4bb2-9d5c-9117ca265d81 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 27.4 2019 ASHRAE Handbook-HVAC Applications (SI) handling units that serve process control rooms and motor control centers is strongly recommended in new-construction plants. Switchgear and motor control centers are not as heat-sensitive as control rooms, but the moisture-laden air carries chemical residues onto the contact surfaces. Arcing, corrosion, and general deteriora- tion can result. A minimum amount of filtered, outdoor air and air conditioning is used to protect these areas. In most projects, the electric distribution control system (DCS) is energized before the room air conditioning is installed and started. Ifa temporary air conditioner is used in the DCS room, a condensate drain pan and temporary drain pipe should be installed to keep con- densate from the cable channel beneath the DCS panels. Paper Testing Laboratories Design conditions in paper mill laboratories must be followed rigidly. The most recognized standard for testing environments for paper and paper products (paperboard, fiberboard, and con- tainers) is TAPPI (the Technical Association of the Pulp and Paper Industry) Standard T402. ASTM E171 is also relevant. Standard pulp and paper testing laboratories have three envi- ronments: preconditioning, conditioning, and testing. The physi- cal properties of a sample are different if it is brought to the testing humidity from a high humidity than if it is brought from a lower humidity. Preconditioning at lower relative humidity tends to eliminate hysteresis. For a preconditioning atmosphere, TAPPI Standard T402 recommends 10 to 35% rh and 22 to 40°C db. Samples are usually conditioned in a controlled, conditioned cabinet. Conditioning and testing atmospheres should be maintained at 50 土 2.0% rh and 23°C 士 1 K db. However, a change of 1 K db at 23°C without starting a humidifier causes the relative humidity to fluctuate as much as 3%. A dry-bulb temperature tolerance of ±0.5 K must be held to maintain a ±2% rh. A well-designed tem- perature and humidity control system should be provided. Miscellaneous Areas The pulp digester area contains many components that release heat and contribute to dusty conditions. For batch digesters, the chip feeders are a source of dust and need hooded exhaust and makeup air. The wash and screen areas have numerous components with hooded exhausts that require considerable makeup air. Good venti- lation controls fumes and humidity. The lime kiln feed-end releases extremely large amounts of heat and requires high ventilation rates or air conditioning. Recovery-boiler and power-boiler buildings have conditions similar to those of power plants; the ventilation rates are also simi- lar. The control rooms are generally air conditioned. The grinding motor room, in which groundwood is made, contains many large motors that require ventilation to keep the humidity low. System Selection The system and equipment selected for air conditioning a pulp and paper mill depends on many factors, including the plant layout and atmosphere, geographic location, roof and ceiling heights (which can exceed 30 m), and degree of control desired. Chilled- water systems are economical and practical for most pulp and paper operations, because they have both the large cooling capacity needed by mills and the precision of control to maintain the proper temperature and humidity in laboratories and finishing areas. In the bleach plant, the manufacture of chlorine dioxide is enhanced by using water with a temperature of 7°C or lower; this water is often supplied by the chilled-water system. If clean plant or process water is available, water-cooled chillers are satisfactory and may be sup- plemented by water-cooled direct-expansion package units for small, remote areas. However, if plant water is not clean enough, a separate cooling tower and condenser water system should be installed for the air conditioning. Most manufacturers prefer water-cooled over air-cooled sys- tems because of the gases and particulates present in most paper mills. The most prevalent contaminants are chlorine gas, caustic soda, borax, phosphates, and sulfur compounds. With efficient air cleaning, the air quality in and about most mills is adequate for properly placed air-cooled chillers or condensing units that have properly applied coil and housing coatings. Phosphor-free brazed coil joints are recommended in areas where sulfur compounds are present. Heat is readily available from processing operations and should be recovered whenever possible. Most plants have good-quality hot water and steam, which can be used for unit heater, central station, or reheat quite easily. Evaporative cooling should be considered. Newer plant air-conditioning methods, using energy conservation techniques such as temperature destratification and stratified air conditioning, have application in large structures. Absorption sys- tems should be considered for pulp and paper mills because they provide some degree of energy recovery from the high-temperature steam processes. BIBLIOGRAPHY ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. ACGIH. 2009. Industrial ventilation: A manual of recommended practice, 29th ed. American Conference of Governmental Industrial Hygienists, Cincinnati, OH. ASTM. 2015. Standard specification for standard atmospheres for condi- tioning and testing flexible barrier materials. Standard E171-11 (2015). American Society for Testing and Materials, West Conshohocken, PA. TAPPI. 2009. Conditioning and testing atmospheres for paper, board, pulp handsheets, and related products. ANSI/TAPPI Test Method T402. Tech- nical Association of the Pulp and Paper Industry, Norcross, GA. Inc. ASHRAE, 2019 user. single for Licensed Related Commercial Resources | {}
b748df6d-2d0d-4efb-aee7-87dd86fcf7db | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 28 POWER PLANTS General Design Criteria 28.1 Ventilation Approach 28.4 Applications 28.4 Steam Generator Buildings: Industrial and Power Facilities ・・ 28.5 Turbine Generator Building 28.7 Combustion Turbine Areas · 28.9 Main Control Center 28.9 T HIS chapter discusses HVAC systems for industrial facilities that produce process heat and power and for electrical generating stations and transmission facilities. Not every type of power plant is specifically covered, but the process areas addressed normally correspond to similar process areas in any given plant. For example, wood-fired boilers are not specifically discussed, but the requirements for coal-fired boilers generally apply. Aspects of HVAC system design unique to nuclear power plants are covered in Chapter 29. Caution: Certain industrial spaces may contain flammable, com- bustible, and/or toxic concentrations of vapors or dusts under either normal or abnormal conditions. In spaces such as these, there are fire- and life-safety issues that may be beyond the scope of this chap- ter and not completely addressed. Recognized authorities such as the National Fire Protection Association (NFPA), the Occupational Safety and Health Administration (OSHA), the American National Standards Institute (ANSI), the facility's insurance carriers, and au- thorities having jurisdiction (AHJs) can be consulted for advice regarding specific situations. In all situations, engineers, designers, and installers who encounter conflicting codes and standards must defer to the code or standard that best addresses and safeguards life safety or seek advice from the AHJ and insurance carrier. 1. GENERAL DESIGN CRITERIA Space-conditioning systems in power plant buildings are de- signed to maintain an environment conducive to reliable operation of power generation systems and equipment and the convenience and safety of plant personnel. A balance should be achieved between the cost of the process systems designed to operate in a specified environment and the cost of providing HVAC to modify or condition the environment. Environmental criteria for personnel safety and comfort are gov- erned by several sources. The U.S. Occupational Safety and Health Administration (OSHA) defines noise, thermal environment, and air contaminant exposure limits. Chapters 15 and 32 of this volume and Industrial Ventilation by the American Conference of Governmen- tal Industrial Hygienists (ACGIH 2016) also provide guidance for safety in work spaces, primarily in the areas ofindustrial ventilation and worker-related heat stress. Worker comfort is somewhat subjec- tive and more difficult to quantify. The plant owner or operator ordinarily establishes the balance between cost and worker comfort. Exhaust vents are subject to regulation of the plant's air quality permit and local air pollution control board' s requirements. For this reason, all exhaust vent locations should be properly identified and classified, and coordinated with the plant's environmental compli- ance permits. Treatment of exhaust streams is discussed in Chapter The preparation of this chapter is assigned to TC 9.2, Industrial Air Condi- tioning. ¦ Substation and Switchyard Control Structures ¦ 28.9 ¦ ¦ --- ¦ --- ¦ ¦ Turbine Lubricating Oil Storage. ¦ 28.10 ¦ ¦ Oil Storage and Pump Buildings. ¦ 28.10 ¦ ¦ Coal Crusher and Coal Transportation ¦ ¦ ¦ System Buildings 4+ ¦ 28.10 ¦ ¦ --- ¦ --- ¦ ¦ Heating/Cooling Systems ¦ 28.11 ¦ ¦ Energy Recovery ¦ 28.12 ¦ ¦ Safety Considerations ¦ 28.12 ¦ 30 of the 2016 ASHRAE Handbook- -HVAC Systems and Equip- ment. Criteria should be clearly defined at the start of design, because they document an understanding between the process designer and the HV AC system engineer that is fundamental to achieving the envi- ronment required for the various process areas. Typical criteria for a coal-fired power plant are outlined in Table 1 Review criteria for compliance with local codes, the plant operator's experience and preferences, and the facility's overall financial objectives. Additional discussion of criteria may be found in the sections on specific areas. Temperature and Humidity Due to the heavy mass of buildings and structures at fuel-fired power plants, brief variations in outdoor air temperature have little or no short-term effect on indoor temperatures, even when those areas are ventilated with 100% outdoor air. (It takes a couple of months to achieve equilibrium on some of these structures.) Chapter 14 of the 2017 ASHRAE Handbook-Fundamentals shows outdoor design in the 0.4% (Cooling)/99.6% (Heating) col- umns that suggests that the outdoor temperatures for cooling load design can exceed those in the tables about 0.4% of the time annu- ally. Because temperature excursions above the ASHRAE design outdoor air temperatures are brief (1 to 4 h), the effect on indoor room temperature is considered to be negligible. Hence, using out- door temperatures as shown in Chapter 14 of the 2017 ASHRAE Handbook-Fundamentals for the design of HVAC systems is acceptable. Certain areas such as electrostatic precipitator transformer/recti- fier (TR) set and control enclosures are sometimes cooled with 100% outdoor air. These and other similar enclosures are typically insulated prefabricated structures with little or no thermal mass. Although the ASHRAE 99.6%/0.4% conditions may be adequate, extreme weather conditions or other cooling methodologies need to be considered. Indoor temperatures should match the specified operating tem- peratures of the equipment. Electrical equipment (such as switchgear, motor control centers, and motors) typically determines the design temperature limits in the plant; common temperature rat- ings are 40 or 50°C. Other areas such as elevator machine rooms may include electronic equipment with temperature restrictions. In plant areas where compressed-gas containers are stored, the design temperature is dictated by the gas supplier. Typically, the minimum temperature should be high enough that the gas volume can be effectively released from the containers. If the gas is hazard- ous (e.g., chlorine), the minimum temperature does not apply during personnel occupancy periods, when high dilution ventilation rates are needed. Practical ventilation rates for fuel-fired power plants provide in- door conditions 6 to 11 K above the outdoor ambient. Therefore, 28.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
84f91e17-b8ff-4f2c-8621-fddf6da27960 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 28.2 2019 ASHRAE Handbook-HVAC Applications (SI) Table 1 Design Criteria for Fuel-Fired Power Plant ¦ Building/Area ¦ Design Outdoor Cooling/ Heating Dry-Bulba ¦ Indoor Temperature, °C ¦ Indoor Temperature, °C ¦ Relative Humidity, % ¦ Room Ventilation Rate, ach* ¦ Filtration Efficiency, % ¦ Pressur- ization ¦ Redundancyb ¦ Noise Criterion ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Building/Area ¦ Design Outdoor Cooling/ Heating Dry-Bulba ¦ Maximum ¦ Minimum ¦ Relative Humidity, % ¦ Room Ventilation Rate, ach* ¦ Filtration Efficiency, % ¦ Pressur- ization ¦ Redundancyb ¦ Noise Criterion ¦ ¦ Steam Turbine Area ¦ Steam Turbine Area ¦ Steam Turbine Area ¦ Steam Turbine Area ¦ Steam Turbine Area ¦ Steam Turbine Area ¦ Steam Turbine Area ¦ Steam Turbine Area ¦ Steam Turbine Area ¦ Steam Turbine Area ¦ ¦ Suboperating level ¦ 0.4%/99.6% ¦ Design outdoor + 6 ¦ 7 ¦ None ¦ 30 ¦ None ¦ None ¦ Multiplicity ¦ Background ¦ ¦ Above operating floor ¦ 0.4%/99.6% ¦ Design outdoor + 6 ¦ 7 ¦ None ¦ 10 ¦ None ¦ None ¦ Multiplicity ¦ Background ¦ ¦ Combustion Turbine Area ¦ 0.4%/99.6% ¦ Design outdoor + 5 ¦ 7 ¦ None ¦ 20 ¦ None ¦ None ¦ Multiplicity ¦ Background ¦ ¦ Steam Generator Area ¦ Steam Generator Area ¦ Steam Generator Area ¦ Steam Generator Area ¦ Steam Generator Area ¦ Steam Generator Area ¦ Steam Generator Area ¦ Steam Generator Area ¦ Steam Generator Area ¦ Steam Generator Area ¦ ¦ Below burner elevation ¦ 0.4%/99.6% ¦ Design outdoor + 6 ¦ 7 ¦ None ¦ 30 ¦ None ¦ None ¦ Multiplicity ¦ Background ¦ ¦ Above operating floor ¦ 0.4%/99.6% ¦ Design outdoor + 6 ¦ 7 ¦ None ¦ 15 ¦ None ¦ None ¦ Multiplicity ¦ Background ¦ ¦ Other Non-Air-Conditioned Areas ¦ Other Non-Air-Conditioned Areas ¦ Other Non-Air-Conditioned Areas ¦ Other Non-Air-Conditioned Areas ¦ Other Non-Air-Conditioned Areas ¦ Other Non-Air-Conditioned Areas ¦ Other Non-Air-Conditioned Areas ¦ Other Non-Air-Conditioned Areas ¦ Other Non-Air-Conditioned Areas ¦ Other Non-Air-Conditioned Areas ¦ ¦ Shops ¦ 1%/99% ¦ Design outdoor + 6 ¦ 18 ¦ None ¦ 15 ¦ None ¦ None ¦ None ¦ 85 dBA ¦ ¦ Air-Conditioned Areasd ¦ Air-Conditioned Areasd ¦ Air-Conditioned Areasd ¦ Air-Conditioned Areasd ¦ Air-Conditioned Areasd ¦ Air-Conditioned Areasd ¦ Air-Conditioned Areasd ¦ Air-Conditioned Areasd ¦ Air-Conditioned Areasd ¦ Air-Conditioned Areasd ¦ ¦ Control rooms and control equipment rooms con- taining instruments and electronics ¦ 0.4%/99.6% ¦ 24 1 ¦ 22 1 ¦ 30 to 65 ¦ ASHRAE Std. 62.1 ¦ 85 to 90 (see text) ¦ Positive ¦ 100% ¦ NC-40° ¦ ¦ Offices ¦ 1%/99% ¦ 26 ¦ 21 ¦ 30 to 65 ¦ ASHRAE Std. 62.1 ¦ ASHRAE Std. 62.1 ¦ Positive ¦ None ¦ See text ¦ ¦ Laboratories ¦ 1%/99% ¦ 26 ¦ 21 ¦ 30 to 65 ¦ ASHRAE Std. 62.1 ¦ High ¦ Positive ¦ None ¦ See text ¦ ¦ Locker rooms and toilets ¦ 1%/99% ¦ 26 ¦ 21 ¦ None ¦ ASHRAE Std. 62.1 ¦ ASHRAE Std. 62.1 ¦ Negative ¦ None ¦ See text ¦ ¦ Shops (air-conditioned) ¦ 1%/99% ¦ 26 ¦ 18 ¦ None ¦ ASHRAE Std. 62.1 ¦ None ¦ None ¦ None ¦ 85 dBA ¦ ¦ Mechanical Equipment ¦ Mechanical Equipment ¦ Mechanical Equipment ¦ Mechanical Equipment ¦ Mechanical Equipment ¦ Mechanical Equipment ¦ Mechanical Equipment ¦ Mechanical Equipment ¦ Mechanical Equipment ¦ Mechanical Equipment ¦ ¦ Pumps, large power ¦ 0.4%/99.6% ¦ Design outdoor + 6 ¦ 7 ¦ None ¦ 30 ¦ None ¦ None ¦ Multiplicity ¦ Background ¦ ¦ Valve stations, miscellaneous ¦ 0.4%/99.6% ¦ Design outdoor + 6 ¦ 7 ¦ None ¦ 15 ¦ None ¦ None ¦ None ¦ 85 dBA ¦ ¦ Elevator machine rooms ¦ 0.4%/99.6% ¦ 32 ¦ 7 ¦ None ¦ None ¦ Low ¦ Positive ¦ None ¦ 85 dBA ¦ ¦ Fire pump area ¦ 0.4%/99.6% ¦ NFPA Std. 20 ¦ NFPA Std. 20 ¦ None ¦ NFPA Std. 20 ¦ None ¦ None ¦ None ¦ 85 dBA ¦ ¦ Diesel generator area ¦ 0.4%/99.6% ¦ Design outdoor + 6 ¦ 7 ¦ None ¦ 30 ¦ None ¦ None ¦ None ¦ Background ¦ ¦ Electrical Equipmentd ¦ Electrical Equipmentd ¦ Electrical Equipmentd ¦ Electrical Equipmentd ¦ Electrical Equipmentd ¦ Electrical Equipmentd ¦ Electrical Equipmentd ¦ Electrical Equipmentd ¦ Electrical Equipmentd ¦ Electrical Equipmentd ¦ ¦ Enclosed transformer equipment areas ¦ 0.4%/99.6% ¦ Design outdoor + 6 ¦ 7 ¦ None ¦ 60 ¦ Low ¦ Positive ¦ 100% ¦ 85 dBA ¦ ¦ Critical equipment ¦ 0.4%/99.6% ¦ Design outdoor + 6 ¦ 7 ¦ None ¦ 30 ¦ None ¦ Positive ¦ 100% ¦ 85 dBA ¦ ¦ Miscellaneous electrical equipment ¦ 0.4%/99.6% ¦ Design outdoor + 6 ¦ 7 ¦ None ¦ 20 ¦ None ¦ None ¦ Multiplicity ¦ 85 dBA ¦ ¦ Water Treatment equipment rooms ¦ Water Treatment equipment rooms ¦ Water Treatment equipment rooms ¦ Water Treatment equipment rooms ¦ Water Treatment equipment rooms ¦ Water Treatment equipment rooms ¦ Water Treatment equipment rooms ¦ Water Treatment equipment rooms ¦ Water Treatment equipment rooms ¦ Water Treatment equipment rooms ¦ ¦ Chlorine When temporarily occupied ¦ 0.4%/99.6% ¦ Design outdoor + 6 ¦ None ¦ None ¦ 60 ¦ None ¦ Negative ¦ None ¦ 85 dBA ¦ ¦ When unoccupied ¦ 0.4%/99.6% ¦ Design outdoor + 6 ¦ 16 ¦ None ¦ 15 ¦ None ¦ Negative ¦ None ¦ 85 dBA ¦ ¦ Chemical treatment ¦ 0.4%/99.6% ¦ Design outdoor + 6 ¦ 16 ¦ None ¦ 10 ¦ None ¦ None ¦ None ¦ 85 dBA ¦ ¦ Battery Roomse ¦ 0.4%/99.6% ¦ 25e ¦ 25e ¦ None ¦ As required for hydrogen dilution ¦ None ¦ Negative or neutral ¦ Multiplicity ¦ 85 dBA ¦ ¦ Substations ¦ 0.4%/99.6% ¦ 24 to 27f ¦ 21 ¦ None ¦ IEEE Std. C2; ASHRAE Std. 62.1 ¦ 30 to 65%g ¦ Positive ¦ 100% ¦ NC-55h ¦ ¦ *Listed numbers are for estimating purposes only. When heat gain data are available, use Equation dSee ASHRAE research project RP-1104 (White and Pahwa 2003) and (1) to calculate required ventilation rate. RP-1395 (White and Piesciorovsky 2010) for heat release values. aSee Chapter 14 of the 2017 ASHRAE Handbook-Fundamentals for design dry-bulb temperature °See ASHRAE Guideline 21-2012 and section on Battery Rooms in this data corresponding to given annual cumulative frequency of occurrence and specific geographic chapter. location of plant. fSubstation maintained for telecom ¦ *Listed numbers are for estimating purposes only. When heat gain data are available, use Equation dSee ASHRAE research project RP-1104 (White and Pahwa 2003) and (1) to calculate required ventilation rate. RP-1395 (White and Piesciorovsky 2010) for heat release values. aSee Chapter 14 of the 2017 ASHRAE Handbook-Fundamentals for design dry-bulb temperature °See ASHRAE Guideline 21-2012 and section on Battery Rooms in this data corresponding to given annual cumulative frequency of occurrence and specific geographic chapter. location of plant. fSubstation maintained for telecom ¦ *Listed numbers are for estimating purposes only. When heat gain data are available, use Equation dSee ASHRAE research project RP-1104 (White and Pahwa 2003) and (1) to calculate required ventilation rate. RP-1395 (White and Piesciorovsky 2010) for heat release values. aSee Chapter 14 of the 2017 ASHRAE Handbook-Fundamentals for design dry-bulb temperature °See ASHRAE Guideline 21-2012 and section on Battery Rooms in this data corresponding to given annual cumulative frequency of occurrence and specific geographic chapter. location of plant. fSubstation maintained for telecom ¦ *Listed numbers are for estimating purposes only. When heat gain data are available, use Equation dSee ASHRAE research project RP-1104 (White and Pahwa 2003) and (1) to calculate required ventilation rate. RP-1395 (White and Piesciorovsky 2010) for heat release values. aSee Chapter 14 of the 2017 ASHRAE Handbook-Fundamentals for design dry-bulb temperature °See ASHRAE Guideline 21-2012 and section on Battery Rooms in this data corresponding to given annual cumulative frequency of occurrence and specific geographic chapter. location of plant. fSubstation maintained for telecom ¦ *Listed numbers are for estimating purposes only. When heat gain data are available, use Equation dSee ASHRAE research project RP-1104 (White and Pahwa 2003) and (1) to calculate required ventilation rate. RP-1395 (White and Piesciorovsky 2010) for heat release values. aSee Chapter 14 of the 2017 ASHRAE Handbook-Fundamentals for design dry-bulb temperature °See ASHRAE Guideline 21-2012 and section on Battery Rooms in this data corresponding to given annual cumulative frequency of occurrence and specific geographic chapter. location of plant. fSubstation maintained for telecom ¦ *Listed numbers are for estimating purposes only. When heat gain data are available, use Equation dSee ASHRAE research project RP-1104 (White and Pahwa 2003) and (1) to calculate required ventilation rate. RP-1395 (White and Piesciorovsky 2010) for heat release values. aSee Chapter 14 of the 2017 ASHRAE Handbook-Fundamentals for design dry-bulb temperature °See ASHRAE Guideline 21-2012 and section on Battery Rooms in this data corresponding to given annual cumulative frequency of occurrence and specific geographic chapter. location of plant. fSubstation maintained for telecom ¦ *Listed numbers are for estimating purposes only. When heat gain data are available, use Equation dSee ASHRAE research project RP-1104 (White and Pahwa 2003) and (1) to calculate required ventilation rate. RP-1395 (White and Piesciorovsky 2010) for heat release values. aSee Chapter 14 of the 2017 ASHRAE Handbook-Fundamentals for design dry-bulb temperature °See ASHRAE Guideline 21-2012 and section on Battery Rooms in this data corresponding to given annual cumulative frequency of occurrence and specific geographic chapter. location of plant. fSubstation maintained for telecom ¦ *Listed numbers are for estimating purposes only. When heat gain data are available, use Equation dSee ASHRAE research project RP-1104 (White and Pahwa 2003) and (1) to calculate required ventilation rate. RP-1395 (White and Piesciorovsky 2010) for heat release values. aSee Chapter 14 of the 2017 ASHRAE Handbook-Fundamentals for design dry-bulb temperature °See ASHRAE Guideline 21-2012 and section on Battery Rooms in this data corresponding to given annual cumulative frequency of occurrence and specific geographic chapter. location of plant. fSubstation maintained for telecom ¦ *Listed numbers are for estimating purposes only. When heat gain data are available, use Equation dSee ASHRAE research project RP-1104 (White and Pahwa 2003) and (1) to calculate required ventilation rate. RP-1395 (White and Piesciorovsky 2010) for heat release values. aSee Chapter 14 of the 2017 ASHRAE Handbook-Fundamentals for design dry-bulb temperature °See ASHRAE Guideline 21-2012 and section on Battery Rooms in this data corresponding to given annual cumulative frequency of occurrence and specific geographic chapter. location of plant. fSubstation maintained for telecom ¦ *Listed numbers are for estimating purposes only. When heat gain data are available, use Equation dSee ASHRAE research project RP-1104 (White and Pahwa 2003) and (1) to calculate required ventilation rate. RP-1395 (White and Piesciorovsky 2010) for heat release values. aSee Chapter 14 of the 2017 ASHRAE Handbook-Fundamentals for design dry-bulb temperature °See ASHRAE Guideline 21-2012 and section on Battery Rooms in this data corresponding to given annual cumulative frequency of occurrence and specific geographic chapter. location of plant. fSubstation maintained for telecom ¦ temperature equipment. bMultiplicity indicates that the HVAC system should have multiple units. gEquivalent to rough-in MERV 6 prefilter and MERV 12 secondary filter. °See Figure 7 in Chapter 8 ofthe 2017 ASHRAE Handbook-Fundamentals for noise criterion curves. hLower criteria should be considered for occupied substations. Inc. ASHRAE, 2019 user. single for Licensed | {}