9c083673-2b17-424d-825c-8c9b480bf9e2 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Power Plants 28.3 ventilation design criteria establish a temperature rise above the design outdoor temperature to produce an expected indoor tem- perature that matches the electrical equipment ratings. For example, an outdoor extreme design temperature of 44°C with a ventilation system designed for a 6 K rise would meet the require- ments of 50°C-rated plant equipment. Because excursions above selected design outdoor air temperature are often brief (e.g., 2 to 3 h), the effect on room temperature is minimal. In addition, the electrical equipment temperature ratings are associated with de- sign life, not sudden failures. In hot climates where outdoor temperatures may cause indoor temperatures to exceed electrical equipment ratings for extended periods, evaporative cooling or air conditioning of electrical equipment areas may be required to hold temperatures below the equipment design values. When high area temperatures are possible, the quality of environment for plant maintenance workers should also be considered. Velocity (spot) cooling may be necessary in some areas to support work ac- tivities. Low temperatures may affect plant reliability because of the po- tential for freezing. Selection of the low design temperature should be balanced by selection of the heating design margin. The indoor design temperatures of 2 to 4°C may be used for providing for freeze protection. In the heating system design, credit is generally not taken for heat generated from operating equipment. The selection of outdoor design humidity levels affects the selec- tion of cooling towers and evaporative cooling processes and the sizing of air-conditioning coils for outdoor air loads. When values from Chapter 14 of the 2017 ASHRAE Handbook-Fundamentals are used for design, the mean coincident wet bulb is appropriate. If extreme dry-bulb temperatures are selected for the design basis, the use of extreme wet bulbs is too restrictive because the extremes are not coincident. It is prudent to use the wet bulb associated with the 1% dry bulb when extreme dry-bulb temperatures are used for design. Indoor design humidity is not a factor in ventilated areas unless the plant is in a harsh, corrosive environment. In this case, lower humidity reduces the potential for corrosion. In air-conditioned areas for personnel or electronic equipment, ASHRAE Standard 62.1, Instrumentation, Systems, and Automation Society (ISA) Standard 71.04, and manufacturers' recommendations dictate the humidity criteria. Equipment Selection Equipment should be selected to successfully operate in the localized environment in which it is installed. This may require additional insulation (as opposed to that required for a typical com- mercial space) on equipment such as air handlers and piping located in hot areas (i.e., 43 to 49°C). Direct-expansion condensing units may need to be selected for ambient environments greater than 35°C iflocated on building roof decks or where higher than ambient tem- peratures can be expected. In urban industrial areas, HVAC items such as copper coils and piping may need to be either coated with a polyurethane, polyester, or epoxy coating or special ordered using suitable materials to pro- tect the equipment from corrosion caused by hydrogen sulfide, ammonia, and similar substances. Equipment located inside powerhouses that may be subjected to the effect of flue gas, fly ash, coal dust, etc., should be specified to operate within that environment. Ventilation Rates Ventilation within plant structures provides heat removal and dilution of potentially hazardous gases. Ventilation rates for heat removal are calculated during HVAC system design to meet sum- mer indoor design temperatures. The numbers in Table 1 for air change rates are for estimating ap- proximate ventilation needs. Actual heat emission rates should be obtained from equipment manufacturers (White and Piesciorovsky 2010; White et al. 2004). American Boiler Manufacturer's Associa- tion (ABMA) heat loss curves (Stultz and Kitto 2005) can be used to approximate heat loads from boiler casings if better information is not available. The ventilation rate for room heat removal is q Q = tr to cp (1) where 0 = ventilation rate, m3/s 9 = room heat, kW tr = suggested room temperature from Table 1, °C to = outdoor air temperature, °C air density, kg/m3 Cp = specific heat of air = 1.0 kJ/(kg·K) Hazardous gases are mostly handled by the process system design functions. Natural gas and other combustible fuel gases are controlled by ignition safeties and may contain odorants for detection. Hydrogen and other gases used for generator and bus cooling are monitored for leakage by pressure loss or makeup rates. Escaped gases are diluted by outdoor air infiltration. For a building with very tight construction (i.e., very little natural infiltration), perform an analysis to verify that dilution rates are acceptable. Flue gas is confined to the boiler and flue gas ductwork and gen- erally poses no hazard. In some types of boilers and associated gas ducts, however, flue gas is at a higher pressure than the surroundings and can leak into occupied areas. Also, special-treatment gases such as ammonia or sulfur compounds encountered in flue gas condition- ing systems can leak into the boiler building, depending on the location of the treatment device in the flue gas stream. In these cases, gas detection monitors should be used. Some areas containing combustible liquids may require a mini- mum ventilation rate of 5 L/(s·m2) as required by NFPA Standard 30, with compressed gas storage areas falling under NFPA Stan- dard 55. Chlorine Room Ventilation Chlorine gas is often used in power generation facilities for treat- ment of raw water coolant, cooling tower/condenser water, potable water, and sanitary sewage treatment. Based on an immediately dan- gerous to life or health (IDLH) concentration of 10 mg/kg, chlorine is classified as corrosive and a highly toxic chemical, and the ventila- tion system designer should review the latest safety data sheets and recommended/required exposure/control limits before undertaking a ventilation design (NIOSH 1994). The chlorine storage room is required to have a dedicated exhaust designed to operate anytime the room or facility is occupied and to operate in the event a leak is detected. The ventilation system should consist of supply and exhaust fans. The ventilation system should not be operated continuously unless required to maintain the storage room at a slight negative pressure with respect to an adjoining space. Any chlorine leak in the room should be contained and exhausted to the environment in a controlled manner. Exhaust intakes should be located within about 305 mm of the floor because chlorine is heavier than air. The supply air source should be located high and designed to provide a clean sweep of the room, ensuring good air distribution. A minimum ventilation rate of 5 L/(s·m2) or 30 air changes per hour (whichever is higher) for the chlorine room is recommended. The fan switches with indicating lights, along with the light switch, should be located just outside the chlorine room entry door, which should have a small transparent glass window. Because chlorine gas is corrosive, the exhaust fan should be designed with a totally Inc. ASHRAE, 2019 user. single for Licensed | {}
56433f54-032a-4435-952a-db043f1c9bef | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 28.4 2019 ASHRAE Handbook-HVAC Applications (SI) enclosed corrosion-protected motor. Heating should be provided in the room to maintain temperatures at about 10 to 16°C to ensure freeze protection is provided to the valve train and associated gas pip- ing. The heating source should not be any local combustion device (e.g., a gas fired unit heater); electric is preferable. The hot airflow should be directed away from chlorine storage containers. The max- imum room temperature should be maintained at less than 52°C. Chlorine detection should be provided where possible, with local and possibly remote alarming to enable activation of the ventilation system and discharge any leaked chlorine in a controlled manner. Ventilation system and chlorine room designers should obtain additional information on ventilation system design requirements from NFPA Standards 55 and 400, Centers for Disease Control (NIOSH), OSHA, and information from chlorine manufacturers and suppliers. Infiltration and Exfiltration Infiltration of outdoor air into boiler and power-generation struc- tures and exfiltration of room air from these buildings are driven by thermal buoyancy ofheated air. Both infiltration and exfiltration are beneficial; infiltration air dilutes fugitive fumes, whereas exfiltration air carries out excess heat during hot weather. However, infiltration adds to the cold-weather load on the heating system. Filtration and Space Cleanliness Filtration of ventilation air for process areas is usually not needed because some process areas are dirtier than the outdoor sur- roundings, and the process equipment is designed to operate in a dusty environment. However, the plant may be located in an area with sources of outdoor particulate contaminants that need to be managed to protect the process equipment. Power plants in dusty or sandy areas, or where there are seasonal nuisances such as airborne plant matter, may require filtration of ventilation air. Plants at industrial sites such as refineries and paper mills may need to address gaseous contaminants and corrosive gases, as well. Indoor air cleanliness is a concern in control room HV AC system design. Even if the control center is in an independent building, remote from the boiler-turbine building, other operations such as coal transportation, coal crushing, fuel/air distribution and com- bustion, ash handling, fume heat recovery, fume/smoke exhaust diffusion, and so forth may contaminate the entire plant and its sur- roundings. When potential outdoor contaminants are a factor, the quality of outdoor air may need to be evaluated. This may include collection of typical particulates and the use of corrosion coupons to quantify gaseous contaminants. The U.S. Environmental Protection Agency (EPA) is a good data source. Filtration requirements may include 30% dust-spot test efficiency prefilters, 65 to 90% efficiency final filters, and gas-phase filtration units. Air-conditioned areas for people should satisfy ASHRAE Standard 62.1 requirements. Air-conditioned areas for control and electrical equipment should meet the requirements of the equipment manufacturer(s). Guidelines for reliability of electrical equipment are found in ISA Standard 71.04. Redundancy Maintaining design operating temperatures in the power plant is essential for reliable operation. Operating electrical equipment above its rated temperature reduces equipment life. Sensitive electronic equipment, such as in the main control center, may not function reli- ably at high temperatures. Low temperatures also affect plant avail- ability; for example, low temperatures in batteries or freezing of pipes, instrument lines, or tanks could prevent normal operation. The HV AC systems or components essential for plant operation should be designed with redundancy to ensure plant availability. Automatic switchover to the back-up system may be required in normally unoccupied areas. Where back-up systems are impracti- cal, consider using temperature monitoring and alarming systems to initiate temporary corrective measures. HVAC systems that include multiple units (indicated as "multi- plicity" in Table 1) also improve power plant reliability. A space ventilated by multiple fans, such as four at 1/4 capacity, may retain sufficient ventilation even if one fan is out of service. Noise Pay attention to noise levels produced by HVAC system equip- ment both inside and outside plant spaces, and establish indoor noise guidelines for air-conditioned areas and ventilated areas with continuous occupancies. Outdoor noise levels are established by the environmental noise pollution concerns of adjacent areas. Air-conditioned indoor spaces should meet the normal sound level guidelines for occupancies (e.g., offices) listed in Chapter 49. Special occupancies such as control rooms should follow the guide- lines in Table 1. Ventilated areas of the plant should be treated as other industrial areas following OSHA regulations. Sound levels in Table 1 are sug- gested guidelines that may be appropriate in the absence of a specific engineered solution to meet the OSHA requirements. Where "back- ground" is indicated in Table 1, noise generated by HVAC equipment is usually not a major noise source in comparison to the noise from processes or equipment such as turbine generators, motors, pumps, and relieving of process steam. In these areas, overall noise level cri- teria are established by the process equipment requirements. HVAC system components contribute to the overall noise level outside the plant buildings either by generating noise or by having ventilation openings. HVAC designs for power plants in urban areas can be significantly influenced by outdoor noise level require- ments. Equipment may have to include sound-absorbing materials or be located indoors in sound attenuation enclosures. Openings may require acoustical louvers. Ductwork and Equipment Location All outdoor HV AC equipment should be secured to foundations or structures to prevent being blown into transmission and other equip- ment in the event ofhigh winds. In addition, ductwork and equipment in the room should be adequately supported and restrained to prevent collateral damage to the switching equipment by failed HV AC equip- ment/ductwork in the event of an earthquake or similar event, following local codes and plant design criteria. Preventing damage from dripping/overflowing condensate or other water sources should also be considered. Also, where possible, equipment and system com- ponents must meet CAN/CSA Standard C2.1 and NFPA Standard 70 guidance for minimum distance from energized transmission equip- ment to ensure adequate separation from energized equipment and power lines. 2. VENTILA TION APPROACH Summer ventilation can be achieved by natural draft, forced mechanical supply and exhaust, or natural and mechanical combined systems. Natural-draft systems use a combination of adjustable inlet louvers and open doors or windows and relieve warmed air through roof or high side-wall openings. Mechanical systems use fans, power roof ventilators (PRVs), or air-handling units to move air. A combined system typically uses lower and upper wall and roof openings for natural ventilation while using mechanical ventilation as a supplement. With any ventilation arrangement, maintain physical separation of inlet and outlet openings to minimize recirculation, as discussed in Chapter 24 of the 2017 ASHRAE Handbook- -Funda- mentals. Inc. ASHRAE, 2019 user. single for Licensed | {}
4b8283b0-4c32-4ef5-abd6-090a8541e73a | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Power Plants 28.5 3. APPLICATIONS Large plants or units with layouts containing large ducts and equipment in the ventilation airflow path, possibly with limited separation between pieces of major equipment and/or exterior walls, imposing a pressure drop exceeding the capability of gravity ventilation systems, require mechanical assistance. The plant design may have cavities, such as the area under the boiler arch and between the casing and flue gas duct (see Figures 1 and 2), which require mechanical ventilation. Areas of the plant such as the con- veyor gallery usually require mechanical assistance in the makeup air system to ensure pressurization control and proper functioning of dust collectors and associated equipment. Natural or gravity systems are appropriate for facilities without basements and with relatively open airflow paths. The pressure drop of intake louvers, control dampers, powerhouse airflow path, and exhaust louvers/gravity vents should not exceed the minimum ex- pected buoyancy forces. Be sure to configure the system so as not to interfere with mechanical dust collection equipment. In any system configuration, the engineer should ensure all areas of the plant are provided airflow. Air intakes and supply ducts/fans should be located to prevent short-circuiting with relief openings. Ventilation air should be supplied to electrical boards and other equipment located in upper elevations of the plant, because these areas are usually significantly hotter than the lower elevations. Driving Forces Natural ventilation systems use the thermal buoyancy of the air as the motive force for air movement through a building. Equations for determining differential pressures for natural ventilation are found in Chapter 16 of the 2017 ASHRAE Handbook-Fundamen- tals. With natural ventilation, air enters the enclosed space and is heated by the plant equipment. The difference in density between the inside air and the outdoor air causes air to be drawn into the building at low elevations and relieved at high elevations. Mechanical ventilation depends on fans (or fans and buoyancy forces) to provide required ventilation regardless of the building configuration or the temperature difference. Air Distribution With natural ventilation, small differential pressures drive air movement. Accordingly, air is drawn into the building at low veloc- ities; it penetrates a short distance into the building and then disperses. Mechanical ventilation supplied from the walls or roof can dis- tribute air more effectively throughout the structure. A combined system uses both natural and mechanical ventilation to achieve effective air distribution and prevent air stagnation. A typ- ical combined system uses lower-level sidewall openings as the primary natural air intake and roof or upper-level sidewall openings for hot-air relief. The location and size of openings can prevent hot- air accumulation under the roof naturally. Provide mechanical ventilation where sufficient airflow cannot otherwise be established. Inlet and Exhaust Areas Because of the low differential pressure driving the air, natural ventilation requires numerous large inlet louver and exhaust relief areas. Mechanical ventilation requires fewer openings. Noise Openings required for natural ventilation allow noise generated by indoor plant equipment to pass more easily to the outdoors. Mechanical equipment such as fans and PRVs generate noise directly, but the noise level can be managed by fan selection and acoustical treatment. Plant Cleanliness Natural ventilation creates negative pressure in the lower por- tions of the building, which may draw dust and fumes into the building through openings near ground level. Mechanical ventilation can pressurize the building and can draw air from relatively clean sources at higher elevations. Economics The primary advantage to natural ventilation is that there are no operating costs for fan power. Because natural ventilation is pas- sive, it is more reliable and has lower maintenance costs than a mechanical system. However, natural ventilation may not always be the most economical selection. The cost of louvers and inlet open- ings, architectural features, and gravity relief openings to achieve an acceptable ventilation rate may be higher than the first cost for mechanical ventilation. Another consideration is the average building temperature. Be- cause internal heat is the driving force, the naturally ventilated building is normally warmer than the power-ventilated building. This warmer average temperature may shorten the life of plant equipment such as expansion joints, seals, motors, electrical switch- gear, and instrumentation. Warmer temperatures may also affect operator performance. The large louver areas associated with natural ventilation may allow greater infiltration, thereby increasing the winter heating load. This additional heating cost may offset some of the summer energy savings of natural ventilation. A combined system takes on the s5trengths of both natural and mechanical ventilation and can offer the advantages of reduced cap- ital and operating costs. 4. STEAM GENERATOR BUILDINGS: INDUSTRIAL AND POWER FACILITIES A steam generator uses heat energy to convert water to steam. The two basic subsystems of a steam generator are the heat energy system and the steam process system. The heat energy system for a fueled (oil, gas, coal, etc.) steam generator includes fuel distribution piping or conveyors, prepara- tion subsystems, and supply rate and ignition controls. Provision to supply and regulate combustion air is required at the combustion chamber; flue gas is handled downstream of the combustion area. With ash-producing fuels, bottom ash below the steam generator and fly ash entrained in the flue gas must be processed. Figure 1 shows a steam generator building with typical components. Steam process components typically found in the steam genera- tor building include an enclosure for the fire and heat transfer sur- faces and feedwater equipment such as pumps, piping, and controls. Steam lines for primary and reheat steam are typically routed from the steam drum and reheat sections of the steam generator to the steam turbine or process systems. The heat energy and steam process systems impose requirements on the HVAC systems for specific areas of the steam generator building. Burner Areas Fuel (gas, oil, coal, etc.) is transferred to the furnace, mixed with combustion air, and ignited in the burner area of the steam genera- tor. Instrumentation must modulate the fuel in response to combustion needs. Viewports typically allow operators to monitor combustion. In many cases, these viewports are equipped with aspi- rating air systems to limit the amount of flue gas and heat escaping the boiler and entering the boiler room. The burner area requires special attention for the steam gener- ator building ventilation system. This area is often occupied by plant operators who monitor and inspect the controls and the Inc. ASHRAE, 2019 user. single for Licensed | {}
3398e9c5-85ec-429e-a652-5be76eedd8ea | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 28.6 2019 ASHRAE Handbook-HVAC Applications (SI) ![image](/image/placeholder) REHEAT LINES MAIN STEAM ATT EMPERATORS NES STEAM PENTHOUSE DRUM PLATEN SECONDARY ISECONDARY REHEAT SUPERHEATER SUPERHEATER SUPERHEATER CONVEYOR GALLERY PRIMARY SUPERHEATER DOWNCOMERS COAL ECONOMIZER SILO GAS PROPORTIONING DAMPERS COAL ECONOMiZER INLET FLUE GAS OVERFIRE AIR PORTS SECONDARY AIR BURNER LEVELS BURNERS R WINDBOX II AIR HEATER COAL FEEDERS III GAS OUTLET PULVERIZERS (COAL MILL) PRIMARY AIR FANS TEMPERING AIR DUCTS PRIMARY AIR DUCT Fig. 1 Steam Generator Building (Courtesy The Babcock & Wilcox Company) combustion process. Heat is radiated and conducted to adjacent spaces from inspection ports, penetrations, and the steam genera- tor. Fumes and combustion gases also can leak. Steam Drum Instrumentation Area Both the burner area operator and the controls require ventilation with outdoor air. Outdoor air also provides dilution for fugitive fumes. Outdoor air can be ducted to burner areas and dis- charged by supply registers or blown directly into the area with wall-mounted fans, depending on the building arrangement. The flow rate is difficult to quantify; generally, 60 air changes per hour (ach) supplied to an area 4 to 6 m around the steam generator pro- vide adequate ventilation. Consider providing spot or localized velocity cooling of personnel workstations. In cold climates, out- door air may need to be tempered with indoor air or with heating coils. A typical steam generator has a steam drum at the top of the boiler that provides the water-to-steam interface. The water level in the drum is monitored to regulate the flow of steam and feed- water. This is a critical steam generator control function, so accurate and reliable process flow measurement is important. The steam drum instrumentation area may include sections of uninsulated furnace surface, which conducts and radiates heat to the surrounding area. The ventilation system should remove this heat to ensure that area temperatures are within instrumentation temperature limits. Instrumentation may need to be shielded from hot surfaces. Velocity cooling may be needed at operator worksta- tions. Wall-mounted panel fans in the outer walls are an option for providing ventilation air during warm weather. Heating is gener- ally not a concern unless the steam generator is expected to be out of service during cold weather. Once-through steam generators do not have drums, but have instrumentation in similar high-temperature, dusty areas. Local Control and Instrumentation Areas In addition to the drum and burners, the steam generator building may house local control areas for functions such as fuel supply, Inc. ASHRAE, 2019 user. single for Licensed | {}
910d3268-1f9e-4df5-a67a-aa53b041c696 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Power Plants 28.7 draft fans, or ash handling. Because areas around a steam generator may be hot and dirty, the location and selection of the control equip- ment should be coordinated between the electrical system engineer and the HVAC system engineer. The alternatives are to (1) locate the control equipment remotely from the steam generator, (2) use electrical components that can withstand the environment, or (3) provide a local environmentally controlled enclosure. The first alternative requires additional cable and raceway and perhaps additional signal boosters and condition- ers. The second alternative requires more robust electrical equipment that can tolerate extremely hot or dirty areas. When the electrical and control system design dictates that the equipment be located near the steam generator, a dedicated enclo- sure with a supporting environmental control system may be necessary. A typical environmental control system may control an air-handling unit capable of providing adequate filtration, pressur- ization, and temperature control. The temperature control may be obtained with a chilled-water or direct-expansion (DX) coil with a remote condensing unit. An air-cooled condensing unit may be used ifit is rated to match the surroundings. Coal- and Ash-Handling Areas Coal is typically stored on site, either in piles or in storage struc- tures, including semienclosed, fully enclosed, and underground storage facilities. Material-handling equipment moves the coal to conveyors for transportation to preconditioning equipment (e.g., a crusher). Processed coal is conveyed to steam generator building storage silos. Coal feed equipment regulates the supply of coal from the silos either to the burner or to final processing equipment such as pulverizing mills. Many new power plants are designed to burn low-cost coals from Wyoming's Powder River Basin and other similar coal seams. Many of these coals are extremely friable when dry, creating signif- icant amounts of dust during handling. In new plants, the material handling and ventilation systems should be designed to control dusting, preferably by using modern chutework and coal-handling machinery design to reduce or control dust emissions during fuel handling. This can reduce the effects of mechanical dust collectors and associated makeup air on plant HVAC systems. Some coals spontaneously begin to burn during normal outdoor ambient weather and normal powerhouse interior conditions. Under some conditions, accumulated coal dust spontaneously smolders, then suddenly flashes if the surface crust of the pile is broken, exposing the smoldering coal to oxygen. It is important that equip- ment in areas subject to dust accumulation be designed to reduce dust accumulation with sloped or curved surfaces, and designed to facilitate manual cleaning and washdown. Spontaneous combustion must be addressed in ventilation and dust collector design and installation to facilitate emptying dust out of the collector without exposing plant personnel to fire and explosion hazards. Coal-handling areas in the steam generator building that require special ventilation system consideration are the conveyor, silo, feeder, mill, and their transition areas, and ash-handling areas. Conveyor Areas. Primary concerns are dust control, outgassing from the coal, freezing of the coal and personnel access areas, and fire protection. Dust can be a concern because of the potential for environmental emission and also as a personnel and/or explosive hazard. Dust may be controlled by water-based spray systems or by air induction pickups at the point of generation. Control of fugitive dust at conveyor transfer points involves spe- cific concerns. Outdoor transfer points fall under the facility's air permit requirements for fugitive dust emissions and thus could require controls. For indoor transfer points and conveyors, the fugi- tive dust quantity could drive the electrical hazardous location from NFPA Standard 70 (NEC) Class II, Division II to Class II, Division 1, requiring different hazardous location rating for electrical components in the area. Since 2008, OSHA has been providing enhanced enforcement of existing industry combustible dust stan- dards through the directive CPL-03-00-08. Additional information is available in NFPA Standards 652 and 654, which sometimes are more stringent than the classification criteria for hazardous loca- tions provided in NFPA Standard 499. Some types of coal may outgas small quantities of methane, which could accumulate in the conveyor and storage structures. See the section on Coal Crusher and Coal Transportation System Build- ings for a discussion of ventilation of methane fumes. Natural or forced ventilation must remove heat from conveyor motors, other equipment, and building envelope loads. Ventilation air can also remove outgassed fumes. Generally, ventilation re- quirements can be as low as 2 to 5 ach. If air entrainment dust collection equipment is used, include provisions for makeup in the design. If natural openings are not sufficient for makeup air, sup- ply ventilation fans may need to be electrically interlocked to operate with the dust suppression/collection equipment. Makeup air may have to be heated if freeze protection is a design criterion. Unit heaters are generally used for spot heating. The unit heater should be specified to the hazard classification for the area it serves. Because coal dust can produce acids when wet, consider specifying noncorrosive materials and coatings. NFPA Standard 120 and the U.S. Bureau of Mines (1978) pro- vide other safety considerations for coal handling and preparation areas. Silo and Feeder Areas. Coal is generally fully contained by feeders and silos, so no special ventilation is needed. Occasionally, coal systems include an inert gas purge system for fire prevention. Ventilation may be needed for life safety dilution ventilation of purge gases. Coal Mill Areas. Coal mills require large power motors for the grinding process. These motors may have their own ventilation sys- tem, or the motor heat may be rejected directly to the surrounding space. The challenge for the ventilation system is to provide enough ventilation to remove heat without creating high air velocities that disturb accumulated dust. Blowing dust can pose health risks to operators and create a dust ignition hazard. Although occurrence of dust ignition air-to-dust ratios is possible, this area is generally not classified as hazardous. The dust ignition risk is managed by house- keeping, maintenance of seals on the mill equipment, and other dust-control measures. Forced supply ventilation is generally required for equipment cooling. Sidewall propeller fans work well if the mills are arranged near outer walls. Mills located in the interior of the building may require ducted supply air. Supply air velocities at the coal-handling equipment must be lower than the particulate entrainment velocity for the expected dust size. The maximum air velocity is established using the particle size distribution spectrum and the associated air settling velocities indicated in Figure 3 and Table 1 of Chapter 1 1 of the 2017 ASHRAE Handbook- -Fundamentals. Many utilities use carbon monoxide (CO) monitoring/trending to detect fires in coal bunkers, silos, and other areas. These systems are sometimes integrated with dust collector and other exhaust streams in these areas. Specification and design of the CO monitoring should be the responsibility of a special hazards fire protection engi- neer and coordinated with the industrial ventilation and HV AC design. The National Fire Protection Association (NFPA) does not dif- ferentiate between coal types/seams in the codes and standards. The utility industry, however, has accumulated experience and established best practices in handling these fuels. This information is shared between member utilities through groups such as Edison Electric Institute and Electric Power Research Institute. Other Inc. ASHRAE, 2019 user. single for Licensed | {}
1c00b016-ce59-4102-a5fb-3f719e323d84 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 28.8 2019 ASHRAE Handbook-HVAC Applications (SI) ![image](/image/placeholder) LOUVERED STAIR SUPPLY OR PENTHOUSE PENTHOUSE EXHAUST DEAERATOR MEZZANINE PLATFORM STEAM GENERATOR DEAERATOR DRUM □ STORAGE STEAM GENERATOR BUILDING A TANK PLATFORM c 0 . E P o P - P 6 P 0 O D S P P P p eye G 0 O P 타 모 모 V 투 ECONOMIZER 0 O 0 INLET 모 모 구 P POWER ROOF 급 - VENTILATOR 음 모 □ 6 BRIDGE CRANE BURNER 。 PLATFORMS 급 □ 由 HEATER FLOOR TURBINE BUILDING OPERATING FLOOR TYPICAL AIRFLOW THROUGH WINDOWS, 금 모 모 모 무 Turbine LOUVERS, AND FANS SUB- OPERATING 연구 LEVEL) 四 설 三 MEZZANINEFLOOR 과 "HEIR ASH HANDLING ILII PLANT SUB- OPERATING ELECTRIC - TRANSFORMER AREA GROUND ROOMS LEVEL ° 0 FLOOR O AIR PREHEAT COILS Fig. 2 Generation Building Arrangement (Courtesy Black & Veatch Corporation) sources of specific requirements include local fire code authorities and the plant's insurance carrier. Ash-Handling Areas. Ash is generated when coal or heavy fuel oil is burned. Fine ash particles carried by the flue gas from the top of the steam generator are called fly ash. Ash that accumulates as slag in the bottom of the steam generator is called bottom ash. Ash-handling equipment generally demands no special HVAC system consideration. Although fly ash is captured in the flue gas stream by a baghouse or electrostatic precipitator, uncaptured (fugi- tive) fly ash can create problems in equipment mechanisms because of its abrasiveness. If fugitive fly ash is expected to be in the air, HVAC equipment in the ash-handling areas should include filters to capture the ash before it enters building areas. Stack Effect One consideration in HVAC system design for a steam generator building is the stack effect caused by buoyancy of heated air. A 90 m tall steam generator building with -18°C outdoor air tempera- ture and 38°C indoor air temperature may have 125 Pa (gage) negative internal pressure at ground level. This high level of nega- tive pressure causes abnormally large forces on doors, creating a hazard for operators. Sources of Combustion Air Large-draft fans supply combustion air for the steam generator. A positive-pressure steam generator is supplied by forced-draft fans, and a negative-pressure steam generator uses induced-draft fans. A balanced-draft steam generator, typical for a larger unit, uses both forced- and induced-draft fans. Because the air is heated to furnace temperatures in the combustion process, part of the fuel energy is used to heat the air. Forced-draft fans on a large steam generator can supply 50 m3/s or more to the combustion process. A significant amount of energy is needed to preheat the combustion air. Two prevailing methods of preheating combustion air are used. One method is to draw air in from outdoors and heat it using steam or hot-water coils using energy directly from the power cycle. Another method uses heat rejected from steam generator surfaces to the building space to heat combustion air. This approach provides energy savings over heating outdoor air. Temperatures in higher levels of the generator building can be 38°C or higher. Heat recov- ery is accomplished by locating the draft fan intake high in the building. Although the potential for savings is large in a cold cli- mate, the total effect on building heating and ventilation systems should be evaluated. One effect is that drawing the air from the building makes the building pressure more negative; this increases infiltration and adds to the building heating system load, possibly offsetting the potential power cycle thermal efficiency advantage. Increased negative pressure can also contribute to stack effect prob- lems associated with negative pressure low in the building. The draft fan can also be used to supplement ventilation during warm outdoor conditions. 5. TURBINE GENERATOR BUILDING As shown in Figure 2, a turbine generator building usually includes a high-bay operating level, a deaerator mezzanine, and one or more suboperating levels. Typically, the turbines and electric generators are located along the centerline of the building between the operating level and the first suboperating level and are the major heat sources in the building. Deaerators are another significant heat contributor; the deaerator mezzanine is commonly open to the tur- bine operating level. Other room heat sources are steam, steam condensate and hot-water piping, heat exchangers, steam valve sta- tions and traps, motors, electric transformers, and other electrical equipment. Local Control and Instrumentation Areas Some power plants include a local turbine-generator control panel on the operating floor. The local control panel area of the tur- bine generator may be either enclosed or open; for the enclosed Inc. ASHRAE, 2019 user. single for Licensed | {}
df1bdd1e-aac2-4b9d-a3b8-b4b0f79801d0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Power Plants 28.9 arrangement, the environmental requirements are the same as those given in the Main Control Center section. For an open arrangement, velocity cooling with conditioned air improves the operator's working environment. Because the area may be directly exposed to high-temperature surroundings, the rec- ommended velocity of the conditioned air discharge is 1.5 to 3 m/s, depending on its service distance and workers' preference. The air distribution system should have manually adjustable air deflectors for operator comfort. In addition, the control panel may need a sep- arate cooling source. Deaerator Mezzanine The deaerator and associated storage tank reject significant heat at the deaerator mezzanine level. This plant area also typically includes instrumentation and control equipment enclosures; accord- ingly, the area should have local ventilation to provide the necessary cooling. Bridge Crane Operating Rooms Outdoor air entering the building is heated by process heat, rises toward higher elevation, and is relieved through openings. The bridge crane operating room is as high as the roof beam and within the building exhaust airstream. If the outdoor air temperature is 35°C, the crane operating room may be surrounded by 40°C or hot- ter air. Hence, the bridge crane operating room is normally air con- ditioned. Because the bridge crane operating room moves within the building during its operation, through-the-wall mounted air conditioners are commonly used; to simplify the electrical work, an additional power plug in the crane for the air conditioner should be provided by the crane supplier. Include provisions for the cooling- coil condensate drain in the design. Suboperating Level The turbine generator is located on the operating floor, a large deck surface open to the turbine building roof. The deck may be 70% or more of the turbine building area. Below the operating level are one or more suboperating levels. Ventilation supply air should be provided to the suboperating levels and at the lower elevations of the operating floor. Air rising through the operating levels brings room heat to the roof area, where it is relieved through high- elevation openings (gravity vents) or exhausted by roof-mounted exhaust fans or PR Vs. The major heat sources in the suboperating levels are high- temperature mechanical and piping systems. Other contributors are electric transformer room exhaust, switchgear room exhaust, electric reactor room exhaust, electric motor heat, etc. Electrical equipment exhaust heat in the turbine generator building is small compared to heat emitted from mechanical and piping systems. Accordingly, ventilation air from the plant distribution electric room can generally be exhausted directly into the turbine building without ducting to the outdoors. Conditioned air may be supplied to local instrumentation panel areas. For plants in cold climates (temperatures below 0°C), consider spot heating and/or exterior door heated-air curtains. Also consider providing freeze protection for piping close to building walls; stack effect and wind-driven infiltration can increase local heating requirements at the building perimeter. This problem can be addressed by adding capacity to installed heating systems or by pro- viding mobile, temporary heating. Electric Transformer Rooms Transformer rooms are typically located at a suboperating level between the turbine building and steam generator buildings. To isolate dust, the transformer rooms should not have inlet openings to the steam generator building. The transformer room exhaust air temperature should not exceed the design limit of the transformers. Typically, air intake is from a turbine building suboperating level or from outdoors, and exhaust air discharges at the higher level ofthe transformer room toward the turbine building. Plant Electrical Distribution Equipment and Switchgear/MCC Rooms Air for the main station switchgear and motor control center (MCC) rooms should be relatively clean. Supply air from outdoors should be filtered with MERV 6 (30% efficiency) air filters. Air can be relieved through louvers into the plant or to the outdoors. A similar approach is used for the ventilation system for an elec- tric reactor room. If the reactors have ducted connections for the exhausts, a removable section may be required so that the ducts can be disassembled when the reactor is lifted during maintenance. Isophase Bus Duct Cooling Power from the generator is conveyed by isophase bus ducts to the main transformer. This generates heat, which must be dissipated to a heat sink unless the bus duct is rated for natural cooling. A spe- cialized forced-air system cools the isophase bus duct and consists of cooling coils, fans, dampers, and filters. For a low-velocity sys- tem, air is supplied to the cooler along two phases of the bus duct and returned in the third phase. For a higher-velocity system, air is supplied and returned midway between the transformer and gener- ator, or is supplied at the generator end along bus ducts of all three phases and returned at the transformer end. Isophase bus cooling is essential for power production and delivery, so it is important to specify sufficient redundancy (in the form of dual fans, dual cooling coils and a bypass duct to provide cooling with outdoor air, or another source) in the system design. 6. COMBUSTION TURBINE AREAS Combustion turbines are adaptable for outdoor or indoor instal- lation. The outdoor type is usually a skid-mounted structure, with support systems typically designed and furnished by the combus- tion turbine vendor. The indoor type is typically enclosed in a weatherproof and acoustically treated enclosure and may have indoor support systems, designed and installed separately. Combustion turbine installations have some or all of the following support facilities: fuel oil handling facility, natural gas pressure-reducing facility, office or administration areas, mainte- nance shops, battery rooms, control rooms, distributed control system (DCS) control room, communication or computer room, and a water treatment facility. Heating and ventilation design issues associated with combustion turbines include airflow, combustion air source, hot duct and equipment surfaces, fuel supply, turbine inlet cooling, noise, etc. The turbine manufacturer typically establishes HVAC require- ments and, if required by the purchaser, provides HVAC equipment for the various compartments on the turbine skid. Turbine ventila- tion and equipment requirements should be coordinated with the building ventilation design. Turbine and generator casings and the surface of the exhaust duct are large contributors to the heat removal requirements. Insulate hot surfaces with appropriate materials as much as is practical and with approval of the turbine manufacturer, with appropriate airflow established to eliminate hot spots. When heat recovery equipment is installed in the turbine ex- haust, allow for the additional heat rejected into the building because of increased back pressure on the hot exhaust. Inc. ASHRAE, 2019 user. single for Licensed | {}
23a61f90-b696-494b-bff9-bbad916de500 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 28.10 2019 ASHRAE Handbook-HVAC Applications (SI) Airflow through the combustion turbine building should consider combustion air requirements, combustible gas dilution requirements based on design leakage rates, heat removal requirements, exhaust gas dilution, and electrical component cooling requirements. Com- bustion turbines draw combustion air through ducts from outside the building. The system design should ensure control of the building pressurization to keep the building under positive pressure, and building outdoor air should be filtered. This also offsets infiltration of dust, rain, snow, insects, and other contaminants into the building. System design should address freeze protection for vulnerable com- ponents. For cold-climate applications during normal operation, mixing outdoor and building air to keep the outdoor supply air tem- perature above freezing is recommended. In electrically classified installations, the ventilation system must switch to 100% outdoor air during upset conditions. Noise from combustion turbines is managed by a combination of site location considerations, acoustic enclosures; sound attenuation devices and engineered sound controls include those that are part of HVAC systems. HVAC design requirements for various areas of the building or turbine skid are in Table 1. The design should use NFPA standards such as 37, 70, and 90A; insurance carrier requirements; and appli- cable local codes and standards. Coordinate HVAC system design and operation with fire protection systems to ensure adequate concentration of fire suppressant and to prevent fire and smoke spread. HV AC systems also must shut down when fire or extremely high concentrations of gases are detected. 7. MAIN CONTROL CENTER The main control center usually includes a control room, elec- tronic and electric control panel and instrumentation rack room, computational equipment server room, automation process control system room, telecommunications equipment room, battery room, UPS room, engineer and operator training simulation room, and associated administration areas. Because the control center usually contains temperature- sensitive electronic equipment critical to plant operation, it is gen- erally provided with redundant air-handling units and refrigeration equipment. A back-up power supply may also be required. Passive components such as distribution ductwork and piping do not have to be duplicated. Design controls so that failure of a component com- mon to both the primary and back-up systems does not cause failure ofboth systems; manual changeover is a simple solution. Ifthe main control building is located in a fly-ash-contaminated area, room pressurization is highly recommended. Control Rooms The control room houses the microprocessor, printer, electronic and emergency response controls, fire protection controls, commu- nication and security systems, regional system networks, accesso- ries, and relevant wiring and tubing systems. An air-conditioning system typical for office occupancy, with features to meet overall design requirements for reliability and the specific environmental needs of the control equipment, is generally appropriate. Battery Rooms Battery rooms should be maintained between approximately 21 and 27°C for optimum battery capacity and service life. Tempera- ture variations are acceptable as long as they are accounted for in battery sizing calculations, but the minimum room design tempera- ture should be considered in determining battery capacity. Batteries typically used in power generation facilities produce hydrogen gas, so the HVAC system must be designed to limit the hydrogen con- centration in the room. See IEEE Standard 1635/ASHRAE Guideline 21-2012 for methods of estimating hydrogen generation by various battery types and operating modes and optimizing the design of the ventilation system. That guideline recommends a maximum average concentration in the room of <2% by volume; however, the designer may consider a lower value based on project requirements. Chemical Analysis Facilities Many generation facilities have water chemistry laboratories equipped with various analytical devices for monitoring and con- trolling boiler feed water and cooling tower water chemistry. If the laboratories contain fume hoods, the hood exhaust and room makeup air supply should be designed in accordance with ACGIH (2016), NFPA Standard 45, and applicable chapters of the ASHRAE Hand- books. 8. SUBSTATION AND SWITCHY ARD CONTROL STRUCTURES Substations and switchyards increase electricity voltage from the power plant generator output voltage to transmission-level voltage, and regulate power for distribution levels. These facilities are gen- erally located remotely, so their HVAC design should be simple, reliable, and easy to maintain. Design Considerations The design of the HVAC, filtration, and pressurization system should be based on the type of equipment in the room and its sensitivity to dust, smoke, temperatures, and humidity. Consider- ations include reliability, simplicity, and low installation and maintenance costs. ANSI/IEEE Standard C2 addresses HVAC requirements. If the substation control building is occupied, typi- cal human comfort conditions for office areas (see Table 1) are adequate; otherwise, temperature limitations and humidity control protect equipment in the room. Filtration with MERV 7 or 8 effi- ciency filters protects equipment from dust and prolongs its life. If the substation control building is located in a heavy industrial area or near a chemical or a wastewater plant, provide gas-phase filtra- tion to remove airborne contaminants and protect the electrical equipment from corrosion. When designing outdoor air economizers for cooling the area, use MER v 12 efficiency filters. In addition, if electrical panels or enclosures are susceptible to dust, it may be necessary to pressurize the room to control infil- tration and prevent entry of dust in the building. For critical applications or remote locations, design fans and other HVAC equipment with 100% redundancy, and ensure the standby unit autostarts after a failure of the primary unit. Substations have bat- teries and chargers that provide back-up power for operation during blackouts or other power disruptions. Batteries and char- gers should preferably be in a separate room, in accordance with Table 1 and the section on Battery Rooms. Typical cooling systems in substations and switchyards control structures include packaged, split-type, or wall-mounted DX air- conditioning units. The design should be simple, so that equipment repair or replacement can be performed as quickly as possible and the system returned to service. HVAC systems in dispatch and load control centers should be designed like those for process computer rooms and data centers, with similar temperature, relative humidity, cleanliness, reliability, and redundancy considerations. These facilities are continuously occupied, and the HVAC system should be designed as for a control room. 9. TURBINE LUBRICATING OIL STORAGE A typical power plant has a turbine lubricating oil storage tank and associated filtration equipment. If this storage area is inside the Inc. ASHRAE, 2019 user. single for Licensed | {}
fe9eb00c-140c-480a-838b-7009172bbd51 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Power Plants 28.11 building, the tank should be vented to the outdoors or ventilation rates should provide for dilution of oil fumes. The ventilation sys- tems should be coordinated with fire protection systems to ensure adequate fire suppressant concentration and to prevent spread of fire. 10. OIL STORAGE AND PUMP BUILDINGS At a power plant, fuel oil may be the main source of energy for the steam generator, combustion turbine, or diesel generator. It may also be a back-up or supplemental fuel. Coal-fueled plants usually use oil or gas as the initial light-off fuel or for operation of an aux- iliary steam generator. Auxiliary steam generators provide initial plant warm-up and building heating. Oil for combustion is generally light oil such as No. 2 fuel oil, or heavy oil such as No. 6. Light oils can be pumped at normal tem- peratures, but heavy oils are highly viscous and may need to be heated for pumping. Oils are usually received by rail or truck, trans- ported by pipeline, and stored in tanks. Enclosures for pumps, valves, heat exchangers, and associated equipment should be heated and ventilated to remove excess heat and to dilute hydrocarbon fumes. Tank ventilation is an integral part of the tank and piping system design, which is separate from the enclosure ventilation design. Fuel oils are classified in NFPA Stan- dard 30 as either combustible or flammable, depending on their vapor pressure at the indoor design temperature. Flammable liquids are hazardous; combustible liquids are not. HV AC systems for areas containing combustible fuels must fol- low ventilation principles for heat removal and for good air mixing. Ventilation rates should dilute fumes expected from evaporation of spilled or leaking fuel, following ACGIH (2016) guidelines and safety data sheets (SDSs) provided by the material manufacturer. For fuel handling confined to piping systems, the expected leakage is nearly zero, so very low fresh air rates are required for ventilation (generally less than 1 ach). If fuel is handled in open containers or hoses, higher rates are prudent. Ifthe fuel is flammable at temperatures expected in the room, fol- low NFPA Standard 30 and other safety and building codes. Electrical systems may need to be classified for operation in a haz- ardous location. 11. COAL CRUSHER AND COAL TRANSPORTATION SYSTEM BUILDINGS Coal-handling facilities at a power plant receive and prepare coal and then transport it to the burners. Intermediate steps in the process may include long- or short-term storage, cleaning, and crushing. Receipt may include barge, rail car, or truck unloading. Storage may be in piles on the ground, underground, or in barns or silos. At the site, the coal is handled by mobile equipment or conveyor systems. The following general HVAC considerations apply for the types of structures involved. Potential for Dust Ignition Explosion Most types of coal readily break down into dust particles when handled or conveyed. The dust can become fine enough and occur in the right particle size distribution and concentration to create a dust explosion. The design engineer should review and apply the refer- enced NFPA standards and guidelines to determine the dust ignition potential for each ventilation system application. Ventilation of Conveyor and Crusher Motors in Coal Dust Environment Heat from motors and process equipment should be removed through ventilation, either by using ducted, ventilated motors or by ventilating the building enclosures. Ventilation in enclosures con- taining coal should keep the velocity below the entrainment velocities of the expected particle sizes. Table 1 in Chapter 11 ofthe 2017 ASHRAE Handbook-Fundamentals has information on set- tling velocity. Generally, air should be mechanically exhausted to allow ventilation air to enter the building through louvers at low velocities. Cooling or Ventilation of Electrical and Control Equipment Electrical and control equipment may be located near coal piles or other coal-handling facilities. Air-conditioned control rooms should be pressurized with filtered outdoor air. Ventilated motor control or switchgear areas should also be pressurized with filtered air. Because ofhigh dust concentrations in coal yards, ordinary filter media have a short life; a solution is to use inertial filters. For air- conditioned areas, inertial filters can be followed by higher-efficiency media filters. For electrical equipment rooms adjacent to an area with the potential for a dust ignition explosion, follow NFPA Standard 496, which recommends the flow of clean air away from electrical equip- ment into the dusty area. Ventilation of Methane Fumes Methane and other hydrocarbons are present in coal both as free gas in cracks and voids and as adsorbents within the coal. Although most of the methane is released from the interstitial coal structure during mining and handling, some methane or other potentially flammable gases may remain in the coal. Thus, flammable concen- trations of methane can accumulate when large amounts of coal are stored. The design engineer should identify the potential for meth- ane accumulation when designing for structures associated with silos or coal storage buildings. At the mine or mine mouth, methane gas emission rates as high as 150 L/Mg · day are possible; at other locations, the rate is usually less than 30 L/Mg · day. Dust collection air exhaust or natural ventilation is often sufficient to prevent the methane level from reaching the 1% explosion limit. The design engineer should apply guidelines from NFPA Standards 85, 120, and 850. Underground Tunnels and Conveyors Enclosed conveyors are generally of loose construction and re- quire no ventilation. Smoke or gases in underground conveyor tunnels, hoppers, or conveyor transfer points could cause a person- nel safety hazard. Ventilation systems should be coordinated with escape route passages to move fresh air from the direction of the egress. Ventilation rates in the range of2 to 5 ach are generally ap- propriate for normal system operation. Dust Collectors Dust collectors are used primarily in coal- and limestone- handling operations to reduce the spread of fugitive dust. Collector effects on plant air supply, disposal of collected dust, and associated fire safety and air quality permit issues must be considered. Consult Chapter 15 in this volume, Chapters 29 and 30 in the 2016 ASHRAE Handbook-HVAC Systems and Equipment, and applicable ACGIH publications for detailed design and specification guidance. Provide adequate make-up air to ensure proper dust collector operation. Successful coal dust control depends on proper conveyor transfer chute design (including transfer hoods, settling boxes, and skirt board seals) and on proper selection of air intake velocities and airflow quantities at transfer points or chutes. Most conveyor manu- facturers either have proprietary transfer chute designs meeting these objectives or follow guidance from ACGIH (2016) and other author- itative sources. Airflow associated with these pickup points may be sufficient to meet the ventilation requirements. Air inlets must be provided. If additional ventilation is needed, the ventilation fan must coordinate Inc. ASHRAE, 2019 user. single for Licensed | {}
15e2af9e-1dfa-491d-b356-ca2c4006ecbf | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 28.12 with the dust collection system. For heated structures, makeup air may need to be heated. Dust collectors should be located in an area where the exhaust can be easily vented to a safe outdoor location because this exhaust stream may contain combustible gas. Dust collectors and associated ductwork may be required to either contain the detonation pressure of an explosion or relieve the pressure through relief panels or blast doors to the outdoors. Fire or explosion suppression systems may be required by the AHJ. Dust collection systems in this application are typically required to conform to NFPA Standards 67, 68, and 120 in addition to other referenced NFPA and other applicable standards. 12. HEA TING/COOLING SYSTEMS Selection of the heating and cooling systems in a power plant depends on several variables, including the geographical location and orientation ofthe plant and the type of fuel used. Most plants are ventilated with outdoor air, but it is customary in hot climates to air- condition many plant areas. Evaluate heating alternatives (e.g., steam, hot water, gas, electricity) to identify the most economical choice. Electricity is the primary energy source for general-purpose cooling of various areas of the plant. Areas such as the main control room, office areas, and electrical switchgear/MCC rooms are air- conditioned for continuous human occupancy or for maintaining the operability of the electrical equipment and controls. Spot cooling may also be needed at local control panel areas in the power gener- ation (turbine-electrical generator building) and steam generator (boiler) buildings. Cooling The cooling source may be either a centrally located system pro- viding chilled water to various area coolers or individual DX area coolers with either air- or water-cooled condensing units. Selection depends on the layout of the areas to be cooled and the comparative costs of the two options. The condensing system of the water chiller may be cooled with either air or available water from the plant ser- vice water system. Air-cooled chillers are used when air near the proposed chiller location is moderately clean and no fly ash or coal dust problem is anticipated. For a water-cooled system, a closed- loop cooling tower is sometimes used if service water is poor or unavailable (e.g., during start-up or plant outages). To protect chillers from fouling and corrosion by the service water, a heat ex- changer is sometimes used between the chiller condenser and the service water source. In a power plant with several operating units and individual self-supporting chilled-water systems, the chilled- water systems of each unit are sometimes interconnected to provide back-up and redundancy. Heating Heating in various areas of the power plant is usually provided by electric, steam, or hot-water unit heaters or heating coils in air- handling units. In a hot-water distribution system, glycol is usually added into the system for protection against freezing. Because the building's s stack effect induces large quantities of infiltration air, heating requirements in the lower levels of the steam generator building may increase when the steam generator is operating. Pres- surization fans directing cooler, outdoor air into the warmer upper elevations of the plant can offset this infiltration. Also, the design engineer may evaluate redistribution of hotter air from higher to lower elevations. An alternative to heating the open areas of the plant is to use pipe- line heat tracing and spot heating at personnel workstations. For this approach, the design engineer should consider all components that may require heat tracing, such as instrument lines, small and large pipes, traps, pumps, tanks, and other surfaces that may be subject to 2019 ASHRAE Handbook-HVAC Applications (SI) freezing temperatures. Often the large number of components and surfaces to be heat traced and insulated makes this impractical. Hydroelectric Power Plants Hydroelectric power plants consist ofa dam structure, draft tubes with gates, and turbine generators. The facility may be arranged with the generation components within the dam structure or within structures attached to the dam. HVAC systems should be provided for reliable operation of the mechanical, electrical, and control equipment and office areas. The system design should consider the geographical location, humidity, degree of automation needed, and potential for flooding. Dams are typically built in remote locations, so the design and arrangement of the equipment, air intakes, and exhaust ports should consider the potential for vandalism. Accordingly, intakes should include security grating or bars, should not provide a line of sight into the structure, and should be constructed of heavy-gage steel to thwart bullets. HVAC equipment should be indoors if practical, or made otherwise inaccessible. Humidity is a major design consideration. The lake surface and outfall structure create humid outdoor conditions. Outdoor air used for ventilation may introduce humidity into indoor spaces that may cause corrosion of electrical and control equipment. In addition, dam structure and turbine components below the lake water level are usually at temperatures colder than the dew point of the outdoor air. Introducing unconditioned outdoor air can create a significant amount of condensation on structure and equipment surfaces. Another consideration of the remote location of hydroelectric plants is that the HV AC systems need to be reliable and able to oper- ate with minimum attention by operating and maintenance personnel. Thus, these systems may require seasonal changeover features and fully automatic functions. System controls should be integrated with the generation plant controls, such as communication of status and alarm of critical functions to an off-site monitoring facility. HVAC design should consider the maximum and minimum lake water level. Intakes and exhausts should be above the maximum design flooding level. Suction points for cooling water sources should be below the minimum water level. Because of the potential for introducing outdoor humidity, cooling of mechanical equipment areas (e.g., turbine generator hall, turbine and wicker gate) should use a minimum amount of ventila- tion air. When practical, dehumidify air mechanically or with coils using cold lake water. Areas with heat-producing equipment such as for stop-log storage generally do not need ventilation air, which may introduce unwanted humidity. To minimize the effect of out- door air humidity on electrical and control equipment areas, consider using water-cooled equipment and radiant cooling to cool structural surfaces. Design battery rooms and oil storage areas for the specific hazards to minimize excessive ventilation rates. 13. ENERGY RECOVERY Energy recovery should be considered in any new system design or system upgrade. Considerations in the power plant should in- clude the following: · Interfaces with existing plant process systems. Using waste steam or steam bled from a process stream must consider process system behavior during generating unit start-up, part load, full load, shutdown, and cold standby/shutdown conditions. Any water returned to the boiler steam cycle must consider effects on the gen- erating unit boiler water chemistry/water treatment. · Operating environment, including cross contamination of clean airstreams from dirty airstreams, dusty environments, and corro- sive conditions from substances such as flue gas. For details, see Chapter 26 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment. Inc. ASHRAE, 2019 user. single for Licensed | {}
8dd71378-f0e4-4310-909e-9d1290c53c48 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Power Plants 28.13 · Safety, including issues resulting from the presence of coal dust, flammable gases, etc. Consult fire codes and insurance underwrit- ers for guidance. · Control strategies. · Constructability. · Codes, standards, and local rules and regulations. Energy recovery systems should be evaluated by economic anal- ysis of life-cycle costs, including · Initial cost, including equipment and installation cost · Fuel and station service power cost · Operating cost savings · Maintenance cost Utility economic evaluations should follow the accounting guidelines and requirements as established by the Federal Energy Regulatory Commission (FERC). See Chapter 38 for further infor- mation on owning and operating costs. 14. SAFETY CONSIDERATIONS Power plant HVAC systems should be engineered and designed to operate safely and reliably. HVAC systems often interface with other plant systems; specific requirements for these interfaces and for plant safety are defined by applicable codes and standards, regu- latory authorities, owners' requirements, and insurance carriers. These requirements vary regionally, and appropriate authorities must be consulted during the design and modification of HVAC systems. REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. ACGIH. 2016. Industrial ventilation: A manual of recommended practice, 29th ed. American Conference of Governmental Industrial Hygienists, Cincinnati, OH. ASHRAE. 2016. Ventilation for acceptable indoor air quality. ANSI/ ASHRAE Standard 62.1-2016. ASHRAE. 2012. Guide for the ventilation and thermal management of bat- teries for stationary applications. IEEE/ASHRAE Guideline 21-2012. CAN/CSA. 2017. Single-phase and three-phase liquid-filled distribution transformers. ANSI/CAN/CSA Standard C2.1-2006 (R2017). Canadian Standards Association International, Toronto. IEEE. 2017. National electrical safety codeⓇ (NESCⓇ). ANSI/IEEE Stan- dard C2-2017. Institute of Electrical and Electronic Engineers, Piscat- away, NJ. IEEE. 2018. IEEE/ASHRAE guide for the ventilation and thermal manage- ment of batteries for stationary applications. IEEE Standard 1635-2018. Institute of Electrical and Electronics Engineers, Piscataway, NJ. ISA. 2013. Environmental conditions for process measurement and control systems: Airborne contaminants. ANSI/ISA Standard ISA-71.04-2013. Instrumentation, Systems, and Automation Society, Research Triangle Park, NC. NFPA. 2016. Installation of stationary pumps for fire protection. ANSI/ NFPA Standard 20. National Fire Protection Association, Quincy, MA. NFPA. 2018. Flammable and combustible liquids code. ANSI/NFPA Stan- dard 30. National Fire Protection Association, Quincy, MA. NFPA. 2018. Installation and use of stationary combustion engines and gas turbines. NFPA Standard 37. National Fire Protection Association, Quincy, MA. NFPA. 2019. Fire protection for laboratories using chemicals. NFPA Stan- dard 45. National Fire Protection Association, Quincy, MA. NFPA. 2016. Compressed gases and cryogenic fluids code. NFPA Standard 55. National Fire Protection Association, Quincy, MA. NFPA. 2016. Guide on explosion protection for gaseous mixtures in pipe systems. NFPA Standard 67. National Fire Protection Association, Quin- cy, MA. NFPA. 2013. Standard on explosion protection by deflagration venting. NFPA Standard 68. National Fire Protection Association, Quincy, MA. NFPA. 2017. National electrical codeⓇ (NECⓇ). ANSI/NFPA Standard 70. National Fire Protection Association, Quincy, MA. NFPA 2015. Boiler and combustion systems hazards code. ANSI/NFPA Standard 85. National Fire Protection Association, Quincy, MA. NFPA. 2018. Installation of air conditioning and ventilating systems. NFPA Standard 90A. National Fire Protection Association, Quincy, MA. NFPA. 2015. Fire prevention and control in coal mines. ANSI/NFPA Stan- dard 120. National Fire Protection Association, Quincy, MA. NFPA. 2016. Hazardous materials code. NFPA Standard 400. National Fire Protection Association, Quincy, MA. NFPA. 2017. Purged and pressurized enclosures for electrical equipment. ANSI/NFPA Standard 496. National Fire Protection Association, Quin- cy, MA. NFPA. 2017. Recommended practice for the classification of combustible dusts and of hazardous (classified) locations for electrical installations in chemical process areas. NFPA Standard 499. National Fire Protection Association, Quincy, MA. NFPA. 2016. Standard on the fundamentals of combustible dust. NFPA Standard 652. National Fire Protection Association, Quincy, MA. NFPA. 2017. Standard for the prevention of fire and dust explosions from the manufacturing, processing, and handling of combustible particulate sol- ids. NFPA Standard 654. National Fire Protection Association, Quincy, MA. NFPA. 2015. Recommended practice for fire protection for electric generat- ing plants and high voltage direct current converter stations. ANSI/NFPA Standard 850. National Fire Protection Association, Quincy, MA. NIOSH. 1994. Table ofIDLH values: Chlorine. National Institute for Occu- pational Safety and Health, Washington, D.C. www.cdc.gov/niosh/idlh /7782505.html. OSHA. 2008. Combustible dust national emphasis program. OSHA Direc- tive CPL-03-00-008. Occupational Safety and Health Administration, Washington, D.C. Stultz, S.C., and J.B. Kitto, eds. 2005. Steam, its generation and use, 41st ed. The Babcock & Wilcox Company, Barberton, OH. U.S. Bureau of Mines. 1978. Methane emissions from gassy coals in storage silos. Report of Investigation 8269. White, W., and E.C. Piesciorovsky. 2009. Building heat load contributions from medium and low voltage switchgear, part I: Solid rectangular bus bar heat losses (RP-1395). ASHRAE Transactions 115(2). Paper LO-09-034. White, W., and E.C. Piesciorovsky. 2010. Heat gain from electrical and con- trol equipment in industrial plants, part II. ASHRAE Research Project, RP-1395 Final Report. White, W., A. Pahwa, and C. Cruz. 2003. Heat gain from electrical and con- trol equipment in industrial plants (RP-1104). ASHRAE Research Proj- ect, Final Report. Paper NA-04-9-2a. White, W., A. Pahwa, and C. Cruz. 2004. Heat loss from electrical and con- trol equipment in industrial plants: Part II, results and comparisons (RP- 1104). ASHRAE Transactions 110(2). Paper NA-04-9-2b. BIBLIOGRAPHY NFPA. 2008. Fire protection handbook, 20th ed., Section 14: Detection and alarm. National Fire Protection Association, Quincy, MA. 1 Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
34d22f07-fa18-45c7-8503-09bd872c9e3a | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 29 NUCLEAR FACILITIES GENERAL DESIGN ISSUES 29.1 As Low as Reasonably Achievable (ALARA) 29.1 Design 29.1 Normal or Power Design Basis 29.1 Safety Design Basis 29.1 Outdoor Conditions 29.2 Indoor Conditions 29.2 Indoor Pressures 29.2 Airborne Radioactivity 29.2 Tornado/Missile Protection 29.2 Fire Protection 29.2 Smoke Management 29.3 DEPARTMENT OF ENERGY FACILITIES 29.4 Confinement Systems 29.4 Ventilation 29.5 THEI are discussed in this chapter. Such facilities include nuclear HVAC requirements for facilities using radioactive mate- power plants, fuel fabrication and processing plants, plutonium pro- cessing plants, hospitals, corporate and academic research facilities, and other facilities housing nuclear operations or materials. The in- formation presented here should serve as a guide; however, careful and individual analysis of each facility is required for proper applica- tion. 1. GENERAL DESIGN ISSUES Criticality, radiation fields, and regulation are three issues that are more important in the design of nuclear-related HV AC systems than in that of other special HV AC systems. Criticality. Criticality considerations are unique to nuclear facil- ities. Criticality is the condition reached when the chain reaction of fissionable material, which produces extreme radiation and heat, becomes self-sustaining. Unexpected or uncontrolled conditions of criticality must be prevented at all cost. In the United States, only a limited number of facilities, including fuel-processing facilities, weapons facilities, naval shipboard reactors, and some national lab- oratories, handle special nuclear material subject to criticality con- cerns. Radiation Fields. All facilities using nuclear materials contain radiation fields. They pose problems of material degradation and per- sonnel exposure. Although material degradation is usually addressed by regulation, it must be considered in all designs. The personnel exposure hazard is more difficult to measure than the amount ofmate- rial degradation because a radiation field cannot be detected without special instruments. It is the responsibility of the designer and of the end user to monitor radiation fields and limit personnel exposure. Regulation. In the United States, the Department of Energy (DOE) regulates weapons-related facilities and national laboratories, and the Nuclear Regulatory Commission (NRC) regulates commercial nuclear plants. Other local, state, and federal regulations may also be applicable. For example, meeting an NRC requirement does not re- lieve the designer or operator of the responsibility of meeting Occu- pational Safety and Health Administration (OSHA) requirements. The preparation of this chapter is assigned to TC 9.2, Industrial Air Conditioning. ¦ COMMERCIAL FACILITIES ¦ 29.6 ¦ ¦ --- ¦ --- ¦ ¦ Operating Nuclear Power Plants ¦ 29.6 ¦ ¦ New Nuclear Power Plants ¦ 29.7 ¦ ¦ PLANT HVAC&R SYSTEMS ¦ 29.8 ¦ ¦ Pressurized- Water Reactors ¦ 29.8 ¦ ¦ Boiling- Water Reactors ¦ 29.9 ¦ ¦ Heavy Water Reactors ¦ 29.10 ¦ ¦ Areas Outside Primary Containment ¦ 29.10 ¦ ¦ Nonpower Medical and Research ¦ ¦ ¦ Reactors ¦ · 29.11 ¦ ¦ --- ¦ --- ¦ ¦ Laboratories ¦ 29.11 ¦ ¦ Decommissioning Nuclear Facilities ¦ 29.11 ¦ ¦ Waste-Handling Facilities ¦ 29.12 ¦ ¦ Reprocessing Plants ¦ 29.12 ¦ ¦ Mixed-Oxide Fuel Fabrication Facilities ¦ 29.12 ¦ The design of an HVAC system to be used near radioactive materials must follow all guidelines set by these agencies and by the local, state, and federal governments. For facilities outside the United States, a combination of national, local, and possibly some U.S. regulations apply. In Canada, the Cana- dian National Safety Commission (CNSC), formerly the Atomic Energy Control Board (AECB), is responsible for nuclear regulation, whereas in the United Kingdom, the Nuclear Installations Inspec- torate (NII) and the Environment Agency (EA), are involved in issu- ing operation licenses. 1.1 AS LOW AS REASONABLY ACHIEV ABLE (ALARA) ALARA means that all aspects of a nuclear facility are designed to limit worker exposure and discharges to the environment to the minimum amount of radiation that is reasonably achievable. This refers not to simply meeting legal requirements, but rather to attaining the lowest cost-effective levels within those requirements. 1.2 DESIGN HVAC requirements for a facility using or associated with radio- active materials depend on the type of facility and the specific ser- vice required. The following are design considerations: · Physical layout of the HVAC system that minimizes the accumu- lation of material within piping and ductwork · Control of the system so that portions can be safely shut down for maintenance and testing or in the case of any event, accident, or natural catastrophe that causes radioactivity to be released · Modular design for facilities that change operations regularly · Preservation of confinement integrity to limit the spread of radio- active contamination in the physical plant and surrounding areas The design basis in existing nuclear facilities requires that safety- class systems and their components have active control for safe shut- down of the reactor, for mitigating a design basis accident (DBA) and for controlling radiation release to the environment as the result of an accident. Advanced nuclear steam supply systems (NSSS) are being de- signed that incorporate more passive control to minimize dependence on mechanical equipment to mitigate the consequences of a DBA. 29.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
2676501e-6685-4cdd-b8f7-7571dbe1729a | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 29.2 2019 ASHRAE Handbook -HVAC Applications (SI) 1.3 NORMAL OR POWER DESIGN BASIS The normal or power design basis for nuclear power plants covers normal plant operation, including normal operation mode and normal shutdown mode. This design basis imposes no require- ments more stringent than those specified for standard indoor con- ditions. 1.4 SAFETY DESIGN BASIS The safety design basis establishes special requirements neces- sary for a safe work environment and public protection from expo- sure to radiation. Any system designated essential or safety related must mitigate the effect of a design basis accident, or natural catastrophe that may result in the release of radioactivity into the surroundings or the plant atmosphere. These safety systems must be operable at all times unless allowed by a limited condition of oper- ation (LCO). The degree to which an HVAC system contributes to safety determines which components must function during and after a DBA or specific combinations of such events as a safe shutdown earthquake (SSE), a tornado, a loss of coolant accident (LOCA), fuel-handling accident (FHA), control rod drop accident (CRDA), main steam line break (MSLB), and loss of off-site electrical power (LOSP). Non-safety-related systems are not credited in any design basis accident and are designed not to adversely affect safety-related systems. Most U.S. nuclear facilities (both NRC and DOE regulated) were built and licensed under the deterministic approach for safety clas- sification of structures, systems, and components (SSC). This approach is changing to a probabilistic risk assessment (PRA) clas- sification system. NRC classifies SSCs as safety-significant (SS) or low safety-significant (LSS), and categorizes them in four groups per 10 CFR 50.69 (RISC-1, safety related and safety significant; RISC-2, non-safety-related and safety significant; RISC-3, safety related and low safety significant; RISC-4, non-safety-related and low safety significant). NRC Regulatory Guide 1.201 provides information on safety classification of systems, structures, and com- ponents. The U.S. DOE classifies SSCs based on DOE Order 420.1 and DOE Standards 1020 and 1189. System Redundancy. Systems important to safety must be redundant and single-failure-proofed. Such a failure should not cause a failure in the back-up system. For additional redundancy requirements, refer to the section on Commercial Facilities. Seismic Qualification. All safety-class components, including equipment, pipe, duct, and conduit, must be seismically qualified by testing or calculation to withstand and perform under the shock and vibration caused by an SSE or an operating-basis earthquake (OBE) (the largest earthquake postulated for the region). This qualification also covers any amplification by the building structure. In addition, any HVAC component that could, if it failed, jeopardize the essen- tial function of a safety-related component, must be seismically qualified or restrained to prevent such failure. Environmental Qualification. Safety-class components must be environmentally qualified; that is, the useful life of the compo- nent in the environment in which it operates must be determined through a program of accelerated aging. Environmental factors such as temperature, humidity, pressure, and cumulative radiation dose must be considered. Quality Assurance. All designs and components of safety-class systems must comply with the requirements of a quality assurance (QA) program for design control, inspection, documentation, and traceability of material. For U.S. plant designs, refer to Appendix B ofTitle 10 ofthe U.S. Code ofFederal Regulations, Part 50 (10 CFR 50) or ASME Standard NQA-1 for quality assurance program requirements. Canadian plant designs use two related series of quality assur- ance standards: CAN3-286.0 and its six daughter standards, plus four standards in the N299 series. Quality programs in the United Kingdom are based on ISO 9000. For other countries, refer to the applicable national regulations. Emergency Power. All safety-class systems must have a backup power source such as an emergency diesel generator. 1.5 OUTDOOR CONDITIONS Chapters 14 and 15 of the 2017 ASHRAE Handbook- -Funda- mentals, the U.S. National Oceanic and Atmospheric Administra- tion, national weather service ofthe site country, or site meteorology can provide information on outdoor conditions, temperature, humid- ity, solar load, altitude, and wind. Nuclear facilities generally consist of heavy structures with high thermal inertia. Time and temperature lag should be considered in determining heat loads. For some applications, such as diesel gen- erator buildings or safety-related pumphouses in nuclear power plants, the 24 h average temperature may be used as a steady-state value. For critical ventilation system design, site meteorological data should be evaluated. 1.6 INDOOR CONDITIONS Indoor temperatures are dictated by occupancy, equipment or process requirements, and comfort requirements based on personnel activities. HV AC system temperatures are dictated by the environ- mental qualification of the safety-class equipment located in the space and by ambient conditions during the different operating modes of the equipment. 1.7 INDOOR PRESSURES Where control of airflow pattern is required, a specific building or area pressure relative to the outdoor atmosphere or to adjacent areas must be maintained. The effect of prevailing wind speed and direction, based on site meteorological information, should be con- sidered. For process facilities with pressure zones, the pressure rela- tionships are specified in the section on Confinement Systems. In facilities where zoning is different from that in process facili- ties, and in cases where any airborne radioactivity must not spread to rooms within the same zone, this airborne radioactivity must be controlled by airflow. 1.8 AIRBORNE RADIOACTIVITY The level of airborne radioactivity within a facility and the amount released to the surroundings must be controlled to meet the require- ments of 10 CFR 20, 10 CFR 50, 10 CFR 61, 10 CFR 100, 10 CFR 835, and U.S. DOE Policy P 450.4A, or equivalent national regula- tions of the site country. 1.9 TORNADO/MISSILE PROTECTION Protection of buildings, housings, and essential equipment from effects of tornados and missiles launched by wind or other design basis events is required to allow controlled shutdown of the plant. A tornado passing over a facility causes a sharp drop in ambient pres- sure. If exposed to this transient pressure, ducts and filter housings could collapse because the pressure inside the structure would still be that of the environment prior to the pressure drop. Protection is usually provided by tornado dampers and missile barriers in all appropriate openings to the outdoors. Tornado dampers are heavy- duty, low-leakage dampers designed for pressure differences in excess of20 kPa. They are normally considered safety-class and are environmentally and seismically qualified. 1.10 FIRE PROTECTION Fire protection for HVAC and filtration systems must comply with applicable requirements of RG 1,189, Appendix R of 10 CFR Inc. ASHRAE, 2019 user. single for Licensed | {}
a1a519aa-5de5-42f4-8640-92e68853d834 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Nuclear Facilities 29.3 50, and NFPA, UL, and ANSI or equivalent standards of the site country. Design criteria should be developed for all building fire pro- tection systems, including secondary sources, filter plenum protec- tion, fire dampers, and systems for detection/suppression and smoke management. Fire protection systems may consist of a combination of building sprays, hoses and standpipes, and gaseous or foam sup- pression. The type of fire postulated in the Fire Hazard Analysis (FHA) or equivalent determines which kind of system is used. A requirement specific to U.S. nuclear commercial facilities is protection of carbon filter plenums and ventilation ductwork. Man- ually activated water sprays (window nozzles, fog nozzles, or stan- dard dry pipe/wet pipe system spray heads) are usually used for fire suppression in carbon filter plenums. Heat detectors and fire suppression systems should be consid- ered for special equipment such as glove boxes. Application of the two systems in combination allows the shutdown of one system at a time for repairs, modifications, or maintenance. In a DOE facility, the exhaust system duct penetrating a fire-rated boundary does not need a fire damper for maintaining the integrity of the boundary ifthe duct is fire rated. The exhaust duct may be rat- ed at up to two hours by either wrapping, spraying, or enclosing the duct in an approved material and qualifying it by an engineering analysis. Additional design guidance can be obtained from the Nu- clear Air Cleaning Handbook (DOE-HDBK-1 169-2003) and Fire Protection (DOE-STD- 1 066-2016). Fire protection and smoke control criteria can be found in NFPA Standards 801, 803, 804, 805, and 901, or equivalent standards of the site country. 1.11 SMOKE MANAGEMENT The design objective for smoke management in a nuclear facility is to protect the plant operators and equipment from internally and externally generated smoke. Smoke management involves (1) use of materials with low smoke-producing characteristics, (2) prevention of smoke movement to areas where operators may be overcome, (3) use of differential pressures to contain smoke to fire areas, (4) smoke venting to permit access to selected areas, and (5) purging to permit access to areas after a fire. Smoke control may be static, by prevention of smoke movement (NFPA 90A), or it may be dynamic, by controlling building pressure or air velocities (NFPA 92A). Ventilation systems in the affected areas should be shut down to prevent smoke from migrating and overcoming occupants in other areas. Smoke management for an internal fire source should allow the plant operator to shut down the reactor in a controlled manner and maintain shutdown condition. Smoke from an external fire should be isolated and appropriate measures provided to prevent smoke from entering the main control room envelope. This envelope includes the main control room and other necessary areas such as restrooms, kitchens, and offices. The location of the safe shutdown panels and the pathway to the safe shutdown panel must be such that, in case of abandonment of the main control room because of fire and smoke, safe egress is ensured. Capabilities should be provided for purging smoke from fire areas to permit reentry into the areas after the fire is isolated and extinguished. Venting may be used to remove heat and smoke at the point of the fire to permit firefighting and to control pressures gen- erated by fires. NFPA 90A, 204, and 92A and NUREG 800 SRP Branch Tech- nical Position CMEB 9.5.1.1 provide guidance for smoke manage- ment and discuss the discharge of smoke and corrosive gases. Control Room Habitability Zone The HVAC system in a control room is a safety-related system that must fulfill the following requirements during all normal and postulated accident conditions: · Maintain conditions comfortable to personnel, and ensure that control room equipment functions continuously and complies with its qualification limit · Protect personnel from exposure to radiation or toxic chemicals, in the event of a design basis accident · Protect personnel from combustion products (smoke) emitted from on-site and off-site fires · Limit unfiltered in-leakage to that credited in the design basis dose calculation. Additional information may be obtained from the NRC Standard Review Plans (NUREG 800), Sections 6.4 and 9.4.1, and TSTF Standard 448, Revs. 0 and 3. Air Filtration HVAC filtration systems can be designed to remove either radio- active particles or radioactive gaseous iodine from the airstream. They filter potentially contaminated exhaust air prior to discharge to the environment and may also filter potentially contaminated make- up air for power plant control rooms and technical support centers. The composition of the filter train is dictated by the type and con- centration of the contaminant, the process air conditions, and the fil- tration levels required by the applicable regulations (e.g., NRC Regulatory Guides RG 1.52, RG 1.140; ASME AG-1, N509, and 510 [for equipment designed to N509], and N511 [for equipment designed to AG-1]; 10 CFR 20, 10 CFR 100). Filter trains may con- sist of one or more of the following components: prefilters, high- efficiency particulate air (HEPA) filters, carbon filters (adsorbers), heaters, demisters and associated ductwork, housings, fans, damp- ers, and instrumentation. For nuclear-safety-related versions of this equipment, the latest edition of ASME AG-1 codifies rules for materials; design; inspection and testing; fabrication; packaging, shipping, receiving, storage, and handling; and quality assurance. Information common to all equipment is compiled in AG-1, Section AA: General Requirements. The AG-1 code discusses specific rules for each of the major components in separate sections For DOE facilities, the Nuclear Air Cleaning Handbook (DOE- HDBK-1169-2003) recommends the design of systems and use of major components for nuclear process facilities and laboratories. Demisters (Mist Eliminators). Demisters are required to pro- tect HEPA and carbon filters if entrained moisture droplets are expected in the airstream. They should be fire resistant. For details, see AG-1, Section FA. Heaters. Electric heating coils may be used to limit the relative humidity to 70% for carbon filters based on credited laboratory test condition. For safety-class systems, electric heating coils should be connected to the emergency power supply. Interlocks should be pro- vided to prevent heater operation when the exhaust fan is de- energized. For details, see AG-1, Section CA. Prefilters/Postfilters. Extended-surface filters are selected for the efficiency required by the particular application. AG-1, Table FB-4200-1, lists the average atmospheric dust spot efficiency ranges. AHRI 850 provides efficiency tolerances for the various classes. These types of filters are often used as prefilters for HEPA filters to prevent them from being loaded with atmospheric dust and to minimize replacement costs. High-efficiency (90 to 95%) filters are also often used as postfilters downstream of the carbon filter in lieu of downstream HEP As. For details, see AG-1, Section FB. European filter standards use efficiency tolerances from ISO 16890 in place of ARI 850. HEPA Filters. HEPA filters are used where there is a risk of par- ticulate airborne radioactivity. For details, see AG-1, Sections FC and FK. For DOE sites, the construction and quality assurance testing of HEPA filters are per DOE Standards 3020 and 3025. Carbon Filters. Activated carbon adsorbers are used mainly to remove radioactive iodine in gaseous state. Bed depths are typically Inc. ASHRAE, 2019 user. single for Licensed | {}
4575d697-68b8-4ee3-b2d7-9e292f941102 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 29.4 2019 ASHRAE Handbook-HVAC Applications (SI) 50 or 100 mm. Carbon filters have an efficiency 95 to 99% for organic iodine, although they lose efficiency as relative humidity increases. For this reason, they are often preceded by a heating ele- ment to keep the relative humidity of the entering air below 70%, and are tested at that condition. If the heater operation is not credited for maintaining relative humidity of the air stream, the carbon is tested at relative humidity of 95%. Nuclear carbon filters can be either tray type (Type II), rechargeable (Type III), or modular (Type IV). For details on each type, see AG-1, Sections FD, FE, and FH. Carbon efficiency is tested in accordance with Generic Letter 99-02 and ASTM D3803-89 (2014) or its latest edition. Both carbon and HEPA filters may be affected by exposure to paint solvent, chemicals, and fire, and thus should be evaluated on exposure. Design information for ventilation and air-conditioning system design, ductwork, housings, fans, dampers, and instrumentation are contained in AG-1, Sections CA, RA, SA, HA, BA, DA, and IA, respectively. Sand Filters. Sand filtration is a passive air filtration system that consists of multiple layers of sand and gravel through which air is drawn and filtered. The air enters an inlet tunnel that runs the entire length of the filter. Smaller cross-sectional laterals running perpen- dicular to the inlet tunnel distribute air across the base of the sand. Air rises through several layers of various sizes of sand and gravel, typically at a facial velocity of 25 mm/s. It is then collected in the outlet tunnel for discharge to the atmosphere. Sand filters require no maintenance, and the sand is not changed or replaced during its active service life. A detailed discussion of sand filters is given in Chapter 9 of the DOE's (2003) Nuclear Air Cleaning Handbook. Additionally, AG-1, Section FL, issued by ASME's Code of Nuclear and Air Gas Treatment (CONAGT) Committee, addresses deep bed sand filters. 2. DEPARTMENT OF ENERGY FACILITIES Inc. ASHRAE, 2019 user. single for Licensed The following discussion applies to U.S. National Laboratory facilities. Nonreactor nuclear HVAC systems must be designed in accordance with DOE Order 0 420.1 and the associated DOE stan- dards, guides, and handbooks listed at the end of this chapter. Crit- ical items and systems in plutonium processing facilities are designed to confine radioactive materials under both normal and DBA conditions. 2.1 CONFINEMENT SYSTEMS Zoning Typical process facility confinement systems are shown in Fig- ure 1. Process facilities comprise several zones. Primary Confinement Zone. This zone includes the interior of the hot cell, canyon, glove box, or other means of containing radio- active material. Containment must prevent the spread of radioactiv- ity within or from the building under both normal conditions and upset conditions up to and including a facility DBA. Complete iso- lation from neighboring facilities is necessary. Multistage HEPA fil- tration of the exhaust is required. Secondary Confinement Zone. This zone is bounded by the walls, floors, roofs, and associated ventilation exhaust systems of the operating and maintenance areas or rooms surrounding the pri- mary confinement zone. Tertiary Confinement Zone. This zone is bounded by the walls, floors, roofs, and associated ventilation exhaust systems of the facility. They provide a final barrier against the release ofhazardous material to the environment. Radiation monitoring may be required at exit points. ![image](/image/placeholder) TERTIARY CONFINEMENT ATMOSPHERE SECONDARY CONFINEMENT PRIMARY CONFINEMENT AIRFLOW BUILDING OPERATION/ GLOVE BOXES STRUCTURE MAINTENANCE ROOMS MOST NEGATIVE MORE NEGATIVE NEGATIVE SUPPORT BUILDINGS SLIGHTLY NEGATIVE Fig. 1 Typical Process Facility Confinement Categories Uncontaminated Zone. This zone includes offices and cold shop areas. Air Locks Air locks in nuclear facilities are used as safety devices to main- tain a negative differential pressure when a confinement zone is accessed. They are used for placing items in primary confinement areas and for personnel entry into secondary and tertiary confine- ment areas. Administrative controls ensure proper operation of the air lock doors. There are three methods of ventilating personnel air locks (ven- tilated vestibules): · The clean conditioned supply air method, where the air lock is at positive pressure with respect to the adjacent zones. For this method to be effective, the air lock must remain uncontaminated at all times. · The flow-through ventilation air method, where no conditioned air is supplied to the air lock and the air lock stays at negative pressure with respect to the less contaminated zone. · The combined ventilation air method, which is a combination of the other two methods. This may be the most effective method, when properly designed. Zone Pressure Control Negative static pressure increases (becomes more negative) from the uncontaminated zone to the primary confinement zone, causing any air leakage to be inward, toward areas of higher potential con- tamination. All zones should be maintained negative with respect to atmospheric pressure. Zone pressure control cannot be achieved through the ventilation system alone; confinement barrier construc- tion must meet all applicable specifications. Confinement barriers are enhanced by the use of a cascaded ven- tilation system, in which pressure gradients cause air to flow from areas of lower contamination to areas of higher contamination through engineered routes. In a cascade ventilation system, air is routed through areas or zones from lower contamination to higher contamination and then to highest contamination, thus reducing the number of separate ventilation systems and the amount of air required for contamination control. Cascade Ventilation Properly designed air locks should be provided for access be- tween noncontaminated and contaminated areas. If there is a poten- tial for development of differential pressure reversal, HEPA filters | {}
81d4031e-33a6-4c55-99e5-24c42579fcbf | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Nuclear Facilities 29.5 should be used at the inlet air openings between areas ofhigher and lower contamination levels to control the spread of contamination into less contaminated or cleaner areas. Appropriate sealing mech- anisms should be used for doors or hatches leading into highly con- taminated areas. Differential Pressures Differential pressures help ensure that air flows in the proper direction in case of a breach in a confinement zone barrier. The design engineer must incorporate the desired magnitudes of the dif- ferential pressures into the design early to avoid later operational problems. These magnitudes are normally specified in the design basis document of the safety analysis report (SAR). The following are approximate values for differential pressures between the three confinement zones. Primary Confinement. With respect to the secondary confine- ment area, air-ventilated glove boxes are typically maintained at pressures of-75 to -312 Pa, inert gas glove boxes at-75 to-375 Pa, and canyons and cells at a minimum of -250 Pa. Secondary Confinement. Differential pressures of -25 to - 37 Pa with respect to the tertiary confinement area are typical. Tertiary Confinement. Differential pressures of -2.5 to - 37 Pa with respect to the atmosphere are typical. 2.2 VENTILA TION Ventilation systems are designed to confine radioactive materials under normal and DBA conditions and to limit radioactive discharg- es to allowable levels. They ensure that airflows are, under all normal conditions, toward areas (zones) of progressively higher potential ra- dioactive contamination. Air-handling equipment should be sized conservatively so that upsets in the airflow balance do not cause the airflow to reverse direction. Examples of upsets include improper use of an air lock, a credible breach in the confinement barrier, or ex- cessive loading of HEPA filters. HEPA filters at the ventilation inlets in all primary confinement zone barriers prevent movement of contamination toward zones of lower potential contamination in case of an airflow reversal. Venti- lation system balancing helps ensure that the building air pressure is always negative with respect to the outdoor atmosphere. Recirculating refers to the reuse of air in a particular zone or area. Room air recirculated from a space or zone may be returned to the primary air-handling unit for reconditioning and then, with the approval of health personnel, be returned to the same space (zone) or to a zone of greater potential contamination. All air recirculated from secondary and tertiary zones must be HEPA-filtered before reintroduction to the same space. Recirculating air is not permitted in primary confinement areas, except those with inert atmospheres. A safety analysis is necessary to establish minimum acceptable response requirements for the ventilation system and its compo- nents, instruments, and controls under normal, abnormal, and acci- dent conditions. Analysis determines the number of exhaust filtration stages re- quired in different areas of the facility to limit (in conformance with the applicable standards, policies, and guidelines) the amount of radioactive or toxic material released to the environment during normal and accident conditions. Consult DOE Order 0 420.1, Stan- dard 1189, and Handbook 1169 (DOE 2003) for air-cleaning system criteria. Ventilation Requirements A partial recirculating ventilation system may be considered for economic reasons. However, it must be designed to prevent contam- inated exhaust from entering the room air-recirculating systems. The exhaust system is designed to (1) clean radioactive contam- ination from the discharge air, (2) safely handle combustion products, and (3) maintain the building under negative pressure rel- ative to the outdoors. Provisions may be made for independent shutdown of ventilation systems or isolation of portions of the systems to facilitate opera- tions, filter change, maintenance, or emergency procedures such as firefighting. All possible effects of partial shutdown on the airflows in interfacing ventilation systems should be considered. Positive means must be provided to control the backflow of air that might transport contamination. A HEPA filter installed at the interface between the enclosure and the ventilation system minimizes con- tamination in the ductwork; a prefilter reduces HEPA filter loading. These HEPA filters should not be considered the first stage of an air- borne contamination cleaning system. The following is a partial list of elements that may be included in the overall air filtration and air-conditioning system: Ventilation Systems · · · · Air-sampling devices · Pre- and/or postfilters (e.g., carbon adsorbers, deep bed sand, HEPA) Scrubbers · Demisters · Process vessel vent systems · Condensers · Distribution baffles · Fire suppression systems · Fire and smoke dampers · Exhaust stacks · Fans · Coils · Heat removal systems · Pressure- and flow-measuring devices Duct test ports Radiation-measuring devices · Criticality-safe drain systems · Tornado dampers · Smoke dampers The ventilation system and associated fire suppression system are designed for fail-safe operation. The ventilation system is equipped with alarms and instruments that report and record its behavior through readouts in control areas and utility service areas. Control Systems Control systems for HVAC systems in nuclear facilities have some unique safety-related features. Because the exhaust system is to remain in operation during both normal and accident-related con- ditions, redundancy in the form of standby fans is often provided. These standby fans and their associated isolation dampers energize automatically upon a set reduction in either airflow rate or specific location pressure, as applicable. For DOE facilities, maintaining exhaust airflow is important, so fire dampers are excluded from all potentially contaminated exhaust ducts. Pressure control in the facility interior maintains zones of in- creasing negative pressure in areas of increasing contamination po- tential. Care must be taken to prevent wind from unduly affecting the atmospheric control reference. Pulsations can cause the pressure control system to oscillate strongly, resulting in potential reversal of relative pressures. One alternative is to use a variety of balancing and barometric dampers to establish an air balance at the desired dif- ferential pressures, lock the dampers in place, and then control the exhaust air to a constant flow rate. Air and Gaseous Effluents Containing Radioactivity Air and all other gaseous effluents are exhausted through a ven- tilation system designed to remove radioactive particulates. Exhaust Inc. ASHRAE, 2019 user. single for Licensed | {}
0681fb58-5da4-42f4-a594-462297514a1c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 29.6 2019 ASHRAE Handbook-HVAC Applications (SI) ducts or stacks located downstream of final filtration that may con- tain radioactive contaminants should have two monitors, one a con- tinuous air monitor (CAM) and the other a fixed sampler. These monitors may be a combination unit. Exhaust stacks from nuclear facilities are usually equipped with an isokinetic sampling system that relies on a relatively constant airflow rate. The isokinetic sensing probe is a symmetrically arranged series of pickup tubes connected through sweeping bends to a stainless steel header that connects with capillary tubing to a sampling station (CAM). The air velocity through an isokinetic sampling system should be the same as the airstream being sampled. This ensures that particles captured by the isokinetic sampling probe and conveyed to the sampling sta- tion are the same size particles that are conveyed in the airstream being sampled. Typically, an exhaust system flow controller modu- lates the exhaust fan inlet dampers or motor speed to hold the exhaust airflow rate steady while the HEPA filters load. CAMs can also be located in specific ducts where a potential for radiological contamination has been detected. These CAMs are generally placed beyond the final stage of HEPA filtration, as spec- ified in HPS Standard N13.1. Each monitoring system is connected to an emergency power supply. The following are design considerations for CAM systems: · Maintain fully developed turbulent flow at the nonisokinetic sam- pling point. · Maintain fully developed laminar flow at the isokinetic sampling point. · Ensure fully developed turbulent flow is established between the final filtration and the isokinetic sampling point. · For accurate CAM operation, heat tracing on the sampling air tubing may be required. · Maintain the ratio of the sample airflow rate to total discharge air- flow rate constant. 3. COMMERCIAL FACILITIES 3.1 OPERATING NUCLEAR POWER PLANTS The two kinds of commercial light-water power reactors cur- rently in operation in the United States, and in many other countries, are the pressurized water reactor (PWR) and the boiling water reac- tor (BWR). Heavy water (deuterium oxide) reactors are used in Canada and some other countries. Gas-cooled reactors constitute most of the installed base in Great Britain, but are in the process of being phased out. For all these types, the main objective of the HVAC systems, in addition to ensuring personnel comfort and reli- able equipment operation, is protecting operating personnel and the general public from airborne radioactive contamination during nor- mal and accident conditions. Radiation exposure limits are con- trolled by 10 CFR 20. The "as low as reasonably achievable" (ALARA) concept is the design objective of the HVAC system. The radiological dose is not allowed to exceed the limits as defined in 10 CFR 50 and 10 CFR 100. For other countries operating commercial nuclear plants, the specific national rules and regulations should be consulted. NRC Regulatory Guides (RGs) delineate techniques of evaluating specific problems and provide guidance to applicants concerning the information the NRC needs for its review of the facility. The regulatory guides that relate directly to HVAC system design are RG 1.52, RG 1.78, RG 1,140, RG 1,194, RG 1.196, and RG 1.197. Deviations from RG criteria must be justified by the owner and approved by the NRC. Some countries also invoke NRC regulatory guides as part of the design requirements. Deviations from RG criteria must be requested through the applicable govern- ment agency in the country of construction. The design of the HV AC systems for a U.S. nuclear power gener- ating station must ultimately be approved by the NRC in accordance with Appendix A of 10 CFR 50. The NRC developed standard re- view plans (SRPs) as part of Regulatory Report NUREG-0800 to provide an orderly and thorough review. The SRP provides a good basis or checklist for the preparation of a safety analysis report (SAR). The SRP is the basis for information provided by an appli- cant in an SAR as required by Section 50.34 of10 CFR 50. Technical specifications for nuclear power plant systems are developed by the owner and approved by the NRC as outlined in Section 50.36 of 10 CFR 50. Technical specifications define the safety limits, limiting conditions for operation (LCO), and surveillance requirements (SR) for all systems important to plant safety. Minimum requirements for the performance, design, construc- tion, acceptance testing, and quality assurance of equipment used in safety-related air and gas treatment systems in nuclear facilities are found in ASME N509, N510, N511, and AG-1. Temperature and humidity conditions are dictated by the nuclear steam supply system (NSSS). For U.S. plants, the common modes of operation are normal, hot shutdown, cold shutdown, and refueling. Normal Operation. NSSS temperature and humidity require- ments are specified by the NSSS supplier. Some plants require recir- culation filtration trains in the containment building to control the level of airborne contamination. In existing plants, containment cooling is necessary for maintaining the components in the contain- ment and to ensure that design limits are not exceeded during acci- dents. Cooling is provided by a containment cooling system. Some next-generation plants are mostly of passive design and thus do not need active containment cooling systems. Refueling Condition. The temperature in the refueling or fuel- handling area is determined by the need to perform refueling activ- ities safely. Also, because personnel work in protective clothing, they can be vulnerable to heat stress. To prevent this, area cooling can be provided by a normal non-safety-related cooling system. Outdoor air should be provided for ventilation. Accident Scenarios Plants are analyzed for four types of accidents: (1) loss of coolant accident (LOCA), (2) fuel handling accident (FHA), (3) control rod drop accident (CRDA), and (4) a main steam line break (MSLB). For all plant types, it necessary to evaluate the limiting accident event and to conduct safety assessments, so measures can be taken to mitigate any accident's any accident's consequences. Major NSSS Types Pressurized- Water Reactors (PWRs). These reactors, widely used in the United States, use enriched uranium for fuel. The reactor, steam generators, and other components of the NSSS are housed in the containment structure. Other support systems are housed in the auxiliary building, control building, turbine building, and diesel building. In PWR design, the steam turbine is powered by nonradioactive steam for the generation of electricity. General de- sign requirements of the PWR plant are contained in ANSI/ANS Standard 56.6-1986. Figure 2 shows a typical PWR. Boiling- Water Reactor (BWRs). Also widely used in the United States, this type of design reactor uses enriched uranium for fuel. The reactor pressure vessel and related piping are housed with- in the primary containment, which is also referred to as the drywell (Figure 3). The drywell is a low-leakage, pressure-retaining struc- ture designed to withstand the high temperature and pressure from a major break in the reactor coolant line. The drywell is housed within a concrete structure called the secondary containment or the reactor building. Other support systems are housed in the control building, turbine building, and diesel building. In BWR design, the steam turbine is powered by radioactive steam for the generation of Inc. ASHRAE, 2019 user. single for Licensed | {}
eb1eca1e-2ee0-4b15-9bfd-a4d556c7f0a1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Nuclear Facilities 29.7 ![image](/image/placeholder) STEAM LINE CONTAINMENT COOLING SYSTEM 3 STEAM 4 GENERATOR TURBINE REACTOR GEN- CONTROL RODS ERA- VESSEL TOR HEATER CON- DENSER CON- 2 DEN- COOLANT LOOP CORE SATE 1 PUMPS FEED PUMPS REACTOR PRESSURIZER DEMINERALIZER COOLANT PUMPS EMERGENCY WATER SUPPLY SYSTEMS Fig. 2 Typical Pressurized- w ater Reactor (From NRC web site: www.nrc.gov) ![image](/image/placeholder) CONTAINMENT COOLING SYSTEM 4 STEAM LINE REACTOR VESSEL TURBINE SEPARATORS GENERATOR AND DRYERS HEATER FEEDWATER CONDENSER 3 CONDEN- CORE SATE 1 and 2 PUMPS FEED PUMPS CONTROL RODS DEMINERALIZER RECIRCULATION PUMPS EMERGENCY WATER SUPPLY SYSTEMS Fig. 3 Typical Boiling-Water Reactor (From NRC web site: www.nrc.gov) electricity. General design requirements of the BWR plant are con- tained in ANSI/ANS Standard 56.7-1987. Heavy Water Reactors. Canadian power reactors use natural uranium fuel and heavy water (deuterium oxide), which acts as a moderator and a coolant source. The reactor core is mounted in a large, horizontal steel vessel called a calandria, which is enclosed in a concrete containment structure. This design enables the reactors to be refueled while the unit is operating at full power. Commercial Plant License Renewal and Power Uprate Nuclear power plants were originally licensed for a 40 year term and a defined power output capacity. Most nuclear plants currently operating in the United States have applied for or will be applying for license renewal to extend the plant operating license from 40 to 60 years. As part of the license renewal process, passive plant com- ponents, such as HVAC ductwork and piping, are reviewed, and renewal licenses are granted based on the commitment to perform aging management review (AMR) oflong-lived components. Credit is taken for the maintenance rule to address upkeep and replacement of active components. Maintenance rule requirements are outlined in 10 CFR 50.65, Nuclear Energy Institute documents, Nuclear Management Resources Council (NUMARC) 93-0, and NRC Reg- ulatory Guide RG 1.160. In addition to license renewal, most plants are increasing their power output capacity by as much as 5 to 15% by conducting power uprate evaluations. Power uprates are often done in steps, and are often categorized as (1) measurement uncertainty recapture power uprates, (2) stretch power uprates, and (3) extended-power uprates. As part of the power uprate, the effects of power output on plant and HV AC systems are evaluated, and these systems are upgraded as needed. 3.2 NEW NUCLEAR POWER PLANTS Many new nuclear power generation plants are being considered for construction in the United States, as well as in other parts of the world. The U.S. NRC has streamlined the application and licensing process for the new reactors, and the Code of Federal Regulations 10 CFR 52 governs the issuance of combined construction and oper- ating license. The new plants are being designed and licensed to sat- isfy the demand for additional generation capacity in a competitive environment, while contributing to sustainable growth. Advantages of the newer plants include standardized designs with shortened construction times; up to 60-year service life; and the possibility of using flexible fuel (including mixed oxide [MOX] fuel). The status of design certification and combined construction and operating license (COL) applications for various new U.S. plants can be found at the NRC Web site (www.nrc.gov). New reactors being considered in the United States are the ad- vanced passive 1000 (AP1000), economic simplified boiling-water reactor (ESBWR), U.S. evolutionary power reactor (USEPR), ad- vanced boiling-water reactor (ABWR) and U.S. advanced pressur- ized water reactor (USAPWR). The AP1000 and the ESBWR use passive cooling systems, and the need for safety-related HVAC sys- tems is limited. The ABWR and the USAPWR are enhanced de- signs of the boiling water reactor and pressurized water reactor, respectively, and HVAC systems for these reactors are not expected to be very much different than those at currently operating BWR and PWR plants. The USEPR is a pressurized water reactor of Eu- ropean design. Brief overviews ofHV AC for AP1000, ESBWR, and USEPR plants are as follows. Advanced Passive AP1000 HVAC systems at AP1000 plants have several differences from those at pressurized-water reactor plants. The main control room (MCR) has both a normal and an emergency HVAC system. The normal system maintains temperature and relative humidity during normal plant operation, and the emergency system uses passive cooling heat sinks to maintain habitability in the main control room during accident conditions. The normal HVAC system has supple- mental air filtration that can be used to filter outdoor air with HEPA and charcoal filters, and maintains the main control room at a slight positive pressure to prevent infiltration of unfiltered air into the main control room envelope. On detection of high radiation in the supply air or an extended loss of ac power, the normal system is iso- lated and the safety-related emergency habitability system is acti- vated. During emergency-mode operation, air is supplied to the MCR from pressurized storage tanks that are sized to meet the ven- tilation and pressurization requirements for a 72 h accident event. Inc. ASHRAE, 2019 user. single for Licensed | {}
ee2e4589-5d9f-49fb-b008-2e42d58bc628 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 29.8 2019 ASHRAE Handbook-HVAC Applications (SI) Passive heat sinks are used in the MCR, instrumentation and control (I&C), and dc equipment rooms to limit temperature rise in those rooms after loss of normal HVAC systems. The heat sinks primarily consist of the thermal mass of concrete in the ceilings and walls. Safety-related HVAC equipment is limited to containment isolation valves, control room isolation valves, and the emergency habitability system. Limiting active safety equipment and using passive safety features is part of the AP1000 design philosophy. The AP1000 has a containment air filtration system, but it serves no safety-related function and is isolated during accident condi- tions. It is designed to provide intermittent venting of the contain- ment to the atmosphere during normal plant operation. HVAC systems serving the AP1000 diesel generator, radioactive waste (radwaste), annex, and turbine buildings are similar to those in exist- ing PWRs, with a few exceptions: (1) the containment HVAC recir- culation system is non-safety-related; (2) the containment HVAC recirculation system uses chilled water to cool containment; and (3) the diesel generators (and thus the diesel generator building) are not safety related. Economic Simplified Boiling- Water Reactor (ESBWR) ESBWR HVAC systems have several differences from those at operating boiling-water reactor plants. The control building ventila- tion system has two subsystems: the control building general-area ventilation system (CBGA VS), which serves general areas in the control building, and the control room habitability-area (CRHA) ventilation system (CRHA VS), which serves the main control room. The CRHA VS provides cooling to MCR, which is served by two redundant recirculation air-handling units (AHUs). Recirculation air-handling units in the main control room draw air from the ceiling space plenum, condition it, and discharge it to an underfloor air dis- tribution system. There is an outdoor air AHU for providing makeup to the MCR for normal habitability. During emergency mode, the CRHA is isolated at the boundary by isolation dampers. The recir- culation AHU continues to cool while a battery-powered emergency filter unit (EFU) with HEPA and carbon filters provides filtered out- door air. If power is lost, the EFU continues to operate for pressur- ization and to maintain the MCR at 30 Pa positive relative to the surroundings for the 72 h accident coping period. During this time, the walls and boundary areas act as passive heat sinks to limit the temperature rise in the main control room. The reactor building (RB) ventilation system (RBVS) has three non-safety-related subsystems: the contaminated-area ventilation subsystem (CONA VS), refueling and pool-area ventilation subsys- tem (REPA VS), and the reactor building clean-area ventilation sub- system (CLA VS). These systems are separated from the each other with isolation dampers. The CLA VS and CONA VS subsystems are split into separate trains for serving the two halves of the RB. The RBVS has two non-safety-related filter trains (with HEPA and carbon filters), which are backed up with power supply from the die- sel generators. Those systems operate on loss of power, but are not credited in the accident analysis. The fuel building ventilation sys- tem (FBVS) has two non-safety-related subsystems: the fuel build- ing general-area ventilation subsystem (FBGA VS) and the fuel building fuel-pool-area ventilation subsystem (FBFPVS). The FBGA VS and the FBFPVS subsystems are once-through systems, and room coolers provide supplementary cooling for selected rooms in the fuel building. The ESB WR uses a centralized non-safety-related chilled-water plant and provides chilled water to various buildings, including the drywell, based on the primary/secondary loop design concept. U.S. Evolutionary Power Reactor (USEPR) Unlike the AP1000 and the ESB WR, the USEPR is not of pas- sive design and is similar to PWR plants, except that the emergency (safety) systems have a four-loop or four-train design: there are four electrical trains of safety systems, four emergency diesels and four loops of safety chilled water. The main control room HV AC system has an active and diverse cooling system consisting of two trains of safety-related water-cooled chillers and two trains of safety-related air-cooled chillers. The main control room air-conditioning system (CRACS) is designed to maintain habitability in the main control room and adjoining rooms during normal operation and during accident conditions involving radiation and toxic gas releases. The CRACS maintains the control room envelope at a 30 Pa positive pressure relative to surrounding areas during accident conditions. The CRACS filtration and air-conditioning equipment and associated ductwork are located inside the control room pressure boundary, thus eliminating the potential for in leakage of unfiltered air. Smoke detectors and toxic gas sensors in the outdoor air supply duct actuate an alarm in the main control room and automatically place the cool- ing system in recirculation mode. The containment building ventilation system (CBVS) is com- posed of three separate subsystems: the (1) non-safety-related full- and low-flow containment purge system, (2) non-safety-related containment filtration system, and (3) safety-related containment cooling system. The containment low-flow purge subsystem oper- ates during normal plant operation to facilitate containment entry and to support outages activities, whereas the full-flow purge system operates only during outages to control the containment en- vironment. The containment filtration subsystem consists of a filter unit with HEPA and carbon filters and a heater, and is used for clean- up of the containment environment. The containment cooling sub- system contains fans, cooling coils, and associated ductwork for cooling various areas of the containment. 4. PLANT HVAC&R SYSTEMS 4.1 PRESSURIZED-W ATER REACTORS Containment Building Containment Cooling. The following systems are typical for containment cooling: Reactor containment coolers. These units remove most of the heat load. Distribution of the air supply depends on the containment layout and the location of the major heat sources. Reactor cavity air-handling units orfans. These units are usually transfer fans without coils that provide cool air to the reactor cavity. Control rod or control element drive mechanism (CRDM or CEDM) air-handling units. The CRDM and CEDM are usually cooled by an induced-draft system using exhaust fans. Because the flow rates, pressure drops, and heat loads are generally high, the air should be cooled before it is returned to the containment atmosphere. Essential containment cooling units. The containment air-cooling system, or a part ofit, is normally designed to provide cooling during normal plant operation and after a postulated accident. The system must be able to perform at high temperature, pressure, humidity, and levels ofradioactivity. Cooling coils are provided with essential plant service water. System design must accommodate both normal and accident con- ditions. The ductwork must be able to endure the rapid pressure build-up associated with accident conditions, and fan motors must be sized to handle the high-density air. In addition, the system must be analyzed to identify measures to mitigate the effect of water hammer as addressed in NRC's Generic Letter 96-06. Radioactivity Control. Airborne radioactivity is controlled by the following means: Essential air filtration units. Redundant filter units powered by two Class 1E buses are used to reduce the amount of airborne radio- activity. The typical system consists ofa demister, a heater, a HEPA Inc. ASHRAE, 2019 user. single for Licensed | {}
8bb0ec3d-ff48-41c7-ac40-7b6238cee7b0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Nuclear Facilities 29.9 filter bank, and a carbon adsorber, possibly followed by a second HEPA filter bank or by a high-efficiency (90 to 95%) filter bank. The electric heater is designed to reduce the relative humidity of the incoming air from 100% to less than 70%. All the components of the air filtration unit are environmentally qualified (EQ), and designed to meet the requirements of a LOCA. In the case of an accident and the subsequent operation of the filter train, the carbon can become loaded with radioactive iodine such that the decay heat could cause the carbon to self-ignite if the airflow stops. Heat build-up in the carbon adsorber bed should be evaluated, and an appropriate redundant decay heat removal mech- anism should be provided. Containment power access purge or minipurge. Ventilation is sometimes necessary during normal operation, when the reactor is under pressure, to control containment pressure or the level of air- borne radioactivity within the containment. The maximum opening size allowed in the containment boundary during normal operation is 200 mm. The system consists of a supply fan, double containment isola- tion valves in each ofthe containment wall penetrations (supply and exhaust), and an exhaust filtration unit with a fan. The typical filtra- tion unit contains a HEPA filter and a carbon adsorber, possibly fol- lowed by a second HEPA filter or by a medium-efficiency (90 to 95%) filter bank. The system is non-safety-related, and operates during personnel access into the containment with the reactor under pressure. During normal plant operation, the containment tends to- ward positive pressure because of air leaks and the exhaust fan is often operated as needed to control pressure inside the containment. This minipurge system should not be connected to any duct sys- tem inside the containment. It should include a debris screen within the containment over the inlet and outlet ducts, so that the contain- ment isolation valves can close even if blocked by debris or col- lapsed ducts. Containment refueling purge. Ventilation is required to control the level of airborne radioactivity during refueling. Because the reactor is not under pressure during refueling, there are no restric- tions on the size of the penetrations through the containment boundary. Large openings of 1000 to 1200 mm, each protected by double containment isolation valves, may be provided. The required ventilation rate is typically based on 1 air change per hour. The system consists of a supply air-handling unit, double con- tainment isolation valves at each supply and exhaust containment penetration, and an exhaust fan. Filters are recommended. Containment combustible gas control. In the case of a LOCA, when a strong solution of sodium hydroxide or boric acid is sprayed into the containment, various metals react and produce hydrogen. Also, if some ofthe fuel rods are not covered with water, the fuel rod cladding can react with steam at elevated temperatures to release hydrogen into the containment. Therefore, redundant hydrogen recombiners are needed to remove hydrogen from the containment atmosphere, recombine the hydrogen with oxygen, and return the air to the containment. The recombiners may be backed up by spe- cial exhaust filtration trains. 4.2 BOILING-WATER REACTORS Primary Containment The primary containment HV AC system consists ofrecirculating cooling units. It normally recirculates and cools the primary con- tainment air to maintain the environmental conditions specified by the NSSS supplier. During an accident, the system may perform a safety-related function of recirculating the air to prevent stratifica- tion of any hydrogen that may be generated if the system is credited in the accident analysis. Depending on the specific plant design, the cooling function may or may not be safety related. Primary contain- ment cooling is necessary for maintaining the life ofthe components inside the containment and for ensuring that the safety temperature limit of the primary containment is maintained during an accident. Resistance temperature detectors (RTDs) measure containment temperatures at various locations, and provide input into the volu- metric average temperature, which is used as the measure of the containment temperature. The plant's technical specification oper- ating limit is established based on the volumetric average tem- perature. Temperature problems have been experienced in many BWR primary containments because of temperature stratification and underestimation of heat loads. The cooling system should be designed to adequately mix the air to prevent stratification. Heat load calculations should include a safety factor sufficient to allow for deficiencies and degradation in insulation. Reactor Building The reactor building completely encloses the primary contain- ment, auxiliary equipment, and refueling area. Under normal con- ditions, the reactor building HVAC system maintains the design space conditions and minimizes the release of radioactivity to the environment. The HVAC system consists of a 100% outdoor air cooling system. Outdoor air is filtered, heated, or cooled as required before being distributed throughout the various building areas. The exhaust air flows from areas with the least potential contamination to areas of most potential contamination. Before exhausting to the environment, potentially contaminated air is filtered with HEPA fil- ters and carbon adsorbers; all exhaust air is monitored for radioac- tivity. To ensure that no unmonitored exfiltration occurs during normal operations, the ventilation systems maintain the reactor building at a negative pressure relative to the atmosphere. During an event involving a LOCA, MSLB, FHA, or high radia- tion in the ventilation exhaust, the HVAC system's safety-related function is to isolate the secondary containment consisting of the re- actor building and the refueling area. Once isolated by fast-closing valves, the secondary containment boundary functions to contain any leakage from the primary containment or refueling area. Once the secondary containment is isolated, a safety-related standby gas treatment system (SGTS) is started to reduce the ground level releases by drawing down the secondary containment pressure to about -60 Pa within 120 s. The SGTS exhausts air from the sec- ondary containment to the environment at an elevated release loca- tion referred to as the main stack. The SGTS consists of redundant filtration trains, which consist primarily of HEPA filters and carbon adsorbers. The capacity of the SGTS is based on the amount of ex- haust air needed to reduce the pressure in the secondary containment and maintain it at the design level, given the containment leakage rates and required drawdown times. In addition to the SGTS, some designs include safety-related re- circulating air systems within the secondary containment to mix, cool, and/or treat the air during accidents. These recirculation sys- tems sometimes use portions of the normal ventilation system ductwork; therefore, if the ductwork is used for that purpose, then it must be classified as safety related. Other than the emergency core cooling system (ECCS) pump rooms, the isolated secondary containment area is not cooled during accident events. All safety-related components in the secondary containment must be environmentally qualified to operate at the maximum temperature and the temperature profile for the accident event. Safety-related room coolers served by the plant service water provide cooling to the emergency core cooling system (ECCS) pumps during accident conditions. Turbine Building Only a BWR supplies radioactive steam directly to the turbine, which could cause a release of airborne radioactivity to the surround- ings. Therefore, areas of the BWR turbine building in which release of airborne radioactivity is possible should be enclosed. These areas Inc. ASHRAE, 2019 user. single for Licensed | {}
af40875d-726f-4366-aded-c7c17d977ea1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 29.10 Inc. ASHRAE, 2019 user. single for Licensed must be ventilated and the exhaust filtered to ensure that no radioac- tivity is released to the atmosphere. Filtration trains are non-safety- related and they typically consist of a prefilter, a HEPA filter, and a carbon adsorber, possibly followed by a second HEPA filter bank or by a medium-efficiency (90 to 95%) filter bank. Filtration require- ments and testing are based on the plant and site configuration and commitments for 10 CFR 50, Appendix I requirements. Depending on outdoor air conditions at the location, the turbine building is cooled either with outdoor air or by area coolers served by a dedi- cated chilled-water system. 4.3 HEA VY WATER REA CTORS Containment Inlet Air-Conditioning/Exhaust Ventilation System The production of heavy water in sufficient quantities for the needs of a heavy water reactor is complex and expensive. Once pro- duced, however, deuterium oxide (D2O) may be reused indefinitely as long as it does not become contaminated. Because heavy water reactor containments are vented and require makeup air, ordinary water (H2O) is one contaminant that must be contained. This is nor- mally accomplished by means of a non-nuclear safety desiccant air- conditioning unit mounted on the roof of the service building. This unit typically contains a rotary desiccant dryer, hot-water heating coils and chilled-water cooling coils both upstream and downstream of the desiccant wheel, a desiccant regeneration duct containing an electric heater, and a flow control system. The resulting inlet makeup air contains very little moisture. To prevent any radioactive contaminants from escaping up the stack, the containment exhaust ventilation unit typically contains a prefilter bank, a HEPA filter bank, a Type III carbon filter, a second HEPA filter bank, and an exhaust fan. 4.4 AREAS OUTSIDE PRIMARY CONTAINMENT All areas located outside the primary containment are designed to the general requirements contained in ANSI/ANS Standard 59.2. These areas are common to any type of plant. Auxiliary Building The auxiliary building contains a large amount of support equip- ment, much of which handles potentially radioactive material. The building may be air conditioned for equipment protection, and the exhaust is filtered to prevent the release of potential airborne radio- activity. The filtration trains typically consist of a prefilter, a HEPA filter, and a carbon adsorber, possibly followed by a second HEPA filter bank or by a high-efficiency (90 to 95%) filter bank. The HVAC system is a once-through system, as needed for gen- eral cooling. Ventilation is augmented by area or room coolers in the individual equipment rooms requiring additional cooling. The building is maintained at negative pressure relative to the outdoors. If the equipment in these rooms is not safety related, the area is cooled by normal air-conditioning units. If they are safety related, the area is cooled by safety-related or essential area or room coolers units powered from the same Class 1E (according to IEEE Standard 323) power supply as the equipment in the room. The normal and essential functions may be performed by one cooling unit having both a normal and an essential cooling coil and a safety-related fan served from a Class 1E bus. The normal coil can be a direct-expansion or chilled-water cooling coil served by a nor- mal chilled-water system. The essential coil operates with chilled water from a safety-related chilled-water system or the plant service water, or a safety-related cooling water source. 2019 ASHRAE Handbook- -HVAC Applications (SI) Control Room The control room HV AC system serves the control room habit- ability zone (those spaces that must be habitable following a pos- tulated accident to allow orderly shutdown of the reactor) and performs the following functions: · Controls indoor environmental conditions · Provides pressurization to prevent infiltration · Minimizes unfiltered in-leakage to the level credited in control room operator dose assessments · Protects the zone from hazardous chemical fume or particle intru- sion · Protects the zone from fire · Removes noxious fumes, such as smoke In defining the control room envelope or pressure boundary, it is necessary to ensure that, in the event of abandonment as a result of fire or smoke in the control room, access to the remote shutdown panel is safeguarded. Design requirements for the control room HV AC system are out- lined in 10 CFR 50, GDC 19 Appendix A, Standard Review Plan Sections 6.4 and 9.4.1, NCR Regulatory Guides RG 1.52, 1.78, 1,194, 1.196, and 1.197, and NUREG 0737. In 2003, NRC issued Generic Letter 2003-01 to address control room habitability find- ings at U.S. nuclear power plants, which suggested that licensees may not have been meeting the control room licensing and design basis, and applicable regulatory requirements, and that existing technical specification surveillance requirements may not have been adequate. As a result, all nuclear plants are required to conduct con- trol room inleakage testing using the tracer gas (SF6) to validate the integrity of the control room boundary and to ensure compliance with dose assessments per GDC 19, Appendix A. It is also necessary to develop and maintain a control room integrity program in accor- dance with the plant technical specification requirements to control and maintain boundary breaches. Plants are also required to conduct self-assessments of their control room habitability program every three years and inleakage testing every six years. Control room HVAC filter units are designed to filter radioactive contaminants and are fabricated, designed, and tested per ASME Standards N509, N510, N511, and AG-1. Control Cable Spreading Rooms These rooms are located directly above and below the control room. They are usually served by an independent ventilating or cooling system or by the air-handling units that serve the electric switchgear room or the control room. Diesel Generator Building Nuclear power plants have an auxiliary or back-up power source for all essential and safety-related equipment in case of loss of off- site electrical power. The auxiliary power source consists of at least redundant diesel generators, each sized to meet the emergency power load. Heat released by the diesel generator and associated auxiliary systems is normally removed by a safety-related ventila- tion. Emergency Electrical Switchgear Rooms These rooms house the electrical switchgear that controls essen- tial or safety-related equipment. The switchgear located in these rooms must be protected from excessive temperatures (1) to ensure that its qualified life, as determined by environmental qualification, is maintained and (2) to preserve power circuits required for proper operation of the plant, especially its safety-related equipment. | {}
b9aaa0b7-16fc-4059-9683-56934afa8ef5 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Nuclear Facilities 29.11 Battery Rooms Battery rooms should be maintained at approximately 20 to 25°C for optimum battery capacity and service life. Temperature variations are acceptable as long as they are accounted for in bat- tery sizing calculations. The minimum room design temperature should be taken into account in determining battery capacity. Because batteries produce hydrogen gas during charging periods, the HVAC system must be designed to limit the hydrogen concen- tration to the lowest of the levels specified by IEEE Standard 484, ASHRAE guidelines, OSHA, and the lower explosive limit (LEL) (see Chapter 11 of the 2017 ASHRAE Handbook-Fundamentals for more information). The IEEE 1635/ASHRAE Guideline 21 recommends limiting hydrogen concentration (by volume) in the battery room to 2% or less. If battery design information is not available, it is recommended that the exhaust system be designed to provide a minimum of five air changes per hour. Fuel-Handling Building New and spent fuel is stored in the fuel-handling building. The building is air conditioned for equipment protection and ventilated with a once-through air system to control potential airborne radio- activity. Normally, the level of airborne radioactivity is so low that the exhaust need not be filtered, although it should be monitored. If significant airborne radioactivity is detected, as can happen during an FHA, the normal building ventilation is isolated and the safety- related system started automatically. The safety-related ventilation system should exhaust through filtration trains powered by Class 1E buses. Personnel Facilities For nuclear power plants, these areas usually include decontam- ination facilities, laboratories, and medical treatment rooms. Pumphouses Cooling water pumps are protected by houses that are often ven- tilated by fans to remove the heat from the pump motors. If the pumps are essential or safety related, the ventilation equipment must also be considered safety related. Radioactive Waste Building The building is normally air conditioned for equipment protec- tion and ventilated to control potential airborne radioactivity. The air may require filtration through HEPA filters and/or carbon adsorbers prior to release to the atmosphere. Technical Support Center The technical support center (TSC) is an outside facility located close to the control room. Although normally unoccupied, it is used by plant management and technical support personnel during training exercises and accident events. The TSC HV AC system is designed to provide the same level of comfort (temperature and humidity) and radiological habitability conditions as provided for the control room. The TSC HVAC system is a non-safety-related system, but is augmented to the same level of importance as the main control room HVAC system. An air filtration system (HEPA, carbon, postfilter) provides the facility protection from radiological releases during an accident. Additional compo- nents, such as moisture separators, heaters, and prefilters, are some- times also used. Because the operation and availability of the TSC is credited in the plant's emergency operating procedures, the TSC HVAC system should be designed with some redundancy such that maintenance on the HVAC system does not require declaration of the TSC as unavailable. Consult NUREG-0696 for additional infor- mation. 4.5 NONPOWER MEDICAL AND RESEARCH REACTORS The requirements for HVAC and filtration systems for nuclear nonpower medical and research reactors are set by the NRC. The criteria depend on the type of reactor (ranging from a nonpressur- ized swimming pool type to a 10 MW or more pressurized reactor), the type of fuel, the degree of fuel enrichment, and the type of facil- ity and environment. Many of the requirements discussed in the sec- tions on various nuclear power plants apply to a certain degree to these reactors. It is therefore imperative for the designer to be familiar with the NRC requirements for the reactor under design. 4.6 LABORATORIES Requirements for HVAC and filtration systems for laboratories using radioactive materials are set by the DOE and/or the NRC. Lab- oratories located at DOE facilities are governed by DOE regulations. All other laboratories using radioactive materials are regulated by the NRC. Other agencies may be responsible for regulating other toxic and carcinogenic material present in the facility. Laboratory containment equipment for nuclear processing facil- ities is treated as a primary, secondary, or tertiary containment zone, depending on the level of radioactivity anticipated for the area and on the materials to be handled. For additional information see Chap- ter 17. Glove Boxes Glove boxes are windowed enclosures equipped with one or more flexible gloves for handling material inside the enclosure from the outside. The gloves, attached to a porthole in the enclosure, seal the enclosure from the surrounding environment. Glove boxes permit hazardous materials to be manipulated without being released to the environment. Because the glove box is usually used to handle hazardous mate- rials, the exhaust is filtered with a HEPA filter before leaving the box and prior to entering the main exhaust duct. In nuclear processing facilities, a glove box is considered primary confinement (see Figure 1), and is therefore subject to the regulations governing those areas. For non-nuclear processing facilities, the designer should know the designated application of the glove box and design the system according to the regulations governing that particular application. Additional information for glove boxes can be found in docu- mentation published by the American Glovebox Society (AGS). Laboratory Fume Hoods Nuclear laboratory fume hoods are similar to those used in non- nuclear applications. Air velocity across the hood opening must be sufficient to capture and contain all contaminants in the hood. Excessive hood face velocities should be avoided because they cause contaminants to escape when an obstruction (e.g., an operator) is positioned at the hood face. For information on fume hood testing, refer to ASHRAE Standard 110. Radiobenches A radiobench has the same shape as a glove box except that in lieu of the panel for the gloves, there is an open area. Air velocity across the opening is generally the same as for laboratory hoods. The level of radioactive contamination handled in a radiobench is much lower than that handled in a glove box. 4.7 DECOMMISSIONING NUCLEAR FACILITIES The exhaust air filtration system for decontamination and de- commissioning (D&D) activities in nuclear facilities depends on the type and level of radioactive material expected to be found during Inc. ASHRAE, 2019 user. single for Licensed | {}
97f22c15-9504-49bd-b8e0-5f1a7c732116 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 29.12 2019 ASHRAE Handbook-HVAC Applications (SI) the D&D operations. The exhaust system should be engineered to accommodate the increase in dust loading, with more radioactive contamination than is generally anticipated, because the D&D ac- tivities dislodge previously fixed materials, making them airborne. Good housekeeping measures include chemical fixing and vacuuming the D&D area as frequently as necessary. The following are some design considerations for ventilation sys- tems required to protect the health and safety of the public and the D&D personnel: · Maintain a higher negative pressure in the areas where D&D activities are being performed than in any of the adjacent areas. · Provide an adequate capture velocity and transport velocity in the exhaust system from each D&D operation to capture and transport fine dust particles and gases to the exhaust filtration system. · Exhaust system inlets should be as close to the D&D activity as possible to enhance the capture of contaminated materials and to minimize the amount of ductwork that is contaminated. A mov- able inlet capability is desirable. · With portable enclosures, filtration of the enclosure inlet and exhaust air must sustain the correct negative internal pressure. Low-Level Radioactive Waste Requirements for the HVAC and filtration systems of low-level radioactive waste facilities are governed by 10 CFR 61. Each facility must have a ventilation system to control airborne radioac- tivity. The exhaust air is drawn through a filtration system that typ- ically includes a demister, heater, prefilter, HEPA filter, and carbon adsorber, maybe followed by a second filter. Ventilation systems and their CAMs should be designed for the specific characteristics of the facility. 4.8 WASTE-HANDLING FACILITIES The handling of radioactive waste requires inventory control of the different radioactive wastes. See the section on Codes and Stan- dards for pertinent publications. 4.9 REPROCESSING PLANTS A reprocessing plant is a specific-purpose facility. Spent nuclear fuel is opened and the contents dissolved in nitric acid to enable the constituents to be chemically separated and recovered. The offgas contains hazardous chemical and radioactive contaminants. Special cleanup equipment, such as condensers, scrubbers, cyclones, mist eliminators, and special filtration, is required to capture the vapors. 4.10 MIXED-OXIDE FUEL FABRICA TION FACILITIES The mixed-oxide (MOX) fuel fabrication facility (MFFF) is designed to produce MOX fuel for use in commercial nuclear power plants. In the United States, this facility is DOE operated and NRC licensed. MOX fuel fabrication consists of blending polished pluto- nium dioxide with uranium dioxide to form mixed-oxide pellets and loading them into fuel rods that form fuel assemblies for use as nuclear fuel. The MFFF HVAC design includes several important design features, and it complies with the performance criteria of 10 CFR 70, ASME AG-1, IEC/IEEE 60780-323, IEEE 344, and other applicable codes and standards. In addition to maintaining the design environmental conditions, the HVAC systems are designed to maintain a pressure differential between the building confinement zones and between the building and the outdoors to ensure that cascaded airflow is from zones of lesser contamination potential to zones of greater contamination. The supply air system provides air to all confinement zones. Each confinement zone has its own exhaust system, and the pressure boundaries are maintained by cascaded airflow from tertiary confinement (negative) to secondary confinement (more negative), and then to primary confinement (most negative) zones. Primary and secondary confinement ventilation exhaust systems include both the intermediate and the final filter units in series. Tertiary con- finement exhaust systems include only the final filter units. Interme- diate filter units contain roughing filter(s) (i.e., stainless steel mesh filter) and HEPA filter(s) in series. Final filter units contain roughing filter(s), prefilter(s) (i.e., stainless steel/glass fiber mesh filter), and two banks of HEPA filter(s) in series. Air locks between confinement zones are designed to minimize personnel contamina- tion exposure by maintaining pressures between various zones. Pri- mary and secondary confinement exhaust systems are provided with on-site emergency diesel power, and battery back-up is provided for the primary confinement exhaust system. Glove boxes (GB) are provided with room ventilation air, dry air, or inert gas, as determined by the process requirements. GB exhaust piping is connected to common headers for intermediate and final filtration. The ventilation system is designed to maintain a normal operating pressure of -300 to -500 Pa. Pressure-relief valves and vacuum breakers are provided to keep GB pressures within their structural design limits under conditions such as loss of supply flow or failed open valves. Additionally, dump valves (high- volume relief valves connected to exhaust header) are provided to ensure that, in the event of a glove port or bag port breach, the cap- ture velocity at the breach is at least 0.6 m/s. Detailed analysis, using compressible-flow pipe network analysis software, is performed for the MFFF ventilation systems and GB ventilation system. and the results are used for airflow bal- ancing and to confirm that confinement is maintained during normal and design-basis accident conditions. Sprinkler systems for HEPA filtration units are eliminated by in- tegrating ventilation exhaust system design with fire-safety design. To confirm this design approach, a prototype final filter unit is tested in a testing laboratory for higher soot loading and differential pres- sures than calculated design values. The test results should show no breach in any filter in the prototype unit. Sheet metal thickness and reinforcement for galvanized steel and stainless steel duct systems, with pressures from +7.5 to -7.5 kPa, round duct diameter up to 1525 mm, rectangular duct width up to 3660 mm, and temperature exposure up to 204°C, are designed using SMACNA standards. Seismic supports for the duct systems and redundant tornado dampers at outer wall openings are designed to protect the duct systems during abnormal events. RESOURCES Where edition or reaffirmation dates are not listed, the latest date applies. AGS ¦ Guide 006 ¦ Standard of Practice for the Design and Fab- rication of Nuclear Application Gloveboxes ¦ ¦ --- ¦ --- ¦ ¦ Guide 010 ¦ Standard of Practice for Glovebox Fire Pro- tection ¦ ¦ ANS Standards ¦ ¦ ¦ Standard 56.6 ¦ Pressurized Water Reactor Containment Ventilation Systems (ANSI approved; with- drawn) ¦ ¦ Standard 56.7 ¦ Boiling Water Reactor Containment Ventila- tion Systems (ANSI approved; withdrawn) ¦ ¦ Standard 59.2 ¦ Safety Criteria for HVAC Systems Located Outside Primary Containment (ANSI ap- proved; withdrawn) ¦ Inc. ASHRAE, 2019 user. single for Licensed | {}
b4397699-eda7-4361-bf40-c048e4a00afa | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Nuclear Facilities 29.13 ¦ AHRI Standard 850 ¦ Performance Rating of Commercial and Industrial Air Filter Equipment (ANSI approved) ¦ Standard 1128 Standard 1129 Standard 3020 3025 ¦ Good Practices for Occupational Radiological Protection in Plutonium Facili- ties Tritium Handling and Safe Storage Specification for HEPA Filters Used by DOE Contractors Testing of ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ASHRAE Standard 110 ¦ Method ofTesting Performance of Laboratory Fume Hoods (ANSI approved) ¦ Standard 1168 Standard 1189 ¦ Confinement Ventilation and Process Gas Treatment Functional Area Qualification Standard Integration of Safety into the Design Process ¦ ¦ ASME ¦ ¦ ¦ ¦ ¦ Standard AG-1 ¦ Code on Nuclear Air and Gas Treatment ¦ ¦ ¦ ¦ ¦ Nuclear Power Plant Units and ¦ ¦ ¦ ¦ Standard N509 ¦ Air-Cleaning Components ¦ Standard ¦ Quality Assurance Inspection and HEPA Filters ¦ ¦ Standard N510 Standard N511 ¦ Testing of Nuclear Air Treatment Systems In-Service Testing ofNuclear Air Treatment, Heating, Ventilating, and Air-Conditioning Systems ¦ HPS Standard N13.1 ¦ ¦ ¦ ¦ ¦ ¦ Sampling and Monitoring Releases of Air- borne Radioactive Substances from the Stack and Ducts of Nuclear Facilities (ANSI ¦ ¦ Standard NQA-1 ¦ Quality Assurance Program Requirements ¦ ¦ approved) ¦ ¦ ASTM ¦ for Nuclear Facility Applications ¦ ISO Standards Standard 16890 ¦ Air Filters for General Ventilation ¦ ¦ Standard D3803 ¦ Standard Test Method for Nuclear-Grade Activated Carbon ¦ ISO 9000 Series IEC/IEEE ¦ Quality Management Systems ¦ ¦ Standards ¦ ¦ ¦ Nuclear Facilities-Electrical Equipment Important to Safety- Qualification ¦ ¦ Canadian CAN3-N286 Series CAN3-N299 Series Code of Federal 10 CFR Part 50 ¦ Quality Assurance for Nuclear Power Plants Quality Assurance Program Requirements for the Supply of Items and Services for Nu- clear Power Plants ¦ Standard 60780 IEEE Standard 344 ¦ Seismic Qualification of Equipment for Nu- clear Power Generating Stations ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Recommended Practices for Installation Design and Installation of Vented Lead-Acid Batteries for Stationary Applications (ANSI approved) ¦ ¦ Part 20 ¦ Regulations Title 10 of the Code ofFederal Regulations Standards for Protection Against Radiation ¦ Standard 484 IEEE/ASHRAE ¦ ¦ ¦ Part 50.69 ¦ Domestic Licensing of Production and Utili- zation ¦ ¦ ¦ ¦ ¦ Facilities Risk-Informed Categorization and Treatment of Structures, Systems and Components for ¦ Standard 1635/ ¦ Guide for the Ventilation and Thermal Man- agement of Batteries for Stationary Applica- ¦ ¦ ¦ Nuclear Power Reactors Licenses, Certifications, and Approvals for Nuclear Power Plants ¦ Guideline 21 NFPA ¦ tions ¦ ¦ ¦ Land Disposal of Radioactive Waste ¦ Standard 90A ¦ Standard for the Installation of Air Condi- ¦ ¦ Part 52 Part 61 Part 65 ¦ Requirements for Monitoring the Effective- ness of Maintenance at Nuclear Power Plants ¦ Standard 90B ¦ tioning and Ventilating Systems (1999) Standard for the Installation of Warm Air Heating and Air Conditioning Systems ¦ ¦ ¦ Domestic Licensing of Special Nuclear Ma- terial ¦ ¦ (1999) ¦ ¦ Part 70 ¦ ¦ ¦ Standard Air Con- ¦ ¦ Part 100 ¦ Reactor Site Criteria ¦ Standard 91 ¦ for Exhaust Systems for veying of Vapors, Gases, Mists, and Particu- late Solids ¦ ¦ Part 835 ¦ Occupational Radiation Protection ¦ ¦ ¦ ¦ Guides ¦ ¦ ¦ ¦ ¦ DOE ¦ ¦ Standard 92A ¦ Recommended Practice for Smoke Control Systems for Smoke and Heat Venting Radioactive ¦ ¦ Guide 420.1-1A DOE Handbooks ¦ Nonreactor Nuclear Safety Design Guide for use with DOE O420.1C, Facility Safety ¦ Standard ¦ Standard Standard for Facilities Handling Materials ¦ ¦ ¦ ¦ 204 Standard 801 ¦ ¦ ¦ HDBK-1132-99 HDBK-1169-2003 Orders ¦ Design Considerations ¦ Standard 803 ¦ Standard for Fire Protection for Light Water Nuclear Power Plants ¦ ¦ DOE ¦ Nuclear Air Cleaning Handbook ¦ Standard 804 ¦ Standard for Fire Protection for Advanced Light Water Reactor Electric Generating Plants ¦ ¦ Order 420.1 ¦ Facility Safety ¦ ¦ ¦ ¦ ¦ ¦ Standard 805 ¦ Fire Protec- ¦ ¦ ¦ ¦ ¦ Performance Based Standard for for Light Water Plants ¦ ¦ DOE Policy Policy P 450.4A DOE Standards Standard 1020 Standard 1066 ¦ Integrated Safety Management Policy ¦ ¦ tion Reactor Electric Gener- ating ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Hazards Analysis ¦ Standard 806 ¦ Performance Based Standard for Fire Protec- ¦ ¦ ¦ Natural Phenomena and Design Criteria for Department of Energy ¦ ¦ tion for Advanced Nuclear Reactor Electric ¦ ¦ ¦ Facilities Fire Protection ¦ Standard 901 ¦ Generating Plants Classifications for Incident Reporting and Fire Protection Data ¦ Inc. ASHRAE, 2019 user. single for Licensed | {}
b06b1f0a-462d-4ccc-86c4-263181c8fe88 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 29.14 2019 ASHRAE Handbook- - HVAC Applications (SI) ¦ NRC ¦ ¦ RG 1.197 ¦ Demonstrating Control Room Envelope ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ NUMARC 93-01 ¦ Industry Guideline for Monitoring the Effec- tiveness of Maintenance at Nuclear Power Plants ¦ RG 1.201 ¦ Integrity at Nuclear Power Reactors Guidelines for Categorizing Structures, Sys- tems, and Components in Nuclear Power Plants Safety Signifi- ¦ ¦ NUREG-0696 ¦ Functional Criteria for Emergency Response Facilities ¦ ¦ According to Their cance ¦ ¦ NUREG-0737 ¦ Clarification of TMI Action Plan Require- ments ¦ RG 1.52, Rev. 3 ¦ Design, Testing, and Maintenance Criteria for Engineered Safety Feature Atmospheric and ¦ ¦ NUREG-0800 ¦ Standard Review Plans ¦ ¦ Cleanup System Air Filtration Adsorp- tion Units ofL WR Nuclear Power Plants ¦ ¦ 6.4 ¦ Control Room Habitability ¦ RG 1.78, Rev. 2 ¦ Assumptions for Evaluating the Habitability ¦ ¦ ¦ System Control Room Area Ventilation System ¦ ¦ of Nuclear Power Plant Control Room During a Postulated Hazardous Chemical Release ¦ ¦ 9.4.1 9.4.2 ¦ Spent Fuel Pool Area Ventilation System ¦ ¦ ¦ ¦ 9.4.3 ¦ Auxiliary and Radwaste Building Ventila- Systems ¦ ¦ ¦ ¦ 9.4.4 ¦ tion Turbine Area Ventilation System ¦ Generic Letters ¦ ¦ ¦ 9.4.5 ¦ Engineered Safety Feature Ventilation Sys- ¦ 96-06 ¦ Assurance of Equipment Operability and Containment Design-Basis ¦ ¦ Regulatory Guides ¦ tem ¦ ¦ Integrity During ¦ ¦ RG 1,140, Rev. 2 ¦ Design, Testing, and Maintenance Criteria for Normal Ventilation Exhaust System Air ¦ 99-02 ¦ Accident Conditions Laboratory Testing of Nuclear Grade Activated Charcoal ¦ ¦ ¦ Filtration and Adsorption Units of L WR ¦ ¦ ¦ ¦ RG 1.160 ¦ Nuclear Power Plants Monitoring the Effectiveness of Mainte- nance at Nuclear Power Plants ¦ 2003-01 ¦ Control Room Habitability ¦ ¦ RG 1.189 ¦ Fire Protection for Operating Nuclear Power Plants ¦ Technical Specifications ¦ Task Force (TSTF) ¦ ¦ ¦ ¦ 448 ¦ Control Room Habitability ¦ ¦ RG 1.194 ¦ Atmospherior Relative Concentrations for Room Radiological Habitability ¦ ¦ ¦ ¦ ¦ ¦ ¦ ASHRAE Journal articles ¦ ¦ RG 1.196 ¦ Assessments at Nuclear Power Plants Control Room Habitability at Light- Water Nuclear Power Reactors ¦ ASHRAE members can research project final .org. Articles reports bers ¦ access and ASHRAE reports at technologyportal.ashrae and are also available forpurchase by nonmem- in the online ASHRAE Bookstore at www.ashrae.org/bookstore. ¦ Inc. ASHRAE, 2019 user. single for Licensed Related Commercial Resources | {}
3f46b2b2-3377-4600-ada4-802ffc660961 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 30 MINE AIR CONDITIONING AND VENTILATION ¦ Definitions ¦ 30.1 ¦ ¦ --- ¦ --- ¦ ¦ Sources of Heat Entering Mine Air ¦ 30.2 ¦ ¦ Heat Exchangers ¦ 30.4 ¦ ¦ Mine-Cooling Techniques ¦ · 30.7 ¦ I N underground mines, lower worker productivity, illness, and potentially death can result from poor working environment con- ditions. It is therefore extremely important to design, install, and manage underground ventilation systems with the necessary care and attention. Excess humidity, high temperatures, inadequate oxygen, and excessive concentrations ofpotentially dangerous gases can significantly affect the quality of the working environment if not properly controlled. Ventilation and air cooling are needed in under- ground mines to minimize heat stress and remove contaminants. As mines become deeper, heat removal and ventilation problems be- come more difficult and costly to solve. Caution: This chapter presents only a very brief overview of the principles of mine ventilation planning. The person responsible for such planning should either be an experienced engineer, or work un- der the direct supervision of such an engineer. Several English- language texts have been written on mine ventilation since 1980 (Bossard 1982; Hall 1981; Hartman et al. 1997; Hemp 1982; Kennedy 1996; McPherson 1993; Mine Ventilation Society of South Africa 1982; Tien 1999). The ventilation engineer is strongly encour- aged to study these references. Certain industrial spaces may contain flammable, combustible, and/or toxic aerosol concentrations under either normal or abnormal conditions. In spaces such as these, there are fire- and life-safety issues that this chapter may not completely address. Special precau- tions must be taken in accordance with requirements of recognized authorities such as the National Fire Protection Association (NFPA), the Occupational Safety and Health Administration (OSHA), and the American National Standards Institute (ANSI). In all situations, engineers, designers, and installers who encounter conflicting codes and standards must defer to the most stringent code or standard, or that which best addresses and safeguards life safety. The facility's insurance carriers and relevant authorities having jurisdiction (AHJs) can be consulted for advice regarding specific situations. 1. DEFINITIONS Definitions specific to mine ventilation and air conditioning are as follows. Heat stress is a qualitative assessment of the work environment based on temperature, humidity, air velocity, and radiant energy. Many heat stress indices have been proposed (see Chapter 9 of the 2017 ASHRAE Handbook-Fundamentals for a thorough discus- sion); the most common in the mining industry are effective tem- perature (Hartman et al. 1997), air cooling power (Howes and Nixon 1997), and wet-bulb temperature. The following wet-bulb tempera- ture ranges were derived from experience at several deep western U.S. metal mines: twb ≤ 27°C Worker efficiency 100% 27 < twb ≤ 29°C Economic range for acclimatized workers 29 < twb ≤ 33°C Safety factor range; corrective action required The preparation of this chapter is assigned to TC 9.2, Industrial Air Conditioning. ¦ Selecting a Mine-Cooling Method ¦ 30.9 ¦ ¦ --- ¦ --- ¦ ¦ Mechanical Refrigeration Plants ¦ 30.9 ¦ ¦ Mine Air Heating ¦ 30.10 ¦ ¦ Mine Ventilation ¦ 30.11 ¦ 33°C < twb Only short-duration work with adequate breaks Heat strain is the physiological response to heat stress. Effects include sweating, increased heart rate, fatigue, cramps, and progres- sively worsening illness up to heat stroke. Individuals have different tolerance levels for heat. Reject temperature, based on the heat stress/strain relationship, is the wet-bulb temperature at which air should be either rejected to exhaust or recooled. Reject temperature ranges between 25.5 and 29°C wb, depending on governmental regulation, air velocity, and expected metabolic heat generation rate of workers. Specifying the reject temperature is one of the first steps in planning air- conditioning systems. The ventilation engineer must be able to jus- tify the reject temperature to management, because economics are involved. If set too high, work productivity, health, safety, and mo- rale suffer; iftoo low, capital and operating costs become excessive. Critical ventilation depth is the depth at which the air tempera- ture in the intake shaft rises to the reject temperature through auto- compression and shaft heat loads. Work areas below the critical ventilation depth rely totally on air conditioning to remove heat. The critical ventilation depth is reached at about 2500 to 3000 m, depending on surface climate in the summer, geothermal gradient, and shaft heat loads such as pump systems. Base heat load is calculated at an infinite airflow at the reject temperature passing through the work area. The temperature of an infinite airflow will not increase as air picks up heat. Actual heat load is measured or calculated at the average stope temperature. It is always greater than the base heat load because the average stope tem- perature is lower than the reject temperature. More heat is drawn from the wall rock. Marginal heat load is the difference between base and actual heat loads. Itis the penalty paid for using less than an infinite airflow (i.e., the lower the airflow, the lower the inlet tem- perature required to maintain the reject temperature and the higher the heat load). Temperature-dependent heat sources (TDHs) depend on the temperature difference between the source and air. Examples include wall rock, broken rock, and fissure water (in a ditch or pipe). Temperature-independent heat sources (TIHs) depend only on the energy input to a machine or device after the energy required to raise the potential energy of a substance, if any, is deducted. Exam- ples include electric motors, lights, substation losses, and the calo- rific value of diesel fuel. Passive thermal environmental control separates heat sources from ventilating airflows. Examples include insulating pipes and wall rock, and blocking off inactive areas. Active thermal environ- mental control removes heat via airflow and air conditioning quickly enough that air temperature does not rise above the reject. Positional efficiency, an important design parameter for mine cooling systems, is the cooling effect reaching the work area divided by the machine evaporator duty. The greater the distance between the machine and work area, the more heat that the cooling medium (air or water) picks up en route. Percent utilization is the ratio of the evaporator duty of the refrig- eration plant over a year in energy units to the duty if the plant had 30.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
18626f36-0061-416d-b5bf-70258da124a8 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 30.2 worked the entire year at 100% load. This consideration becomes important when evaluating surface versus underground plants. Coefficient of performance (COP) is usually defined as the evaporator duty divided by the work of compression in similar units. In mines, the overall COP is used: the evaporator duty divided by all power-consuming devices needed to deliver cooling to the work sites. This includes pumps and fans as well as refrigeration machine compressors. A shaft is a vertical opening or steep incline equipped with skips to hoist ore and the cages (elevators) that move personnel and sup- plies. Electric cables and pipes for fresh water, compressed air, cooling water, pump water, and other utilities are installed in shafts. Drifts and tunnels are both horizontal openings; a tunnel opens to daylight on both ends, whereas a drift does not. In metal mining, a stope is a production site where ore is actually mined. In coal mining, coal is usually produced by either longwall (one continuous production face many metres long) or room-and-pillar (multiple production faces in a grid of rooms with supporting pillars in between) methods. 2. SOURCES OF HEAT ENTERING MINE AIR Adiabatic Compression Air descending a shaft increases in pressure (because of the mass of air above it) and thus also increases in temperature, as if com- pressed in a compressor. This is because of conversion of potential energy to internal energy, even if there is no heat interchange with the shaft and no evaporation of moisture. For dry air at standard conditions (15°C at 101.325 kPa), the spe- cific heat at constant pressure Cp is 1.004 kJ/(kg· K). For most work, Cp can be assumed constant, but extreme conditions might warrant a more precise calculation: 1 kJ is added (for descending airflow) or subtracted (for ascending airflow) to each kilogram of air for every 102 m. The dry-bulb temperature change is 1/(1.004 x 102 x 1) = 0.00977 K per metre or 1 K per 102 m of elevation. The specific heat for water vapor is 1.884 kJ/(kg·K). So, for constant air/vapor mix- tures, the change in dry-bulb temperature is (1 + W)/(1.004 + 1.884W) per 102 m of elevation, where W is the humidity ratio in kilograms of water per kilogram of dry air. Inc. ASHRAE, 2019 user. single for Licensed The theoretical heat load imposed on intake air by adiabatic com- pression is given in Equation (1), which is a simplified form of the general energy equation: 9 = QPE △d where (1) 9 theoretical heat of autocompression, W 0 = airflow in shaft, m3/s P = air density, kg/m3 E = energy added per unit distance of elevation change, 1 kJ/(102 m·kg) △d = elevation change, m Example 1. What is the equivalent heat load from adiabatic compression of 140 m3/s at 1.12 kg/m3 density flowing down a 1500 m shaft? Solution: 9 = (140)(1.12)(1/102)(1500) = 2306 kW The adiabatic compression process is seldom truly adiabatic: autocompression is a more appropriate term. Other heating or cooling sources, such as shaft wall rock, introduction of groundwater or water sprayed in the shaft to wet the guides, compressed-air and water pipes, or electrical facilities, often mask the effects of adiabatic compression. The actual temperature increase for air descending a shaft usually does not match the theoretical adiabatic temperature increase, for the following reasons: 2019 ASHRAE Handbook-HVAC Applications (SI) · The effect of seasonal and daily surface temperature fluctuations, such as cool night air on the rock or shaft lining (rock exhibits thermal inertia, which absorbs and releases heat at different times of the day) · The temperature gradient of rock related to depth · Evaporation of moisture in the shaft, which suppresses the dry- bulb temperature rise while increasing the moisture content of the air The wet-bulb temperature lapse rate varies, depending on the entering temperature and humidity ratio, and the pressure drop in the shaft. It averages about 1.4 K wet bulb per 300 m, and is much less sensitive to evaporation or condensation than the dry bulb. Electromechanical Equipment Electric motors and diesel engines transfer heat to the air. Loss components of substations, electric input to devices such as lights, and all energy used on a horizontal plane appear as heat added to the mine air. Energy expended in pumps, conveyors, and hoists to increase the potential energy of a material does not appear as heat, after losses are deducted. Vehicles with electric drives, such as scoop-trams, trucks, and electric-hydraulic drill jumbos, release heat into the mine at a rate equivalent to the nameplate and a utilization factor. For example, a 100 kW electric loader operated at 80% of nameplate for 12 h a day liberates (100 kJ/s)(12 h)(3600 s/h)(0.80) = 3 456 000 kJ/day. Dividing by 24 h/day gives an average heat load over the day of 144 000 kJ/h. During the 12 h the loader is operating, the heat load is doubled to 288 000 kJ/h. The dilemma for the ventilation engi- neer is that, ifheat loads are projected at the 144 000 rate, the stope temperature will exceed the reject temperature for half the day, and the stope will be overventilated for the other half; if projected at 288 000 kJ/h, the stope will be greatly overventilated when the loader is not present. Current practice is to accept the additional heat load while the loader is present. Operators get some relief when they leave the heading to dump rock, at which time the ventilation system can partially purge the heading. Diesel equipment dissipates about 90% of the heat value of the fuel consumed, or 35 000 kJ/L, to the air as heat (Bossard 1982). The heat flow rate is about three times higher for a diesel engine than for an equivalent electric motor. If the same 100 kW loader discussed previously were diesel powered, the heat would aver- age about 475 000 kJ/h over the day, and 950 000 kJ/h during actual loader operation. Both sensible and latent heat components of the air are increased because combustion produces water vapor. If a wet scrubber is used, exhaust gases are cooled by adi- abatic saturation and the latent heat component increases even further. Fans raise the air temperature about 0.25 K per kPa static pres- sure. Pressures up to 2.5 kPa are common in mine ventilation. This is detrimental only when fans are located on the intake side of work areas or circuits. Groundwater Transport ofheat by groundwater has the largest variance in mine heat loads, ranging from essentially zero to overwhelming values. Groundwater usually has the same temperature as the virgin rock. Ventilating airflows can pick up more heat from hot drain water in an uncovered ditch than from wall rock. Thus, hot drain water should be stopped at its source or contained in pipelines or in COV- ered ditches. Pipelines can be insulated, but the main goal is isolat- ing the hot water so that evaporation cannot occur. Heat release from open ditches increases in significance as air- ways age and heat flow from surrounding rock decreases. In one Montana mine, water in an open ditch was 22 K cooler than when it flowed out of the wall rock; the heat was transferred to the air. | {}
da768c3c-8be8-4cbd-a5bd-e226f9df53bd | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Mine Air Conditioning and Ventilation 30.3 Table 1 Maximum Virgin Rock Temperatures ¦ Mining District ¦ Depth, m ¦ Temperature, °C ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Kolar Gold Field, India ¦ 3350 ¦ 67 ¦ ¦ South Africa ¦ 3660 ¦ 52 to 57 ¦ ¦ Morro Velho, Brazil ¦ 2440 ¦ 54 ¦ ¦ North Broken Hill, Australia ¦ 1080 ¦ 44 ¦ ¦ Great Britain ¦ 1220 ¦ 46 ¦ ¦ Braloroe, BC, Canada ¦ 1250 ¦ 45 ¦ ¦ Kirkland Lake, Ontario ¦ 1830 ¦ 27 ¦ ¦ Falconbridge Mine, Ontario ¦ 1830 ¦ 29 ¦ ¦ Lockerby Mine, Ontario ¦ 1220 ¦ 36 ¦ ¦ Levac Borehold (Inco), Ontario ¦ 3050 ¦ 53 ¦ ¦ Garson Mine, Ontario ¦ 1520 ¦ 26 ¦ ¦ Lake Shore Mine, Ontario ¦ 1830 ¦ 23 ¦ ¦ Hollinger Mine, Ontario ¦ 1220 ¦ 14 ¦ ¦ Creighton Mine, Ontario ¦ 3050 ¦ 59 ¦ ¦ Superior, AZ ¦ 1220 ¦ 60 ¦ ¦ San Manuel, AZ ¦ 1370 ¦ 48 ¦ ¦ Butte, MT ¦ 1590 ¦ 66 ¦ ¦ Homestake Mine, SD ¦ 2440 ¦ 57 ¦ ¦ Ambrosia Lake, NM ¦ 1220 ¦ 60 ¦ ¦ Brunswick #12, New Brunswick, Canada ¦ 1130 ¦ 23 ¦ ¦ Belle Island Salt Mine, LA ¦ 430 ¦ 31 ¦ Source: Fenton (1972). Table 2 Thermal Properties of Rock Types ¦ Rock Type ¦ Thermal Conductivity, W/(m·K) ¦ Diffusivity, m2/h ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Coal ¦ 2.20 ¦ 0.005 ¦ ¦ Gabro ¦ 2.37 ¦ 0.009 ¦ ¦ Granite ¦ 1.92 ¦ 0.012 ¦ ¦ Pyritic shale ¦ 3.65 ¦ 0.007 ¦ ¦ Quartzite ¦ 5.50 ¦ 0.008 ¦ ¦ Sandstone ¦ 1.97 ¦ 0.006 ¦ ¦ Shale ¦ 2.39 ¦ 0.003 ¦ ¦ Rhyolite ¦ 3.46 ¦ 0.004 ¦ ¦ Sudbury ore ¦ 2.60 ¦ 0.005 ¦ ¦ North Idaho metamorphic ¦ 5.11 ¦ 0.010 ¦ Source: Mine Ventilation Services Inc., Fresno, CA. Reprinted with permission. Evaporation of water from wall rock surfaces lowers the surface temperature of the rock, which increases the temperature gradient of the rock, depresses the dry-bulb temperature of the air, and allows more heat to flow from the rock. Most of this extra heat is expended in evaporation. Example 2. Water leaks from a rock fissure at 1.26 L/s and 52°C. If the water enters the shaft sump at 29°C, what is the rate of heat transfer to the air? Solution: Heat rate = (1.26 L/s)(1 kg/L)[4.1868 kJ/(kg·K)](52 - 29°C) = 121.33 kW Wall Rock Heat Flow Wall rock is the main heat source in most deep mines. Tempera- ture at the earth's core has been estimated to be about 5700°C. Heat flows from the core to the surface at an average of 0.07 W/m2. The implication for mine engineers is that a geothermal gradient exists: rock gets warmer as the mine deepens. The actual gradient varies from approximately 1 to over 7 K per 100 m of depth, depending on the thermal conductivity oflocal rock. Table 1 gives depths and max- imum virgin rock temperatures (VRTs) for various mining dis- tricts. Table 2 gives thermal conductivities and diffusivities for rock types commonly found in mining. These two variables are required for wall rock heat flow analysis. Wall rock heat flow is unsteady-state: it decays with time because of the insulating effect of cooled rock near the rock/air boundary. Equations exist for both cylindrical and planar openings, but this sec- tion discusses cylindrical equations (Goch and Patterson 1940). The method can solve for either instantaneous or average heat flux rate. The instantaneous rate is recommended because it is better used for older tunnels or drifts. For newer drifts, a series of instantaneous rates over short time periods is equivalent to the average rate. The Goch and Patterson calculations are easily performed on a computer using the following variables and equations: au Fo = 2 r (2) 3 = {1.017 + 0.7288 log10(Fo) + 0.1459[log10(Fo)]2 - 0.01572[log10(Fo)]3 - 0.004525 [log10(Fo)]4 + 0.001073 [log10(Fo)]5}-1 k(tvr-ta)(�) Heat flux, W/m2 = r (3) (4) Total heat flow (W) = (Heat flux)(L)(P) where (5) Fo = Fourier number, dimensionless k = thermal conductivity of rock, W/(m·K) L = length of section, m P = perimeter of section, m r = radius of circular section, m, or equivalent radius of rectangular section; r = (A/�)1/2, where A = cross-sectional area of section, m2 ta = air dry-bulb temperature, °C tvr = virgin rock temperature, °C a = thermal diffusivity of rock (equals k/pc), m2/h, where p = rock density, kg/m3 c = heat capacity, kJ/(kg·K) 3 = function ofFourier number for instantaneous rate, dimensionless (Whillier and Thorpe 1982) 0 = average age of section, h Example 3. A 150 m long section of drift, 3.7 m high by 4.5 m wide, was driven in quartzite with a VRT of 43°C. The drift was started 20 days before the face was reached, and the face is 1 day old. One design crite- rion is keeping the average dry-bulb temperature of the air in the drift at 27°C. How much heat will flow into the section? Solution: From Table 2, the thermal conductivity of quartzite is 5.50 W/(m . K) and the diffusivity is 0.008 m2/h. The average age of the section is (20 + 1 days)/2 = 10.5 days, or 252 h. The cross-sectional area of the drift is 3.7 x 4.5 = 16.65 m2 and the perimeter is (3.7 + 4.5) x 2 = 16.4 m. The equivalent radius of the drift is (16.65/�)1/2 = 2.30 m. The following equations are then applied: au (0.008)(252) Using Equation (2), Fo = = = 0.381 2 2 r 2.30 Using Equation (3), 8 = 1.336 Using Equation (4), k(tvr-ta)(�) (5.50)(43-27)(1.336) Heat flux = = r 2.30 = 51.12 W/m2 Using Equation (5), Total heat flow = (Heat flux)(L)(P) = (51.12)(150)(16.4) = 125 755 W Inc. ASHRAE, 2019 user. single for Licensed | {}
051383fd-2ef5-40a6-8c82-2fc19e488465 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 30.4 Thus, to keep the average temperature of the drift section at 27°C db, 126 kW of refrigeration are needed in that section. The Goch and Patterson method lacks a convective heat transfer coefficient at the rock/air boundary, and overestimates heat transfer in a dry drift by 8 to 15%. It also does not have a wetness factor. Because a drift with water on the perimeter draws more heat from wall rock, the method underestimates heat flow. Almost all drifts have some wetness on the floor, back, and side walls, though it may not be visible. Comparisons of the Goch and Patterson method with field measurements and results from commercial software under typical conditions (a drift with 20 to 60% of the perimeter wetted) indicate that the overestimate is nearly equal to the underestimate. When using Goch and Patterson for drift heat loads, keep drift sec- tion lengths under 60 m and do not apply any contingency factor to the calculated heat load. Heat load calculations for stoping require a large number of vari- ables. Irregular shapes, sporadic advance rates, intermittent TIH sources, fissure water, and non-homogeneous or anisotropic (with directionally differing heat conducting properties) rock are difficult to model (Duckworth and Mousset-Jones 1993; Marks and Shaffner 1993). For cut-and-fill stoping with a sand floor, measured heat loads are about 70% of the heat loads predicted by Goch and Patterson. Other stoping methods such as room-and-pillar or tabular reef mining are more amenable to planar heat load equations. Pat- terson (1992) gives empirical graphs relating heat load to produc- tivity and depth. Ventilation engineers needing to project heat loads for new mines or extensive tunnel projects can write their own computer program using the Goch and Patterson equations, or use a commercial soft- ware package. These programs account for convective heat transfer, wetness, elevation changes, and TIH sources that can make hand calculations tedious. However, program input must be carefully derived or the output will be misleading. Heat from Broken Rock Freshly blasted broken rock can liberate significant amounts of heat in a confined area. The broken rock's initial and final tempera- tures, and cooling of the rock en route from the face to the hoisting facility, must be estimated. Heat, kJ = (mass)(specific heat)(VRT - final temperature) (6) Inc. ASHRAE, 2019 user. single for Licensed Heat Heat load, W = (time, s) Example 4. A 3.7 m high by 4.5 m wide by 3 m long drift round is blasted in quartzite where the VRT is 49°C. Quartzite has a 2700 kg/m3 density and a 0.8 kJ/(kg · K) specific heat. By the time the rock is hoisted to the surface 4 h later, it has cooled to 32°C. What is the heat load imposed on the drift and shaft? (7) Solution: Heat = (3.7 m x 4.5 m x3 m x 2700 kg/m3)[0.8 kJ/(kg·K)] x (49 - 32°C) = 1.8342 x 106 kJ Heat load = 1.8342 x 106 kJ = 127 kW 14 400 s Heat from Other Sources Heat produced by oxidation oftimber and sulfide minerals can be locally significant and even cause mine fires. Fortunately, timber is seldom used for ground support in modern mines. Heat from blast- ing can also be appreciable. The typical heat potential in various explosives is similar to that of 60% dynamite, about 4200 kJ/kg. This heat is usually swept out of the mine between shifts and thus is not tallied in heat load projections. Body metabolism is only a con- cern in refuge chambers and is rarely (if ever) included in heat load projections. Although these heat sources are usually neglected, the 2019 ASHRAE Handbook- - HVAC Applications (SI) ventilation engineer must remain vigilant for cases where local effects might be significant. Summation of Mine Heat Loads Mine cooling requirements should be estimated after mining methods, work sites, production rates, and equipment are specified, and heat sources identified. The time frame, during which the ven- tilation and cooling systems must provide an acceptable work envi- ronment, is normally 10 years, but can vary. Total heat for a mine or mine section is the summation of all TIH and TDH sources. It helps to plot heat sources on a schematic. The heat load from the surface to the entrance of the stope is assessed first, starting with TIH sources because they influence TDH sources. Shaft heat loads, autocompression, and drift heat loads are added to the air en route to stopes. The process should take only one iteration to find a stope entering temperature. Stope heat load is calculated by assuming that the wet bulb leaving the stope equals the design reject temperature. The air temperature entering the stope is estimated, and heat load equations are used to calculate the exit temperature. If this exit temperature exceeds the reject temperature, a lower stope entering temperature is assumed and a new exit temperature is calculated. The process is repeated with new stope entering temperatures until the calculated stope exit temperature equals the design reject temperature. If the entering stope temperature calculated from the surface is greater than the entering stope temperature calculated from the re- ject temperature, higher airflow or air conditioning will be needed. Psychrometrics can determine the size of the airflow increase or cooling required. 3. HEAT EXCHANGERS Underground heat exchangers can be water-to-refrigerant, air-to- refrigerant, water-to-water, air-to-water, or air-to-air. Brine can be used instead of water where freezing might occur. Heat exchangers can be direct (e.g., spray chambers) or indirect (e.g., conductive heat transfer through tubes or plates). See Chapters 19 to 24, 26 to 30, 37 to 40, and 42 to 48 ofthe 2016 ASHRAE Handbook-HVAC Systems and Equipment for general guidelines when designing large cooling plants for mine duty. Shell-and-Tube and Plate Heat Exchangers Shell-and-tube heat exchangers are the mainstay of refrigeration machines used in mines. Machines in the 700 to 1400 kW range may use either direct expansion (DX) or flooded evaporators. In both cases, the working fluid (refrigerant or water) is circulated through the tubes. South African mines often use plate-and-frame evaporators in large surface chilled-water plants (van der Walt and van Rensburg 1988). These machines can cool water to within a degree of freezing without danger of rupture. In contrast, shell-and-tube evaporators should not be expected to chill water below 3°C. Manufacturers must be consulted. Shell-and-tube water-to-water heat exchangers have been used in mine cooling systems to avoid pumping return water against high heads (the U-tube effect). Chilled water from the surface is sent down to the high-pressure (tube) side of the exchanger. Water on the low-pressure side operates district chiller systems or spot coolers. The shell-and-tube water-to-water heat method is not very popular, perhaps because it requires high-pressure supply and return piping. The second law of thermodynamics limits the approach temperature of the outlet high-pressure water to the inlet low-pressure water temperature. This tends to limit heat removal in deep mines that would require at least three heat exchanger sta- tions, in series, in the shaft. | {}
78603011-bd47-42b9-af00-22ff0afdcc24 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Mine Air Conditioning and Ventilation 30.5 Cooling Coils Cooling coils can be DX or chilled-water coils. DX coils are used with spot coolers and typically range from 50 to 200 kW. Some modern spot coolers use dual coils in parallel for compactness. Chilled-water coils, used in district chiller systems, are also used in a wide range of sizes. Air-side fouling is the main operational problem with cooling coils in mines. Coils with fin spacing tighter than 4.2 mm are not recommended. Water-side fouling is minimal if the water is of fair quality, the circuit is closed, and a corrosion inhibitor is added to the circuit. Small Spray Chambers Small spray chambers can be used as an alternative to cooling coils. Heat transfer is direct, air-to-water. Spray chamber mainte- nance is minimal, and the amount of water sprayed is typically one- half to one-third that required for a cooling coil at the same duty. Some washing effect also occurs in the chamber. Spray chambers are open systems that dump water into a ditch or collection pond after spraying. This water drains to the dewatering system or is pumped back to the chiller plant. Small spray chambers are still popular for small duties in mines that chill service water, but the pumping system must be able to handle the increased service water requirement. Cooling Towers When heat loads are large, the full capacity of a mine's heat removal system will probably be needed. A key component of the heat removal system is exhaust air. The ventilation engineer for a deep, hot mine must be proficient at designing underground cooling towers for condenser heat rejection, and spray chambers for cooling airflows. Rather than using the standard HVAC&R method of assessing cooling tower performance, as described in Chapter 40 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment, mining engi- neers use the South African factor-of-merit method, developed in the 1970s for designing direct-contact heat exchangers (Bluhm 1981; Burrows 1982; Whillier 1977). This method requires a psy- chrometric program and the following equations: �=h-(cpm)(W)(t) Note that t is either the wet-bulb temperature for air, or the water temperature, depending on whether Eai or Ewi is calculated. 9 = (Mw)(cpw)(twi-two) q= (Ma)(Sao - Eai) twi two nw = twi tai (8) (Mw)(cpw)(twi-tai) R= (Ma)(�wi-�ai) F N= ) (1 - F)(R 0.4 (9) -N(1 -R) (1 - e ) nw = (for counterflow towers) -N(1 - R) (1 - Re ) where a = air Cpw = specific heat of water at constant pressure, 4.1868 kJ/(kg· K) (10) (11) (12) (13) (14) F = factor of merit, roughly equivalent to UA factor in conductive heat transfer, dimensionless; ranges from 0 (no heat transfer) to 1 (as much as heat transfer as allowed by second law takes place) h = enthalpy of moist air, kJ/kg i = inlet M = mass flow rate, water or air, kg/s N = number of transfer units, an intermediate factor for calculating water efficiency nw = water efficiency, dimensionless 0 = outlet 9 = heat rate to be transferred in chamber, W R = tower capacity factor, dimensionless; ratio of heat capacity of water to heat capacity of air under limits of second law t = temperature, °C W = humidity ratio of moist air, kg water per kg air w = water � = energy of air, kJ/kg; total enthalpy minus enthalpy of liquid water evaporated into air (approximated by cpwWt, where tis wet bulb); dependent only on wet bulb and barometric pressure Designing an underground cooling tower requires the exhaust air mass flowrate Ma, the wet- and dry-bulb temperatures available at the tower, and the ambient barometric pressure. A psychrometric program is needed to calculate enthalpy, density, humidity ratio, and specific volume from the wet bulb, dry bulb, and barometric pres- sure. Tower airflow is taken from measurements or from the mine plan. The temperature, if not measurable (e.g., in a new mine), can be assumed to approach the reject temperature. Experience shows that air usually enters exhaust at about 27 to 28°C wb. Designing a cooling tower involves the following steps: 1. Calculate heat rejection rate in the tower (evaporator duty x condenser heat rejection factor, typically between 1.2 and 1.4). Discuss with the manufacturer. 2. Select condenser water flow and use Equation (9) to calculate Atw in the tower and machine condensers. 3. Specify cooling tower diameter and tower air velocity. 4. Calculate Mw/Ma. 5. Calculate heat rejection rate per m3/s in tower. 6. Calculate air enthalpy h and use Equation (8) to calculate Eai- 7. Select a factor of merit for tower using Table 3. 8. Estimate tower capacity factor R (e.g., R = 0.5). Using R = 1 in Equation (14) will result in division by zero. Skip to Step 10 if R = 1, and use the value of F for nw. 9. Use Equation (13) to calculate N. 10. Use Equation (14) to calculate water efficiency nw. 11. Use Equation (11) to calculate inlet water temperature twi⌀ 12. Use Equation (8) to calculate Ewi, the energy of air at inlet water temperature twi. 13. Use Equation (12) to calculate a new tower capacity factor R. 14. Compare the R calculated in Step 13 with the R estimated in Step 8. If different by more than 1%, return to Step 8 and re- estimate R. Repeat Steps 9 to 14 until the calculated Ris within 1% of the estimated R. 15. Calculate air and water temperatures leaving the tower and the evaporation rate. Keep the following empirical design criteria in mind during Steps 1 to 5: Inc. ASHRAE, 2019 user. single for Licensed · Realistic Atw in tower is 6.6 to 8.8 K · Realistic water loading in tower is 4 to 12 L/s per square metre · Optimum water velocity in machine condenser tubes (0.015 to 0.066 m/s, per manufacturer' s recommendations) is based on tub- ing material and water quality · Realistic maximum air velocity in tower is 8 m/s · Realistic ratios of the mass flows of water to air Mw/Ma range from 0.5 to 2.5 · A realistic heat rejection rate in tower is 20 to 40 kW per L/s | {}
d35d9d72-5451-4092-b213-dcb5a07ae450 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 30.6 2019 ASHRAE Handbook- - HVAC Applications (SI) Table 3 Factors of Merit ¦ ¦ Factor of ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ Merit Range ¦ Source ¦ ¦ Vertical counterflow, open, unpacked ¦ 0.50 to 0.70 ¦ Hemp 1982 ¦ ¦ Horizontal cross-flow ¦ ¦ ¦ ¦ Single-stage ¦ 0.40 to 0.55 ¦ Hemp 1982 ¦ ¦ Two-stage ¦ 0.57 to 0.72 ¦ Marks 1988 ¦ ¦ Three-stage ¦ 0.69 to 0.81 ¦ Marks 1988 ¦ ¦ Four-stage ¦ 0.76 to 0.87 ¦ Marks 1988 ¦ ¦ Commercial packed cooling ¦ ¦ ¦ ¦ Counterflow tower ¦ 0.68 to 0.78 ¦ Patterson 1992 ¦ ¦ Cross-flow tower ¦ 0.55 to 0.65 ¦ Patterson 1992 ¦ Values outside these design parameters are sometimes used (especially when plant duty is increased at a future date), but the penalty paid is a higher condensing temperature and lower COP. Once 9, F, Ma , tai, and Mw are specified, only one twi, two, and tao will balance all equations. Example 5. Design a cooling tower for a 3500 kW refrigeration plant planned for a deep, hot mine. Exhaust airflow for heat rejection is 118 m3/s at 28°C saturated. Barometric pressure is 104.983 kPa (300 m below sea level). What size cooling tower is needed, how much condenser cooling water is required, what are the inlet and outlet air and water temperatures, and how much makeup water is needed? Solution: Step 1. For a refrigeration plant to produce 3500 kW of cooling, it must reject about 3500 kW x 1.25 condenser heat rejection factor = 4375 kW. Step 2. Select a condenser water flow. For this example, start with 0.018 L/s per kilowatt rejected. The condenser flow is thus 78.75 L/s, or 78.75 kg/s at 1 kg/L. The change in water temperature is calculated from Equation (9): 4375 kW Atw = = 13.3 K (78.75 kg/s)[4.1868 kJ/(kg·K)] That exceeds the realistic 6.6 to 8.8 K Atw, so arbitrarily increase the water flow to 125 L/s and recalculate △tw. In practice, selecting the con- denser water flow is anything but arbitrary. Generally, the higher the flow, the better, but higher flows require larger condensers to keep tube velocity within design limits, larger cooling towers with more nozzles, and significantly larger pumps. Actual condenser water flow is a compro- mise between machine and tower performance, capital cost, and overall plant COP (operating cost). At 125 L/s for this example, Atw = 8.4 K, which is acceptable. Step 3. Specify cooling tower diameter by using a midrange value to 8 L/s per m2. 125 L/s (�/4)d2 = d= 4.46 m 업 4.5 m 8 L/(s·m ) 3 118 m /s Air velocity = = 7.42 m/s (< 8 m/s; acceptable) (元/4)(4.52) Step 4. Calculate Mw/Ma. Mw = (125 L/s)(1 kg/L) = 125 kgw/s The specific volume for 28°C saturated inlet air at 104.983 kPa is 0.86 m3/kga. Ma is therefore 3 118 m /s Ma = = 137 kga/s 3 /kga 0.86 m 125 Mw/Ma = = 0.9142 (0.5 < Mw/Ma < 2.5; acceptable) 137 Step 5. The heat rejection rate in the tower is 4375 kW = 37 kW per m3/s 3 118 m /s This rate is approaching the upper acceptable limit. Consideration should be given to routing more air through the tower if possible. All design criteria have now been met. Step 6. The enthalpy of air hai at 28°C saturated and 104.983 kPa is 109 kJ/kg. Eai = 109 - (4.1868)(0.037)(28) = 104.66 kJ/kg. Step 7. Select a factor of merit for the tower. From Table 3, an open, unpacked, vertical counterflow cooling tower can conservatively be expected to have a 0.55 factor of merit. If the tower is well designed and actually has a higher factor, the tower will return cooler water to the plant and COP will increase. Step 8. Estimate R = 0.5 (first pass). Step 9. Calculate N from Equation (13): 0.55 N= = 1.613 (1 - 0.55)(0.50.4 ) Step 10. Calculate nw from Equation (14): 1 -e -1.613(1-0.5) nw = 0.713 1 - 0.5e -1.613(1-0.5) from Equation (11) (after manipulation, and Step 11. Calculate twi assuming that twi - two = △tw): At. 8.3 W twi 0.713 = + tai = + 28 = 39.64°C n W Step 12. Ewi at 39.64°C and 104.983 kPa = 180.75 - (4.1868)(0.047) (39.64) = 172.95 kJ/kg. Step 13. Calculate the new R using Equation (12): (125)(4.1868)(39.64-28) R = = 0.651 (137)(172.95- 104.66) Step 14. The new R is higher than the 0.5 R estimated in Step 8. Return to Step 8 and iterate until the R calculated in Step 13 equals the R projected in Step 8. This occurs at R = 0.662. Step 15. All other values can now be calculated. Per Step 11, twi = 39.64°C two = 39.64 - 8.3 = 31.34°C 4375 kW Eao = Eai + = 104.66 + 31.93 (137 kg/s) = 136.59 kJ/kg tao = 34.7°C (via psychrometric iteration) The water evaporated in the tower is the difference in humidity ratios △W x the mass flow of dry air. From psychrometric equations, W28°C = 0.0237 kgw/kga and W34.7°C = 0.0347 kgw/kga. Inc. ASHRAE, 2019 user. single for Licensed Evaporation rate = (137 kgg/s)(0.0347 - 0.0237 kgw/kga) = 1.5 L/s Total makeup water depends on evaporation rate, water carry- over (if any), and blowdown used to control dissolved solids in the condenser circuit. Leakages and carryover can be deducted from the blowdown. Makeup water is usually planned at 1 to 3% of the con- denser water flow, depending on the quality of the makeup water, allowable cycles of concentration of dissolved solids, and water treatment plan. Vertical unpacked cooling towers in mines often use clog- resistant full-cone nozzles circling the top of the tower, at least 12 m above the pond. South African mines tend to use ham-type sprayers. | {}
46b5d8e5-28f1-4555-b066-a8ca2e29a6f7 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Mine Air Conditioning and Ventilation 30.7 Nozzle pressure of 200 kPa (gage) is typically specified: lower water pressures do not generate the fine water droplets preferred for heat transfer, and higher pressures increase pumping costs. Higher pressures can also impinge water drops into side walls, where the water runs in sheets down the sides. This drastically reduces the sur- face area of the water flow, which reduces heat transfer. Rings cir- cling the tower are recommended to kick water running down the sides back into the airstream. Unpacked towers do not have as high a factor of merit as towers with film packing or splash bars, but they are virtually maintenance free and have low resistance to airflow. Figure 1 shows a typical underground vertical counterflow cooling tower. After a cooling tower begins operation, the actual factor of merit should be determined. This is accomplished by measuring air and water flow rates and temperatures at the tower inlet and outlet, and then working the cooling tower equations in reverse. The actual factor of merit can be used to determine performance at other inlet conditions. This applies to mine, industrial, and commercial cooling towers. Large Spray Chambers (Bulk Air Coolers) The procedure for designing spray coolers is the same as for cooling towers, with the following minor changes: q = Mwcpw(two - twi) q = Ma(�ai - �ao) -R(1 -Ⓧ) 1 - e nw R where X = eN for horizontal cross-flow chambers. (15) A perfect counterflow tower has a factor of merit of 1.0, but the factor of merit for a single cross-flow chamber (see Chapter 40 in the 2016 ASHRAE Handbook-HVAC Systems and Equipment) cannot exceed 0.63 (Bluhm 1981). Two-stage cross-flow chambers are most often specified. Counterflow performance is approxi- mated, and the counterflow equation for water efficiency can be used. Three-stage chambers can be designed when water flow must (16) (17) ![image](/image/placeholder) NOZZLES (TYPICAL) CATWALK PLAN VIEW AIRDOOR AIRFLOW MAINTENANCE ACCESS WITH SCREENS AND LADDERS WATER RINGS E 15 HOT WATER FROM PLANT AIRFLOW POND BOX COOL WATER TO PLANT SUCTION SIDE VIEW Fig. 1 Underground Open Counterflow Cooling Tower be limited to control pumping costs. Four-stage chambers are rarely cost effective in mining applications. Spray chambers often use vee-jet nozzles at 200 kPa (gage), placed uniformly along the chamber length and designed to cover the cross section evenly. Sprays should just reach the back of the chamber. Mist eliminators are usually installed at the chamber exit. Whereas cooling towers need makeup water to replace evaporated water, bulk air coolers gain water through condensation. This water can be sent to the condenser side as makeup. Figure 2 shows a typ- ical two-stage horizontal cross-flow spray chamber. 4. MINE-COOLING TECHNIQUES A mine-cooling system typically sends air, water, or ice into the mine at a low enthalpy state and removes it at a higher one. In hot mines, heat is typically rejected to water being pumped to the sur- face, and to exhaust air being drawn from the mine. There are many combinations and variations on how this is accomplished. Economics and site-specific conditions determine the optimum methods. Increasing Airflows This alternative should be considered first: it is usually less expensive to moderately increase airflows than to install refrigera- tion if the mine is above the critical ventilation depth. Increasing airflows also helps remove diesel fumes, which is increasingly important for modern mining. However, in deep (usually older) mines with small cross-sectional airways, airflow increases may not be practical because of the cube relationship between fan power and airflow increase through a given resistance. Circuit resistance reduc- tion via new airways or stripping existing airways is very expensive. Chilling Service Water When a mine requires additional heat removal, and airflow increases are not practical, consider chilling the service water. Most mining methods require that water be sprayed on rock immediately after blasting to control dust; chilled water can intercept rock heat before the heat escapes into the air. This is a very flexible method of heat removal because it is applied when and where it is needed the most. After blasted rock is removed, the water is turned off and routed elsewhere. Main water lines should be insulated when ser- vice water is chilled. Fig. 2 Two-Stage Horizontal Spray Chamber ![image](/image/placeholder) FAN BULKHEAD (3) FANS, 56 kW EACH AIRFLOW DEMISTER PANEL DAM DOOR SPRAY NOZZLES SPRAY (TYPICAL) PATTERN SUCTION FIRST-STAGE BOX WATER SPRAYS DAM POND SECOND-STAGE DAM WATER SPRAYS SECOND- POND STAGE 5800 kW DUTY PUMP INSTALLED AT HOMESTAKE GOLD MINE CHILLED WATER 95 L/s SUCTION FROM PLANT BOX 70 m3/s WARM WATER 30 m LONG by 5.5 m WIDE by 4.5 m HIGH TO PLANT Inc. ASHRAE, 2019 user. single for Licensed | {}
c47f18f2-7eaa-4407-a3b9-188365803fa4 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 30.8 2019 ASHRAE Handbook- -HVAC Applications (SI) Water is usually chilled in surface plants. A single-pass system is used if regional water supplies are plentiful. If scarce, water is pumped to the surface, recooled, and returned underground. Recy- cling can ease discharge permit requirements and thus save on treat- ment costs. Some mines have zero discharge permits. Regions with low winter temperatures and low relative humidities during summer have a natural cooling capacity that is adaptable to water chilling on the surface. Warm mine water is precooled in an evaporative cooling tower before being sent to the refrigeration plant. Reducing Water Pressure and Energy Recovery Systems All mines send water underground for drilling, cleaning, sup- pressing dust, and wetting broken rock. Hot mines using extensive cooling systems often send large volumes of water underground solely for air conditioning. The pressure of descending water must be broken periodically. The most common methods are the open cascade system and pressure-reducing valves. Turbines can also break the pressure and recover a significant portion of the potential energy that would otherwise be lost. Two types of turbines are suit- able for mine use: the Pelton wheel, which is most often used, and a centrifugal pump specially designed to run in reverse. The Pelton wheel rotor is shaped like the spokes of a wheel, with cups attached to the ends of the spokes. One or two nozzles shoot high-pressure water onto the cups, spinning the wheel. It is at least 80% efficient over a range of flows, simply constructed, and readily controlled. A wide operating range is important because water demand fluctuates. A turbine can turn either a generator or pump. Turning a generator is preferred because it separates service and cooling water from the mine dewatering system so that downtime in one system is less likely to disrupt the other. Besides providing power to help return service water to the surface, turbines have another advantage: unrecovered potential energy is con- verted to heat at a rate of 1 kJ/kg per 102 m of depth. If, for example, a 1830 m deep mine uses 63 L/s for air conditioning without energy recovery, the water will heat by 4.28 K. If 80% efficient turbines are used, the water temperature rise is about 0.2 x 4.28 = 0.856 K. The refrigerating effect lost is only 225 instead of 1129 kW. Other energy recovery devices include hydrotransformers (large pistons transfer force from the high-pressure side to the lower- pressure side), and three-pipe feeder systems that deliver chilled water on one side while pumping out crushed ore on the other. These concepts have been tested in Europe and South Africa. Bulk Cooling Versus Spot Cooling Inc. ASHRAE, 2019 user. single for Licensed Engineers must balance bulk cooling and spot cooling. Bulk cooling using a centrally located plant cools the entire mine, or a large section of it. Benefits are lower cost per kilowatt installed, generally better maintenance, and lower temperatures in non-stop- ing areas such as haul drifts. Bulk cooling intake air is often done at warm-climate mines to provide winter-like or better conditions year round. Air is cooled in large direct-contact spray chambers adjacent to the shaft and then injected into the shaft below the main landing. Cooling the entire mine draws more heat from surrounding wall rock, so a larger system must be designed to ensure proper stope cooling (i.e., positional efficiency suffers). When a multilevel mine is bulk cooled, cooling may be wasted on upper levels where heat load is low. Spot cooling provides adequate temperature control in explora- tion and development headings, and in stopes on the fringes of mining activity. Total heat load is lower, but cost per kilowatt is higher, and temperatures in some areas might exceed design limits. Combination (Integrated) Surface Systems Combination (or integrated) systems can cool both air and water. Surface plants devote a higher fraction of cooling capacity to bulk cool intake air in the summer. In winter, a higher fraction is used to ![image](/image/placeholder) PRECOOLING CONDENSER TOWER COOLING TOWER BULK REFRIGERATION AIR PLANT CHILLED- COOLER WATER COND RESERVOIR EVAP SURFACE COOLED-AIR CHILLED-WATER DOWN SHAFT DOWN SHAFT PUMP WATER SHAFT PELTON TURBINE MINE PUMP STATION THREE-PIPE CASCADING TO WORK AREAS SERVICE WATER SUPPLY SYSTEM TO WORK AREAS MINE PUMP STATION Fig. 3 Integrated Cooling System chill service or air-conditioning water. Water is delivered under- ground via open or closed systems, with or without energy recovery. Figure 3 shows components of an integrated mine cooling system. Underground Refrigeration Larger refrigeration machines also can be located underground. They usually produce chilled water for cooling air in spray cham- bers, and heat is rejected to exhaust air via cooling towers. Another method is to operate district cooling systems, using a chiller to pro- duce water for a closed network of cooling coils installed in parallel. These coils can be used in auxiliary systems at individual work areas, or installed in a bank. As with spot coolers, coils should be installed upwind ofblasting to limit air-side fouling. Condenser heat from district chiller systems is rejected either to service water or to the mine-dewatering system. Ice Plants For ultradeep mines (>3660 m), or those at the performance limits of existing water and airflow heat rejection systems, ice cooling should be considered. In going from 0 to 32°C before being pumped out of the mine, cooling water starting as ice can remove about 4.5 times the heat as the same mass flow of chilled water in going from 7 to 32°C: Heat removal (kJ/kg) = Sensible + Latent Heat removal of chilled water = [4.1868 kJ/(kg· K)](32 - 7) = 105 kJ/kg Heat removal of ice = [4.1868 kJ/(kg · K)](32 - 0) + 335 kJ/kg = 469 kJ/kg Heat removal factor increase ofice over water = 469/105 = 4.5 South African mines have been at the forefront in this application (Sheer et al. 2001). Both chunk and slurry delivery methods send ice to underground chambers, where it mixes with warm water returning from the mining area. The cold mixed water is then sent back to the mining area. Several successful systems have been installed. Cost has dropped as technology improves; the overall COP ofice systems for ultradeep mines is now competitive with traditional cooling methods. | {}
92387d75-ac46-41e4-ad79-d37238d9c7a2 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Mine Air Conditioning and Ventilation 30.9 Thermal Storage This Canadian innovation uses near-surface ice stopes or rock rubble to effectively and inexpensively heat intake air in the winter and cool it in the summer (Stachulak 1989). Controlled Recirculation This technique, used in conjunction with bulk air cooling, can reduce ventilation and air-conditioning requirements in older, deep mines, especially heavily mechanized ones (Tien 1999). Besides increasing air velocities in work areas without drawing more surface air through a high-resistance circuit, controlled recirculation re- duces the heat load caused by autocompression. Using Equation (1), for every 47 m3/s at standard density brought from the surface, the lost cooling capacity per 300 m of descent is 1 kJ/kg Heat Load = (47 m3/s)(1.2 kg/m3) (300 m) 102 m = 166 kW lost per 47 m3/s, per 300 m Controlled recirculation systems must be designed very care- fully, with stringent monitoring and control safeguards. Operator Cabs and Cooling Vests Mechanization can add significant heat, especially in confined auxiliary-ventilated spaces. Most noncoal mines have converted to diesel equipment, although some use electric loaders and trucks. Coal mines are also mechanizing, but more slowly. The biggest problem with diesel engine heat is related to the greatest advantage of these vehicles: mobility. Heat and emissions from a diesel vehicle in a confined area can tax almost any ventilation system. Increas- ingly, cabs are being specified for large diesel vehicles. Cabs come equipped with window-type air conditioners and HEPA filters to capture diesel particulate and dust. After the diesel vehicle has left the heading, the mine ventilation and cooling system can provide an acceptable environment for other personnel. Cabs are expensive; however, because a loader often visits multiple headings in a week, the cost of a cab is much less than maintaining the design reject wet- bulb temperature in all headings at all times. Cooling vests are not popular in mining. They are bulky, reduce mobility, and are time-consuming to prepare and use. Vests have limited application for mechanics, electricians, pipe-fitters, and others who must enter hot areas to set up ventilation and cooling. Vests using blue-ice packs or dry ice last two to three hours; those using compressed-air venturi-type coolers require an umbilical cord. Other Methods Other methods being developed include the air cycle (air, com- pressed on the surface and sent underground to a turbine, turns a generator and exits at -40°C), and the ammonia cycle (sending down liquid ammonia, evaporating it, and sending the vapor back to surface condensers). These methods may be best suited to ultradeep mines where other cooling methods are already fully developed. Transferring heat from current stopes to wall rock or rock rubble in previously worked-out stopes (the only method that does not remove heat from the mine) has also been considered. Refrigeration equipment would have to operate at a high condensing temperature to produce water hot enough to transfer heat to worked-out stopes. 5. SELECTING A MINE-COOLING METHOD After mine-cooling and ventilation requirements have been pro- jected, the designer must analyze and select the best method(s) for meeting those requirements. Cost-benefit analysis is the most widely used, but hardware reliability, dependency on outside fac- tors, flexibility, safety, and technological level are just as important. Some factors to consider include the following: · Seasonal ambient conditions. Warm-climate mines tend to bulk- cool air on the surface in industrial direct-contact spray chambers located close to the intake shaft. · Orebody and mining methods. The more massive the orebody, the more ideal bulk cooling becomes. When stopes are scattered and continuously advanced into new areas, district or spot cooling might be better. · Mining rate. This is critical: heat removal is energy, but not nec- essarily power, related. A fast mining rate prompts a high instan- taneous heat load (kilowatts), but less heat energy (kilojoules) per tonne of production. This is because wall rock is covered by fill or isolated before its total heat energy has escaped into the airstream. The kilojoules per tonne of production incurs the air-conditioning costs. Leave as much heat in the wall rock as possible. · Size and condition of major airways. In older mines, small air- ways often limit airflow increases. This may prompt the need for air conditioning sooner than it normally would have been necessary. · Heat sources. The contribution of TIH and TDH sources to the total can help determine the balance of passive to active thermal environmental controls, the ratio of airflow to air conditioning, and whether cabs should be specified. · Cost of power, water, labor, and supplies. Knowing these costs is critical for assessing optimum capital expenditure to control operating costs. For example, if power cost is high, spending extra for a higher-COP system may be warranted. · Governmental regulations. Heat stress standards can influence the size of the system. Other safety issues may constrain design, such as not using combustible pipe insulation or ammonia machines underground. Basic cooling alternatives for specific cases are summarized in Table 4. Airflows are described as limited, medium, or large. One way to express airflow for a given mine is the ratio of tonnes of air- flow per tonne of ore. Limited airflow is defined as less than 8 tonnes of air per tonne of ore, medium airflow is 8 to 16 tonnes per tonne, and large airflow is over 16 tonnes per tonne. These ranges are based on an unpublished study of approxi- mately 100 mines of all types, worldwide. The ranges discussed are for heat removal only. Additional airflow for methane or radon removal must be addressed separately. 6. MECHANICAL REFRIGERA TION PLANTS Surface Plants Centrifugal or helical rotary screw machines are typically used in surface plants to chill water or bulk-cool air. Banks of machines are usually installed in parallel: plant design must accommodate one machine being down at any given time for maintenance while others operate. Shell-and-tube heat exchangers are standard, although plate-and-frame are used if water close to the freezing point is spec- ified. The most common refrigerant for positive-displacement com- pression is HCFC-22. Ammonia is also commonly used in surface plants. Absorption machines can be considered if external waste heat is available. Underground Plants Large underground plants do the same work as surface plants, but are closer to work areas. Better positional efficiency and percent utilization are the advantages. Whereas surface plants use atmo- spheric air for heat rejection, underground plants use mine exhaust air, which raises natural ventilation pressure and aids circuit fans. Inc. ASHRAE, 2019 user. single for Licensed | {}
0201052e-0a81-49df-814c-30782248b7d0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 30.10 Table 4 Basic Cooling Alternatives ¦ ¦ Warm Climate ¦ Cool/Cold Climate ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Massive orebody (deep) ¦ Large or medium airflow Chill service water Bulk-cool air on surface Bulk-cool air underground ¦ Medium airflow Chill service water Bulk-cool air underground Thermal storage ¦ ¦ Massive orebody (shallow) ¦ Large airflow Bulk-cool air on surface Chill service water Shell and tube ¦ Large or medium airflow Chill service water on surface Shell and tube ¦ ¦ Scattered orebody (multilevel) ¦ Large airflow if not too deep Chill service water Bulk-cool air on surface District chiller systems Spot coolers/spray chambers ¦ Large or medium airflow Chill service water District chiller systems Thermal storage ¦ ¦ Ultradeep orebody (massive and/or multilevel) ¦ Limited airflow Chill service water District chiller systems Ice cooling Controlled recirculation ¦ Limited airflow Chill service water District chiller systems Ice cooling Controlled recirculation ¦ ¦ Small orebody Porous rock ¦ Bulk-cool air on surface Chill service water District chiller systems Spot coolers District chiller systems Spot coolers ¦ District chiller systems Chill service water Spot coolers District chiller systems Spot coolers ¦ Components for underground machines must be disassembled for transport down the shaft. The main disadvantage of underground refrigeration is that heat rejection is limited by the amount of available exhaust air. Exca- vating underground refrigeration rooms and spray chambers is more costly than erecting prefabricated surface buildings. Mainte- nance is also more difficult because of shaft logistics. Power is more difficult to supply to an underground facility, and subject to more disruptions. Spot Coolers Spot coolers with 50 to 350 kW capacity allow driving long development headings, or cooling exploration sites before installing primary ventilation and cooling equipment. Development headings can be advanced more rapidly and under more comfortable condi- tions. Condenser heat is most often removed by service water, although some air-to-air condensers are used. Spot coolers use reciprocating, scroll, or small screw compres- sors. Hermetic scroll compressors are becoming more popular because they handle liquid slugging better than reciprocating com- pressors and are less expensive. Spot coolers use direct exchange (DX) air-cooling coils. The packaged unit includes a fan, which draws air through the coil (or coils, in a dual-coil unit) and then blows it through duct to the heading. Spot coolers must be compact and portable because they are moved often. The service water required is typically 0.02 L/s per kilowatt, but can be less ifthe water temperature is under 13°C, or more ifit is over 21 °C. A return drain pipe is recommended to prevent contact between hot discharge water (often over 38°C) and ambient air. Coils sometimes receive dusty air immediately after blasting; if so, coils must be washed at least every other day. Spot coolers are expensive, but often are the only choice for cooling exploration, development, and small-scale stoping on the fringes of mining activity. 2019 ASHRAE Handbook-HVAC Applications (SI) Maintenance Mines with extensive systems (e.g., a large chiller plant, or over 10 spot coolers) should employ a mechanic specializing in refriger- ation. Mines with over 7000 kW probably need a second mechanic. These persons should be factory trained and must be certified to handle refrigerants. Refrigeration specialists can be assisted period- ically or full time by apprentice mechanics. Another viable approach is a maintenance contract with the equipment manufacturer or sup- plier, or an independent HVAC&R shop. Some mines have a full- time person cleaning coils. A fouling factor (m2 · K/W) should be calculated from lab analy- sis of the condenser water, especially for district chillers using sump water. Planning a tube-cleaning regimen, either manual, acid circu- lation, or automatic with brushes and a flow reversal valve, is criti- cal. Underground condensers can become plugged within a couple of weeks without cleaning, depending on the fouling factor. Water treatment is needed to control scale, corrosion, and organisms in sur- face or underground plants with cooling towers. 7. MINE AIR HEATING Cold-climate mines typically heat intake air in the winter. In Canada, heating intake air can cost more than all other ventilation costs combined (Hall et al. 1989). However, without heat, water in the shaft will freeze, disrupting hoisting operations and damaging shaft support members, cables, and pipes. Very cold air and icy floors are safety and health hazards; heavy gloves and other protec- tive clothing required can make routine tasks difficult. Intake air is typically heated to just above the freezing point. Autocompression and shaft heat loads further temper the air as it downcasts into the mine. Steam coils operated by boilers burning wood, coal, fuel oil, or natural gas often served as shaft heaters in the past. Electric resistance heaters have also been used, but they are expensive to operate. Waste heat from compressor stations has also been used. When exhaust and intake shafts are located close together, a cir- culating glycol or heat pump system can be used to transfer heat from exhaust air to intake. For every kelvin of total heat (sensible plus latent) given up by warm saturated exhaust air, the same mass flow of cold intake air can be heated sensibly by 4 K. Either coils or a cooling tower extracts heat from exhaust air, and then coils trans- fer this heat to the intake air. Controlled recirculation (up to 25% of total airflow) can also be applied to heat intake air (Hall et al. 1989). The system is temporarily shut down during blasting. Some cold-climate mines isolate the primary production shaft from the ventilation circuit. A slight upcast flow of uncontaminated air maintains good conditions in the shaft for hoisting ore and moving personnel and supplies. The disadvantage of this method is that ventilation duties of the production shaft must be transferred to one or more expensive stand-alone intake airways. Natural gas and/or propane heaters are typically used at modern mines. Natural gas is preferred because it is less expensive and it burns more cleanly. Where natural gas is not available, propane must be trucked to the mine site. The same heater can burn either natural gas or propane; thus, propane can be used for back-up in case natural gas is cut off (mechanical conversion is required from gas to propane). Direct-fired heaters are usually preferred because the entire heat value of the fuel enters the intake airstream. If indi- rect heaters are used, roughly 15 to 25% of the heatis lost up the flue pipe. Two types ofnatural gas or propane heaters have been used to heat intake air: (1) a grid of burner bars installed in a housing at the intake shaft, sometimes with louvers to adjust the flow of intake air and to mix air from the heaters with outdoor air; and (2) a crop dryer type of burner. Temperature sensors installed downstream can modulate Inc. ASHRAE, 2019 user. single for Licensed | {}
dede4f9a-4120-4a1e-b939-de349736ad0b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Mine Air Conditioning and Ventilation 30.11 Table 5 Heating Values for Fuels ¦ Fuel ¦ Value ¦ Source ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Natural gas ¦ 37 250 kJ/m3 ¦ Kennedy 1996 ¦ ¦ Propane ¦ 25 000 kJ/L ¦ Kennedy 1996 ¦ ¦ Bituminous coal ¦ 28 600 to 33 500 kJ/kg ¦ Abbeon Cal 2001 ¦ ¦ Fuel oil ¦ 40 000 kJ/L ¦ Abbeon Cal 2001 ¦ ¦ Wood ¦ 4 350 000 to 9 000 000 kJ/m3 ¦ Abbeon Cal 2001 ¦ both heater types to ensure that no more heat is applied than neces- sary to bring the temperature of the mixed intake air to 1°C. Carbon monoxide sensors should also be installed downstream of the heaters. Experience at two mines in the western United States shows that the CO content of intake air heated by direct-fired burners can reach 10 to 20 mg/kg. Equation (18) is used to calculate the total heat required, assum- ing that the air has a low humidity ratio (which is the case for very cold air), and that no water is evaporated in the heater. Heating val- ues for different fuels are given in Table 5. Heat, kW = (Airflow, m3/s)(density, kg/m3) x [1 kJ/(kg·K)](△t, K) (18) where At = 1°C minus the intake air temperature. Example 6. A mine is located where the atmospheric air temperature can drop to -30°C for two or more weeks per year. Occasionally the tem- perature drops to -35°C. An intake shaft handles 190 m3/s, and the den- sity of air entering the shaft in winter is 1.12 kg/m3. What heating should be installed at the shaft intake to keep the shaft free of ice? Solution: Sizing heaters is usually based on average cold periods, not extreme cold snaps. Here, a direct-fired heater is sized to raise -30°C air to 1°C. When the temperature drops to -35°C for short periods, intake airflow should be temporarily reduced. Using Equation (18), Heat = (190)(1.12)(1)[1 - (-30)] = 6600 kW If natural gas is used, the volume required is 6600 kW = 0.18 m3/s = 638 m3/h 3 37 250 kJ/m If propane is used, the litres required are 6600 kW = 0.264 L/s = 950 L/h 25 000 kJ/L 8. MINE VENTILA TION Mine ventilation supplies air (oxygen) to underground facilities, and removes dangerous or harmful contaminants such as methane, radon, strata gases, dust, blasting fumes, and diesel emissions. Ven- tilation also removes heat and helps control humidity in hot mines. Planning a ventilation system consists of five basic steps: (1) deter- mining airflows; (2) planning the primary circuit; (3) specifying cir- cuit fans, ventilation controls, and their installation; (4) determining auxiliary system requirements; and (5) assessing health and safety aspects. Determining Airflows Mining operations generate differing types and amounts of con- taminants, and airflows dilute and remove these contaminants. The ventilation engineer must work closely with mine planning staff to understand where and how much production will take place, and what contaminants will be generated. The federal Mine Safety and Health Administration (MSHA 2013) regulates contaminant con- centrations to limits specified in the Federal Register, CFR 30. Controlling the most problematic contaminant normally keeps all others within their legal limits. For coal mines, contaminants of concern are typically methane and coal dust; for uranium mines, radioactive dust and radon progeny; for non-dieselized hard rock mines, usually silica dust and blasting fumes; for dieselized mines, typically diesel emissions. Design airflows for dieselized nonuranium metal mines range from 0.05 to 0.09 m3/s per diesel kilowatt, depending on the reference cited. With the current emphasis on controlling diesel emissions, planning should start at 0.06 m3/s per kilowatt. Total airflow is a summation of airflows for individual work areas, plus a leakage factor. Leakage is defined as airflow that does not ventilate any active work area or permanent site such as a pump room. A "tight" system minimizes leakage through well- constructed doors and seals, by minimizing the number of possible leakage paths, and by careful fan placement. Leakage can range from 10% of total airflow at a tight metal mine to 80% at some coal mines. The ratio of tonnes of air per tonnes of ore production is about 2 to 4 for block cave mines, 6 to 8 for nondieselized cut-and-fill metal mines, and 9 to 16 for dieselized metal mines. Gassy coal and ura- nium mines can have significantly higher ratios, depending on the methane or radon generation rate. Example 7. A new mechanized cut-and-fill gold mine is planned. Ore pro- duction is expected to be 1 088 400 tonnes per year. Intake air density is 1.12 kg/m3. What is the rough airflow required for ventilation? Solution: The airflow range is 9 to 16 tonnes of air per tonne of ore for dieselized metal mines. For a first-pass guess, assume an average 12.5 tonnes per tonne. The total mass of the air through the mine in a year is (1 088 400 tonnes ore per year) x (12.5 tonnes air per tonne ore) = 13 605 000 tonnes air per year (13 605 000 tonnes/yr)(1000 tonnes/kg) Airflow, m3/s = = 385 m3/s (1.12 kg/m )(31 536 000 s/yr) Ratios provide a good first guess. However, the ventilation engi- neer should derive the total airflow by listing all operations, estimat- ing leakages, and adding the specific airflows required to ventilate each operation (zero-based planning). As with reject temperature, the total airflow selected should be economically justifiable to man- agement. Airflow specification may change with time because of produc- tion, equipment, or mining method changes. Planning the Circuit With airflow specified and work sites plotted, the ventilation engineer must lay out the primary circuit. The three basic types of airways are intake, work area, and exhaust. Sizing airways is nor- mally based on keeping velocity within acceptable limits: if velocity is too low, the airway is oversized and thus costs more than necessary; if it is too high, pressure drop is too large and raises operating costs. Air velocity should not exceed 6 m/s in production shafts and haul drifts. Higher velocities can create dust problems and lead to employee discomfort. However, velocities in bare circu- lar concrete exhaust shafts can approach 25 m/s if necessary. Air velocity in vertical upcast exhaust shafts should avoid the 7 to 12 m/s range because water droplets become entrained into the air- stream and may form sheets, causing surging at the main fan. Resistance to airflow is calculated using Atkinson's (1854) and McPherson's (1993) equations: △H = R,PQ2 Inc. ASHRAE, 2019 user. single for Licensed where (19) AH = pressure drop, Pa | {}
ab0af505-95a6-4ebe-a453-4c44db5ffed3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 30.12 R turbulent resistance, m 4 P air density, kg/m3 0 airflow, m3/s (20) fLP R = 3 2A where t coefficient of friction, dimensionless L length, m P perimeter of opening, m A = area of opening, m2 For rectangular drifts, the f factor ranges from 0.0067 for a smooth, concrete-lined straight drift to 0.027 for an unlined, irreg- ular curved drift. For shafts, the f factor ranges from 0.004 for a smooth-sided borehole to over 0.15 for a heavily timbered rectan- gular shaft. See Hartman et al. (1997), McPherson (1993), and Tien (1999) for more precise airway resistance specification. Example 8. Mine plans call for 30 m3/s to be sent through 610 m of 3 m wide by 3 m high drift. The f factor from measurements of similar drifts is 0.020. The average temperature is 24°C wb and 27°C db. The barometric pressure is 95 kPa. What is the resistance of this drift, and what is the air pressure drop? Solution: Using psychrometric equations in Chapter 1 of the 2017 ASHRAE Handbook-Fundamentals, the density is 1.09 kg/m3. fLP (0.020)(610)(12) R = = 0.1004 m-4 3 3 2A 2(9) AH = R PQ2 = (0.1004)(1.09)(30)2 = 98.5 Pa, or 0.0985 kPa A mine ventilation circuit contains airways in series and in par- allel. The overall resistance (Hartman et al. 1997) is For series: RT= R1 + R2 + R3 + ... + Rn 1 1 1 1 1 For parallel: = + + + ... + RT N 1 ~ 2 R3 へ n R R R Example 9. If Airway #1 has a resistance of 0.1, Airway #2 has a resis- tance of 0.2, and Airway #3 has a resistance of 0.3, what is the resis- tance of these three branches in series and in parallel? Solution: Series: R = 0.1 + 0.2 + 0.3 = 0.6 m 4 Parallel: 1 1 1 1 + + V R V(0.1) V (0.2) ~ (0.3) R = 0.0192 m 4 1 1 1 1 + + VR V(0.1) V (0.2) V(0.3) R = 0.0192 (Pa・s2)/m6 Modern ventilation network computer analysis uses Kirchhoff' s laws to balance airflows: (1) the summation of airflows into a junc- tion equals the summation out, and (2) the summation of pressure drops around any enclosed mesh equals zero. Computer simulation allows quick analysis of a wide range of scenarios. Most programs use a balancing algorithm based on the work of Hardy Cross in the 1960s and 1970s. The program iterates as it converges on final balanced airflows. Fan curves or regulators can be inserted in almost any branch. 2019 ASHRAE Handbook- -HVAC Applications (SI) Regulators or section booster fans control airflow in branches. Without regulation, too little or too much airflow may occur; never- theless, circuits should be designed with as many free-split branches (branches without a fan or regulator) as possible to minimize overall resistance. Free-split branches are often located in circuit extremities. A mine should have more intakes than exhausts. This enhances safety, because miners have more escape paths, and because more paths bring in fresh air if a fire occurs in one of the intakes. Also, exhaust shafts can generally handle greater air velocities and hence larger quantities, so fewer exhaust shafts are needed. Metal mines often contain circuit booster fans. Underground boosters can create neutral points in the system where air short cir- cuits from intake to exhaust above the point, and recirculates from exhaust to intake below the point. Uncontrolled recirculation should be minimized. Exhausting primary circuits are commonly used in both metal and coal mines (intakes do not have airlocks). Under normal opera- tion, this produces a negative mine pressure gradient. If fans fail or are deactivated, barometric pressure in the mine rises, which temporarily helps keeps methane in coal mines from flowing away from gob (mining waste) areas (Kennedy 1996). Specifying Circuit Fans Primary fans are either centrifugal or axial. South African mines typically use large centrifugals, whereas most U.S. and Canadian mines use axials. Both types have advantages. Efficiency (up to 90%) is about the same with either type. Centrifugals are heavier duty, quieter, do not have a pronounced stall region, and can generate higher static pressures (over 7.5 kPa). Axials are more compact, and airflows can be easily adjusted by blade angle changes. Primary fans range from 75 to over 2600 kW each. Surface installations with mul- tiple fans are common for large airflows and for back-up operation when one fan is turned off for maintenance. Circuit fans can also be installed underground, especially in metal mines. (21) (22) The HVAC systems or components essential for plant operation should be designed with redundancy to ensure plant availability. Automatic switchover to the back-up system may be required in normally unoccupied areas. Where back-up systems are impractical, consider using temperature monitoring and alarming systems to initiate temporary corrective measures. Primary fans are specified while the circuit is designed. Engineers must often balance airway considerations (sizes and numbers) and fan specifications. Select a fan that will operate on an efficient part of its curve. Fan speed, quantity, pressure, and power are related in the fan laws equations, described in Chapter 21 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment. It is also important to anticipate future circuit changes as mining operations advance. The fan installation must be designed after primary fans are selected. Consequences of fan downtime must be carefully consid- ered, especially for coal mines, because methane concentrations can increase when circuit airflows decrease. Fans exhausting a mine are typically mounted horizontally near a vertical shaft or borehole. A 90° transition turns the air into the fan inlet. An isola- tion door is installed between the transition and fan. Coal mines require a blast door to dampen a shock wave caused by a possible methane or coal dust explosion. An evase, or diffuser, is attached to the fan outlet to recover part of the velocity pressure exiting the mine. Noise levels produced by HVAC system equipment both inside and outside plant spaces are an important consideration, as is the establishment of noise guidelines for air-conditioned areas and ven- tilated areas with continuous occupancies. Outdoor noise levels are established by the environmental noise pollution concerns of adja- cent areas. A silencer can be added if surface noise reduction is Inc. ASHRAE, 2019 user. single for Licensed | {}
b072312e-fbc4-40b2-959d-78f5a51de982 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Mine Air Conditioning and Ventilation 30.13 desired. Noise level can be managed by fan selection and acoustical treatment. Increasingly, variable-speed drives are used with electric motors to turn the fans. These drives provide soft start, and speeds from 50 to 100% of synchronous speed, and even to 110% for temporary emergency duty. The installation must be designed for accessibility and ease of maintenance. Determining Auxiliary System Requirements Auxiliary fan and duct systems deliver air into dead-end head- ings. These systems are generally not permitted in coal mines but are common in metal mines. A blowing system is most often used. A fan is set in a fresh air base at the start of a drift, and duct is installed as the drift advances. For drifts under 300 m, flexible brattice-cloth duct can be used. Longer drifts that require booster fans need rigid duct because duct gage pressure can drop below atmospheric. Rigid duct also offers less resistance than brattice- cloth duct, but it is about eight times as expensive. The air quantity needed at the face is determined by the equip- ment used and the rate at which blasting and diesel fumes must be removed. Ducts are sized for the air quantity needed and for space limitations in the drift. Fans are selected to provide the specified air- flow. In general, a single-stage axial fan can generate up to 2.5 kPa static pressure, which should deliver required airflow up to 760 m through properly sized duct. A larger duct or a two-stage axial fan is needed if distance is much longer. For very long drifts, booster fans are needed about every 760 m. An exhausting system is often used for drifts requiring quick ingress after blasting. Air flows to the face through the drift, cap- tures fumes, and is blown back to the circuit through duct. This keeps the drift clear of fumes. Disadvantages include the following: (1) the air picks up heat and humidity en route to the face, (2) rigid duct is required, and (3) the face is not swept by air as with a blow- ing system. A face overlap fan and duct can be installed. Chapter 21 of the 2017 ASHRAE Handbook-Fundamentals provides a friction chart for round duct. However, it is better to acquire the friction chart of the specific duct being considered from the supplier. Shock losses through couplings and bends must be tal- lied. One important consideration is leakage through couplings. This can be minimized by careful installation, keeping duct pressure under 2.5 kPa static pressure, and installing longer pieces of duct (up to 30 m for brattice cloth, or 6 m for rigid). Cassettes loaded with brattice-cloth duct are now used for drifts driven by rapidly advancing tunnel boring machines. Duct damage is common in mines. Mobile equipment and fly rock from blasting can punch holes in the duct. These factors can drastically reduce airflow. Take care to minimize damage, and to quickly repair or replace damaged pieces. Assessing Health and Safety Few aspects of underground mining have as direct an impact on health, safety, and morale as ventilation. No component of ventila- tion design should be undertaken without a rigorous review of health and safety aspects, including the risk of · Fire and explosion · Dangerous and toxic substances · Heat · Ventilation equipment usage For metal mines, fire is the most significant potential ventilation hazard. Fuel, heat, and oxygen are required for combustion; removing any of these components will prevent combustion. Fuel sources such as oil, diesel fuel, and blasting agents are kept in spe- cial areas designed to keep out ignition sources. Sprinkler or chem- ical suppression systems can be installed in these areas as well as in repair shops. Mobile equipment fires are a special concern for mod- ern mining: vehicles should be fitted with a dry chemical fire sup- pression system, triggered either automatically or by the operator. Electric substation and conveyor fires can be very dangerous. Engineers should anticipate various scenarios in ventilation cir- cuits. What are the fire risks in any given area? If a fire broke out in any location, how would circuits respond? W ould fire-induced nat- ural drafts change airflow quantities and directions? How would fire be detected, how would miners be notified, how would they escape, and how would the fire be fought? MSHA requires that refuge chambers be constructed if miners cannot be hoisted to the surface within 1 h of notification. The ventilation staff must work closely with the safety department and mine management in preplanning how to respond to different emergencies. Spontaneous combustion is a problem for both metal and coal mines. Fortunately, timber is now seldom used for ground support, although many older mines have worked-out areas that contain timber. Coal, being combustible, can be particularly troublesome. Circuits must be designed so that spontaneous combustion fires will not contaminate active workings. For coal mines, methane and coal dust explosions pose the great- est risk. Equipment must be rated "permissible, , , non-sparking. or Airways should be coated with rock dust to prevent a methane igni- tion from propagating. Methane is explosive in air from 5 to 15% concentration. Whenever methane reaches 0.25%, MSHA requires that changes be made to improve ventilation. At 0.5%, further steps must be taken, and no other work is permitted until the concentra- tion drops. At 1%, all personnel except those working on ventilation must be evacuated from the affected area. Ventilation is the first line of defense against toxic or asphyx- iating gases. These can be generated by blasting (CO, CO2, NH3, and NOx) and by diesel engines (CO, NOx, SO2, various hydro- carbon compounds, and soot). The rock itself can release CO2 and H2S. The relationship between heat stress and accident frequency has been clearly established in South African mines (Stewart 1982). W ork area temperatures should be kept under 29.5°C wb, especially where heavy physical work is performed. Ventilation and air-conditioning equipment may also pose health and safety risks. All fan inlets require screens. Fans should be equipped with vibration sensors that can deactivate the fan if neces- sary. Silencers may be needed if personnel work nearby. Refrigera- tion rooms must be well ventilated in case of a sudden refrigerant release. Duct, pipe insulation, and other substances such as foam for seals should be approved by MSHA in accordance with 30 CFR Part 7. Electrical systems must meet rigorous MSHA codes. REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. Abbeon Cal, Inc. 2001. Pocket ref, 2nd ed. T.J. Glover, ed. Sequoia Publishing, Littleton, CO. Atkinson, J.J. 1854. On the theory of the ventilation of mines. North of England Institute of Mining Engineering. Bluhm, S.J. 1981. Heat transfer characteristics of direct-contact crossflow heat exchangers. Master's thesis presented to the University of the Wit- watersrand. Republic of South Africa. Bossard, F. 1982. Sources ofheat entering mine air. Mine Ventilation Design Practices, 1st ed. Butte, MT. Burrows, J. 1982. Refrigeration- Theory and operation. Environmental engineering in South African mines, pp. 631-637. Mine Ventilation Society of South Africa. Duckworth, I., and P. Mousset-Jones. 1993. A detailed heat balance study of a deep level mechanized cut-and-fill stope. Proceedings of the 6th U.S. Mine Ventilation Symposium, 441-447. SME, Littleton, CO. pp. Inc. ASHRAE, 2019 user. single for Licensed | {}
a3f524f5-abf7-4f16-a500-ec4e5b478922 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 30.14 2019 ASHRAE Handbook- -HVAC Applications (SI) Fenton, J.L. 1972. Survey of underground mine heat sources. Master's thesis, Montana College of Mineral Science and Technology, Butte. Goch, D.C., and H.S. Patterson. 1940. The heat flow into tunnels. Journal of the Chemical, Metallurgical and Mining Society of South Africa 41. Hall, A.E., D.M. Mchaina, and S.G. Hardcastle. 1989. The use of controlled recirculation to reduce heating costs in Canada. Proceedings of the 4th International Mine Ventilation Congress. Australasia Institute ofMining and Metallurgy, Melbourne, Australia. Hall, C.J. 1981. Mine ventilation engineering. Society of Mining Engineers and Lucas-Guinn Co., Hoboken, NY. Hartman, H.L., J.M. Mutmansky, R. V. Ramami, and Y.J. Wang. 1997. Mine ventilation and air conditioning, 3rd ed. John Wiley & Sons, New York. Howes, M.J., and C.A. Nixon. 1997. Development of procedure for safe working in hot conditions. Proceedings of the 6th International Mine Ventilation Congress, pp. 191-197. SME, Littleton, CO. Kennedy, W.R. 1996. Practical mine ventilation. Intertec Publishing, Chicago. Marks, J.R. 1988. Computer-aided design of large underground direct- contact heat exchangers. Master's thesis, University of Idaho. Marks, J.R., and L.M. Shaffner. 1993. An empirical analysis of ventilation requirements for deep mechanized stoping at the Homestake Gold Mine. Proceedings ofthe 6th U.S. Mine Ventilation Symposium, Salt Lake City, pp. 381-385. SME, Littleton, CO. McPherson, M.J. 1993. Subsurface ventilation and environmental engineering. Chapman & Hall, NY. Mine Ventilation Society ofSouth Africa. 1982. Environmental engineering in South African mines. Mine Ventilation Society ofSouth Africa, Johan- nesburg. MSHA. 2013. Mineral resources. Code of Federal Regulations Title 30 CFR, Parts 1 through 199. Mine Safety and Health Administration, U.S. Department of Labor, Washington, D.C. www.ecfr.gov. Patterson, A.M. ed. 1992. The mine ventilation practitioner 's data book. The Mine Ventilation Society of South Africa. Sheer, T.J., M.D. Butterworth, and R. Ramsden. 2001. Ice as a coolant for deep mines. Proceedings of the 7th International Mine Ventilation Congress. Research and Development Center for Electrical Engineering and Automation in Mining, Kracow. Stachulak, J. 1989. Ventilation strategy and unique air conditioning at INCO Limited. Proceedings ofthe 4th U.S. Mine VentilationSymposium, Berkeley, CA. Society for Mining Metallurgy and Exploration, Little- ton, CO. Stewart, J.M. 1982. Practical aspects ofhuman heat stress. In Environmental engineering in South African mines, p. 574. Burrows, Hemp, Holding and Stroh, eds. The Mine Ventilation Society of South Africa. Tien, J.C. 1999. Controlled recirculation. In Practical mine ventilation engi- neering, pp. 370-392. Intertec Publishing, Chicago. van der Walt, J., and C.S.J. van Rensburg. 1988. The options for cooling deep mines. Proceedings of the 4th International Mine Ventilation Con- gress, p. 401. Australasian Institute of Mining and Metallurgy, Mel- bourne, Australia. Whillier, A. 1977. Predicting the performance of forced-draught cooling towers. Journal of the Mine Ventilation Society of South Africa 30 (1):2-25. Whillier and Thorpe. 1982. Sources ofheat in mines. In Environmental engi- neering in South African mines, Burrows, Hemp, Holding and Stroh, eds. Mine Ventilation Society of South Africa. Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
3666cc5e-269b-45a8-8d15-74fcbcd235f1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 31 INDUSTRIAL DRYING SYSTEMS ¦ Mechanism of Drying ¦ 31.1 ¦ ¦ --- ¦ --- ¦ ¦ Applying Hygrometry to Drying ¦ 31.1 ¦ ¦ Determining Drying Time ¦ 31.2 ¦ ¦ Drying System Selection ¦ 31.3 ¦ ¦ Types of Drying Systems ¦ ··· 31.3 ¦ D and solids. The term is most commonly used, however, to RYING removes water and other liquids from gases, liquids, describe removing water or solvent from solids by thermal means. Dehumidification refers to the drying of a gas, usually by conden- sation or by absorption with a drying agent (see Chapter 32 of the 2017 ASHRAE Handbook-Fundamentals). Distillation, particu- larly fractional distillation, is used to dry liquids. It is cost-effective to separate as much water as possible from a solid using mechanical methods before drying using thermal methods. Mechanical methods such as filtration, screening, press- ing, centrifuging, or settling require less power and less capital outlay per unit mass of water removed. This chapter describes industrial drying systems and their advan- tages, disadvantages, relative energy consumption, and applications. Special Warning: Certain industrial spaces may contain flam- mable, combustible, and/or toxic concentrations of vapors or dusts under either normal or abnormal conditions. In spaces such as these, there are life-safety issues that this chapter may not completely address. Special precautions must be taken in accordance with requirements ofrecognized authorities such as the National Fire Pro- tection Association (NFPA), the Occupational Safety and Health Administration (OSHA), and the American National Standards Institute (ANSI). In all situations, engineers, designers, and install- ers who encounter conflicting codes and standards must defer to the code or standard that best addresses and safeguards life safety. 1. MECHANISM OF DRYING When a solid dries, two processes occur simultaneously: (1) the transfer ofheat to evaporate the liquid and (2) the transfer of mass as vapor and internal liquid. Factors governing the rate of each process determine the drying rate. The principal objective in commercial drying is to supply the required heat efficiently. Heat transfer can occur by convection, con- duction, radiation, or a combination of these. Industrial dryers differ in their methods of transferring heat to the solid. In general, heat must flow first to the outer surface of the solid and then into the inte- rior. An exception is drying with high-frequency electrical currents, where heat is generated within the solid, producing a higher tem- perature at the interior than at the surface and causing heat to flow from inside the solid to the outer surfaces. 2. APPL YING HYGROMETRY TO DRYING In many applications, recirculating the drying medium improves thermal efficiency. The optimum proportion of recycled air balances the lower heat loss associated with more recirculation against the higher drying rate associated with less recirculation. Because the humidity of drying air is affected by the recycle ratio, the air humidity throughout the dryer must be analyzed to determine whether the predicted moisture pickup of the air is physically The preparation of this chapter is assigned to TC 9.2, Industrial Air Conditioning. attainable. The maximum ability of air to absorb moisture corresponds to the difference between saturation moisture content at wet-bulb (or adiabatic cooling) temperature and moisture content at supply air dew point. The actual moisture pickup of air is determined by heat and mass transfer rates and is always less than the maximum attainable. ASHRAE psychrometric charts for normal and high tempera- tures (No. 1 and No. 3) can be used for most drying calculations. The process does not exactly follow the adiabatic cooling lines because some heat is transferred to the material by direct radiation or by con- duction from the metal tray or conveyor. Example 1. A dryer has a capacity of 41 kg of bone-dry gelatin per hour. Initial moisture content is 228% bone-dry basis, and final moisture con- tent is 32% bone-dry basis. For optimum drying, supply air is at 48.9°C db and 29.4°C wb in sufficient quantity that the exhaust air is 37.8°C db and 29.2°C wb. Makeup air is available at 26.7°C db and 18.3°C wb. Find (1) the required amount of makeup and exhaust air and (2) the percentage of recirculated air. Solution: In this example, the humidity in each of the three airstreams is fixed; hence, the recycle ratio is also determined. Refer to ASHRAE Psychrometric Chart No. 1 to obtain the humidity ratio of makeup air and exhaust air. To maintain a steady-state condition in the dryer, water evaporated from the material must be carried away by exhaust air. Therefore, the pickup (the difference in humidity ratio between exhaust air and makeup air) is equal to the rate at which water is evaporated from the material divided by the mass of dry air exhausted per hour. Step 1. From ASHRAE Psychrometric Chart No. 1, the humidity ratios are as follows: ¦ ¦ Dry bulb, °C ¦ Wet bulb, °C ¦ Humidity ratio, g/kg dry air ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Supply air ¦ 50 ¦ 30 ¦ 18.7 ¦ ¦ Exhaust air ¦ 40 ¦ 29.5 ¦ 22 ¦ ¦ Makeup air ¦ 27 ¦ 18.6 ¦ 10 ¦ Moisture pickup is 22 - 10 = 12 g/kg (dry air). The rate of evapora- tion in the dryer is 41[(228 - 32)/100] = 80.36 kg/h = 22.3 g/s The dry air required to remove the evaporated water is 22.3/12 = 1.86 kg/s. Step 2. Assume x = percentage of recirculated air and (100 - x) = percentage of makeup air. Then Humidity ratio of supply air = (Humidity ratio of exhaust and recirculated air)(x/100) + (Humidity ratio of makeup air)(100 - x)/100 Hence, 18.7 = 22(x/100) + 10(100 - x)/100 x = 72.5% recirculated air 100 - x = 27.5% makeup air 3. DETERMINING DRYING TIME The following three methods of finding drying time are listed in order of preference: 31.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
d47f47db-f095-43d6-93c8-3d4600206eab | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 31.2 2019 ASHRAE Handbook-HVAC Applications (SI) · Conduct tests in a laboratory dryer simulating conditions for the commercial machine, or obtain performance data using the com- mercial machine. · Ifthe specific material is not available, obtain drying data on sim- ilar material by either of the above methods. This is subject to the investigator's experience and judgment. · Estimate drying time from theoretical equations (see the Refer- ences). Care should be taken in using the approximate values obtained by this method. When designing commercial equipment, tests are conducted in a laboratory dryer that simulates commercial operating conditions. Samples used in the laboratory tests should be identical to the mate- rial found in the commercial operation. Results from several tested samples should be compared for consistency. Otherwise, test results may not reflect the drying characteristics of the commercial mate- rial accurately. When laboratory testing is impractical, commercial drying data can be based on the equipment manufacturer's experience. Commercial Drying Time When selecting a commercial dryer, the estimated drying time determines what size machine is needed for a given capacity. If the drying time has been derived from laboratory tests, the following should be considered: · In a laboratory dryer, considerable drying may result from radia- tion and heat conduction. In a commercial dryer, these factors are usually negligible. · In a commercial dryer, humidity may be higher than in a labora- tory dryer. In drying operations with controlled humidity, this factor can be eliminated by duplicating the commercial humidity condition in the laboratory dryer. · Operating conditions are not as uniform in a commercial dryer as in a laboratory dryer. · Because of the small sample used, the test material may not be representative of the commercial material. Thus, the designer must use experience and judgment to modify the test drying time to suit the commercial conditions. Dryer Calculations Inc. ASHRAE, 2019 user. single for Licensed To estimate preliminary cost for a commercial dryer, the circu- lating airflow rate, makeup and exhaust airflow rate, and heat balance must be determined. Circulating Air. The required circulating or supply airflow rate is established by the optimum air velocity relative to the material. This can be obtained from laboratory tests or previous experience, keeping in mind that the air also has an optimum moisture pickup. (See the section on Applying Hygrometry to Drying.) Makeup and Exhaust Air. The makeup and exhaust airflow rate required for steady-state conditions within the dryer is also dis- cussed in the section on Applying Hygrometry to Drying. In a continuously operating dryer, the relationship between moisture content of the material and quantity of makeup air is given by GT(W2 - W1) = M(W1 - w2) where GT = dry air supplied as makeup air to the dryer, kg/s M = stock dried in a continuous dryer, kg/s W1 = humidity ratio of entering air, kg water vapor per kg dry air W2 = humidity ratio of leaving air, kg water vapor per kg dry air (in a continuously operating dryer, W2 is constant; in a batch dryer, W2 varies during part of the cycle) W1 = dry basis moisture content of entering material, kg of water/kg W2 = dry basis moisture content of leaving material, kg of water/kg (1) In batch dryers, the drying operation is given as dw GT(W2-W1)=(M1) d0 where (2) M1 = mass of material charged in a discontinuous dryer, kg per batch dw/d0 = instantaneous time rate of evaporation corresponding to W The makeup air quantity is constant and is based on the average evaporation rate. Equation (2) then becomes identical to Equation (1), where M = M1/0. Under this condition, humidity in the batch dryer decreases during the drying cycle, whereas in the continuous dryer, humidity is constant with constant load. · Radiation and convection losses from the dryer · Heating ofthe commercial dry material to the leaving temperature (usually estimated) · Vaporization of the water being removed from the material (usu- ally considered to take place at the wet-bulb temperature) · Heating of the vapor from the wet-bulb temperature in the dryer to the exhaust temperature · Heating of the total water in the material from the entering tem- perature to the wet-bulb temperature in the dryer · Heating of the makeup air from its initial temperature to the exhaust temperature Heat Balance. To estimate the fuel requirements of a dryer, a heat balance consisting of the following is needed: The energy absorbed must be supplied by the fuel. The selection and design of the heating equipment is an essential part of the over- all design of the dryer. Example 2. Magnesium hydroxide is dried from 82% to 4% moisture con- tent (wet basis) in a continuous conveyor dryer with a fin-drum feed (see Figure 7). The desired production rate is 0.38 kg/s. The optimum circulating air temperature for drying is 71.1°C, which is not limited by the existing steam pressure of the dryer. Step 1. Laboratory tests indicate the following: Specific heats ¦ air (ca) ¦ = 1.00 kJ/(kg·K) ¦ ¦ --- ¦ --- ¦ ¦ material (cm) ¦ 1.25 kJ/(kg·K) ¦ ¦ water (cw) ¦ = 4.18 kJ/(kg·K) ¦ ¦ water vapor (cv) ¦ = 1.84 kJ/(kg·K) ¦ Temperature of material entering dryer = 15°C Temperature of makeup air ¦ dry bulb ¦ = ¦ 21.1°C ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ wet bulb ¦ = ¦ 15.6°C ¦ Temperature of circulating air dry bulb 71.1°C wet bulb = 37.8°C ¦ Air velocity through drying bed ¦ = 1.27 m/s ¦ ¦ --- ¦ --- ¦ ¦ Dryer bed loading ¦ = 33.3 kg/m2 ¦ ¦ Test drying time ¦ = 25 min ¦ Step 2. Previous experience indicates that the commercial drying time is 70% greater than the time obtained in the laboratory test. Thus, the commercial drying time is estimated to be 1.7 x 25 = 42.5 min. Step 3. The holding capacity of the dryer bed is 0.38(42.5 X 60) = 969 kg at 4% (wet basis) The required conveyor area is 969/33.3 = 29.1 m2. Assuming the con- veyor is 2.4 m wide, the length of the drying zone is 29.1/2.4 = 12.125 m. Step 4. The amount of water in the material entering the dryer is 0.38[82/(100 + 4)] = 0.30 kg/s The amount of water in the material leaving is 0.38[4/(100 + 4)] = 0.015 kg/s Thus, the moisture removal rate is 0.30 - 0.015 = 0.285 kg/s. Step 5. The air circulates perpendicular to the perforated plate con- | {}
d48d22aa-7fbd-4b82-852f-8be1e1d86621 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Industrial Drying Systems 31.3 veyor, so the air volume is the face velocity times the conveyor area: Air volume = 1.27 x 29.1 = 36.96 m3/s ASHRAE Psychrometric Charts 1 and 3 show these air properties: Supply air (71°C db, 38°C wb) Humidity ratio = 29.0 g/kg (dry air) Specific volume = 1.02 m3/kg (dry air) Makeup air (21°C db, 15.5°C wb) Humidity ratio W1 = 8.7 g/kg (dry air) The mass flow rate of dry air is 36.96/1.02 = 36.24 kg/s Step 6. The amount of moisture pickup is 0.285/36.24 = 7.9 g/kg (dry air) The humidity ratio of the exhaust air is W2 = 29.0 + 7.9 = 36.9 g/kg (dry air) Substitute in Equation (1) and calculate GT as follows: G�(36.9 - 8.7)(1 kg/1000 g) = (0.38/1.04)(82 - 4)/100 GT= 10.11 kg (dry air)/s Therefore, ¦ Makeup air ¦ 100 x 10.11/36.24 = 27.9% ¦ ¦ --- ¦ --- ¦ ¦ Recirculated air ¦ = 72.1% ¦ ¦ Step 7. Heat Balance ¦ ¦ ¦ Sensible heat of material ¦ = M(tm2 - tml)cm ¦ ¦ ¦ = (0.38/1.04)(38 - 15)1.25 ¦ ¦ ¦ = 10.5 kW ¦ ¦ Sensible heat of water ¦ = Mw1(tw-tml)cw ¦ ¦ ¦ = 0.30(38 - 15)4.18 ¦ ¦ ¦ = 28.8 kW ¦ ¦ Latent heat of evaporation ¦ = M(w1 -w2)H ¦ ¦ ¦ = 0.285 kg/s x 2411 kJ/(kg ·K) ¦ ¦ ¦ = 687.1 kW ¦ ¦ Sensible heat of vapor ¦ = M(t2-tw)cv ¦ ¦ ¦ = 0.285(71 -38)1.84 ¦ ¦ ¦ = 17.3 kW ¦ ¦ Required heat for material ¦ = 741.1 kW ¦ The temperature drop (12 - 13) through the bed is Required heat 741.1 = 20 K Supplied air, kg/s xca 36.24 x 1.00 Therefore, the exhaust air temperature is 71 - 20 = 51°C. Required heat for makeup air = GT(t3 -ti)ca = 10.1(51 -21)1.00 = 303 kW The total heat required for material and makeup air is 741.1 + 303 = 1044. 1 kW Additional heat that must be provided to compensate for radiation and convection losses can be calculated from the known construction of the dryer surfaces. 4. DRYING SYSTEM SELECTION A general procedure for selecting a drying system is as follows: 1. Survey of suitable dryers. 2. Preliminary cost estimates of various types. (a) Initial investment (b) Operating cost 3. Drying tests conducted in prototype or laboratory units, prefera- bly using the most promising equipment available. Sometimes a pilot plant is justified. 4. Summary of tests evaluating quality of samples of the dried products. Factors that can overshadow the operating or investment cost include the following: ![image](/image/placeholder) SATURATED AIR TO HEAT EXCHANGER STEAM HEATED PERFORATED TOP ROLL FEED PIPE AIR-CONDITIONED ROTA TION SPACE KNIFE STEAM HEATED DRUM TAKE-OFF ROLLS SERIES MATERIAL COMES OF OFF IN SHEET, IS MOTOR BROKEN OFF iNTO DRIVEN SCREW CONVEYOR FANS- PREHEATED AIR Fig. 1 Drum Dryer · Product quality, which should not be sacrificed · Dusting, solvent, or other product losses · Space limitation · Bulk density of the product, which can affect packaging cost Friedman (1951) and Parker (1963) discuss additional aids to dryer selection. 5. TYPES OF DRYING SYSTEMS Radiant Infrared Drying Thermal radiation may be applied by infrared lamps, gas-heated incandescent refractories, steam-heated sources, and, most often, electrically heated surfaces. Infrared heats only near the surface of a material, so it is best used to dry thin sheets. Using infrared heating to dry webs such as uncoated materials has been relatively unsuccessful because of process control prob- lems. Thermal efficiency can be low; heat transfer depends on the emitter's characteristics and configuration, and on the properties of the material to be dried. Radiant heating is used for drying ink and other coatings on paper, textile fabrics, paint films, and lacquers. Inks have been spe- cifically formulated for curing with tuned or narrow wavelength infrared radiation. Ultraviolet Radiation Drying Ultraviolet (UV) drying uses electromagnetic radiation. Inks and other coatings based on monomers are cure-dried when exposed to UV radiation. This method has superior properties (Chatterjee and Ramaswamy 1975): the print resists scuff, scratch, acid, alkali, and some solvents. Printing can also be done at higher speeds without damage to the web. Major barriers to wider acceptance of UV drying include the high capital installation cost and the increased cost of inks. The cost and frequency of replacing UV lamps are greater than for infrared ovens. Overexposure to radiation and ozone, which is formed by UV radiation , s effect on atmospheric oxygen, can cause severe sunburn and possibly blood and eye damage. Safety measures include fitting the lamp housings with screens, shutters, and exhausts. Conduction Drying Drying rolls or drums (Figure 1), flat surfaces, open kettles, and immersion heaters are examples of direct-contact drying. The heat- ing surface must have close contact with the material, and agitation may increase uniform heating or prevent overheating. Conduction drying is used to manufacture and dry paper products. It(1) does not provide a high drying rate, (2) does not furnish uniform Inc. ASHRAE, 2019 user. single for Licensed | {}
4c33dc78-9349-4776-aab7-4538cfcd689e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 31.4 2019 ASHRAE Handbook- -HVAC Applications (SI) ![image](/image/placeholder) PLATEN + LARGE AIR GAP RF FIELD THIN WEB PLATEN Fig. 2 Platen-Type Dielectric Dryer heat and mass transfer conditions, (3) usually results in a poor mois- ture profile across the web, (4) lacks proper control, (5) is costly to operate and install, and ⑥ usually creates undesirable working con- ditions in areas surrounding the machine. Despite these disadvantages, replacing existing systems with other forms of drying is expensive. For example, Joas and Chance (1975) report that RF (dielectric) drying of paper requires approximately four times the capital cost, six times the operating (heat) cost, and five times the maintenance cost of steam cylinder conduction drying. However, augmenting conduction drying with dielectric drying sections offsets the high cost of RF drying and may produce savings and increased profits from greater production and higher final moisture content. Further use of large conduction drying systems depends on reducing heat losses from the dryer, improving heat recovery, and incorporating other drying techniques to maintain quality. Dielectric Drying When wet material is placed in a strong, high-frequency (2 to 100 MHz) electrostatic field, heat is generated within the material. More heat is developed in the wetter areas than in the drier areas, resulting in automatic moisture profile correction. Water is evapo- rated without unduly heating the substrate. Therefore, in addition to its leveling properties, dielectric drying provides uniform heating throughout the web thickness. Dielectric drying is controlled by varying field or frequency strength; varying field strength is easier and more effective. Re- sponse to this variation is quick, with neither time lag nor thermal lag in heating. The dielectric heater is a sensitive moisture meter. Several electrode configurations are used. The platen type (Fig- ure 2) is used for drying and baking foundry cores, heating plastic preforms, and drying glue lines in furniture. The rod or stray field types (Figure 3) are used for thin web materials such as paper and textile products. The double-rod types (over and under material) are used for thicker webs or flat stock, such as plywood. Dielectric drying is popular in the textile industry. Because air is entrained between fibers, convection drying is slow and uneven. Because the yarn is usually transferred to large packages immedi- ately after drying, however, even and correct moisture content can be obtained by dielectric drying. Knitting wool seems to benefit from internal steaming in hanks. Warping caused by nonuniform drying is a serious problem for plywood and linerboard. Dielectric drying yields warp-free products. Dielectric drying is not cost effective for overall paper drying but has advantages when used at the dry end of a conventional steam drum dryer. It corrects moisture profile problems in the web without overdrying. This combination of conventional and dielectric drying is synergistic: the drying effect of the combination is greater than the sum of the two types of drying. This is more pronounced in thicker web materials, accounting for as much as a 16% line speed increase and a corresponding 2% energy input increase. ![image](/image/placeholder) RF FIELD WEB + ELECTRODES VARIABLE AIR GAP CONFIGURATION 1 TO RF GENERATOR ELECTRODES CONFIGURATION 2 TO RF GENERATOR ELECTRODES Fig. 3 Rod-Type Dielectric Dryers SECTION THROUGH ![image](/image/placeholder) DRYER NEAR FEED END HOT-AIR WET MATERIAL CHAMBERS FROM BIN EXHAUST DUCT SECTION WET HOT-AIR NEAR MOIST DRY MATERIAL MATERIAL INLET DISCHARGE MATERIAL END DRY MATERIAL DISCHARGE Fig. 4 Cross Section and Longitudinal Section of Rotary Dryer Microwave Drying Microwave drying or heating uses ultrahigh-frequency (900 to 5000 MHz) radiation. It is a form of dielectric heating and is used for heating nonconductors. Because of its high frequency, micro- wave equipment is capable of generating extreme power densities. Microwave drying is applied to thin materials in strip form by passing the strip through the gap of a split waveguide. Entry and exit shielding make continuous process applications difficult. Its many safety concerns make microwave drying more expensive than dielectric drying. Control is also difficult because microwave drying lacks the self-compensating properties of dielectrics. Convection Drying (Direct Dryers) Some convection drying occurs in almost all dryers. True con- vection dryers, however, use circulated hot air or other gases as the principal heat source. Each means of mechanically circulating air or gases has its advantages. Rotary Dryers. These cylindrical drums cascade the material being dried through the airstream (Figure 4). The dryers are heated directly or indirectly, and air circulation is parallel or counterflow. The rotating-louver dryer is a variation, introducing air beneath the flights to provide close contact. Inc. ASHRAE, 2019 user. single for Licensed | {}
e13dd916-1e5b-4e60-9b45-b7ed8d406c00 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Industrial Drying Systems 31.5 ![image](/image/placeholder) BAFFLE EXHAUST BLOWER HEATING SURFACE 。 MAKEUP AIR BAFFLES Fig. 5 Compartment Dryer Showing Trucks with Air Circulation Cabinet and Compartment Dryers. These batch dryers range from the heated loft (with only natural convection and usually poor and nonuniform drying) to self-contained units with forced draft and properly designed baffles. Several systems may be evacuated to dry delicate or hygroscopic materials at low temperatures. Material is usually spread in trays to increase the exposed surface. Figure 5 shows a dryer that can dry water-saturated products. When designing dryers to process products saturated with sol- vents, special features must be included to prevent explosive gases from forming. Safe operation requires exhausting 100% of the air cir- culated during the initial drying period or any part of the drying cycle when solvent is evaporating at a high rate. At the end of the purge cycle, the air is recirculated and heat is gradually applied. To prevent explosions, laboratory dryers can be used to determine the amount of air circulated, cycle lengths, and rate that heat is applied for each product. In the drying cycle, dehumidified air, which is costly, should be recirculated as soon possible. The air must not be recirculated when cross-contamination of products is prohibited. Dryers must have special safety features in case any part of the drying cycle fails. The following are some of the safety design fea- tures described in Industrial Ovens and Driers (FM Global 2014): · Each compartment must have separate supply and exhaust fans and an explosion-relief panel. · The exhaust fan blade tip speed should be 25 m/s for forward- inclined blades, 35 m/s for radial-tip, and 38 m/s for backward- inclined. These speeds produce high static pressures at the fan, ensuring constant exhaust volumes under conditions such as neg- ative pressures in the building or downdrafts in the exhaust stacks. · Airflow failure switches in both the supply and exhaust ducts must shut off fans and the heating coil and must sound an alarm. · A high-temperature limit controller in the supply duct must shut off the heat to the heating coil and must sound an alarm. · An electric interlock on the dryer door must interrupt the drying cycle if the door is opened beyond a set point, such as that wide enough for a person to enter for product inspection. Tunnel Dryers. Tunnel dryers are modified compartment dryers that operate continuously or semicontinuously. Fans circulate heated air or combustion gas is circulated by fans. The material is handled on trays or racks on trucks and moves through the dryer either intermittently or continuously. The airflow may be parallel, counterflow, or a combination obtained by center exhaust (Figure ![image](/image/placeholder) EXHAUST AIR AUTO DAMPERS MAKEUP AIR (DEHUMIDIFIED IF REQUIRED) △△△ AIR AIR SAFETY , SWITCH RECIRC. 0- FILTERS AUTO DAMPERS イト AK スト 7.5 70 45 TRUCK WHEEL GUIDE Fig. 6 Explosionproof Truck Dryer Showing Air Circulation and Safety Features 6). Air may also flow across the tray surface, vertically through the bed, or in any combination of directions. By reheating or recirculat- ing the air in the dryer, high saturation is reached before the air is exhausted, thus reducing the sensible heat loss. The following problems with tunnel dryers have been experi- enced and should be considered in future designs: · Operators may overload product trays to increase output, but this can overtax the system and increase drying time. · Sometimes air from the drying tunnel is discharged into the pro- duction area, increasing the humidity. Air from the drying tunnel should be discharged to the drying system return or outdoors. · Overloaded product trays add pressure drop, which decreases flow through the dryer. The control panel should indicate vali- dated flow through the tunnel. High and low flow and high mois- ture levels should trigger alarms. · Cycle times can be reduced by designing dryers for cross flow rather than end-to-end flow. A variation of the tunnel dryer is the strictly continuous dryer, which has one or more mesh belts that carry the product through it, as shown in Figure 7. Many combinations of temperature, humidity, air direction, and velocity are possible. Hot air leaks at the entrance and exit can be minimized by baffles or inclined ends, with the material entering and leaving from the bottom. High- v elocity Dryers. High-velocity hoods or dryers have been used to supplement conventional cylinder dryers for drying paper. When used with conventional cylinder dryers, web instability and lack of process control result. Where internal diffusion is not the controlling factor in the drying rate, applications such as thin per- meable webs offer more promise. Spray Dryers. Spray dryers have been used in producing dried milk, coffee, soaps, and detergents. Because the dried product (in the form of small beads) is uniform and drying time is short (5 to 15 s), this drying method has become more important. When a liq- uid or slurry is dried, the spray dryer has high production rates. Inc. ASHRAE, 2019 user. single for Licensed | {}
25341e95-60dd-44de-ab25-4a1b36fb0eab | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 31.6 ![image](/image/placeholder) FIN-DRUM FEED DRYER FAN , " : 서명 MILLE , 또는 :: 0 과 N ▼ FAN FAN Fig. 7 Section of Blow-Through Continuous Dryer ![image](/image/placeholder) SPRAY NOZZLES: IN PRACTICE EXHAUST HIGH-PRESSURE MILK, THERE ARE A NUMBER OF PRECONCENTRATED THESE, EACH IN THE CENTER OF AN AIR CHAMBER AIR FILTERS CLOTH BAG FILTERS AIR AIR MILK AIR MILK DRIES IN THIS ZONE, FALLS OUT AS POWDER HOPPER FAN HEATING COILS POWDERED MILK REMOVED HERE Fig. 8 Pressure-Spray Rotary Spray Dryer Spray drying involves atomizing a liquid feed in a hot-gas drying medium. The spray can be produced by a two-fluid nozzle, a high- pressure nozzle, or a rotating disk. Inlet gas temperatures range from 93 to 760°C, with the high temperatures requiring special con- struction materials. Because thermal efficiency increases with the inlet gas temperature, high inlet temperatures are desirable. Even heat-sensitive products can be dried at higher temperatures because of the short drying time. Hot gas flow may be either con- current or countercurrent to the falling droplets. Dried particles settle out by gravity. Fine material in the exhaust air is collected in cyclone separators or bag filters. Figure 8 shows a typical spray drying system. The physical properties of the dried product (such as particle size, bulk density, and dustiness) are affected by atomization char- acteristics and the temperature and direction of flow of the drying gas. The product's final moisture content is controlled by the humid- ity and temperature of the exhaust gas stream. Currently, pilot-plant or full-scale production operating data are required for design purposes. The drying chamber design is deter- mined by the nozzle 's spray characteristics and heat and mass transfer rates. There are empirical expressions that approximate mean particle diameter, drying time, chamber volume, and inlet and outlet gas temperatures. Freeze Drying Freeze drying has been applied to pharmaceuticals, serums, bac- terial and viral cultures, vaccines, fruit juices, vegetables, coffee and tea extracts, seafoods, meats, and milk. The material is frozen, then placed in a high-vacuum chamber connected to a low-temperature condenser or chemical desiccant. Heat is slowly applied to the frozen material by conduction or infra- red radiation, allowing the volatile constituent, usually water, to sublime and condense or be absorbed by the desiccant. Most freeze- drying operations occur between -10 and -40°C under minimal pressure. Although this process is expensive and slow, it has advan- 2019 ASHRAE Handbook-HVAC Applications (SI) tages for heat-sensitive materials (see Chapter 29 of the 2018 ASHRAE Handbook- - Refrigeration). Vacuum Drying Vacuum drying takes advantage of the decrease in the boiling point of water that occurs as the pressure is lowered. Vacuum drying of paper has been partially investigated. Serious complications arise ifthe paper breaks, and massive sections must be removed. Vacuum drying is used successfully for pulp drying, where lower speeds and higher masses make breakage relatively infrequent. Fluidized-Bed Drying A fluidized-bed system contains solid particles through which a gas flows with a velocity higher than the incipient fluidizing veloc- ity but lower than the entrainment velocity. Heat transfer between the individual particles and the drying air is efficient because there is close contact between powdery or granular material and the flu- idizing gas. This contact makes it possible to dry sensitive materials without danger of large temperature differences. The dried material is free-flowing and, unlike that from con- vection dryers, is not encrusted on trays or other heat-exchanging surfaces. Automatic charging and discharging are possible, but the greatest advantage is reduced process time. Only simple controls are important: over (1) fluidizing air or gas temperatures and (2) the drying time of the material. All fluidized-bed dryers should have explosion-relief flaps. Both the pressure and flames of an explosion are dangerous. When toxic materials are used, uncontrolled venting to the atmosphere is prohibited. Explosion suppression systems, such as pressure- actuated ammonium-phosphate extinguishers, have been used instead of relief venting. An inert dryer atmosphere is preferable to suppression systems because it prevents explosive mixtures from forming. When organic and inflammable solvents are used in the fluidized- bed system, the closed system offers advantages other than explosion protection. A portion of the fluidizing gas is continuously run through a condenser, which strips the solvent vapors and greatly reduces air pollution problems, thus making solvent recovery conve- nient. Materials dried in fluidized-bed installations include coal, lime- stone, cement rock, shales, foundry sand, phosphate rock, plastics, medicinal tablets, and foodstuffs. Leva (1959) and Othmer (1956) discuss the theory and methods of fluidization of solids. Clark (1967) and Vanecek et al. (1966) developed design equations and cost estimates. Agitated-Bed Drying Uniform drying is ensured by periodically or continually agitat- ing a bed of preformed solids with a vibrating tray, a conveyor, or a vibrating mechanically operated rake, or, in some cases, by partial fluidization of the bed on a perforated tray or conveyor through which recycled drying air is directed. Drying and toasting cereals is an important application. Drying in Superheated Vapor Atmospheres When drying solids with air or another gas, the vaporized sol- vent (water or organic liquid) must diffuse through a stagnant gas film to reach the bulk gas stream. Because this film is the main resistance to mass transfer, the drying rate depends on the solvent vapor diffusion rate. If the gas is replaced by solvent vapor, resis- tance to mass transfer in the vapor phase is eliminated, and the drying rate depends only on the heat transfer rate. Drying rates in solvent vapor, such as superheated steam, are greater than those in air for equal temperatures and mass flow of the drying media. This method also has higher thermal efficiency, easier solvent recovery, and a lower tendency to overdry, and it eliminates oxida- Inc. ASHRAE, 2019 user. single for Licensed | {}
4fdc6122-6cbb-4f64-8605-4fc611b507dd | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Industrial Drying Systems 31.7 tion or other chemical reactions that occur when air is present. In drying cloth, superheated steam reduces the migration tendency of resins and dyes. Superheated vapor drying cannot be applied to heat-sensitive materials because of the high temperatures. Commercial drying equipment with recycled solvent vapor as the drying medium is available. Installations have been built to dry textile sheeting and organic chemicals. Flash Drying Finely divided solid particles that are dispersed in a hot gas stream can be dried by flash drying, which is rapid and uniform. Commercial applications include drying pigments, synthetic resins, food products, hydrated compounds, gypsum, clays, and wood pulp. Constant-Moisture Solvent Drying In some cases it is desirable to dry organic solvents from a sub- stance without changing moisture content. This is particularly true in drying pharmaceutical products, which are commonly bound with solvents such as isopropyl alcohol (IPA) or acetone. Loss ofmoisture content can affect the stability of some pharmaceutical compounds, which therefore must be liberated of bound solvents without chang- ing the relative humidity. Most pharmaceutical facilities producing oral solid dosage (OSD) forms manufacture in spaces that range from 30 to 45% rh. To maintain this level ofhumidity at the tempera- tures needed to liberate the organic solvents at the required rate, an oven must be fitted with an adequately sized humidifier. Figure 9 shows the compartment dryer from Figure 5 adapted for constant- moisture drying. Itis vital to size the preheat coil to the humidifier to allow enough "room" to provide the humidification level required. The amount of preheat is usually enough to provide makeup air to the oven at 90% rh. This allows the oven heaters to control drying temperature at the more common oven humidity levels of 30 to 45% rh. If elec- tric heat is used, the ability to constantly vary the capacity of the heaters must be provided; silicon-controlled rectifiers (SCRs) are commonly used. Additional insulation on the outside of the oven and the ductwork from the humidifier section onward should also be considered. Care must be taken to ensure that unwanted condensation does not form inside the oven. Dripping moisture can sometimes ruin the product, causing a substantial economic loss. If the product is pharmaceuti- cal, then the humidifier makeup water source should be deionized or produced to comply with U.S. Pharmacopoeia 34-National For- mulary-29 (effective August 2010). ![image](/image/placeholder) STEAM HUMIDIFIER MAKEUP FAN EXHAUST HUMIDITY SENSOR HEATERS RECIRCULATION FAN ▼ Fig. 9 Humidified Cross-Flow Tray Dryer REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. Chatterjee, P.C., and R. Ramaswamy. 1975. Ultraviolet radiation drying of inks. British Ink Maker 17(2):76. Clark, W.E. 1967. Fluid bed drying. Chemical Engineering 74(March): 177. FM Global. 2014. Industrial ovens and driers. Data Sheet No. 6-9. FM Global, Johnson, RI. Friedman, S.J. 1951. Steps in the selection of drying equipment. Heating and Ventilating (February):95. Joas, J.G., and J.L. Chance. 1975. Moisture leveling with dielectric, air impingement and steam drying-A comparison. TAPPI 58(3):112. Leva, M. 1959. Fluidization. McGraw-Hill, New York. Othmer, D.F. 1956. Fluidization. Reinhold Publishing, New York. Parker, N.H. 1963. Aids to drier selection. Chemical Engineering 70(June 24):115. U.S. Pharmacopoeia 34-National Formulary-29. 2010. Vanecek, V., M. Markvart, and R. Drbohlav. 1966. Fluidized bed drying. Chemical Rubber Company, Cleveland, OH. Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
065a8f9b-38eb-44af-839a-fbf555cc6e5c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 32 VENTILATION OF THE INDUSTRIAL ENVIRONMENT ¦ Ventilation Design Principles ¦ 31.2 ¦ ¦ --- ¦ --- ¦ ¦ General Comfort and Dilution Ventilation ¦ 31.2 ¦ ¦ Heat Control. ¦ 31.5 ¦ ¦ Energy Conservation, Recovery, and Sustainability ¦ ···· 31.6 ¦ INDUSTRIAL environments require ventilation to reduce expo- to excess heat and contaminants that are generated in the workplace; in some situations, cooling may also be required. Venti- lation is primarily used to control excess heat, odors, and hazardous particulate and chemical contaminants. These could affect workers' health and safety or, in some cases, become combustible or flamma- ble when allowed to accumulate above their minimum explosive concentration (MEC) or lower flammable limit (LFL) [also called the lower explosive limit (LEL)] (Cashdollar 2000). Excess heat and contaminants can best be controlled by using local exhaust systems whenever possible. Local exhaust systems capture heated air and contaminants at their source and may require lower airflows than general (dilution) ventilation. See Chapter 32 for more information on the selection and design of industrial local exhaust systems. General ventilation can be provided by mechanical (fan) systems, by natural draft, or by a combination of the two. Combination sys- tems could include mechanically driven (fan-driven) supply air with air pressure relief through louvers or other types of vents, and mechanical exhaust with air replacement inlet louvers and/or doors. Mechanical (fan-driven) supply systems provide the best control and the most comfortable and uniform environment, especially when there are extremes in local climatic conditions. The systems typically consist of an inlet section, filtration section, heating and/or cooling equipment, fans, ductwork, and air diffusers for distributing air in the workplace. When toxic gases or vapors are not present and there are no aerosol contaminants associated with adverse health effects, air cleaned in the general exhaust system or in packaged air filtration units can be recirculated via a return duct. When applied appropri- ately, air recirculation can be a major contributor to a sustainable in- dustrial ventilation design and may reduce heating and cooling costs. In addition, regardless of the method selected, any positive ven- tilation into an industrial space should be from a source that is essen- tially free of any contaminants under both normal and abnormal conditions in the surrounding atmosphere. In many cases, this may require a sealed intake stack or ductwork, as opposed to a perimeter wall hood or other air intake device, wherein the source of intake should be from a point well above or beyond the veil of the hazard- ous space that may surround a ventilated space. Where this cannot be achieved, additional action should be undertaken (e.g., providing particulate or carbon filtration). A general exhaust system, which removes air contaminated by gases, vapors, or particulates not captured by local exhausts, usually consists of one or more fans, plus inlets, ductwork, and air cleaners or filters. After air passes through the filters, it is either discharged outdoors, or partially recirculated within the building. The air filtra- tion system , s cleaning efficiency should conform to environmental regulations and depends on factors such as building location, back- ground contaminant concentrations, type and toxicity of contami- nants, and height and velocity of building exhaust discharge. Many industrial ventilation systems must handle simultaneous exposures to temperature extremes and hazardous substances. In The preparation of this chapter is assigned to TC 5.8, Industrial Ventilation Systems. these cases, the required ventilation can be provided by a combina- tion of local exhaust, general ventilation air supply, and general exhaust systems. The ventilation engineer must carefully analyze supply and exhaust air requirements to determine the worst case. For example, air supply makeup for hood exhaust may be insufficient to control heat exposure. It is also important to consider seasonal cli- matic effects on ventilation system performance, especially for nat- ural ventilation systems. Duct material and its compatibility with the exhaust airstream is also important to consider when ventilating haz- ardous, abrasive, or corrosive substances. Most importantly, ifthe hazardous substances are ignitable gases or dusts, all electrical components of the ventilation system should be rated for the proper electrical classification in the absence of any ventilation, regardless of their locations in the ventilation system. In specifying acceptable chemical contaminant and heat expo- sure levels, the industrial hygienist or industrial hygiene engineer must consult the appropriate occupational exposure limits that apply as well as any governing standards and guidelines. The leg- islated limits for the maximum airborne concentration of chemical substances to which a worker may be exposed are listed as (1) max- imum average exposures to which a worker may be exposed over a given work day (generally assumes an 8 to 10 h work day and a tra- ditional 40 h work week); (2) short-term exposure limits, which are the maximum average airborne concentration to which a worker may be exposed over any 15 min period; and (3) ceiling limits, which are the maximum airborne concentration to which a worker may be exposed at any time. However, occupational exposure limits for cold, heat, and contaminants are not lines of demarcation between safe and unsafe exposures. Rather, they represent conditions to which it is believed nearly all workers may be exposed day after day without adverse and/or long-term effects. Because a small percentage of workers may be affected by occupational exposure below the regulated limits, it is prudent to design for control to the most conservative occupational exposure limits (OELs) available. In the case of exposure to hazardous chemicals, the number of contaminant sources, their generation rates, and the effectiveness of exhaust hoods may not be known. Consequently, the ventilation engineer must rely on industrial hygiene engineering practices when designing toxic and/or hazardous chemical controls. Close coopera- tion among the industrial hygienist, process engineer, and ventila- tion engineer is required. In the case of exposure to flammable or ignitable chemicals, the specific gravity of the contaminant source(s), their concentration, and the rating of all electrical devices in the space, along with any source or point of excessive heat, must be carefully considered to prevent possible loss of life or severe injury. As with all hazardous chemicals, cooperation of knowledgeable experts, including electri- cal engineers, is required. This chapter describes principles of ventilation practice and includes other information on industrial hygiene in the industrial environment. Publications from the American Industrial Hygiene Association (AIHA 2011), British Occupational Hygiene Society (BOHS 2002), U.S. Department of Health and Human Services (DHHS 1986), National Safety Council (2012), and U.S. National 32.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
791c82aa-717a-4afb-8e71-d6992df69cd3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 32.2 2019 ASHRAE Handbook-HVAC Applications (SI) Institute for Occupational Safety and Health (NIOSH 1986) provide further information on industrial hygiene principles and their appli- cation. 1. VENTILATION DESIGN PRINCIPLES Special Warning: Certain industrial spaces may contain flam- mable, combustible, and/or toxic concentrations of vapors or dusts under either normal or abnormal conditions. In spaces such as these, there are life safety issues that this chapter may not com- pletely address. Special precautions must be taken in accordance with requirements of recognized authorities such as the National Fire Protection Association (NFPA), the Occupational Safety and Health Administration (OSHA), and the American National Stan- dards Institute (ANSI). In all situations, engineers, designers, and installers who encounter conflicting codes and standards must defer to the code or standard that best addresses and safeguards life safety. General Ventilation General ventilation supplies and/or exhausts air to provide heat relief, dilute contaminants to an acceptable level, and replace exhaust air. Ventilation can be provided by natural or mechanical supply and/or exhaust systems. Industrial areas must comply with ASHRAE Standard 62. 1-2013 and other standards as required (e.g., by NFPA). Outdoor air is unacceptable for ventilation ifit is known to contain any contaminant at a concentration above that given in ASHRAE Standard 62. 1. If air is thought to contain any contami- nant not listed in the standard, consult relevant federal, state, pro- vincial, or local jurisdictions for acceptable exposure levels. In addition to their role in controlling industrial contaminants, general ventilation rates must be sufficient to dilute the carbon dioxide produced by occupants to a level acceptable under ASHRAE Stan- dard 62.2. For complex industrial ventilation problems, experimental scale models and computational fluid dynamics (CFD) models are often used in addition to field testing. Makeup Air When large volumes of air are exhausted to provide acceptable comfort and safety for personnel and acceptable conditions for pro- cess operations, this air must be replaced, either through intentional design strategy or through paths ofleast resistance. A safe and effec- tive ventilation design should be strategic about the mechanism, locations, and physical parameters by which makeup air enters the occupied space. Makeup air, consistently provided by good air dis- tribution, allows more effective cooling in the summer and more efficient and effective heating in the winter. When makeup air design is not incorporated into the ventilation design scheme, it may lead to inefficient operation of local exhaust systems and/or com- bustion equipment and cross-drafts that affect occupant comfort and environmental control settings. Relying on windows or other air inlets that cannot function in year-round weather conditions is dis- couraged. Some factors to consider in designs for makeup air include Inc. ASHRAE, 2019 user. single for Licensed · Makeup air must be sufficient to replace air being exhausted or consumed by combustion processes, local and general exhaust systems (see Chapter 32), or process equipment. (Large air com- pressors can consume a large amount of air and should be consid- ered if air is drawn from within the building.) · Makeup air systems should be designed to eliminate uncomfort- able cross-drafts by properly arranging supply air outlets, and to prevent infiltration (through doors, windows, and similar open- ings) that may make hoods unsafe or ineffective, defeat envi- ronmental control, bring in or stir up dust, or adversely affect processes by producing temperature or airflow disturbances. The · · · · · design engineer needs to consider side drafts and other sources of air movement close to the capture area of a local exhaust hood. In industrial applications, it is common to see large fans blowing air onto workers positioned in front of the hood. This can render the local exhaust hood ineffective to the point that no protection is pro- vided for the worker: Ahn et al. (2008), Caplan and Knutson (1977, 1978), and Tseng et al. (2010) found that air movement in front of laboratory hoods can cause contaminants to escape from the hood and into the operator's breathing zone. Hoods should be located safe distances from doors and openable windows, supply air diffusers, and areas of high personnel traffic (AIHA Standard Z9.5; NFPA Standard 45). Makeup air should be obtained from a clean source with no more than trace amounts of any airborne contaminants or hazardous, ignitable substances. Supply air can be filtered, but infiltration air cannot. For transfer air use, see ASHRAE Standard 62. 1. Makeup air for spaces contaminated by toxic, ignitable, or com- bustible chemicals may have to be acquired through carefully sealed ductwork from an area know to be free of contamination and be supplied at sufficient rates, pressures, and mixing efficien- cies to (1) remove all contamination, and (2) prevent infiltration of similar contaminants from surrounding areas or adjacent spaces. Makeup air should be used to control building pressure and air- flow from space to space to (1) avoid positive or negative pres- sures that make it difficult or unsafe to open doors, (2) minimize drafts, and (3) prevent infiltration. Makeup air should be used to reduce contaminant concentration, to control temperature and humidity, and minimize undesirable air movement. Makeup air systems should be designed to recover heat and con- serve energy (see the section on Energy Conservation, Recovery, and Sustainability). For more information on potential adverse conditions caused by specific negative pressure levels in buildings, see ACGIH (2013) and Chapter 28 in the 2016 ASHRAE Handbook- HVAC Systems and Equipment. 2. GENERAL COMFORT AND DILUTION VENTILA TION Effective air diffusion in ventilated rooms and the proper quan- tity of conditioned air are essential for creating an acceptable work- ing environment, removing contaminants, and reducing installation and operating costs of a ventilation system. Ventilation systems must supply air at the proper velocity and temperature, with result- ing contaminant concentrations within permissible occupational exposure limits (OELs). For the industrial environment, the most common objective is to provide tolerable (acceptable) working con- ditions rather than comfort (optimal) conditions. General ventilation system design is based on the assumption that local exhaust ventilation, radiation shielding, and equipment insulation and encapsulation have been selected to minimize both heat load and contamination in the workplace (see the section on Heat Control). When work operations are generally restricted, such as with equipment operating stations or control booths, spot conditioning of the work environment with clean conditioned air (see the section on Makeup Air) may further reduce the reliance on general ventilation for conditioning or contaminant dilution. In cold climates, infiltration and heat loss through the building enve- lope may need to be minimized by pressurizing buildings. For more information on dilution ventilation, see ACGIH (2013). Quantity of Supplied Air Sufficient air must be supplied to replace air exhausted by process ventilation and local exhausts, dilute contaminants (gases, vapors, or | {}
2ff1d425-c311-4232-b8d3-66307202fe92 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Ventilation of the Industrial Environment 32.3 airborne particles) not captured by local exhausts, prevent the entry of contaminants or hazardous (ignitable) substances from any sur- rounding atmosphere during ingress or egress, and provide the required thermal environment. The amount of supplied air should be the largest of the amounts needed for temperature control, dilution, and replacement. Air Supply Methods Air supply to industrial spaces can be by natural or mechanical ventilation systems. Although natural ventilation systems driven by gravity forces and/or wind effect are still widely used in industrial spaces (especially in hot premises in cold and moderate climates), they are inefficient in large buildings, may cause drafts, and may not sufficiently solve air contamination problems, because the prereq- uisite environmental conditions may not be available during all required periods of need or there is no practical filtration method available. Thus, most ventilation systems in industrial spaces are either mechanical (fan-driven) or a combination of mechanical sup- ply with natural exhaust, using louvers or doors for air pressure relief (or for air replacement in exhaust systems). The most common methods of air supply to industrial spaces are mixing, displacement, and localized. Mixing Air Distribution. In mixing systems, air is normally supplied at velocities much greater than those acceptable in the occupied zone. Supply air temperature can be above, below, or equal to the air temperature in the occupied zone, depending on the heating/cooling load. The supply air diffuser jet mixes with room air by entrainment, which reduces air velocities and equalizes the air temperature. The occupied zone is ventilated either directly by the air jet or by reverse flow created by the jet. Properly selected and designed mixing air distribution creates relatively uniform air velocity, temperature, humidity, and air quality conditions in the occupied zone and over the room height. Note that supply systems should introduce air into the workspace in such a way as to not inter- fere with contaminant control systems such as ventilation hoods. If possible, ventilation hoods (e.g., fume hoods) should have quiescent air conditions (~0.5 m/s) at their face. Displacement Ventilation Systems. Conditioned air that is slightly cooler than the desired room air temperature in the occupied zone is supplied from air outlets at low air velocities (~0.5 m/s or less). Because ofbuoyancy, the cooler air spreads along the floor and floods the room 's lower zone. Air close to the heat source is heated and rises upward as a convective air stream; in the upper zone, this stream spreads along the ceiling. The height of the lower zone depends on the air volume and temperature supplied to the occupied zone and on the amount of convective heat discharged by the sources. Typically, outlets are located at or near the floor, and supply air is introduced directly into the occupied zone. In some applications (e.g., in computer rooms or hot industrial buildings), air may be sup- plied to the occupied zone through a raised floor. Exhaust or air returns are located at or close to the ceiling or roof. Displacement ventilation is common in European countries. It is an option when contaminants are released in combination with sur- plus heat, and contaminated air is warmer (more buoyant) than the surrounding air. It is not a good choice when air turbulence can inter- fere with convective conveyance of heat and contaminants. Further information on displacement air distribution systems can be found in Chen and Glicksman (2003) and Goodfellow and Tahti (2001). Localized Ventilation. Air is supplied locally for occupied re- gions or a few permanent work areas (Figure 1). Conditioned air is supplied toward the occupants' breathing zone to create comfort- able conditions and/or to reduce the concentration of pollutants. These zones may have air that is cleaner than the surrounding air, and should generally be compliant with ASHRAE Standard 62.1. In localized ventilation systems, air is supplied through one of the fol- lowing devices: ![image](/image/placeholder) A. AIR SHOWERS me B. AIR OASIS WITH HORIZONTAL AIR SUPPLY C. AIR OASIS WITH VERTICAL AIR SUPPLY Fig. 1 Localized Ventilation Systems Inc. ASHRAE, 2019 user. single for Licensed | {}
39bb9884-e8c4-47cd-85f6-9747bd3506f5 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 32.4 2019 ASHRAE Handbook-HVAC Applications (SI) · Nozzles or grilles (e.g., for spot cooling), specially designed low- velocity/low-turbulence devices · Perforated panels suspended on vertical duct drops and positioned close to the workstation Local Area and Spot Cooling In hot workplaces that have few work areas, itis likely impracti- cal to maintain a comfortable environment in the entire space. How- ever, environmentally controlled cabins, individual cooling, and spot cooling and extraction can improve working conditions in occupied areas. Certain applications require minimum distances from supplied air (and natural ventilation points) to ensure airflow in ventilated hoods and cabinets is not affected. Environmentally controlled cabins (e.g., operating cabs, pul- pits, control rooms, enclosures) can provide thermal comfort, and, when pressurized with a dedicated clean-air supply (either dedi- cated source or through effective filtration), can improve air quality in occupational environments. There usually are significant eco- nomic benefits to properly designing, installing, and maintaining worker-protective environmental enclosures. Spot cooling, probably the most popular method of improving the thermal environment, can be provided by radiation (changing mean radiant temperature), convection (changing air velocity and/or air supply temperatures), or both. Spot-cooling equipment is fixed at the workstation, whereas in individual cooling, the worker wears the equipment. Local exhaust ventilation (spot extraction) is another method to remove excess heat from a process or source ofhigh temperature, and should be the first step considered for energy saving over spot cooling. Locker Room, Toilet, and Shower Space Ventilation Ventilation oflocker rooms, toilets, and shower spaces is import- ant in industrial facilities to remove odor and reduce humidity. In some industries, control of workroom contamination requires pre- vention ofboth ingestion and inhalation routes of exposure, so ade- quate hygienic facilities, including appropriate ventilation, may be required in locker rooms, changing rooms, showers, lunchrooms, and break rooms. State, provincial, and local regulations should be consulted early in design. Supply air may be introduced through doors or wall grilles. In some cases, workplace air may be so contaminated that filtration or a dedicated source of clean supply air is required. When control of workroom contaminants is inadequate or not feasible, reduce employee exposure by positively pressurizing locker rooms, lunch- rooms, and break rooms to minimize the level of contamination in those areas. Treated supply air may be ineffective in some applica- tions because it can introduce drafts and outdoor contamination or result in excessive condensation in a humid indoor environment. When mechanical ventilation of supply air is used, the supply system should have adequate ducting and air distribution devices, such as diffusers or grilles, to distribute air throughout the area. In locker rooms, take exhaust primarily from the toilet and shower spaces as needed and secondarily from the lockers. Exhaust- ing from the room 's open ceiling areas should be a last option. ASHRAE Standard 62.1 and many local mechanical codes provide requirements for these areas. Roof v entilators Roof ventilators are heat escape ports located high in a building and should be properly enclosed for weathertightness (Goodfellow 1985). Stack effect and some wind induction are the motive forces for gravity- (buoyancy-) driven operation of continuous and round ventilators. Round ventilators can be equipped with a fan barrel and motor, allowing gravity or forced ventilation operation. Many ventilator designs are available, including the low ventila- tor, which consists of a stack fan with a rain hood, and a ventilator with a split butterfly closure that floats open to discharge air and closes by a counterweight. Both use minimum enclosures and have little or no gravity capacity. Split butterfly dampers tend to increase fan airflow noise and are subject to damage from slamming during strong winds. Because noise is frequently a problem in powered roof ventilators, the manufacturer's sound rating should be reviewed. Sound attenuators should be installed where required to meet the design sound ratings. Continuous ventilation monitors remove substantial, concen- trated heat loads most effectively. One type, the streamlined con- tinuous ventilator, is efficient, weathertight, and designed to prevent backdraft; it usually has dampers that may be closed in win- ter to conserve building heat. Its capacity is limited only by the available roof area and the proper location and sizing of low-level air inlets. Continuous ventilation to achieve a slight pressure above the surrounding atmosphere (referred to as pressurization by NFPA) also can be used to reduce or declassify the electrical clas- sification of enclosed spaces. Typically, reductions from class I, zone 1 or division 1 to class I, zone 2 or division 2 can be achieved by following the recommendations of NFPA Standard 496. This allows using general-purpose electrical devices instead of zone 2 or division 2 devices, or using zone 2 or division 2 electrical devices instead of zone 1 or division 1 devices, which (1) greatly reduces the cost of electrical equipment and (2) provides a sound alternative when particular devices are not available for the higher (more vola- tile) electrical area classifications. Gravity ventilators, also highly effective, have low operating costs, do not generate noise, and are self-regulating (i.e., higher heat release increases airflow through the ventilators). Gravity ventilators can be affected by environmental conditions and thus should only be used for heat control rather than for the control of gaseous or aerosol contaminants. Care must be taken to ensure pos- itive pressure at the ventilators, particularly during the heating sea- son. Otherwise, outside air will enter the ventilators. Next in order of heat removal capacity are (1) round gravity or wind-band ventilators, (2) round gravity ventilators with fan and motor added, (3) low-hood powered ventilators, and (4) vertical upblast powered ventilators. The shroud for the vertical upblast design has a peripheral baffle to deflect air upward instead of down- ward. Vertical discharge is highly desirable to reduce roof damage caused by hot air ifit contains condensable oil or solvent vapor. Ven- tilators with direct-connected motors are desirable to avoid belt maintenance. Round gravity ventilators are applicable for ware- houses with light heat loads and for manufacturing areas with high roofs and light loads. Streamlined continuous ventilators must operate effectively without mechanical power. To ensure ventilator performance, suffi- cient low-level openings must be provided for incoming air; insuf- ficient inlet area and significant space air currents are the most common reasons gravity roof ventilators malfunction. A positive supply of air around hot equipment may be necessary in large build- ings where external wall inlets are remote from the equipment. Chapter 16 of the 2017 ASHRAE Handbook-Fundamentals has additional information on ventilation and infiltration. The cost of electrical power for mechanical ventilation over that ofroof ventilators can be offset by the advantage of constant airflow. Mechanical ventilation can also create the pressure differential nec- essary for good airflow, even with small inlets. Inlets should be sized correctly to avoid infiltration and other problems caused by high neg- ative pressure in the building. Often, a mechanical system is justified to supply enough makeup air to maintain the work area under posi- tive pressure. Roof ventilators can comprise either mechanically operated open- ings or fan-powered mechanical exhaust. Operator-assisted openings Inc. ASHRAE, 2019 user. single for Licensed | {}
b76d0de9-afe9-4e98-ad38-d5300dc58740 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Ventilation of the Industrial Environment 32.5 or dampers are usually used in shops with high ceilings, and must be installed when natural ventilation is used to provide air to the space. 3. HEAT CONTROL Ventilation control alone may frequently be inadequate for meet- ing heat stress standards for industrial work areas. Optimum solu- tions may involve additional controls such as spot cooling, changes in work/rest patterns, and radiation shielding. Ventilation for Heat Relief Many industrial processes release large amounts of heat and moisture to the environment. In such environments, it may not be economically feasible to maintain comfort conditions (ASHRAE Standard 55), particularly during summer. Comfortable conditions are not physiologically necessary: the body must be in thermal bal- ance with the environment, but this can occur at temperature and humidity conditions well above the normal comfort zone. In areas where heat and moisture generated by a process are low to moderate, comfort conditions may not have to be provided if personnel expo- sures are infrequent and brief. In such cases, ventilation may be the only control necessary to prevent excessive physiological heat stress. The engineer must distinguish between control needs for hot/dry industrial areas and warm/moist conditions. In hot/dry areas, a pro- cess gives off only sensible (primarily convective and radiant) heat without adding moisture to the air. This increases the heat load on exposed workers, but the rate of cooling by evaporation of perspira- tion may not be significantly reduced. Body heat equilibrium may be maintained, but could cause excessive perspiration. Hot/dry work situations occur around furnaces, forges, metal-extruding and roll- ing mills, glass-forming machines, etc. In warm/moist conditions, a wet process may generate a signifi- cant latent heat load. The rise in sensible heat load on workers may be insignificant, but the increased moisture content of the air can seriously reduce cooling by evaporation of perspiration, making warm/moist conditions potentially more hazardous than hot/dry. Typical warm/moist operations are found in textile mills, laundries, dye houses, and deep mines, where water is used extensively for dust control. Industrial heat load is also affected by local climate. Solar heat gain and elevated outdoor temperatures increase the heat load at the workplace, but may be insignificant compared to process heat gen- erated locally. The moisture content of outdoor air is an important factor that can affect hot/dry work situations by restricting an indi- vidual's evaporative cooling. For warm/moist working environ- ments, solar heat gain and elevated outdoor temperatures are even more important because moisture contributed by outdoor air is insignificant compared to that released by the process. Both ASHRAE Standard 55 and International Organization for Standardization (ISO) Standard 7730 specify thermal comfort con- ditions. Methods for evaluating the general thermal state of the body both in comfort conditions and under heat and cold stress are based on analysis of the heat balance for the human body, as discussed in Chapter 9 of the 2017 ASHRAE Handbook-Fundamentals. A per- son may find the thermal environment unacceptable or intolerable because of local effects on the body caused by asymmetric radia- tion, air velocity, vertical air temperature differences, or contact with hot or cold surfaces (floors, machinery, tools, etc.). Heat Stress- Thermal Standards Another heat stress indicator for evaluating an environment's heat stress potential is the wet-bulb globe temperature (WBGT), defined as follows: Outdoors with solar load WBGT = 0. 7tnwb + 0.2tg + 0. 1tdb Indoors, or outdoors with no solar load WBGT = 0. 7tnwb + 0.3tg (2) where Coefficients in Equations (1) and (2) represent the fractional contri- butions of the component temperatures. tnwb temperature (no defined range of = naturally ventilated wet-bulb air velocity; different from saturation temperature or psychrometric wet-bulb temperature), °C � = globe temperature (Vernon bulb thermometer, 150 mm diameter), °C tdb = dry-bulb temperature (sensor shaded from solar radiation), °C The WBGT index is an international standard (ISO Standards 7243, 7730, and 7933) for evaluating hot environments. The WBGT index and activity levels should be evaluated on 1 h mean values; that is, WBGT and activity are measured and estimated as time-weighted averages on a 1 h basis for continuous work, or on a 2 h basis when exposure is intermittent. Although recommended by NIOSH, the WBGT has not been accepted as the sole legal standard by the Occu- pational Safety and Health Administration (OSHA), and it may not apply for non-U.S. jurisdictions. The WBGT is generally used in conjunction with other methods to determine heat stress. Exposure limits for heat stress for different levels of physical activity are shown in Figure 2 (NIOSH 1986), which depicts the allowable work regime (in terms of rest periods and work periods each hour) for different levels of work over a range of WBGT. When applying Figure 2, assume that the rest area has the same WBGT as the work area. The curves are valid for workers acclimatized to heat. ASHRAE Standard 62.1 provides some metabolic rates for different activities that can be used with Figure 2. Refer to NIOSH (1986) for recommended WBGT limits for nonacclimatized workers. Chart Type: line 100 200 300 400 500 600 item_01 34°C 32°C 30°C 28°C 26°C 24°C Fig. 2 Recommended Heat Stress Exposure Limits for Heat-Acclimatized Workers [Adapted from NIOSH (1986)] (1) Inc. ASHRAE, 2019 user. single for Licensed | {}
3e0d5428-1d1f-4750-96d4-d09b28ac2ae0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 32.6 2019 ASHRAE Handbook-HVAC Applications (SI) Although Figure 2 is useful for evaluating heat stress exposure limits, it is of limited use for control purposes or for evaluation of comfort. Air velocity and psychrometric wet-bulb measurements are usually needed to specify proper controls, and are only mea- sured indirectly in WBGT determinations. Information on other useful tools, including the heat stress index (HSI), can be found in Chapter 9 of the 2017 ASHRAE Handbook-Fundamentals and in ISO Standards 7243, 7730, and 7933. The thermal relationship between humans and their environment is determined by four independent environmental variables: · Air temperature · Radiant temperatures · Moisture content of the air · Air velocity Together with the rate of internal heat production (metabolic rate) and clothing variables, these factors may combine in various ways to create different degrees of heat stress. The HSI is defined as the percent of the skin that is wetted by perspiration: HSI = EsklE, max 100 where (3) Esk = evaporative heat loss from the skin, W/m2 Emax possible evaporative heat loss from the skin, W/m2 = maximum and incorporates relative contributions of metabolism, radiant heat gain (or loss), convective heat gain (or loss), and evaporative (per- spiration) heat gain (or loss). For supplemental information on eval- uation and control ofheat stress using methods such as reduction of radiation, changes in work/rest pattern, spot cooling, and cooling vests and suits, refer to ACGIH (2013), Brief et al. (1983), Caplan (1980), NIOSH (1986), and Ontario MOL (2009). Heat Exposure Control Control at Source. Heat exposure can be reduced by providing sufficient insulation to hot equipment or locating it outdoors or in zones with general or local exhaust ventilation, covering steaming water tanks, providing covered drains for direct removal of hot water, and maintaining tight joints and valves where steam may escape. Local Exhaust Ventilation. Local exhaust ventilation removes heated air generated by a hot process and/or gases emitted by pro- cess equipment, while removing a minimum of air from the sur- rounding space. Local exhaust systems, including heat exposure control using overhead canopy hoods, are discussed in detail in Chapter 32 and McKernan et al. (2014). Radiation Shielding. In some industries, the major environmen- tal heat load is radiant heat from hot objects and surfaces, such as furnaces, ovens, furnace flues and stacks, boilers, molten metal, hot ingots, castings, and forgings. Because air temperature has no sig- nificant effect on radiant heat flow, ventilation is oflittle help in con- trolling such exposure. The only effective control is to reduce the amount of radiant heat impinging on the workers by insulating or placing radiation shields around the source. Radiation shields are effective in the following forms: · Reflective shielding. Sheets of reflective material or insulating board are temporarily attached to the hot equipment or arranged in a semiportable floor stand. · Absorptive shielding (water-cooled). These shields absorb and remove heat from hot equipment. · Transparent shields. Heat-reflective tempered plate glass, re- flective metal chain curtains, and close-mesh wire screens mod- erate radiation without obstructing the view of hot equipment. · Flexible shielding. Aluminum-treated fabrics give a high degree of radiation shielding. · Protective clothing. Reflective garments such as aprons, gauntlet gloves, and face shields provide moderate radiation shielding. For extreme radiation exposures, complete suits with vortex tube cooling may be required. Ifthe shield is a good reflector, it remains relatively cool in severe radiant heat. Bright or highly polished tinplate, stainless steel, and ordinary flat or corrugated aluminum sheets are efficient and dura- ble. Foil-faced plasterboard, although less durable, reflects well on one side. To be efficient, however, the reflective shield must remain bright. Radiation shields are much more efficient when used in mul- tiple layers; they should reflect the radiant heat back to the primary source, where the resulting hot gases can be removed by local ex- haust. However, unless the shield completely surrounds the primary source, some infrared energy is reflected into the cooler surround- ings and possibly into an occupied area. The direction of reflected heat should be studied to ensure proper shielding installation. Spot Cooling. Ifthe workplace is located near a source of radiant heat that cannot be entirely controlled by radiation shielding, spot cooling can be used. See Chapter 20 in the 2017 ASHRAE Hand- book-Fundamentals and data from spot-cooling diffuser manufac- turers for further information. 4. ENERGY CONSERVATION, RECOVERY, AND SUSTAINABILITY Because of the large air volumes required to ventilate industrial plants, energy conservation and recovery should be practiced, and can provide substantial savings if this practice does not compromise overriding life safety concerns. Therefore, after all critical life safety issues have been adequately addressed, energy recovery should be incorporated into preliminary planning for an industrial plant wherever and whenever it is both safe and practical to deploy. When selecting energy recovery equipment, ensure that materials are compatible with all contaminants and hazardous substances that may be exhausted. Verify the acceptability of the energy recovery method with local codes. In some cases, it is possible to provide unheated or partially heated makeup air to the building. Although most energy conserva- tion and recovery methods in this section apply to heating, the sav- ings possible with cooling systems are similar. The following are some methods of energy conservation and recovery: · In the original design phase, process and equipment insulation and heat shields should be provided to minimize heat loads. Vapor- proofing and reducing the glass area may be required. Exhaust requirements for hoods and processes should be reviewed and kept to a practical, safe minimum; for more on local exhaust systems, see Chapter 32. · Design the supply and exhaust general ventilation systems for optimal operation throughout the year. Provide air as close to the occupied zone as possible without affecting exhaust operation. Clean, recirculated air can be used in winter makeup ifit does not increase the levels of contamination in the space (see the follow- ing bullet points for more details and restrictions) (ACGIH 2013). Supply and exhaust systems may be interlocked together to avoid overpressurization of the space by the supply unit if intermittent extracts are used. · Supply air can be passed through air-to-air, liquid-to-air, or hot- gas-to-air heat exchangers to recover building or process heat. Rotary, regenerative, coil energy recovery (runaround), and air- to-air heat exchangers are discussed extensively in Chapters 25 and 26 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment. Energy recovery is also discussed in Chapters 5 and 11 of ACGIH (2013). · Operate the system for economy if this does not compromise life safety. Although CO2-based demand control ventilation (DCV) is unsuitable for industrial spaces where human activity is not the Inc. ASHRAE, 2019 user. single for Licensed | {}
c9699bc9-d8cc-419e-9e84-27bea016f8f1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Ventilation of the Industrial Environment 32.7 · main reason for ventilating the space (DOE 2004), industrial spaces may offer their own kind of demand control ventilation for providing makeup air to offset process and exhaust hood exhaust volumes. If the space does not contain a potential source of toxic contaminants or hazardous (ignitable) substances, shut such sys- tems down at night, on weekends, or whenever possible, and oper- ate makeup air in balance with the needs of process equipment and exhaust hoods. Keep heating supply air temperatures at the mini- mum, and cooling supply temperatures at the maximum, consis- tent with process needs and employee comfort. Keep the building in pressure balance so that uncomfortable drafts do not necessitate excessive heating. Increase the deadband/control limits If the exhaust air has contaminants that do not pose an unaccept- able health risk, and does not contain a potential source ofhazard- ous (ignitable) substances, then recirculation can be considered. However, even then, contaminant concentrations in recirculated air must be determined so that allowable limits in the space are not exceeded. As recirculated air returns to the space, the concentra- tion of contaminants in the partially filtered return air adds to the contaminant levels already existing in the space. It must be deter- mined whether the concentration increases beyond the allowable time-weighted average (TW A) exposure limit during the period for which the worker is exposed. This period is usually assumed to be 8 h for an 8 h work shift, but could be any period of exposure. Once installed, real-time or periodic monitoring is likely required to sup- port this determination. Depending on the contaminant's toxicity, the monitoring system may be required to perform some form of corrective action or shut down once a target level (a percentage of the safe exposure limit) concentration is attained. Predicted energy cost savings from recirculation should be weighed against the nec- essary costs of air cleaning and monitoring requirements (to include calibration and maintenance of monitoring equipment). Assuming equilibrium has been established, the predicted TWA concentration at the workers' breathing zone can be calculated (ACGIH 2013): QB CB = CG - C M 1 - f + C o - CM f QA + KBCR + 1 - KB CM where (4) CB = TWA worker breathing zone contaminant concentration during recirculation, ppm QB = total ventilation airflow without considering recirculation, m3/s QA = total ventilation airflow including recirculation, m3/s CG = average space concentration if no recirculation, ppm fraction of time worker spends at workstation Co = TWA contaminant concentration at breathing zone of workstation if no recirculation, ppm KB = fraction ofworker breathing zone air that consists ofrecirculated air, 0 to 1.0 CR = recirculated air (after air cleaner) discharge concentration, ppm, or 1 - CE KRCM CR = 1 - 1 - K R (5) = fractional air cleaner efficiency for contaminant CE = (local) exhaust concentration without recirculation, ppm KR = fraction of exhaust air that is recirculated air, 0 to 1.0 CM = replacement air contaminant concentration, ppm 2013). Local exhaust is recirculated through an air cleaner with an efficiency of 0.75. Recirculated air is directed toward the worker spaces, such that KB = 0.5 and KR = 0.8 (more of the recirculated air is locally exhausted than enters the worker's breathing zone). The worker is at the workstation 100% of the time (f = 1). The makeup air has a concentration of 5 ppm (CM), the local exhaust has a concentration of 500 ppm (CE), the space has an average concentration of 20 ppm (CG), and without recirculation the worker's breathing zone is 35 ppm (Co). Solution: The concentration CB at the breathing zone with recirculation is determined from 1 - 0.75 500 - 0.8 5 CR = 155 ppm 1 - 1 - 0.75 0.8 and 4.7 CB = 20 - 5 1 - 1 + 35 - 5 1 + 0.5 155 2.35 + 1 - 0.5 5 = 110 ppm which may or may not exceed the allowable TWA exposure limit of the worker space, depending on the specific contaminant. REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. Other recirculation system examples are given in Chapter 8 of Goodfellow and Tahti (2001). Example 1. An industrial space uses 4.7 m3/s for ventilation, of which 2.35 m3/s is general exhaust and 2.35 m3/s local exhaust (ACGIH ACGIH. 2013. Industrial ventilation: A manual of recommended practice for design, 28th ed. American Conference of Governmental Industrial Hygienists, Cincinnati, OH. Ahn, K., S. Woskie, L. DiBerardinis, and M. Ellenbecker. 2008. A review of published quantitative experimental studies on factors affecting labora- tory fume hood performance. Journal of Occupational and Environmen- tal Hygiene 5(11):735-753. AIHA. 2011. The occupational environment: Its evaluation, control, and management, 3rd ed., vols. 1 and 2. D.H. Anna, ed. American Industrial Hygiene Association, Falls Church, VA. AIHA. 2012. The laboratory ventilation standard. ANSI/AIHA Standard Z9.5-2012. American Industrial Hygiene Association, Falls Church, VA. ASHRAE. 2013. Thermal environmental conditions for human occupancy. ANSI/ASHRAE Standard 55-2013. ASHRAE. 2013. Ventilation for acceptable indoor air quality. ANSI/ ASHRAE Standard 62. 1-2013. ASHRAE. 2013. Ventilation and acceptable indoor air quality in low-rise residential buildings. ANSI/ASHRAE Standard 62.2-2013. BOHS. 1987. Controlling airborne contaminants in the workplace. Techni- cal Guide 7. Science Review Ltd. and H&H Scientific Consultants for British Occupational Hygiene Society, Leeds, U.K. Brief, R.S., S. Lipton, S. Amamnani, and R. W. Powell. 1983. Development of exposure control strategy for process equipment. Annals of the Amer- ican Conference of Governmental Industrial Hygienists (5). Caplan, K.J. 1980. Heat stress measurements. Heating, Piping and Air Con- ditioning (February):55-62. Caplan, K.J., and G. W. Knutson. 1977. The effect of room air challenge on the efficiency of laboratory fume hoods. ASHRAE Transactions 83(1): 141-156. Caplan, K.J., and G. W. Knutson. 1978. Laboratory fume hoods: Influence of room air supply. ASHRAE Transactions 84(1):522-537. Cashdollar, K.L. 2000. Overview of dust explosibility characteristics. Jour- nal of Loss Prevention in the Process Industries 13(3):183-199. Avail- able from www.ofc.govimicshinining/works/covershershee1051 .html. Chen, Q., and L. Glicksman. 2003. System performance evaluation and design guidelines for displacement ventilation. ASHRAE. DHHS. 1986. Advanced industrial hygiene engineering. PB87-229621. U.S. Department of Health and Human Services, Cincinnati, OH. DOE. 2004. Demand-controlled ventilation using CO2 sensors. Federal Technology Alert DOE/EE-0293. U.S. Department of Energy, Wash- ington, D.C. Available at permanent access.gpo.govips99139ffa_ca2 .pdf. Goodfellow, H.D. 1985. Advanced design ofventilation systemsfor contam- inant control. Elsevier Science B. V., Amsterdam. Inc. ASHRAE, 2019 user. single for Licensed | {}
07036b6b-86c9-4fa6-8a2f-e754e4bd44e8 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 32.8 2019 ASHRAE Handbook-HVAC Applications (SI) Goodfellow, H., and E. Tahti, eds. 2001. Industrial ventilation design guide- book. Academic Press, New York. ISO. 1989. Hot environments- Estimation of the heat stress on working man, based on the WBGT-index (wet bulb globe temperature). Standard 7243. International Organization for Standardization, Geneva. ISO. 2005. Ergonomics of the thermal environment-Analytical determina- tion and interpretation of thermal comfort using calculation of the PMV and PPD indices and local thermal comfort criteria. Standard 7730. Inter- national Organization for Standardization, Geneva. ISO. 2004. Ergonomics of the environment- Analytical determination and interpretation ofheat stress using calculation of the predicted heat strain. Standard 7933. International Organization for Standardization, Geneva. McKernan, J.L., M.J. Ellenbecker, C.A. Holcroft, and M.R. Petersen. 2014. Development and validation of proposed ventilation equations for improved exothermic process control. 2014 ASHRAE Winter Confer- ence, Paper NY-14-C069. National Safety Council. 2012. Fundamentals of industrial hygiene, 6th ed. Chicago, IL. NFPA. 2011. Standard on fire protection for laboratories using chemicals. Standard 45-2011. National Fire Protection Association, Quincy, MA. NFPA. 2013. Purged and pressurized enclosures for electrical equipment. Standard 496-2013. National Fire Protection Association, Quincy, MA. NIOSH. 1986. Criteria for a recommended standard: Occupational exposure to hot environments. CDC/NIOSH Publication 86-113. National Insti- tute for Occupational Safety and Health, Washington, D.C. Available from www.cdc.gov/niosh/docs/86-113/. Ontario MOL. 2009. Heat stress (health and safety guidelines). Ontario Ministry of Labor. Available from www.labour.gov.on.ca/english/hs /pubs/gl_heat.php. Tseng, L.-C., R.F. Huang, and C.-C. Chem. 2010. Significance offace veloc- ity fluctuation in relation to laboratory fume hood performance. Indus- trial Health 48(1):43-51. Available at www.jniosh.go.jp/en/indu_hel/pdff /IH_48_1_43.pdf. BIBLIOGRAPHY Alden, J.L., and J.M. Kane. 1982. Design of industrial ventilation systems, 5th ed. Industrial Press, New York. Anderson, R., and M. Mehos. 1988. Evaluation of indoor air pollutant con- trol techniques using scale experiments. ASHRAE Indoor Air Quality Conference. ASHRAE. 2012. Method of testing general ventilation air-cleaning devices for removal efficiency by particle size. ANSI/ASHRAE Standard 52.2- 2012. Balchin, N.C., ed. 1991. Health and safety in welding and allied processes, 4th ed. Abington Publishing, Cambridge. Bartknecht, W. 1989. Dust explosions: Course, prevention, protection. Springer- Verlag, Berlin. Burgess, W.A., M.J. Ellenbecker, and R.D. Treitman. 1989. Ventilation for control ofthe work environment. John Wiley & Sons, New York. Cawkwell, G.C., and H.D. Goodfellow. 1990. Multiple cell ventilation model with time-dependent emission sources. Proceedings of the 2nd International Conference on Engineering Aero- and Thermodynamics of Ventilated Rooms, Al-9, Oslo. Chamberlin, L.A. 1988. Use of controlled low velocity air patterns to improve operator environment at industrial work stations. M.A. thesis, University of Massachusetts. Cole, J.P. 1995. Ventilation systems to accommodate the industrial process. Heating, Piping, Air Conditioning (May). Constance, J.D. 1983. Controlling in-plant airborne contaminants. Marcel Dekker, New York. Cralley, L. V., andL.J. Cralley, eds. 1986. Patty 's industrial hygiene and tox- icology, vol. 3: Industrial hygiene aspects of plant operations. John Wiley & Sons, New York. EC. 1994. Directive 94/9/EC on equipment and protective systems intended for use in potentially explosive atmospheres (ATEX). European Commis- sion, Brussels, Belgium. Available from ec.europa.eu/enterprise/sectors /mechanical/Cocumentalegisiatizationa/index_extin EC. 1999. Directive 99/92/EC on minimum requirements for improving the safety and health protection ofworkers potentially at riskfrom ex- plosive atmospheres. European Commission, Brussels, Belgium. Avail- able from oo-/eversunquallegal-comentENTXT/Mer>CHLERSU99 Fanger, P.O. 1982. Thermal comfort. Robert E. Krieger, Malabar, FL. Flagan, R.C., and J.H. Seinfeld. 1988. Fundamentals of air pollution engi- neering. Prentice-Hall, Englewood Cliffs, NJ. Godish, T. 1989. Indoor airpollution control. Lewis Publishers, Chelsea, MI. Goldfield, J. 1980. Contaminant concentration reduction: General ventila- tion versus local exhaust ventilation. American Industrial Hygienists Association Journal 41(November). Goodfellow, H.D. 1986. Proceedings of Ventilation '85. Elsevier Science B.V. · Amsterdam. Goodfellow, H.D. 1987. Encyclopedia ofphysical science and technology, vol. 14: Ventilation, industrial. Academic Press, San Diego, CA. Goodfellow, H.D., and J. W. Smith. 1982. Industrial ventilation-A review and update. American Industrial Hygiene Association Journal 43 (March):175-184. Harris, R.L. 1988. Design of dilution ventilation for sensible and latent heat. Applied Industrial Hygiene 3(1). Hayashi, T., R.H. Howell, M. Shibata, and K. Tsuji. 1987. Industrial venti- lation and air conditioning. CRC, Boca Raton, FL. Heinsohn, R.J. 1991. Industrial ventilation engineering principles. John Wiley & Sons, New York. Holcomb, M.L., and J.T. Radia. 1986. An engineering approach to feasibil- ity assessment and design of recirculating exhaust systems. Proceedings of Ventilation '85. Elsevier Science B. V., Amsterdam. HSE. 2013. Control of substances hazardous to health regulations. Health and Safety Executive, London, U.K. Jackman, R. 1991. Displacement ventilation. Presented at CIBSE National Conference (April), University of Kent, Canterbury. Laurikainen, J. 1995. Displacement ventilation system design method. Sem- inar presentations, Part 2. INVENT Report 46. FIMET, Helsinki. Licht, W. 1988. Air pollution control engineering, 2nd ed. Marcel Dekker, New York. McDermott, H.J. 1985. Handbook of ventilation for contaminant control, 2nd ed. Ann Arbor Science Publishers, Ann Arbor, MI. Mehta, M.P., H.E. Ayer, B.E. Saltzman, and R. Ronk. 1988. Predicting con- centration for indoor chemical spills. Presented at ASHRAE Indoor Air Quality Conference. NFPA. [Annual.] National fire codesⓇ. National Fire Protection Associa- tion, Quincy, MA Olesen, B. W , and A.M. Zhivov. 1994. Evaluation ofthermal environment in industrial work spaces. ASHRAE Transactions 100(2):623-635. Pozin, G.M. 1993. Determination ofthe ventilating effectiveness in mechan- ically ventilated spaces. Proceedings ofthe 6th International Conference on Indoor Air Quality (IAQ '93), Helsinki. Room Vent '90. 1990. Proceedings of the 2nd International Conference on Engineering Aero- and Thermodynamics of Ventilated Rooms, Oslo. Room Vent '92. 1992. Proceedings of the 3rd International Conference on Engineering Aero- and Thermodynamics of Ventilated Rooms, Aalborg, Denmark. Room Vent '94. 1994. Proceedings of the 4th International Conference on Engineering Aero- and Thermodynamics of Ventilated Rooms, Krakow. Room Vent '96. Proceedings ofthe 5th International Conference on Air Dis- tribution in Rooms, Yokohama. Schroy, J.M. 1986. A philosophy on engineering controls for workplace pro- tection. Annals of Occupational Hygiene 30(2):231-236. Shilkrot, E.O., and A.M. Zhivov. 1996. Zonal model for displacement ven- tilation design. Room Vent '96, Proceedings of the 5th International Con- ference on Air Distribution in Rooms, vol. 2. Yokohama. Skaret, E. 1985. Ventilation by displacement- Characterization and design applications. Elsevier Science B. V., Amsterdam. Skaret, E., and H.M. Mathisen. 1989. Ventilation efficiency-A guide to efficient ventilation. ASHRAE Transactions 89(2B):480-495. Skistad, H. 1994. Displacement ventilation. Research Studies Press, John Wiley & Sons, West Sussex, U.K. Stephanov, S.P. 1986. Investigation and optimization of air exchange in industrial halls ventilation. Proceedings of Ventilation '85. Elsevier Sci- ence B. V., Amsterdam. Vincent, J.H. 1989. Aerosol sampling, science and practice. John Wiley & Sons, Oxford, U.K. Volkavein, J.C., M.R. Engle, and T.D. Raether. 1988. Dust control with clean air from an overhead air supply island (oasis). Applied Industrial Hygiene 3(August):8. Wadden, R.A., and P.A. Scheff 1982. Indoor air pollution: Characteriza- and control. John & Sons, New York. L0092. tion, prediction, Wiley Inc. ASHRAE, 2019 user. single for Licensed | {}
10bf024b-08e8-472c-9cac-4e1b67aae837 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Ventilation of the Industrial Environment 32.9 Wilson, D.J. 1982. A design procedure for estimating air intake contamina- tion from nearby exhaust vents. ASHRAE Transactions 89(2A):136-152. Zhivov, A.M., and B. W. Olesen. 1993. Extending existing thermal comfort standards to work spaces. Proceedings of the 6th International Confer- ence on Indoor Air Quality (IAQ '93), Helsinki. Zhivov, A.M. E.O. Shilkrot, P.V. Nielsen, and G.L. Riskowski. 1997. Dis- placement ventilation design. Proceedings ofthe 5th International Sym- posium on Ventilation for Contaminant Control (Ventilation '97), vol. I, Ottawa. Inc. ASHRAE, 2019 user single for Licensed Related Commercial Resources | {}
9a3646ad-1495-4334-9ef7-1494510e6c4c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 33 INDUSTRIAL LOCAL EXHAUST SYSTEMS ¦ Local Exhaust Fundamentals ¦ 32.2 ¦ ¦ --- ¦ --- ¦ ¦ Air Movement in Vicinity of Local Exhaust ¦ 32.3 ¦ ¦ Other Local Exhaust System Components ¦ 32.6 ¦ ¦ Operation ···· ¦ 32.9 ¦ I NDUSTRIAL exhaust ventilation systems contain, collect, and remove airborne contaminants consisting of particulate matter (dusts, fumes, smokes, fibers), vapors, and gases that can create a hazardous, unhealthy, or undesirable atmosphere. Exhaust systems can also salvage usable material, improve plant housekeeping, and capture and remove excessive heat or moisture. Industrial exhaust systems must comply with ASHRAE Standard 62.1 and other stan- dards as required [e.g., National Fire Protection Agency (NFPA) stan- dards]. Special Warning: Certain industrial spaces may contain flam- mable, combustible and/or toxic concentrations of vapors or dusts under either normal or abnormal conditions. In spaces such as these, there are life safety issues that this chapter may not completely address. Special precautions must be taken in accordance with requirements ofrecognized authorities such as the National Fire Pro- tection Association (NFPA), Occupational Safety and Health Administration (OSHA), and American National Standards Institute (ANSI). In all situations, engineers, designers, and installers who encounter conflicting codes and standards must defer to the code or standard that best addresses and safeguards life safety. Local Exhaust Versus General Ventilation Local exhaust ventilation systems can be the most performance- effective and cost-effective method of controlling air pollutants and excessive heat. For many operations, capturing pollutants at or near their source is the only way to ensure compliance with occupational exposure limits that are measured within the worker's breathing zone. When properly designed, local exhaust ventilation optimizes ventilation exhaust airflow, thus optimizing system acquisition costs associated with equipment size and operating costs associated with energy consumption and makeup air tempering. Chapters 2 and 3 in ACGIH (2013) also discuss this topic at length. In some industrial ventilation designs, the emphasis is on filtering air captured by local exhausts before exhausting it to the outdoors or returning it to the production space. As a result, these systems are evaluated according to their filter efficiency or total particulate removal. However, if an insufficient percentage of emissions are captured, the degree of air-cleaning efficiency sometimes becomes irrelevant. For a process exhaust system in the United States, the design engineer must verify ifthe system is permitted by the 1990 Clean Air Act. For more information, see the Environmental Protection Agency's web site (www.epa.gov/air/caa/). The pollutant-capturing efficiency of local ventilation systems depends on hood design, the hood' s position relative to the source of contamination, temperature of the source being exhausted, and the induced air currents generated by the exhaust airflow. Selection and positioning of the hood significantly influence initial and operating costs of both local and general ventilation systems. In addition, poorly designed and maintained local ventilation systems can cause The preparation of this chapter is assigned to TC 5.8, Industrial Ventilation Systems. deterioration of building structures and equipment, negative health effects, and decreased worker productivity. No local exhaust ventilation system is 100% effective in capturing pollutants and/or excess heat. In addition, installation oflocal exhaust ventilation system may not be possible in some circumstances, because of the size, mobility, or mechanical interaction requirements of the process. In these situations, general ventilation is needed to dilute pollutants and/or excess heat. Where pollutants are toxic or present a health risk to workers, local exhaust is the appropriate approach, and dilution ventilation should be avoided. Air supplied by the general ventilation system is usually conditioned (heated, humid- ified, cooled, etc.). Supply air replaces air extracted by local and gen- eral exhaust systems and improves comfort conditions in the occupied zone. Chapter 1 1 of the 2017 ASHRAE Handbook -Fundamentals COV- ers definitions, particle sizes, allowable concentrations, and upper and lower explosive limits of various air contaminants. Chapter 31 of this volume, Goodfellow and Tahti (2001), and Chapter 2 of ACGIH (2013) detail steps to determine air volumes necessary to dilute con- taminant concentration using general ventilations. Sufficient makeup air must be provided to replace air removed by the exhaust system. If replacement air is insufficient, building pressure becomes negative relative to atmospheric pressure and allows air to infiltrate through open doors or window cracks, and can reverse flow through combustion equipment vents. A negative pressure as little as 12 Pa can cause drafts and might cause back- drafts in combustion vents, thereby creating potential health and safety hazards. From the sustainability perspective, a negative plant static pressure can also result in excessive energy use. If workers near the plant perimeter complain about cold drafts, unit heaters are often installed. Heat from these units often is drawn into the plant interior, overheating the interior. Too often, this overheating is addressed by exhausting more air from the interior, causing increased negative pressure and more infiltration. Negative plant pressure reduces the exhaust volumetric flow rate because of increased system resistance, which can also decrease local exhaust efficiencies or require additional energy to overcome the increased resistance. Wind effects on building balance may also play a role, and are discussed in Chapter 24 of the 2017 ASHRAE Handbook - Fundamentals. Exhaust system discharge may be regulated under various fed- eral, state, and local air pollution control regulations or ordinances. These regulations may require exhaust air treatment before dis- charge to the atmosphere. Chapter 30 of the 2016 ASHRAE Hand- book-HVAC Systems and Equipment provides guidance and recommendations for discharge air treatment. Positive-pressure plants and balanced plants (those with equal exhaust and replacement air rates) use less energy. However, ifthere are clean and contaminated zones in the same building, the desired airflow direction is from clean to dirty, and zone boundary construc- tion and pressure differentials should be designed accordingly. 33.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
5c7c103b-354b-455c-bb1e-dc318fb46bde | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 33.2 2019 ASHRAE Handbook- -HVAC Applications (SI) 1. LOCAL EXHAUST FUND AMENTALS System Components Local exhaust ventilation systems typically consist of the follow- ing basic elements: · Hood to capture pollutants and/or excessive heat · Ducted system to transport polluted air to air cleaning device or building exhaust · Air-cleaning device to remove captured pollutants from the air- stream for recycling or disposal · Air-moving device (e.g., fan or high-pressure air ejector), which provides motive power to generate the hood capture velocity plus overcome exhaust ventilation system resistance · Exhaust stack, which discharges system air to the atmosphere System Classification Contaminant Source Type. Knowing the process or operation is essential before a local exhaust hood system can be designed. Hood Type. Exhaust hoods are typically round, rectangular, or slotted to accommodate the geometry of the source. Hoods are either enclosing or nonenclosing (Figure 1). Enclosing hoods pro- vide more effective and economical contaminant control because their exhaust rates and the effects of room air currents are minimal compared to those for nonenclosing hoods. Hood access openings for inspection and maintenance should be as small as possible and out of the natural path of the contaminant. Hood performance (i.e., how well it captures the contaminant) should ideally be verified by an industrial hygienist. A nonenclosing hood can be used if access requirements make itnecessary to leave all or part ofthe process open. Careful attention must be paid to airflow patterns and capture velocities around the process and hood (under dynamic conditions) and to the process characteristics to make nonenclosing hoods effective. The use of moveable baffles, curtains, strip curtains, and brush seals may allow the designer to increase the level of enclosure without interfering with the work process. The more of the process that can be enclosed, the less exhaust airflow required to control the contaminant(s). System Mobility. Local exhaust systems with nonenclosing hoods can be stationary (i.e., having a fixed hood position), move- able, portable, or built-in (into the process equipment). Moveable hoods are used when process equipment must be accessed for repair and loading and unloading of materials (e.g., in electric ovens for melting steel). The portable exhaust system shown in Figure 2 is commonly used for temporary exhausting of fumes and solvents in confined spaces or during maintenance. It has a built-in fan and filter and an exhaust hood connected to a flexible hose. Built-in local exhaust ![image](/image/placeholder) ENCLOSING HOOD HOOD BELT 0 BELT HOPPER HOPPER ENCLOSING HOOD NONENCLOSING HOOD Fig. 1 Enclosing and Nonenclosing Hoods (Adapted from ACGIHⓇ, Industrial Ventilation: A Manual ofRecom- mended Practice, 27th ed. Copyright 2010. Reprinted with permission.) systems are commonly used to evacuate welding fumes, such as hoods built into stationary or turnover welding tables. Lateral ex- haust hoods, which exhaust air through slots on the periphery of open vessels, such as those used for galvanizing metals, are another example of built-in local exhaust systems. Effectiveness of Local Exhaust The most effective hood design uses the minimum exhaust air- flow rate to provide maximum contaminant control without com- promising operator capability to complete the work task. Capture effectiveness should be high, but it is difficult and costly to develop hoods with efficiencies approaching 100%. Makeup air supplied by general ventilation to replace exhausted air can dilute contaminants that are not captured by the hood. Enclosing more of the process reduces the need to protect against contaminant escape through cross drafts, convective currents, or process-generated contaminant momentum. In turn, this reduces the exhaust airflow required to control the contaminant(s). Capture Velocity. Capture velocity is the air velocity required to entrain contaminants at the point of contaminant generation up- stream of a hood. The contaminant enters the moving airstream near the point of generation and is carried along with the air into the hood. Designers use a designated capture velocity Vc to determine a volumetric flow rate to draw air into the hood. Table 1 shows ranges of capture velocities for several industrial operations. These figures are based on successful experience under ideal conditions. Once capture velocity upstream of the hood and hood position relative to the source are known, then the hood flow rate can be determined for the particular hood design. Velocity distributions for specific hoods must be known or determined. Hood v olumetric Flow Rate. For a given hood configuration and capture velocity, the exhaust volumetric flow rate (the airflow rate that allows contaminant capture) can be calculated as Q。 = V。 A⌀ (1) where Q。 = exhaust volumetric flow rate, m3/s V⌀ = average air velocity in hood opening that ensures capture velocity at point of contaminant release, m/s Ao = hood opening area, m2 Low face velocities require that supply (makeup) air be as uni- formly distributed as possible to minimize the effects of room air currents. This is one reason replacement air systems must be designed with exhaust systems in mind. Air should enter the hood ![image](/image/placeholder) Inc. ASHRAE, 2019 user. single for Licensed Fig. 2 Portable Fume Extractor with Built-in Fan and Filter | {}
fd4dc2f6-450c-4160-8675-038b1606d5fd | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Industrial Local Exhaust Systems 33.3 Table 1 Range of Capture (Control) Velocities ¦ Condition of Contaminant Dispersion ¦ Examples ¦ Capture ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ Examples ¦ Velocity, m/s ¦ ¦ Released with essentially no velocity into still air ¦ Evaporation from tanks, degreasing, plating ¦ 0.25 to 0.5 ¦ ¦ Released at low velocity into moderately still air ¦ Container filling, low-speed conveyor transfers, welding ¦ 0.5 to 1.0 ¦ ¦ Active generation into zone of rapid air motion ¦ Barrel filling, chute loading of conveyors, crushing, cool shakeout ¦ 1.0 to 2.5 ¦ ¦ Released at high velocity into zone of very rapid air motion ¦ Grinding, abrasive blasting, tumbling, hot shakeout ¦ 2.5 to 10 ¦ Note: In each category above, a range of capture velocities is shown. The proper choice of values depends on several factors (Alden and Kane 1982): Lower End of Range Upper End of Range 1. Room air currents favorable to 1. Distributing room air currents capture 2. Contaminants oflow toxicity or 2. Contaminants ofhigh toxicity of nuisance value only 3. Intermittent, low production 4. Large hood; large air mass in motion 3. High production, heavy use 4. Small hood; local control only ![image](/image/placeholder) 45° MINIMUM 45° MINIMUM SOLID ANGULAR SPLIT BAFFLE BAFFLE BAFFLE OR FILTERS Fig.3 Use of Interior Baffles to Ensure Good Air Distribution uniformly. Hood flanges, side baffles, and interior baffles are some- times necessary (Figure 3). Airflow requirements for maintaining effective capture velocity at a contaminant source also vary with the distance between the source and hood. Chapter 3 of ACGIH (2013) provides methodol- ogy for estimating airflow requirements for specific hood configu- rations and locations relative to the contaminant source. Airflow near the hood can be influenced by drafts from supply air jets (spot coolingjets) or by turbulence of the ambient air caused by jets, upward/downward convective flows, moving people, mobile equipment, and drafts from doors and windows. Process equipment may be another source of air movement. For example, high-speed rotating machines such as pulverizers, high-speed belt material transfer systems, falling granular materials, and escaping compressed air from pneumatic tools all produce air currents. These factors can significantly reduce the capturing effectiveness of local exhaust systems and should be accounted for in the exhaust system design. ![image](/image/placeholder) PROCESS PROCESS SLOT GOOD BAD Fig. 4 Influence of Hood Location on Contamination of Air in the Operator's Breathing Zone (Adapted from ACGIHⓇ, Industrial Ventilation: A Manual of Recom- mended Practice, 28th ed. Copyright 2013.) Exhausted air may contain combustible pollutant/air mixtures. If it does, the amount by which the exhaust airflow rate should be increased to dilute combustible mixture must be verified to meet the requirements ofNational Fire Protection Association (NFPA) Stan- dards 86 and 329. Principles of Hood Design Optimization Numerous studies of local exhaust systems and common prac- tices have led to the following hood design principles: · Hood location should be as close as possible to the source of con- tamination. · The hood opening should be positioned so that it causes the con- taminant to deviate the least from its natural path. · The hood should be located so that the contaminant is drawn away from the operator's breathing zone. · Hood size must be the same as or larger than the cross section of flow entering the hood. If the hood is smaller than the flow, a higher volumetric flow rate is required. · W orker position with relation to contaminant source, hood design, and airflow path should be evaluated based on the princi- ples given in Chapters 3 and 10 of ACGIH (2013). · Canopy hoods (Figure 4) should not be used where the operator must bend over a tank or process (ACGIH 2013). 2. AIR MOVEMENT IN VICINITY OF LOCAL EXHAUST Air capture velocities in front of the hood opening depend on the exhaust airflow rate, hood geometry, distance from hood face and surfaces surrounding the hood opening. Figure 5 shows velocity contours for an unflanged round duct hood. Studies have established the similarity of velocity contours (expressed as a percentage of the hood entrance velocity) for hoods with similar geometry (Dalla- Valle 1952). Figure 6 shows velocity contours for a rectangular hood with an aspect ratio (width divided by length) of 0.333. The profiles are similar to those for the round hood but are more elon- gated. If the aspect ratio is lower than about 0.2 (0.15 for flanged openings), the flow pattern in front of the hood changes from approximately spherical to approximately cylindrical. Velocity decreases rapidly with distance from the hood; per DallaValle, velocity decreases on the order of 1/(distance from suction inlet squared). Inc. ASHRAE, 2019 user. single for Licensed The design engineer should consider side drafts and other sources of air movement close to the capture area of a local exhaust hood. Caplan and Knutson (1977, 1978) found that air movement in front oflaboratory hoods can cause contaminants to escape from the | {}
43b8607a-ac9c-4590-98c9-c3274a1acd6e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 33.4 2019 ASHRAE Handbook-HVAC Applications (SI) X-Axis: OUTWARD DISTANCE FROM PIPE MOUTH, % OF D Y-Axis: PIPE DIAMETER D Chart Type: line (0) (10) (20) (30) (40) (50) (60) (70) (80) (90) (100) (110) (120) item_01 70% 70% 60% 50% 40% 30% 20% 10% 10% 5% 5% 5% 5% Fig. 5 Velocity Contours for Plain Round Opening (Alden and Kane 1982; used by permission) hood and into the operator's breathing zone. In industrial applica- tions, it is common to see large fans blowing air onto workers who are located in front of an exhaust hood. This can render the local exhaust hood ineffective to the point that no protection is provided for the worker and/or their adjacent co-workers. Pressure Loss in Hoods and Ducts A vena contracta forms in the entrance of the hood or duct and produces a pressure loss, which can be described using pressure loss coefficient C。 or a static pressure entry loss (ACGIH 2013). When air enters a hood, the pressure loss, called hood entry loss, may have several components, depending on the hood's complexity. Simple hoods usually have a single pressure loss coefficient CL specified, defined as Fig. 6 Velocity Contours for Plain Rectangular Opening with Sides in a 1:3 Ratio (Alden and Kane 1982; used by permission) X-Axis: OUTWARD DISTANCE FROM HOOD MOUTH, % OF W Y-Axis: OUTWARD DISTANCE FROM HINDS Chart Type: line (0) (20) (40) (60) (80) (100) (120) (140) (160) item_01 100% OF W 100% OF W 100% OF W 100% OF W 100% OF W 100% OF W 100% OF W 100% OF W 100% OF W Inc. ASHRAE, 2019 user. single for Licensed Ps = -Pv (3) P CL = N s, h (2) where CL = pressure loss coefficient depending on hood type and geometry, dimensionless 성 V 2/2, dynamic pressure inside duct caused by moving airstream (constant in duct after vena contracta), Pa, where is air density, kg/m3 Ps.h pressure in hood duct because of velocity pressure increase static and hood entry loss, Pa More information on loss factors and the design of exhaust ductwork is in Chapter 21 of the 2017 ASHRAE Handbook Funda- mentals, ACGIH (2013), and Brooks (2001). The loss coefficient CL is different from the hood entry loss coef- ficient. The entry loss coefficient C。 relates duct total pressure loss to duct velocity pressure. From Bernoulli's equation, hood total pressure is approximately zero at the entrance to the hood, and therefore the static pressure is equal to the negative of the velocity pressure: Static pressure in the hood/duct is the static pressure (velocity pressure) plus the head loss, which is expressed as a fraction of the velocity pressure, as Ps,h = Pv + CoPv Rearranged, the hood/duct static pressure Ps,h suction) for (hood hoods is (4) and the change in total pressure is Ps,h二 (1 + Co)Pv Pt=Ps.h -Pv = CoPv Loss coefficients C⌀ for various hood shapes are given in Figure 7. For tapered hoods, Figure 5 shows that the optimum hood entry angle to minimize entry loss is 45°, but this may be impractical in many situations because of the required transition length. A 90° angle, with a corresponding loss factor of 0.25 (for rectangular openings), is typical for many tapered hoods. (5) Example 1. A nonenclosing side-draft flanged hood (Figure 8) with face dimensions of0.45 by 1.2 m rests on the bench. The required volumetric flow rate is 0.74 m3/s. The duct diameter is 230 mm; this gives a duct velocity of 17.6 m/s. The hood is designed such that the largest angle of transition between the hood face and the duct is 90°. What is the suction pressure (static pressure) for this hood? Assume air density at 22°C. ⑥ | {}
7dadd0c3-dc9d-43e0-b2e7-8a5ef73aa92b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Industrial Local Exhaust Systems 33.5 ![image](/image/placeholder) A. PLAIN DUCT END B. FLANGED DUCT END C. ORIFICE AT DUCT END C。 = 1.0 C。 = 0.50 C。 = 1.78 (USE Pv OF ORIFICE) 1.10 1.00 0 C° 0.90 0.80 FACTOR FACE AREA AT LEAST 2 TIMES 0.70 DUCT AREA 0.60 LOSS RECTANGULAR 0.50 AND SQUARE 0.40 0.30 0.20 FACE AREA AT ENTRY LEAST 2 TIMES ROUND 0.10 DUCT AREA 0 0.00 0 20 40 60 80 100 120 140 150 160 0 INCLUDED ANGLE IN DEGREES D. TAPERED HOODS FLANGED OR UNFLANGED: ROUND, SQUARE, OR RECTANGULAR 0 IS THE MAJOR ANGLE ON RECTANGULAR HOODS Fig. 7 Entry Losses for Typical Hoods Inc. ASHRAE, 2019 user. single for Licensed ![image](/image/placeholder) BENCH WORK SURFACE EXHAUST INTAKE Fig. 8 Hood on Bench Solution: The two transition angles cannot be equal. Whenever this is true, the larger angle is used to determine the loss factor from Figure 7. Because the transition piece originates from a rectangular opening, the curve marked "rectangular" must be used. This corresponds to a loss factor of 0.25. The duct velocity pressure is 2 V2 1.19 17.6 Pv = = 184 Pa 2 2 From Equation (5), Ps,h = (1 + 0.25)(184) = 230 Pa Compound Hoods. Losses for multislot hoods (Figure 9) or single-slot hoods with a plenum (compound hoods) must be ana- lyzed somewhat differently. The slots distribute air over the hood face and do not influence capture efficiency. Slot velocity should be approximately 10 m/s to provide required distribution at minimum energy cost; plenum velocities are typically 50% of slot velocities (approximately 5 m/s). Higher velocities dissipate more energy and can cause hot spots in the face of the hood. ![image](/image/placeholder) EXHAUST INTAKE SLOTS Fig. 9 Multislot Nonenclosing Hood Losses occur when air passes through the slot and when air enters the duct. Because the velocities, and therefore the velocity pres- sures, can be different at the slot and at the duct entry locations, the hood suction must reflect both losses and is given by Ps,h = Pv + (CoPv)s +(CoPv)d (7) Example 2. A multislot hood has three slots, each 25 by 1000 mm. At the top of the plenum is a 90° transition into the 250 mm duct. The volu- metric flow rate required for this hood is 0.78 m3/s. Determine the hood suction (static pressure). Assume air density at 22°C. where the first Pv is generally the higher of the two velocity pres- sures, S refers to the slot, and d refers to the duct entry location. Solution: The slot velocity Vs is 0.78 Vs = 으 = = 10.4 m/s A 3 0.025 1 which is near the minimum slot velocity of 10 m/s. Substituting this velocity, The duct area is 0.0491 m2. Therefore, duct velocity and velocity pres- sure are V 2 2 1.19 10.4 Pv = = = 64.4 Pa 2 2 Vd= Q/A 0.78 Va = = 15.9 m/s 0.0491 Substituting this velocity, 2 1.19 15.9 Pv = 150.4 Pa 2 For a 90° transition into the duct, the loss factor is 0.25. For the slots, the loss factor is 1.78 (Figure 7). The duct velocity pressure is added to the sum of the two losses because it is larger than the slot velocity pres- sure. Using Equation (7), Ps,h = 150.4 + (1.78)(65) + (0.25)(150.4) = 303.7 Pa Exhaust volume requirements, minimum duct velocities, and entry loss factors for many specific operations are given in Chapter 10 of ACGIH (2013). | {}
6ed70d29-56c3-40c8-b98f-8c839eb77b7a | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 33.6 2019 ASHRAE Handbook- -HVAC Applications (SI) Overhead Canopy Hoods Ifa hot work process cannot be completely enclosed, place a can- opy hood above the process so that the contaminant convectively moves toward the hood. Canopy hoods should be applied and designed with caution to avoid drawing contaminants across the operator's breathing zone (see Figure 4). The hood's height above the process should be minimized to reduce total exhaust airflow rate. Efficiencies in ventilation capture can be gained when venti- lating heated processes with canopy hoods, because heated air naturally moves upward because of its reduced density (i.e., buoy- ancy). Canopy hoods are most effective when contaminant is released over a well-defined area, and the contaminant is entrained in the rising, buoyant plume. Room cross drafts can substantially deflect the rising plume when it is created by a low-temperature process, or when cross drafts are greater than 0.25 m/s between the process and the canopy inlet. When determining proper hood selec- tion and design parameters, carefully consider process informa- tion, such as required worker access to the process, process-related material movement within the plume, and the hazard potential of the contaminants associated with the process. Canopy hoods without side walls are the least effective and effi- cient method of controlling hot process plumes. The limitation of any hood design with distance between the hood face and surface of the source is the ability of cross drafts to interfere with capturing contaminants rising from the hot process. Where cross drafts greater than 0.25 m/s are present, hood designs should include side walls. At a minimum, one side wall should be included in the hood design on the side of the process where the cross draft originates (upstream side). Canopy Hoods with Sidewalls When side walls are included, or when the process is close to a structural wall, the plume may attach to the wall. In this event, the plume entrainment volume is reduced compared to that in an unbounded plume, and the resulting flow in the plume is reduced to halfthe flow of an unbounded plume. Ifthere are two walls attached at a right angle, the flow is reduced to 1/4 of the unbounded plume flow (Nielsen 1993). Low Canopy Hoods Whenever the distance between a canopy hood and the hot source is within 0.9 m or the source diameter, whichever is smaller, this hood is considered to be a low canopy hood. Its close proximity to the source does not allow sufficient time for the plume to expand; thus, the diameter or cross section of the hot air column is approxi- mately the same as the source. Under this design scenario, the diam- eter or side dimensions of the hood need only be about 0.3 m larger than the source diameter at its widest cross-section (Hemeon 1963, 1999). For rectangular sources, rising plumes may be better con- trolled if the hood shape reflects that of the source. In this circum- stance, perform the hood airflow and design calculations as for a cir- cular source, once for the length and once for the width dimensions. High Canopy Hood Use as Redundant Control Measure The high canopy hood without side walls is the least favorable canopy design. The design can be used as a redundant measure for controlling large-volume process plumes. High canopy hoods are not recommended as a primary control measure for heated pro- cesses, because of the large volumes of air displaced to remove pol- lutants from the workplace. For example, arc furnace charging has a limited duration, and restricted canopy hood use while the furnace is being charged reduces the required volume of replacement air. Ideally, high canopy hood faces without walls should be round, because rising air from point sources and compact shapes (i.e., not line sources) becomes circular in cross section as it rises (Bill and ![image](/image/placeholder) WIL ≥ 0.2 < 0.2 WIL W A. SIDEDRAFT HOOD B. SLOT HOOD Fig. 10 Sidedraft Hood and Slot Hood on Tank Gebhart 1975). This occurs because turbulence sweeps the plume edges inward to a minimal volume. However, it is more cost effec- tive to manufacture and install square or rectangular hoods. Baffles are recommended at the face of rectangular canopy hoods to approximate the area of a round hood face. Ventilation Controls for Large-Scale Hot Processes Equations to approximate the velocity, area, and volumetric flow of rising air above a large-scale cylindrical heated process with excess air temperatures ( t 92°C) are available from several sources (ACGIH 2013; Goodfellow 1985; Hemeon 1963, 1999; U.S. Public Health Service 1973). These equations derive from compilation of empirical research by Hemeon and others, and are useful for traditional large-scale, high-temperature processes (e.g., arc furnaces, tapping operations). Ventilation Controls for Small-Scale Hot Processes New equations to approximate the velocity, area, and volumetric flow of the rising air above a small-scale heated process have been validated within a range of excess air temperatures (-1 K t 30 K) (McKernan and Ellenbecker 2007; McKernan et al. 2007a, 2007b). These equations are based on modern research applicable to designing engineering controls for heated processes, as well as his- toric work by Hemeon and others (Goodfellow 1985; Hemeon 1963, 1999; U.S. Public Health Service 1973). They are particularly useful for approximating volumetric flow from discrete low- temperature sources. The historic equations of Hemeon and others continue to be useful for the traditional large-scale, high tempera- ture processes (e.g., arc furnaces, tapping operations). Sidedraft Hoods Sidedraft hoods typically draw contaminant away from the operator' s breathing zone. With a buoyant source, a sidedraft hood requires a higher exhaust volumetric flow rate than a low canopy hood. If a low canopy hood restricts the work process, a sidedraft hood may be more cost effective than a high canopy hood. Exam- ples of sidedraft hoods include multislotted "pickling" hoods near welding benches (Figure 9) and slot hoods on tanks (Figure 10). 3. OTHER LOCAL EXHAUST SYSTEM COMPONENTS Duct Design and Construction Inc. ASHRAE, 2019 user. single for Licensed Duct Considerations. The second component ofa local exhaust ventilation system is the duct through which contaminated air is transported from the hood(s). Round ducts are preferred because they (1) offer more uniform velocity to resist settling of material, (2) can withstand the higher static pressures normally found in industrial exhaust systems, and (3) are easier to seal. When design | {}
8ccf950e-325c-4f25-a98b-b24c0bb65df8 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Industrial Local Exhaust Systems 33.7 Table 2 Contaminant Transport Velocities ¦ Nature of Contaminant Examples ¦ Nature of Contaminant Examples ¦ Minimum Transport Velocity, m/s ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Vapor, gases, smoke ¦ All vapors, gases, smoke ¦ Usually 5 to 10 ¦ ¦ Fumes ¦ Welding ¦ 10 to 13 ¦ ¦ Very fine light dust ¦ Cotton lint, wood flour, litho powder ¦ 13 to 15 ¦ ¦ Dry dusts and powders ¦ Fine rubber dust, molding powder dust, jute lint, cotton dust, shavings (light), soap dust, leather shavings ¦ 15 to 20 ¦ ¦ Average industrial dust ¦ Grinding dust, buffing lint (dry), wool jute dust (shaker waste), coffee beans, shoe dust, granite dust, silica flour, general material handling, brick cutting, clay dust, foundry (general), limestone dust, asbestos dust in textile industries ¦ 18 to 20 ¦ ¦ Heavy dust ¦ Sawdust (heavy and wet), metal turnings, foundry tumbling barrels and shakeout, sandblast dust, wood blocks, hog waste, brass turnings, cast-iron boring dust, lead dust ¦ 20 to 23 ¦ ¦ Heavy and moist dust ¦ Lead dust with small chips, moist cement dust, asbestos chunks from transite pipe cutting machines, buffing lint (sticky), quicklime dust ¦ 23 and up ¦ Source: Adapted from ACGIH (2013). limitations require rectangular or flat oval ducts, the aspect ratio (height-to-width ratio) should be as close to unity as possible. Minimum transport velocity is the velocity required to trans- port particles without settling. Table 2 lists some generally accepted transport velocities as a function of the nature of the contaminants (ACGIH 2013). The values listed are typically higher than theoret- ical and experimental values to account for (1) damage to ducts, which increases system resistance and reduces volumetric flow and duct velocity; (2) duct leakage, which tends to decrease velocity in the duct system upstream of the leak; (3) fan wheel corrosion or erosion and/or belt slippage, which could reduce fan volume; and (4) reentrainment of settled particles caused by improper operation of the exhaust system. Design velocities can be higher than mini- mum transport velocities but should never be significantly lower. When particle concentrations are low, the effect on fan power is negligible. Using standard duct sizes and fittings decreases cost and delivery time. Information on available sizes and cost of nonstan- dard sizes can be obtained from the contractor(s). Duct Losses. Chapter 21 of the 2017 ASHRAE Handbook- - Fundamentals covers the basics of duct design and design of metal-working exhaust systems. Loss coefficients are found in the ASHRAE Duct Fitting Database CD-ROM (ASHRAE 2008). For systems conveying particles, elbows with a centerline radius- to-diameter ratio (r/D) greater than 1.5 are the most suitable. If r/D 1.5, abrasion in dust-handling systems can reduce the life of elbows. Elbows, especially those with large diameters, are often made of seven or more gores. For converging flow fittings, a 30° entry angle is recommended to minimize energy losses and abrasion in dust- handling systems (Chapter 21 of the 2017 ASHRAE Handbook Fundamentals). Where exhaust systems handling particles must allow for a sub- stantial increase in future capacity, required transport velocities can be maintained by providing open-end stub branches in the main duct. Air is admitted through these stub branches at the proper pres- sure and volumetric flow rate until the future connection is installed. Figure 1 1 shows such an air bleed-in. Using outside air minimizes replacement air requirements, though care must be taken to consider potential adverse effects of temperature or humidity extremes asso- ciated with the two air streams. The size of the opening can be cal- culated by determining the pressure drop required across the orifice from the duct calculations. Then the orifice velocity pressure can be determined from one of the following equations: P t,o P v,o = C where P v,o velocity pressure, Pa = orifice To = total pressure to be dissipated across orifice, Pa ![image](/image/placeholder) BLEED IN BRANCH DUCT FROM VENTILATED OPERATION Fig. 11 Air Bleed-In C 0 = orifice loss coefficient referenced to the velocity at the orifice cross-sectional area, dimensionless (see Figure 7) Once the velocity pressure is known, orifice velocity and size can be determined. Occasionally, a counterweighted backdraft damper or spring- loaded air admittance valve, configured to allow airflow into the duct but not out, is used as an air bleed in lieu of an orifice in systems that operate under varying airflow conditions. This ensures the proper quantity of transport airflow inside the duct, helping to elim- inate material fallout and subsequent duct blockage. (8) Integrating Duct Segments. Most systems have more than one hood. If the pressures are not designed to be the same for merging parallel airstreams, the system adjusts to equalize pressure at the common point; however, the resulting flow rates of the two merging airstreams will not necessarily be the same as designed. As a result, the hoods can fail to control the contaminant adequately, exposing workers to potentially hazardous contaminant concentrations. Two design methods ensure that the two pressures will be equal. The pre- ferred design self-balances without external aids. This procedure is described in the section on Industrial Exhaust System Duct Design in Chapter 21 ofthe 2017 ASHRAE Handbook-Fundamentals. The second design, which uses adjustable balance devices such as blast gates or balancing dampers, is not recommended, especially when abrasive material is conveyed. Duct Construction. Elbows and converging flow fittings should be made of thicker material than the straight duct, especially if abra- sives are conveyed. Elbows with rD 2 with replaceable wear plates (wear backs) in the heel are often used where particulate load- ing is extremely heavy or the particles are very abrasive. When cor- rosive material is present, alternatives such as special coatings or different duct materials (fibrous glass or stainless steel) can be used. Cleanout openings should be located to allow access to the duct inte- rior in the event of a blockage. Certain contaminants may require washdown systems and/or fire detection and suppression systems to comply with safety or fire prevention codes. These require- ments should be verified with local code officials and insurance Inc. ASHRAE, 2019 user. single for Licensed | {}
50761695-f579-4c57-93eb-94284c13d868 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 33.8 2019 ASHRAE Handbook-HVAC Applications (SI) underwriters. NFPA standards provide guidance on fire safety. Industrial duct construction is also described in Chapter 19 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment, and in Sheet Metal and Air Conditioning Contractors' National Associa- tion (SMACNA) Standard 005-1999. Air Cleaners Air-cleaning equipment is usually selected to (1) conform to fed- eral, state, or local emissions standards and regulations; (2) prevent reentrainment of contaminants to work areas; (3) reclaim usable materials; (4) allow cleaned air to recirculate to work spaces and/or processes; (5) prevent physical damage to adjacent properties; and ⑥ protect neighbors from contaminants. Factors to consider when selecting air-cleaning equipment in- clude the type of contaminant (number of components, particulate versus gaseous, moisture and heat in the airstream, and pollutant concentration), contaminant characteristics (e.g. volatility, reactiv- ity), required contaminant removal efficiency, disposal method, and air or gas stream characteristics. Auxiliary systems such as instru- ment-grade compressed air, electricity, or water may be required and should be considered in equipment selection. Specific hazards such as explosions, fire, or toxicity must be considered in equipment selection, design, and location. See Chapters 29 and 30 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment for informa- tion on equipment for removing airborne contaminants. Consult an applications engineer when selecting equipment. The cleaner' s pressure loss must be added to overall system pres- sure calculations. In some cleaners, specifically some fabric filters, loss increases as operation time increases. System design should incorporate the maximum pressure drop ofthe cleaner, or hood flow rates will be lower than designed during most of the duty cycle. Also, fabric collector losses are usually given only for a clean air plenum. A reacceleration to the duct velocity, with the associated entry losses, must be calculated during design. Most other cleaners are rated flange-to-flange with reacceleration included in the loss. Air-Moving Devices The type of air-moving device selected depends on the type and concentration of contaminant, the pressure rise required, and allow- able noise levels. Fans are usually used. Chapter 21 ofthe 2016 ASH- RAE Handbook-HVAC Systems and Equipment describes available fans; Air Movement and Control Association Publication 201 (AMCA 2002) describes proper connection of the fan(s) to the sys- tem. The fan should be located downstream of the air cleaner when- ever possible to (1) reduce possible abrasion of the fan wheel blades and (2) create negative pressure within the air cleaner and the entire length of dirty duct so that air leaks into the exhaust system through- out its dirty side and control of the contaminant is maintained. Fans handling flammable or explosive dusts should be specified as spark-resistant. AMCA provides three different spark-resistant fan construction specifications. Consult the fan manufacturer when handling these materials. Multiple NFPA standards give fire safety requirements for fans and systems handling explosive or flammable materials. When possible, devices such as fans and pollution-control equip- ment should be located outside classified areas, and/or outside the building, to reduce the risk of fire or explosion. In some instances, the fan is located upstream from the cleaner to help remove dust. This is especially true with cyclone collectors, for example, which are used in the woodworking industry. If explosive, corrosive, flammable, or sticky materials are handled, an injector (also known as an eductor) can transport the material to the air- cleaning equipment. Injectors create a shear layer that induces airflow into the duct. Injectors should be the last choice because their efficiency seldom exceeds 10%. Energy Recovery to Increase Sustainability Energy transfer from exhausted air to replacement air may be economically feasible, depending on the (1) location of the exhaust and replacement air ducts, (2) temperature of the exhausted gas, and (3) nature of the contaminants being exhausted. Heat transfer effi- ciency depends on the type of heat recovery system used. If exhausted air contains particulate matter (e.g., dust, lint) or oil mist, the exhausted air should be filtered to prevent fouling the heat exchanger. If exhausted air contains gaseous and vaporous or vola- tile contaminants, such as hydrocarbons and water-soluble chemi- cals, their effect on the heat recovery device should be investigated. Chapter 26 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment discusses air-to-air energy recovery systems. When selecting energy recovery equipment for industrial ex- haust systems, cross-contamination from the energy recovery de- vice must be considered. Some types of energy recovery equipment may allow considerable cross contamination (e.g., some heat wheels) from the exhaust into the supply airstream, whereas other types (e.g., runaround coils) do not. The exhaust side of the energy recovery device should be negatively pressured compared to the supply side, so that any leakage will be from the clean side into the contaminated side. This is not acceptable for some applications. The material of the energy recovery device must be compatible with the pollutants being exhausted. If the exhaust airstream de- stroys the heat exchanger, contamination can enter the supply air- stream and cause additional equipment damage as well as increase exposure to workers. Exhaust Stacks The exhaust stack must be designed and located to prevent reen- training discharged air into supply system inlets. The building's shape and surroundings determine the atmospheric airflow over it. Chapter 45 covers exhaust stack design. The typical code-required minimum stack height is intended to provide protection for workers near the stack, so discharged air is above their breathing zone. The minimum required stack height does not protect against reentrain- ment of contaminated exhaust into any outside air intakes. If rain protection is important, a no-loss stack head design (ACGIH 2013; SMACNA Standard 005) is recommended. Weather caps deflect air downward, increasing the chance that contaminants will recirculate into air inlets, have high friction losses, and provide less rain protection than a properly designed stack head. Weather caps should never be used with a contaminated or hazardous exhaust stream. Figure 12 contrasts flow patterns of weather caps and stack heads. Loss data for stack heads are presented in the Duct Fitting Database CD-ROM (ASHRAE 2008). Losses in straight-duct stack heads are balanced by the pressure regain at the expansion to the larger-diameter stack head. Instrumentation and Controls Some industrial exhaust systems may require positive verifica- tion of system airflow. Indicators of performance failure may require both audible and visual warning indicators. Other instru- mentation, such as dust collector level indication, rotary lock valve operation, or fire detection, may be required. Selection of electronic monitoring instruments should consider durability expectations, maintenance, and calibration requirements. Interfaces may be required with the process control system or with the balance of the plant ventilation system. Electrical devices in systems conveying flammable or explosive materials or in a hazardous location may need to meet certain electrical safety and code requirements. These requirements are determined by the owner, process equipment manufacturer, federal and state regulations, local codes, and/or insurance requirements. Inc. ASHRAE, 2019 user. single for Licensed | {}
c5765ae6-75aa-4f36-87e0-1f3d00eb87e4 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Industrial Local Exhaust Systems 33.9 ![image](/image/placeholder) STACK HEAD WEATHER CAP 50 12 V EQUAL VELOCITY CONTOURS VELOCITY, 60 10 4 2 75 8 DIAMETERS DISCHARGE 6 DIAMETERS 0 150 2 100 4 4 60 50_ % 2 6 30 8 100 0 12 10 8 6 4 2 V DIAMETERS RIGHT (Discharges upward) WRONG (Discharges downward) Fig. 12 Comparison of Flow Pattern for Stack Heads and Weather Caps 4. OPERATION System Testing and Balancing After installation, an exhaust system should be tested and bal- anced to ensure that it operates properly, with the required flow rates through each hood. If actual flow rates are different from design val- ues, they should be corrected before the system is used. Testing is also necessary to obtain and document baseline data to determine (1) compliance with federal, state, and local codes; (2) by periodic inspections or real-time monitoring, whether maintenance on the system is needed to ensure design operation; (3) whether a system has sufficient capacity for additional airflow; (4) whether system leakage is acceptable; and (5) compliance with testing, adjusting, and balancing (TAB) standards. AMCA (1990) and Chapter 5 of ACGIH (2007) contain detailed information on preferred methods for testing systems. Operation and Maintenance Periodic inspection and maintenance are required for proper operation of exhaust systems. System designers should keep this requirement in mind and account for it through the installation of clean-out/inspection doors and through strategic placement of equipment that ensures access for maintenance activities. Systems are often changed or damaged after installation, resulting in low duct velocities and/or incorrect volumetric flow rates. Low duct velocities can cause contaminants to settle and plug the duct, reduc- ing flow rates at affected hoods. Adding hoods to an existing system can change volumetric flow at the original hoods. In both cases, changed hood volumes can increase worker exposure and health risks. The maintenance program should include (1) inspecting ductwork for particulate accumulation and damage by erosion or physical abuse, (2) checking exhaust hoods for proper volumetric flow rates and physical condition, (3) checking fan drives, (4) main- taining air-cleaning equipment according to manufacturers' guide- lines, and (5) confirming that the system continues to meet compliance with worker exposure and environmental pollution requirements. These and other details are also discussed in ACGIH (2007). REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal. ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. ACGIH. 2007. Industrial ventilation: A manual of recommended practice for operation and maintenance. Committee on Industrial Ventilation, American Conference of Governmental Industrial Hygienists, Cincin- nati, OH. ACGIH. 2013. Industrial ventilation: A manual of recommended practice for design, 28th ed. Committee on Industrial Ventilation, American Con- ference of Governmental Industrial Hygienists, Cincinnati, OH. Alden, J.L., and J.M. Kane. 1982. Design of industrial ventilation systems, 5th ed. Industrial Press, New York. AMCA. 1990. Field performance measurement of fan systems. Publication 203-90. Air Movement and Control Association International, Arlington Heights, IL. AMCA. 2002. Fans and systems. Publication 201-02. Air Movement and Control Association International, Arlington Heights, IL. ASHRAE. 2013. Ventilation for acceptable indoor air quality. ANSI/ ASHRAE Standard 62.1-2013. ASHRAE. 2008. Duct fitting database. Bill, R.G., and B. Gebhart. 1975. The transition of plane plumes. Interna- tional Journal of Heat and Mass Transfer 18:513-526. Brooks, P. 2001. Designing industrial exhaust systems. ASHRAE Journal 43(4):1-5. Caplan, K.J., and G. W. Knutson. 1977. The effect of room air challenge on the efficiency of laboratory fume hoods. ASHRAE Transactions 83(1): 141-156. Caplan, K.J., and G. W. Knutson. 1978. Laboratory fume hoods: Influence of room air supply. ASHRAE Transactions 82(1):522-537. DallaValle, J.M. 1952. Exhaust hoods, 2nd ed. Industrial Press, New York. Goodfellow, H. 1985. Design of ventilation systems for fume control. In Advanced design ofventilation systemsfor contaminant control, pp. 359- 438. Elsevier, New York. Goodfellow, H., and E. Tahti, eds. 2001. Industrial ventilation design guide- book. Academic Press, New York. Hemeon, W.C.L. 1963. Exhaust for hot processes. Ch. 8 in Plant and process ventilation, 2nd ed., pp. 160-196. Industrial Press, New York. Hemeon, W.C.L. 1999. Exhaust for hot processes. Ch. 8 in Hemeon 's plant and process ventilation, 3rd ed., pp. 117-147, D.J. Burton, ed. Lewis, New York. McKernan, J.L., and M.J. Ellenbecker. 2007. Ventilation equations for improved exothermic process control. Annals of Occupational Hygiene 51:269-279. McKernan, J.L., M.J. Ellenbecker, C.A Holcroft, and M.R. Petersen. 2007a. Evaluation ofa proposed area equation for improved exothermic process control. Annals of Occupational Hygiene 51:725-738. McKernan, J.L., M.J. Ellenbecker, C.A. Holcroft, and M.R. Petersen. 2007b. Evaluation of a proposed velocity equation for improved exothermic pro- cess control. Annals of Occupational Hygiene 51:357-369. NFPA. 2015. Ovens and furnaces. ANSI/NFPA Standard 86. National Fire Protection Association, Quincy, MA. NFPA. 2010. Recommended practice for handling releases of flammable and combustible liquids and gases. ANSI/NFPA Standard 329. National Fire Protection Association, Quincy, MA. Nielsen, P. V. 1993. Displacement ventilation: Theory and design. Aalborg University, Aalborg, Denmark. SMACNA. 1999. Round industrial duct construction standards, 2nd ed. ANSI/SMACNA/BSR Standard 005-1999. Sheet Metal and Air Condi- tioning Contractors' National Association, Chantilly, VA. U.S. Public Health Service. 1973. Air pollution engineering manual. Publi- cation 999-AP-40. BIBLIOGRAPHY Bastress, E., J. Niedzwocki, and A. Nugent. 1974. Ventilation required for grinding, buffing, and polishing operations. Publication 75107. U.S. Department of Health, Education, and Welfare. National Institute for Occupational Safety and Health, Washington, D.C. Baturin, V. V. 1972. Fundamentals of industrial ventilation, 3rd English ed. Pergamon, New York. Braconnier, R. 1988. Bibliographic review of velocity field in the vicinity of local exhaust hood openings. American Industrial Hygiene Association Journal 49(4):185-198. Brandt, A.D., R.J. Steffy, and R.G Huebscher. 1947. Nature of airflow at suction openings. ASHVE Transactions 53:5576. Inc. ASHRAE, 2019 user. single for Licensed | {}
2c62df2e-20b7-4a32-80b0-cd5b33774c5c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 33.10 2019 ASHRAE Handbook-HVAC Applications (SI) British Occupational Hygiene Society (BOHS). 1987. Controlling airborne contaminants in the workplace. Technical Guide 7. Science Review Ltd. and H&H Scientific Consultants, Leeds, U.K. Burgess, W.A., M.J. Ellenbecker, and R.D. Treitman. 1989. Ventilation for control ofthe work environment. John Wiley & Sons, New York. Chambers, D.T. 1993. Local exhaust ventilation: A philosophical review of the current state-of-the-art with particular emphasis on improved worker protection. DCE, Leicester, U.K. EC. 1994. Directive 94/9/EC on equipment and protective systems intended for use in potentially explosive atmospheres (ATEX). European Commis- sion, Brussels, Belgium. Available from ec.europa.eu/enterprise/sectors /mechanical Cocumentallegisiatizationavindex_entm EC. 1999. Directive 99/92/EC on minimum requirementsfor improving the safety and health protection of workers potentially at riskfrom explo- sive atmospheres. European Commission, Brussels, Belgium. Avail- able from eunkan.sunquou.su/egal-contentENTAT/uri-CELEX 31999 L0092. Flynn, M.R., and M.J. Ellenbecker. 1985. The potential flow solution for air- flow into a flanged circular hood. American Industrial Hygiene Journal 46(6):318-322. Fuller, F.H., and A. W. Etchells. 1979. The rating of laboratory hood perfor- mance. ASHRAE Journal 21(10):49-53. Garrison, R.P. 1977. Nozzle performance and design for high-velocity/low- volume exhaust ventilation. Ph.D. dissertation. University of Michigan, Ann Arbor. Goodfellow, H.D. 1986. Ventilation '85 (Conference Proceedings). Elsevier, Amsterdam. Hagopian, J.H., and E.K. Bastress. 1976. Recommended industrial ventila- tion guidelines. Publication 76162. U.S. Department of Health, Educa- tion, and Welfare, National Institute for Occupational Safety and Health, Washington, D.C. Heinsohn, R.J. 1991. Industrial ventilation: Engineering principles. John Wiley & Sons, New York. Heinsohn, R.J., K.C. Hsieh, and C.L. Merkle. 1985. Lateral ventilation sys- tems for open vessels. ASHRAE Transactions 91(1B):361-382. Hinds, W. 1982. Aerosol technology: Properties, behavior, and measure- ment of airborne particles. John Wiley & Sons, New York. Huebener, D.J., and R. T. Hughes. 1985. Development of push-pull ventila- tion. American Industrial Hygiene Association Journal 46(5):262-267. Kofoed, P., and P.V. Nielsen. 1991. Thermal plumes in ventilated rooms Vertical volume flux influenced by enclosing walls. Presented at 12th Air Infiltration and Ventilation Centre Conference, Ottawa. Ljungqvist, B., and C. Waering. 1988. Some observations on "modern" design of fume cupboards. Proceedings of the 2nd International Sympo- sium on Ventilationfor Contaminant Control, Ventilation '88. Pergamon, U.K. Morton, B.R., G. Taylor, and J.S. Turner. 1956. Turbulent gravitational con- vection from maintained and instantaneous sources. Proceedings of Royal Society 234A:1. Posokhin, V.N., and A.M. Zhivov 1997. Principles of local exhaust design. Proceedings of the 5th International Symposium on Ventilation for Con- taminant Control, vol. 1. Canadian Environment Industry Association (CEIA), Ottawa. Qiang, Y.L. 1984. The effectiveness ofhoods in windy conditions. Kungliga Tekniska Hoggskolan, Stockholm. Safemazandarani, P., and H.D. Goodfellow. 1989. Analysis of remote recep- tor hoods under the influence of cross-drafts. ASHRAE Transactions 95(1):465-471. Sciola, V. 1993. The practical application of reduced flow push-pull plating tank exhaust systems. Presented at 3rd International Symposium on Ven- tilation for Contaminant Control, Ventilation '91, Cincinnati, OH. Sepsy, C.F., and D.B. Pies. 1973. An experimental study of the pressure losses in converging flow fittings used in exhaust systems. Document PB 221 130. Prepared by Ohio State University for National Institute for Occupational Health. Shibata, M., R.H. Howell, and T. Hayashi 1982. Characteristics and design method for push-pull hoods: Part I-Cooperation theory on airflow; Part 2-Streamline analysis ofpush-pull flows. ASHRAE Transactions 88(1): 535-570. Silverman, L. 1942. Velocity characteristics of narrow exhaust slots. Journal ofIndustrial Hygiene and Toxicology 24 (November):267. Sutton, O.G. 1950. The dispersion ofhot gases in the atmosphere. Journal of Meteorology 7(5):307. Zarouri, M.D., R.J. Heinsohn, and C.L. Merkle. 1983. Computer-aided design of a grinding booth for large castings. ASHRAE Transactions 89(2A):95-118. Zarouri, M.D., R.J. Heinsohn, and C.L. Merkle. 1983. Numerical computa- tion of trajectories and concentrations of particles in a grinding booth. ASHRAE Transactions 89(2A):119-135. Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
ee29bc0e-9b77-4b9e-8918-8c0c1fdc7869 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 34 KITCHEN VENTILATION ¦ COMMERCIAL KITCHEN VENTILATION ¦ 34.1 ¦ HVAC System Design ¦ 34.31 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Commissioning ¦ 34.2 ¦ Exhaust Systems ¦ 34.32 ¦ ¦ Ventilation Design ¦ 34.2 ¦ Exhaust Fans ¦ 34.33 ¦ ¦ System Integration and Design ¦ 34.3 ¦ Fire Safety ¦ 34.34 ¦ ¦ Energy Considerations ¦ 34.6 ¦ System Commissioning and Air Balancing ¦ 34.38 ¦ ¦ Thermal Comfort. ¦ 34.9 ¦ Operations and Maintenance ¦ 34.39 ¦ ¦ Commercial Exhaust Hoods ¦ 34.10 ¦ RESIDENTIAL KITCHEN VENTILATION. ¦ 34.41 ¦ ¦ Cooking Effluent Generation and Control. ¦ 34.21 ¦ Exhaust Systems ¦ 34.41 ¦ ¦ Replacement (Makeup) Air Systems. ¦ 34.25 ¦ RESEARCH ¦ 34.43 ¦ T HIS chapter focuses primarily on commercial kitchen ventila- tion (CKV) systems in restaurants and institutional food service facilities, and incorporates the research and experience (including all steps of the design process) amassed by TC 5.10 over the past two decades. Although a brief section on residential kitchen ventilation has been retained, only minor updates have been incorporated over the history of this chapter. Given ongoing debate on residential range hood performance, TC 5.10 anticipates sponsoring research to provide a basis for enhanced design of residential kitchen ventilation (RKV) systems. To provide a means for codifying critical CKV items as well as provide expertise to code-writing authorities, TC 5.10 sponsors Standing Standard Project Committee (SSPC) 154, Ventilation for Commercial Cooking Operations. SSPC-154's scope includes pro- viding the most complete design guidance available on commercial kitchen ventilation components and systems. Specific areas include kitchen hoods, exhaust systems, and replacement air systems. SSPC-154 relies on the significant field experiences of the man- ufacturers, designers, and users of kitchen ventilation systems. ASHRAE Standard 154 is intended to serve as a template for stan- dardization, harmonization, and ongoing revision of related model and adopted codes and to bring consistency to design requirements and applications of commercial kitchen ventilation systems. 1. COMMERCIAL KITCHEN VENTILATION Kitchen ventilation is a complex web ofinterconnected HV AC sys- tems. The main components typically include (1) cooling to address heat from cooking appliances, (2) replacement air to provide proper pressurization during cooking operations, and (3) exhaust to remove heat and effluent generated by cooking appliances. System design includes aspects of air conditioning, fire safety, ventilation, building pressurization, refrigeration, air distribution, and food service equipment. Kitchens are in many buildings, including restaurants and retail malls (see Chapter 2), hotels (Chapter 7), hospitals (Chapter 9), single- and multifamily dwellings (Chapter 1), educa- tional facilities (Chapter 8), and correctional facilities. Each building type has special requirements for its kitchens, but many basic needs are common to all. This chapter provides an understanding of the different components of kitchen ventilation systems and where they can be applied. Additionally, background information is included to provide an understanding of the history and rationale behind these design decisions. Kitchen ventilation has at least two purposes: (1) to provide a comfortable environment in the kitchen and (2) to ensure the safety The preparation of this chapter is assigned to TC 5.10, Kitchen Ventilation. of personnel working in the kitchen and of other building occupants. Comfort criteria often depend on the local climate, because some kitchens are not air conditioned. Kitchen ventilation ensures safety by providing the means to remove heat, smoke, and grease (cooking effluent) produced during normal cooking operations. HVAC system designers are most frequently involved in commer- cial kitchen applications, in which cooking effluent contains large amounts of grease or water vapor. Residential kitchens typically use a totally different type of hood. The amount of grease produced in residential applications is significantly less than in commercial appli- cations, so the health and fire hazard is much lower. The centerpiece of almost any kitchen ventilation system is an exhaust hood(s), used primarily to remove cooking effluent from kitchens. Effluent includes gaseous, liquid, and solid contaminants produced by the cooking process, and may also include products of fuel and even food combustion. These contaminants must be removed for both comfort and safety; effluent can be potentially life- threatening and, under certain conditions, flammable. Finally, note that the arrangement of food service equipment and its coordination with the hood(s) can greatly affect the energy used by these systems, which in turn affects kitchen operating costs. Quite often, the hood selection and appliance layout is determined by a kitchen facility designer. To minimize energy use and ensure a properly designed kitchen ventilation system, the HVAC engineer should reach out to the kitchen designer and share the practices and ideas presented in this chapter. Sustainability Kitchens are some of the most intensive users of energy for a given floor area when compared to other commercial or institutional occu- pancies. In addition to energy used during cooking, the kitchen ven- tilation system must address the large amount of heat emitted or convected into the kitchen from the cooking equipment, and supply and condition the replacement air needed to support the cooking effluent exhaust system as well as ensure acceptable indoor environ- mental quality (IEQ). An additional factor to be considered is the cooking effluent, and any treatments that may be required before it is discharged into the atmosphere. Given these factors, it is imperative that the kitchen ventilation system be designed with careful consideration of both first costs and operating costs. Maintenance costs should also be considered, including scheduled equipment service and replacement (e.g., hoods and exhaust duct cleaning, hood filter cleaning, fire protection system inspection, charging, refusing), any corresponding labor, and any production downtime as a result of the maintenance. To ensure all of these criteria are accounted for in the kitchen ven- tilation design, the integrated building design approach described in Chapter 60 is recommended. 34.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
fb7f262f-9791-4810-a128-a126e854c24b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 34.2 2019 ASHRAE Handbook-HVAC Applications (SI) 1.1 COMMISSIONING Because CKV systems are very complex operational environ- ments, it is strongly recommended that ASHRAE Standard 202 and the guidance in Chapter 44 be followed for any commercial kitchen ventilation project. Sections of this chapter contain the technical information necessary to address all four phases of commissioning. Addressing the following topics is recommended when developing and executing any commissioning plan: 1. Owners project requirements (OPR) a. System manual outline i. System selection: specific kitchen ventilation use re- quirements (by owner or design team) ii. Type of facility (e.g., commissary, quick service, full service, institutional) iii. Cooking appliances selection based on menu, type of cooking, and special/unusual considerations iv. Other considerations 1. System cost 2. Kitchen space comfort targets 3. Energy use and sustainability targets 4. Replacement air requirements 5. Cooking exhaust a. Duct routing and egress b. Effluent control requirements c. Air discharge and outlet restrictions 6. Other mechanical services a. HVAC equipment location b. Utility services 7. Future expansion 8. Ongoing maintenance requirements 2. Design phase a. Systems manual outline (i.e., design intent): the engineer's response to the OPR b. Hood selection based on appliance line up (very critical because it affects exhaust rate) c. Replacement air method, and kitchen air movement d. Accounting for kitchen equipment heat gains e. System control strategies, including demand-controlled kitchen ventilation (DCKV) systems f. Exhaust effluent control measures g. Energy saving measures h. Exhaust system requirements i. Fire safety j. Codes and standards i. NFPA Standard 96 ii. ASHRAE Standard 154 111. IMC (ICC 2018) iv. UL Standard 710 V. UL Standard 762 3. Construction phase a. Submittal review and coordination with all disciplines b. Installation and execution with end use in mind c. Exhaust duct construction d. Air outlet and inlet locations and adjustments e. Technical commissioning of the following: i. System controls for replacement air and exhaust air, including DCKV systems ii. Cooking effluent control equipment iii. Cooking fire suppression systems iv. Air system testing, balancing, and adjustment 4. Occupancy and operations a. Owner and user training of systems i. Exhaust and replacement air controls, including DCKV systems ii. Cooking effluent control iii. Cooking fire suppression b. Maintenance schedule c. Recommissioning plan d. Consequences of any revision/remodel (e.g., changing cooking equipment) 1.2 VENTILA TION DESIGN Design Process Designing a CKV or even a high-end residential kitchen ventila- tion system requires a different design approach and process than for most traditional HVAC systems. Design considerations include large replacement air requirements, large internal heat gains, kitchen workers' comfort, minimizing HVAC system energy use, and fire safety, all of which are equally high priorities that must be addressed during system design. Necessary steps to design the ventilation systems for a commer- cial kitchen are as follows. Details for each step can be found in the subsequent sections in this chapter, or in the other Handbook chap- ters. 1. Kitchen facilities design (including cooking menu and appli- ance selection and placement). This design is typically per- formed by the food service consultant (FSC). Additionally, determine which appliances require an exhaust hood. 2. Exhaust hood selection, including exhaust air rates. Often over- looked, but one of the most critical design decisions for any CKV system: hood selection directly affects exhaust rates, the corre- sponding replacement air requirements, CKV system heat gain and loss calculations, and the system 's overall energy use. Con- siderations include a. Appliance duty rating, fuel type (e.g., gas, solid fuel, electric, combination), cooking emission, and thermal plume character b. Type I or Type II, based on appliance use or process c. Hood style (e.g., canopy, island, back shelf) d. Energy saving options (e.g., side panels, extra overhang, demand control kitchen ventilation) e. Life-cycle cost analysis 3. CKV system integration and design. Determine exactly what the CKV system should accomplish, and how to holistically inte- grate it into the building. 4. Replacement air design. Addresses the need for delivering the replacement air into the kitchen. Considerations include a. Transfer air, comfort supply air, or direct makeup air (or any combination) b. ASHRAE Standard 62.1 compliance c. Adjacent zone air classifications d. Replacement and supply air delivery systems 5. CKV system controls. Maintain pressurization and comfort for the kitchen, dining area, and if applicable any adjoining zones. Accommodate any demand control systems, including DCKV and adjacent zones' demand-controlled ventilation (DCV) sys- tem(s). 6. Heat gain and loss calculations a. Appliance heat gains b. Replacement air 7. Exhaust system design a. Duct type selection b. Fire safety c. Air discharge d. Effluent control devices e. Fire suppression 8. HVAC system design a. Equipment selection b. Diffuser and return grille layout (very critical) Inc. ASHRAE, 2019 user. single for Licensed | {}
e11d297c-ea64-40df-953b-c1f87a48abe3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Kitchen Ventilation 34.3 9. Hood and replacement air commissioning specifications (e.g., air balancing, troubleshooting) Note: the CKV design engineer is recommended to engage the FSC during steps 1 and 2 to identify areas where both designs can be harmonized for optimal CKV performance. 1.3 SYSTEM INTEGRA TION AND DESIGN Ideally, system integration and balancing bring the many venti- lation components together to provide the most comfortable, effi- cient, and economical performance of each component and of the entire system. In commercial kitchen ventilation, the replacement air system(s) must integrate and balance with the exhaust system and/or facility HVAC system(s). Even optimal system designs re- quire field testing and balancing once installed. It is important to verify compliance with design, and equally important to confirm that the design meets the needs of the operating facility. Air balance is a critical step in any CKV commissioning process. The following fundamentals should be considered and applied to all food service facilities, including restaurants, within the constraints of the particular facility and its location, equipment, and systems. Principles Although there are exceptions, the following are the fundamental principles of integrating and balancing food service facility systems for comfort, control, and economical operation: · The building should always be slightly positively pressurized (e.g. +1.25 Pa) compared to atmosphere to prevent infiltration of outdoor air. Infiltrated air contains contaminants and insects, and adds to the heat load. · Every kitchen should always be slightly negatively pressurized (-0.25 Pa) to adjacent rooms or areas immediately surrounding it to help contain odors in the kitchen and to prevent odor migration out of the kitchen. · System HV AC design should prevent air supplied to the kitchen from being returned and supplied to non-kitchen areas. Odor con- tamination is an obvious potential problem. In addition, in condi- tions such as seasonal transitions, when adjacent zones may be in different modes (e.g., economizer versus air conditioning or heat- ing), comfort may be adversely affected. Ideally, the kitchen HVAC system should be separate from all other zones' HVAC systems. Three situations to consider are the following: - During seasonal transitions, the kitchen zone may require air conditioning or may be served by ventilation air only, while dining areas require heating. Even in kitchens that require cooling when the adjacent dining areas require heating, it is still important to maintain the pressure differential between these spaces and continue transfer of dining-area air into the kitchen. - To limit kitchen personnel discomfort, it is important to control the low-temperature MUA set point and prevent drastic temperature variations between the kitchen space and MUA being introduced. If dedicated kitchen MUA requires heating, thermostatic control of the MUA heating source should ideally be based on kitchen space temperature rather than outdoor air temperature. MUA heating should be interlocked with kitchen HVAC cooling to prevent simultaneous heating and cooling. Location of HVAC thermostats in kitchens must account for the potential conflicting temperatures. - Ideally, will should be no perceptible drafts in dining areas, and temperature variations of no more than 0.6 K. Kitchens might not be draft free; however, velocities at or near exhaust hoods should be no greater than 0.4 m/s. Kitchen comfort is greatly impacted by radiant heat in work areas, but it is desirable to maintain sensible temperatures within 3 K of design conditions. These conditions can be achieved with even distribution and thorough circulation of air in each zone by an adequate number of registers sized to preclude high air velocities. If there are noticeable drafts or temperature differences, dining customers will be uncomfortable and facility personnel are generally less comfortable and less productive. Both design concepts and operating principles for proper integra- tion and balance are involved in achieving desired results under varying conditions. The same principles are important in almost every aspect of food service ventilation. In restaurants with multiple exhaust hoods, or hoods with de- mand control systems, exhaust airflow volume may vary throughout the day. Replacement air must be controlled to maintain proper building and kitchen differential pressures to ensure the kitchen remains negative to adjacent areas at all operating points. The more variable the exhaust, or the smaller and more numerous the zones involved, the more complex the design, but the overall pressure relationship principles must be maintained to provide optimum comfort, efficiency, and economy. A different application is a kitchen with one side exposed to a larger building with common or remote dining. Examples include a food court in a mall or a small restaurant in a hospital, airport, or similar building. Positive pressure at the front of the kitchen might cause some cooking grease, vapor, and odors to spread into the common building space, which would be undesirable. In such a case, the kitchen area is held at a negative pressure relative to other common building areas as well as to its own back room storage or office space. Such spaces that include direct-vent appliances, such as gas-fired water heaters, must maintain the pressure required for safe appliance operation. Design Best Practices Life-Cycle Cost Analysis (LCC). As with any engineering design, many considerations must be taken into account to ensure the CKV system operates properly and with the best interest of end users in mind. Life-cycle cost analysis compares the real cost of owning and operating two or more systems over a given period of time (typ- ically 10 to 20 years). For each system, the total life-cycle cost can be calculated using Equation (1) (Fuller and Peterson 1996): LCC = I + Repl - Res + E + W + OM&R where LCC = Total LCC in present-value dollars of given alternative I = Present-value investment costs Repl = Present-value replacement costs Res = Present-value residual (scrap) costs E = Present-value energy costs W = Present-value water costs OM&R = Present-value, nonfuel, operating, maintenance and repair costs (1) For the kitchen ventilation systems covered in this chapter, the lifetime is typically longer than 10 years; if 10 years is used as the span of the analysis, the replacement costs and scrap costs are zero. For ventilation systems, energy costs could include items such as hood lights, exhaust fans, and the associated HVAC energy to con- dition supply air; water costs could include heating hot water (if applicable) used for hoods with wash or mist systems; OM&R could include maintenance items, the costs to remove and clean the pri- mary grease extractors in the hood, and periodic replacement of fil- ters in pollution control systems. For CKV systems, the analysis is typically a comparison of the first cost of the equipment to the operating costs. For CKV systems, the primary operating costs are for conditioning the outdoor air used as replacement air for the kitchen hood exhaust. As such, different climates may yield different LCA values for identical designs. It is recommended that LCAs be performed on the following items: Inc. ASHRAE, 2019 user. single for Licensed | {}
3d2008a0-7492-4472-85f7-48a531efe729 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 34.4 2019 ASHRAE Handbook-HVAC Applications (SI) · Hoods, including size, type, and options (e.g., increased over- hangs and side panels); in some instances, even different manu- facturers may yield different results. · Exhaust fans. · Makeup air/replacement air designs (comparing untempered to tempered makeup air). · Cooking effluent reduction technologies to duct cleaning costs. An example of LCA for a kitchen is selecting the exhaust fan. Table 1 lists several fans that can perform the required, duty. If first cost is considered, the physically smallest (fan A) is the best choice. However, when applying a LCA, the larger fan C is the best option. Incorporating Variable-Frequency Drives (VFDs) for Exhaust Fan Control Many kitchen exhaust fans, especially those that are part of a DCKV system, use VFDs to control their speed. If applicable, the VFD will be supplied by the DCKV system supplier, and it should be installed adjacent to the exhaust hood it serves. If the building in which it is installed has the exhaust fans located a considerable dis- tance away, as in tall buildings, the following must be taken into consideration: · VFDs should have a separate conduit from the VFD to motor. In some cases, VFD output circuits may share conduit for short dis- tances (e.g., in a cable tray, through a roof penetration), for up to 4.6 m. · If VFD output circuits share conduit for more than 4.6 m, then output reactors should be installed on every VFD. · No more than two VFD output circuits should share a single con- duit for more than 4.6 m. · Longer VFD-to-motor distances increase the probability that the motor will see higher voltage spikes, which can lead to the motor burning up. The issue gets worse with higher voltages. Methods to address this issue include the following: - Specify an inverter-duty motor rated for 1600 V P-P is critical (NEMA Standard MG1.1 Part 31) - Use a lower switching frequency. This can cause more audible noise at the motor, but is easier on the hardware. - Use an output reactor, mounted close to the VFD, to help ab- sorb spikes and reduce reflected wave phenomena on load side of VFD. - An output filter, mounted close to the VFD, can also be used, but not in conjunction with output reactors. This provides additional protection to the motor with longer modulated wiring distances. 、 Input reactors, mounted close to the VFD, help smooth out power going to the line side of the VFD and help with rough output voltage on the load side. · If possible, locate the VFD closer to the motor to reduce the mod- ulated power run from the VFD to the serving motor. · For retrofit projects, replace existing motors to prevent motor burn- out. If existing motor are to be reused, use the following recommended limitations on distance from VFD to motor. Be rea- sonably conservative, but remember the risk of motor failure always exists. - 230 V AC motors: up to 60 m from VFD to motor - 460 V AC motors: up to 20 m from VFD to motor - 575 V AC motors: up to 12 from VFD to motor - If VFD-to-motor wiring distances exceed these limits, then output reactors are recommended · For new construction and retrofit projects where the motor is replaced, consider the following limitations on distance from VFD to motor: - New motors should comply with NEMA Standard MG1 Part 31, which states that the motor winding insulation must be able to withstand voltage spikes of 1600 V peak-to-peak in 0.1 us. - Totally enclosed fan-cooled (TEFC) motors should be used if they fit in the housing of the existing fan. - Open dripproof (ODP) motors may be used where TEFC motors do not fit. - Where the nominal AC voltage is 575 V (e.g., Canada), new motors must have insulation able to withstand 1700 V p-p. - Limitations on VFD-to-motor distance when the motor is new and known to meet the standards of NEMA Standard MG-1 Part 31 are · 230 V AC motors: up to 152 m from VFD to motor · 460 V AC motors: up to 60 m from VFD to motor · 575 V AC motors: up to 30 m from VFD to motor · If VFD-to-motor wiring distance exceeds these limits, then output reactors are recommended Dedicated Fan Versus Manifold Exhaust Systems. Whether to connect each exhaust hood to its own dedicated exhaust fan is typ- ically dictated by the physical constraints of the building into which the CKV system is being installed. The duct shaft space needed to install multiple exhaust ducts is not permitted on most projects, es- pecially for any multistory building. Additionally, installing multiple exhaust ducts increases the first cost. Thus, many designs use manifold exhaust systems, which consist of multiple exhaust hoods served by a single exhaust fan. The primary advantage of using a manifold exhaust system is first cost. Less ductwork is needed, which also reduces the amount of floor area lost to duct riser shafts. Additionally, fewer exhaust fans are needed, reducing the costs of equipment as well as associ- ated electrical power wiring. Table 1 Size, First Cost, and Operating Cost of 5 Upblast Exhaust Fans Operating at the Same Design Duty Design Duty: Belt Drive Upblast Fan: 1888 L/s at 373.2 Pa ¦ Belt Drive Upblast Fan ¦ Wheel Diameter, mm ¦ Relative Cost ¦ Est. Cost ¦ Operating Cost/Yr, $ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ A ¦ 469.9 ¦ 1 ¦ $750 ¦ $1082 ¦ ¦ B ¦ 542.925 ¦ 1.09 ¦ $818 ¦ $1106 ¦ ¦ C ¦ 622.3 ¦ 1.23 ¦ $923 ¦ $1023 ¦ ¦ D ¦ 565.15 ¦ 2.09 ¦ $1568 ¦ $995 ¦ ¦ E ¦ 685.8 ¦ 2.81 ¦ $2108 ¦ $937 ¦ Table 2 Life-Cycle Analysis of Five Different Exhaust Fans Operating at Same Design Duty* ¦ Belt Drive Upblast Fan ¦ Wheel Diameter (mm) ¦ Cost of Ownership for Years 0 to 10 ¦ Cost of Ownership for Years 0 to 10 ¦ Cost of Ownership for Years 0 to 10 ¦ Cost of Ownership for Years 0 to 10 ¦ Cost of Ownership for Years 0 to 10 ¦ Cost of Ownership for Years 0 to 10 ¦ Cost of Ownership for Years 0 to 10 ¦ Cost of Ownership for Years 0 to 10 ¦ Cost of Ownership for Years 0 to 10 ¦ Cost of Ownership for Years 0 to 10 ¦ Cost of Ownership for Years 0 to 10 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Belt Drive Upblast Fan ¦ Wheel Diameter (mm) ¦ 0 ¦ 1 ¦ 2 ¦ 3 ¦ 4 ¦ 5 ¦ 6 ¦ 7 ¦ 8 ¦ 9 ¦ 10 ¦ ¦ A ¦ 469.9 ¦ $750 ¦ $1,832 ¦ $2,915 ¦ $3,997 ¦ $5,079 ¦ $6,161 ¦ $7,244 ¦ $8,326 ¦ $9,408 ¦ $10,490 ¦ $11,573 ¦ ¦ B ¦ 543.6 ¦ $818 ¦ $1,923 ¦ $3,029 ¦ $4,135 ¦ $5,241 ¦ $6,347 ¦ $7,453 ¦ $8,559 ¦ $9,665 ¦ $10,770 ¦ $11,876 ¦ ¦ C ¦ 622.3 ¦ $923 ¦ $1,945 ¦ $2,968 ¦ $3,990 ¦ $5,013 ¦ $6,036 ¦ $7,058 ¦ $8,081 ¦ $9,104 ¦ $10,126 ¦ $11,149 ¦ ¦ D ¦ 566.4 ¦ $1,568 ¦ $2,562 ¦ $3,557 ¦ $4,551 ¦ $5,546 ¦ $6,540 ¦ $7,535 ¦ $8,529 ¦ $9,524 ¦ $10,518 ¦ $11,513 ¦ ¦ E ¦ 685.8 ¦ $2,108 ¦ $3,045 ¦ $3,982 ¦ $4,919 ¦ $5,856 ¦ $6,793 ¦ $7,730 ¦ $8,667 ¦ $9,605 ¦ $10,542 ¦ $11,479 ¦ *Energy costs = $0.03/MJ; operating 18 h/day and 7 days/week. Inc. ASHRAE, 2019 user. single for Licensed | {}
622cbc63-3818-4ae6-a1ef-7bc702ef1653 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Kitchen Ventilation 34.5 The primary disadvantage of manifolded exhaust systems is the challenge of accurately controlling exhaust airflow at each individ- ual hood. Due to fire codes, air-balancing dampers can only be in- stalled as part of the hood collar, and they must be specifically listed for their intended application. Additionally, ifa DCKV system is in- corporated, the exhaust airflow can only be reduced when either (1) all cooking equipment under all hoods goes into part-load opera- tion, or (2) specialized control dampers listed for installation and operation in cooking exhaust systems are installed along with the necessary controls to integrate with the DCKV system. These de- tails should be considered when performing a life-cycle cost analy- sis of a manifolded exhaust system. An additional disadvantage is that, should the fan fail, the entire cooking operation loses function. For dedicated fan-to-hood systems, first costs are indeed greater for the extra ducts and fans. But the advantages include being able to control exhaust air for each hood simply by changing fan speed. This approach works for both initial balancing and for DCKV con- trol. If a cooking appliance is not being used, the associated fan can be shut off instead of operating at reduced airflow. Finally, should a fan fail, the entire cooking operation will not have to cease. Multiple-Hood Systems Served by Single Exhaust Fan Single kitchen exhaust duct/fan systems serving multiple hoods (i.e., manifold exhaust systems) present unique design and balancing challenges. Air balance is one of the main challenges. These systems may be designed with bleed ducts and/or balancing dampers to facilitate balancing the air draw ofindividual hoods. The dampers can be of blade types that can be set in position manually or operated automatically by a programmable actuator. Balancing dampers must be listed for use with kitchen hoods. Additionally, hood filters are sized to allow pressure loss equalization along the hood for hood containment and capture (C&C). Some filters are adjustable, but should not be used when they can be interchanged between hoods or within the same hood, because such interchange can alter the commissioned air balance ofthe hoods and exhaust fan. Balancing can also be accomplished by changing the number and/or size of filters. DCKV in single or manifold applications can automatically pro- vide real-time balancing by using an engineered system listed for use with commercial kitchen hoods, such as one or more of the fol- lowing: cooking activity sensors, variable-speed exhaust and supply fans, and volume-balancing dampers to modulate hood exhaust. However, the ductwork still must be properly designed to allow each hood to achieve design airflows during full-load cooking opera- tions. When physical space allows, it is good practice to use a sep- arate exhaust fan for each hood. This effectively provides system redundancy and less complexity when balancing. Exhaust for solid-fuel cooking equipment should be separate from all other exhaust systems. Light-duty smokers, flavoring equipment, or fireboxes that use solid fuel can be installed under the hood serving other cooking equipment, subject to restrictions under NFPA Standard 96 and building codes, including size, fuel load and storage, open flame design, and ash removal and disposal. In some multitenant installations, the duct design may be com- pleted and installed before the tenants have been identified. In cases such as master kitchen-exhaust systems, which are sometimes used in shopping center food courts, no single group is responsible for the entire design. The base building designer typically lays out ductwork to (or through) each tenant space, and each tenant selects a hood and lays out connecting ductwork. Often, the base building designer has incomplete information on tenant exhaust requirements. Therefore, one engineer must be responsible for defining criteria for each tenant' s design and for evaluating proposed tenant work to ensure that tenant designs match the system ' s capacity. The engineer should also evaluate any proposed changes to the system, such as changing tenancy. Rudimentary computer modeling of the exhaust system may be helpful (Elovitz 1992). Given the unpredictability and vola- tility of tenant requirements, it may not be possible to balance the entire system perfectly. However, without adequate supervision, itis very probable the system will not achieve proper balance. For greatest success with multiple-hood exhaust systems, mini- mize pressure losses in ducts by keeping velocities low, minimizing sharp transitions, and using hoods with relatively high pressure drops. When pressure loss in the ducts is low compared to the loss through the hood, changes in pressure loss in the ductwork because of field conditions or changes in design airflow have a smaller effect on total pressure loss and thus on actual airflow. Minimum code-required air velocity (2.5 m/s) must be main- tained in all parts of the exhaust ductwork at all times. If fewer or smaller hoods are installed than the design anticipated, resulting in low velocity in portions of the ductwork, the velocity must be brought up to the minimum. One way is to introduce outdoor air, preferably untempered, through a bleed duct system directly into the exhaust duct (Figure 1). The bypass duct should connect to the top or sides (at least 50 mm from the bottom) of the exhaust duct to prevent backflow of water or grease through the bypass duct when fans are off. This arrangement is also shown in NFPA Standard 96 and should be discussed with the authority having jurisdiction. A fire damper is required in the bleed duct, located close to the exhaust duct. Bypass duct construction should be the same as the ex- haust duct construction, including enclosure and clearance require- ments, for at least a metre beyond the fire damper or as required by the local authority having jurisdiction (AHJ). Means to adjust the bleed airflow must be provided upstream of the fire damper. All dampers must be in the clean bleed air duct so they are not exposed to grease-laden exhaust air. The difference in pressure between bleed and exhaust air duct may be great; the balancing device must be able to make a fine airflow adjustment against this pressure difference. It is best to provide two balancing devices in series, such as an orifice plate or blast gate for coarse adjustment, followed by an opposed-blade damper for fine adjustment. Directly measuring air velocities in the exhaust ductwork to as- sess exhaust system performance may be desirable. Velocity (pitot- tube) traverses may be performed in kitchen exhaust systems, but holes drilled for the pitot tube must be liquidtight to maintain the fire-safe integrity of the ductwork, per NFPA Standard 96. Holes should never be drilled in the bottom of a duct, where they may col- lect grease. Velocity traverses should not be performed when cooking is in progress because grease collects on the instrumenta- tion. Dynamic V olumetric Flow Rate Effects Minimum exhaust flow rates for kitchen hoods are determined ei- ther by laboratory tests or by building code requirements. Energy codes specify maximum airflow rates. In either case, the installed ![image](/image/placeholder) VOLUME DAMPER FIRE DAMPER AND/OR 300 mm 300 mm ORIFICE PLATE MIN. MIN EXHAUST BLEED AIR SOURCE DUCT EXHAUST DUCT CONSTRUCTION AND CLEARANCES HVAC DUCT CONSTRUCTION Fig. 1 Bleed Method of Introducing Outdoor Air Directly into Exhaust Duct (Brohard et al. 2003) Inc. ASHRAE, 2019 user. single for Licensed | {}
06bae84e-edef-48d4-803e-7698e118bef4 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 34.6 2019 ASHRAE Handbook- -HVAC Applications (SI) system must ensure proper capture and containment under maximum cooking load conditions. The majority of kitchen exhaust systems use fixed-speed fans, which move the same volume of air at a given speed regardless ofair density. Although the air volume remains con- stant, heat and moisture generated by the cooking process affect mass flow. Exhaust fans for kitchen ventilation systems, like for other high- temperature exhaust processes, must be selected to provide ade- quate airflow at standard conditions to meet the mass flow needs of the actual cooking process. Testing for hood listing in accordance with UL Standard 710, for example, requires capture and contain- ment testing using actual cooking, with cooking appliance heated to controlled surface temperatures and food product cooked, including flare-ups, to determine airflow. This airflow must be converted to standard air conditions to provide proper design ratings for fan selections. 1.4 ENERGY CONSIDERA TIONS Restaurants and commercial kitchens are the largest consumers of energy per unit of floor area when compared to other commercial or institutional occupancies (Itron and California Energy Commis- sion 2006). Primary drivers of commercial kitchen energy use are the cooking appliances and the HVAC system. Often, the largest energy-consuming component in a commercial food service facility is the kitchen exhaust. However, energy consumption associated with commercial kitchen ventilation (CKV) and HVAC systems, as well the conservation potential, can vary significantly (Fisher 2003). Beyond the design exhaust ventilation rate itself, the magni- tude of energy consumption and cost of a CK v system is affected by factors such as geographic location (i.e., climate), system operating hours, static pressure and fan efficiencies, replacement air heating and cooling set points and level of dehumidification, efficiency of heating and cooling systems, level of interaction between kitchen and building HV AC system, appliances under the hood and associ- ated radiant heat gain to space, and applied utility rates. Minimizing the exhaust airflow needed for cooking appliances and reducing ra- diant load from the appliances are primary considerations in opti- mizing CKV system design. Because climatic zones vary dramatically in temperature and humidity, energy-efficient designs have widely varying rates of returns on the investment. In new fa- cilities, the designer can select conservation measures suitable for the climatic zone and the HV AC system to maximize the economic benefits. The operating cost burden has stimulated energy efficiency design concepts and operating strategies discussed in this section and detailed in industry design guidelines (PG&E 2004). It has also impacted changes to ASHRAE Standard 90.1. The Kitchen Exhaust Systems section of ASHRAE Standard 90.1 states that if a CKV system has a total exhaust airflow rate greater than 2.4 m3/s, the design must adhere to maximum exhaust rates specified for the different hood types. These rates apply to listed hoods, and are set 30% below the minimum values for unlisted hoods dictated by the International Mechanical CodeⓇ (IMC) (ICC 2018). If a kitchen or dining facility has a total kitchen hood exhaust airflow rate greater than 2.4 m3/s, it must have one of the following: · At least 50% of all replacement air is transfer air that would oth- erwise be exhausted · Demand ventilation system(s) on at least 75% of the exhaust air, capable of at least 50% reduction in exhaust and replacement air system airflow rates, including controls necessary to modulate air- flow in response to appliance operation and to maintain full cap- ture and containment of smoke, effluent, and combustion products during cooking and idle · Listed energy recovery devices with a sensible heat recovery ef- fectiveness of not less than 40% on at least 50% of the total ex- haust airflow Energy Conservation Strategies Specifying Exhaust Hoods for Minimal Airflow. The type and style of exhaust hood selected depends on factors such as restaurant type, restaurant menu, and food service equipment installed, as well as flexibility for future kitchen upgrades. Exhaust flow rates are largely determined by the food service equipment and hood style. Wall-mounted canopy hoods function effectively at lower exhaust flow rates than single-island hoods. Single- and double-island can- opy hoods are more sensitive to replacement air supply and cross drafts than wall mounted canopy hoods (Swierczyna et al. 2010). Engineered back shelf (proximity) hoods may exhibit the lowest capture and containment flow rates. In some cases, a back shelf hood performs the same job as a wall-mounted canopy hood at one- third the exhaust rate. Cooking appliance type and duty rating must be included in the specification process, because not all hoods (par- ticularly back shelf hoods) are rated or designed for all cooking appliance types or duty ratings. Threshold exhaust rates for a specific hood and appliance con- figuration may be determined by laboratory testing under the spec- ifications of ASTM Standard F 1 704-17. Similar in concept to the listed airflow rates derived from UL Standard 710, the threshold of containment and capture (C&C) for an ASTM Standard F1 704 test is established under ideal laboratory conditions and is only a refer- ence point for specifying the exhaust airflow rate for a CKV system. Side Panels and Overhang. In many cases, side (or end) panels allow a reduced exhaust rate because they direct replacement air- flow to the front ofthe hood and cooking equipment. They are a rel- atively inexpensive way to improve capture and containment and reduce the total exhaust rate. Itis important to know that partial side panels can provide almost the same benefit as full panels. Although tending to defy its definition as an "island" canopy, end panels can improve the performance of a double- or single-island canopy hood. A significant benefit of end panels, when hoods are exposed to cross drafts, is mitigation of the negative effect those drafts have on hood performance. However, air distribution designs that elim- inate cross drafts are preferred. Increasing overhang is another specification detail that can improve the hood's ability to capture and allow reduced exhaust rates. It is important that the engineer and food service designers work closely on appliance placement size and type, because they affect hood sizing, which in turn affects lighting, HVAC, and most importantly hood performance. A hood that is too small (i.e., little or no overhang) may often not be capa- ble of working properly at any airflow rate, whereas those with generous overhang may operate well at airflow rates reduced by 30% or more. Custom-Designed Hoods. Hoods can be custom designed for specific cooking appliances or cooking processes. Customization often reduces exhaust and replacement air quantities and conse- quently reduces fan sizes, energy use, and energy costs. To operate at flow rates lower than required by code, custom-designed hoods must be either listed or approved by the local code official. The cost involved with custom design makes the process more appli- cable to chain restaurants, such as quick service, where a specific design may be installed repeatedly. Some single-site establish- ments may have architectural restrictions that demand a custom solution. Transfer Air. ASHRAE Standard 62.1 specifies the quantity of outdoor air that must be provided to ventilate public spaces, such as dining rooms, in food service establishments. Standard 62.1 allows this ventilation air to be reused by transfer from the ventilated public spaces to the kitchen, where it can be used to replace air exhausted by the hood system and assist kitchen comfort. Transfer air must meet Inc. ASHRAE, 2019 user. single for Licensed | {}
4354ee75-a513-4508-bb07-e13eaad60fbe | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Kitchen Ventilation 34.7 the requirements as prescribed in ASHRAE Standard 62.1 (section 5.16.3). By maximizing transfer of air from adjoining public spaces to the kitchen, the designer is able to minimize the quantity of dedicated outdoor air supplied to the kitchen as replacement air. This can reduce the energy load on the replacement air system, as well as improve thermal comfort in the kitchen. Most quick-service and fast-casual restaurants do not physically segregate the kitchen from the dining room, so conditioned air can be easily transferred from the dining area to the kitchen. In restaurants where the kitchen and dining room are physically segregated, ducts between the two areas may be required for proper flow of replacement air into the kitchen. Transfer fans may be required to overcome duct losses, because the differential pressure between spaces may be very low (<1.25 Pa). This design can reduce kitchen replacement air requirements and enhance employee com- fort, especially ifthe kitchen is not air conditioned. Codes may restrict transfer of air from adjoining spaces, other than public dining areas, in buildings such as hospitals. Adjoining spaces should not be overven- tilated to increase transfer airflow, because the heating and cooling conditions for dining and other public spaces are more energy-intense than for conditioning replacement air introduced directly into the kitchen. Demand-Controlled Kitchen Ventilation Demand-controlled kitchen ventilation (DCKV) refers to any engineered, automated method of modulating (e.g., variable reduc- tion) the amount of air exhausted for a specific cooking operation in response to a part-load or no-load condition (e.g., by duct tempera- ture, opacity, or appliance surface temperatures). A DCKV system is different from a DCV system in that the con- trolling demand factor is the kitchen 's cooking operations and not space carbon dioxide (CO2) levels. In conjunction with this, the amount of replacement air (consisting of makeup, transfer, and out- door air) is also modulated to maintain the same relative air ratios, airflow patterns, and pressurizations. Failure to integrate systems could cause negative pressure. The design of all involved ventilation systems must account for DCKV, to create a fully integrated system. Complete capture and containment of all smoke and greasy vapor must be maintained when a DCKV exhaust system operates at less than 100% of design airflow. Selection of all components, and design of the DCKV system, must be such that stable operation can be maintained at all modu- lated and full-flow conditions. When DCKV is used as the method of compliance with ASHRAE Standard 90.1 (section 6.5.7.1.4 part b), it must meet all requirements of that section. When DCKV is used as the method of compliance with ASHRAE Standard 62.1 it must meet the minimum exhaust air rates per Table 6.5 and minimum ventilation air rates per Table 6.2.2.1, ensuring ventilation during periods of occupancy. The exhaust system configuration and equipment to be served by a DCKV system must be evaluated to determine the feasibility and cost benefits resulting from its use. An example of a situation where a DCKV system may not be appropriate is when gas-underfired broilers are present. Evaporative Cooling. Direct evaporative coolers are an alterna- tive to mechanical cooling (or, for that matter, no cooling) of re- placement air only in dry climates where dehumidification is not required. Indirect evaporative cooling has a wider range in geo- graphical applications. Water costs, availability, and use restrictions should be considered. Heat Recovery from Exhaust Hood Ventilation Air. High- temperature effluent, often in excess of 200°C, from the cooking equipment mixes with replacement room air, resulting in exhaust air temperatures well over 35°C. It is frequently assumed that this heated exhaust air is suitable for heat recovery; however, over time, smoke and grease in the exhaust air can foul the heat transfer sur- faces. Under these conditions, the heat exchangers require regular maintenance (e.g., automatic washdown) to maintain heat recovery effectiveness and mitigate risk of fire. Because heat recovery sys- tems are expensive, food service facilities with large ventilation rates and relatively light-duty cooking equipment are the best can- didates for this equipment. Hospitals are a good example, with large exhaust rates and very low levels of grease production from the ![image](/image/placeholder) MUA UNIT EXHAUST FAN 00 00 DCKV CONTROLLER VFDS 료 COOKING LOAD DETECTION SENSORS LOCATED IN THE FIRE HOOD AND DUCT SUPPRESSION Fig. 2 Typical DCKV Equipment and Configuration Inc. ASHRAE, 2019 user. single for Licensed | {}
1202f829-5132-46f6-917e-82affeb3c6cf | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 34.8 2019 ASHRAE Handbook-HVAC Applications (SI) cooking equipment. An exhaust hood equipped with heat recovery is more likely to be cost-effective where the climate has very cold winters (well below 0°C). A mild climate is not conducive to use of this conservation measure. See Chapter 26 in the 2016 ASHRAE Handbook-HVAC Systems and Equipment for more information on air-to-air heat recovery. Optimized Heating and Cooling Set Points. IMC (ICC 2018) re- quires that replacement air be conditioned to within 5.6 K of the kitchen space, except when replacement air is part of the air-condition- ing system and does not adversely affect comfort conditions in the occupied space. The exception is important because it allows the design to be optimized to take advantage of the typically lower heating balance points of commercial kitchens. A commercial kitchen may be considered comfortable at temperatures of up to 29°C when space humidity is 60%. During heating seasons, space humidity is typically not an issue if the kitchen exhaust sys- tems are properly designed and operated. During the heating sea- son, space gains from unhooded appliances and radiant gains from hooded appliances, lighting, refrigeration units, and staff make it possible to maintain comfort using lower supply air temperatures. During cooling seasons, in climatic areas that require dehumidifi- cation, consideration must be given to all sources that may intro- duce moisture into commercial kitchens, including internal cooking, holding, and washing as well as local makeup air (MUA) systems or kitchen HV AC systems not designed for continuous de- humidification. Humidity control ( 60%) allows optimization of cooling set points at higher temperatures while maintaining a comfortable working environment. A dedicated outdoor air system (DOAS) providing conditioned outdoor for kitchen heating, cooling, and dehumidification also optimizes set points by using economizer operation when outdoor air alone (no conditioning) can maintain kitchen set points. Using dedicated outdoor air to heat, cool, and dehumidify outdoor air to control space comfort and humidity and replace air exhausted through the hood has been demonstrated to be an energy-effective design for optimizing heating and cooling set points (Brown 2007). Accordingly, when local MUA systems are used, it is essential that the heating set point of those units not be set higher than the forecasted heating/cooling balance point (e.g., 13°C) to avoid simultaneous replacement air heating and HVAC cooling. It may be more difficult to control comfort when local MUA (e.g., at 13°C) is introduced into a kitchen being heated by a conventional HVAC system introducing kitchen supply air at temperatures 27°C. Reduced Exhaust and Associated Duct Velocities Tempering outdoor replacement air can account for a large part of a food service facility's heating and cooling costs. By reducing exhaust flow rates (and the corresponding replacement air quantity) when little or no product is being cooked, energy cost can be sig- nificantly reduced when combined with a DCKV system. Field evaluations by one large restaurant chain suggest that cooking ap- pliances may operate under no-load conditions for 75% or more of an average business day (Spata and Turgeon 1995). However, it has been difficult to reduce exhaust flow rates in a retrofit situation because of the minimum duct velocity restriction. National Fire Protection Association (NFPA) Standard 96 had historically required a minimum duct velocity of 7.62 m/s. The common belief was that, if duct velocity were lowered, a higher per- centage of grease would accumulate on the ductwork, which would then require more frequent duct cleaning. However, no data or research could be identified to support this assumption. Therefore, ASHRAE research project RP-1033 (Kuehn 2000) was undertaken to determine the true effect of duct velocity on grease deposition. The project analyzed grease deposition as a function of mean duct velocity, using octanoic acid (commonly found in cooking oils and other foods). The results showed that, for design duct velocities below the traditional 7.5 m/s threshold, grease deposition was not increased; in fact, in isothermal conditions, as duct velocity de- creased, grease deposition on all internal sides of the duct also decreased. These results led to NFPA Standard 96 and the IMC changing their minimum duct velocity requirements from 7.62 m/s to 2.54 m/s. Another significant finding in the study was that, if there is a large temperature gradient between exhaust air inside the duct and the external duct wall, the rate of grease deposition increases sig- nificantly. Therefore, duct insulation should be considered where there are large temperature variations. The primary benefit of these code-approved duct velocity chang- es is the potential for reduced food service energy consumption. By reducing excessive exhaust airflows, while maintaining necessary capture and containment, energy for fans as well as for heating, cooling and/or dehumidifying air that was previously wasted may now be saved. Previously, if a restaurant remodeled their cooking operation and the remodel resulted in reduced exhaust airflows, the owner had to install new, smaller-diameter ductwork to comply with the 7.62 m/s duct velocity requirement. This is often too costly, if not also physically impractical. Now, if a system designed for heavy-duty equipment upgrades to more energy-efficient, lighter- duty equipment, exhaust airflows can be reduced without the ex- pense of modifying ductwork. Reduced code-approved duct velocity also facilitates application of DCKV systems with less resistance from local code authorities. From a new-facility design perspective, it is recommended that most kitchens be designed for an in-duct velocity between 7.62 and 9.1 m/s. This allows for reducing the airflows to 2.5 m/s if needed in the future or as part of a demand-ventilation control strategy. Due to a higher risk of duct fires associated with solid-fuel cook- ing equipment, the DCKV application is typically limited to two- speed on/off fan cycles. Dampers, if used for solid fuel, must adhere to the requirement ofliquidtight connection and must not downgrade the ductwork. The dampers are mechanically locked in position and must be approved by a fire inspector. NFPA Standard 96 requires listed dampers for the application. Duct sizes for solid fuel typically maintain 7.62 m/s duct velocity. Exhaust from heavy-duty solid fuel cooking can be treated and cooled down by an in-line water mist duct section. The duct system monitors and cycles water mist to maintain a set exhaust tempera- ture threshold. Listed grease ducts have a threshold not exceeding 260°C for continuous exhaust. The design temperature must consid- er flammability of creosote buildup on duct walls, produced from solid fuel burning as it mixes with cooking vapor from cooking. Creosote and soot mixtures on duct walls can have a lower flash point than grease alone and pose a fire hazard (see the Fire Safety section). Dishroom Ventilation Many different types of dishwashing and warewashing equip- ment are used in the food service industry: powered sink washers; troughs; undercounter, door-type, conveyor-type, and flight-type warewashers; and rack washers. Ancillary equipment such as pre- rinse valves, scrappers, hoses, and drying dishes are also sources of loads. Each type of equipment operates differently and generates different levels of sensible, latent, and moisture loads to the space. Loads depend on whether the appliance is ventilated, whether san- itization occurs by hot water or chemicals, and the effectiveness of the local ventilation. Historically, data on heat gains and cooling loads have been scarce. This made it difficult to estimate loads, leading to potentially undersized ventilation and resulting in hot and humid dishrooms with condensation on walls and supply diffusers. ASHRAE research is currently under way to determine heat and moisture loading from these types of equipment. ASHRAE research project Inc. ASHRAE, 2019 user. single for Licensed | {}
b56c564b-0b8c-4b71-b9a7-213ee9fd6897 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Kitchen Ventilation 34.9 RP-1469 (Stoops et al. 2013) found that dishrooms had latent and sensible loads significantly larger than the spaces were designed for, resulting in hot and humid space conditions and the possibility of mold growth. International Mechanical CodeⓇ (ICC 2014), section 507.3, states that: "type II hoods shall be installed above dishwashers and appliances that produce heat or moisture and do not produce grease or smoke as a result of the cooking process, except where the heat and moisture loads from such appliances are incorporated into the HVAC system design or into the design of a separate removal system. The only reliable data for the calculations are listed in Table 5F from Chapter 18 of the 2017 ASHRAE Handbook-Fundamen- tals. The internal heat gain calculation is essentially the same for hooded and unhooded appliances. For unhooded dishwashers, the total latent and sensible (convective and radiant) emissions load the space. The designer cannot assume there is no load from low-tem- perature and heat recovery models. For hooded dishwashers, the emissions are the sensible radiant load. However, if ventilation is inadequate, an appreciable amount of convective load can spill into the space and create hot and humid conditions. Only limited heat gain values are available from manufacturers. Manufacturers have only recently begun applying ASTM Standard F2474 to determine sensible and latent loads from dishwashers. Un- derwriters Laboratories' new listing and labeling program requires heat recovery dishwashers to list and label the sensible and latent loads during heavy-load operations. Heat gain testing per ASTM Standard F2474 is a requirement for heat recovery dishwashers as part of a supplement to UL Standard 921. Industry is beginning to realize the opportunities and benefits of heat recovery in a commercial food service facility. The range of application varies from air-to-water heat exchangers above fryer flues, to grease filters incorporating fin-and-tubes to transfer the high-quality heat to preheat water for the dish machine or water heater or to preheat makeup air. In any case, heat exchanger effec- tiveness ranges between 18 and 63%. The designer must realize that not all the heat is recovered: some amount ofheat (both sensible and latent) is released to the space. In the same way, a recirculating or ductless hood system loads the space with nearly the entire plug load from the hood/appliance system. Heat is emitted to the space from heat recovery kitchen equipment, depending on the effective- ness of the heat exchanger. Table 5F in Chapter 18 of the 2017 ASHRAE Handbook-Fundamentals lists the residual heat gain for a few dish machine types. However, as designs become more effi- cient (e.g., heat pump dish machines releasing 20 to 21 °C dry-bulb temperatures), there is always an amount of moisture that must be considered along with elevated dry-bulb temperatures. Designing for High-Performance Green Building Compliance under ANSI/ASHRA E/USGBC/IES Standard 189.1 There are several sections in this standard that any CKV system must comply with in order to be considered a high-performance green building. Air-Side Economizer Controls for Replacement Air (Makeup Air). Given the large quantities ofreplacement air typically required for a CKV system, the use of air-side economizers should be eval- uated for every location. This evaluation should include comparing the CKV system 's typical daily hours of operation to the number of hours of free cooling available in the local climate. Some locations in ASHRAE climate zones 1A and 1B may still benefit from using air-side economizers, especially if they operate enough hours of the year that they can take advantage of free cooling. ENERGY STAR Appliances. Commercial food service appli- ances (e.g., fryers, hot food holding cabinets, refrigerators and freez- ers, steam cookers, ice machines, dishwashers, griddles, ovens) should bear the ENERGY STAR label. Equipment selection guid- ance and specifications can be found at www.energystar.gov/. DCKV for Airflow Greater than 0.9 m3/s. Kitchen/dining facilities with total kitchen hood exhaust airflow rates above 0.9 m3/ s must comply with at least one of the following: · At least 50% of all replacement air must be transfer air that would otherwise be exhausted. · At least 75% of kitchen hood exhaust air must be controlled by a demand ventilation system(s), which must (1) be able to reduce exhaust and replacement air system airflow rates by no more than the larger of 50% of total design exhaust and replacement air system airflow rate, or the outdoor airflow and exhaust rates required to meet the ventilation and exhaust requirements of Sec- tions 6.2 and 6.5 of ANSI/ASHRAE Standard 62.1 for the zone; (2) include controls to modulate airflow in response to appliance operation and to maintain full capture and containment of smoke, effluent, and combustion products during cooking and idle; (3) include controls that result in full flow when the demand ventila- tion system(s) fail to modulate airflow in response to appliance operation; and (4) allow occupants to temporarily override the system(s) to full flow. · Listed energy recovery devices with a sensible heat recovery ef- fectiveness of not less than 40% must be applied on at least 50% of the total exhaust airflow. · In climate zones 1B, 2B, 3B, 4B, 5B, 6B, 7B, and 8B, when re- placement air is uncooled or cooled without mechanical cooling, the capacity of any nonmechanical cooling system(s) (e.g., natu- ral or evaporative cooling) must be demonstrated to be no less than the system capacity of a mechanical cooling system(s) nec- essary to meet the same loads under design conditions. Outdoor Airflow Measuring. Each mechanical ventilation system shall have a permanently installed device to measure the minimum outdoor airflow rate that meets the following require- ments: · The device must use methods described in ASHRAE Standard 111. · The device , s accuracy must be 10% of the minimum outdoor air- flow. Where the minimum outdoor airflow varies, as in demand control ventilation systems, the device must maintain this accu- racy over the entire range of occupancy and system operation. · The device must be able to notify the building operator, either by activating a local indicator or by sending a signal to a building monitoring system, whenever an outdoor air fault condition exists. This notification requires manual reset. Exception: Constant-volume air supply systems that do not use demand control ventilation and use an indicator to confirm that the intake damper is open to the position needed to maintain design minimum outdoor airflow do not require notification ability. Energy Measurement Devices. Energy consumption must be measured by devices to track and record energy profiles so that peri- odic assessments can be made to assure continued future perfor- mance. In addition to whole-building monitoring, submetering may be required on specific appliance lineups depending upon capacity. See section 7 of ANSI/ASHRAE/USGBC/IES Standard 189.1 for additional information. Commissioning. Facilities with a gross floor area over 465 m2 must be commissioned. Commissioning is essential to ensure that the building, including the kitchen exhaust and HVAC systems, functions as intended. For additional information on high perfor- mance building commissioning requirements, see section 10 of ANSI/ASHRAE/USGBC/IES Standard 189.1. Inc. ASHRAE, 2019 user. single for Licensed | {}
04ee8995-c114-4cb6-afff-5bc8692b8936 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 34.10 2019 ASHRAE Handbook-HVAC Applications (SI) 1.5 THERMAL COMFORT Due to the many heating, ventilation, and air conditioning oper- ations that can occur (sometimes simultaneously) in a commercial kitchen, determining parameters for a thermally comfortable envi- ronment poses a challenge. ASHRAE research project RP-1469 (Stoops et al. 2013) was executed in response to this dilemma. Data were gathered by surveying kitchen workers in over 100 U.S. restaurants, including casual dining, institutional, and quick-service restaurant dishrooms, in different climates, in both summer and winter. The data points were evaluated to quantify thermal comfort in commercial kitchens (Figure 3). The researchers developed a kitchen comfort zone as a region of the psychrometric chart, including a region with a percent dissatis- fied PD < 12%. However, nearly 60% of the temperature and humidity data collected in the study were outside the bounds of the comfort zone. The operative temperature was as high as 42°C, and relative humidity was as high as 78%. Such conditions lead to poor working environment, low productivity, bad morale, and mold growth. Based on these results, it is recommended that commercial kitchen design conditions should align with the results shown on the chart, with maximum dry-bulb temperature of 46°C and humidity 60%. Dishwashing Area Previously, there was inadequate design data to calculate the internal loads from dishwashing equipment. This resulted in under- sized HVAC equipment and poor air distribution, leading to hot and humid kitchens. The findings of RP-1469 determined that the oper- ative temperatures were as high as 29°C and with 71% rh; the cor- relating average predicted mean vote was above 2 (warm). The long-term measurements found considerable daily temperature variations in the dishwashing area from 24 to 32°C during working hours. If the dishwashing area was open to the cooking line, the thermal radiation from the hot appliance line raised the operative temperature by an additional 5.6 K, it was reported to peak as high as 39°C. The relative humidity in the kitchen space was recorded during the working hours in the three different kitchen zones (i.e., cook line, prep line, and dishwashing area). The relative humidity was up to 55% higher in the dishwashing area than in the other two zones. Long term data at some quick serve restaurants recorded humidity averages up to 69% in the dishwashing area during the summer. 1.6 COMMERCIAL EXHAUST HOODS The design, engineering, construction, installation, and mainte- nance of commercial kitchen exhaust hoods are governed by nation- ally recognized standards (e.g., NFPA Standard 96) and model codes (e.g., the IMC, International Fuel Gas Code [IFGC; ICC]). In some cases, local codes may prevail. Before designing a kitchen ventilation system, the designer should identify governing codes and consult the AHJ. Local authorities with jurisdiction may have amendments or additions to these standards and codes. The type of hood required, or whether a hood is required, is de- termined by the type and quantity of emissions from cooking. Hoods are not typically required over electrically heated appliances such as microwave ovens, toasters, steam tables, popcorn poppers, Chart Type: line WET BULB TEMPERATURE RELATIVE HUMIDITY WEIT BULB TEMPERATURE item_01 100% 80% 60% Fig. 3 Thermal Comfort Zone for Commercial Kitchens Work Space Based On the Results From RP-1469: Comfort in Commercial Kitchens (Stoops et al. 2013) Inc. ASHRAE, 2019 user. single for Licensed | {}
7b2e4fdc-b0e9-4ffc-9834-70dabb9f6a13 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Kitchen Ventilation 34.11 hot dog cookers, coffee makers, rice cookers, egg cookers, holding/ warming ovens (as mentioned in ASHRAE Standard 154), or heat lamps. Appliances can be unhooded only if the additional heat and moisture loads have been considered in a thorough load calculation and accounted for in design of the HVAC system. Temperature and humidity in the kitchen space should be based on recommendations of ASHRAE Standard 55. Hood Types Many types, categories, and styles of hoods are available, and selection depends on many factors. Hoods are classified by whether they are designed to handle grease; Type I hoods are designed for removing grease and smoke, and Type II hoods are not. Model codes distinguish between grease-handling and non-grease-handling hoods, but not all model codes use Type I/Type II terminology. A Type I hood may be used where a Type II hood is required, but the reverse is not allowed. However, characteristics of the equipment and processes under the hood, and not necessarily the hood type, determine the requirements for the entire exhaust system, including the hood. A Type I hood is used for collecting and removing grease par- ticulate, condensable vapor, and smoke. It includes (1) listed grease filters, baffles, or extractors for removing the grease and (2) fire- suppression system. Type I hoods are required over cooking equip- ment that produce smoke or grease-laden vapors (e.g., ranges, fry- ers, griddles, gas underfired and electric broilers, ovens). A Type II hood collects and removes steam and heat where grease or smoke is not present. It may or may not have grease filters or baffles and typically does not have a fire-suppression system. Itis usually used over dishwashers. A Type II hood is sometimes used over ovens, steamers, or kettles if they do not produce smoke or grease-laden vapor and as authorized by the AHJ. Type I Hoods Categories. Type I hoods fall into two categories: unlisted and listed. Unlisted hoods are no longer allowed under ASHRAE Stan- dard 154. However, if they are used, they must meet the design, construction, and performance criteria of applicable national and local codes and are not allowed to have fire-actuated exhaust damp- ers. Listed hoods are listed in accordance with Underwriters Labo- ratories (UL) Standard 710 and are constructed in accordance with the terms of the hood manufacturer' s listing, and are required to be installed in accordance with either NFPA Standard 96 or the model codes. Model codes include exceptions for listed hoods to show equivalency with the model code requirements. The two subcategories of Type I listed hoods, as covered by UL Standard 710, are exhaust hoods with and without exhaust dampers. UL listings also distinguish between water-wash and dry hoods. All listed hoods are subjected to electrical (if applicable), tem- perature, and cooking smoke and flare-up (capture and contain- ment) tests. A listed exhaust hood with exhaust damper includes a fire-actuated damper, typically at the exhaust duct collar. In the event of a fire, the damper closes to prevent fire from entering the duct. Fire-actuated exhaust dampers are permitted only in listed hoods. Also, listed hoods that incorporate an integral supply air plenum include a fire-actuated damper in that plenum; the damper's location in the supply air plenum depends on plenum configuration. Refer to NFPA Standard 96 and UL Standard 710 for examples of the damper in exhaust hood supply air plenum. Grease Removal. Most grease removal devices in Type I hoods operate on the same general principle: exhaust air passes through a series of baffles that create a centrifugal force to throw grease par- ticles out of the airstream as the exhaust air passes around the baf- fles. The amount of grease removed varies with baffle design, air velocity, temperature, type of cooking, and other factors. NFPA Standard 96 does not allow use of mesh-filter as primary grease filter. To date, stand-alone mesh filters have not met the require- ments of UL Standard 1046, and therefore cannot be used as prima- ry grease filters. For cooking with solid-fuel equipment, embers from wood burning promote duct fires. The grease filters for solid- fuel hoods are supplied with metal screens to protect to some extent against embers entering the exhaust duct. Typically, design practice for heavy-duty solid-fuel cooking equipment evaluates if water mist cooling is required to protect the exhaust system from duct fires. ASTM Standard F2519 provides a test method to determine the grease particle capture efficiency of grease filters and extractors. Grease removal devices generally fall into the following types: · Baffle filters have a series of vertical baffles designed to capture grease and drain it into a container. The filters are arranged in a channel or bracket for easy insertion and removal for cleaning. Each hood usually has two or more baffle filters, which are typi- cally constructed of aluminum, steel, or stainless steel and come in various standard sizes. Filters are cleaned by running them through a dishwasher or by soaking and rinsing. NFPA Standard 96 requires that grease filters be listed. Listed grease filters are tested and certified by a nationally recognized test laboratory in accordance with UL Standard 1046. · Removable extractors (also called cartridge filters) have a sin- gle horizontal-slot air inlet. The filters are arranged in a channel or bracket for easy insertion and removal for cleaning. Each hood usually has two or more removable extractors, which are typically constructed of stainless steel and contain a series of horizontal baffles designed to remove grease and drain it into a container. Available in various sizes, they are cleaned by running them through a dishwasher or by soaking and rinsing. Removable ex- tractors may be classified by a nationally recognized test labora- tory in accordance with UL Standard 1046, or may be listed as part of the hood in accordance with UL Standard 710. Hoods that are listed with removable extractors cannot have those extractors replaced by other extractors. · Stationary extractors are integral to the listed water-wash ex- haust hoods and are typically constructed of stainless steel and contain a series ofhorizontal baffles that run the full length of the hood. The baffles are not removable for cleaning, though some have doors that can be removed to clean the extractors and plenum. · Water-wash hoods fall into two classifications: clean-in-place and cold-water mist styles. Clean-in-place hoods reduce or elim- inate the need for kitchen staff to manually clean the hood com- ponents; these hoods may have fixed stationary or removable grease extractors. These systems may automate the removal of the grease load on the filters, hood plenums, and ductwork. Typ- ical hoods include one or more manifolds with spray nozzles that, when activated, wash out the collected grease with hot, detergent-injected water. The wash cycle is activated periodi- cally, typically after cooking equipment and fans have been turned off. Washdown cycles can lasts 3 to 10 min, depending on the hood manufacturer, type of cooking, duration of operation, water temperature, and pressure. Most water-wash hood manu- facturers recommend a water temperature of 54 to 80°C and water pressure of 200 to 550 kPa. Average water consumption varies from 0.1 to 0.3 L/s per linear metre of hood, depending on man- ufacturer. Most water-wash hood manufacturers provide an optional automatic means of activating the water-wash system in the event of a fire. Some water-wash hood manufacturers provide continuous cold water mist as an option. The cold water runs continuously during cooking and may or may not be recirculated, depending on the manufacturer. Typical cold-water usage is 3.5 mL/s per linear metre of hood. The advantage of this method is that it improves grease extraction and removal, partly through condensation of the Inc. ASHRAE, 2019 user. single for Licensed | {}
1b48da4f-b71d-4f5e-bb72-3e83e73f53ea | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 34.12 2019 ASHRAE Handbook- -HVAC Applications (SI) grease. Many hood manufacturers recommend continuous cold water in hoods located over solid-fuel-burning cooking equipment, because the water acts as a spark arrestor to satisfy code require- ments. Multistage filters use two or more stages of filtration to remove a larger percentage of grease. They typically consist of a baffle filter or removable extractor followed by a higher-efficiency filter, such as a packed bead bed. Each hood usually has two or more multi- stage filters, which are typically constructed of aluminum or stain- less steel and are available in standard sizes. Filters are cleaned by running them through a dishwasher or by soaking and rinsing. NFPA Standard 96 requires that grease filters be listed, so these multistage filters must be tested and certified by a nationally rec- ognized test laboratory in accordance with UL Standard 1046. UL Standards 710 and 1046 do not include grease extraction effi- ciency tests. Historically, grease extraction efficiency rates published by filter and hood manufacturers were usually derived from tests conducted by independent test laboratories retained by the manufac- turer. Test methods and results therefore have varied greatly. In 2005, however, a new grease filter and extractor test standard was published: ASTM Standard F2519, which determines the grease particle capture efficiency ofboth removable filters and fixed extractors such as those used in water-wash hoods. The filters are evaluated by pressure drop as well as particulate capture efficiency. The test generates a controlled quantity of oleic acid particles in size ranging from 0.3 to 10 m that are released into a hood to represent the cooking effluent. The particles are then sampled and counted downstream in the duct with an optical particle counter, with and without the filter or extractor in place. The difference in the counts is used to calculate the particulate capture efficiency graphed versus particle size. ASTM Standard F2519 measures particulate capture efficiency only, not vapor removal efficiency. A more detailed expla- nation is available in the Exhaust Systems section of this chapter. · Wall-mounted canopy, used for all types of cooking equipment located against a wall. · Back shelf/proximity, used for counter-height equipment typi- cally located against a wall, but possibly freestanding. · Pass-over, used over counter-height equipment when pass-over configuration (from cooking side to serving side) is required. · Single-island canopy, used for all types of cooking equipment in a single-line island configuration. · Double-island canopy, used for all types of cooking equipment mounted back-to-back in an island configuration. · Eyebrow, used for direct mounting to ovens and some dishwashers. Styles. Figure 4 shows the six basic styles for Type I hood appli- cations. These style names are not used in all standards and codes but are well accepted in the industry. The styles are as follows: Applying Back-Shelf-Style Exhaust Hoods. Due in part to the close proximity of back shelf hoods to the cooking surface, when back shelf hoods are properly applied over appropriate appliances, the exhaust airflow may be reduced to achieve significant energy savings by reducing both exhaust fan motor energy use and makeup air energy. In addition to lower airflows, back shelf hoods can pro- vide health and comfort advantages by exhausting cooking effluent back away from and below the operator's breathing zone. Close proximity to the appliance also creates the potential for a more open ceiling space, which may be used to locate ceiling lighting fixtures to properly illuminate both the kitchen and appliance work surfaces, as well as providing open ceiling spaces to optimize location of HVAC diffusers. Back shelf hoods operate best when located over appropriate appliances, such as those with flat horizontal cooking surfaces, including griddles, under-fired broilers, and deep fat fryers. How- ever, not all appliances can be properly operated when located under a back shelf hood. Examples are upright appliances such as ovens, Fig. 4 Styles of Commercial Kitchen Exhaust Hoods ![image](/image/placeholder) Sts 1 일 WALL-MOUNTED CANOPY BACK SHELF PASS-OVER SINGLE-ISLAND CANOPY DOUBLE-ISLAND CANOPY EYEBROW Inc. ASHRAE, 2019 user. single for Licensed · | {}
675256b5-d425-41a9-a074-5c3b1c9c9cb6 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Kitchen Ventilation 34.13 unless specifically design for such use, and appliances with lids that block effluent from entering the hood, such as tilting fry pans. Itis important to match appliance and hood duty ratings, because maintaining proper capture and containment airflow rates is critical for back shelf hoods. Be mindful of how required setback and side overhang will be impacted by final appliance placement. Consider also the impact of gas lines, electrical connection, and even appli- ance gas regulators on final appliance location. Sometimes these connection points can cause the appliances to be relocated so that they are no longer properly located under the hood. These hoods require a more detailed analysis of operation and future menu considerations. Additionally, application of back shelf hoods requires more coordination between specifiers and users to be sure selections support food service operations. Attention should also be paid to the need to enclose or trim the connecting exhaust duct runs in a manner that complies with both fire safety and health regulations. It is also necessary to confirm that a fixed-pipe fire suppression system can be designed and installed to provide proper fire safety protection for the appliances and the exhaust system. Do not specify back shelf hoods over cooking appliances or cooking operations than cannot be properly protected by an approved fire suppression system. Sizing. The size of the exhaust hood relative to cooking appliances is important in determining hood performance. Usually the hood must extend horizontally beyond the cooking appliances (on all open sides on canopy-style hoods and over the ends on back shelf and pass- over hoods) to capture expanding thermal currents rising from the appliances. For unlisted hoods, size and overhang requirements are dictated by the prevailing code; for listed hoods, by the terms of the manufacturer's listing. Overhang varies with hood style, distance between hood and cooking surface, and characteristics of cooking equipment. With back shelf and pass-over hoods, the front of the hood may be kept behind the front of the cooking equipment (set- back) to allow head clearance for the cooks. These hoods may require a higher front inlet velocity to capture and contain expanding thermal currents. ASHRAE research (Swierczyna et al. 2006, 2010) indicates that an appliance front overhang of230 to 460 mm for can- opy style and a 250 mm setback for back shelf/proximity style are preferable to current code minimums. All styles may have full or par- tial side panels to close the area between appliances and the hood. This may eliminate the side overhang requirement and generally reduces the exhaust flow rate requirement. Exhaust Flow Rates. Exhaust flow rate requirements to capture, contain, and remove effluent vary considerably depending on hood style, overhang, distance from cooking surfaces to hood, presence and size of side panels, cooking equipment, food, and cooking pro- cesses involved. The hot cooking surfaces and product effluent create thermal air currents that are captured by the hood and then exhausted. The velocity of these currents depends largely on surface temperature and tends to vary from 0.08 m/s over steam equipment to 0.8 m/s over charcoal broilers. The required flow rate is deter- mined by these thermal currents, a safety allowance to absorb cross- currents and flare-ups, and a safety factor for the style of hood. Overhang and the presence or absence of side panels help deter- mine the safety factor for different hood styles. Gas-fired cooking equipment may require an additional allowance for exhaust of com- bustion products and combustion air. Because itis not practical to place a separate hood over each piece of equipment, general practice (reflected in ASHRAE Standard 154) is to categorize equipment into four groups, as shown in Table 3. Table 4 lists the required hood type by duty level. These categories apply to unlisted and listed Type I hoods. ASHRAE Standard 154-2016 requires that all Type I hoods be listed; unlisted hoods are not allowed. The exhaust flow rate require- ment is based on the group of equipment under the hood. If there is more than one group, the flow rate is based on the heaviest-duty group unless the hood design allows different rates over different sections of the hood. Though considered obsolete based on laboratory tests and re- search, some local codes may still require exhaust flow rates for un- listed canopy hoods to be calculated by multiplying the horizontal area of the hood opening by a specified air velocity. Some jurisdic- tions may use the length of the open perimeter of the hood times the vertical height between hood and appliance instead ofthe horizontal hood area. Swierczyna et al. (1997) found that these methods of cal- culation result in higher-than-necessary exhaust flowrates for deeper hoods, because the larger reservoirs of deeper hoods typi- cally increase hood capture and containment performance. Table 5 lists typical exhaust flow rates for listed hoods. Typical design rates for listed hoods are based on published rates for listed hoods serving single categories of equipment, which vary from man- ufacturer to manufacturer. Rates are usually lower for listed hoods than for unlisted hoods, and it is generally advantageous to use listed hoods. Actual exhaust flow rates for hoods with internal short-circuit replacement air are typically higher than those in Table 5, although net exhaust rates (actual exhaust less internal makeup air quantity) are lower, which seriously compromises the hood's capture and con- tainment performance (Brohard et al. 2003). Listed hoods are allowed to operate at their listed exhaust flow rates by exceptions in the model codes. The exhaust flow rates for listed hoods are established by conducting tests per UL Standard 710. Typically, exhaust flow rates are much lower than those dic- tated by the model codes. Note that listed flow rate values are estab- lished under draft-free laboratory conditions, and actual operating conditions may compromise listed performance. Thus, manufacturers may recommend design values above their listed val- ues. Hoods listed in accordance with UL 710 cover one or more cooking duty ratings: light, medium, heavy, and extra heavy. These duty ratings correspond to minimum cooking surface temperatures during tests of 103, 205, 315, and 370°C respectively. In applica- tion, these temperature ratings correspond to duty ratings (see Table 4). The total exhaust flow rate is calculated by multiplying the hood exhaust flow rate by hood length. ASTM Standard F1704 details a laboratory flow visualization procedure for determining the capture and containment threshold of an appliance/hood combination. This procedure can be applied to all hood types and configurations installed over any cooking appliances. ASTM Standard F2474 also provides a laboratory test procedure for determining heat gain of specific combinations of exhaust hood, cooking equipment, type of foods, and cooking processes. Results from a series of interlab heat gain tests (Fisher 1998; Swierczyna et al. 2008) have been incorporated in Chapter 18 of the 2017 ASHRAE Handbook- -Fundamentals. Island Canopy Hoods Island canopy hoods, particularly single-island style, have become popular in open cafeteria operations such as those found in university food service. In many cases, the food service consultant specifies gas underfired broilers and other heavy-duty cooking equipment as part of the design. For a given line of appliances, a single-island canopy hood requires significantly more exhaust than a wall-mounted canopy hood. Single-island canopy hoods present the most difficult capture and containment challenge in hood applications, and are often the source of the "hood" problem in a kitchen with display cooking. To address the lack of reliable performance data on island canopy hoods, ASHRAE research project RP-1480 (Swierczyna et al. 2010) was un- dertaken to determine appropriate exhaust airflow rates. The objec- tive was to expand the database for the exhaust rates required for Inc. ASHRAE, 2019 user. single for Licensed | {}
3d210e05-4564-48d0-86fd-9ede9e5ac4b7 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 34.14 Table 3 Appliance Types by Duty Category ¦ Light duty (200°C) ¦ Electric or gas ¦ Ovens (including standard, bake, roasting, revolving, re-therm, convection, combinationconvection/steamer, conveyor, deck or deck-style pizza, pastry) Steam-jacketed kettles Compartment steamers (both pressure and atmospheric) Cheesemelters Re-thermalizers ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Medium duty (200°C) ¦ Electric Electric or gas ¦ Discrete element ranges (with or without oven) Hot-top ranges Griddles Double-sided griddles Fryers (including open deep-fat fryers, donut fryers, kettle fryers, pressure fryers) Pasta cookers Conveyor (pizza) ovens Tilting skillets/braising pans Rotisseries ¦ ¦ Heavy duty (315°C) ¦ Gas Electric or gas ¦ Open-burner ranges (with or without oven) Gas underfired broilers Chain (conveyor) broilers Wok ranges Overfired (upright) salamander broilers ¦ ¦ Extra-heavy duty (370°C) ¦ ¦ Appliances using solid fuel such as wood, charcoal, briquettes, and mesquite to provide all or part of the heat source for cooking. ¦ capture and containment of standardized cook lines under four island canopy hood configurations: rear filter single island, V-bank single is- land, and 2.4 m deep and 3 m deep double-island hoods. Four side panel designs, four supply air strategies, and two makeup air tempera- ture set points were also evaluated to quantify the effects of these fea- tures on island hood performance. Swierczyna et al. (2010) confirmed that single-island canopy hoods need significantly higher exhaust airflow rates than their wall-mounted counterparts to effectively ventilate cooking equip- ment for a given duty class. For example, although an exhaust rate of 460 to 620 (L · s)/m can be adequate for complete capture and containment with a wall-mounted canopy hood over a heavy-duty appliance line (ASHRAE Standard 154; PG&E 2010), a single- island canopy hood may require an exhaust rate in excess of 770 (L ·s)/m in many situations (measured along one side of the canopy hood). In fact, there were several test scenarios for single-island hoods where an exhaust rate in excess of 1080 (L · s)/m was required to achieve capture and containment. This contradicts common design practice, where the specified ventilation rates are often much closer to those for wall-canopy hoods. Single-island hood performance was improved by the larger hood's V-bank filter configuration over the smaller hood' s rear filter configuration for most test configurations. The plume was better aligned with the filters and was drawn toward the center, relative to the front and rear of the hood. The larger v -bank hood was found to be less sensitive to local air replacement. However, aggressive appliance plumes that focused on the flat bottom of the V-bank, or replacement air strategies that were focused at the side of the V- bank, proved challenging and indicated that a change of filter bank profile may improve hood performance. The performance of a double-island canopy hood, with bal- anced replacement air, can be comparable to back-to-back wall- mounted canopy hoods for a given duty class of appliances. For example, a heavy-duty front line and a light-duty back line under the double-island hood required an exhaust airflow rate approxi- 2019 ASHRAE Handbook-HVAC Applications (SI) Table 4 Type I Hood Requirementsa by Appliance Type ¦ Appliance Description ¦ ¦ --- ¦ ¦ Light Duty ¦ ¦ Braising pan/tilting skillet, electric ¦ ¦ Oven, baking, electric and gas ¦ ¦ Rotisserie, electric and gas ¦ ¦ Combination, electric and gas ¦ ¦ Convection, full-size, electric and gas ¦ ¦ Convection, half-size, electric and gas (protein cooking) ¦ ¦ Conveyor, electric ¦ ¦ Deck, electric and gas ¦ ¦ Duck, electric and gas ¦ ¦ Revolving rack, electric and gas ¦ ¦ Rapid cook, electric ¦ ¦ Roasting, electric and gas ¦ ¦ Rotisserie, electric and gas ¦ ¦ Stone hearth, gas ¦ ¦ Range, cook-top, induction ¦ ¦ Discrete element, electric (with or without oven) ¦ ¦ Salamander, electric and gas ¦ ¦ Medium Duty ¦ ¦ Braising pan/tilting skillet, gas ¦ ¦ Broiler, chain conveyor, electric ¦ ¦ Electric, under-fired ¦ ¦ Fryer, doughnut, electric and gas ¦ ¦ Kettle, electric and gas ¦ ¦ Open deep-fat, electric and gas ¦ ¦ Pressure, electric and gas ¦ ¦ Griddle, double-sided, electric and gas ¦ ¦ Flat, electric and gas ¦ ¦ Oven, conveyor, gas ¦ ¦ Range, open-burner, gas (with or without oven) ¦ ¦ Hot top, electric and gas ¦ ¦ Smoker, electric and gas ¦ ¦ Heavy Duty ¦ ¦ Broiler, chain conveyor, gas ¦ ¦ Electric and gas, over-fired (upright) ¦ ¦ Gas, under-fired ¦ ¦ Grill, plancha, electric and gas ¦ ¦ Oven, tandoor, gas ¦ ¦ Range, wok, gas and electric ¦ ¦ Extra-Heavy Duty ¦ ¦ Oven, stone hearth, wood-fired or wood for flavoring ¦ ¦ Solid-fuel cooking appliances combusting a solid fuel (such as wood, charcoal, or coal) to provide all or part of the heat for the cooking processb ¦ ¦ aWhere recirculating systems or recirculating hoods are used, the additional heat and moisture loads generated by such appliances should be accounted for in the sensible and latent loads for the HVAC system. bSolid-fuel flavoring cooking appliances should comply with Table 1 as if they do combust solid fuel. ¦ not Source: ASHRAE Standard 154-2016; Table 1. Table 5 Typical Exhaust Flow Rates by Cooking Equipment Category For Listed Type I Hoods Exhaust Flow Rate, L/s per linear metre of hood ¦ Type of Hood ¦ Light Duty ¦ Medium Duty ¦ Heavy Duty ¦ Extra-Heavy Duty ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Wall-mounted canopy ¦ 230 to 310 ¦ 310 to 465 ¦ 310 to 620 ¦ 540+ ¦ ¦ Single-island canopy ¦ 390 to 465 ¦ 465 to 620 ¦ 465 to 930 ¦ 850+ ¦ ¦ Double-island canopy (per side) ¦ 230 to 310 ¦ 310 to 465 ¦ 390 to 620 ¦ 775+ ¦ ¦ Eyebrow ¦ 230 to 390 ¦ 230 to 390 ¦ ¦ ¦ ¦ Back shelf/proximity/ pass-over ¦ 155 to 310 ¦ 310 to 465 ¦ 465 to 620 ¦ Not recommended ¦ Inc. ASHRAE, 2019 user. single for Licensed | {}
c3e7de22-c69d-4ec1-b588-32068a712b86 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Kitchen Ventilation 34.15 mately 470 L/(s·m) (measured along both sides of the hood). This rate is comparable to the ventilation rate for similar appliance duty classes under wall-mounted canopy hoods (Swierczyna et al. 2006). The double-island hood configuration performed as if a wall existed between them. Furthermore, the back-to-back appli- ance lines created a converging thermal plume that helped direct the plume toward the filter bank. However, without a wall between them, the double-island hood system was more susceptible to cross drafts than a wall-mounted hood configuration. The configuration, volume, and temperature of makeup air was critical to the performance of the double-island canopy hood. Con- sistent with previous research (Brohard et al. 2003), reducing local makeup airflow rates and velocities corresponded with reduced cap- ture and containment exhaust rates, in most cases. When air volume and associated velocity and turbulence near the hood was minimized, the appliance plumes were more stable and the hood was able to capture and contain at a lower exhaust rate. However, when local makeup air was introduced aggressively through four-way diffusers, perforated diffusers, or a high-flow perforated perimeter supply sys- tem, hood performance degraded severely. For double-island configu- rations, a perforated perimeter supply system operated at a low-flow, low-velocity condition was the best of the local makeup air configu- rations tested. When the perforated perimeter supply system deliv- ered low-flow, low-velocity air adjacent to the hood (i.e., less than 60% of replacement air requirement), hood performance improved significantly over the high-flow, high-velocity introduction (i.e., greater than 60% of replacement air requirement), and in some cases, better than the exhaust-only configuration with displacement supply. Higher replacement air temperatures from ceiling diffusers also de- graded the performance ofisland hoods. Unbalanced replacement air distribution was extremely detrimental to the performance of the double-island hoods. Other research highlights the advantages of using side panels for wall-mounted canopy hoods and a variety of replacement air condi- tions (Brohard et al. 2003; Swierczyna et al. 2006). However, results from the double-island canopy hood testing regarding side panels were inconclusive. A more extensive side panel (and center partition) investigation would need a larger laboratory where replacement air was introduced more uniformly around the hood to eliminate the effect of relatively high, directional local velocities. A partition between the two appliances lines improved perfor- mance of a double-island hood when coupled with a balanced sup- ply on both sides of the hood. However, if as little as 470 L/s was exhausted from the side opposite from the supply air delivery, per- formance of the double-island hood degraded. This was contrary to the expectation that the partition would be more of a benefit with unbalanced replacement air and its ability to mitigate the effect of cross drafts. Increased hood overhang was shown to be one of the most effec- tive performance enhancements for island canopy hoods. With a heavy-duty three-broiler appliance line centered front-to-rear under the single island hoods, rather than at a minimum prescriptive front overhang dimension, a 14% exhaust reduction was possible for the smaller rear filter hood, and a 40% exhaust reduction was possible for the larger V-bank hood. Likewise, when side overhang was increased to 610 mm from the minimum of 150 mm, a 41 % exhaust rate reduction was found for both single-island hoods. However, the results did not show a significant performance difference between the 2.4 m and 3 m deep double-island hoods. Increased side over- hang was found to be one of the most effective performance enhancements for double-island canopy hoods. Increasing the side overhang to 610 mm resulted in a 250 L/(s·m) reduction in exhaust flow rate. Tailored exhaust bias for double-island hoods may improve hood performance. With more exhaust volume focused over the more challenging appliances, the exhaust rate can be reduced for a given configuration. However, application of a specific bias for other applications or hood dimensions may yield different performance results and should be verified. Specification of enhanced hood edge geometry should be consid- ered by manufacturers and end-users. Although each design needs to be properly evaluated for its effect on hood performance, the design tested in this project was effective and was typical of edge design currently found in the industry. Performance in the field should be verified to ensure proper hood capture and containment operation. As shown by RP-1480 (Swierczyna et al. 2010), many factors interact in the kitchen and affect hood performance. These interactions cannot be perfectly predicted for each installation. Therefore, a field test is best to verify proper kitchen ventilation and hood performance. Wall Canopy Hoods, Appliance Positioning, and Diversity ASHRAE research project RP-1202 (Swierczyna et al. 2006) quantified the effect of the position and/or combination of appli- ances under a wall canopy exhaust hood on the minimum C&C exhaust rate. Effects of side panels, front overhang, and rear seal were also investigated. The scope of this laboratory study was to investigate similar and dissimilar appliances under a 3 m wall- mounted canopy hood. The appliances included three full-sized electric convection ovens, three two-vat gas fryers, and three 0.9 m gas underfired broilers, representing the light, medium, and heavy- duty appliance categories, respectively. In addition to various phys- ical appliance configurations, appliances were also varied in their usage: either off, at idle conditions, or at cooking conditions. A sup- plemental study investigated the effect of appliance accessories (including shelving and a salamander) and hood dimensions (including hood height, depth, and reservoir volume) on the mini- mum exhaust rate required for complete capture and containment. The study demonstrated that subtle changes in appliance posi- tion and hood configuration could dramatically affect the exhaust rates required for complete capture and containment, regardless of appliance duty and/or usage. The wide range in C&C values for a given hood/appliance setup explains why a similar hood installed over virtually the same appliance line may perform successfully in one kitchen and fall short of expectations in another facility. The following conclusions are specific to the conditions tested by Swierczyna et al. (2006). Airflow Requirements for Like-Duty Appliance Lines. Evalu- ation supported widely accepted commercial kitchen ventilation (CKV) design practices: higher ventilation rates are required for pro- gressively heavier-duty appliances (Table 6). For a 3 m wall- mounted canopy hood, at a defined median or good-case installation, the light-duty oven line required 520 L/s (1 70 L/[s · m]), the medium- duty fryer line required 1130 L/s (370 L/[s · m]), and the heavy-duty broiler line required 2075 L/s (680 L/[s · m]) to achieve C&C. Sim- ply increasing front overhang as noted between the worst- and good- case installations in Table 6 reduced the C&C exhaust rate by 10 to 27%. Installing side panels in addition to the increased front over- hang (best-case scenario) reduced the exhaust requirements by an additional 18 to 33%. Appliance position testing confirmed the exhaust rate of an appliance line is most dependent on the duty of the end appliance. The end appliance drove the exhaust rate more than additional volume from the other two appliances, as they changed from off to cooking conditions or were varied in duty class. In most cases, the lowest exhaust requirements for particular appliance lines were achieved when the lowest-duty appliance was at the end ofthe appli- ance line. In other words, hood performance was optimized when the heaviest-duty appliance was in the middle of the appliance line. Appliance Positioning (Front-to-Back) and Rear Seal. In- creasing the front overhang by pushing appliances toward the back Inc. ASHRAE, 2019 user. single for Licensed | {}
6df59e62-0090-4d32-b424-c1d93442ed09 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 34.16 2019 ASHRAE Handbook-HVAC Applications (SI) Chart Type: bar 152 mm Front Overhang to Frent of Cooking Surface 305 mm Front Overhang to Front of Cooking Surface 457 mm Front Overhang to Front of Cooking Surface item_01 2410L/s 2080L/s 1330L/s (w.s)/� RATE, · Without Rear Seal Between Appliance and Wall ② With Rear Seal Between Appliance and Wall FLOW Fig. 5 Capture and Containment Exhaust Rates for Gas Underfired Broilers under 3 m Wall Canopy Hood With and Without Rear Appliance Seal at Various Front Overhangs (Swierczyna et al. 2006) EXHAUST wall significantly decreased the required exhaust rates, not only be- cause of the increased distance from the hood to the front of the appliance, but also because of the decreased distance between the back of the appliance and the wall. With a rear seal in place, some of the replacement air, which would have otherwise been drawn up from behind the appliances, was instead drawn in along the perim- eter of the hood, helping guide the plume into the hood, as shown in Figure 5. Diversity in Appliance Usage. Operation diversity was evalu- ated with cook lines of three similar appliances and included com- binations of cook and off conditions. In most cases, operation correlated directly with the required exhaust rate, with an emphasis on the operation of the end appliances (Figure 6). The capture and containment rate for the end appliance cooking and the other two like-duty appliances off was nearly the same rate as all three appli- ances cooking. Changing the condition of end appliances from off to cooking had the greatest effect for medium-duty fryers, which required a 450 L/s increase in the exhaust rate. Because the fryers were thermostatically controlled, they responded to cooking operations by firing the burners. This, combined with an aggressive cooking plume, required a significantly increased exhaust rate for C&C. An aggressive thermal plume was present for the three heavy-duty gas underfired broilers; the exhaust rate increased 400 L/s. For the light-duty electric convection oven, there was a 95 L/s difference in turning the end appliances from off to cook. Figure 6 also shows that cooking with only the center appliance, with the two end appli- ances turned off, greatly reduced the exhaust requirement. Diversity in Appliance Duty and Position (Side-to-Side). The study found that the capture and containment rate of a multiduty ap- pliance line was less than the rate of the heaviest duty appliance in that line, applied over the length of the hood (Figure 7). C&C Hood Side Panels. Side panels installed on the 3 m hood improved hood performance dramatically, by preventing the plume from spilling at the side ofthe hood and by increasing velocity along the front of the hood. Combining side panels (measuring 0.3 by 0.3 m by 45° 0.6 by 0.6 m by 45° , 0.9 by 0.9 m by 45°, 1.2 by 1.2 m , by 45° , or full) with the maximum hood overhang resulted in the lowest exhaust requirement for all cases tested. The example of the three two-vat gas fryer line is shown in Figure 8. Effect of Shelving on Hood Capture and Containment Perfor- mance. Neither solid nor tubular shelving over the six-burner range required an increase in the exhaust rate. In fact, tubular shelving Chart Type: bar THREE BROILERS THREE FRYERS THREE OVENS item_01 1980U/s 1510U/s 1000U/s Fig. 6 Exhaust Capture and Containment Rates for One or Three Appliances Cooking from Like-Duty Classes under a 3 m Wall-Canopy Hood (Swierczyna et al. 2006) Chart Type: bar Broiler Cooking Oven Cooking Dryer Cooking item_01 1510L/s 1330L/s 1440L/s Fig. 7 Capture and Containment Exhaust Rates for Cooking Conditions on Multiduty Appliance Lines (Compared with Single-Duty Lines with Only One Appliance Operating) under 3 m Wall Canopy Hood (Swierczyna et al. 2006) mounted to the back of the appliance showed a slight enhancement compared to having no shelving installed. Effect of Hood Depth, Reservoir, and Mounting Height on Capture and Containment Performance. Comparing the 1.2 and 1.5 m deep hoods, the deeper hood reduced capture and contain- ment exhaust rates when appliances were positioned with maximum front overhang and minimum rear gap. The deeper hood had a neg- ative effect when appliances remained in the minimum front over- hang position. The effect of hood depth in conjunction with front overhang, side panels, and rear seal is shown in Figure 9. Another advantage of the 1.5 m over the 1.2 m hood was its abil- ity to capture and contain the plume when an oven door was opened. For a 1.2 m hood and a 150 mm front overhang, an exhaust rate of 570 L/s was required for the three electric ovens with the doors closed and 2450 L/s with the doors open. Similarly, for a 1.5 m deep hood with an 460 mm front overhang, 570 L/s was required for three ovens with the doors closed and 1600 L/s with the doors open. The setup and schlieren views are shown in Figure 10. Inc. ASHRAE, 2019 user. single for Licensed | {}
c64ec837-cd2b-47c7-83fb-4fce3b673809 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Kitchen Ventilation 34.17 The reservoir volume of the hood was increased by changing the hood height from 0.6 to 0.9 m. When the gas underfired broiler was operated in the left appliance position, the increased hood volume marginally improved capture and containment performance. In contrast, a significant improvement was found for the appliance in the center position. This improvement indicated the plume was well located in the hood, and the increased hood volume may have allowed the plume to roll inside the hood and distribute itself more evenly along the length of the filter bank. Minimizing hood mounting height had a positive effect on cap- ture and containment performance. In most cases, a direct correla- tion could be made between the required exhaust rate and hood height for a given appliance line. The typical 2 m mounting height (for a canopy hood) was increased to 2.1 to 2.3 m. For the gas un- derfired broiler installed at the end of the hood, increasing the hood Chart Type: bar Without 0.3 x 0.3 m 0.6 x 0.6 m 0.9 x 0.9 m 1.2 x 1.2 m Full item_01 1560U/s 1330U/s 1470U/s 1330U/s 1210U/s 1280U/s Fig. 8 Exhaust Capture and Containment Rates for Three Two-Vat Gas Fryers with Various Side Panel and Overhang Configurations under 3 m Wall Canopy Hood (Swierczyna et al. 2006) height by 0.3 m required a 14% increase in exhaust. However, when the broiler was in the center position, the increased hood height did not compromise capture and containment performance and required exhaust rate was reduced. The dramatic reduction in the exhaust re- quirement as the hood-to-appliance distance was reduced below the 2 m mounting height illustrated the potential for optimizing CKV systems by using close-coupled or proximity-style hoods. This effect is shown in Figure 11. Design Guidelines. Swierczyna et al. (2006) illustrated the potential for large variations in the airflow requirements for a spec- ified appliance line and hood configuration. Best-practice design considerations that became evident included the following: · Position heavy-duty appliances (e.g., broilers) in middle ofthe line. · Position light-duty appliances (e.g., ovens) on the end of the line. ![image](/image/placeholder) 3000 L/s 2690 900 RATE, 2500 L/(s·m) 800 2080 700 2000 1890 FLOW 1660 600 RATE, 1500 1370 1370 500 1280 EXHAUST 1230 400 FLOW 1000 1000 300 200 500 C&C 100 EXHAUST 0 0 C&C Overhang Panels Overhang Overhang Clearance Clearance Clearance Clearance Clearance Overhang Overhang Clearance Clearance Panets Overhang Overhang Seal Side Side Front BOS Clearance Front Frant Rear Front Rear Rear 배우님 Overhang Rear 100 님 W/Raju Front Rear Rear Front W/Rear Front .2m wg Clearance mm Rear mm mm ww ww WELL ww Front WW ww ww ww From ww pz Overhang 2A 0in 152 572 mm 但如 명 797 u 0in 114 114 좌 797 457 袋 24.0in w/1 114 6 1.2x1 mm 24.0in Seal 114 wiRear □1.2 m Hood Depth ⌀1.5m Hood Depth Fig. 9 Exhaust Capture and Containment Rates for Heavy-Duty Gas Underfired Broiler Line under 3 m Wall Canopy Hood with 1.2 and 1.5 m Hood Depths and Front Various Front Overhangs (Swierczyna et al. 2006) ![image](/image/placeholder) SCHLIEREN VIEW OF SPILLAGE WITH SCHLIEREN VIEW DURING CAPTURE AND (A) NORMAL VIEW (B) 1.2 m DEEP HOOD WITH 150 mm OF FRONT OVERHANG (C) CONTAINMENT WITH 1.5 m DEEP HOOD WITH 460 mm OF FRONT OVERHANG Fig. 10 Three Ovens under Wall-Mounted Canopy Hood at Exhaust Rate of 1600 L/s (Swierczyna et al. 2006) Inc. ASHRAE, 2019 Ⓒ user. single for Licensed | {}
bc477522-a9de-46ea-8cb4-15e5f88b96e7 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 34.18 2019 ASHRAE Handbook- -HVAC Applications (SI) Table 6 Capture and Containment Exhaust Rates for Three Like-Duty Appliance Lines at Cooking Conditions with Various Front Overhang and Side Panel Configurations under 3 m Wall-Mounted Canopy Hood ¦ ¦ Best Case ¦ Good Case ¦ Worst Case ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Three electric full-sized convection ovens ¦ 230 mm front overhang full side panels ¦ 230 mm front overhang ¦ 150 mm front overhang ¦ ¦ ¦ 130 L/(s·m) ¦ 170 L/(s·m) ¦ 190 L/(s·m) ¦ ¦ Three two-vat gas fryers ¦ 460 mm front overhang partial side panels ¦ 460 mm front overhang ¦ 150 mm front overhang ¦ ¦ ¦ 250 L/(s·m) ¦ 370 L/(s·m) ¦ 510 L/(s·m) ¦ ¦ Three gas underfired broilers ¦ 300 mm front overhang partial side panels ¦ 300 mm front overhang ¦ 0 mm front overhang (150 mm cook surface) ¦ ¦ ¦ 510 L/(s·m)* ¦ 680 L/(s·m) ¦ 790 L/(s·m) ¦ * Adding a rear seal between back of appliance and wall to best-case configuration (150 mm of front overhang and partial side panels) further improved hood performance to an exhaust rate of 1320 L/s (430 L/[s·m]). Source: Swierczyna et al. (2006). Table 7 Exhaust Static Pressure Loss of Type I Hoods for Various Exhaust Airflows* ¦ ¦ Hood Static Pressure Loss, Pa ¦ Hood Static Pressure Loss, Pa ¦ Hood Static Pressure Loss, Pa ¦ Hood Static Pressure Loss, Pa ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Type of Grease Removal Device ¦ 230 to 390 L/(s·m) ¦ 390 to 540 L/(s·m) ¦ 540 to 700 L/(s·m) ¦ 700 to 850 L/(s·m) ¦ ¦ Baffle filter ¦ 60 to 125 ¦ 125 to 190 ¦ 190 to 250 ¦ 250 to 310 ¦ ¦ Extractor ¦ 200 to 340 ¦ 325 to 425 ¦ 425 to 750 ¦ 720 to 1050 ¦ ¦ Multistage ¦ 140 to 275 ¦ 275 to 425 ¦ 425 to 720 ¦ 720 to 1000 ¦ *Values based on 500 mm high filters and 7.5 m/s through hood/duct collar. · Push back appliances (maximize front overhang, minimize rear gap). · Seal area between rear of appliance and wall. · Use side panels, end panels, and end walls. · Installing shelving or ancillary equipment (e.g., salamander) behind or above a range should not negatively affect C&C perfor- mance, if other best practices (e.g., maximizing hood overhang) are observed. · Use larger hoods, both deeper and taller. · Installing hoods at lowest height practical (or allowed by code) to minimize distance from cooking surface to hood improves C&C performance. · Introduce replacement air at low velocity. Do not locate four-way diffusers near hood, and minimize use of air curtains. Replacement (Makeup) Air Options. Air exhausted from the kitchen must be replaced. Replacement air can be brought in through traditional methods, such as ceiling diffusers, or through systems built as an integral part of the hood. It may also be intro- duced using low-velocity displacement diffusers or transfer air from other zones. For further information, see the section on Replace- ment (Makeup) Air Systems. Static Pressure. Static pressure drop through hoods depends on the type and design of the hood and grease removal devices, size of duct and duct connections, and flow rate. Table 7 provides a general guide for determining static pressure loss depending on the type of grease removal device and exhaust flow rate. Manufacturers' data should be consulted for actual values. Static pressure losses for exhaust ducts should be calculated for each installation. Type II Hoods Type II hoods (Figure 12) can be divided into the following two application categories: · Condensate hood. For applications with high-moisture exhaust, condensate forms on interior surfaces of the hood. The hood is designed to direct the condensate toward a perimeter gutter for collection and drainage, allowing none to drip onto the appliance Chart Type: bar 2.3 m Hood-HooFloor 2.1 m Hood-to-Floor 2.0 m Hood-to-Floar 1.7 m Hood-to-Floor 1.1 m Hood-to-Floar item_01 2320L/s 2180L/s 2030L/s 1470L/s 190L/s Fig. 11 Exhaust Capture and Containment Rates for a Gas Underfired Broiler under 3 m Wall Canopy Hood at Various Mounting Heights (Swierczyna et al. 2006) ![image](/image/placeholder) REMOVABLE CONDENSATE BAFFLES DRAIN FITTING CONDENSATE GUTTER CONDENSATE HOOD HEAT/FUME HOOD Fig. 12 Type II Hoods Inc. ASHRAE, 2019 user. single for Licensed | {}
cce4394a-b6d6-4f0d-b75e-c4a47a1a4df6 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Kitchen Ventilation 34.19 Table 8 Type II Hood Duty Classification by Appliance Type ¦ Appliance Description ¦ Size ¦ ¦ --- ¦ --- ¦ ¦ Hood Not Required ¦ ¦ ¦ Cabinet, holding, electric ¦ All ¦ ¦ Cabinet, proofing, electric ¦ All ¦ ¦ Cheesemelter, electric ¦ All ¦ ¦ Coffee maker, electric ¦ All ¦ ¦ Cooktop, induction, electric ¦ All ¦ ¦ Dishwasher, door-type rack, hot-water sanitizing, heat recovery and vapor reduction, electric ¦ All ¦ ¦ Door-type rack, chemical sanitizing, heat recovery and vapor reduction, electric ¦ All ¦ ¦ Door-type dump and fill, hot-water sanitizing, electric ¦ All ¦ ¦ Door-type dump and fill, chemical sanitizing, electric ¦ All ¦ ¦ Pot and pan, hot-water sanitizing, heat recovery and vapor reduction, electric ¦ All ¦ ¦ Powered sink, electric ¦ All ¦ ¦ Under-counter, chemical sanitizing, electric ¦ All ¦ ¦ Under-counter, electric ¦ All ¦ ¦ Undercounter, hot-water sanitizing, heat recovery and vapor reduction, electric ¦ All ¦ ¦ Drawer warmer, 2 drawer, electric ¦ All ¦ ¦ Egg cooker, electric ¦ All ¦ ¦ Espresso machine, electric ¦ All ¦ ¦ Grill, panini, electric ¦ All ¦ ¦ Hot dog cooker, electric ¦ All ¦ ¦ Hot plate, countertop, electric ¦ All ¦ ¦ Ovens, microwave, electric ¦ All ¦ ¦ Popcorn machine, electric ¦ All ¦ ¦ Re-thermalizer, electric ¦ All ¦ ¦ Rice cooker, electric ¦ All ¦ ¦ Steam table, electric ¦ All ¦ ¦ Steamers, bun, electric ¦ All ¦ ¦ Steamer, compartment atmospheric, countertop, electric ¦ All ¦ ¦ Compartment pressurized, countertop, electric ¦ All ¦ ¦ Table, hot food, electric ¦ All ¦ ¦ Toaster, electric ¦ All ¦ ¦ Waffle iron, electric ¦ All ¦ ¦ Light-Duty Type II Hooda,c ¦ ¦ ¦ Kettle, steam jacketed, tabletop, electric, gas and direct steam Oven, convection, half-size, electric and gas (non-protein cooking) ¦ < 76L All ¦ ¦ Pasta cooker, electric ¦ All ¦ ¦ Re-thermalizer, gas ¦ All ¦ ¦ Rice cooker, gas ¦ All ¦ ¦ ¦ ¦ ¦ Steamer, atmospheric, gas ¦ All ¦ ¦ Pressurized, gas ¦ All ¦ ¦ Atmospheric, floor-mounted, electric ¦ All ¦ ¦ Pressurized, floor-mounted, electric ¦ All ¦ ¦ Kettle, steam-jacketed floor mounted, electric, gas, and direct steam ¦ < 76L ¦ ¦ Medium-Duty Type II Hooda,c ¦ ¦ ¦ ¦ All ¦ ¦ Dishwasher, conveyor rack, chemical sanitizing Conveyor rack, hot water sanitizing ¦ All ¦ ¦ Door-type rack, chemical sanitizing ¦ All ¦ ¦ Door-type rack, hot water sanitizing Pot and pan, hot-water sanitizing ¦ All All ¦ ¦ Pasta cooker, gas ¦ All ¦ ¦ Steam-jacketed kettle, floor mounted, electric and gas ¦ < 76L ¦ aA hood should be provided for an electric appliance ifit produces 5 mg/m3 of grease or more when measured at 236 L/s. bWhere hoods are not required, the additional heat and moisture loads generated by such appliances should be accounted for in the sensible and latent loads for the HVAC system. cWhere recirculating systems or recirculating hoods are used, the additional heat and moisture loads generated by such appliances should be accounted for in the sensible and latent loads for the HVAC system. Source: ASHRAE Standard 154-2016; Table 2. below. Hood material is usually noncorrosive, and filters are usu- ally installed. Heat/fume hood. For hoods over equipment producing heat and fumes Filters installed. · only. are usually not ASHRAE Standard 154 sets minimum exhaust airflow require- ments for Type II hoods based on the duty rating of the appliance underneath the hood. Table 8 classifies Type II appliances as either light or medium duty, and Table 9 gives minimum net airflow requirements. Inc. ASHRAE, 2019 user. single for Licensed | {}
612c1acd-0e9f-4373-9dde-76e55f8d55bb | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 34.20 2019 ASHRAE Handbook- -HVAC Applications (SI) Table 9 Minimum Net Exhaust Airflow Requirements for Type II Hoods ¦ ¦ Minimum Net Exhaust Flow Rate per Linear Hood Length, L/(s·m) ¦ Minimum Net Exhaust Flow Rate per Linear Hood Length, L/(s·m) ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Type of Hood ¦ Light-Duty Equipment ¦ Medium-Duty Equipment ¦ ¦ Wall-mounted canopy ¦ 310 ¦ 465 ¦ ¦ Single island ¦ 620 ¦ 775 ¦ ¦ Double island (per side) ¦ 388 ¦ 465 ¦ ¦ Eyebrow ¦ 388 ¦ 388 ¦ ¦ Back shelf/pass-over ¦ 310 ¦ 465 ¦ Source: ASHRAE Standard 154-2011. Ventilation Rates for Hooded Door Dishwashers The ventilation rates for high-temperature sanitizing door-type dish machines in the model codes are inadequate to capture and con- tain the heat and steam from the dishwashing operation. The exhaust rates of 154 and 310 L/s per metre of hood in the IMC and UMC (Uniform Mechanical Code; IAPMO 2018), respectively, often do not capture the heat and steam released from the machine. The min- imum recommendation is 464 L/s per metre of hood for canopy hoods over high-temperature sanitizing door-type machines. Front and side overhangs are critical for capture of the thermal plume from door-type machines, 305 mm on the side and front are the min- imum recommendation. Door-type machine operations are good candidates for demand control kitchen ventilation (DCKV) systems. The DCKV system should initialize ramp-up at the beginning of the wash cycle, not the end ofthe cycle, when it is too late to capture the thermal plume from the door opening. Door-type dishwashers are also good candidates for exhaust air heat recovery in the ventilation system. The exhaust air steam is clean and hot and heat exchangers can take advantage of latent heat in addition to sensible heat. Low-temperature sanitizing door-type machines should not be placed directly under return air grilles. Ventilation for Conveyor Dish Machines Conveyor dish machines' exhaust ductwork are typically pant- leg connections to vent cowls at the entrance and exit of the dish machine. The exhaust airflow rates at the vent cowls are typically 94 L/s at the entrance and 189 L/s at the exit. The actual airflow rates are difficult to measure in the field and are rarely verified. There- fore, a visual capture and containment assessment is recommended, with field adjustment as necessary to maintain capture and contain- ment at the entrance and exit. Even with a well-balanced airflow, convective loads escape from the curtains, door seals, and drains. These other convective loads could contribute more than 4690 W (with 40% of the load being latent) (PG&E 2011) and should be accounted for in the internal heat load calculation for the dishroom. As an alternative to a pant-leg exhaust system, a canopy exhaust hood with a minimum ventilation rate of 308 L/s per metre of hood should be considered. The convective load to space can nearly be eliminated if the canopy hood incorporates adequate overhang (305 mm overhang on both sides, and 610 mm overhang on both the front and rear). Recirculating Systems A recirculating system, previously called a ductless hood, con- sists of a cooking appliance/hood assembly designed to remove grease, smoke, and odor and to return the treated exhaust air directly back into the room. HV AC design must consider that recirculating systems discharge the total amount of heat and moisture generated by the cooking process back into the kitchen space, adding to the cooling load. These hoods typically contain the following components in the exhaust stream: (1) a grease removal device such as a baffle filter, (2) a high-efficiency particulate air (HEPA) filter or an electrostatic precipitator (ESP), (3) some means of odor control such as acti- vated charcoal, and (4) an exhaust fan. NFPA Standard 96, Chapter 13, is devoted entirely to recirculating systems and contains spe- cific requirements such as (1) design, including interlocks of all critical components to prevent operation of the cooking appliance if any of the components are not operating; (2) fire extinguishing system, including specific nozzle locations; (3) maintenance, including a specific schedule for cleaning filters, ESP, hood, and fan; and (4) inspection and testing of the total operation and inter- locks. In addition, NFPA Standard 96 requires that all recirculating systems be listed by a testing laboratory. The recognized standard for a recirculating system is UL Standard 710B. Recirculating sys- tems should not be used over gas-fired or solid-fuel-fired cooking equipment. Designers should thoroughly review NFPA Standard 96 require- ments and contact a manufacturer of recirculating systems to obtain specific information needed for the design and listing infor- mation before incorporating this type of system into a food service design. Downdraft Appliance Ventilation Systems These systems are intended to remove smoke, grease-laden vapors, odors, and other impurities from the air by drawing the cooking effluents away from cooking appliances and downward into ventilation systems. According to UL Standard 710B, these systems are used with electric cooking appliances only. A down- draft system listed to UL Standard 710B, for recirculating applica- tions, consists of a fire extinguishing system unit, grease filters, interlocks, etc., all contained within a suitable enclosure. Downdraft systems operate on a different principle than typical exhaust hoods. With a customary exhaust hood, the buoyant thermal plume from cooking rises into the exhaust hood by gravity, provided overhang is sufficient, cross drafts do not interfere, etc., as ex- plained previously. Thereafter, one or more exhaust fans create a low pressure are in the hood plenum, and the exhaust contents are carried outdoors from the hood. In contrast, downdraft ventilation systems include an exhaust fan that creates a low pressure at an inlet beside or behind a cooking surface, or between two cooking surfaces. The exhaust fan draws cooking effluents, possibly including combustion products, through a grease filter in the exhaust inlet, to be transported outdoors or recirculated into the cooking space. Downdraft appliance ventilation systems are described and COV- ered by NFPA Standard 96, Chapter 15, and if used for recircula- tion, are listed to UL Standard 710B. If used to ventilate processes producing smoke or grease laden vapor, these systems must comply with NFPA Standard 96, Chapter 15, which references other requirements in NFPA Standard 96: · Clearance requirements in Section 4.2 · Hood requirements of Chapter 6 · Grease removal device requirements of Chapter 7 · Special-purpose filters listed in accordance with ANSI/UL Stan- dard 1046 · Exhaust duct requirements of Chapter 7 · Air movement requirement of 8.2. 1.2 and 8.2.2.3 · Fire-extinguishing requirements of Chapter 10 and Section 15.2 · Maintenance requirements of Chapter 11 · Safety requirements of Chapter 12 Important additional requirements are provided by NFPA Stan- dard 96, sections 15.1.2 though 15.4. Caution is advised for application of downdraft ventilation systems to commercial kitchens. Pulling effluent away from a Inc. ASHRAE, 2019 user. single for Licensed | {}
3e9bfb39-61a5-4a4e-a53f-f5eff2841146 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Kitchen Ventilation 34.21 ![image](/image/placeholder) TYPE I COOKING PROCESS STANDARD- EXHAUST EFFICIENCY GREASE TEMPERATURE LIGHT DUTY? EXTRACTION AT LESS THAN VENTILATION 54°C HOOD EXHAUST MEDIUM GREASE OPTIONAL TEMPERATURE EXTRACTION AT GREASE MEDIUM DUTY? LESS THAN VENTILATION CONTROL 66°C HOOD SYSTEMS HIGH-EFFICIENCY EXHAUST OPTIONAL GREASE TEMPERATURE GREASE HEAVY DUTY? EXTRACTION AT GREATER THAN CONTROL VENTILATION 66°C SYSTEMS HOOD HIGH-EFFICIENCY OPTIONAL SOLID GREASE EXTRA-HEAVY SPARK GREASE FUEL EXTRACTION AT DUTY? ARRESTOR CONTROL COOKING VENTILATION SYSTEMS HOOD Fig. 13 Typical Filter Guidelines Versus Appliance Duty and Exhaust Temperature Table 10 Recommended Duct-Cleaning Schedules ¦ Type or Volume of Cooking ¦ Inspection ¦ ¦ --- ¦ --- ¦ ¦ ¦ Frequency ¦ ¦ Solid fuel ¦ Monthly ¦ ¦ High-volume cooking (gas charbroiler or wok cooking) ¦ Quarterly ¦ ¦ Moderate-volume ¦ Semiannually ¦ ¦ Low-volume (churches, day camps, seasonal businesses) ¦ Annually ¦ Source: Reproduced with permission from the 2017 edition ofNFPA 96, Standard for Ventilation Control and Fire Protection of Commercial Cooking Operations, Copy- rightⒸ 2016, National Fire Protection Association. All rights reserved. This reprinted material is not the complete and official position of the NFPA on the referenced sub- ject, which is represented only by the standard in its entirety which can be which can be viewed for free access or purchased through the NFPA web site at www.nfpa.org. flat-surface griddle is one popular application of these systems, particularly in Asian-style steakhouses, where the griddles are used intermittently and the exhaust inlet is slightly close to the edges of the cooking surface. More challenging is trying to pull vapors from the tops of commercial cooking vessels, such as on range tops, because cooking effluents might be emitted above and out of reach of the downdraft inlet suction. For gas appliances, also remember that air movement created by downdraft inlet suction might be suf- ficient to interfere with the operation of nearby gas burners. Field Performance Testing Once kitchen ventilation systems have been installed, it is important to verify that they operate correctly. ASHRAE Standard 154 describes performance testing for both Type I and Type II hood applications. For Type II hoods, the requirement is that the hood must be operating at the minimum airflow shown in Table 9. For Type I hoods, all appliances must be turned on and either actual or simulated cooking must be performed to verify that the hood system has achieved proper capture and containment. 1.7 COOKING EFFLUENT GENERATION AND CONTROL Air quality, fire safety, labor cost, and maintenance costs are important concerns involved with emissions from a commercial cooking operation. Cooking emissions have also been identified as a major component of smog particulate. This has led to regulation in some major cities, requiring reduction of emissions from specific cooking operations. In a fire, grease deposits within a duct act as fuel. Reducing this grease can help prevent a small kitchen fire from becoming a major structural fire. In the past, the only control of grease build-up in exhaust ducts was frequent duct cleaning, which is expensive and disruptive to kitchen operation. It also depends on frequent duct inspections and regular cleaning. Grease build-up on fans, fire noz- zles, roofs, and other ventilation equipment can be costly in addi- tional maintenance and replacement costs. From an energy and sustainability perspective, it is desirable to reduce the atmospheric emissions and achieve the highest grease extraction or destruction with the lowest energy costs possible. For mechanical extractors, the pressure drop of the filters is the predominant driver for energy usage, whereas for other control systems there may be electrical components or water use that needs to be evaluated. Figure 13 pres- ents some design guidance for what filtration may be desirable under various exhaust temperature and/or duty level situations. Another issue that commonly comes up during kitchen design and operation is how often ductwork needs to be cleaned in restau- rants. Table 10 presents inspection schedules adapted from Table 11.4 of NFPA Standard 96. Inc. ASHRAE, 2019 user. single for Licensed | {}
009cf8c3-c4bc-4d8c-b8f2-3ce9c396a459 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 34.22 2019 ASHRAE Handbook-HVAC Applications (SI) ![image](/image/placeholder) 18 6y 16 □ VAPOR 14 PRODUCT 12 10 kg GREASE/1000 8 FOOD EMISSIONS, 6 4 2 0 GRIDDLE STEAK GRIDDLE ELECTRIC FRYER ELECTRIC FRYER OVEN BROILER CHICKEN BROILER CHICKEN OVEN PIZZA GRIDDLE HAMBURGER CONVEYOR OVER-FIRED ELECTRIC OVEN GAS BROILER GAS ELECTRIC GAS GAS CLAMSHELL Fig. 14A Grease in Particulate and Vapor Phases for Commercial Cooking Appliances with Total Emissions Approximately Less Than 50 kg/1000 kg of Food Cooked Effluent Generation During cooking operations on appliances, effluent is generated, which includes water vapor and organic material (in both particulate and vapor form) released from the food. The combustion of fuel and grease contributes to the mixture released from the cooking, includ- ing condensable and noncondensable gases. For solid-fuel cooking, the effluent mixture contains not only toxic contaminants, but also condensable creosote (which has a lower flash point and increases risk of duct fires). Particle Size Comparisons (from Exhaust Systems). Efflu- ent from five types of commercial cooking equipment has been measured under a typical exhaust hood (Kuehn et al. 1999). Foods that emit relatively large amounts of grease were selected. Figures 14A and 14B show the measured amount of grease in the plume entering the hood above different appliances and the amount in the vapor phase, particles below 2.5 m in size (PM2.5), particles less than 10 m in size (PM10), and the total amount of particulate grease. Ovens and fryers generate little or no grease particulate emissions, whereas other processes generate significant amounts. However, gas underfired broilers (referred to as "gas broilers" in Figures 14A and 14B) generate much smaller particulates compared to the griddles and ranges, and these emissions depend on the broiler design. The amount of grease in the vapor phase is significant and varies from 30% to over 90% by mass; this affects the design approach for grease removal systems. Carbon monoxide (CO) and carbon dioxide (CO2) emissions are present in solid fuel and natural gas combustion processes but not in processes from electrical appliances. Additional CO and CO2 emissions may be generated by gas underfired boilers when grease drippings land on extremely hot surfaces and burn. Nitrogen oxide (NOx) emissions appear to be exclusively associated with gas appli- ances and related to total gas consumption. Figure 14C shows the measured plume volumetric flow rate entering the hood. In general, gas appliances have slightly larger flow rates than electric because additional products of combustion must be vented. Gas underfired and electric broilers have plume flow rates considerably larger than the other appliances shown. Effluent flow rates from gas underfired and electric broilers are approximately 100 times larger than the actual volumetric flow rate created by vaporizing moisture and grease from food. The differ- Chart Type: bar GAS BROILER HAMBURGER HAMBURGER ELECTRIC BROILER HAMBURGER CONVEYOR BROILER HAMBURGER SOLID FUEL BROILER HAMBURGER CHINESE WOK CUBED CHICKEN BREAST item_01 50kg GREASE/100 kg 30kg GREASE/100 kg 40kg GREASE/100 kg 150kg GREASE/100 kg 250kg GREASE/100 kg Fig. 14B Grease in Particulate and Vapor Phases for Commercial Cooking Appliances with Total Emissions Approximately Greater Than 50 kg/1000 kg of Food Cooked Chart Type: bar Gas Griddle (hamburger) Elec. Griddle (phamburger) Gas Fryer (potates) Elec. Gas Broiler (hamburger) Gas Broiler (chicken breast) Elec. Broiler (chausage breast) Gas Elec. Oven (sausaulage pizza) Gas Range (spaghetti, sausage, sauce) item_01 290L/s 960L/s 100L/s 570L/s 470L/s 200L/s 190L/s 190L/s Fig. 14C Plume Volumetric Flow Rate at Hood Entrance from Various Commercial Cooking Appliances (Kuehn et al. 1999) ence is caused by ambient air entrained into the effluent plume before it reaches the exhaust hood. Thermal Plume Behavior The most common method of contaminant control is to install an air inlet device (a hood) where the plume can enter it and be con- veyed away by an exhaust system. The hood is generally located above or behind the heated surface to intercept normal upward flow. Understanding plume behavior is central to designing effective ven- tilation systems. Effluent released from a noncooking cold process, such as metal grinding, is captured and removed by placing air inlets so that they catch forcibly ejected material, or by creating airstreams with sufficient velocity to induce the flow of effluent into an inlet. This technique has led to an empirical concept of capture velocity that is often misapplied to hot processes. Effluent (such as grease and smoke from cooking) released from a hot process and contained in a plume may be captured by locating an inlet hood so that the plume flows into it by buoyancy. Hood exhaust rate must equal or slightly exceed plume volumetric flow rate, but the hood need not actively induce capture ofthe effluent ifthe hood is large enough at its height above the cooking operation to encompass the plume as it expands Inc. ASHRAE, 2019 user. single for Licensed | {}
47a01db0-43c6-4bff-a5b0-e35b8a615b7f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Kitchen Ventilation 34.23 A. TEST SETUP: Two gas underfired broilers under 2.5 m long wall-mounted canopy hood, cooking hamburgers. B. Schlieren photo of capture and containment at 2075 L/s exhaust rate. Hot, clear air visualization, cooking. no C. Schlieren photo of spillage and containment at 1550 L/s exhaust rate. Hot, clear air visualization, no cooking. Fig. 15 Hot-Air Plume from Cooking Appliances under Wall-Mounted Canopy Hood during its rise. Additional exhaust airflow may be needed to resist cross currents that carry the plume away from the hood. A heated plume, without cross currents or other interference, rises vertically, entraining additional air, which causes the plume to enlarge and its average velocity and temperature to decrease. Ifa sur- face parallel to the plume centerline (e.g., a back wall) is nearby, the plume will be drawn toward the surface by the Coanda effect. This tendency may also help direct the plume into the hood. Figure 15 illustrates a heated plume with and without cooking effluent as it rises from heated cooking appliances. Figure 15A shows two gas underfired broilers cooking hamburgers under a wall-mounted, exhaust-only, canopy hood. Note that the hood is mounted against a clear back wall to improve experimental observation. Figures 15B and 15C show the hot-air plume without cooking, visualized using a schlieren optical system, under full capture and spillage conditions, respectively. Effluent Control Effluents generated by cooking include grease in particulate (solid or liquid) and vapor states, smoke particles, and volatile organic compounds (VOCs or low-carbon aromatics, which are sig- nificant contributors to odor). Grease vapor is condensable and may condense into grease particulate in the exhaust airstream when diluted with room-temperature air or when it is exhausted into the cooler outdoor atmosphere. Effluent controls in the vast majority of kitchen ventilation sys- tems are limited to removing solid and liquid grease particles by mechanical grease removal devices in the hood. More effective devices reduce grease build-up downstream of the hood, lowering the frequency of duct cleaning and reducing the fire hazard. The reported grease extraction efficiency ofmechanical filtration systems (e.g., baffle filters and slot cartridge filters) may reflect the particulate removal performance of these devices. These devices are listed for their ability to limit flame penetration into the plenum and duct. Grease extraction performance can be evaluated using ASTM Standard F2519. Smaller aerodynamic particles (<2.5 m) are not easily removed by mechanical extractors. If these particles must be removed, a pollution control unit is typically added, which removes Chart Type: bar Gas_Griddle Elec._Gramburger Gas_Elec._Fryer Elec._Potatoes Gas_Broiler Elec._hamburger Elec._Chicken_breast Elec._Bausanage_pizza Gas_Oven Elec._Range item_01 35% 70% 40% 60% 35% 70% 40% 30% 25% 20% Fig. 16 Particulate Versus > apor-Phase Emission Percentage per Appliance (Average) (Gerstler et al. 1998) a large percentage of the grease that escaped the grease removal device in the hood, as well as smoke particles. Grease Extraction ASHRAE research project RP-745 (Gerstler et al. 1998) found that a significant proportion of grease effluent may be in vapor form (Figure 16), which is not removed by mechanical extractors. The particulate range from cooking operations ranges from 0.01 to 100 m. Different cooking operations have different ranges of particle sizes in the cooking plume and have been measured for many appliances (Gerstler et al. 1998; Kuehn et al. 2008). Grease particulates larger than 20 m are too heavy to remain airborne and drop out of the airstream. Figure 17 compares the size of particles from kitchen exhaust to common items. Inc. ASHRAE, 2019 user. single for Licensed | {}
4d961c38-7adf-4ec9-aee3-993ca868e94b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 34.24 2019 ASHRAE Handbook-HVAC Applications (SI) Each combination of food product, cooking equipment, and cooking temperature creates a unique particle emissions profile, these profiles change over time during the cooking process. For example, the initial drop of French fries into a fryer gives off a short blast of large particles, whereas cooking a hamburger on a griddle gives off a continuous stream ofparticles and vapor. Burgers cooked on a broiler tend to burn and emit very small particles (< 1 m in size). Variations in the food product itself can also change the emissions of a cooking process. Hamburger with 23% fat content produces more grease than a 20% fat burger. Chicken breast may have a dif- ferent effluent characteristic than chicken legs or thighs. Even cook- ing chicken with or without the skin changes the properties of emissions. Figures 18 and 19 show typical particle emission profiles for a gas griddle and gas underfired broiler both cooking hamburgers (Kuehn et al. 1999). ASTM Standard F2519-05 can be used to determine fractional filter efficiency for grease particulate. A fractional efficiency curve is a graph that gives a filter' s efficiency over a range of particle sizes. Fractional efficiency curves are created by subjecting a test filter to a controlled distribution of particles and measuring the quantity of particles at each given size before and after the filter. The amount of reduction of particles is used to calculate the efficiency at each given size. The fractional efficiency curve for a typical 510 by 510 mm baffle filter tested at 540 L/(s· m) is shown in Figure 20. Extraction efficiencies must be compared at the same airflow per linear length offilter. This gives a consistent way of comparing per- formance of extraction devices that may be built very differently, such as hoods with removable extractors and with stationary extractors. This is also consistent with the way exhaust flow rates X-Axis: Diameter, Hm Chart Type: line Coarse Sand Diameter of Human Hair Bacteria LUNG-DAMAGING Dust Tobacco Smoke Smog Viruses Cooking Emissions item_01 1000 100 10 10 1 1 0.01 100 for hoods are commonly specified. The airflow rate through a hood changes hood efficiency by changing the velocity at which the air travels through a filter. To demonstrate what a filter fractional efficiency means with an actual cooking process, the gas underfired broilers (referred to as "charbroiler") emissions curve and the baffle filter efficiency curve have been plotted on one graph in Figure 21. The area under each emission curve is representative of the total particulate emissions for the gas underfired broiler. As can be seen by comparing the graph before and after the baffle filter, there is very little reduction in the amount of grease exhausted to the duct. The area under the "charbroiler after baffle" curve represents the amount of grease par- ticulate exhausted into the duct. The graphs and efficiencies shown here are only for particulate grease. There is also a vapor component of the grease that is exhausted, which cannot be removed by filtration. Some of the vapor condenses and is removed as particulate before reaching the filter. Some condenses in the duct and accumulates on the duct and fan. However, with elevated temperatures in the exhaust airstream, vapor may pass through and exit to the atmosphere. Higher efficiency at a specific particle size may not be the only selection criteria for grease extraction. From an energy and sustain- ability standpoint, the ideal goal would be to have the highest grease extraction at the lowest pressure drop possible. Smaller particles can only be removed by shifting the efficiency curve towards the left. More effective devices reduce grease build-up downstream ofthe hood, lowering the frequency of duct cleaning and reducing the fire Chart Type: line 0. μm 1 μm 10 μm 100 μm item_01 0mg/m3 0mg/m3 20mg/m3 160mg/m3 Fig. 17 Size Distribution of Common Particles Fig. 18 Gas Griddle Mass Emission Versus Particle Size (Kuehn et al. 1999) Fig. 19 Gas Underfired Broiler Mass Emission Versus Particle Size (Kuehn et al. 1999) Chart Type: line 0. μm 1 μm 10 μm 100 μm item_01 20mg/m3 40mg/m3 140mg/m3 20mg/m3 Chart Type: line 0. μm 1 μm 10 μm 100 μm item_01 0% 0% 20% 90% Fig. 20 Baffle Filter Particle Efficiency v ersus Particle Size (Kuehn et al. 1999) Inc. ASHRAE, 2019 user. single for Licensed | {}
30e30278-3a1e-4c9f-a260-3c114b822d74 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Kitchen Ventilation 34.25 hazard. Having higher-efficiency grease removal devices in the hood reduces the maintenance of downstream control equipment. Concerns about air quality also emphasize the need for higher- efficiency grease extraction from the exhaust airstream than can be provided by filters or grease extractors in exhaust hoods. Cleaner exhaust discharge to the outdoors may be required by increasingly stringent air quality regulations or where the exhaust discharge con- figuration is such that grease, smoke, or odors in discharge would create a nuisance. In some cases, exhaust air is cleaned so that it can be discharged inside (e.g., through recirculating systems). Several systems have been developed to clean the exhaust airstream, each of which presents special fire protection issues. Where odor control is required in addition to grease removal, activated charcoal, other oxidizing bed filters, or deodorizing agents are used downstream of the grease filters. Because much cooking odor is gaseous and therefore not removed by air filtration, filtration upstream of the charcoal filters must remove virtually all grease in the airstream to prevent grease build-up on the charcoal filters. See Chapter 12 of the 2017 ASHRAE Handbook- -Fundamentals for more information. The following technologies are applied to varying degrees for control of cooking effluent. They are listed by order of use in the exhaust stream after a mechanical filtration device, with particulate control upstream ofVOC control. After the description of each tech- nology are qualifications and concerns about its use. There is no consensus test protocol for evaluating these technologies in kitchen applications. Electrostatic Precipitators (ESPs). Particulate removal is by high-voltage ionization, then collection on flat plates. · Condensed grease can block airflow, especially when mounted out- doors. · As the ionizer section becomes dirty, efficiency drops because the effective ionizer surface area is reduced. · Under heavy loading, the unit may shut down because of voltage drop. Ultraviolet (UV) Destruction. This system uses ultraviolet light to chemically convert the grease into an inert substance and ozone. Construction (not performance) is evaluated for safety in accor- dance with UL Standard 710C. · Requires adequate exposure time for chemical reactions. · Personnel should not look at light generated by high-intensity UV lamps. · Exhaust fans should operate when UV lights are on because some forms of UV generate ozone. · UV is more effective on very small particles and vapor. Chart Type: line 0. μm 1 μm 10 μm 100 μm item_01 10mg/m3 20mg/m3 30mg/m3 180mg/m3 Fig. 21 Baffle Filter Particle Efficiency v ersus Particle Size (Kuehn et al. 1999) · The required frequency of duct cleaning is reduced. · Lamps need to be replaced periodically; as lamps become dirty, efficiency drops. Water Mist, Scrubber, and w ater Bath. Passage ofthe effluent stream through water mechanically entraps particulates and con- denses grease vapor. · High airflow can reduce efficiency of water baths. · Water baths have high static pressure loss. · Spray nozzles need much attention; water may need softening to minimize clogging. · Drains tend to become clogged with grease, and grease traps require more frequent service. Mist and scrubber sections need significant length to maximize exposure time. Pleated, Bag, and HEPA Filters. These devices are designed to remove very small particles by mechanical filtration. Some types also have an activated-carbon face coating for odor control. · Filters become blocked quickly if too much grease enters. · Static loss builds quickly with extraction, and airflow drops. · Almost all filters are disposable and very expensive. Activated-Carbon Filters. VOC control is through adsorption by fine activated charcoal pellets or granules. · Require a large volume and thick bed to be effective. · Are heavy and can be difficult to replace. · Expensive to change and recharge. Many are disposable. · Ruined quickly if they are grease-coated or subjected to water. · Some concern that carbon is a source of fuel for a fire. Oxidizing Pellet Bed Filters. VOC and odor control is by oxi- dation of gaseous effluent into solid compounds. · Require a large volume and long bed to be effective. · Are heavy to handle and can be difficult to replace. · Expensive to change. · Some concern about increased oxygen available in fire. Incineration. Particulate, VOC, and odor control is by high- temperature oxidation (burning) into solid compounds. · Must be at system terminus and clear of combustibles. · Are expensive to install with adequate clearances. · Can be difficult to access for service. · Very expensive to operate. Catalytic conversion. A catalytic or assisting material, when ex- posed to relatively high-temperature air, provides additional heat adequate to decompose (oxidize) most particulates and VOCs. · Requires high temperature (230°C minimum). · Expensive to operate because of high temperature requirement if integrated into the hood (can be cost-effective at the appliance level). 1.8 REPLA CEMENT (MAKEUP) AIR SYSTEMS In hood systems, where air exhausted through the hood is dis- charged to the outdoors, the volume of air exhausted must be replaced with uncontaminated outdoor air. Outdoor air must be introduced into the building through properly designed replacement air systems. Proper replacement air volume and distribution allow the hood ex- haust fan to operate as designed and facilitate proper building pres- surization, which is required for safe operation of direct-vent gas appliances (such as water heaters), prevention of kitchen odors mi- grating to adjacent building spaces, and/or maintaining a comfortable building environment. Proper pressurization enhances the building environment by preventing suction ofunfiltered and/or unconditioned outdoor air into the building envelope through doors, windows, or air Inc. ASHRAE, 2019 user. single for Licensed | {}
bba22bf6-dac1-4507-bb8d-1f834bb7defc | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 34.26 2019 ASHRAE Handbook-HVAC Applications (SI) Table 11 Outdoor Air Requirements for Dining and Food Preparation Areas ¦ Facility Type ¦ Airflow Rate, L/s per person ¦ Maximum Occupancy, persons/100 m2 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Restaurant dining area ¦ 3.8 ¦ 70 ¦ ¦ Cafeterias and fast food dining area ¦ 3.8 ¦ 100 ¦ ¦ Bars/cocktail lounges ¦ 3.8 ¦ 100 ¦ ¦ Kitchen (cooking) spaces ¦ 3.8 ¦ 20 ¦ Note: All areas are assumed nonsmoking. Source: ASHRAE Standard 62.1. handlers. IMC (ICC 2018a) requires neutral or negative pressuriza- tion in rooms with mechanical exhaust. NFPA Standard 96 requires enough replacement air to prevent negative pressures from exceeding 5 Pa, which may still be excessive for proper drafting of some direct vent appliances. To ensure pressure control, IMC also requires elec- trical interlock between exhaust and replacement air sources. This electrical interlock prevents excessive negative or positive pressures created by the exhaust fan or replacement air unit operating inde- pendently. Indoor Environmental Quality Traditionally, the primary purpose of replacement air has been to ensure proper operation of the hood. Kitchen thermal comfort and indoor environmental quality (IEQ) have been secondary. In some applications, thermal comfort and IEQ can be improved through adequate airflow and proper introduction ofreplacement air. In many of today's applications, outdoor air that meets IEQ standards is the most energy-efficient source for kitchen hood replacement air. Table 11 gives ASHRAE Standard 62.1 requirements for outdoor air per person; these requirements may be increased or decreased in certain areas if approved by the authority having jurisdiction. Outdoor air requirements affect HVAC system sizing and may require another means of introducing outdoor air. A further requirement of Standard 62.1, that outdoor air be sufficient to provide for an exhaust rate of at least 3.5 L/s per square metre of kitchen space, is generally easily met due to cooking ventilation rates. Replacement Air Introduction Replacement air may be introduced into the building through dedicated makeup air units, conventional HVAC apparatus, dedi- cated hood-system makeup air units (discussed in the section on Air Distribution), or in very limited climates, ventilators that include no conditioning means. Using enthalpy or temperature control for determining dedicated makeup air unit operation is recommended. These controls turn compressor(s), water supply, or heat sources off when outdoor air conditions warrant, while maintaining kitchen comfort, thus con- serving energy and saving money without the use of additional economizer damper systems. Dedicated Makeup Air Units. These units are specifically de- signed to heat, dehumidify, or cool 100% outdoor air. These dedi- cated units typically include modulating, heating, dehumidification, and cooling systems that react to outdoor air conditions and prevent cycling of these conditioning systems. Cycling leads to space discom- fort and higher unit energy consumption. Hot-gas reheat (HGRH) may also be included to aid in continuous dehumidification (when required by outdoor air conditions) while maintaining space com- fort. See Chapter 28 of the 2016 ASHRAE Handbook-HVAC Sys- tems and Equipment for more information on makeup air units. Conventional HV AC Units. Conventional HVAC units require fixed outdoor air intakes or economizer-controlled outdoor air dampers when they (1) supply outdoor air to meet spaces' ventilation requirements, (2) are adjacent to the kitchen area, and (3) only sec- ondarily transfer the outdoor component of the total airflow to the kitchen. To alleviate any potential overpressurization occurrences, HVAC units with economizers should have a barometric relief damper either in the return ductwork or in the HVAC unit itself. As the amount of outdoor air increases, the increasing pressure in the system opens the relief damper, so that the return air volumetric rate is only enough to maintain approximately the amount of design supply air. The amount of air required for dedicated replacement air becomes the minimum set point for the economizer damper when the hoods are operating. Fixed outdoor air intakes must be set to allow the required amount of replacement air. Outdoor air dampers should be interlocked with hood controls to open to a preset minimum posi- tion when the hood system is energized. If the zone controls call for cooling, and outdoor conditions are within economizer range, the outdoor damper may be opened to allow greater amounts of outdoor air. The maximum setting for out- door air dampers in unitary HVAC units is typically 25 to 30% of total unit air volume when the units are operating in their heating or cooling (i.e., noneconomizer) mode. Field experience has shown that large increases in air discharge velocities or volumes can occur at diffusers when HVAC units go into economizer mode. This is because the static loss through the fresh-air intake is considerably less than through the return air duct system, and thus a change from return air to fresh air reduces the overall static through the system, resulting in a relative increase in the total system flow. This can cre- ate air balance problems that negatively affect hood performance because of interference with capture and containment supply flow patterns at the hoods. A large increase in air velocity or volume from supply diffusers indicates a need for better balance between the fresh air and return air static losses. Some HVAC manufacturers state that a relief fan is required to ensure proper air balance if economizer controls call for outdoor air greater than 50% during economizer operation mode. A relief fan addresses static losses in the return duct system, thus helping minimize the static difference with the fresh-air intake. Lack of a barometric relief damper, or constrictions in the return ductwork, also may be the source of the problem. In smaller commercial buildings, including restaurants and strip centers, individual unitary rooftop HVAC equipment is common. This unitary equipment may not be adequate to supply 100% of the replacement air volume. Outdoor air must be considered during ini- tial unit selection to obtain desired unit operation and space com- fort. The space in which the hood is located should be kept at a neutral or negative pressure relative to adjacent spaces. Therefore, HVAC economizers are not recommended for equipment supplying air directly to the space in which the hood is located, unless the economizer installation includes equipment and controls to main- tain overall system air balance and to prevent excessive air dis- charge velocities or volumes. In climates with higher summer dew-point design conditions, consider adding active dehumidification (such as hot-gas reheat) for units supplying outdoor air for ventilation at rates greater than 10% of unit total airflow. Replacement Air Categories Three categories of replacement air have been defined for design of energy-efficient replacement air systems: supply, makeup, and transfer. IAQ engineers must design outdoor air systems to meet total building ventilation requirements. Replacement air for kitchen ventilation must integrate into the total building IAQ design. Total kitchen ventilation replacement air may consist of only dedicated makeup air; however, in many energy-efficient designs, outdoor air required for ventilating the kitchen or adjacent spaces is used as supply or transfer air to augment or even eliminate the need for ded- icated makeup air. Typically, replacement air will be a combination Inc. ASHRAE, 2019 user. single for Licensed | {}
390c5385-3e2b-48cc-8a5f-673eed469f19 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Kitchen Ventilation 34.27 of categories from multiple sources. The source of replacement air typically determines its category. Kitchen supply air is outdoor air introduced through the HVAC or ventilating apparatus, dedicated to the comfort conditioning of the space in which the hood is located. In many cases this may be an ideal source of replacement air because it also provides comfort conditioning for the occupants. Makeup air is outdoor air introduced through a system dedi- cated to providing replacement air specifically for the hood. It is typically delivered directly to or close to the hood. This air may or may not be conditioned. When conditioned, it may be heated only; generally only in extreme environments will it be cooled. When included, makeup air typically receives less conditioning than space supply air. The IMC (ICC 2018a) requires makeup air be conditioned to within 5.5 K of the kitchen space, except when introducing replacement air that does not decrease kitchen comfort (see the section on Energy Considerations for additional informa- tion). This can be accomplished with proper distribution design. Typical sources of makeup air heating include direct and indirect gas-fired units, hot-water coils (with freeze protection), and, in some cases or geographic areas, electric resistance heating. When cooling is provided, the outdoor air design conditions must be con- sidered. A low-dew-point design is required for effective use of evaporative coolers. Higher-dew-point design temperatures may require water or direct exchange (DX) coils for cooling and/or dehumidification. Temperature of makeup air introduced varies with distribution system and type of operation. Transfer air is outdoor air, introduced through the HVAC or ven- tilating apparatus, dedicated to comfort conditioning and ventilation requirements of a space adjacent to the area in which the hood is located. The device providing transfer air must operate and supply outdoor air whenever the hood is operating. Air must not be trans- ferred from spaces where airborne contaminants such as odors, germs, or dust may be introduced into the food preparation or serving areas. Air may be transferred through wall openings, door louvers, or ceiling grilles connected by duct above the ceiling. Depending on grille and duct pressure drop, a transfer fan(s) may be required to avoid drawing transfer air through lower-pressure-drop openings at velocities that may be detrimental to food service processes. When using openings through which food is passed, transfer velocities should not exceed 0.25 m/s to avoid excessive cooling of the food. Transfer air is an efficient source of replacement air because it per- forms many functions, including ventilating and/or conditioning the adjacent space, replacing air for the hood, and additional condition- ing for the space in which the hood is located. Only the portion of air supplied to the adjacent space that originated as outdoor air may be transferred for replacement air. The IMC (ICC 2018a) recognizes the use of transfer air as a replacement air source. In large buildings such as malls, supermarkets, and schools, adequate transfer air may be available to meet 100% of hood replacement air requirements. Malls and multiple-use-occupancy buildings may specify a minimum amount of transfer air to be taken from their space to keep cooking odors in the kitchen, or they may specify the maximum transfer air available. Code restrictions may prevent the use of corridors as spaces through which transfer air may be routed. Conditions of trans- fer air are determined by conditioning requirements of the space into which the air is initially supplied. Air Distribution The design of a replacement air distribution system may enhance or degrade hood performance. Systems that use a combination of kitchen supply, makeup, and transfer air include various compo- nents of distribution. Distribution from each source into the vicinity of the hood must be designed to eliminate high velocities, eddies, swirls, or stray currents that can interrupt the natural rising of the thermal plume from cooking equipment into the hood, thus degrading the performance of the hood. Methods of distribution may include conventional diffusers, compensating hood designs, transfer devices, and simple openings in partitions separating building spaces. Regardless of the method selected, it is important to always deliver replacement air to the hood (1) at proper velocity and (2) uniformly from all directions to which the hood is open. This minimizes excessive cross-currents that could cause spillage. Proper location and/or control of HV AC return grilles is therefore critical. The higher air velocities typically recommended for general ventilation or spot cooling with unconditioned air (0.4 to 1.0 m/s at worker) should be avoided around the hood. Hood manufacturers offer a variety of compensating hoods, plenums, and diffusers de- signed to introduce replacement air effectively. Hood-Supplied Replacement Air (Compensating Hoods). A common way of distributing replacement air is through compen- sating systems that are integral with the hood. Figure 22 shows four typical compensating hood configurations. Because actual flows and percentages may vary with hood design, the manu- facturer should be consulted about specific applications. The following are typical descriptions of configurations that include perimeter supply. Brohard et al. (2003) investigated the effects of six methods of introducing replacement air on three hood styles, Three hood types were tested: (1) wall-mounted canopy, (2) island-mounted canopy, and (3) proximity (back shelf). Gas underfired broilers and gas grid- dles, respectively representing heavy-duty and medium-duty appli- ances, were tested. Idle and emulated cooking conditions were also tested. The MUA strategies included (1) displacement ventilation (base case), (2) ceiling diffuser, (3) hood face diffuser, (4) air curtain diffuser, (5) back wall supply, and ⑥ short-circuit supply. The influences of air mass disturbances (drafts) and tapered side panels were also investigated. Each replacement air strategy and specific configuration tested compromised the exhaust hood's ability to completely capture and contain the thermal plume and/or effluents at higher replacement airflow rates (expressed as a percentage of the threshold exhaust rate). Temperature of locally supplied makeup air also affected hood performance, because air density affects the dynamics of air movement around the hood. Generally, hotter makeup air temperatures (e.g., greater than 32°C) affect hood per- formance more adversely than cooler air (e.g., less than 24°C). Air Curtain Supply. This method is typically used for spot-cooling the cooking staff to counter the severe radiant heat generated from equipment such as gas or electric broilers. The air must be heated and/ or cooled, depending on local climate. Air curtain discharge can be along the length of the hood front only or along all open sides of the ![image](/image/placeholder) FRONT-FACE DISCHARGE DOWN DISCHARGE INTERNAL DISCHARGE BACK WALL DISCHARGE Fig. 22 Compensating Hood Configurations Inc. ASHRAE, 2019 user. single for Licensed | {}
7f5423d6-707e-489b-831f-7536064e163a | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 34.28 2019 ASHRAE Handbook HVAC Applications (SI) hood. When discharge velocity is too low, air tends to enter the hood directly and may have little effect on hood performance. When dis- charge velocity is too high, air entrains the cooking plume and spills it into the room. Ideal velocity and throw can improve hood perfor- mance and redirect the thermal plume toward the filters. Discharge velocities must be carefully selected to avoid discomfort to personnel and cooling of food. Limit the percentage of makeup air supplied through an air cur- tain to less than 20% of the hood's exhaust flow. At these low air velocities, an air curtain may enhance capture and containment, depending on design details. However, at higher makeup airflow rates, the air curtain is one ofthe worst performing makeup air strat- egies. The negative effect of an air curtain is clearly illustrated in Figure 23 by the schlieren flow visualization recorded during a test of a wall-mounted canopy hood operating over two gas underfired broilers. Introducing makeup air through an air curtain is a risky option. An air curtain (by itself or in combination with another pathway) is not recommended, unless velocities are minimized and the designer has access to performance data on the actual air curtain configura- tion being specified. Typical air curtains are easily adjusted, which could cause cooking effluent to spill into the kitchen by inadver- tently creating higher-than-specified discharge velocities. Inc. ASHRAE, 2019 user. Back- Wall Supply. A makeup air plenum is installed between the back of the hood and wall. The full-length plenum typically extends down the wall to approximately 150 mm below the cooking surface or 600 to 900 mm above the floor. The depth of the plenum is typi- cally 150 mm. Makeup air is discharged behind and below the cooking equipment. The bottom of the plenum is provided with dif- fusers and may also include a balancing damper. As with front-face discharge, air volume and discharge velocity dictate how far into the space the makeup air will travel. The amount of travel and local cli- mate dictate the amount of heating and/or cooling needed. Support for wall shelves, salamander broilers, or cheesemelters mounted under the hood must be considered. The plenum structure typically does not provide sufficient support for mounting these items. single for Licensed Fig. 23 Schlieren Image Showing Thermal Plume Being Pulled Outside Hood by Air Curtain (Brohard et al. 2003) ![image](/image/placeholder) /↓ Back-wall supply can be an effective strategy for introducing makeup air (Figure 24). In most cases, it allows significant amounts of air to be locally supplied without a detrimental effect on hood C&C performance. Local makeup air mostly enters the kitchen space, rather than remaining contained in the cooking zone. This potentially creates an additional heat and moisture load on the kitchen, particularly because most replacement air supplied is mixed with room air before being exhausted. Front-Face Supply. Supplying air through the front face of the hood is a configuration recommended by many hood manufacturers. In theory, air exits the front-face unit horizontally into the kitchen space. However, a front-face discharge with louvers or perforated face can perform poorly, ifits design does not consider discharge air velocity and direction. Figure 25 presents a poorly designed per- forated face supply, which can negatively affect hood capture perfor- mance in the same way as an air-curtain or four-way diffuser. To improve front-face performance, internal baffling and/or a double layer of perforated plates may be used improve the uniformity of air- flow. In addition, greater distance between the lower capture edge of the hood and the bottom of the face discharge area may decrease the tendency of the replacement air supply to interfere with hood capture and containment. In general, face discharge velocities should not exceed 0.75 m/s (i.e., replacement air flow rate divided by gross discharge area) and should exit the front face in a horizontal direction. To help ensure proper performance, the discharge of the back- wall supply should be at least 300 mm below cooking surfaces of appliances, to prevent the relatively high-velocity makeup air from interfering with gas burners and pilot lights. Back-wall plenums with larger discharge areas may provide increased airflow rates as long as discharge velocities remain below maximum thresholds. The quantity of air introduced through the back-wall supply should be no more than 60% of the hood's exhaust flow. Internal Makeup Air. This method, also known as short-circuit, introduces makeup air directly into the exhaust hood cavity. This design has limited application, and the amount of air that can be introduced varies considerably with the type of cooking equipment and exhaust flow rate. As noted previously, thermal currents from ![image](/image/placeholder) Fig. 24 Schlieren Image Showing Thermal Plume Being Captured with Back-Wall Supply (Brohard et al. 2003) | {}
8f0e50e6-fb7c-4868-a1e8-1d93e8559c23 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Kitchen Ventilation 34.29 cooking equipment create a plume of a certain volume that the hood must remove. The hood must therefore draw at least this vol- ume of air from the kitchen, in addition to any internal makeup. If the net exhaust flow rate (total exhaust less internal makeup air) is less than the plume volume, part of the plume may spill out of the hood. Internal makeup air is typically not conditioned; however, depending on local climate, manufacturer's design, type of cooking equipment, and local codes, conditioning may be required. Some local authorities approve internal discharge hoods, and some do not. For unlisted hoods, IMC (2018a) requires the net quantity of exhaust air to be calculated by subtracting any airflow supplied directly to a hood cavity from the total exhaust flow rate of a hood. Listed hoods are operated in accordance with the terms of the list- ing. All applicable codes must be consulted to ensure proper crite- ria are followed. When short-circuit hoods are operated with excessive internal makeup air, they typically fail to capture and contain the cooking effluent (Figure 26). ASHRAE Standard 154 limits the quantity of internal replacement air to no more than 10% of the exhaust airflow. Additionally, the introduction of untempered makeup air results in uncomfortable kitchen conditions. Independent research (Brohard et al. 2003) recommends not using this compensating hood design; therefore, there is no additional design information in this chapter. Multiple Discharge. This method may combine internal, perim- eter, air curtain, and/or front face. Each may be served by a separate or common plenum. Balancing dampers may be provided for one or both discharge arrangements. These dampers may be used to fine- tune the amount of air discharged through the air curtain or front face. However, this method inherits the performance problems of each of the individual types, and combining them tends to com- pound these issues. Perforated Perimeter Supply. Perforated perimeter supply is sim- ilar to a front-face supply, but the air is directed downward, as in Figure 27, toward the hood capture area. This may be advantageous under some conditions, because air is directed downward into the hood capture zone. ![image](/image/placeholder) Fig. 25 Schlieren Image Showing Thermal Plume Being Pulled Outside Hood by Front Face (Brohard et al. 2003) For proper hood performance, discharge velocities should not exceed 0.75 m/s (i.e., makeup airflow rate divided by gross discharge area) from any section of the diffuser, and the distance to lower edge of the hood should be no less than 460 mm, or the system begins to act like an air curtain. An increase in the plenum discharge area ![image](/image/placeholder) Fig. 26 Schlieren Image Showing Thermal Plume Being Displaced by Short-Circuit Supply, Causing Hood to Spill (Brohard et al. 2003) ![image](/image/placeholder) Fig. 27 Schlieren Image Showing Effective Plume Capture with Replacement Air Supplied Through 400 mm Wide Perforated Perimeter Supply, Shown with Additional Front Overhang (Brohard et al. 2003) Inc. ASHRAE, 2019 Ⓒ user. single for Licensed | {}
d7f5fb6e-0deb-4441-a59b-cfd334cc5b6d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 34.30 2019 ASHRAE Handbook HVAC Applications (SI) lowers the velocity for a given flow of replacement air and reduces the chance ofit affecting capture and containment. If the perforated perimeter supply is extended along the sides of the hood as well as the front, the increased area allows proportionally more makeup air to be supplied. In all cases, the velocity downward 50 mm above the lower edge of the hood should not exceed 0.4 m/s. Room-Supplied Makeup Air (Diffusers and Grilles). There are various ways to distribute replacement air in the vicinity of the hood to avoid cross currents that degrade hood performance. Non- aspirating diffusers are recommended, especially adjacent to the hood. For more information on diffusers, see Chapter 20 of the 2017 ASHRAE Handbook-Fundamentals, Chapter 20 of the 2016 ASH- RAE Handbook-HVAC Systems and Equipment, and Chapter 58 of this volume. Typical devices include the following. Directional Ceiling Diffusers. Air from these two- or three- way diffusers should not be directed toward exhaust hoods, where it might disturb the thermal plume and adversely affect hood performance. The diffuser should be located so that the jet velocity at the lip of the hood does not exceed 0.4 m/s. Four- Way Directional Ceiling Diffusers. Four-way directional diffusers located close to kitchen exhaust hoods (Figure 28) can have a detrimental effect on hood performance, particularly when flow through the diffuser approaches its design limit. They are not recommended within 4.5 m of the hood. Perforated Ceiling Diffusers. These nonaspirating, perforated- face diffusers may have internal deflecting louvers, but should not be capable of directing the airflow toward the hood. The diffuser should be located so that the jet velocity at the lip of the hood does not exceed 0.4 m/s. In some code jurisdictions, when conventional ceiling diffusers are used, only perforated diffusers are allowed in commercial kitchens. Perforated ceiling diffusers can be used near the hood, although a greater number of these diffusers may be re- quired to reduce air velocities for a given supply rate. To help ensure proper hood performance, air from a perforated diffuser near the hood should not be directed toward the hood. If ceiling-supplied air ![image](/image/placeholder) Fig. 28 Schlieren Image Showing Thermal Plume Being Pulled Outside Hood by Air Discharged from Four-Way Diffuser (Brohard et al. 2003) must be directed toward a hood, air discharge velocity at the diffuser face should be selected so that the terminal velocity does not exceed 0.4 m/s at the edge of the hood capture area. Slot Diffusers. Because the slot opening of these devices is gen- erally small compared to air volume, air velocity is often higher than that which would be obtained with two-, three-, and four-way dif- fusers. Also, because airflow is mostly downward, the potential for negatively affecting hood performance is quite high if outlets are near the hood. If used with relatively high ceilings, the potential for negative impact is less because the velocity diminishes as air dif- fuses downward. Slot diffusers are usually nonaspirating. Displacement Diffusers. These devices, designed to provide low- velocity laminar flow over the diffuser surface, typically supply air from 10 to 21 °C in a kitchen, depending on equipment loads. Hotter, stratified air is removed from the ceiling through exhaust ducts or returned to the HVAC system to be conditioned. In contrast with ceiling diffusers, which require complete mixing to be effective, stratification is the desired effect with displacement diffusers. Displacement diffusers were used to determine the baseline for Brohard et al. 's (2003) replacement air study, because they pro- vided a uniform, nearly laminar bulk airflow. This low-velocity bulk airflow is optimal for attaining C&C with the lowest exhaust rate. Therefore, supplying replacement air through displacement diffusers (Figure 29) may be an effective strategy for introducing replacement air. Adequate wall or floor space is required to accom- modate displacement diffusers. Other Factors That Influence Hood Performance. Hood Style. Wall-mounted canopy hoods function effectively with a lower exhaust flow rate than single-island hoods. Island canopy hoods are more sensitive to makeup air supply and cross drafts than wall-mounted canopy hoods. Back-shelf/proximity hoods generally exhibit lower capture and containment exhaust rates, and in some cases, perform the same job at one-third of the exhaust rate required by a wall-mounted canopy hood. ![image](/image/placeholder) Fig. 29 Schlieren Image Showing Plume Being Effectively Captured when Replacement Air Is Supplied at Low v elocity from Displacement Diffusers (Brohard et al. 2003) Inc. ASHRAE, 2019 user. single for Licensed | {}
b3972181-1143-438d-ae65-bf7e8c98704c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Kitchen Ventilation 34.31 Cross Drafts. Cross drafts have a detrimental effect on all hood/ appliance combinations. Cross drafts adversely affect island canopy hoods more than wall-mounted canopy hoods. A fan in a kitchen, especially pointing at the cooking area, severely degrades hood per- formance and may make capture impossible. Cross drafts required at least a 37% increase in exhaust flow rate; in some cases, C&C could not be achieved with a 235% increase in exhaust rate (Brohard et al. 2003). Cross drafts can result from portable fans, movement in the kitchen, or an unbalanced HVAC system, which may pull air from open drive-through windows or doors. Side Panels. Side (or end) panels allow a reduced exhaust rate in most cases, because they direct replacement airflow to the front of the hood. Installing side panels improved C&C performance for static conditions an average 10 to 15% and up to 35% for dynamic (cross-draft) conditions. They are a relatively inexpensive way to enhance performance and reduce the total exhaust rate. Partial side panels can provide virtually the same benefit as full panels. One of the greatest benefits of side panels is to mitigate the negative effect of cross drafts. Brohard et al. (2003) recommend reducing the impact that locally supplied makeup air may have on hood performance by minimizing makeup air velocity as it is introduced near the hood. This can be accomplished by minimizing the volume of makeup air through any single distribution system or by distributing through multiple config- urations. The chances of makeup air affecting hood performance increase as the percentage of the locally supplied makeup air (rela- tive to the total exhaust) is increased. In fact, the 80% rule of thumb for sizing airflow through a makeup air system may be a recipe for trouble. Effective introduction of replacement air (whether supplied through displacement ventilation diffusers, perforated diffusers lo- cated in the ceiling, and/or as transfer air from adjacent spaces) should be designed to limit velocities approaching the hood to less than 0.4 m/s. Design Recommendations. The first step to reducing the re- placement air requirement is lowering the design exhaust rate, which can be accomplished by prudent selection and application of UL Standard 710 listed hoods. Using side panels on canopy hoods may increase effectiveness and mitigate cross drafts, and is highly recom- mended where applicable. The next step is to take credit for outdoor air that must be supplied by the HVAC system to meet code require- ments for space or occupant ventilating. Depending on the architec- tural layout, it may be practical to transfer most of this air to the kitchen. Assuming the transfer air is conditioned and properly intro- duced, it may enhance hood performance and improve the kitchen environment. For more information, see the sections on Energy Considerations and Commercial Exhaust Hoods in this chapter. 1.9 HV AC SYSTEM DESIGN As mentioned previously, one purpose of kitchen ventilation is to provide a comfortable environment for employees. Engineers who are used to designing HVAC loads for more traditional spaces (e.g., offices) may not realize how different the kitchen environment can be: kitchens require a much greater quantity of outdoor air as makeup, and have much higher internal loads (including sensible radiated heat gain from appliances underneath hoods, sensible and latent loads from unhooded equipment including warewashers, and sometimes outdoor air loads). Hooded and Unhooded Appliance Loads One of the challenges in performing cooling and heating load calculations for a kitchen is determining the space heat gains from the cooking appliances. Given that many of the largest cooking appliances include exhaust hoods to remove the smoke, grease, and Table 12 Appliance Heat Gain Reference ¦ Appliance Location ¦ Fuel Source ¦ Chapter 18, 2017 ASHRAE Handbook- Fundamentals Table Reference ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Unhooded ¦ All ¦ 5A and 5B ¦ ¦ Hooded ¦ Electric ¦ 5C ¦ ¦ Hooded ¦ Gas ¦ 5D ¦ ¦ Hooded ¦ Solid Fuel ¦ 5E ¦ ¦ Hooded and unhooded dishwashers ¦ All ¦ 5F ¦ Table 13 Heat Gain from Outdoor Air Infiltration Chapter 18, 2017 ASHRAE Handbook- Fundamentals ¦ Type of Heat Gain ¦ Equation ¦ Equation Reference ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Sensible ¦ Is = 1.23Qs t ¦ (9) ¦ ¦ Latent ¦ ql = 3010�s W ¦ (10) ¦ ¦ Total (Sensible + Latent) ¦ It = 1.20s t ¦ (7) ¦ Notes: Qs is flow in m3/s, t is °C, W is kg water per kg air, h is kJ/kg, and 9 is heat gain in W. is the difference between outdoor and space-neutral (room design) conditions. heat, determining the heat gain can be challenge. There may also be a large number of smaller appliances that do not include exhaust hoods and which reject all their heat directly to the space. Tables 5A to 5F in Chapter 18 of the 2017 ASHRAE Hand- book-Fundamentals list typical equipment and the heat rejected into the kitchen. The data contained in these tables were updated as part of ASHRAE research project RP-1362 (Swierczyna et al. 2008). Table 12 summarizes which tables to use for what type of equipment. For the majority of appliances, table heat gain values were deter- mined during idle or standby condition: that is, the appliance was fully warmed up and in its ready-to-cook condition. (Typically, an appliance is in standby for as much as 70% of the day.) For appli- ances installed under an exhaust hood, the amount ofheat emitted as radiation is listed, because this heat ends up heating nearby objects. For the appliances that are not installed under a hood because of their low energy consumption or lack of cooking effluent, the amount of both sensible and latent heat is listed, in addition to the radiation. The greatest challenge with using these data is determining the diversity or usage factor of the appliances. It may be difficult to anticipate how often the appliance will be at full cooking or at some standby condition. Any assumptions made can be rendered incor- rect by a change in kitchen throughput or sales. Determining the correct heat gain is an involved procedure that requires input from the entire kitchen design team. Outdoor Air Loads If the outdoor air is not conditioned to a space-neutral (or space design) condition, then the sensible and latent loads from this volume of air will impact the existing HVAC system at least to some extent because however the air is introduced into the kitchen some of it will enter the kitchen space especially if that air is hot and humid. Table 13 summarizes the relevant equations from Chapter 18 of the 2017 ASHRAE Handbook-Fundamentals. It is recom- mended that the load from at least 50% of the outdoor air brought into the kitchen to replace the exhaust air be used in the heat gain calculations. Inc. ASHRAE, 2019 user. single for Licensed | {}
f014d768-3bde-4a9d-97e4-5606ab9740f9 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 34.32 Chart Type: line 18 21 24 27 30 33 36 39 item_01 0 0 0 0 1.75 1.25 1.75 1.75 Fig. 30 Summer Temperatures by Height and Kitchen Zone in Casual Kitchens The remaining heat gains from lighting, envelope, and people can be calculated following the procedure described in Chapter 18 of the 2017 ASHRAE Handbook- -Fundamentals. Thermal Comfort Research Results ASHRAE research project RP-1469 (Stoops et al. 2013) con- ducted a large field survey on kitchens in the United States to iden- tify how well engineers are satisfying design kitchen conditions. Researchers monitored space conditions in 105 kitchens during the summer. Figures 30 to 32 show the resulting temperatures in three areas of the restaurant (kitchen, food preparation, and warewashing) as a function of height above the floor. Stoops et al. found that temperature increases with height above the floor: although floor-level temperatures ranged from approxi- mately 24 to 28°C, at head level for staff temperatures ranged from 30 to 37°C. Higher temperatures at increasing heights can be par- tially attributed to radiated heat gain from the appliances underneath hood(s), but there is no question that the space conditions were not being met on average for most of the kitchens monitored in this study, even at the floor level. See Chapter 9 of the 2017 ASHRAE Handbook-Fundamentals for more information. 1.10 EXHAUST SYSTEMS Exhaust systems remove effluent produced by appliances and cooking processes to provide fire and health safety, comfort, and aesthetics. Typical exhaust systems simultaneously incorporate fire prevention designs and fire suppression equipment. In most cases, these functions complement each other, but in other cases they may seem to conflict. Designs must balance these functions. For exam- ple, fire-actuated dampers may be installed to minimize the spread of fire to ducts, but maintaining an open duct might be better for removing smoke of an appliance fire from the kitchen. Duct Systems Exhaust ducts convey exhaust air from the hood to the out- doors, along with any grease, smoke, VOCs, and odors that are not extracted from the airstream along the way. These ducts may also be used to exhaust smoke from a fire. To be effective, ducts must be greasetight; it must be clear of combustibles, or combustible mate- 2019 ASHRAE Handbook-HVAC Applications (SI) Chart Type: line 18 21 24 27 30 33 36 39 item_01 0.0°C 0.0°C 0.0°C 1.5°C 1.0°C 1.0°C 1.5°C 1.5°C Fig.31 Summer Temperatures by Height and Kitchen Zone in Institutional Kitchens Chart Type: line 18 21 24 27 30 33 36 39 item_01 0.0°C 0.0°C 0.0°C 1.5°C 1.5°C 1.5°C 1.5°C 1.0°C Fig. 32 Summer Temperatures by Height and Kitchen Zone in Quick-Service Restaurant Kitchens rial must be protected so that it cannot be ignited by a fire in a duct; and ducts must be sized to convey the volume of airflow necessary to remove the effluent. Model building codes, such as the IMC (ICC 2018a), and stan- dards, such as NFPA Standard 96, set minimum air velocity for exhaust ducts at 2.5 m/s. Maximum velocities are limited by pres- sure drop and noise and typically do not exceed 12.5 m/s. Until recently, NFPA Standard 96 and the IMC had set the minimum air velocity through the duct at 7.5 m/s. However, based on ASHRAE research (Kuehn 2000) that indicated that there is no basis for spec- ifying 7.5 m/s minimum duct velocity for commercial kitchen ven- tilation and that grease deposition in ducts does not increase when duct velocity is lowered to 2.5 m/s, NFPA and IMC requirements Inc. ASHRAE, 2019 user. single for Licensed | {}
25b39115-e0a3-4063-b5b4-6a85d46894e3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Kitchen Ventilation 34.33 were changed to 2.5 m/s. This allows flexibility for design of variable-speed exhaust systems and retrofitting older systems, though because of spatial and cost constraints, current design prac- tice for new single-speed systems generally is to design duct veloc- ity between 7.6 and 9 m/s. Ducts should have no traps that can hold grease, which would be an extra fuel source in the event of a fire, and ducts should pitch toward the hood or an approved reservoir for constant drainage of liquefied grease or condensates. On long duct runs, allowance must be made for possible thermal expansion because of fire, and the slope back to the hood or grease reservoir must conform to local code requirements. Single-duct systems carry effluent from a single hood or section of a large hood to a single exhaust termination. In multiple-hood systems, several branch ducts carry effluent from several hoods to a single master duct that has a single termination. See the section on Multiple-Hood Systems for more information. Ducts may be round or rectangular. Standards and model codes contain minimum specifications for duct materials and construc- tion, including types and thickness of materials, joining methods, and minimum clearance of 460 mm to combustible materials. Listed factory-built modular grease duct systems are available as an alter- native to code-prescribed welded systems. These listed systems typ- ically incorporate stainless steel liners and double-wall, insulated construction, allowing reduced clearances to combustibles and non- welded joint construction. When fire-rated enclosures are required for grease ducts, either fired-rated enclosures are built around the duct or the newer listed, field-applied grease duct enclosures can be used directly on the grease duct, or the newer listed, factory-built, modular grease ducts with insulated construction can be used as an integral fire-rated enclosure. Most of these listed systems allow zero clearance to com- bustibles and also provide 1 h or 2 h fire resistance rating, and can be used in lieu of a fire-rated enclosure required in NFPA Standard 96 and IMC (ICC 2018a). See Chapter 19 in the 2016 ASHRAE Hand- book-HVAC Systems and Equipment and the Fire Safety section in this chapter for more information on grease duct construction. 1.11 EXHAUST FANS Types of Exhaust Fans Exhaust fans for kitchen ventilation must be capable ofhandling hot, grease-laden air. The fan should be designed to keep the motor out of the airstream and should be effectively cooled to prevent pre- mature failure. To prevent roof damage, the fan should contain and properly drain all grease removed from the airstream. See Chapter 21 in the 2016 ASHRAE Handbook- -HVAC Systems and Equip- ment and the Fire Safety section in this chapter for more information on fans. The following types of exhaust fans are commonly used; all have centrifugal wheels with backward-inclined blades: · Power roof ventilator (PRV). Also known as upblast fans, PRVs are designed for mounting at the exhaust duct outlet (Figure 33), and discharge upward or outward from the roof or building. Alu- minum upblast fans must be listed for the commercial kitchen exhaust application in compliance with UL Standard 762, and must include a grease drain, grease collection device, and integral hinge kit to permit access for duct cleaning. · Centrifugal fan. Also known as a utility set, this is an AMCA Arrangement 10 centrifugal fan, including a field-rotatable blower housing, blower wheel with motor, drive, and often a motor/drive weather cover (Figure 34). These fans are typically constructed of steel and roof-mounted. Where approved, centrifugal fans can be mounted indoors and ducted to discharge outdoors. The inlet and outlet are at 90° to each other (single width, single inlet), and the outlet can usually be rotated to discharge at different angles around a vertical circle. The lowest part of the fan must drain to an approved container. When listed in accordance with UL Standard 762, a grease drain, grease collection device, and blower housing access panel are required. · Tubular centrifugal. These fans, also known as inline fans, have the impeller mounted in a cylindrical housing discharging the gas in an axial direction (Figure 35). Where approved, these fans can be located in the duct inside a building if exterior fan mounting is not practical for wall or roof exhaust. They are always constructed of steel. The gasketed flange mounting must be greasetight yet removable for service. The lowest part of the fan must drain to an approved container. When listed in accordance with UL Standard 762, a grease drain, grease collection device, and blower housing access panel are required. ![image](/image/placeholder) Fig. 33 Power Roof Ventilator (Upblast Fan) ![image](/image/placeholder) DUCT DUCT DUCT UTILITY WHEEL · TE FAN SIDE VIEW END VIEW Fig. 34 Centrifugal Fan (Utility Set) ![image](/image/placeholder) Fig. 35 Tubular Centrifugal (Inline) Fan Inc. ASHRAE, 2019 user. single for Licensed | {}
488bab5b-0dc9-4694-bed4-a180e5fe6a9e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 34.34 2019 ASHRAE Handbook- - HVAC Applications (SI) ![image](/image/placeholder) GREASE TRAP GREASE TRAP Fig. 36 High-Plume Fan · High-plume fan. These fans may be used for kitchen applications when the requirements for a high exhaust plume are required (Figure 36). These fans generate a high nozzle exit velocity, which forces the exhaust plume to higher elevations and thus discharges smoke and grease laden vapors into the atmosphere. This fan is applicable when the intent is to prevent re-entraining smoke and grease-laden kitchen exhaust into the building makeup air system, or to discharge it over neighboring buildings or structures. When listed in accordance with UL Standard 762, a grease drain, grease collection device, and blower housing access panel are required. Because of the size and weight of these fans, the installation should be verified for structural integrity by a structural engineer. Items to be evaluated may include roof load, wind load, and seismic conditions. Exhaust Terminations Rooftop. Rooftop terminations are preferred because discharge can be directed away from the building, the fan is at the end of the system, and the fan is accessible. Common concerns with rooftop terminations are as follows: · Exhaust system discharge should be arranged to minimize reentry of effluent into any fresh-air intake or other opening to any build- ing. This requires not only separating the exhaust from intakes, but also knowledge of the direction ofthe prevailing winds. Some codes specify a minimum distance to air intakes. See Chapter 46 of this volume for more information on exhaust discharge princi- ples and considerations. · In the event of a fire, neither flames, radiant heat, nor dripping grease should be able to ignite the roof or other nearby structures. · All grease from the fan or duct termination should be collected and drained to a remote closed container to preclude ignition. · Rainwater should be kept out ofthe exhaust system, especially out ofthe grease container. Ifthis is not possible, then the grease con- tainer should be designed to separate water from grease and drain the water back onto the roof. Figure 37 shows a rooftop utility set with a stackhead fitting, which directs exhaust away from the roof and minimizes rain penetration. Discharge caps should not be used because they direct exhaust back toward the roof and can become grease-fouled. ![image](/image/placeholder) UPPER STACK HELD OFF 4Dh FROM LOWER STACK 13 mm ON ALL SIDES. BRACKET UPPER STACK TO LOWER STACK + , 150 mm MIN. I REDUCER IF NECESSARY FOR ROUND DUCT, TO INCREASE STACK Dh = D. VELOCITY TO DISPERSE EFFLUENT FOR RECTANGULAR DUCT, Dh = (H + W)/2 UTILITY SET Fig. 37 Rooftop Centrifugal Fan (Utility Set) with Vertical Discharge Outside Wall. Wall terminations are less common today but are still occasionally used in new construction. The fan may or may not be the terminus of the system, located on the outside of the wall. Common concerns with wall terminations are as follows: · Discharge from the exhaust system should not be able to enter any fresh-air intake or other opening to any building. · Adequate clearance to combustibles must be maintained. · To avoid grease draining down the side of the building, duct sec- tions should pitch back to the hood inside, or a grease drain should be provided to drain grease back into a safe container inside the building. · Discharge must not be directed downward or toward any pedes- trian areas. · Louvers should be designed to minimize their grease extraction and to prevent staining of the building facade. Recirculating Systems. With these units, itis critical to keep com- ponents in good working order to maintain optimal performance. Otherwise, excessive grease, heat, and odors will accumulate in the premises. As with other terminations, containing and removing grease and keeping the discharge as far as possible from combustibles are the main concerns. Some units are fairly portable and could be set in an unsafe location. The operator should be made aware of the impor- tance of safety in locating the unit. These units are best for large, unconfined areas with a separate outdoor exhaust to keep the envi- ronment comfortable. 1.12 FIRE SAFETY The combination of flammable grease vapor and particulates car- ried by kitchen ventilation systems and the potential of cooking equipment to be an ignition source creates a higher hazard level than normally found in HVAC systems. Design of an exhaust system serving commercial cooking equipment that may produce grease- laden vapors (i.e., a Type I exhaust system) must include a fire sup- pression system, as required by NFPA Standard 96 and the Interna- tional Mechanical Code (IMC; ICC 2018a). The IMC further requires that the fire suppression system comply with the Interna- tional Building Code (IBC; ICC 2018c) and the International Fire Code (IFC; ICC 2018d). By further reference, these codes and stan- Inc. ASHRAE, 2019 user. single for Licensed | {}
f18810e9-9f1b-4bc4-900d-968688f96f0d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Kitchen Ventilation 34.35 dards require that automatic fire suppression systems for Type I hoods must be listed to UL Standard 300. Replacement air systems, air-conditioning systems serving a kitchen, and exhaust systems serving cooking equipment that does not produce grease-laden vapor have no specific fire protection re- quirements beyond those applicable to similar systems not located in kitchens. However, an exhaust system serving any grease-produc- ing cooking equipment must be considered a grease exhaust system even ifit also serves non-grease-producing equipment. Fire safety starts with proper design, followed by proper operation and maintenance of the cooking equipment and the exhaust system, including frequent and thorough cleaning of grease deposits in the area of appliances, and exhaust filters, hoods, and ducts. After that, the three primary aspects of fire protection in a grease exhaust system are (1) to extinguish a fire quickly once it has started, (2) to prevent the spread of fire from or to the grease exhaust system, and (3) to prevent heat transfer to building components from a grease duct fire ifthe fire- extinguishing system fails. Additionally, UL Standard 300 requires that the fire suppression system not disperse burning grease outside the fire zone, and that, after a fire is suppressed by a fire suppression system, it must remain suppressed for at least 20 min. Solid-Fuel Cooking. When solid-fuel cooking is used in com- mercial kitchens, fire risk is increased by the formation and deposi- tion of combustible creosote in exhaust systems. Creosote is formed when unburnt vapors from solid-fuel combustion condense in exhaust systems. Creosote production is increased when moisture is present in solid-fuel combustion, such as when green or wet wood is burned, or when solid fuel is burned in the presence offuel gas com- bustion products, one of which is water vapor. Chapter 14 ofNFPA Standard 96 provides extensive requirements for solid-fuel cooking operations. Note that solid-fuel cooking appliances are referred to as "extra-heavy-duty cooking appliances" in the IMC and are defined as those using open-flame combustion of solid fuel at any time during the cooking process. Fire Suppression Systems NFPA Standard 96 requires that exhaust systems serving grease- producing equipment must include a fire-extinguishing system that protects the cooking equipment, hood interior, hood filters or grease extractors, ducts, and any other grease-removal devices in the system. Actuation of any fire-extinguishing system must not depend on building electricity. If actuation relies on electricity, it must be sup- plied with standby power, usually in the form of battery backup. Listed fire suppression systems must also automatically shut off all supplies of fuel and energy to all equipment protected by that system. Any gas appliance not requiring protection but located under the same ventilating equipment must also be shut off. On operation of an extinguishing system, all electrical sources located under the ventilating equipment, if subject to exposure to discharge from the fire-extinguishing system, must be shut off. If the exhaust system is in a building with a fire alarm system, actuation of the fire- extinguishing system should send a signal to the fire alarm system. With solid-fuel cooking, there is no practical means of stopping combustion of the burning fuel, and consequently, detection, activa- tion, and performance of fire suppression systems are especially important. Dry and Wet Chemical Systems. Wet chemical and combina- tions of wet chemical and water fire-extinguishing systems have comprised the majority of fire suppression systems since the publi- cation of UL Standard 300 in 1994 and its subsequent citation by codes and standards. Dry chemical systems were popular through the early 1990s, but their use declined because they do not meet the requirements of UL Standard 300 and must be replaced with UL Standard 300 listed systems. Wet chemical systems are covered in NFPA Standard 17A, and though obsolete since UL Standard 300 was published, dry chemical systems are covered in NFPA Standard 17. Both standards provide detailed application information. Fire suppression systems are tested for their ability to extinguish fires in cooking operations in accordance with UL Standard 300. Wet chemical systems extinguish fires by reacting with fats and grease to saponify, or form a soapy foam layer, which prevents oxy- gen from reaching the burning surface. This suppresses the fire and prevents reignition. Saponification is particularly important with deep fat fryers, where the frying medium may be hotter than its autoignition temperature for some time after the fire is extinguished. If the foam layer disappears or is disturbed before the frying medium has cooled below its autoignition temperature, the fat can reignite. Frying media commonly used today, which contain a high per- centage of vegetable oils, have autoignition points of about 360 to 375°C when new. Contamination and deterioration through normal use lowers the autoignition point. In addition to the formation of a foam blanket instead ofa thin layer of powder, another advantage of wet chemical systems over dry chemical systems is that the former cools the frying media, bringing it below the autoignition point more quickly. With solid-fuel cooking, the flash point ofliquid cre- osote ranges from 74 to 92°C and the autoignition temperature for solid creosote ranges from 233 to 360°C. These temperatures sug- gest that creosote in ducts from solid-fuel cooking can be a greater fire hazard than grease alone. For a wet chemical system protecting the entire exhaust system, fire-extinguishing nozzles are located over the cooking equipment being protected, in the hood to protect grease-removal devices and the hood plenum, and at the duct collar (downstream from any fire dampers and pointing in the direction of effluent flow) to protect the grease duct. Two types of nozzle arrangements are common for protecting appliances. Appliance specific coverage is provided by nozzles that are usually directed at the centers ofindividual appliances. Overlap- ping coverage is provided by a generally greater number of evenly spaced nozzles. Although overlapping coverage is slightly more expensive to install and maintain, this arrangement solves the com- mon problem of appliances being periodically rearranged under hoods to meet operational needs. The duct nozzle is rated to protect an unlimited length of duct, so additional nozzles are not required further downstream in the duct. Additional nozzles and piping in ducts would also make periodic duct cleaning more difficult. Listed fire-extinguishing systems are available as pre-engineered (packaged) systems, installed by authorized exhaust hood manufac- turers or local authorized fire suppression system distributors/ dealers. In either case, required periodic maintenance of fire sup- pression systems is performed by local authorized fire suppression system distributors/dealers. Chemical systems typically consist of one or more tanks of chem- ical agent, a propellant gas cartridge, piping to the suppression noz- zles, fire detectors, and auxiliary equipment. Auxiliary equipment may include manual actuation ("pull") stations, gas shutoff valves (spring-loaded or solenoid-actuated), and auxiliary electric contacts. Fire detection is required at the entrance to each duct (or ducts, in hoods with multiple duct takeoffs). The fire detectors are typi- cally fusible links that melt at a set temperature associated with a fire, although electronic detection with battery back-up is also available. Actuation of chemical suppression systems is typically mechan- ical, requiring no electric power, by means of a spring-loaded device that pierces the seal on a propellant canister. Fire detectors are typ- ically interconnected with the system actuator by steel cables in ten- sion, so that melting of any fusible links, in series configuration, releases the tension on the steel cables, causing the spring-loaded Inc. ASHRAE, 2019 user. single for Licensed | {}
f17474d7-8116-437c-a03d-2e783a5752c4 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 34.36 2019 ASHRAE Handbook-HVAC Applications (SI) actuator to release the propellant and force suppressant through pipes and nozzles. The total length of the steel cable and number of pulley elbows allowed in the detection system are limited. A manual pull station is typically connected to the system actuator by steel cable. If a mechanical gas shutoff valve is used, it is also typically connected to the system actuator by steel cable. System actuation also switches auxiliary dry electrical contacts, which can be used to shut off elec- trical cooking equipment, operate an electric gas valve, shut off a replacement air fan, keep the related exhaust fan running, and/or send an alarm signal to the building fire alarm system. With electri- cally actuated fire suppression systems, detection is by electronic temperature sensors, and manual pulls are electric, in place of fus- ible links, cables, pipes, and pulleys. Manual pull stations are generally required to be at least 3 m from the cooking appliance and in a path of egress. Some code authorities may prefer that the pull station be installed closer to the cooking equipment for faster response; however, ifit is too close, it may not be possible to approach it once a fire has started. Refer to the applicable code requirements for each jurisdiction to determine specific requirements for location and mounting heights of pull sta- tions. w ater Systems. W ater can be used for protecting cooking equip- ment, hoods, and exhaust systems. Standard fire sprinklers may be used throughout the system, except over deep-fat fryers, where spe- cial automatic spray nozzles specifically listed for the application must be used. These nozzles must be aimed properly and supplied with the correct water pressure. Many hood manufacturers market a pre-engineered water spray system that typically includes a cabinet containing the necessary plumbing and electrical components to monitor the system and initiate fuel shutoff and building alarms. Application of standard fire sprinklers for protection of cooking equipment, hoods, and exhaust systems is covered by NFPA Stan- dard 13. NFPA Standards 25 and 96 cover maintenance of sprinkler systems serving an exhaust system. The sprinklers must connect to a wet-pipe building sprinkler system installed in compliance with NFPA Standard 13. One advantage of a sprinkler system is that it has virtually unlimited capacity, whereas chemical systems have limited chem- ical supplies. Where sprinklers are used in ducts, the duct should be pitched to drain safely. NFPA Standard 13 requires that sprinklers used to protect ducts be installed every 3 m on center in horizontal ducts, at the top of every vertical riser, and in the middle of any ver- tical offset. Any sprinklers exposed to freezing temperatures must be protected. Combination Systems. Hoods that use water either for periodic cleaning (water-wash) or for grease removal (cold-water mist) can use this feature in conjunction with the fire-extinguishing system to protect the hood, grease-removal devices, and/or ducts in the event of a fire, if listed to UL Standard 300. The water supply for these systems may be from the kitchen water supply if flow and pressure requirements are met. Examples include (1) an approved water- wash or water-mist system to protect the hood in combination with a listed wet chemical system to protect ducts and the cooking appliances (2) a listed chemical fire suppression system in the hood backed up by water sprinklers in the duct, or (3) a listed wet chemical system for appliances, with simultaneous use of a hood water-wash system, with foam-forming chemical injected into the water, for hood plenum and duct. Hybrid Systems. Several types of hybrid systems have been developed to improve upon conventional fire suppression system designs. One type connects to the domestic water system and then discharges this water on the protected areas following initial activa- tion and wet chemical agent discharge, but it retains fusible links for detection. A second type provides electronic detection in place of fusible links, cables, cable conduit, pulley elbows, and tees, though it retains conventional wet chemical fire suppressant. Another UL Standard 300 equivalent system (based on UL Outline ofInvestiga- tion 199E) relies on the water supplied by the building's NFPA Stan- dard 13 compliant sprinkler system. Suppression is handled by the activation of sprinklers and hybrid water/aqueous film-forming foam (AFFF) sprinklers directly over the fire location. Electronic Systems. These systems include electronic detection, activation, monitoring, annunciation of issues with readiness for suppression, and battery back-up. Connection to building manage- ment systems or other networks is optionally available. Surfactant is added to the supplied water suppressant to improve water coating of surfaces. Newer systems can also combine cold water and surfactant fire suppression with daily hood and lower duct cleaning by hot water and surfactant. With electronic detection, detectors can be mounted high in ducts, using listed duct penetrations, to better detect fires that autoignite in ducts, such as from solid-fuel cooking and related creosote deposits. Multiple-Hood Systems. All hoods connected to a multiple- hood exhaust system must usually meet several requirements. In the IMC (ICC 2018a), for example, the hoods must be on the same floor of the building, all interconnected hoods must be in the same room or in adjoining rooms, interconnecting ducts must not penetrate assemblies required to be fire-resistance rated, and the grease duct system must not serve solid-fuel-fired appliances. The multiple-hood exhaust system must be designed to (1) pre- vent a fire in one hood or in the duct from spreading through the ducts to another hood and (2) protect against a fire starting in the common duct system. Of course, the first line of protection for the ducts is keeping them clean. Especially in a multiple-tenant sys- tem, a single entity must assume responsibility for cleaning the common duct frequently. Each hood must have its own fire-extinguishing system to protect the hood and cooking surface. A single system might serve more than one hood, but in the event of fire under one hood, the system would discharge its suppressant under all hoods served, resulting in unnecessary cleanup expense and inconvenience. A water-mist sys- tem could serve multiple hoods if sprinkler heads were allowed to operate independently. Because of the possibility of a fire spreading through ducts from one hood to another, the common duct must have its own fire extin- guishing system. The appendices of NFPA Standards 17 and 17A present detailed examples of how common ducts can be protected, either by one system or by a combination of separate systems serving individual hoods. Different types of fire-extinguishing systems may be used to protect different portions of the exhaust system; however, in any case where two different types of system can discharge into the common duct at the same time, the agents must be compatible. As mentioned earlier, actuation of the fire-extinguishing system protecting any hood must shut off fuel or power to all cooking equipment under that hood, but fuel shutoff is not possible with solid-fuel cooking. When a common duct, or portion thereof, is pro- tected by a chemical fire-extinguishing system that activates from a fire in a single hood, NFPA Standards 1 7 and 17A require shutoff of fuel or power to the cooking equipment under every hood served by that common duct, or every portion of it protected by the activated system, even if there is no fire in the other hoods served by that duct. From an operational standpoint, itis usually most sensible to pro- vide one or more fire-extinguishing systems to detect and protect against fire in common ducts and a separate system to protect each hood and its connecting ducts. This prevents a fire in the common duct from causing discharge of fire suppressant under an unaffected hood and it allows unaffected hoods to continue operation in the event ofa fire under one hood unless the fire spreads to the common duct. Inc. ASHRAE, 2019 user. single for Licensed | {}
b4ee9065-1266-4cb3-98c3-63f3ce21bdbb | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Kitchen Ventilation 34.37 Preventing Fire Spread The exhaust system must be designed and installed both to pre- vent a fire started in the exhaust system from damaging the building or spreading to other building areas, and to prevent a fire in one building area from spreading to other parts of the building through the exhaust system. This protection has three main aspects: (1) maintaining clearance from the duct to other portions of the build- ing, (2) either enclosing the duct in a fire-resistance-rated enclosure, or wrapping the duct with a listed fire-rated product, and (3) design- ing, constructing, and testing to ensure integrity of the duct before and during a fire. These methods are sometimes addressed by a listed insulated grease duct system that incorporates an integral fire resistance. Clearance to Combustibles. A grease fire can generate gas temperatures of 1 100°C or greater in the exhaust hood and duct. In such a grease fire, heat radiating from the hot surface can ignite combustible materials near the hood or duct. Additionally, if the hood or duct is not fully welded and liquidtight as required by codes and standards, grease liquid or vapor leaking from the hood or duct can ignite and spread fire to nearby combustible structure. Most codes require a minimum clearance of 460 mm from the hood and grease duct to any combustible material. However, even 460 mm may not be sufficient clearance to prevent ignition of combus- tibles in the case of a major grease fire, especially with large vol- umes of grease in larger ducts. Several methods to protect combustible materials from the radiant heat of a grease fire and allow reduced clearance to combus- tibles are described in NFPA Standard 96 and the IMC (ICC 2018a). Based on testing and listing of grease ducts provided with integral insulation or wrapped with insulation, NFPA Standard 96 and other codes now allow listed insulation to be applied to the duct or a listed factory-built grease duct with integral insulation. For hoods, the clearance can be reduced as prescribed. Listed grease ducts, typically with insulation between double walls or on the outside of single-wall ducts, may be installed with reduced clearance to combustibles in accordance with locally adopted codes and standards, ifinstalled per manufacturers , instruc- tions, which should include specific information regarding the list- ing. Listed grease ducts are tested and evaluated in accordance with UL Standard 1978. NFPA Standard 96 requires a minimum clearance of 75 mm to "limited combustible" materials (e.g., gypsum wallboard on metal studs). The IMC (ICC 2018a) allows reduced clearance of ducts to 75 mm in proximity to noncombustibles on noncombustible struc- ture, such as gypsum wallboard on metal studs. Clearance reduction is also available for hoods, but may differ by local code, so local codes and standards should be consulted accordingly. Note that clearance-to-combustible issues are often seen in inspections of restaurant sites after grease fires. Many instances of inappropriate clearance reduction have been seen in which gypsum wallboard was mistakenly applied to wood studs and joists. In many of these cases, surrounding structure was ignited by heat from a grease fire, in spite of the gypsum wallboard barrier. The issue here is autoignition of the combustible material behind the gypsum wall- board from the high heat of the grease fire, even in cases where the gypsum wallboard layer is intact after the fire. Note that in some codes and standards, gypsum board is considered to be a combustible or limited-combustible material. A simple means of complying with most building codes and standards' clearance requirements is the specification and installa- tion of metal beams, joists, studs, and trusses within 457 mm of appliances, hoods, and ducts. Enclosures. Normally, when a HVAC duct penetrates a fire-re- sistance-rated wall or floor, a fire damper is used to maintain the in- tegrity of the wall or floor. Because fire dampers cannot be installed in a grease duct unless specifically approved for such use, there must be an alternative means of maintaining the integrity of rated walls or floors. Therefore, grease ducts that penetrate a fire-resis- tance-rated wall or floor/ceiling assembly must be continuously en- closed in a fire-rated enclosure from the point the duct penetrates the first fire barrier until the duct leaves the building. Listed grease ducts are also subject to these enclosure requirements. The require- ments are similar to those for a vertical shaft (typically 1 h rating if the shaft penetrates fewer than three floors, 2 h rating ifit penetrates three or more floors), except that the shaft can be both vertical and horizontal. In essence, the enclosure extends the room containing the hood through all the other compartments of the building without creating any unprotected openings to those compartments. Where a duct is enclosed in a rated enclosure, whether vertical or horizontal, clearance must be maintained between the duct and the shaft. NFPA Standard 96 and the IMC (ICC 2018a) require a mini- mum 150 mm clearance and that the shaft be vented to the outdoors. IMC requires that each exhaust duct have its own dedicated enclo- sure. Some listed grease ducts are designed and tested for use without shaft enclosure. Listed grease ducts of this type use fire barrier insu- lation and provide integral fire-rated resistance, which serves the same function as the shaft enclosure. These products are tested and listed in accordance with UL Standard 2221. They must be installed in accordance with the manufacturer's installation instructions. Some insulation materials are listed to serve as a fire-resistance- rated enclosure for a grease duct when used to cover a duct. These insulations are tested and listed in accordance with ASTM Standard E2336. These listed insulations must be applied in accordance with the manufacturer installation instruction. Insulation materials that have not been specifically tested and approved for use as fire protection for grease ducts should not be used in lieu of rated enclosures or to reduce clearance to combusti- bles. Even insulation approved for other fire protection applications, such as to protect structural steel, may not be appropriate for grease ducts because of the high temperatures that may be encountered in a grease fire. Duct Integrity. Ducts must retain integrity and stability during a grease fire so that the fire does not spread through unintended open- ings (poor welds or duct collapse). Factory-built stainless steel ducts are tested and listed to UL Standards 1978 and 2221 and are often dual listed to other high-temperature related all-fuel chimney stan- dards (UL Standards 103 and 2561). A listed duct system is recom- mended for exhaust systems that are four stories in height or greater. Specification oflisted ducts is recommended for all exhaust systems serving solid-fuel cooking. The model codes require testing for all duct joint/seam leakage, though for listed ducts, this testing is only required for duct joints assembled in the field. Exhaust and Supply Fire-Actuated Dampers. Because of the risk that the damper may become coated with grease and become a source of fuel in a fire, balancing and fire-actuated dampers are not allowed at any point in a exhaust system except where specifically listed for use or required as part of a listed device or system. Typically, fire dampers are found only at the hood collar and only if provided by the hood manufacturer as part of a listed hood. Opinions differ regarding whether any fire-actuated dampers should be provided in the exhaust hood. On one hand, a fire-actuated damper at the exhaust collar may prevent a fire under the hood from spreading to the exhaust duct. However, like anything in the exhaust airstream, the fire-actuated damper and fusible link may become coated with grease if not properly maintained, which may impede damper operation. On the other hand, without the fire-actuated damper, the exhaust fan draws smoke and fire away from the hood. Although this cannot be expected to remove all smoke from the kitchen during a fire, it can help to contain smoke in the kitchen and minimize migration of smoke to other areas of the building. Inc. ASHRAE, 2019 user. single for Licensed | {}
f51fea93-8687-4762-9305-f27faa1db700 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 34.38 2019 ASHRAE Handbook- -HVAC Applications (SI) A fire-actuated damper will generally close only in the event of a severe fire; most kitchen fires are extinguished before enough heat is released to trigger the fire-actuated damper. Thus, the hood fire- actuated damper remains open during relatively small fires, allow- ing the exhaust system to remove smoke, but can close in the event of a severe fire, helping to contain the fire in the kitchen area. Fan Operations. If replacement air flow rates exceed 940 L/s, the replacement air supply to the kitchen might be required by some codes and standards to be shut down during fire to avoid feeding air to the fire. However, if the exhaust system is intended to operate during a fire to remove smoke from the kitchen (as opposed to just containing it in the kitchen), the replacement air system must oper- ate as well. Ifthe hood has an integral (internal) replacement air ple- num such as with short-circuit hoods, a fire-actuated damper must be installed in the replacement air plenum to prevent a fire in the hood from entering the replacement air duct. NFPA Standard 96 details the instances where fire-actuated dampers are required in a hood replacement air plenum. Regardless of whether fire-actuated dampers are installed in the exhaust system, NFPA Standard 96 calls for the exhaust fan to con- tinue to run in the event of a fire unless fan shutdown is required by a listed component of the exhaust system or of the fire-extinguishing system. Listed fire-extinguishing systems protecting ducts are tested both with and without airflow, and exhaust airflow is not nec- essary for proper operation. Control Systems. The IMC (ICC 2018a) requires that Type I (grease and smoke) hoods be designed and installed to automati- cally activate related exhaust fans whenever cooking operations occur. 1.13 SYSTEM COMMISSIONING AND AIR BALANCING ANSI/ASHRAE/IES Standard 202 defines commissioning as "a quality-focused process for enhancing delivery of a project. The process focuses upon verifying and documenting that all of the com- missioned systems and assemblies are planned, designed, installed, tested, operated, and maintained to meet the owner's project requirements. " For commercial kitchen ventilation (CKV), commissioning may involve validation of system components that are designed, sup- plied, and/or installed by multiple design professionals, vendors and building trades. This chapter': s sections on Commissioning and Ven- tilation Design include steps that may be used to develop the owner's project requirements (OPR), including system design and installation. It is not unusual for CKV systems to be treated as independent building systems, even though these systems can affect the safety and IEQ (including comfort and odor control) of the entire facility. Some locations may limit the effects the CKV system is allowed to have on the outdoor environment surrounding the facility. Given the CKV system , s potential impacts, it is critical the OPR identifies responsibilities for system performance and its impacts on the facility and its environments. Refer to the System Integration and Design section of this chapter for more information. Air Balancing Kuehn (2010) demonstrated that a high degree of correction is required to achieve accurate airflow measurements with many ofthe instruments commonly used in the field to balance hood systems. Because of the level of correction required, hot-wire anemometers are not recommended. Therefore, balancing is best performed when the manufacturers of all system components provide a certified ref- erence method of measuring the airflow of their equipment, rather than depending on generic measurements of duct flows or other forms of measurement in the field, which, again, can be erroneous. The equipment manufacturer should be able to develop a reference method of measuring airflow in a portion of the equipment that is dynamically stable in the laboratory as well as in the field. This method should relate directly to airflow by graph or formula. Basic tools for balancing include the following: · Volumetric flow hood · Rotating vane anemometer · Velocity grid · Pitot tube/anemometers · Manometer/pressure meter · Voltage/amperage meter(s) · Tachometer Using instruments with current calibration certification or new instruments is recommended. The general steps for air balancing in restaurants are as follows: 1. Verify all exhaust and HVAC equipment is installed correctly and operating correctly, including (but not limited to) verifying that exhaust ducts are fully welded and inspection doors are in place, HV AC and supply ducts are complete and sealed, fans are rotating the correct direction, all exhaust hood grease filters are installed and properly sized, and thermostats are set up correctly and set to on or occupied mode. 2. Tabulated results of measurements should be kept and used to create a balance chart to show the building's net exfiltration or infiltration. 3. Exhaust hoods should be set to their proper flow rates, with supply and exhaust fans on. 4. Next, supply airflow rate, whether part of combined HVAC units or separate replacement air units, should be set to design values through the coils and the design supply flows from each outlet, with approximately correct settings on the outdoor airflow rate. Then, correct outdoor and return airflow rates should be set pro- portionately for each unit, as applicable. These settings should be made with exhaust on, to ensure adequate relief for the outdoor air. Where outdoor air and return air flows of a particular unit are expected to modulate, there should ideally be similar static losses through both airflow paths to preclude large changes in total supply air from the unit. Such changes, if large enough, could affect the efficiency of heat exchange and could also change airflows within and between zones, thereby upsetting air distribution and balance. See Chapter 39 for general HVAC testing, adjusting, and balancing information. 5. Next, outdoor air should be set with all fans (exhaust and supply) operating. Pressure difference between indoors and outdoors should be checked to confirm that (1) nonkitchen zones of the building are at a positive pressure compared to outdoors and (2) kitchen-zone pressure is negative compared to the surround- ing zones, and positive or neutral compared to outdoors. 6. For applications with DCKV systems, proper capture and con- tainment, as well as differential pressures between zones and atmosphere, should be confirmed at minimum and at maximum flow rates. This requires that the replacement airflow rate com- pensate automatically with each increment of exhaust. It may require some adjustments in controls or in damper linkage set- tings to get the correct proportional response. System Tests Cooking Exhaust Duct Leakage. ASHRAE Standard 154 out- lines methods of test for exhaust system duct leakage. In most installations, the hood, exhaust fans, and replacement air equipment will be listed and labeled for its intended use. Exhaust duct systems may be field fabricated or listed factory-built systems. Either system requires joining sections in the field and may include field-installed cleanouts and inspections ports. It is critical to the fire safety of the Inc. ASHRAE, 2019 user. single for Licensed | {}
20558bd7-c135-44c5-931f-78382295f51c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Kitchen Ventilation 34.39 facility and the performance of the CKV system that these duct sys- tems be tested to assure they are properly installed. See Chapter 19 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment for information on HV AC duct construction and leakage criteria. Fire Suppression. Like the duct system, the hood fire suppres- sion system requires some field work to complete the system instal- lation. Typically, the local AHJ requires an operating test of the installed suppression system. Test requirements vary. If the local AHJ does not require such a performance test of the completed sys- tem, the OPR should specify that such a test be conducted. DCKV. When a DCKV system is installed to control the CKV systems, a system test should be conducted. This test should include the full range of the DCKV modulation, including the effects on exhaust and replacement air system performance throughout that full range. Examples include, at DCKV modulation extremes, (1) heating/cooling performance, (2) effective airflow distribution, and (3) maintaining proper pressure balance between the kitchen, adja- cent spaces, and atmosphere. Building Automation System. The CKV system for controlling the temperature and proper pressurization of food preparation spaces and zones must be tested to ensure it operates properly as designed. If other spaces and zones outside of the food preparation zone provide replacement air for the CKV system, then they must also be tested to ensure their proper operation. Performance Test After initial airflows are verified to be at design values and the building is balanced, a performance evaluation of all exhaust hoods should be performed to verify capture and containment (C&C) at the design conditions. ASHRAE Standard 154 outlines performance test methods. Conduct Type I and II hood field testing with all appliances under the hood at operating temperatures, with all the hoods operating at design airflows, with all sources providing replacement air for the hood operating at design airflows, and with all sources of recircu- lated air in the space operating at design airflows. C&C is verified visually by observing smoke or steam produced by actual cooking or dishwashing operation. Simulating devices such as smoke candles or smoke puffers are good for detecting air currents moving inward at the lower edge of the hood, but generally do not produce enough smoke to simulate full-load cooking operation. Note that smoke bombs typically create new effluent from a point source, and though they may create a volume of effluent that is equivalent to that of cooking effluent, their use to determine whether actual cooking effluent would be captured by the hood is not always reliable. Actual cooking at the full load or at the highest production rate is the most reliable method of gener- ating smoke. Note that many health department rules for new facil- ities typically do not allow food to be brought into the facility until all safety and health inspections are complete and approved. Actual cooking may require special arrangements with the AHJ and should be considered in lieu of simulation methods, or as a final method to verify capture as part of the commissioning process for a hood's ventilation system. Hood systems with DCKV should be tested in auto mode to verify that the system responds appropriately to the changes in cooking operation. Begin with the cooking appliances off and con- firm that the system is at minimum airflow. Then, turn cooking appliance on and verify that the airflow increases with increasing temperature. Once the appliances reach cooking temperature, gen- erate smoke through actual cooking and verify C&C or simulation, as described previously. The evaluation should be performed at light, medium, and heavy-load conditions to verify C&C. If hoods fail the performance test, examine the systems and cor- rect any capture problems. Close attention should be given to the design considerations and guidelines in this chapter to correct any performance problems. Follow-Up: Records 1. A punch list of any remaining issues encountered during instal- lation, air balancing, or performance testing should be recorded and submitted to the facility management and any affected con- tractors so that these items can be corrected. 2. When the preceding steps are complete, the system is properly integrated and balanced. At this time, all fan speeds and damper settings (at all modes of operation) should be permanently marked on the equipment and in the test and balance report. Air balance records of exhaust systems, replacement air systems, HVAC supply and return serving the hood area, and individual diffuser and/or grille airflows must also be completed. Ifthe unit includes a fan, records must include fan or unit model(s) and size(s), fan wheel and motor rpm, and fan motor amp draw. These records should be kept by the food service facility for future reference. 3. For new facilities, after two or three days in operation, all belts in the system should be checked and readjusted to correct new belt run-in wear. This examination should take place no later than a week after initial operation, and before the facility opens if possible. Obviously, direct-drive systems do not require this inspection or replacement. 4. Once the facility is operational, check performance of the venti- lation system to verify that the design is adequate for actual cooking operation, particularly at maximum cooking and at out- door environmental extremes. Any necessary changes should be made, and all the records should be updated to show the changes. 5. Rechecking the air balance should not be necessary more than once every two years. If there are any changes, such as adding a new type of cooking equipment or deleting exhaust connections, the system should be modified, rebalanced, and retested accord- ingly. Recommend a rebalance/retest whenever components of the kitchen ventilation and HVAC systems are replaced/modified (e.g., when an exhaust or supply fan is replaced or when supply/ return air outlets are added or relocated within the kitchen). The system should also be rebalanced/retested whenever a cooking appliance is relocated or replaced with an appliance of different function. For example, if a fryer was replaced with a broiler, the ventilation would have to be rebalanced and retested for the broiler. Modifications should be recorded, added to owner's re- cords, and marked on affected equipment. 6. All final operational measurements and recording shall be re- tained as a reference for future energy audit field surveys. 1.14 OPERA TIONS AND MAINTENANCE Sustainability Impact Proper operation and maintenance of all kitchen ventilation sys- tems is an often overlooked requirement, but is one of the most crit- ical, especially given the large amount of resources used in CKV operation. Typically, most attention is focused on the production of food, which is the primary role of any commercial kitchen. Given the kitchen ventilation system 's role in providing replacement air, heating and cooling, and cooking effluent extraction, ensuring it is properly operated and maintained is critical for minimizing both overall system energy use and any environmental impacts both inside and outside the restaurant caused by effluent produced during cooking. Systems that are not operated or maintained correctly are likely to consume excessive energy, may create uncomfortable con- ditions in the kitchen area, may create an environmentally hazard- ous condition in the kitchen (e.g., hoods that do not capture and contain cooking effluent), and may affect outdoor environmental conditions (e.g., when pollution control devices are not operating Inc. ASHRAE, 2019 user. single for Licensed | {}
033c0f70-dc67-49a6-bd34-03279ee943b3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 34.40 2019 ASHRAE Handbook-HVAC Applications (SI) properly). Additionally, given the fire hazards associated with com- mercial cooking, improper operation and maintenance of a kitchen's ventilation system(s) can even create a life safety hazard. Maintain- ing a proper air balance is part ofa kitchen ventilation system 's nec- essary maintenance. See Chapter 40 for more information on the costs associated with building operations and maintenance. Finally, as part of any total commissioning process, the impact of operations and maintenance must be taken into account, especially ensuring that any related tasks can be performed with minimal dis- ruption to food service production. Ifthe system 's proper operations and associated maintenance are not easily performed, they will most likely be deferred or not performed at all. Operation All components of the kitchen's ventilation system, and in some instances the entire building's ventilation system, are designed to operate in balance with each other, even under variable loads, to properly capture, contain, and remove cooking effluent and heat and maintain proper space temperature control in the most efficient and economical manner. Deterioration in any of these components un- balances the system, affecting one or more of its design concepts The ventilation system , s design intent should be fully understood by the owners and operators, so that any deviations in operation can be noted and corrected. This is especially critical when a DCKV sys- tem is used. In addition to creating health and fire hazards, normal cooking effluent deposits can also unbalance the system, so they must be regularly removed. All components of exhaust and replacement air systems affect proper capture, containment, and removal of cooking effluent. In the exhaust system, this includes the cooking equipment itself, exhaust hood, all filtration devices, ducts, exhaust fan, and any dampers. In the replacement air system, this includes the air-handling unit(s) with intake louvers, dampers, filters, fan wheels, heating and cool- ing coils, ducts, and supply registers. In systems that obtain their replacement air from the general HVAC system, this also includes return air registers and ducts. Inc. ASHRAE, 2019 user. single for Licensed When the system is first set up and balanced in new condition, these components are set to optimum efficiency. In time, all compo- nents become dirty; filtration devices, dampers, louvers, heating and cooling coils, and ducts become restricted; fan blades change shape as they accumulate dirt and grease; and fan belts loosen. In addition, dampers can come loose and change position, even closing, and ducts can develop leaks or be blocked if internal insulation sheets fall down. All these changes deteriorate system performance. The operator should know how the system performed when it was new, to better recognize when it is no longer performing the same way. This knowledge allows problems to be found and corrected sooner and the peak efficiency and safety of system operation to better be main- tained. Maintenance Maintenance may be classified as preventive or emergency (breakdown). Preventive maintenance keeps the system operating as close as possible to optimal performance, including maximum production and least shutdown. Itis the most effective maintenance and is preferred. Preventive maintenance can prevent most emergency shutdowns and emergency maintenance. It has a modest ongoing cost and fewer unexpected costs. Clearly the lowest-cost maintenance in the long run, it keeps the system components in peak condition, maximizes the system s energy efficiency, and extends the operating life of all components. Emergency maintenance must be applied when a breakdown occurs. Sufficient staffing and money must be applied to the situa- tion to bring the system back on line in the shortest possible time. Such emergencies can be of almost any nature. They are impossible to predict or address in advance, except to presume the type of com- ponent failures that could shut the system down and keep spares of these components on hand or readily accessible, so they can be quickly replaced. Preventive maintenance, which includes regular inspection of critical system components, is the most effective way to avoid emergency maintenance. Following are brief descriptions of typical operations of various components of kitchen ventilation systems and the type of mainte- nance and cleaning required to bring the abnormally operating system back to normal. Many nontypical operations are not listed here. Any maintenance should include a check of the building auto- mation system (BAS) as it relates to the kitchen ventilation system to ensure it is operating per its original design. Cooking Equipment Normal Operation. Produces properly cooked product, of cor- rect temperature, within expected time. Minimum smoke during cooking. Abnormal Operation. Produces undercooked product, of lower temperature, with longer cooking times. Increased smoke during cooking. Cleaning/Maintenance. Clean solid cooking surfaces between each cycle ifpossible, or at least once a day. Baked-on product insu- lates and retards heat transfer. Filter frying medium daily and change it on schedule recommended by supplier. Check that (1) fuel source is at correct rating, (2) thermostats are correctly calibrated, and (3) conditioned air is not blowing on cooking surface. Solid-fuel appliances are listed as "Extra-Heavy Duty" (see Table 4) and require additional attention. A hood over a solid-fuel appli- ance must be individually vented and therefore not be combined at any point with another duct and fan system. Using a UL Standard 762 upblast, in-line, or utility set fan listed to 205 to 260°C is sug- gested because the airstream temperature may be hotter without cooler air combining from other, typically lower-temperature cooking appliances. Design, installation, and maintenance precau- tions for the use of and emissions from solid fuel include monthly duct cleaning with weekly inspections, spark arrestors, and addi- tional spacing to fryers. Refer to NFPA Standard 96, Chapters 5 to 10 and 14, and IMC, sections 507 and 906, for additional direction. Exhaust Systems (e.g., Hoods) Normal Operation. All cooking vapors are readily drawn into the exhaust hood, where they are captured and removed from the space. The environment immediately around the cooking operation is clear and fresh. Abnormal Operation. Many cooking vapors do not enter the ex- haust hood at all, and some that enter subsequently escape. The en- vironment around the cooking operation, and likely in the entire kitchen, is contaminated with cooking vapors and a thin film of grease. Cleaning/Maintenance. Clean all grease removal devices in the exhaust system. Hood filters should be cleaned at least daily. High- efficiency grease extractors may require frequent cleanings during each shift. For other devices, follow the minimum recommenda- tions of the manufacturer; even these may not be adequate at very high flow rates or with products producing large amounts of efflu- ent. Check that (1) all dampers are in their original position, (2) fan belts are properly tensioned, (3) the exhaust fan is operating at the proper speed and turning in the proper direction, (4) the exhaust duct is not restricted, and (5) the fan blades are clear. NFPA Standard 96 design requirements for access to the system should be followed to facilitate cleaning the exhaust hood, ductwork, and fan. Cleaning should be done if the combustibles' depth is greater than 2 mm in any part of the system, and by a method that leaves no more than a 0.05 mm depth deposit of com- bustibles. Cleaning agents should be thoroughly rinsed off, and all | {}
e4ebe0c4-ada8-443b-94f1-f2a3f4335d2a | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Kitchen Ventilation 34.41 loose grease particles should be removed, because they can ignite more readily. Agents should not be added to the surface after cleaning, because their textured surfaces merely collect more grease more quickly. Fire-extinguishing systems may only be disarmed by properly trained and qualified service personnel before cleaning, to prevent accidental discharge, and then reset by authorized personnel after cleaning. All access panels removed must be reinstalled after cleaning, with proper gasketing in place to prevent grease leaks and escape of fire. Supply, Replacement, and Return Air Systems Normal Operation. The environment in the kitchen area is clear, fresh, comfortable, and free of drafts and excessive air noise. Abnormal Operation. The kitchen is smoky, choking, hot, and humid, and perhaps very drafty with excessive air noise. Cleaning/Maintenance. Check that the replacement air system is operating and is providing the correct amount of air to the space. If it is not, the exhaust system cannot operate properly. Check that dampers are set correctly, filters and exchangers are clean, the belts are tight, the fan is turning in the correct direction, and supply and return ductwork and registers are open, with supply air discharging in the correct direction and pattern. If drafts persist, the system may need to be rebalanced. If noise persists in a balanced system, system changes may be required. Filter cleaning or changing frequency varies widely depending on the quantity of airflow and contamination of local air. Once determined, the cleaning schedule must be maintained. With replacement air systems, the air-handling unit, coils, and fan are usually cleaned in spring and fall, at the beginning ofthe seasonal change. More frequent cleaning or better-quality filtering may be re- quired in some contaminated environments. Duct cleaning for the system is on a much longer cycle, but check local codes because stricter requirements are sometimes invoked. Ventilation systems should be cleaned by professionals to ensure that none of the expen- sive system components are damaged. Cleaning companies should be required to carry adequate liability insurance. The Power Washers of North America (PWNA) and the International Kitchen Exhaust Cleaning Association (IKECA) provide descriptions of proper cleaning and inspection techniques and lists of their members. Recommended Frequency of Maintenance Proper preventative maintenance and periodic recommissioning and rebalancing is necessary for achieving the designed perfor- mance and life cycle of the CKV systems. The following recom- mendations are based on field experience: · Recommission and rebalance CKV systems, at minimum, every five years. · Recommission and rebalance CKV systems any time changes are made to the CKV equipment, related HVAC equipment, or to the cooking operations. For example, replacing exhaust or makeup fans, relocating supply or return air grilles, relocating cooking equipment, or replacing cooking equipment with equipment of a different function (e.g., a fryerreplaced with a broiler). These new or altered systems need to be tested, balanced, and commissioned for the new usage. · Recommission and rebalance CKV systems any time performance issues arise, such as smoke or heat loss from the kitchen hoods, abnormal space temperatures, high-velocity air currents at pass- through windows, condensation, negative building pressure, etc. · Performance verification check of all control systems related to the CKV system every two years. · Capture and containment verification check of kitchen exhaust hoods every year. · Verify proper outside air quantities every two years. Preventative maintenance is key to maintaining designed perfor- mance and life cycle cost of a CKV system. As grease builds up inside the kitchen exhaust ductwork, so does the static pressure and the corresponding potential for a fire. Depending on the available static that the exhaust fan was selected, pressure loss increase could become more than the fan can handle, which would reduce the required airflow rate, creating poor smoke and heat capture as well as overloading the fan. 2. RESIDENTIAL KITCHEN VENTILATION Although commercial and residential cooking processes can be similar, their ventilation requirements and procedures are different. Differences include exhaust airflow rate and hood installation height. In addition, residential kitchen ventilation is less concerned with re- placement air, and energy consumption is comparatively insignificant because of lower airflow, smaller motors, and intermittent operation. Equipment and Processes Although the physics of cooking and the resulting effluent are about the same, residential cooking is usually done more conserva- tively. Heavy-duty and extra-heavy-duty equipment, such as upright broilers and solid-fuel-burning equipment (described in Table 3), are not used. Therefore, the high ventilation rates of commercial kitchen ventilation and equipment for delivering these rates are not often found in residential kitchens. However, some residential kitchens are designed to operate with commercial-type cooking equipment, with higher energy inputs rates than usually found. In these cases, the required hood may be similar to a commercial hood, and the required ventilation rate may approach that required for small commercial facilities. Cooking effluent and by-products of open-flame combustion must be more closely controlled in a residence than in a commercial kitchen, because any escaping effluent can be dispersed throughout a residence, whereas a commercial kitchen is designed to be nega- tively pressurized relative to surrounding spaces. By-products of cooking and natural gas burning processes, such as PM2.5, CO2, CO, and HCHO (formaldehyde), can negatively impact indoor air quality and respiratory health and should be considered during sys- tem design. A residence also has a much lower outdoor air ventila- tion rate, making the presence of any escaped contaminant more persistent. This situation makes residential kitchen ventilation a dif- ferent kind of challenge, because problems cannot be resolved by simply increasing the ventilation rate at the cooking process. Active research is being conducted to better understand the health risks that can be caused by the effluent produced from residential cooking, and the best means for mitigating those risks. Residential cooking always produces a convective plume that car- ries with it cooking effluent, often including grease vapor and parti- cles, as well as water vapor, and by-products of combustion when natural gas is the energy source. Sometimes there is spatter as well, but those particles are so large that they are not removed by ventila- tion. Residential kitchen hoods depend more on thermal buoyancy than mechanical exhaust to capture cooking effluent and by-products of combustion. 2.1 EXHAUST SYSTEMS Hoods and Other Ventilation Equipment Wall-mounted, conventional range hoods ventilate most residential kitchens. There are unlimited style-based variations of the conven- tional range hood shape. Deep canopy hoods are somewhat more ef- fective because of their capture volume. Other styles have less volume, or a more flat bottom, and may be somewhat less effective at capturing effluent. To the extent that residential range hoods are often Inc. ASHRAE, 2019 user. single for Licensed | {}
0b49ec97-950b-4be0-aef2-2d2e4b6dec6b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 34.42 2019 ASHRAE Handbook-HVAC Applications (SI) mounted between cabinets, with portions of the cabinets extending be- low the sides of the hood, performance may be improved because the cabinet sides help contain and channel the exhaust flow into the hood. An increasingly popular development in residential kitchen ven- tilation is using a ventilating microwave oven in place of the typical residential range hood. Microwave ovens used for this purpose typ- ically include small mesh filters mounted on the bottom of the oven and an internal exhaust fan. Means are usually provided to direct the exhaust flow in two directions: back into the kitchen or upward to an exhaust duct leading outdoors. The latter is more expensive, but highly preferred; otherwise, if directed back to the kitchen, walls, ceiling, and cabinet surfaces are likely to become coated with grease from condensed grease vapor, and grease residue can damage paint and varnish. Additionally, typical microwave oven ventilators do not include vertical surfaces that provide a reservoir volume to con- tain the convective plume during transient effects, such as removing the lid from a cooking vessel. Consequently, microwave oven ventilators often provide lower exhaust capture and containment performance than standard range hoods. Downdraft range-top ventilators have also become more pop- ular. Functionally, these are an exception, because they capture contaminants by producing velocities over the cooking surface greater than those of the convective plume. With enough velocity, their operation can be satisfactory; however, velocity may be lim- ited to prevent adverse effects such as gas flame disturbance and cooking process cooling. Additionally, this method is more effec- tive for exhaust from cooking near the range surface, and it is usu- ally much less effective for capturing the convective plume from taller cooking vessels, because the convective plume is too far above the ventilator intake to be affected by it. Ironically, many high-end kitchens have less efficient ventilation than standard range hoods. Inefficient methods include · Mounting range tops in cooking islands with no exhaust hood or other means of ventilation · Mounting ovens in cabinets, separate from rangetops, without any way to remove heat and effluents from the oven · Using low-profile exhaust devices with insufficient overhang over the appliance and no reservoir to contain convective plume during dynamic effects · Having duct runs, particularly in larger homes, with very high static pressure losses, so that the actual exhaust flow rate is much lower than the nominal exhaust fan rating Whole-kitchen exhaust fans were more common in the past, but they are still used. Mounted in the kitchen wall or ceiling, they ven- tilate the entire kitchen volume rather than capturing contaminants at the source. For kitchen exhaust fans not above the cooking sur- face, and without a capturing hood, 15 air changes per hour (ach) is recommended; for ceiling-mounted fans, this is usually sufficient, but for wall-mounted fans, it may be marginal. Residential exhaust hoods are often furnished with multiple- speed fans, so that users can match exhaust fan speeds (and noise) with the cooking process and resultant convective plume. Carrying this concept further, there are high-end residential exhaust hood man- ufacturers that provide an automatic two-speed control that increases fan speed when higher convective plume temperature is sensed. Continuous low-level, whole-building ventilation is increasingly used to ensure good indoor air quality in modern, tightly built houses with less infiltration. ASHRAE Standard 62.2 requires kitchen ven- tilation in most residences. Some whole-building ventilation sys- tems can intermittently increase airflow to achieve the needed reduction in cooking effluent. In that case, there must be provision to avoid introducing and accumulating grease and other cooking effluent that may cause undesirable growth of microorganisms. Differences Between Commercial and Residential Equipment Safety requirements covering residential cooking area fans are contained in UL Standard 507. These fans and accessories are intended for use in conjunction with residential gas and electric cooking appliances only, and are investigated to determine the effects of increased air temperature and grease on electrical compo- nents. The filters provided as a part of the fan are also checked for flammability and smoke propagation. Products include hood fans intended to mount directly over (but not directly on) ranges, sepa- rate hoods provided with lights or other wiring and intended for use over ranges in conjunction with a remote blower, downdraft fans, and oven ventilators for use over wall-insert ovens. Fans intended for mounting directly on cooking equipment are investigated in conjunction with the cooking appliances, and are typically listed as part of the accessory to the cooking appliance. Fans installed in close proximity to a stove, range, or oven where fumes, grease- laden air, or the like may be present and intended to discharge air away from the cooking area should be installed to discharge air to the exterior of the building and not into concealed walls or ceiling spaces or into the attic. Ductless fans intended for use in cooking areas are not required to discharge air to the building exterior. Fire-actuated dampers are never part of the hood and are almost never used. Grease filters in residential hoods are much simpler, and grease collection channels are rarely used because inadequate main- tenance could allow grease to pool, creating a fire and health hazard. Conventional residential wall hoods usually have standard dimen- sions that match the standard 75 mm modular grid of residential cab- inets. Heights of 150, 230, 300, and 610 mm are common, as are depths from 430 to 520 mm. Width is usually the same as the cooking surface, with 760 mm width nearly standard in the United States. Current U.S. Housing and Urban Development (HUD) Man- ufactured Home Construction and Safety Standards call for 75 mm overhang per side. Hood mounting height is usually 460, 610, or 760 mm, and some- times even higher with a sacrifice in collection efficiency. A lower- mounted hood captures more effectively because there is less oppor- tunity for lateral air currents to disrupt the convective plume. Studies show 460 mm is the minimum height for cooking surface access. Some codes require a minimum of 760 mm from the cooking surface to combustible cabinets. In that case, the bottom of a 150 mm hood can be 610 mm above the cooking surface. A minimum airflow rate (exhaust capacity) of 60 L/s per linear metre of hood width has long been recommended by the Home Ventilating Institute (HVI 2004), and confirmed by field tests. Ad- ditional capacity, with speed control, is desirable for handling un- usually vigorous cooking and cooking mistakes, because airflow can be briefly increased to clear the air, and speed can be reduced to a quieter level for normal cooking. Recommended minimum exhaust airflow rates vary among model codes. A minimum airflow rate (exhaust capacity) of 60 L/s per linear metre of hood width has long been recommended by the Home Ventilating Institute (HVI 2004), and confirmed by field tests. ASHRAE Standard 90.2 requires a minimum exhaust rate of 47 L/s intermittent. IMC (ICC 2018a) requires a minimum exhaust rate of 47 L/s intermittent or 12 L/s continuous. Additional capacity, with speed control, is desirable for handling unusually vigorous cooking and cooking mistakes, because airflow can be briefly increased to clear the air, and speed can be reduced to a quieter level for normal cooking. In some instances, commercial cooking equipment is used in res- idential applications. In these instances, special care should be taken for using adequate Type I or Type II exhaust hoods, ducting, and air flow requirements that are more in line with commercial or mechan- ical codes, because residential codes do not address this scenario. Inc. ASHRAE, 2019 user. single for Licensed | {}
de7badb2-1a58-4298-9831-0cdf36dd39b3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Kitchen Ventilation 34.43 Exhaust Duct Systems Residential hoods offer little opportunity for custom design of an exhaust system. The range hood has a built-in duct connector and the duct should be the same size, whether round or rectangular. A hood includes either an axial or a centrifugal fan. The centrifugal fan can develop higher pressure, but the axial fan is usually adequate for low-volume hoods. The great majority of residential hoods in the United States have HVI-certified airflow performance. In all cases, it is highly preferable to vent the exhaust hood outdoors through a roof cap, rather than venting back into the home, whether into the kitchen or elsewhere. Replacement (Makeup) Air The exhaust rate ofresidential hoods is generally low enough and natural infiltration sufficient to avoid the need for replacement air systems. Although this may cause slight negative pressurization of the residence, it is brief and is usually less than that caused by other equipment. Still, backdrafts through the flue of a combustion appli- ance should be avoided and residences with gas furnace and water heater should have the flue checked for adequate flow. NFPA Stan- dard 54 provides a method oftesting flues for adequate performance. Sealed-combustion furnaces and water heaters are of less concern. Sometimes commercial-style cooking equipment approved for residential use is installed in residences. IMC (ICC 2018a) requires that exhaust hood systems capable of exhausting 189 L/s or greater be provided with makeup air at a rate equal to the exhaust rate. Addi- tionally, the makeup air system is to be equipped with a means of closure and operated simultaneously with the exhaust system to ensure proper building pressurization. High-Rise Systems Multistory structures with a common exhaust system serving multiple kitchen areas have additional requirements, as detailed in the Domestic Kitchen Exhaust Equipment section of the IMC. Typ- ically, each resident's hood fan discharges into a common exhaust riser duct, at the top of which is a large fan rated for kitchen exhaust duty. A diversity factor is included in the sizing of this duct and fan, because not all of the kitchen hoods will operate simultaneously. Static pressure sensor(s) located in the duct riser controls the speed of this fan so that a small but continuous negative duct pressure is maintained regardless of the number of hoods being operated. Makeup air for this kitchen exhaust is typically provided by a cen- tral makeup air unit that serves the entire building's makeup air needs, including those for other exhausts (e.g., toilets, clothes dry- ers). Commissioning of these makeup and exhaust air systems is required to ensure each area has sufficient exhaust airflow to remove convective heat and effluent generated by the cooking process. Energy Conservation The energy cost of residential hoods is quite low because of the few annual running hours and the low rate of exhaust. For example, it typically costs less than $10 per heating season in Chicago to run a hood and heat replacement air, based on running at 70 L/s for an hour a day and using gas heat. Fire Protection for Residential Hoods Residential hoods must be installed with metal (preferably steel) duct, positioned to prevent grease pooling. Residential hood exhaust ducts are almost never cleaned, and there is no evidence that this causes fires. There have been some attempts to make fire extinguishers available in residential hoods, but none has met with broad accep- tance. However, grease fires on the residential cooking surface, almost always the result of unattended cooking, continue to occur. There is no industry-accepted standard of design in residential fire-extinguishing equipment. When extinguishing systems are Table 14 Summary of TC 5.10 Research Projects ¦ Year(s) ¦ ASHRAE Project ¦ Title ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 1993 to 1994 ¦ RP-623 ¦ A Field Test Method for Determining Exhaust Rates in Grease Hoods for Commercial Kitchens (Gordon and Parvin 1994) ¦ ¦ 1996 to 1997 ¦ RP-851 ¦ Determining the Efficiency of Grease- Removal Devices in Commercial Kitchen Applications (Schrock 1998) ¦ ¦ 1998 to 1999 ¦ RP-745 ¦ Identification and Characterization of Efflu- ents from Various Cooking Appliances and Processes as Related to Optimum Design of Kitchen Ventilation Systems (Gerstler et al. 1998) ¦ ¦ 2000 to 2001 ¦ RP-1033 ¦ Effects of Air Velocity on Grease Deposition in Exhaust Ductwork (Kuehn 2000) ¦ ¦ 2001 to 2003 ¦ RP-1151 ¦ Development of a Draft Method of Test for Determining Grease Removal Efficiencies (Welch 2004) ¦ ¦ 2003 to 2005 ¦ RP-1202 ¦ Effect of Appliance Diversity and Position on Commercial Kitchen Hood Performance (Swierczyna et al. 2006) ¦ ¦ 2007 to 2008 ¦ RP-1375 ¦ Characterization ofEffluents from Additional Cooking Appliances (Kuehn 2008) ¦ ¦ 2008 to 2009 ¦ RP-1362 ¦ Revised Heat Gain and Capture and Contain- ment Exhaust Rates from Typical Commer- cial Cooking Appliances (Swierczyna 2008) ¦ ¦ 2008 to 2010 ¦ RP-1376 ¦ Method ofTest to Evaluate Field Performance of Commercial Kitchen Ventilation Sys- tems (Kuehn 2010) ¦ ¦ 2008 to 2009 ¦ RP-1480 ¦ Island Hood Energy Consumption and Energy Reduction Strategies (Swierczyna et al. 2010) ¦ ¦ 2010 to 2013 ¦ RP-1469 ¦ Thermal Comfort in Commercial Kitchens (Stoops 2013) ¦ ¦ 2013 to 2015 ¦ RP-1631 ¦ Countertop Commercial Appliance Emis- sions (Zhang 2015) ¦ ¦ 2017 to present ¦ RP-1614 ¦ Developing a Test Method to Determine the Effectiveness of UVC Systems on Commer- cial Cooking Effluent ¦ installed over residential range tops, the system should comply with UL Standard 300A. Maintenance All listed hoods and kitchen exhaust fans are designed for clean- ing, which should be done at intervals consistent with the cooking practices of the user. Although cleaning is sometimes thought to be for fire prevention, the health benefits of removing nutrients avail- able for the growth of organisms can be more important. 3. RESEARCH Research Overview ASHRAE Technical Committee TC 5.10, Kitchen Ventilation, has been active in research related to kitchen ventilation, as shown in Table 14. This research has tended to focus on answering ques- tions related to field-related issues, such as how to measure exhaust airflow rates for hood and replacement air systems (RP-623 and RP-1376) and how much grease is produced by cooking appliances (RP-745 and RP-1375), and a current project is evaluating the grease and heat gain from unhooded countertop cooking appliances (RP-1631). Some of the research focused on design aspects of kitchen ventilation systems, from optimizing exhaust hood perfor- mance (RP-1202 and RP-1480), to evaluating the grease removal efficiency of filtering devices (RP-851 and RP-1151) and reducing Inc. ASHRAE, 2019 user. single for Licensed | {}
67aa00c4-5030-4ba8-ba25-19743582fe8c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 34.44 2019 ASHRAE Handbook-HVAC Applications (SI) the velocity of airflow in the exhaust ductwork (RP-1033). Other projects evaluated relationships between appliances and ventilation systems and the HVAC system in the space (RP-1362). A comprehensive study has been conducted using both field mea- surements and field surveys regarding thermal comfort in commercial kitchens (RP-1469), and a research project (RP-1614) has been initi- ated on developing a method of test to determine the effectiveness of UVC systems installed in commercial kitchen ventilation systems. Benefits to the HV AC Industry Many of the research projects that TC 5.10 sponsored have affected energy use and sustainability in the food service industry. RP-1033 data showed that grease deposition on the walls of duct actually decreased when the duct velocity was lowered from 7.6 m/ s to 2.5 m/s. These data allowed both NFPA Standard 96 and the International Mechanical Code (ICC 2009) to allow lower duct velocities. These changes allow demand-controlled ventilation systems (in which airflow is lowered during noncooking periods of the day) to be used across the United States to achieve significant energy savings. The two projects related to hood performance (RP-1202 and RP- 1480) not only evaluated how wall canopy and island hoods perform with various appliances, but also evaluated methods of reducing the exhaust airflows required for the hoods to capture the cooking efflu- ent more efficiently. These include items such as optimizing the appliance position underneath the hoods, installing side panels, and designing hoods to use larger overhangs if possible. If exhaust air is reduced, this also generally reduces how much conditioned air needs to be brought back into the space to replace the air that is exhausted, leading to large energy savings in restaurants. RP-1362 measured the heat gain from appliances underneath hoods, and these data can be used to more accurately size the HVAC equipment needed to condi- tion the kitchen space. Earlier projects related to grease emissions (RP-851, RP-745, and RP-1151) were used to help develop ASTM Standard F2519. Data from these research projects, along with Standard F2519 and data from RP-1375, revolutionized the kitchen ventilation industry with regard to how mechanical filters actually perform in the field and the ASTM Standard provides a framework for making more efficient filters that help reduce the amount of grease built up in ductwork, on exhaust fans, and on the roof of buildings. Another project (RP-1631) evaluated the appliance emissions and heat gain to space from countertop commercial cooking appli- ances to help determine whether these processes require a ventila- tion hood or can be vented to the space RP-623 and RP-1376 both examined how to accurately measure the exhaust and replacement air in food service establishments. By being able to more accurately measure the airflows, restaurants can be properly balanced to the design conditions so that excess energy is not consumed. REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. ASHRAE. 2017. Thermal environmental conditions for human occupancy. ANSI/ASHRAE Standard 55-2017. ASHRAE. 2016. Ventilation for acceptable indoor air quality. ANSI/ ASHRAE Standard 62. 1-2016. ASHRAE. 2016. Ventilation and acceptable indoor air quality in low-rise residential buildings. ANSI/ASHRAE Standard 62.2-2016. ASHRAE. 2016. Energy standard for buildings except low-rise residential buildings. ANSI/ASHRAE Standard 90.1-2016. ASHRAE. 2007. Energy-efficient design of low-rise residential buildings. ANSI/ASHRAE Standard 90.2-2007. ASHRAE. 2008. Testing, adjusting, and balancing of building HVAC sys- tems. ANSI/ASHRAE Standard 111-2008 (RA 2017). ASHRAE. 2016. Ventilation for commercial cooking operations. ANSI/ ASHRAE Standard 154-2016. ASHRAE. 2014. Standard for the design of high-performance green build- ings. ANSI/ASHRAE/USGBC/IES Standard 189.1-2014. ASHRAE. 2013. Commissioning process for buildings and systems. ANSI/ ASHRAE Standard 202-2013. ASTM. 2016. Test methods for fire resistive grease duct enclosure systems. Standard E2336-16. American Society for Testing and Materials, West Conshohocken, PA. ASTM. 2017. Test method for capture and containment performance of commercial kitchen exhaust ventilation systems. Standard F1704-17. American Society for Testing and Materials, West Conshohocken, PA. ASTM. 2017. Test method for heat gain to space performance ofcommercial kitchen ventilation/appliance systems. Standard F2474-17. American Society for Testing and Materials, West Conshohocken, PA. ASTM. 2015. Test method for grease particle capture efficiency of commer- cial kitchen filters and extractors. Standard F2519-05 (R2015). Ameri- can Society for Testing and Materials, West Conshohocken, PA. Brohard, G., D.R. Fisher, V .A. Smith, R.T. Swierczyna, and P.A. Sobiski. 2003. Makeup air effects on kitchen exhaust hood performance. Califor- nia Energy Commission, Sacramento. Brown, S.L. 2007. Dedicated outdoor air system for commercial kitchen ventilation. ASHRAE Journal (July). Elovitz, G. 1992. Design considerations to master kitchen exhaust systems. ASHRAE Transactions 98(1):1 199-1213. Paper AN-92-16-2. Fisher, D.F. 1998. New recommended heat gains for commercial cooking equipment. ASHRAE Transactions 104(2). Paper TO-98-14-1. Fisher, D.F. 2003. Predicting energy consumption: Clearing the air on kitch- ens. ASHRAE Journal (June). Fuller, S., and S. Peterson. 1996. Life-cycle costing manual for the federal energy management program. Handbook (NIST HB) 135. National Insti- tute of Standards and Technology, Gaithersburg, MD. Gerstler, W.D., T.H. Kuehn, D. Y.H. Pui, J. W. Ramsey, M.J. Rosen, R.R. Carlson, and S.D. Petersen. 1998. Identification and characterization of effluents from various cooking appliances and processes as related to op- timum design ofkitchen ventilation systems. ASHRAE Research Project RP-745 (Phase II), Final Report. Gordon, E.B., and F.A. Parvin. 1994. A field test method for determining ex- haust rates in grease hoods for commercial kitchens (RP-623). ASHRAE Transactions 100(2):412-419. Paper 3824. HUD. [Annual]. Manufactured home construction and safety standards. 24 CFR 3280. Code of Federal Regulations, U.S. Department of Housing and Urban Development, Washington, D.C. HVI. 2008. The guide to home ventilation and indoor air quality. Home Ven- tilating Institute, Arlington Heights, IL. IAPMO. 2018. Uniform mechanical code. IAPMO/ANSI Standard UMC 1- 2019. International Association of Plumbing and Mechanical Officials, Ontario, CA. ICC. 2018a. International mechanical code. International Code Council, Washington, D.C. ICC. 2018b. Internationalfuel gas code. International Code Council, Wash- ington, D.C. ICC. 2018c. International building code. International Code Council, Wash- ington, D.C. ICC. 2018d. International fire code. International Code Council, Washington, D.C. Itron, Inc., and California Energy Commission. 2006. California commer- cial end-use survey. CEC-400-2006-005. www.energy.ca.gov/ceus/2006 enduse.html. Kuehn, T.H. 2000. Effects of air velocity on grease deposition in exhaust ductwork (RP-1033). ASHRAE Research Project, Final Report. Kuehn, T.H. 2008. Characterization of effluents from additional cooking appliances. ASHRAE Research Project RP-1375, Final Report. Kuehn, T.H. 2010. Method of test to evaluate field performance of commer- cial kitchen ventilation systems. ASHRAE Research Project RP-1376, Final Report. Kuehn, T.H., W.D. Gerstler, D.Y.H. Pui, and J.W. Ramsey. 1999. Comparison of emissions from selected commercial kitchen appliances and food products. ASHRAE Transactions 105(2):128-141. Paper 4285. NEMA. 2016. Motors and generators. Standard MG 1-2016. National Elec- trical Manufacturers Association, Rosslyn, VA. Inc. ASHRAE, 2019 user. single for Licensed | {}
aba8a4b1-b979-4095-82bd-2c668582e14f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Kitchen Ventilation 34.45 NFPA. 2017. Installation of sprinkler systems. ANSI/NFPA Standard 13- 2017. National Fire Protection Association, Quincy, MA NFPA. 2017. Dry chemical extinguishing systems. ANSI/NFPA Standard 17-2013. National Fire Protection Association, Quincy, MA. NFPA. 2017. Wet chemical extinguishing systems. ANSI/NFPA Standard 17A-2017. National Fire Protection Association, Quincy, MA. NFPA. 2014. Inspection, testing, and maintenance of water-based fire pro- tection systems. Standard 25-2014. National Fire Protection Associa- tion, Quincy, MA. NFPA. 2015. National fuel gas code. Standard 54-2015. National Fire Pro- tection Association, Quincy, MA. NFPA. 2013. Ventilation control and fire protection of commercial cooking operations. Standard 96-2013. National Fire Protection Association, Quincy, MA. PG&E Food Service Technology Center. 2004. Commercial kitchen ventila- tion design guide series. PG&E Food Service Technology Center, San Ramon, CA. PG&E Food Service Technology Center. 2010. Wall-mounted canopy ex- haust hood performance reports: Application of ASTM 1704, standard test method for capture and containment performance of commercial kitchen exhaust ventilation system. PG&E Food Service Technology Center, San Ramon, CA. PG&E Food Service Technology Center. 2011. Dishwashing machine perfor- mance reports. PG&E Food Service Technology Center, San Ramon, CA. Schrock, D. W. 1998. Determining the efficiency of grease-removal devices in commercial kitchen applications (RP-851). ASHRAE Transactions 104(2). Paper TO-98-14-2. Spata, A.J., and S.M. Turgeon. 1995. Impact of reduced exhaust and venti- lation rates at "no-load" cooking conditions in a commercial kitchen during winter operation. ASHRAE Transactions 101(2):606-610. Paper SD-95-01-3. Stoops, J., A. Watkins, E. Smyth, M. Adams, A. Simone, and B.W. Olesen. 2013. Thermal comfort in commercial kitchens. ASHRAE Research Project RP-1469, Final Report. Swierczyna, R.T., V.A. Smith, and F.P. Schmid. 1997. New threshold exhaust flow rates for capture and containment of cooking effluent. ASHRAE Transactions 103(2):943-949. Paper BN-97-17-2. Swierczyna, R. T., P. Sobiski, and D. Fisher. 2006. Effects ofappliance diver- sity and position on commercial kitchen hood performance (RP-1202). ASHRAE Transactions 112(1). Paper CH-06-08-2. Swierczyna, R., D. Fisher, and P. Sobiski. 2008. Revised heat gain and cap- ture and containment exhaust rates from typical commercial cooking appliances. ASHRAE Research Project RP-1362, Final Report. Swierczyna, R., P. Sobiski, and D. Fisher. 2010. Island hood energy con- sumption and energy consumption strategies. ASHRAE Research Proj- ect RP-1480, Final Report. UL. 2010. Factory-built chimneys for residential type and building heating appliances, 11th ed. ANSI/UL Standard 103-2010. Underwriters Labo- ratories, Northbrook, IL. UL. 2005. Fire testing of fire extinguishing systems for protection of restau- rant cooking areas, 3rd ed. ANSI/UL Standard 300-2005. Underwriters Laboratories, Northbrook, IL. UL 2016. Outline ofinvestigation for extinguishing system units for residen- tial range top cooking surfaces, 3rd ed. Standard 300A-2016. Underwrit- ers Laboratories, Northbrook, IL. UL. 2018. Electric fans, 10th ed. ANSI/UL Standard 507-2018. Underwrit- ers Laboratories, Northbrook, IL. UL. 2012. Exhaust hoods for commercial cooking equipment, 6th ed. ANSI/ UL Standard 710-2012. Underwriters Laboratories, Northbrook, IL. UL. 2011. Recirculating systems, 2nd ed. ANSI/UL Standard 710B-2011. Underwriters Laboratories, Northbrook, IL. UL. 2006. Ultraviolet radiation systems for use in the ventilation control of commercial cooking operations, 3rd ed. Standard 710C. Underwriters Laboratories, Northbrook, IL. UL. 2013. Power roof ventilators for restaurant exhaust appliances, 7th ed. Standard 762-2013. Underwriters Laboratories, Northbrook, IL. UL. 2016. Commercial dishwashers, 7th ed. ANSI/UL Standard 921-2016. Underwriters Laboratories, Northbrook, IL. UL. 2010. Grease filters for exhaust ducts, 4th ed. ANSI/UL Standard 1046- 2010. Underwriters Laboratories, Northbrook, IL. UL. 2010. Grease ducts, 4th ed. ANSI/UL Standard 1978-2010. Underwrit- ers Laboratories, Northbrook, IL. UL. 2010. Fire resistive grease duct enclosure assemblies, 2nd ed. Standard 2221-2010. Underwriters Laboratories, Northbrook, IL. UL. 2016. 1400 degree Fahrenheit factory-built chimneys, 2nd ed. ANSI/UL Standard 2561-2016. Underwriters Laboratories, Northbrook, IL. UL. 2004. Fire testing of sprinklers and water spray nozzles for protection of deep fat fryers, 1st ed. Outline ofInvestigation 199E-2004. Underwriters Laboratories, Northbrook, IL. Welch, W.A. 2004. Development of a draft method of test for determining grease removal efficiencies. ASHRAE Research Project RP-1151, Final Report. Zhang, J. 2015. Countertop commercial appliance emissions. ASHRAE Research Project RP-1631. BIBLIOGRAPHY ASTM. 2012. Standard test method for measuring the field performance of commercial kitchen ventilation systems. Standard F2975-12. American Society for Testing and Materials, West Conshohocken, PA. Bevirt, W.D. 1994. What engineers need to know about testing and balanc- ing. ASHRAE Transactions 100(1):705-714. Paper NO-94-04-1. Black, D.K. 1989. Commercial kitchen ventilation- Efficient exhaust and heatrecovery. ASHRAE Transactions 95(1):780-786. Paper CH-89-09-6. Claar, C.N., R.P. Mazzucchi, and J.A. Heidell. 1985. The project on restau- rant energy performance (PREP)-End use monitoring and analysis. U.S. Department of Energy, Office of Building Energy Research and Development, Washington, D.C. Farnsworth, C., A. Waters, R.M. Kelso, and D. Fritzsche. 1989. Develop- ment of a fully vented gas range. ASHRAE Transactions 95(1):759-768. Paper CH-89-09-4. Frey, D.J., K.F. Johnson, and V.A. Smith. 1993. Computer modeling analysis of commercial kitchen equipment and engineered ventilation. ASHRAE Transactions 99(2):890-908. Paper DE-93-13-3. Fritz, R.L. 1989. A realistic evaluation of kitchen ventilation hood designs. ASHRAE Transactions 95(1):769-779. Paper CH-89-09-5. Fugler, D. 1989. Canadian research into the installed performance ofkitchen exhaust fans. ASHRAE Transactions 95(1):753-758. Paper CH-89-09-3. Gordon, E.B., and N.D. Burk. 1993. A two-dimensional finite-element anal- ysis of a simple commercial kitchen ventilation system. ASHRAE Trans- actions 99(2):909-914. Paper DE-93-13-4. Gordon, E.B., D.J. Horton, and F.A. Parvin. 1994. Development and appli- cation of a standard test method for the performance of exhaust hoods with commercial cooking appliances. ASHRAE Transactions 100(2): 988-999. Paper OR-94-15-3. Gordon, E.B., D.J. Horton, and F.A. Parvin. 1995. Description of a commer- cial kitchen ventilation (CKV) laboratory facility. ASHRAE Transactions 101(1):249-261. Paper 3855. Horton, D.J., J.N. Knapp, and E.J. Ladewski. 1993. Combined impact of ven- tilation rates and internal heat gains on HVAC operating costs in commer- cial kitchens. ASHRAE Transactions 99(2):877-883. Paper DE-93-13-1. ICC. 2004. Acceptance criteria for grease duct assemblies. AC101-2004. International Code Council, Washington, D.C. Kelso, R.M., and C. Rousseau. 1995. Kitchen ventilation. ASHRAE Journal 38(9):32-36. Knapp, J.N., and W.A. Cheney. 1993. Development of high-efficiency air cleaners for grilling and deep-frying operations. ASHRAE Transactions 99(2):884-889. Paper DE-93-13-2. Kuehn, T.H., J. Ramsey, H. Han, M. Perkovich, and S. Youssef. 1989. A study of kitchen range exhaust systems. ASHRAE Transactions 95(1): 744-752. Paper CH-89-09-2. Livchak, A., D. Schrock, and Z. Sun. 2005. The effect of supply air systems on kitchen thermal environment. ASHRAE Transactions 111(1):748-754. Paper OR-05-08-3. Parikh, J.S. 1992. Testing and certification of fire and smoke dampers. ASHRAE Journal 34(11):30-33. Pekkinen, J., and T.H. Takki-Halttunen. 1992. Ventilation efficiency and thermal comfort in commercial kitchens. ASHRAE Transactions 98(1): 1214-1218. Paper AN-92-16-3. Pekkinen, J.S. 1993. Thermal comfort and ventilation effectiveness in com- mercial kitchens. ASHRAE Journal 35(7):35-38. Schmid, F.P V.A. Smith, and R. T. Swierczyna. 1997. Schlieren flow visu- alization in commercial kitchen ventilation research. ASHRAE Transac- tions 103(2):937-942. BN-97-17-1. Paper Inc. ASHRAE, 2019 user. single for Licensed | {}
261f4363-e699-4859-87f1-56b6f51c2f5b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 34.46 2019 ASHRAE Handbook- -HVAC Applications (SI) Shaub, E.G., A.J. Baker, N.D. Burk, E.B. Gordon, and P.G. Carswell. 1995. On development ofa CFD platform for prediction of commercial kitchen ventilation flow fields. ASHRAE Transactions 101(2):581-593. Paper SD-95-01-1. Smith, V.A., D.J. Frey, and C. V. Nicoulin. 1997. Minimum-energy kitchen ventilation for quick service restaurants. ASHRAE Transactions 103(2): 950-961. Paper BN-97-17-3. Smith, V.A., R.T. Swierczyna, and C.N. Claar. 1995. Application and en- hancement of the standard test method for the performance of commer- cial kitchen ventilation systems. ASHRAE Transactions 101(2): 594-605. Paper SD-95-01-2. Smith, V.A., and D.R. Fisher. 2001. Estimating food service loads and pro- files. ASHRAE Transactions 107(2). Paper CI-01-10-3. Soling, S.P., and J. Knapp. 1985. Laboratory design of energy efficient ex- haust hoods. ASHRAE Transactions 91(1B):383-392. Paper CH-85-08-2. Swierczyna, R.T., D.R. Fisher, and D.J. Horton. 2002. Effects ofcommercial kitchen pressure on exhaust system performance. ASHRAE Transactions 108(1). Paper AC-02-16-3. Swierczyna, R.T., P.A. Sobiski, and D.F. Fisher. 2006. Effects of appliance diversity and position on commercial kitchen hood performance. ASHRAE Transactions 112(1). Paper CH-06-08-2. VDI Verlag. 1999. Raumlufttechnische Anlagen fur K�chen (Ventilation equipmentfor kitchens). VDI 2052. Wolbrink, D.W., and J.R. Sarnosky. 1992. Residential kitchen ventilation- A guide for the specifying engineer. ASHRAE Transactions 91(1):1187- 1198. Paper AN-92-16-1. Inc. ASHRAE, 2019 user single for Licensed Related Commercial Resources | {}
9ed1aa42-99bd-42c0-b129-7d7ac57acb6f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 35 GEOTHERMAL ENERGY ¦ GROUND-SOURCE HEAT PUMPS ¦ 35.1 ¦ ¦ --- ¦ --- ¦ ¦ Terminology ¦ 35.1 ¦ ¦ General Information ¦ 35.4 ¦ ¦ Ground-Coupled Heat Pump Systems Using Water-Based Heat ¦ Ground-Coupled Heat Pump Systems Using Water-Based Heat ¦ Transfer Fluids 35.4 Ground-Coupled Heat Pump Systems Using Refrigerant-Based Heat Transfer Fluids (Direct Exchange) 35.29 Open-Loop Groundwater Heat Pump System Components. ... 35.30 Open-Loop Groundwater Heat Pump System Design 35.34 Surface Water Heat Pumps 35.37 HE use of geothermal resources can be subdivided into three T general categories: ground-source heat pump applications (gen- erally <32°C, which usually require a heat pump to provide useful energy), intermediate- and low-temperature (<150°C) direct-use applications, and high-temperature (>150°C) electric power produc- tion. This chapter covers only ground-source heat pumps and intermediate- and low-temperature direct use. Design aspects of the building heat pump loop may be found in Chapter 9 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment. 1. GROUND-SOURCE HEAT PUMPS Ground-source heat pumps (GSHPs) were originally developed to heat and cool residential buildings but are also now widely applied in the commercial sector, with a primary goal of improving energy performance over conventional systems. Many installation recommendations and design guides appropriate to residential design must be amended for large buildings. In large buildings, GSHPs save not only energy but also water, because they often displace cooling towers for cooling. Kavanaugh and Rafferty (2014) provide a more complete overview of design of ground- source heat pump systems. Kavanaugh (1991) and Oklahoma State University (1988a, 1988b) discuss design and installation of ground-source heat pumps in more detail, but their focus is primarily residential and light commercial applications. For comprehensive coverage of commercial and institutional design and construction of ground-source heat pump systems, see ANSI/ CSA/IGSHPA Standard C448-16. 1.1 TERMINOLOGY The term ground-source heat pump (GSHP) is applied to a variety of systems that use the ground, groundwater, or surface water as a heat source and sink. The general terms include ground- coupled (GCHP), groundwater (GWHP), and surface-water (SWHP) heat pumps. Many parallel terms exist (e.g., geothermal heat pumps [GHPs], geo-exchange, and ground-source [GS] systems) and are used to meet a variety of marketing or institutional needs (Kavanaugh 1992). See Chapter 9, Applied Heat Pump and Heat Recovery Systems, of the 2016 ASHRAE Handbook-HVAC Systems and Equipment for a discussion of the merits of various other non-geothermal heat sources/sinks. This chapter focuses primarily on the ground heat exchanger portion of GSHP systems, although the heat pump units used in these The preparation of this chapter is assigned to TC 6.8, Geothermal Heat Pump and Energy Recovery Applications. DIRECT-USE GEOTHERMAL ENERGY 35.39 Resources 35.39 Fluids 35.40 Present Use 35.41 Design 35.41 Cost Factors 35.41 Materials and Equipment 35.43 Residential and Commercial Building Applications 35.46 Industrial Applications 35.48 Renewability 35.48 systems are unique to GSHP technology as well. GSHP systems typically use extended-range water-source heat pump units, in most cases of water-to-air configuration. Extended-range units are specifically designed for operation at entering water temperatures between -5°C in heating mode and 40°C in cooling mode. Units not meeting extended-range criteria are not suitable for use in GSHP systems (except for some groundwater heat pump systems). Some applications (e.g., groundwater loops, deep-surface-water loops, interior core zones of ground-coupled loops when perimeter zones require heating) include a free-cooling mode when water-loop temperatures fall near or below 13°C. This is typically accomplished by inserting a water coil in the return air stream before the refrigerant coil. Ground-Coupled Heat Pump Systems The GCHP is a subset of the GSHP and is often called a closed- loop heat pump. A GCHP system consists of a reversible vapor compression cycle that is linked to a closed ground heat exchanger (also called a ground loop) buried in soil (Figure 1). The most widely used unit is a water-to-air heat pump, which circulates water or a water/antifreeze solution through a liquid-to-refrigerant heat exchanger and a buried thermoplastic piping network. Heat pump units often include desuperheater heat exchangers (shown on the left in Figure 1). These devices use hot refrigerant at the compressor outlet to heat water. A second type of GCHP is the direct-exchange configuration (DXGCHP), which circulates the refrigerant directly (rather than a secondary heat transfer fluid) in a network of buried copper piping. The GCHP is further subdivided by whether its ground heat exchanger design is vertical or horizontal. Vertical GCHPs (Figure 2) generally consist of two small-diameter, high-density polyethylene (HDPE) tubes placed in a vertical borehole that is subsequently filled with a solid medium. The tubes are thermally fused at the bottom of the bore to a close return U-bend. Vertical tubes range from 20 to 40 mm nominal diameter. Bore depths normally range from 15 to 120 m depending on local drilling conditions and available equipment, but can go to 180 m or more if procedures for deep boreholes are followed (see the section on Pump and Piping System Options). Boreholes are typically 100 to 150 mm in diameter. To reduce thermal interference between individual bores, a minimum borehole separation distance of 6 m is recommended when loops are placed in a grid pattern. This distance may be reduced when bores are placed in a single row, the annual ground load is balanced (i.e., energy released in the ground is approximately equal to the energy extracted on an annual basis), or water movement or evaporation and subsequent recharge mitigates the effect of heat build-up in the loop field. 35.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
efc2fd33-62b0-44f6-87b3-7fb72269ae5e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 35.2 Advantages of the vertical GCHP are that it (1) requires relatively small plots of ground, (2) is in contact with soil that varies very little in temperature and thermal properties, (3) requires the smallest amount of pipe and pumping energy, and (4) can yield the most efficient GCHP system performance. Disadvantages are (1) typically higher cost because expensive equipment is needed to drill the borehole and (2) the limited availability of contractors to perform such work. ![image](/image/placeholder) AIR OUT INDOOR COIL FAN REFRIGERANT-TO-WATER HEAT EXCHANGER AIR IN 0000 0000 COLD WATER EXPANSION DEVICE REVERSING VALVE OUTLET WATER INLET GROUND LEVEL HOT WATER PUMP COMPRESSOR REFRIGERANT FLOW COOLING POLYETHYLENE U-TUBE HEATING Fig. 1 Vertical Closed-Loop Ground-Coupled Heat Pump System (Kavanaugh 1985) CLOSE HEADER OPTION (RECOMMENDED IF LOOPS BENEATH PARKING LOTS) RETURN SUPPLY HEADER DETAIL NOT RETURN SHOWN HEADER FLOW REDUCERS FLOW FLOW HEADER REDUCERS MODIFIED REVERSE-RETURN FLOW HEADERS U-TUBES 20 to 40 mm. dia. 5 m separation possible if annual heat 6 to 8 m flow is nearly balanced or in residential SEPARATION applications with a single row of bores. Fig. 2 Vertical Ground-Coupled Heat Pump Piping 2019 ASHRAE Handbook- - HVAC Applications (SI) Hybrid systems are a variation of ground-coupled systems in which a smaller ground heat exchanger is used, augmented in cooling mode by a fluid cooler or a cooling tower. This approach can have merit in large cooling-dominated applications. The ground heat exchanger is sized to meet the heating requirements. The downsized loop is used in conjunction with the fluid cooler or cooling tower with an isolation heat exchanger to meet the heat rejection load. Using the cooler reduces the capital cost of the ground heat exchanger in such applications, but somewhat increases maintenance requirements. For heavily heating-dominant applications, a downsized loop also can be augmented with an auxiliary heat source such as electric resistance, solar collectors, or fossil fuel. Horizontal GCHPs (Figure 3) include single-pipe, multiple- pipe, spiral (see Figure 23), and horizontally bored layouts. Single-pipe horizontal GCHPs are placed in narrow trenches at least 1.2 m deep. These designs require the greatest amount of ground area. Multiple pipes (usually two, four, or six), placed in a single trench, can reduce the amount of required ground area. Trench length is reduced with multiple-pipe GCHPs, but total pipe length must be increased to overcome thermal interference from adjacent pipes. The spiral coil further reduces required ground area. These horizontal ground heat exchangers are made by stretching small-diameter polyethylene tubing from the tight coil in which it is shipped into an extended coil that can be placed vertically in a narrow trench or laid flat at the bottom of a wide trench. Recommended trench lengths are much shorter than those of single-pipe horizontal GCHPs, but pipe lengths must be much ![image](/image/placeholder) DOUBLE PIPE IN SINGLE TRENCH 1 2 m 1.5 m 1.8 m 0.6 m Note: If frost line is greater than 0.9 m below grade, average depth of coils should be a minimum of 0.6 m below frost line and upper pipe should be a minimum of 0.3 m below frost line. ![image](/image/placeholder) HEADERS 5 m GROUTED 10 m U-TUBES 15 m Fig. 3 Trenched Horizontal (top) and Horizontally Bored (bottom) Ground-Coupled Heat Pump Piping Inc. ASHRAE, 2019 user. single for Licensed | {}
2c32c648-1e02-469c-970f-c9efa6b060c4 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Geothermal Energy 35.3 ![image](/image/placeholder) HEAT PUMP HEAT CIRCULATING PUMP EXCHANGER PRODUCTION INJECTION WELL WELL Fig. 4 Unitary Groundwater Heat Pump System longer to achieve equivalent thermal performance. When horizontally bored loops are grouted and placed in the deep earth, as shown in the bottom of Figure 3, design lengths are near those for vertical systems, because annual temperature and moisture content variations approach deep-earth values. Advantages of horizontal GCHPs are that (1) they are typically less expensive than vertical GCHPs because relatively low-cost installation equipment is widely available, (2) many residential applications have adequate ground area, and (3) trained equipment operators are more widely available. Disadvantages include (1) a larger ground area requirement; (2) greater adverse variations in performance because ground temperatures and thermal properties fluctuate with season, rainfall, and burial depth; (3) slightly higher pumping-energy requirements; and (4) lower system efficiencies. Oklahoma State University (1988a, 1988b), Remund and Carda (2014), and Svec (1990) discuss design and installation of horizontal GCHPs. Groundwater Heat Pump (GWHP) Systems The second subset of GSHPs is groundwater heat pumps (Figure 4). Until the development of GCHPs, they were the most widely used type of GSHP. In the commercial sector, GWHPs can be an attractive alternative because large quantities of water can be delivered from and returned to relatively inexpensive wells that require very little ground area. Whereas the cost per unit capacity of the ground heat exchanger is relatively constant for GCHPs, the cost per unit capacity of a well water system is much lower for a large GWHP system. A pair of high-volume wells can serve an entire building. Properly designed groundwater loops with correctly developed water wells require no more maintenance than conventional air and water central HVAC. When groundwater is injected back into the aquifer by a second well, net water use is zero. One widely used design places a central water-to-water heat exchanger between the groundwater and a closed water loop, which is connected to water-to-air heat pumps in the building. A second possibility is to circulate groundwater through a heat recovery chiller (isolated with a heat exchanger), and to heat and cool the building with a distributed hydronic loop. ![image](/image/placeholder) PUMP LAKE FLUSH VALVES 6 m 6 m UNBIND COILS FROM TIGHT SHIPPING BUNDLE. SEPARATE AND REBIND IN LOOSE BUNDLES. WEIGHTED TIRES Fig. 5 Lake Loop Piping Both types and other variations may be suited for direct preconditioning in much of the United States. Groundwater below 15°C can be circulated directly through hydronic coils in series or in parallel with heat pumps. The cool groundwater can displace a large amount of energy that would otherwise have to be generated by mechanical refrigeration. Advantages of GWHPs under suitable conditions are (1) they cost less than GCHP equipment, (2) the space required for the water well is very compact, (3) water well contractors are widely available, and (4) the technology has been used for decades in some of the largest commercial systems. Disadvantages are that (1) local environmental regulations may be restrictive, (2) water availability may be limited, (3) fouling precautions may be necessary if groundwater is used directly in the heat pumps and water quality is poor, and (4) pumping energy may be high if the system is poorly designed or draws from a deep aquifer. Surface Water Heat Pump Systems Surface water heat pumps are included as a subset of GSHPs because of the similarities in applications and installation methods. SWHPs can be either closed-loop systems similar to GCHPs or open-loop systems similar to GWHPs. However, the thermal characteristics of surface water bodies are quite different than those of the ground or groundwater. Some unique applications are possible, though special precautions may be warranted. Closed-loop SWHPs (Figures 5 and 36) consist of water-to-air or water-to-water heat pumps connected to a piping network (also called a surface water loop) placed in a lake, river, or other open body of water. A pump circulates water or a water/antifreeze solution through the heat pump water-to-refrigerant heat exchanger and the submerged piping loop, which transfers heat to or from the body of water. The recommended piping material is thermally fused HDPE tubing with ultraviolet (UV) radiation protection. Inc. ASHRAE, 2019 user. single for Licensed Advantages of closed-loop SWHPs are (1) relatively low cost (compared to GCHPs) because of reduced excavation costs, (2) low pumping-energy requirements, (3) low maintenance requirements, and (4) low operating cost. Disadvantages are (1) the possibility of coil damage in public lakes and (2) wide variation in water temperature with outdoor conditions iflakes are small and/or shallow. Such variation in water temperature would cause | {}
26b5f44b-9e12-4858-bac4-9b78b85921d7 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 35.4 2019 ASHRAE Handbook-HVAC Applications (SI) undesirable variations in efficiency and capacity, though not as severe as with air-source heat pumps. Open-loop SWHPs can use surface water bodies the way cooling towers are used, but without the need for fan energy or frequent maintenance. In warm climates, lakes can also serve as heat sources during winter heating mode, but in colder climates where water temperatures drop below 7°C, closed-loop systems are the only viable option for heating. Lake water can be pumped directly to water-to-air or water-to- water heat pumps or through an intermediate heat exchanger that is connected to the units with a closed piping loop. Direct systems tend to be smaller, having only a few heat pumps. In deep lakes (12 m or more), there is often enough thermal stratification throughout the year that direct cooling or precooling is possible. Water can be pumped from the bottom of deep lakes through a coil in the return air duct. Total cooling is possible if water is 10°C or below. Precooling is possible with warmer water, which can then be circulated through the heat pump units. Large-scale cooling-only systems have been deployed successfully in some locations, including Cornell University and the city of Toronto (Cornell University 2006; Enwave [no date]). 1.2 GENERAL INFORMA TION Site Characterization Site characteristics influence the type of GSHP system most suitable for a particular location. Site characterization is the evaluation of a site 's geology and hydrogeology with respect to its effect on GSHP system design. Important issues include presence or absence of water, depth to water, water (or soil/rock) temperature, groundwater quality, depth to rock, rock type, and the nature and thickness of unconsolidated materials overlying the rock. Information about the nature of water resources at the site helps to determine whether an open-loop system may be possible. Depth to water affects pumping energy for an open-loop system and possibly the type of rig used for drilling closed-loop boreholes. Groundwater temperature in most locations is the same as the undisturbed ground temperature. These temperatures are key inputs to the design of GSHP systems. The types of soil and rock allow a preliminary evaluation of the range of thermal conductivity/diffusivity that might be expected. The thickness and nature of the unconsolidated (soil, gravel, sand, clay, etc.) materials overlying the rock affect whether casing is required in the upper portion of boreholes for closed-loop systems, a factor that increases drilling cost. After the GSHP system type has been decided, specific details about the subsurface materials' (rock/soil) thermal conductivity and diffusivity, water well static and pumping levels, drawdown, etc., are necessary to design the system. There are many sources for gathering site characterization information: geologic and hydrologic maps, state geology and water regulatory agencies, the U.S. Geological Survey (USGS 2000), and geotechnical studies of the site. Among the best sources of information are completion reports for nearby water wells. These reports are filed by the driller upon completion of a water well and provide a great deal of information of interest for both open- and closed-loop designs. The most thorough versions of well completion reports (level of detail varies by state) cover all of the issues of interest to GSHP designers. Information about access to and interpretation of these reports and other sources of information for site characterization is included in Rafferty (2000a) and Sachs (2002). Once the type of system has been selected, more site-specific tests (e.g., ground thermal properties test for GCHP, well flow test for GWHP) can be used to determine the parameters necessary for system design. In many areas, ground heat exchangers are regulated by the state or other jurisdictions and under the jurisdiction of a state water rights authority, department of natural resources or environmental quality, or possibly a federal agency such as the U.S. Army Corps of Engineers. The regulation scope may include any type of ground-coupled system. The engineer or designer should be aware of and versed in regulatory issues affecting the project site. More recently, the U.S. Department of Homeland Security has required that certain activities, especially those close to drinking water sources, be excluded or stringently regulated. For security reasons, resource protection zones may not be found in public records archives. The simplest solution may be to contact the permitting authority. Commissioning GSHP Systems The design phase of GSHP commissioning requires a thorough site survey and characterization, accurate load modeling, and ensuring that the design chosen (and its documentation) meets the design intent. The construction phase is dominated by observation of installation and verification of prefunctional checks and tests. It also involves planning, training development, and other activities to help future building operators understand the HVAC system. The acceptance phase starts with functional tests and verification of all test results. It continues with full documentation: completing the commission report to include records of design changes and all as-built plans and documents, and completing the operations and maintenance manual and system manual. Finally, after system testing and balancing is complete, the owner's operating staff are trained. The acceptance phase ends at substantial completion, at which date the warranty period begins. Table 1 provides information on tasks and participants involved in the GSHP commissioning process. Additional details on this topic, along with preventive maintenance and troubleshooting information, are included in Caneta Research (2001). Also, per ANSI/CSA/IGSHPA Standard C448-16, the contractor must provide the owner with a written maintenance procedure. Codes and Standards Current Uniform Code and International Code revisions now address ground-source heat pump systems. The Uniform Code now contains an independent volume, the Uniform Solar Electric and Hydronic Code (IAPMO 2015), which discusses ground- source piping for geothermal systems in Chapters 4 (Hydronics) and 7 (Geothermal Energy Systems). The International Code's Chapter 12 (Hydronic Piping) covers geothermal piping and geothermal systems; ground-source specific information is included in the last section (1210). In addition to standards issued by the International Ground Source Heat Pump Association (IGSHPA 2017), the Canadian Standards Association, in conjunction with U.S. industry and professional organizations, has released a binational standard, ANSI/CSA/IGSHPA Standard C448-16, which covers most forms of open- and closed-loop GSHP and GWHP systems. 1.3 GROUND-COUPLED HEAT PUMP SYSTEMS USING w ATER-BASED HEAT TRANSFER FLUIDS Ground-coupled heat pumps commonly use a secondary water- based heat transfer fluid to extract/reject heat from/to the ground. The fluid exchanges heat with the refrigerant in the heat pump and circulates through the ground in buried thermoplastic tubing. This section discusses how to design different configurations of the ground heat exchanger, considering building loads and the related zone heat pump operations. Inc. ASHRAE, 2019 user. single for Licensed | {}
16af7740-b9b9-4645-a11c-61d0dbac0337 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Geothermal Energy 35.5 Table 1 Example of GSHP Commissioning Process for Mechanical Design ¦ System ¦ Function ¦ Performed By ¦ Witnessed By ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Heat pump piping ¦ Pressure test, clean, and fill ¦ Contractor ¦ A/E ¦ ¦ Ground source piping ¦ Pressure test, clean, fill, and purge air; check for compliance with ICC (2012) sections 1207 and 1208 ¦ Contractor Contractor ¦ A/E ¦ ¦ Pumps ¦ Inspect, test, and start up ¦ Contractor ¦ CA ¦ ¦ Heat recovery unit ¦ Inspect, test, and start up; provide clean set of filters, staff instruction ¦ Manufacturer Contractor Manufacturer ¦ CA/owner ¦ ¦ Heat pump units ¦ Inspect, test, and start up; provide clean filters, staff instruction ¦ Manufacturer Contractor Manufacturer ¦ CA/owner ¦ ¦ Chemical treatment ¦ Flushing and cleaning, chemical treatment, staff instruction ¦ Contractor Contractor/manufacturer Manufacturer ¦ A/E and CA CA/owner ¦ ¦ Balancing ¦ Balancing, spot checking, follow-up site visits ¦ TAB contractor TAB contractor TAB contractor ¦ A/E and CA CA ¦ ¦ Controls Source: Caneta (2001). ¦ Installation/commissioning, staff instruction, performance testing, seasonal testing CA = Commissioning authority ¦ Contractor CA CA CA ¦ CA/owner ¦ A/E = Architect/engineer TAB = Testing, adjusting, and balancing Vertical Design This section provides an overview of a suggested design procedure for vertical, ground-coupled systems; related information and equations are discussed in more detail in Kavanaugh and Rafferty (2014). Several public software programs are available for performing the repetitive computations necessary for system optimization. Shonder et al. (1999, 2000) tested the accuracy of these programs, and agreement was attained with several programs in subsequent evaluations. A more recent publication (Kavanaugh 2008) updates the design recommendations for GCHP systems as follows: 1. Calculate peak zone cooling and heating loads, and estimate off- peak loads. 2. Estimate annual heat rejection into and absorption from the ground heat exchanger to account for potential ground tempera- ture change (see Table 5). 3. Select preliminary loop operating temperatures and flow rate to begin optimization of first cost and efficiency (selecting tem- peratures near normal ground temperature results in high efficiencies but larger and more costly ground heat exchangers). 4. Correct heat pump performance at rated conditions to actual design conditions (see Table 14) 5. Select heat pumps to meet cooling and heating loads, and locate units to ensure accessibility for maintenance and to minimize duct cost and fan power and noise. 6. Arrange heat pump into ground heat exchanger circuits to min- imize system cost, pump energy and electrical demand (see Figures 15 to 17). 7. Conduct site survey to determine ground thermal properties and drilling conditions (see following recommendations). 8. Determine and evaluate possible loop field arrangements that are likely to be optimum for the building and site (bore depth, separation distance, completion methods, annulus grout/fill, and header arrangements); include subheader circuits (typically 5 to 15 U-tubes on each) with isolation valves to allow air and debris flushing of sections ofloop field through a set of full-port purge valves. 9. Determine optimum ground heat exchanger dimensions with Equations (4) and (5) or software; one or more alternatives (depth, number of bores, grout/fill material, etc.) that provide equivalent performance may yield more competitive bids. 10. Iterate to determine optimum operating temperatures, flows, loop field arrangement, depth, bores, grout/fill materials, etc. 11. Lay out interior piping and compute head loss through critical path. 12. Select pumps and control method, determine system efficiency, and consider modifying water distribution system if pump demand exceeds 8% of the system total demand or air distribu- tion system if fan demand exceeds 12% of the system total. Deliverables from this process that are necessary to adequately describe a GCHP installation include, as a minimum, · Heat pump specifications at rated conditions · Pump(s) specifications, expansion tank size, and air separator · Fluid specifications: system volume, inhibitors, antifreeze con- centration (if required), water quality, etc. · Design operating conditions: entering and leaving ground heat exchanger temperatures, return air temperatures (including wet bulb in cooling), airflow rates, and liquid flow rates · Pipe header details with ground heat exchanger layout, including pipe diameters, spacing, and clearance from building and utilities · Bore depth and approximate bore diameter · Piping material specifications, and visual inspection and pressure testing requirements · Grout/fill specifications: thermal conductivity and acceptable placement methods to eliminate voids · Purge provisions and flow requirements to ensure removal of air and debris without reinjecting air when switching to adjacent sub- header circuits · Instructions on connecting to building loop(s) and coordinating building and ground heat exchanger flushing · If applicable, a drilling report from the thermal properties test borehole that includes the type of equipment used (rig, bit, etc.), drilling fluid (air, foam, drilling mud), depth of hole, description of drilled soil or rock, time needed to drill the borehole, any spe- cial conditions encountered. · Sequence of operation for controls Thermal Property Testing. In the design of vertical GCHPs, accurate knowledge of soil/rock formation thermal properties is Inc. ASHRAE, 2019 user. single for Licensed | {}
f5b490a5-9052-467d-b6ac-5cce90408078 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 35.6 2019 ASHRAE Handbook- -HVAC Applications (SI) ![image](/image/placeholder) WATER TANK WITH HEATING ELEMENTS CONNECTION TO ELECTRICAL PURGE VALVES POWER SOURCE INSULATION DATA ACQUISITION INSULATION TEMPERATURE PROBES AND PUMP FLOW METER STANDARD GROUND HEAT EXCHANGER DRILLED TO EXPECTED LOOP DEPTH AT SITE Fig. 6 Thermal Properties Test Apparatus critical. These properties can be estimated in the field by installing a loop of approximately the same size and depth as the heat exchangers planned for the site. The test loop location should be chosen with care, and designed to be used for the eventual full bore- field, especially if geothermal is a likely final system choice (this may require the test loop to meet all local ground heat exchanger standards). Heat is added in a water loop at a constant rate, and data are collected as shown in Figure 6. Inverse methods are applied to find thermal conductivity, diffusivity, and temperature of the forma- tion. These methods are based on either the line source (Gehlin 1998; Mogensen 1983; Witte et al. 2002), the cylindrical heat source (Ingersoll and Zobel 1954), or a numerical algorithm (Austin et al. 2000; Shonder and Beck 1999; Spitler et al. 1999). More than one of these methods should be applied, when possible, to enhance reported accuracy. Recommended test specifications are as follows (Kavanaugh 2000, 2001): · Thermal property tests should be performed for 36 to 48 h. · Heat rate should be 50 to 80 W/m of bore, which are the expected peak loads on the U-tubes for an actual heat pump system. · Standard deviation of input power should be less than ±1.5% of the average value and peaks less than ±10% of average, or result- ing temperature variation should be less than ±0.3 K from a straight trend line ofa log (time) versus average loop temperature. · Accuracy of temperature measurement and recording devices should be ±0.3 K. · Combined accuracy of the power transducer and recording device should be ±2% of the reading. · Flow rates should be sufficient to provide a differential loop tem- perature of 3.7 to 7.0 K. This is the temperature differential for an actual heat pump system. · A waiting period of five days is suggested for low-conductivity soils (k < 1.7 W/[m.K]) after the ground heat exchanger has been installed and grouted (or filled) before the thermal conductivity test is initiated. A delay of three days is recommended for higher- conductivity formations (k > 1. 7 W/[m.K]). · The initial ground temperature measurement should be made at the end of the waiting period by directly inserting a probe inside a liquid-filled ground heat exchanger at three locations, represent- ing the average, or by temperature measurement as liquid exits the loop during the period immediately after start-up. · Data collection should be at least once every 10 min. · All aboveground piping should be insulated with a minimum of 13 mm closed-cell insulation or equivalent. Test rigs should be enclosed in sealed cabinet that is insulated with minimum of a a 25 mm fiberglass insulation or equivalent. · If retesting a bore is necessary, loop temperature should be allowed to return to within 0.3 K of the pretest initial ground tem- perature. This typically requires a 10- to 12-day delay in mid- to high-conductivity formations and 14 days in low-conductivity formations if a complete 48 h test has been conducted. Waiting periods can be proportionally reduced if tests are shorter. Ground Heat Exchanger Sizing. This is perhaps the most criti- cal step in the design ofa vertical GCHP. Ground-loop design meth- ods must proceed with limited information; a major missing component is long-term, field-monitored data, which are needed to further validate the design method to address effects of water move- ment and long-term heat storage more fully. The conservative designer can assume no benefit from water movement; designers who assume maximum benefit must ignore annual imbalances in heat rejection and absorption. Two design methods are presented in the following section. Both methods have been implemented in design software tools, and are based on the assumption that heat transfer in the ground is governed by conduction only. The concentric cylinder source method is based on the solution of the equation for heat transfer from a cylinder buried in the earth. This equation was developed and evaluated by Carslaw and Jaeger (1947) and was suggested by Ingersoll and Zobel (1954) as an appropriate method of sizing ground heat exchangers. Kavanaugh (1985) adjusted the method to account for the U-bend arrangement and hourly heat rate variations. Alternative design methods are described by Eskilson (1987), Morrison (1997), Philippe et al. (2010), Spitler (2000), and Spitler et al. (2000). A second method, attributed to Eskilson, is presented after this first method. Finally, a review of vertical borehole ground heat exchanger design methods has been presented by Spitler and Bernier (2016). Vertical Ground Heat Exchanger Sizing using the Concentric Cylinder Source Method. The method of Ingersoll and Zobel (1954), based on the following steady-state heat transfer equation, can be used to size vertical ground heat exchangers: L t t w q = g R ov (1) where 9 = heat transfer rate, W L = required total bore length, m tg = ground temperature, °C tw = liquid temperature, °C Rov = overall resistance of ground and bore, (m-K)/W The heat rate delivered to the ground in the cooling mode by the condenser includes the heat of the heat pump and auxiliary equip- ment. Thus, qcond can be calculated to be COP + 1.0 C qcond/91c = COP c (2) where COPc = cooling coefficient of performance, W/W qcond = heat pump condenser heat rejection rate to ground, W 91c = building design cooling block load, W 9th = building design heating block load, W However, the heat of the heat pump and auxiliary equipment in heating mode is delivered to the building. Thus the heat removed from the ground by the evaporator is Inc. ASHRAE, 2019 user. single for Licensed | {}
bfb70d22-e14b-44f2-8140-0626dbb58571 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Geothermal Energy 35.7 Table 2 Thermal Properties of Selected Soils, Rocks, and Bore Grouts/Fills ¦ ¦ Dry Density, kg/m3 ¦ Conductivity,* W/(m.K) ¦ Diffusivity, m2/day ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Soils ¦ ¦ ¦ ¦ ¦ Heavy clay, 15% water ¦ 1920 ¦ 1.4 to 1.9 ¦ 0.042 to 0.060 ¦ ¦ 5% water ¦ 1920 ¦ 1.0 to 1.4 ¦ 0.047 to 0.060 ¦ ¦ Light clay, 15% water ¦ 1280 ¦ 0.7 to 1.4 ¦ 0.033 to 0.047 ¦ ¦ 5% water ¦ 1280 ¦ 0.5 to 0.9 ¦ 0.033 to 0.056 ¦ ¦ Heavy sand, 15% water ¦ 1920 ¦ 2.8 to 3.8 ¦ 0.084 to 0.112 ¦ ¦ 5% water ¦ 1920 ¦ 2.1 to 3.3 ¦ 0.093 to 1.200 ¦ ¦ Light sand, 15% water ¦ 1280 ¦ 1.4 to 2.1 ¦ 0.047 to 0.093 ¦ ¦ 5% water ¦ 1280 ¦ 0.9 to 1.9 ¦ 0.056 to 0.121 ¦ ¦ Rocks ¦ ¦ ¦ ¦ ¦ Granite ¦ 2640 ¦ 2.2 to 3.6 ¦ 0.084 to 0.130 ¦ ¦ Limestone ¦ 2400 to 2800 ¦ 2.4 to 3.8 ¦ 0.084 to 0.130 ¦ ¦ Sandstone ¦ ¦ 2.1 to 3.5 ¦ 0.065 to 0.112 ¦ ¦ Shale, wet ¦ 2560 to 2720 ¦ 1.4 to 2.4 ¦ 0.065 to 0.084 ¦ ¦ dry ¦ ¦ 1.4 to 2.1 ¦ 0.056 to 0.074 ¦ ¦ Grouts/Backfills ¦ ¦ Liquid Density, kg/m3 ¦ Conductivity,* W/(m.K) ¦ ¦ Bentonite (20 to 30% solids) ¦ ¦ 1106.1 to 1175.4 ¦ 0.73 to 0.74 ¦ ¦ 10-25% bentonite/20-50% SiO2 35-55% mix water ¦ sand/ ¦ 1350.4 to 1618.8 ¦ 0.99 to 1.64 ¦ ¦ 8-12% bentonite/55-65% SiO2 28-34% mix water ¦ sand/ ¦ 1724.2 to 1788.9 ¦ 1.73 to 2.08 ¦ ¦ Low-density bentonite/graphite additives) ¦ (plus ¦ 1198.3 to 1438.0 ¦ 1.37 to 2.77 ¦ ¦ Neat cement (not recommended) ¦ ¦ 1246.2 to 1773.4 ¦ 1.52 to 2.77 ¦ ¦ 30% concrete/70% SiO2 sand (plus plasticizer) ¦ ¦ 1653.6 to 1917.2 ¦ 0.69 to 0.78 ¦ *Intermediate densities and thermal conductivities can be obtained by mixing silica sand and graphite in different proportions. Contact grout manufacturer for additional information on thermal properties and density of various grout silica sand/graphite mixtures. COP - 1 qevap/ 9lh = COP (3) where 9evap pump evaporator heat extraction rate from is the heat ground, W; 9lh is the building design heating block load, W; and COP is the heating coefficient of performance, W/W. The design (e.g., peak) block load is the average building load during the block (e.g., a specified time period, usually a few hours) on design day (e.g., worst- case weather and occupancy conditions). Ground heat exchanger design also requires calculation of the monthly part-load factors (PLFs), which are the actual monthly loads divided by the monthly load if the building operated continuously at the design block load. Both the design block load and PLFs can be computed using building simulations or design guidelines (see ACCA [2008, 2016] and Chap- ters 17 and 18 of the 2017 ASHRAE Handbook-Fundamentals). Equation (1) can be rearranged to solve for the required bore length L. The steady-state Equation (1) is modified to represent the variable heat rate of a ground heat exchanger by dividing the heat transfer 9 into a series of constant-heat-rate pulses. The thermal resistance Rov is divided into contributions from the ground and borehole. The effective thermal resistance of the ground per unit length is calculated as a function of time corresponding to the time span over which a particular heat pulse occurs (annual Rgas monthly R or peak short-term Rgst); the effective resistance is gm' different from a steady-state resistance in that it accounts for the transient heat flow in the ground. The borehole thermal resistance Rb includes the thermal resistance of the pipe wall and interfaces between the pipe and fluid and the pipe and the ground. The resulting equation takes the following form for the required length to satisfy cooling loads: qaR ga qlc - W Rb + PLF R + F R + c m gm sc gst Lc = + t wo twt : 2 : (4) The required length for heating is (5) qaR ga qlh - Wh Rb + PLF R + F R + m gm sc gst Lh = + t twt wo t. - tp g 2 where F sc short-circuit heat loss factor = L c required total bore length for cooling, m = Ln required total bore length for heating, m = PLF = part-load factor during design month I 9a = net annual average heat transfer to ground, W R = effective thermal resistance of ground (annual pulse), (m-K)/W ga R = effective thermal resistance of ground (peak short term) 1 to 6 h gst recommended, (m-K)/W R = effective thermal resistance of ground (monthly pulse), (m-K)/W gm Rb resistance, (m-K)/W = borehole thermal t = undisturbed ground temperature, °C g 8 = temperature penalty for interference of adjacent bores, °C twi liquid temperature at heat pump inlet, °C = two = liquid temperature at heat pump outlet, °C Wc = system power input at design cooling load, W Wh = system power input at design heating load, W Note: Heat transfer rate, building loads, and temperature penal- ties are positive for heating and negative for cooling. Equations (4) and (5) consider three different pulses of heat to account for long-term heat imbalances, average monthly heat rates during the design month, and maximum heat rates for a short-term period during a design day. This period could be as short as 1 h, but a 4 to 6 h block is recommended. The required total bore length is the larger of the two lengths Lc and Lh calculated with Equations (4) and (5). The heat exchanger will be oversized during the season with shorter calculated L; the resulting increase in efficiency lowers operating costs for that season. However, oversizing the heat exchangers increases first costs, so designers may consider using the shorter calculated L, and supplementing the GSHP system with season-specific equipment (e.g., a cooling tower for cooling, a boiler for heating) to address loads for the season with the longer L. See the section on Hybrid System Design for more information about these configurations. Thermal resistance of the ground is calculated from ground prop- erties, pipe dimensions, grout/fill thermal conductivity, and operating periods of the representative heat rate pulses. Table 2 lists typical thermal properties for soils and fills for the annular region of the boreholes. Type of fill material depends on thermal, regulatory, and economic considerations. Historically, a relatively low-thermal- conductivity bentonite grout common in the water well industry had been used. More recently, thermally enhanced grouts have been developed to supplement or replace conventional grouts. Thermally enhanced grout has three primary components: · Bentonite provides sealing properties to the mixture and sus- pends the thermal additive in the bore column to provide uniform heat transfer from top to bottom. · Thermal additive (either silica sand or graphite) improves over- all grout thermal conductivity (TC) and subsequent heat transfer capabilities. · Mix water amounts are specified by the manufacturer to ensure that the grout will perform as advertised. Inc. ASHRAE, 2019 user. single for Licensed | {}
14f6be38-5d58-435a-9623-35fe8d5c51b3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 35.8 2019 ASHRAE Handbook-HVAC Applications (SI) Table 3 Summary of Potential Completion Methods for Different Geological Regime Types ¦ ¦ Grout ¦ Grout ¦ Grout ¦ ¦ Two-Fill with ¦ Two-Fill with ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Geological Regime Type ¦ 0.6 < k 1.4 W/(m-K) ¦ 1.4 ¦ k> 2.1 W/(m-K) ¦ Backfill with Cuttings or Sand/Gravel Mix ¦ Cuttings or Sand/Gravel Mix Below Aquifers ¦ Other* Below Aquifers ¦ ¦ Clay or low-permeability rock, single-aquifer multiple-aquifer ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ no aquifer ¦ Yes ¦ Yes Yes Yes ¦ Yes Yes Yes ¦ Yes ¦ Yes ¦ Yes Yes ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Yes ¦ Yes ¦ ¦ Permeable rock, ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ no shallow aquifers ¦ ¦ Yes ¦ Yes ¦ Yes ¦ Yes ¦ Yes ¦ ¦ single-aquifer ¦ ¦ Yes ¦ Yes ¦ Yes ¦ Yes ¦ Yes ¦ ¦ multiple-aquifers ¦ ¦ Yes ¦ Yes ¦ Yes ¦ ¦ ¦ ¦ Karst terrains with secondary permeability ¦ ¦ Y es ¦ Yes ¦ Yes ¦ ¦ ¦ ¦ Fractured terrains with secondary permeability ¦ ¦ Y es ¦ Yes ¦ Yes ¦ Yes ¦ Yes ¦ *Use of backfill material that has thermal conductivity of k 2.4 W/(m-K) As with any engineered product, the components must be mixed according to manufacturer specifications to meet the minimum ther- mal performance and permeability requirements for a given project. In some cases, such as when voids, fissures, or caverns are present, drill cuttings or manufactured sand/gravel mixes have been placed instead of bentonite or thermally enhanced grout. Note that placing such fill material from the surface may cause the borehole to bridge, leaving voids or ungrouted sections of the borehole. Also, thermal performance of drill cuttings or manufactured sand/gravel mix is subject to factors such as final placement density and height of the static water table, and is thus difficult to quantify. Because thermal properties of the fill material are critical to overall system performance, use of a tremie pipe to inject grout from the bottom upward is recommended. Nutter et al. (2001) contains a detailed evaluation of potential fills and grouts for vertical boreholes. Also, Jenkins (2009), Sachs (2002), and Skouby (2011) have additional recommendations regarding grout and grout placement. Table 3 summarizes potential completion methods for various geological conditions. "Two-fill" refers to the practice of placing a low-permeability material in the upper part of the hole and/or at intervals where needed to separate individual aquifers, and a more thermally advantageous material in the remaining intervals. When backfill completion methods are allowed in lieu of pressure-tremie grouting, the designer should be aware that thermal properties and subsequent system performance is subject to final backfill density and the location/height of the static water table, as previously mentioned. Borehole thermal resistance, from the fluid to the borehole wall, considers the effects of pipe resistance Rp and bore annulus grout resistance R grt: Rb = Rp + Rgrt Pipe resistance includes the fluid's convective film resistance and the conductive resistance of the pipe walls. Contact resistances are negligible compared to the high resistance of plastic pipe walls and annular grouts. For a single U-tube (two tubes) the pipe resistance is ⑥ Rp = (Rfilm + Rtube)/2 = [1/( dihconv) + ln(do/d,)/2 kp]/2 (7) where hconv pipes, kp is pipe is the convection coefficient inside the thermal conductivity, do is the tube outer diameter, and di is the tube inner diameter. A correlation for the grout's thermal resistance has been developed using shape factor correlations (Remund 1999): Yes = Recommended potentially viable backfill methods ![image](/image/placeholder) A ○○ Bo = 20.10, B1 = -0.9447 B ○ ○ Bo = 17.44, B1 = -0.6052 C Bo = 21.91, B1 = -0.3796 BC COEFFICIENTS UNAVAILABLE ○ ○ DOUBLE DOUBLE U-TUBE ○○ Fig. 7 Coefficients for Equation (8) db 1 I R = k grt 0 d grt where kgrt is the grout' s thermal conductivity and db is bore diameter. Coefficients 0 and in Equation (8) have been developed for three 1 locations ofthe tubes, as shown in Figure 7: centered in the bore and in contact each other (A), centered and spaced evenly in the bore (B), and centered and in contact with the bore wall (C). However, the most likely location of the U-tubes is BC, and coefficients for this location are unavailable. A similar but slightly more detailed solution was developed by Hellstrom (1991) and applied to a few design and simulation tools (Liu 2008; Philippe et. al. 2010). More recently, Javed and Spitler (2017) examined the accuracy of various methods to calculate borehole thermal resistance. (8) Because locations of U-tubes cannot be determined even when spacers are installed, exact computation of bore thermal resistance values is somewhat uncertain. It is possible to apply the results from thermal property tests to calculate the bore thermal resistance if the U-tube dimensions, grout conductivity, and borehole diameter are known (Kavanaugh 2010). Thermal property tests were conducted at 15 installations where these values were known and the bore resistance was calculated. The field calculated bore resistances best matched the values computed with Equations (6) to (8) using Inc. ASHRAE, 2019 user. single for Licensed | {}
7327429e-6abf-413c-b01a-f26222843213 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Geothermal Energy 35.9 Table 4 Thermal Resistance of Bores Rb for Locations B, C, and Double ¦ Tube Diameter and Dimension ¦ Tube Location ¦ Bore Diameter, mm ¦ Thermal Distance of Bore, (m.K)/W ¦ Thermal Distance of Bore, (m.K)/W ¦ Thermal Distance of Bore, (m.K)/W ¦ Thermal Distance of Bore, (m.K)/W ¦ Thermal Distance of Bore, (m.K)/W ¦ Thermal Distance of Bore, (m.K)/W ¦ Thermal Distance of Bore, (m.K)/W ¦ Thermal Distance of Bore, (m.K)/W ¦ Thermal Distance of Bore, (m.K)/W ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Tube Diameter and Dimension ¦ Tube Location ¦ Bore Diameter, mm ¦ Fluid Reynolds Number = 2000 Grout Conductivity, W/(m-K) ¦ Fluid Reynolds Number = 2000 Grout Conductivity, W/(m-K) ¦ Fluid Reynolds Number = 2000 Grout Conductivity, W/(m-K) ¦ Fluid Reynolds Number = 4000 Grout Conductivity, W/(m-K) ¦ Fluid Reynolds Number = 4000 Grout Conductivity, W/(m-K) ¦ Fluid Reynolds Number = 4000 Grout Conductivity, W/(m-K) ¦ Fluid Reynolds Number = 10 000 Grout Conductivity, W/(m-K) ¦ Fluid Reynolds Number = 10 000 Grout Conductivity, W/(m-K) ¦ Fluid Reynolds Number = 10 000 Grout Conductivity, W/(m-K) ¦ ¦ Tube Diameter and Dimension ¦ Tube Location ¦ Bore Diameter, mm ¦ 0.70 ¦ 1.40 ¦ 2.10 ¦ 0.70 ¦ 1.40 ¦ 2.10 ¦ 0.70 ¦ 1.40 ¦ 2.10 ¦ ¦ 25 mm DR 11 HDPE U-Tube ¦ B ¦ 100 ¦ 0.26 ¦ 0.17 ¦ 0.14 ¦ 0.24 ¦ 0.14 ¦ 0.11 ¦ 0.23 ¦ 0.14 ¦ 0.11 ¦ ¦ 25 mm DR 11 HDPE U-Tube ¦ B ¦ 125 ¦ 0.29 ¦ 0.18 ¦ 0.15 ¦ 0.26 ¦ 0.16 ¦ 0.12 ¦ 0.26 ¦ 0.11 ¦ 0.12 ¦ ¦ 25 mm DR 11 HDPE U-Tube ¦ C ¦ 100 ¦ 0.18 ¦ 0.13 ¦ 0.11 ¦ 0.16 ¦ 0.10 ¦ 0.09 ¦ 0.15 ¦ 0.10 ¦ 0.08 ¦ ¦ 25 mm DR 11 HDPE U-Tube ¦ C ¦ 125 ¦ 0.19 ¦ 0.13 ¦ 0.11 ¦ 0.17 ¦ 0.11 ¦ 0.09 ¦ 0.16 ¦ 0.10 ¦ 0.08 ¦ ¦ 25 mm DR 11 HDPE U-Tube ¦ Double ¦ 125 ¦ 0.16 ¦ 0.10 ¦ 0.08 ¦ 0.14 ¦ 0.08 ¦ 0.06 ¦ 0.14 ¦ 0.08 ¦ 0.06 ¦ ¦ 32 mm DR 11 HDPE U-Tube ¦ B ¦ 100 ¦ 0.24 ¦ 0.16 ¦ 0.13 ¦ 0.21 ¦ 0.13 ¦ 0.10 ¦ 0.21 ¦ 0.13 ¦ 0.10 ¦ ¦ 32 mm DR 11 HDPE U-Tube ¦ B ¦ 125 ¦ 0.26 ¦ 0.17 ¦ 0.14 ¦ 0.23 ¦ 0.14 ¦ 0.11 ¦ 0.23 ¦ 0.14 ¦ 0.11 ¦ ¦ 32 mm DR 11 HDPE U-Tube ¦ B ¦ 150 ¦ 0.28 ¦ 0.18 ¦ 0.14 ¦ 0.26 ¦ 0.15 ¦ 0.12 ¦ 0.25 ¦ 0.15 ¦ 0.11 ¦ ¦ 32 mm DR 11 HDPE U-Tube ¦ C ¦ 100 ¦ 0.17 ¦ 0.12 ¦ 0.11 ¦ 0.15 ¦ 0.10 ¦ 0.08 ¦ 0.14 ¦ 0.09 ¦ 0.08 ¦ ¦ 32 mm DR 11 HDPE U-Tube ¦ C ¦ 125 ¦ 0.18 ¦ 0.13 ¦ 0.11 ¦ 0.16 ¦ 0.10 ¦ 0.08 ¦ 0.15 ¦ 0.10 ¦ 0.08 ¦ ¦ 32 mm DR 11 HDPE U-Tube ¦ C ¦ 150 ¦ 0.19 ¦ 0.13 ¦ 0.11 ¦ 0.17 ¦ 0.11 ¦ 0.09 ¦ 0.16 ¦ 0.10 ¦ 0.08 ¦ ¦ 32 mm DR 11 HDPE U-Tube ¦ Double ¦ 125 ¦ 0.15 ¦ 0.09 ¦ 0.07 ¦ 0.13 ¦ 0.08 ¦ 0.06 ¦ 0.13 ¦ 0.08 ¦ 0.06 ¦ ¦ 32 mm DR 11 HDPE U-Tube ¦ Double ¦ 150 ¦ 0.15 ¦ 0.10 ¦ 0.08 ¦ 0.14 ¦ 0.08 ¦ 0.06 ¦ 0.14 ¦ 0.08 ¦ 0.06 ¦ ¦ 40 mm DR 11 HDPE U-Tube ¦ B ¦ 125 ¦ 0.24 ¦ 0.16 ¦ 0.13 ¦ 0.22 ¦ 0.13 ¦ 0.11 ¦ 0.21 ¦ 0.13 ¦ 0.10 ¦ ¦ 40 mm DR 11 HDPE U-Tube ¦ B ¦ 150 ¦ 0.26 ¦ 0.17 ¦ 0.14 ¦ 0.23 ¦ 0.14 ¦ 0.11 ¦ 0.23 ¦ 0.14 ¦ 0.11 ¦ ¦ 40 mm DR 11 HDPE U-Tube ¦ C ¦ 125 ¦ 0.17 ¦ 0.12 ¦ 0.11 ¦ 0.15 ¦ 0.10 ¦ 0.09 ¦ 0.14 ¦ 0.09 ¦ 0.08 ¦ ¦ 40 mm DR 11 HDPE U-Tube ¦ C ¦ 150 ¦ 0.18 ¦ 0.13 ¦ 0.11 ¦ 0.16 ¦ 0.11 ¦ 0.09 ¦ 0.15 ¦ 0.10 ¦ 0.08 ¦ ¦ 40 mm DR 11 HDPE U-Tube ¦ Double ¦ 150 ¦ 0.14 ¦ 0.09 ¦ 0.07 ¦ 0.13 ¦ 0.08 ¦ 0.06 ¦ 0.13 ¦ 0.08 ¦ 0.06 ¦ · Location C at 4 (27%) of the sites · An average of location B and location C at 5 (33%) of the sites · Location B at 5 (33%) of the sites, and · Location A at 1 (7%) site Table 4 provides the bore resistances computed using Equations (6) to (8) for three different grout conductivities, three different fluid flow regimes (Reynolds number = 2000 [laminar], 4000 [transi- tion], and 10 000 [fully turbulent]), three different U-tubes sizes, and three different bore diameters for locations B and C. Resistance is also computed for a double U-tube in a bore. These values were calculated with a value of kp equal to 0.42 W/(m.K). Designers can choose to use the values oflocation B (conservative), BC (average), C (risky), or Double. The most difficult parameters to evaluate in Equations (4) and (5) are the equivalent thermal resistances of the ground. The solutions of Carslaw and Jaeger (1947) require that the time of operation, bore diameter, and thermal diffusivity of the ground be related in the dimensionless Fourier number (Fo): (9) 4 g Fo = d 금 where thermal diffusivity of ground, m2/day g time of operation, days db = bore diameter, m The method may be modified to allow calculation of equivalent thermal resistances for varying heat pulses. A system can be mod- eled by three heat pulses: a 10 year (3650 day) pulse of qa, a 1 month (30 day) pulse of qm, and a 4 h (0.167 day) pulse of qst? Three times are defined as = 3650 days 1 = 3650 + 30 = 3680 days 2 = 3650 + 30 + 0.167 = 3680.167 days f The Fourier number is then computed with the following values: Fof = 4 f/db2 F01 = 4 ( f - 1)/db2 F02 = 4 ( f - 2)/db2 An intermediate step in computing the ground's thermal resistance using the methods of Ingersoll and Zobel (1954) is to identify a G-factor, which is determined from Figure 8 for each Fourier value. The algorithm proposed by Cooper (1976) provides an alternative to using Figure 7. kg R = GFof - GFOI ga k R GFol - GFO2 50 gm k R = GF02 bo gm Correlations for the values of R R and R were presented gst ga' gm' by Philippe et al. (2010) for a wide range of conditions. Ranges of the ground thermal conductivity k, are given in Table 4. State geological surveys are a good source kgd soil and rock data. However, geotechnical site surveys are highly recommended to determine load soil, rock types, and drilling conditions. (10) (11) (12) Performance degrades somewhat because of short-circuiting heat losses between the upward- and downward-flowing legs of a conventional U-bend loop. This degradation can be accounted for by introducing the short-circuit heat loss factor Fsc Equations in (4) and (5), in the following table. Normally U-tubes are piped in parallel to the supply and return headers. Occasionally, when bore depths are shallow, two or three loops can be piped in series. In these cases, short-circuit heat loss is reduced; thus, the values for Fsc are smaller than that for a single bore piped in parallel. Alternatively, Fsc can be set to 1.0 and thermal short-circuiting can be included in Equations (4) and (5) by replacing Rb with an effective borehole thermal resistance Rb (Claesson and Hellstrom 2011). As noted by Javed and Spitler (2016), Rb' * values start to be significantly different from Rb for long boreholes and low flow rates. ¦ ¦ Fse ¦ Fse ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Bores per Loop ¦ 0.036 L/(s.kW) ¦ 0.054 L/(s.kW) ¦ ¦ 1 ¦ 1.06 ¦ 1.04 ¦ ¦ 2 ¦ 1.03 ¦ 1.02 ¦ ¦ 3 ¦ 1.02 ¦ 1.01 ¦ Inc. ASHRAE, 2019 user. single for Licensed | {}
23ea9354-acc9-4f0c-82bf-f0e73dfe7115 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 35.10 Fo NUMBER FOURIER Chart Type: line G-FACTOR 0 G-FACTOR 0.2 G-FACTOR 0.4 G-FACTOR 0.5 G-FACTOR 0.8 G-FACTOR 0.9 G-FACTOR 1 G-FACTOR 2 G-FACTOR 3 G-FACTOR 4 G-FACTOR 5 G-FACTOR 6 G-FACTOR 7 G-FACTOR 8 G-FACTOR 9 G-FACTOR 10 G-FACTOR 11 G-FACTOR 12 item_01 1000000 1000000 1000000 10000000 10000000 10000000 10000000 10000000 10000000 10000000 10000000 100000000 100000000 100000 100000 1000000 1000000 1000000 Fig. 8 Fourier/G-Factor Graph for Ground Thermal Resistance (Kavanaugh and Rafferty 2014) The remaining terms in Equations (4) and (5) are temperatures. The local deep-ground temperature tg can best be obtained from local water well logs and geological surveys. A second, less accurate source is a temperature contour map, similar to Figure 9, prepared by state geological surveys. A third source, which can yield ground temperatures within 2 K, is a map with contours, such as Figure 10. Comparing Figures 9 and 10 indicates the complex variations that would not be accounted for without detailed contour maps. Selecting the temperature twi of water entering the unit is critical in the design process. Choosing a value close to ground temperature results in higher system efficiency, but makes the required ground coil length very long and thus unreasonably expensive. Choosing a value far from tg allows selection of a small, inexpensive ground coil, but the system 's heat pumps will have greatly reduced capacity and increased electric demand. Selecting twi to be 11 to 17 K higher than tg in cooling and 6 to 11 K lower than tg in heating is a good compromise between first cost and efficiency in many regions of the United States. The value for two can be selected by adding/ subtracting the temperature change through the heat pump with twi, where the temperature change is based on the flow rate and heat capacity of the water and the heat rejected/absorbed by the heat pump. A final temperature to consider is the temperature penalty tp, which is added to the undisturbed earth temperature to represent the build-up or reduction of thermal energy around each borehole over a period of forecast years. If annual cooling and heating ground loads are balanced, the temperature penalty will be zero. The tp increases the bore length (Lc, Lh) required to achieve desired performance, and tp increases for closely spaced boreholes; therefore, the designer must select a reasonable separation distance 2019 ASHRAE Handbook- HVAC Applications (SI) ![image](/image/placeholder) 6 7 16 16 HUNTSVILLE 17 FLORENCE 17 17> 16 17 18 17 16 16 17 16 GADSDEN 17 17- 18 19 17 BIRMINGHAM 16 ⑰ 18 17 18 19 19 19 TUSCALOOSA 17118 17 18 19 18~ 19 SELMA 19 20 MONTGOMERY 22 20 21 20 21 20JACKSON 20 21 DOTHAN 21 20 MOBILE 21' Fig. 9 Water and Ground Temperatures in Alabama at 15 and 45 m Depth (Chandler 1987) to balance required land area and bore length. The minimum recommended vertical bore separation distance is 6 m. The temperature penalty approximation method presented here is adapted from Kavanaugh and Rafferty (2014). The net annual heat transfer into and out of the ground qa is a key factor. At the initial design phase, 9a can be computed using estimated equivalent full-load hours (EFLHs), which are equal to the annual load divided by the heat pump capacity; final designs should use a more thorough analysis of site loads. In the EFLH method, the ground thermal load at full heat pump capacity is multiplied by the estimated EFLH values corresponding to the location, building type, and internal loads (Table 5), and these values are summed and divided by 8760 h to determine qa: qa = {capacity[(COP� + 1)/COPc] x EFLHc + capacity[(COP, - 1)/COPh] x EFLH�}/8760 h where capacity is nominal heat pump capacity, which is positive for heating and negative for cooling, in W. (13) To the extent that annual loads are proportional to peak loads, the equivalent full-load hours method provides a simple estimate of annual loads from peak loads. The EFLHs in Table 5 provide a quick means to estimate annual loads needed to size ground heat exchangers at the initial feasibility study phase of a project; the final design should use a more thorough analysis of the site loads. Because EFLHs vary with changes in both annual and peak loads, not all building parameters' effects are included in EFLHs. For instance, building operating hours change annual loads by increasing the amount of time that internal gains are at elevated levels, but they do not change the peak load. Occupancy hours can add load without increasing the installed capacity, thereby changing the EFLHs. Furthermore, changes in other parameters, Inc. ASHRAE, 2019 Ⓒ user. single for Licensed | {}
300878c2-28b7-4575-b7c1-983b8aa38aac | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Geothermal Energy 35.11 ![image](/image/placeholder) 10 WASHINGTON 10 8 MAINE NEW HAMPSHIRE 8 IDAHO MONTANA 8 MINNESOTA VERMONT OREGON NORTH DAKOTA MASSACHUSETTS- 10 8 10 RHODE 9 WISCONSIN ISLAND SOUTH DAKOTA 8 10 10 13- 10 13 MICHIGAN NEW YORK WYOMING 10 NEVADA PENNSYLVANIA 17 NEBRASKA CONNECTICUT 13 CALIFORNIA 15 IOWA ILLINOIS OHIO 입 8 NEW JERSEY COLORADO INDIANA 13 13 13 DELAWARE WEST 17 13 KANSAS VIRGINIA MARYLAND UTAH MISSOURI VIRGINIA 13 KENTUCKY NORTH 17 20 NEW MEXICO CAROLINA OKLAHOMA TENNESSEE 0 ARKANSAS 23 17 17 SOUTH 17 CAROLINA ARIZONA 17 17 20 ALABAMA 20 LOUISIANA GEORGIA TEXAS MISSISSIPPI 23 FLORIDA 23 23 23 27 Fig. 10 Approximate Groundwater Temperature (°C) in the Continental United States such as internal gains, do not necessarily scale with system capacity in the same proportion as annual load, again leading to changing EFLHs. Potential users of EFLHs must understand these sources of variability to use them effectively (Carlson 2001). Adjacent boreholes thermally interfere with each other, effectively restricting the volume of soil available to diffuse heat from/to the bore. Consider an internal bore surrounded by adjacent bores on all four sides (Figure 11). Assuming equal heat exchange from each bore, an adiabatic symmetry boundary exists at half the separation distance between each bore, Sbore2. Net annual energy that would otherwise be diffused beyond the boundary (if the bore were not surrounded by any other bore) is stored in/extracted from and, over time, results in the temperature penalty. The temperature penalty for an internal bore is computed by dividing the stored energy by the heat capacity of the soil within the rectangular prism symmetry boundary: �stored t cpS2 boreL p int (14) where Qstored energy stored (or extracted from) within adiabatic symmetry boundary, kWh k = soil volumetric capacity, kJ/(m3.K) Cp Sbore bore separation distance, m L = total bore length (either Lc or Lh), m An initial guess value is required for L and can be found using Equation (4) or (5) with a reasonable value for tp (e.g. -6 to 6°C). Values for L and tp are iterated to find the final solution. The energy that would have otherwise been stored in imaginary hollow cylinders of soil beyond the symmetry boundary is ![image](/image/placeholder) 「 7080 9 m S 7.5 m bore 6 m OO ADIABATIC SYMMETRY 4.5 m BOUNDARY 3 m ▲ 00 00 INTERNAL BOREHOLE HOLLOW CYLINDERS 00 SURROUNDING BOREHOLES Fig. 11 Representative Soil Cylinders and Adiabatic Symmetry Boundary for Heat Storage Inc. ASHRAE, 2019 Ⓒ user. single for Licensed | {}
d7f60fa5-145b-46d1-baa7-2e5f4ddfefaa | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 35.12 2019 ASHRAE Handbook-HVAC Applications (SI) Table 5 Equivalent Full-Load Hours (EFLH) for Typical Occupancy with Constant-Temperature Set Points EFLH Occupancy ¦ ¦ School ¦ School ¦ Office ¦ Office ¦ Retail ¦ Retail ¦ Hospital ¦ Hospital ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Location ¦ Heating ¦ Cooling ¦ Heating ¦ Cooling ¦ Heating ¦ Cooling ¦ Heating ¦ Cooling ¦ ¦ Atlanta, GA ¦ 290-200 ¦ 690-830 ¦ 690-480 ¦ 1080-1360 ¦ 600-380 ¦ 1380-1860 ¦ 430-160 ¦ 2010-2850 ¦ ¦ Baltimore, MD ¦ 460-320 ¦ 500-610 ¦ 890-720 ¦ 690-1080 ¦ 770-570 ¦ 880-1480 ¦ 590-300 ¦ 1340-2340 ¦ ¦ Bismarck, ND ¦ 500-460 ¦ 150-250 ¦ 990-950 ¦ 250-540 ¦ 900-810 ¦ 340-780 ¦ 730-530 ¦ 540-1290 ¦ ¦ Boston, MA ¦ 520-450 ¦ 300-510 ¦ 1000-960 ¦ 450-970 ¦ 870-760 ¦ 610-1380 ¦ 680-420 ¦ 1020-2330 ¦ ¦ Charleston, WV ¦ 440-310 ¦ 430-570 ¦ 840-770 ¦ 620-1140 ¦ 730-620 ¦ 820-1600 ¦ 550-320 ¦ 1260-2560 ¦ ¦ Charlotte, NC ¦ 320-200 ¦ 650-730 ¦ 780-530 ¦ 1060-1340 ¦ 670-420 ¦ 1350-1830 ¦ 490-180 ¦ 1990-2820 ¦ ¦ Chicago, IL ¦ 470-390 ¦ 280-410 ¦ 920-820 ¦ 420-780 ¦ 810-670 ¦ 550-1090 ¦ 640-400 ¦ 870-1780 ¦ ¦ Dallas, TX ¦ 200-120 ¦ 830-890 ¦ 520-340 ¦ 1350-1580 ¦ 440-280 ¦ 1660-2090 ¦ 310-100 ¦ 2320-3100 ¦ ¦ Detroit, MI ¦ 480-400 ¦ 230-360 ¦ 1020-970 ¦ 390-820 ¦ 900-790 ¦ 530-1170 ¦ 710-460 ¦ 870-1950 ¦ ¦ Fairbanks, AK ¦ 630-560 ¦ 26-54 ¦ 1170-1050 ¦ 64-200 ¦ 1090-930 ¦ 110-320 ¦ 930-690 ¦ 210-600 ¦ ¦ Great Falls, MT ¦ 430-360 ¦ 130-220 ¦ 890-820 ¦ 210-490 ¦ 800-680 ¦ 290-710 ¦ 640-420 ¦ 500-1210 ¦ ¦ Hilo, HI ¦ 1-0 ¦ 1360-1390 ¦ 23-13 ¦ 2440-2580 ¦ 14-8 ¦ 2990-3370 ¦ 0-0 ¦ 4060-4910 ¦ ¦ Houston, TX ¦ 130-90 ¦ 940-1000 ¦ 350-250 ¦ 1550-1770 ¦ 300-190 ¦ 1870-2290 ¦ 200-70 ¦ 2540-3320 ¦ ¦ Indianapolis, IN ¦ 480-400 ¦ 380-560 ¦ 920-840 ¦ 560-1000 ¦ 820-690 ¦ 730-1410 ¦ 640-390 ¦ 1120-2250 ¦ ¦ Los Angeles, CA ¦ 160-80 ¦ 780-910 ¦ 580-370 ¦ 1280-1670 ¦ 440-250 ¦ 1740-2350 ¦ 180-20 ¦ 2740-3770 ¦ ¦ Louisville, KY ¦ 430-290 ¦ 550-670 ¦ 830-710 ¦ 770-1250 ¦ 720-570 ¦ 1000-1720 ¦ 550-300 ¦ 1480-2690 ¦ ¦ Madison, WI ¦ 470-390 ¦ 210-310 ¦ 900-840 ¦ 320-640 ¦ 800-700 ¦ 420-900 ¦ 640-440 ¦ 680-1490 ¦ ¦ Memphis, TN ¦ 240-170 ¦ 700-830 ¦ 600-420 ¦ 1090-1350 ¦ 510-330 ¦ 1350-1780 ¦ 370-140 ¦ 1910-2680 ¦ ¦ Miami, FL ¦ 12-6 ¦ 1260-1300 ¦ 46-34 ¦ 1980-2150 ¦ 37-25 ¦ 2350-2740 ¦ 12-1 ¦ 3110-3890 ¦ ¦ Minneapolis, MN ¦ 500-420 ¦ 200-300 ¦ 950-860 ¦ 320-610 ¦ 860-720 ¦ 430-870 ¦ 700-470 ¦ 680-1420 ¦ ¦ Montgomery, AL ¦ 180-120 ¦ 840-910 ¦ 470-330 ¦ 1260-1510 ¦ 400-250 ¦ 1550-1990 ¦ 260-90 ¦ 2170-2950 ¦ ¦ Nashville, TN ¦ 320-250 ¦ 570-740 ¦ 680-590 ¦ 830-1280 ¦ 590-470 ¦ 1030-1710 ¦ 450-240 ¦ 1490-2620 ¦ ¦ New Orleans, LA ¦ 110-67 ¦ 920-990 ¦ 320-230 ¦ 1500-1720 ¦ 260-160 ¦ 1820-2240 ¦ 160-46 ¦ 2500-3280 ¦ ¦ New York, NY ¦ 440-350 ¦ 360-550 ¦ 870-790 ¦ 540-1040 ¦ 760-630 ¦ 720-1480 ¦ 590-330 ¦ 1160-2440 ¦ ¦ Omaha, NE ¦ 400-330 ¦ 310-440 ¦ 800-720 ¦ 480-820 ¦ 720-600 ¦ 610-1130 ¦ 570-360 ¦ 920-1780 ¦ ¦ Phoenix, AZ ¦ 110-65 ¦ 950-1020 ¦ 290-210 ¦ 1340-1610 ¦ 250-170 ¦ 1630-2090 ¦ 140-34 ¦ 2220-3040 ¦ ¦ Pittsburgh, PA ¦ 500-470 ¦ 300-530 ¦ 950-910 ¦ 440-920 ¦ 840-750 ¦ 600-1310 ¦ 650-420 ¦ 960-2160 ¦ ¦ Portland, ME ¦ 480-400 ¦ 190-300 ¦ 980-880 ¦ 310-630 ¦ 870-710 ¦ 410-900 ¦ 690-420 ¦ 700-1520 ¦ ¦ Richmond, VA ¦ 410-270 ¦ 630-730 ¦ 820-660 ¦ 880-1310 ¦ 710-520 ¦ 1110-1770 ¦ 530-250 ¦ 1650-2760 ¦ ¦ Sacramento, CA ¦ 360-220 ¦ 680-850 ¦ 990-640 ¦ 1080-1430 ¦ 830-480 ¦ 1460-2020 ¦ 540-120 ¦ 2250-3180 ¦ ¦ Salt Lake City, UT ¦ 540-520 ¦ 410-710 ¦ 1060-1040 ¦ 510-1090 ¦ 930-830 ¦ 660-1520 ¦ 720-440 ¦ 1060-2470 ¦ ¦ Seattle, WA ¦ 650-460 ¦ 260-460 ¦ 1370-1270 ¦ 440-1200 ¦ 1170-960 ¦ 710-1860 ¦ 850-360 ¦ 1340-3270 ¦ ¦ St. Louis, MO ¦ 400-280 ¦ 460-550 ¦ 800-710 ¦ 680-1100 ¦ 700-570 ¦ 850-1500 ¦ 550-320 ¦ 1260-2330 ¦ ¦ Tampa, FL ¦ 58-35 ¦ 1050-1110 ¦ 190-140 ¦ 1800-2000 ¦ 160-100 ¦ 2170-2580 ¦ 90-22 ¦ 2910-3710 ¦ ¦ Tulsa, OK ¦ 300-240 ¦ 580-770 ¦ 620-560 ¦ 830-1300 ¦ 540-450 ¦ 1030-1730 ¦ 410-220 ¦ 1470-2630 ¦ Source: Carlson (2001). Notes: 1. The ranges in values are from internal gains at 6.5 at 27 W/m2. 2. Operating with large temperature setbacks during unoccupied periods (effectively turning off the system) reduces heating EFLHs by 20% and cooling EFLHs by 5%, T max �stored = cp L r3-r 글 (15) r = Shore 2 where ro cylinder, m = outer radius of hollow soil ri = inner radius of hollow soil cylinder, m maximum considered radius rmax ち = soil temperature change at average radius r = (ro +ri)/2, °C Note that, because there is some overlap of the innermost hollow cylinder with the symmetry boundary, the impact of the overlap is neglected. The value for r is increased until the temperature rise max in the outermost cylinder is negligible (<0.3 K); beyond this Equations relating EFLH to Heating and Cooling Degree Days allowing calculation of EFLH for locations other than those listed here can be found in Carlson (2001). distance, the storage effect is offset with evaporative cooling and moisture recharge mechanisms. Porous soil with high moisture con- whereas low-porosity soil may require tent may require I'max = Sbores as much as r = 5 x Sbore (Kavanaugh and Rafferty 2014). For a max nominal configuration (Figure 11) with Sbore m, four hollow of 6 cylinders with a 1.5 m width, r⌀ - r⌀ gives sufficiently resolved results; other separation distances may require different numbers and width of cylinders. The average soil temperature change for each cylinder is computed at the average radius, r= (ro + r⌀/2, using the line source method (Carslaw and Jaeger 1959; Ingersoll and Zobel 1954; Kavanaugh and Rafferty 2014): qaI X tr = 2 k L g (16) Inc. ASHRAE, 2019 user. single for Licensed | {}
d0b22d1b-c806-45a5-884c-83f1231ac4da | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Geothermal Energy 35.13 where the I(X) function is formed from the exponential integral; an approximation with less than 1% error for X < 0.7 is 1 X2 X4 I X = 늘 Ei - X2 In + - - x 2 8 2 where is Euler's constant (0.57722....), Eiis the exponential inte- gral, and the X term is 1 r X = 2VFo 2 V (17) where (18) r = (ro + r)/2, average radius of soil cylinder, m = time duration, days The value for is the designer's choice and can be based on expected groundwater movement; 2 (from the preceding Fourier number calculations, value is usually about 10 years) can be used for minimal groundwater movement and vertical percolation of water through the borefield, whereas 365 days can be used for more sub- stantial water movement. Finally, tp is calculated by prorating tp,int based on the number of bores with a particular adjacency: interior, side, comer, midrow, and end (Figure 12), as well as accounting for heat diffusion at the bottom of the borefield: Nint corner midrow end + 0.75Nside + 0.5N + 0.5N + 0.25N + N + N + N + N + CfHoriz t = N int side corner midrow end p x t. p int where (19) Nint = number of interior boreholes, surrounded by four other bores Niside by three other bores = number of side boreholes, surrounded Ncorner = number of corner boreholes, surrounded by two other bores Nmidrow = number of boreholes in middle of row, surrounded by two other bores (only for borefield with a single row) Nend by one other bore (only for = number of end boreholes, surrounded borefield with a single row) CfHoriz = bottom diffusion factor The bottom diffusion factor is the ratio of surface area of the sides and bottom of the borefield to the surface area of the sides: 2Lbore field Lfield + WfieldLfield W + CfHoriz 2Lbore Wfield Lfield + where the individual bore length Lbore is found by dividing L by the number of bores. The borefield length and width are (20) Lfield = Sbore N long - 1 W = Sbore wide - 1 N field (21) (22) bores in the length direction and Nwide where the borefield has N long bores in the width direction (Figure 12). Temperature Penalty Uncertainty. Calculating the temperature penalty is one of the more uncertain parts of heat exchanger length selection. Temperature penalties computed using the concentric cylinder source method presented here (Kavanaugh and Rafferty 2014) differ significantly from those obtained using the g-function approach (see the section on Alternative Sizing Method, after Example 1), as discussed by Bernier et al. (2008). The g-function method accounts for the ground heat conduction with more rigor; it includes both radial and axial heat transfer, rather than only radial heat transfer, and computes the temperature penalty from interfering boreholes at the borehole wall, rather than using the average soil temperature change. Both approaches only consider conductive heat transfer and therefore represent worst- case scenarios, where the actual temperature change is usually mitigated by groundwater recharge (vertical flow), groundwater movement (horizontal flow), and evaporation (and condensation) of water in the soil. Further research is needed to understand which ground heat exchanger sizing method best captures the temperature penalty related to long-term operation in applied systems. Note that, despite the uncertainty in long-term temperature penalty, the concentric cylinder source method has been used in many successful installations of GSHP systems. Groundwater movement strongly affects long-term temperature change in a densely packed bore field (Chiasson et al. 2000a). A related factor is the evaporative cooling effect experienced with heat addition to the ground. Although thermal conductivity is somewhat reduced with lower moisture content (see Table 2), the net effect is beneficial in porous soils when water movement recharges the ground to original moisture levels. A similar effect may be experienced in cold climates when soil moisture freezes and the heat of solidification mitigates excessive temperature decline. Because these effects have not been thoroughly studied, the design engineer must establish a range of design lengths between one based on minimal groundwater movement, as in very tight clay soils with poor percolation rates, and a second based on the higher rates characteristic of porous aquifers. Kavanaugh and Kavanaugh (2012a, 2012b) examined ground heat exchanger performance in 40 commercial buildings with vertical ground heat exchangers and between 5 and 25 years of operation. They calculated maximum approach temperature (difference between average loop temperatures twi and two and initial ground temperature tg) for all of the buildings; higher approach temperatures as years of operation increased would indicate an increase in ground temperature and raise concern about the expected life of ground heat exchangers with imbalanced cooling loads compared to heating loads. In fact, the data suggested that older GSHP systems had lower approach temperatures. Results were not adjusted for many important factors such as vertical bore length, ground thermal properties, and vertical bore separation distance. Newer systems tended to have slightly shorter ground heat exchangers, but this was offset somewhat by the older systems' tendency to have smaller vertical bore separation distances and lower-conductivity grout and fill. Of the loops with the largest approach, three of the newer systems had vertical bore lengths less than 10.4 m/kW. Two systems with long loops but large approach temperatures had low thermal conductivity grout (0.66 W/[m.K]], 4.6 m bore separation, and indoor air temperatures below 21°C. The study's data set is small, and significant long-term temperature change cannot be excluded at this point. Although Chart Type: line Corner_bore Internal_bore Side_bore item_01 4N_value 6N_value 8N_value Fig. 12 Borefield with (A) 20 Boreholes, Nwide long = 5, N = 4 and (B) 4 Boreholes, Nwide = 1, Nlong = 4 (i.e., Single Row) Inc. ASHRAE, 2019 user. single for Licensed | {}
6425bf04-d0e0-4719-8b37-d5c1e8e90c1d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 35.14 2019 ASHRAE Handbook- HVAC Applications (SI) much more field study is desirable, the absence of any significant trend of increased ground temperature (noted by elevation of maximum approach temperature) with increased years of GSHP operation suggests that long-term ground temperature change is not prevalent in properly designed GSHPs. Results from this project cannot be applied to long-term temperature decline in which the amount of heat removed from the ground in heating far exceeds the heat rejected in cooling. In cold climates the heat capacity available at the freeze point of water is significant, but the impact on grout thermal and physical properties also needs further field study. Example 1. Size a vertical ground-coupled heat pump system for a six- zone classroom addition in Atlanta, GA. The addition has a peak cooling (block) load 91c of 72 kW and a peak heating (block) load 9th of 47 kW. The design monthly part-load factor PLF m is 0.28. = 18°C Ground conductivity Ground temperature 18kg and diffusivity ag = 2.4 W/(m-K), 0.1 m2/day Bore fill conductivity k grt = 1.7 W/(m-K) Vertical U-tube = 32 mm, DR11, HDPE, 125 mm borehole diameter 2 X 10 grid (20 vertical bores) with Sbore = 6 m separation Bores per loop = 1, flow is 0.054 L/(s-kW), so Fsc = 1.04 Reynolds number = 4000 (transition flow) Heat pump inlet and outlet temperatures twi and two = 30 and 36°C Heat pump capacity = 72 kW (maximum of peak block cooling and heating loads) Heat pump cooling and heating efficiency (COPC, COPh) = 4.2, 4.4 10 year (3650 day), 1 month (30 day), and 4 h (0.167 day) heat pulse analysis: EFLH。 = 760 h, EFLH, = 245 h (Table 5) COP + 1 4.2 + 1 qcond = (Qlc + W⌀ = 91c x =-72 kW x COP c 4.2 = -89.1 kW COPh + 1 4.4 - T = (QIh - Wh) = 9th x = 47 kW X = 36.3 kW 9evap COPh 4.4 COPc + 1 COPh - 1 capacity EFLH。 + capacity EFLHh COP COP h Inc. ASHRAE, 2019 user. single for Licensed qa 8760 4.2 + 1 4.4 1 -72 760 + 72 245 4.2 4.4 6.2 kW 8760 Fof= (4 X 0.1 m2/day x 3680.167 days)/(0.125 m)2 = 94,200; from Fig. 8, GFof= 0.97 F01 = [4 X 0.1 m2/day X (3680.167 - 3650) days]/(0.125 m) 2 = 772; from Fig. 8, GFol = 0.60 F02 = [4 x 0.1 m2/day X (3680.167 - 3680) days]/(0.125 m)2 = 4.28; from Fig. 8, GFo2 = 0.21 - 6200 0.154 - 89 100 0.11 + 0.28 0.163 + 1.04 0.088 Le = 30 + 36 18 - -0 2 For nonporous soils, a temperature penalty is computed. The annual heat imbalance qa is applied for the 10 years plus one month time dura- tion (3680 days). For the internal bore temperature penalty, the average temperature change for four (the temperature change of a fifth cylinder is less than 0.3 K, so it is not considered) 1.5 m wide hollow cylinders extending beyond the symmetry boundary are computed, beginning with the inner hollow cylinder (ri = Sbore/2 = 6/2 m = 3 m, r⌀ = ri + 1.5 m = 4.5 m, and r = [ro + r]/2 = [4.5 + 3]/2 = 3.75 m): = 1528 m = 1528 m/20 bores = 76 m/bore r 3.75 X= = 0.098 2 2 시 0.1 3680 g For r = 3.75 m, 1 X2 X4 I(X) = ln + - - x 2 8 2 1 0.0982 0.0984 0.5772 = ln + = 2.042 0.098 2 8 2 Repeating for r = 5.25 m: X = 0.137, I(X) = 1.710. Repeating for r = 6.75 m: X = 0.176, I(X) = 1.464. Repeating for r = 8.25 m: X = 0.215, I(X) = 1.271. Rga = (0.97 - 0.60)/2.4 W/(m-K) = 0.154 (m-K)/W For the first iteration, a small value of -0.6 K is used as an initial guess, because the building is slightly cooling dominated (recall that negative values are used for cooling loads): - 6200 0.154 - 89 100 0.11 + 0.28 0.163 + 1.04 0.088 Lc 30 + 36 18 - -0.6 2 = 1592 m, or Lbore = 1592 m/20 bores = 80 m/bore So the average temperature changes of the hollow cylinders are, for the hollow cylinder with r = 3.75 m, Repeating for r = 5.25 m: tr=0.44 K. Repeating for r = 6.75 m: tr= -0.38 K. Repeating for r = 8.25 m: tr = -0.33 K. qaI X -6200 2.042 tr = = -0.52°C 2 kg Lc 2 2.4 1592 The volumetric heat capacity is cp = kg/ g = 2.4 W/(m·K)/(0.1 m2/ day) X 24 h/day = 576 W·h/(m3·K), and the energy stored in the hollow cylinders is ¦ r⌀s ri ¦ cpLe (r.2-r2) tr ¦ Qstored ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 3.0 m, 4.5 m ¦ 576 x 1592 (4.52 - 3.02)(-0.52) ¦ -17.0 x 106 W·h ¦ ¦ 4.5 m, 6.0 m ¦ 576 x 1592 (6.02 - 4.52)(-0.44) ¦ -20.0 x 106 W·h ¦ ¦ 6.0 m, 7.5 m ¦ 576 X 1592 (7.52 - 6.02)(-0.38) ¦ -22.0 X 106 W·h ¦ ¦ 7.5 m, 9.0 m ¦ 576 x 1592 (9.02 - 7.52)(-0.33) ¦ -23.3 x 106 W·h ¦ ¦ ¦ ¦ -82.3 x 10° W·h ¦ R - (0.60-0.21)/2.4 W/(m-K) = 0.1625 (m-K)/W gm R = 0.21/2.4 W/(m-K) = 0.088 (m-K)/W gst Rb = 0.11 (m-K)/W (average of Locations B and C, interpolated between kgrout = 1.4 and 2.1 W/(m·K), transition flow for Re = 4000). The required total bore length, assuming no long-term ground temperature change (tp = 0) caused by moisture evaporation and subsequent groundwater recharge through porous soil is Qstored -82.3 106 tp,int = = -2.5°C cpSboreLc 576 62 1592 2Lbore Wfield + Lfield + Wfield Lfield CfHoriz = 2Lbore Wfield + Lfield 2 80 6 + 54 + 6 54 = 1.034 2 80 6 + 54 Lfield = Sbore(Nlong - 1)=6m (10 - 1) = 54 m Wfield - 1)=6m (2-1) = 6 m = Sbore(Nwide | {}
fbefea30-f418-40e2-88ae-ba70f0a13066 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Geothermal Energy 35.15 Nint + 0.75Nside + 0.5Ncorner re tp int Nint corner CfHoriz + N + Nside 0+ 0.75 16 + 0.5 4 -2.5 = -1.69°C 0 + 16 +4 1.034 For the second iteration, this tp is substituted back into the equation for Lc, which yields 1722 m, and a new corresponding tp is calculated, -1.56 °C. The solution is fully converged after four iterations with Lc = 1708 m Lbore = 85 m tp = -1.58°C Repeat the process using Equation (5) to find the bore length for heating Lh The design bore length is the larger value of Lc and Lh Alternative Sizing Method. The traditional concentric cylinder source design method can be solved using a relatively simple pro- cedure, because the effective ground thermal resistances R R gm, ga, and R are calculated independent of borehole length. In contrast, gst the g-function method, discussed here and used in some software design tools, is more complex and requires a more involved iteration process to evaluate the design length. The benefit of using the g- function method is that it accounts for both radial and axial conduc- tion, and effectively applies the long-term temperature penalty to the borehole wall (rather than using the average soil temperature change). Thermal response factors, also known as g-functions (not to be confused with the G-factor) may be used as an alternative to calculate the ground thermal resistance required in Equations (4) and (5). The concept was first introduced by Eskilson (1987) and extended to short-time steps by Yavuzturk and Spitler (1999). The g-functions give a relation between the heat extracted (or rejected) from the ground per unit borehole length qL and the borehole wall temperature Tb. The borehole wall temperature is given by (23) qL Tb = Tg - g(t/ts, rb/H, B/H) 2 kg where g represents the g-function. As shown in Equation (23), the g- function depends on three non-dimensional parameters: B/H, the ratio of the borehole spacing over the borehole length; rb/H, the ratio of the borehole radius over the borehole length; and t/ts, a nondi- mensional time where ts is a characteristic time ( = H2/9 g). Typical g-functions curves are presented in Figure 13 for a 3 x 2 bore field. The g-function curves are presented graphically in Figure 13 as a function of ln(t/ts) for six bore field spacings (B/H) and for a value of r⌀H = 0.0005. The curve for B/H= corresponds to the g-function of a single borehole. One of the major advantages of these nondimensional curves is that they apply to any 3 2 bore field. Eskilson (1987) provides g-function curves for a number of bore field geometries. Design software tools that use the g-function concept have a relatively large data set of g-function curves to choose from. Eskilson (1987) calculated g-functions using two- dimensional transient finite-difference equations on a radial-axial coordinate system for a single borehole in homogeneous ground. The temperature fields from a single borehole were superimposed in space to obtain the response from a borehole field with a certain configuration. Example 2. Boreholes in a 3 X 2 bore field have the following characteris- tics: rb = 0.05 m, H = 100 m, and B = 5 m. The undisturbed ground temperature is 15°C, the thermal conductivity is 1.5 W/(m · K), and the thermal diffusivity is 1.12e-6 m2/s. What is the resulting borehole wall temperature after 10 years of heat extraction at an average rate of 5 W per metre of bore? Evaluation of the three non-dimensional parameters lead to: rb/H = 0.0005, B/H = 0.05, ts = 31.5 years and ln(t/ts) = -1.15. According to X-Axis: ln(t/t_s) Y-Axis: g(t/ft2/H = 0.0005, D/H = 0.027) Chart Type: line Red Orange Yellow item_01 0.05Diffability (dB) 0.0Diffability (dB) 0.15Diffability (dB) Fig. 13 Typical g-Function Curves for 3 x 2 Bore Field Figure 13, the resulting g-function is 12.3. Using Equation (23), the borehole wall temperature is then equal to 8.5°C. The g-functions can be used to determine the design length of a bore field. One possible approach is to use Equations (4) and (5) but with two modifications. First, when g-functions are used, thermal interference among boreholes is implicitly accounted for and tp can be eliminated. Second, the values of R R and R are now gm' gst based on g-functions. Hence, Equations (㉔ to (26) take the follow- ing forms: g - g 5-5 ty R ga 2 kg g ターケ g 5-12 R gm 2 kg (24) g 5 「2 R gst 2 k g is the g-function evaluated at ln[(tx - ty)/ts] for a where g [ Is field and B/H ratio. Note that determining L (i.e., nb x H, given bore where nb is the number ofboreholes) is an iterative process because R R and R depend on H, which is unknown beforehand. gst ga' gm' Thus, software tools are often required to accomplish this task. Because g-functions account for 3D heat transfer in the borefield, they are considered to be more accurate than the G-factors, which derive from a radial-only heat transfer model. Borehole thermal capacity can be accounted for by using the short-time-step g- functions (Yavuzturk and Spitler 1999). (25) Example 3. A building has a cooling block load of 52 kW with a corre- sponding value of qcond = -66.0 kW. The annual ground imbalance qa = -3.0 kW, PLF 72 0.30, and Fsc= 1.0. The 3 X 2 bore field has the fol- = lowing characteristics: rb = 0.05 m, B = 5 m, and Rb = 0.1 (m· K)/W. The undisturbed ground temperature is 10°C, the thermal conductivity is 3.34 W/(m · K), and the thermal diffusivity is 1. 12 X 10-6m2/s. Calcu- R and Rgst late the equivalent thermal resistances R ga' gm, for three consecutive heat pulses of 10 years, 1 month, and 6 hours and the total required length if the maximum mean fluid temperature in the borehole is to be kept below 35°C. (26) Inc. ASHRAE, 2019 user. single for Licensed From the problem statement, t = 3680.25 days, 12 = 3680 days, and t1 = 3650 days. After iterations, this leads to g = 12.34, g = 0:116 3.99, and g = 1.55; and R = 0.398 (m · K)/W, Rgm 品 (m·K)/W, and R 2割 = 0.074 (m·K)/W; and | {}
8320a703-6a92-4533-a4b4-d33b10447c1d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 35.16 -3000 0.398 - 66 000 0.1 + 0.3 0.116 + 0.074 Lc = = 600 m 10 - 35 Thus, 100 m per bore is required with a borehole spacing of 5 m. This represents a length of 1 1.52 m per kilowatt. Simulation of Ground Heat Exchangers After the design length has been determined, it is often necessary to evaluate the outlet fluid temperature of a bore field as a function of time, generally on an hourly basis, and estimate the annual heat pump energy consumption. Energy simulation can be used to compute this temperature (they can also be used iteratively to assist in sizing the ground heat exchanger). Some energy simulation programs use the duct ground storage (DST) model introduced by Hellstrom (1989) to evaluate the outlet fluid temperature of a bore field as a function of time. Yavuzturk and Spitler (1999) describe the calculation method behind the DST model. The DST model calculates the transient thermal process in densely packed borehole fields. The boreholes are assumed to be evenly distributed within a cylindrical storage region in the ground. Although the DST model was originally intended to simulate borehole thermal energy storage (BTES) systems, it has been used to simulate ground source heat pump systems. Other energy simulation programs have a g-function-based routine to evaluate the outlet fluid temperature of a bore field as a function of time (Fisher et al. 2006; Liu 2008). The following analysis is intended to give only the salient features of an hourly simulation based on g-functions. As an example, assuming that Fsc = 1 and that the borehole length and the inlet fluid temperature are known, and that the heat transfer rates for three consecutive time intervals (0 to t1, t1 to t2, and ち to t3) are given by Q1, Q2, and Q3, then, using temporal superposition, the mean fluid temperature at the end of the third time interval is given by 21 g 0 g + Q2 g ターム -g 13-12 13 -12 + Q3g 「3 なった」 Tm T g 2 kgL Q3Rb L + (27) with Tm = (Twi + Two)/2. Based on the work of Yavuzturk and Spitler (1999), Equation (27) can be generalized for n time steps as follows: n Qi - Qi _ 1 tn ti_ 1 rb B QnRb Ig 2 k L ts L Tm = - g 'H'H - i=1 g Solving Equation (28) can be computationally intensive if the number of time steps is large, because there is no recurrence in the summation term. In other words, the calculations performed at time step n - 1 cannot be used at time step n, and the ground loop loading history must be updated at each time step. Load aggregation is typically used to reduce the number of terms in the summation without sacrificing accuracy. It is based on the fact that recent ground loads have a more significant effect on the current mean fluid temperature than distant ground loads. For example, in the case of hourly simulations, the determination of Tm at the end of a year would require a summation of 8760 hourly terms according to Equation (28). One possible alternative is to aggregate (i.e., average) the ground loads of the first 8000 hours, then aggregate the next 730 hours and keep intact the last 30 hours. The summation term would then be reduced to 32 terms. Other aggregation schemes have been proposed by Bernier et al. (2004), Liu (2005), and Yavuzturk and Spitler (1999). 2019 ASHRAE Handbook-HVAC Applications (SI) Hybrid System Design The design methods described previously size the ground loop for the larger of the heating or cooling loads, including a temperature penalty for the amount of imbalance (which can be large in severe climates). An alternative approach for imbalanced buildings is to partially balance the load on the ground, both at peak and annual scale, by adding a supplemental device to help meet the larger of the two peak loads. This is a hybrid geothermal (or hybrid ground-coupled) system. Hybrids can provide several benefits for buildings with a load imbalance. The biggest economic effect is in decreasing the ground heat exchanger size/ cost. First-cost savings have been reported of 6 to 16% of total HVAC system cost, with little consequence reported on operating cost (Hackel and Pertzborn 2011; Singh and Foster 1998) because the HVAC systems operates for the vast majority of the year at a fraction of peak design. More balanced loads resulting from hybrids can reduce the long-term ground temperature penalty associated with multiyear operation. In most U.S. commercial buildings, the cooling load is dominant both annually and at the peak because of high internal loads, ventilation heat recovery, and good building envelopes. Heat from compressors, pumps, and fans also plays a factor; in heating mode, this heat is delivered to the building, so less heat is required from the ground. As a result, achieving annual thermal balance requires heat pumps in a geothermal system to operate in heating mode 1.6 to 1.8 h for every hour in cooling. The ideal configuration of the ground heat exchanger and sup- plemental cooling device in a hybrid depends on many factors, such as climate, building peak load, and building annual loads. Carefully analyze which approach may work best for a specific building. One common configuration for cooling-dominated systems, a series hybrid, is shown in Figure 14A. This approach could also be taken with a closed-circuit cooling tower (i.e., fluid cooler) downstream of the ground heat exchanger (GHX). In general, it is most effective to place the lower-temperature heat sink downstream; an energy model can help determine which order most often results in this scenario throughout the year. As a rule of thumb, in drier climates with warmer ground (e.g., desert southwestern United States) the tower is almost always the lower-temperature sink, whereas in humid cli- mates with moderate-temperature ground (e.g. southeastern United States), the ground is often the lower-temperature sink. The hybrid can also be configured in parallel, as shown in Figure 14B, which is especially desirable ifthe ground heat exchanger is small in compar- ison to the building peak cooling load (a series system in this example would require a more complex partial GHX bypass). In either case, there are two guidelines for design and operation of hybrid systems: (28) · A valve can be used to bypass the ground heat exchanger when the system is balanced; a dead band of 13 to 24°C can be used for this purpose. This valve can be three-way as shown, or two-way where appropriate. · Cooling towers are optimal when they are oversized, use a variable-speed fan, and minimize fan speed across cells. Control of a cooling-dominated hybrid depends on the configu- ration. If equipment is placed as shown in Figure 14A, the temperature downstream of the tower can be used to control the use and speed of the tower based on a high limit (some additional sav- ings are possible if the tower is controlled by the t between entering fluid and ambient wet-bulb temperatures, though this method depends on a difficult measurement of wet bulb). If the tower is located upstream of the ground heat exchanger, the tem- perature exiting the tower and the ground heat exchanger should both be used in tower control (to ensure the ground is not being cooled). For parallel configurations (Figure 14B), one practical tower control sequence bases tower operation on a calculation of the Inc. ASHRAE, 2019 user. single for Licensed | {}
cd93b913-0dca-4d77-826e-a97a2f192e76 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Geothermal Energy 35.17 ![image](/image/placeholder) SUPPLEMENTAL COOLING SUPPLEMENTAL COOLING DEVICE(S) DEVICE(S) VARIABLE-SPEED VARIABLE-SPEED (e.g., FLUID ▷ (e.g., FLUID ▷ PUMPS (Size at least PUMPS (Size at least COOLER) COOLER) one part load) one part load) > ④ △ 8 HEAT HEAT PUMPS PUMPS DEVICES COULD BE IN OPPOSITE ORDER GROUND GROUND HEAT HEAT EXCHANGER EXCHANGER A B Fig. 14 Hybrid System Configuration Options, (A) Series and (B) Parallel average of fluid temperature entering the heat pumps over the pre- vious week (Xu 2007). Xu also suggests a strategy for controlling the parallel three-way valve. For hybrid systems that require cooling towers, design also needs to consider water efficiency. Proper controls, as discussed previously, are a good start in minimizing water usage. Sequences can include a stage of cooling in which the spray pump is off (for when ambient temperatures are moderate). If the tower is run to precool the ground, this should be done carefully (Pertzborn et al. 2012) to avoid overusing the tower, which could result in significant energy and water penalties. Finally, operators should still follow the fundamental guidance for efficient tower operation (see Chapter 40 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment). A heating-dominated hybrid with a boiler instead of a cooling tower can use a series configuration, with the boiler downstream of the loop (because of the boiler's high temperature output). The boiler is ideally controlled based on the temperature leaving the heat pumps. Sizing hybrid components is a bit more complex than standard systems. For cooling dominated hybrids, Kavanaugh and Rafferty (2014) suggest that heat exchanger length for heating Lh be determined using Equation (5) with heating-mode loop temperatures twi and two as low as possible to minimize Lc. A tower with an isolation heat exchanger is sized to meet the capacity difference between the required cooling length Lc from Equation (4) and the heating length Lh Kavanaugh (1998) revised this method to include an additional iteration to size the ground heat exchanger only after estimating the annual heat rejection from the tower: qtower(rated L/min) = L/minsystem(Lc - Lh))/Le, where Lc is calculated from Equation (5) but based on reduced EFLHc to account for tower operation rejecting an estimated amount of the annual load. The strategy suggests eliminating long-term ground temperature change with additional tower operation. A more detailed study (Hackel et al. 2009) included assumptions about typical installation and operating costs to demonstrate an optimized design strategy for cooling dominated hybrids. Based on life-cycle cost, this approach was roughly attractive whenever the peak heating load was less than 80% of the cooling load; savings increased logarithmically as the ratio decreased below 80%. A variety of cases were modeled, and the simplified best-fit regression for the hybrid ground heat exchanger length Lhyb in a cooling-dominated scenario was found to be proportional to heating load: Lhyb = C1x qw(tg- two) (29) where C1=147 (m · K)/kW, at k =2.4 W/(m ·K). For other ground conductivities, the change in ground heat exchanger size is approx- imately inversely proportional to the change in conductivity. In choosing two, Hackel et al. (2009) also suggest in cooler climates it is often economical to include antifreeze in the system and allow the entering fluid temperature to drop to 2°C or lower. The supplemen- tal cooling device (closed-circuit tower) should then be sized to meet the fraction of the cooling load that this smaller hybridized ground heat exchanger cannot. The study suggests that the tower should even be oversized slightly and its fan put on variable-speed control, to achieve optimal performance. Furthermore, tower sizing should be completed using the local peak wet-bulb and design enter- ing fluid temperature for the hybrid. This basic strategy of sizing hybrids was found to be valid for a wide range of economic scenarios. This economically justifies the general concept laid out in Kavanaugh (1998); however, results showed that it is generally not economically optimal to balance the load on the ground, and some increase in ground temperature can be accepted. Preliminary research showed that running the tower at night or in winter before there was significant cooling load (precooling the ground) to balance the ground load is not always necessary, and if done without care (i.e., in-depth energy analysis) could possibly lead to increased energy consumption (Pertzborn et al. 2012). Regardless of the calculation method used, detailed building load calculation is critical when sizing and configuring a hybrid, to determine the impacts of heating and cooling loads across time scales from peak to annual. Further refinement of hybrid sizing (and control) can be done through energy simulation software, including some of the design software mentioned earlier, as well as a tool created as a result of ASHRAE research project RP-1384 (Hackel et al. 2009). Building energy simulation can estimate loads at every hour of the year, establishing better understanding of annual ground loads as well as the load sharing between ground heat exchanger and supplemental device. Heating-Dominated Hybrids. These hybrids are needed in only very cold climates. In heating-dominated buildings in such climates (i.e., with approximately twice as much annual heating load as cool- ing load), however, a heating-dominated hybrid could decrease the size of the ground heat exchanger. Optimally, the ground heat exchanger is sized to meet the cooling load and a supplemental device meets the remaining heating load through a supplemental heat coil on the ground-coupled fluid loop. Coil energy could be supplied Inc. ASHRAE, 2019 user. single for Licensed | {}
3cab69ca-5b9c-46b7-b412-a146a4d4e9dc | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 35.18 2019 ASHRAE Handbook-HVAC Applications (SI) ![image](/image/placeholder) TWO OR THREE LOOPS 32 mm PER CLASSROOM ⑧ 。 TWO BALL VALVES RETURN SUPPLY 0.06 kW CIRCULATOR PUMP HEAT PUMPS DIFFUSER CLASSROOM CLASSROOM CLASSROOM CORRIDOR CLASSROOM CLASSROOM CLASSROOM : Fig. 15 Unitary GCHP Loops with On/Off Circulator Pumps by gas boiler, solar panels, electric resistance, or another source. Sev- eral things need to be considered if using this approach: · The potentially high temperatures of the heating coil are not COV- ered by typical ground heat exchanger warranties. · Controls must be maintained correctly. Place boiler in series, downstream of ground heat exchanger, with control ofboiler and ground heat exchanger coordinated so that heat is never rejected to the ground while the boiler operates (very little of such heat would be recovered). · The heat pumps operate whenever heating is needed, even though a high-temperature coil is also operating, reducing efficiency. An alternative strategy for heating dominated buildings that poses some advantages is to simply remove some loads in the build- ing from the ground-coupled loop and serve them by boilers, solar panels, or some other source which provides high enough tempera- tures to heat without added heat pump energy. Baseboard, unit heaters, and preheat coils can be good applications for this approach. This may alleviate some of the complications with boiler hybrids discussed previously. Pump and Piping System Options Loop design can have a substantial effect on both pumping power requirements and system installed cost. A GSHP survey (Caneta Research 1995a, 1995b) reported that installed pumping elect/kW of heat pump power varied from 0.0085 to 0.045 kW therm power. This represents 4 to 21% of the total demand of typical GSHP systems and up to 50% of the total energy for some pump control schemes. Table 6 gives a recommended set of guidelines for minimizing the power of closed-loop GSHPs and maximizing system efficiency. Good grades (Table 6) can be obtained by minimizing extensive piping arrangements with long interior and exterior piping runs, high-head-loss fittings, valves, and control devices. Designers must compare the costs and advantages of large central piping loops and larger pumps with those of multiple smaller loops and smaller pumps. Pumping rates greater than 0.05 L/s·kW in closed- loop systems result in marginal equipment capacity gains in modern water-to-air heat pumps, and typically decrease overall system efficiency. Kavanaugh et al. (2002) found the total cost of vertical GCHP ground-loop systems (including headers) ranged from $19 to $82 per metre of vertical bore. The cost of headers is a significant portion of the total and in many cases exceeded the cost of the vertical bore. The savings in vertical loop costs because of central systems' load diversity often is not warranted because of the increased cost of large-diameter piping networks connecting equipment inside the building and below-grade circuits connecting exterior ground heat exchangers. In low-rise buildings with large footprints, such as a school, multiple unitary loop systems (Figure 15) are an effective option to offset the high cost of central interior piping and ground-loop header costs. Although the total length of vertical bore for unitary systems is greater than for central loop systems, the high cost of interior piping, exterior headers, and valve vaults often offsets the bore cost savings. Additionally, pump demand is substantially reduced in the unitary system because of the short header runs, so low-wattage on/off circulator pumps are suggested. A compromise in applications with significant load diversity is to group ground heat exchangers into multiple smaller subcentral loops in different areas of the building (Figure 16). Subcentral loops can be served by on/off circulator pumps located on each heat pump if a Inc. ASHRAE, 2019 user. single for Licensed | {}
2d4fbb0a-5e2b-4d67-91a5-10a11bc79338 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Geothermal Energy 35.19 ![image](/image/placeholder) HEAT PUMP 0.06 kW CIRCULATOR GROUND LOOP TWO BALL VALVES CHECK VALVE 。 。 。 。 。 DIFFUSER コ SUPPLY HEAT PUMPS RETURN 。 CLASSROOM CLASSROOM CLASSROOM CORRIDOR CLASSROOM CLASSROOM CLASSROOM 。 。 。 。 Fig. 16 Subcentral GCHP Loop with On/Off Circulator Pumps ![image](/image/placeholder) GROUND LOOP SUPPLY AND RETURN CENTRAL LOOP FIELD 16 SUBHEADER SETS EACH WITH 10 VERTICAL BUILDING SUPPLY U-TUBE GROUND LOOPS AND RETURN VARIABLE- OR CONSTANT- SPEED PUMP PIPING PUMP ROOM MAIN HEADERS VAULT SECONDARY PUMP ↓ CENTRAL 1 PIPING LOOP IN BUILDING AUXILIARY PUMP PRIMARY OR PRIMARY SECONDARY PUMP PRIMARY/SECONDARY PUMP PIPING Fig. 17 Central Loop GCHP Table 6 Guidelines for Pump Power for GSHP Ground Heat Exchangers ¦ Installed Pump Power ¦ Grade ¦ 0.05 L/s.kW coolb kPa ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ kW pump/100 kW cool ¦ Grade ¦ 0.05 L/s.kW coolb kPa ¦ ¦ < 1.6 ¦ A ¦ < 138 ¦ ¦ 1.1 to 1.6 ¦ B ¦ 138 to 206 ¦ ¦ 1.6 to 2.1 ¦ C ¦ 206 to 275 ¦ ¦ 2.1 to 3.2 ¦ D ¦ 275 to 413 ¦ ¦ > 3.2 ¦ F ¦ > 413 ¦ Source: Kavanaugh and Rafferty (2014). check valve is installed on each heat pump to prevent reverse water circulation through idle units. Figure 17 is an example of a central loop that can effectively reduce the cost of the required vertical bore in buildings with higher load diversities. The central ground heat exchanger consists of several subheader sets, each having 6 to 20 vertical U-tube heat exchangers. The subheaders are gathered into a valve manifold located either near the center of the loop field in a below-grade vault or in the building equipment room. Each subheader set has isolation valves for independent purging of air and debris. Interior piping is similar to conventional water-source heat pump systems in which interior piping is routed to individual water-to-air heat pumps in each zone and/or heat pump water heaters and water-to- water heat pumps. Variable-speed drives (VSDs) are recommended for central loop systems because they offer substantial energy savings compared to primary/secondary pump schemes in GSHP applications. However, in buildings with primary occupancy of less than 60 h per week, measures should be incorporated to turn off the main VSD pump and provide some alternative means of pumping water to critical building zones during low-occupancy or unoccupied periods. Several projects examined installation costs of nonresidential ground source heat pumps beginning in the mid 1990s: a large survey from an ASHRAE-sponsored research project (Caneta 1995) and a condensed report (Caneta 1998) studied systems located in colder climates, and Zimmerman (2000) looked at costs in several Tennessee Valley GSHP schools (Figure 18). Kavanaugh et al. (2012) also studied costs for the complete system Inc. ASHRAE, 2019 Ⓒ user. single for Licensed | {}
5db02c70-03bf-4615-b321-dbf3c98dd8ba | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 35.20 Table 7 Average Costs for Three GSHP Systems ¦ ¦ Caneta (1995) ¦ Zimmerman (2000) ¦ Kavanaugh et al. (2012) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ System average, $/m2 ¦ 98 ¦ 138 ¦ 223 ¦ ¦ Maximum, $/m2 ¦ 154 ¦ 187 ¦ 281 ¦ ¦ Minimum, $/m2 ¦ 29 ¦ 98 ¦ 144 ¦ ¦ Ground loop average, $/m2 ¦ 38 ¦ 40 ¦ 57 ¦ ¦ Maximum, $/m2 ¦ 79 ¦ 62 ¦ 96 ¦ ¦ Minimum, $/m2 ¦ 6.46 ¦ 21 ¦ 36 ¦ ¦ Percent of total system cost ¦ 38.5 ¦ 30.1 ¦ 25.5 ¦ Chart Type: line 1990 1992 1994 1996 1998 2000 item_01 0S/m2 0S/m2 0S/m2 0S/m2 0S/m2 0S/m2 Fig. 18 GSHP System and Loop Cost (Caneta 1995; Zimmerman 2000) Chart Type: bar 1999 2001 2003 2005 2007 2009 2011 item_01 150$/m2 200$/m2 150$/m2 200$/m2 250$/m2 250$/m2 250$/m2 Fig. 19 GSHP System and Ground Loop Cost Based on Building Floor Area and ground loop (Figure 19). Table 7 compiles the average, maximum, and minimum costs for these studies. As Table 7 shows, the percentage of ground loop costs to total GSHP system cost declined from 38.5% in 1995 to 25.5% in 2011. Results indicate there was a 177% increase in HVAC component costs compared to a 52% increase in ground loop costs during this 16 year period. The TX Loop (cost for ground loop installed in Texas) costs are an example of how multiple unitary loops can be very cost effective. Figure 20 shows the results of a cost comparison of a GSHP system with two four-pipe water-cooled chilled/hot-water systems 2019 ASHRAE Handbook-HVAC Applications (SI) Chart Type: bar GSHP CHILLED-WATER CAV CHILLED-WATER VAV item_01 133USD 154USD 184USD Fig. 20 Project Installation Cost Comparison of 530 kW GSHP with Four-Pipe Systems for a 6700 m2 school in Birmingham, Alabama with a 530 kW cooling requirement. The installation cost of the GSHP system was 11.7% lower than that of the constant-air-volume (CAV) system and 31.9% less than the variable-air-volume (VAV) system. Installation costs were based on 2014 data (Means 2014) but assumed the ground loop cost was $49/m of vertical ground heat exchanger. Costs include controls for components (thermostats, VAV actuators, sensors, etc.) but not building automation systems (BAS) or energy recovery units (ERUs). Additional cost data for regions across the United States are available in Battocletti and Glassley (2013). GSHP Piping Materials. It is an industry standard that the buried ground-loop piping materials be fusion welded. For this reason, the current IGSHPA design and installation standards lists only high-density polyethylene (HDPE), and most recently an exception for cross-linked polyethylene (PEX-a) as approved materials for buried pipe. (IGSHPA 2011). ANSI/CSA/IGSHPA Standard C448-16 only discusses HDPE and PEX-a as approved materials for closed-loop buried pipe. In most cases, this pipe is buried without insulation. Distribution systems in a building need to be carefully chosen and not solely driven by cost or ease of installation. As with any system, piping materials must be compatible with system design temperatures and with the fluids conveyed. Closed-loop systems typically use potable water and may also include antifreeze and/or water treatment chemicals. With newer refrigerants, care is needed to ensure the piping materials are compatible with the oils used in the refrigeration system and that equipment seals are compatible with the heat transfer fluids conveyed; for instance, polyolester (POE) oil used with R-410A is not compatible with PVC pipe. Consult chemical resistance charts provided by materials manufacturers. Whether designing a new system or retrofitting an existing one, it is the design engineer's responsibility to size and select the proper piping materials for each application and to select only those materials allowed by code (ICC 2012). In large building systems, the aboveground piping specifications commonly include steel, iron, copper or PVC. Where the hydronic mains are 100 mm or larger, it is often more cost effective to specify steel pipe. Specifying steel pipe may require some type of water treatment to inhibit general corrosion and dielectric isolation when connected to geothermal heat pumps. Water Quality, Heat Transfer Fluids, and Water Treatment. When engineers introduce dissimilar metals into Inc. ASHRAE, 2019 user. single for Licensed | {}
bf98f251-2c10-4320-8b4b-ec2870400bcf | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Geothermal Energy 35.21 closed-loop hydronic piping systems, improperly address water treatment requirements for their designs, or are not properly informed of the local groundwater regulations, water quality problems may result. Poor water quality contributes to a decline in mechanical system performance, increased maintenance, and can reduce the useful lifetime of mechanical system components. The standard working fluid in small residential closed-loop piping systems is either potable water or, in colder regions, an antifreeze solution. Where required, the antifreeze solution is introduced after the ground loop is properly pressure tested, flushed, and purged of debris and air. There has been little problem with or concern about water quality in these GSHP systems, because piping materials have historically been HDPE, copper, or stainless steel hose kits for final connection at the heat pumps. Quality of potable water can vary, depending upon the source, and rules on its use vary from state to state. The chemistry of this water is one of the contributors to corrosion and water quality problems in closed-loop piping systems, so engineers need to be precise with hydronic piping and water treatment system specifications. Chapter 50 offers some guidance on understanding the consequences of water quality on both open- and closed-loop hydronic systems. The type of chemical used for water treatment in closed-loop systems is based on several criteria, including the materials being protected, the quality of the water in the piping system, local regulations, and cost. These systems are typically specified to include a rigorous process for cleaning the distribution piping, flushing the piping systems of air and debris, and then adjusting the water quality of the final local water to meet the long-term performance requirements of the building systems. Chemicals used to adjust water quality for these systems, including corrosion inhibitors, are often not acceptable for use when the circulating fluid is also connected to a ground loop. This is not a problem unless there is a pipe failure or problem with the ground loop, but a potential leak is a concern of the regulatory agencies that protect groundwater in each state. Flush and Purge. To ensure that a geothermal heat pump system provides trouble-free operation, all ground-loop systems must be properly flushed and purged prior to connection to the building piping system (IGSHPA 2011). The current standard of care is defined by IGSHPA as providing a minimum velocity of 0.6 m/s through each piping system (but not in excess of the maximum flow velocity recommended by the pipe and fittings manufacturer) to remove air from the system. Flushing and purging each supply and return circuit in the forward and reverse directions for long enough to remove all debris and air from the system is also recommended. To attain proper flow velocity, appropriately sized and located purge ports and valves should be included in the mechanical design, preferably in a location where manipulation of the valve(s) allows independent flush and purge of the building and/ or the ground loop. Special care should be taken to ensure that air is not pumped from the building into the ground loop. Recommendations for Good GSHP Piping System Design. · Before beginning design, consult the local regulatory agency for guidance on requirements related to the ground-loop portion. In many locations, this may be the Departments of Health or Envi- ronmental Services. Drilling for a vertical closed-loop system may not be allowed. Local groundwater conditions may limit the use of certain working fluids due to the sensitive nature of the resource and the concern for contamination. · Conform to applicable codes on adding nonpotable chemicals to building mechanical piping systems and for any discharge to pub- lic sewage systems. Good piping designs minimize the need for chemical treatment and any potential impact to the environment. · Note that corrosion occurs at some level in all hydronic systems. The best GSHP distribution system from a corrosion standpoint is one that includes only HDPE. Breaking down the system into the subcentral or individual loops may accommodate the use of only HDPE in large buildings. · Review pressure ratings of all piping materials specified for the system design temperatures. · Minimize the number of fittings, valves, and specialties where practical. Fittings, valves, specialties, and pumps perform best when stainless steel or bronze fitted. · Even in a closed-loop piping system, it is possible for air to be introduced by expansion and contraction of the pipe and occa- sional addition of make-up water. For suspended gases, air separators installed upstream of the pumps with an expansion tank can provide deaeration. For dissolved gases, particularly oxygen, the problem can only be addressed with chemical treat- ment. · Itis very important that all ground-loop and building systems are properly flushed and purged of debris. Not only can debris clog equipment, but biological material contributes to a drop in water pH as it decays. · Take a water sample of the local potable water supply if it is planned to be the hydronic system 's working fluid. If dissimilar metals are used and/or the local water quality is poor, a water- treatment specialist can help select a water treatment regimen for the system. Alert the owner to the requirement for periodic mon- itoring of water quality. · If a chemical pot feeder is added into the system as a place to introduce the chemicals for the hydronic system, include an inte- gral filter. The filter will help to maintain water quality and remove residual debris that may break lose after the system has been properly flushed and purged. · If propylene glycol is to be used as an antifreeze, note that con- centrations less than 20% may promote bacterial growth. Check this percentage with the supplier (NGWA 2010). Pressure Considerations in Deeper Vertical Boreholes In deep vertical boreholes, it is especially important for the designer to be aware of conditions that may lead to pipe failure. The hydrostatic pressure exerted on both the inner and outer wall of the U-bend piping during installation should be considered. Internal Pressure Considerations. Pressure is exerted on the inner pipe wall during installation but before grout placement, because the pipe is filled with water to offset its buoyancy in a water- or mud-filled bore. Equation (30) may be used to determine the internal working pressure (IWP) during vertical loop installation. (Note that the depth to the static water table, which is site specific, must be known.) IWP = 9.806 x Depth (30) where IWP = internal working pressure, kPa Depth = depth to static water table, m The internal pressure caused by water column height is offset in the portion of the loop that is installed below the static water table. Once the internal working pressure is known, the designer should ensure that the internal pressure rating (IPR) of the pipe is not exceeded. The IPR ofHDPE is a function of pipe material type (cell classification), wall thickness (DR), and temperature. The IPR for HDPE 3408/3608 and 4710 at 23°C for DR-11 and DR-9 are shown in Table 8; compensating factors to account for other temperatures are shown in Table 9. To determine the IPR at the pipe's actual working temperature, simply multiply the IPR at 23°C by the appropriate temperature compensating multiplier. External Pressure Considerations. Pressure is exerted on the outer pipe wall by the liquid grout slurry as it is pumped into the Inc. ASHRAE, 2019 user. single for Licensed | {}
b33c77af-bad3-476e-8487-0bdd93e53b57 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 35.22 Table 8 Internal Pressure Rating (IPR) for HDPE ¦ ¦ kPa (m of water) ¦ kPa (m of water) ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ HDPE at 23°C ¦ DR-11 ¦ DR-9 ¦ ¦ 3408/3608 ¦ 1103 (112.5) ¦ 1379 (140.6) ¦ ¦ 4710 ¦ 1379 (140.6) ¦ 1724 (175.8) ¦ Source: PPI (2018). Table 9 Temperature Compensating Multipliers for HDPE ¦ Pipe Temperature, °C ¦ Compensating Multiplier ¦ ¦ --- ¦ --- ¦ ¦ -29 ¦ 2.54 ¦ ¦ -23 ¦ 2.36 ¦ ¦ -18 ¦ 2.18 ¦ ¦ -12 ¦ 2.00 ¦ ¦ - 7 ¦ 1.81 ¦ ¦ - 1 ¦ 1.65 ¦ ¦ 4 ¦ 1.49 ¦ ¦ 10 ¦ 1.32 ¦ ¦ 16 ¦ 1.18 ¦ ¦ 23 ¦ 1.00 ¦ ¦ 27 ¦ 0.93 ¦ ¦ 32 ¦ 0.82 ¦ ¦ 38 ¦ 0.73 ¦ ¦ 43 ¦ 0.64 ¦ ¦ 49 ¦ 0.58 ¦ ¦ 54 ¦ 0.50 ¦ ¦ 60 ¦ 0.43 ¦ Source: PPI (2018). Table 10 External Pressure Rating (EPR) for HDPE* ¦ ¦ kPa (m of water) ¦ kPa (m of water) ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ HDPE at 23°C ¦ DR-11 ¦ DR-9 ¦ ¦ 3408/3608 ¦ 1280 (130.5) ¦ 2500 (254.9) ¦ ¦ 4710 ¦ 1349 (137.6) ¦ 2635 (268.7) ¦ *Based on the 1 h apparent modulus rating for HDPE, assuming a safety factor N⌀ = 1.0. Source: PPI (2018). bore. As a liquid, grout rests against the outer pipe wall, exerting pressure until it hardens (sets). In general, the maximum working time for most grouts is 30 to 45 min, depending on factors such as makeup water temperature and chemistry, borehole temperature, etc. After this amount of time, the grout begins to set into its permanent state as a semirigid plug. Note that grouting is not required in some jurisdictions and not addressed in others; this has given rise to substituting a manufactured fill material, which may be acceptable in some cases. After it sets, grout can partially support its own weight. It still exerts some pressure on the outer pipe wall, but the amount is far less compared to when in its liquid state. The amount of pressure exerted by the liquid grout column increases with depth, and is at maximum at the bottom of the bore. Equation (31) calculates the pressure exerted on the outer pipe wall after grout placement and before setting. The external pressure is due to density differences between the liquid grout column on the outer and the fluid (water) on the inner pipe wall: EWP = 0.00981( water) x Depth grout where EWP = external working pressure, kPa ¦ water ¦ density of internal fluid, which is typically water during grout installation, kg/m3 ¦ ¦ --- ¦ --- ¦ ¦ grout ¦ density of the external grouting fluid, kg/m3 ¦ ¦ Depth ¦ = borehole depth, m ¦ (31) 2019 ASHRAE Handbook- -HVAC Applications (SI) Table 11 Safe Deflection Limits for Pressurized Pipe ¦ Dimension Ratio (DR) ¦ Safe Deflection (%) ¦ ¦ --- ¦ --- ¦ ¦ 32.5 ¦ 7.5 ¦ ¦ 26 ¦ 7.5 ¦ ¦ 21 ¦ 7.5 ¦ ¦ 17 ¦ 6.0 ¦ ¦ 13.5 ¦ 6.0 ¦ ¦ 11 ¦ 5.0 ¦ ¦ 9 ¦ 4.0 ¦ ¦ 7.3 ¦ 3.0 ¦ Source: PPI (2018). Table 12 Sustained External Pressure Duration Compensation Factors for HDPE ¦ Duration ¦ PE3408/3608 ¦ PE4710 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 0.5 h ¦ 1.054 ¦ 1.051 ¦ ¦ 1 h ¦ 1.000 ¦ 1.000 ¦ ¦ 2 h ¦ 0.959 ¦ 0.949 ¦ ¦ 10 h ¦ 0.838 ¦ 0.833 ¦ ¦ 12 h ¦ 0.811 ¦ 0.808 ¦ ¦ 24 h ¦ 0.770 ¦ 0.769 ¦ ¦ 100 h ¦ 0.703 ¦ 0.705 ¦ ¦ 1000 h ¦ 0.595 ¦ 0.590 ¦ ¦ 1 yr ¦ 0.514 ¦ 0.513 ¦ ¦ 10 yr ¦ 0.432 ¦ 0.436 ¦ ¦ 50 yr ¦ 0.378 ¦ 0.372 ¦ ¦ 100 yr ¦ 0.365 ¦ 0.359 ¦ Source: PPI (2018). Once the external working pressure is known, the designer should ensure that the external pressure rating (EPR) of the pipe is not exceeded. The EPR ofHDPE is a function of pipe material type (cell classification), wall thickness (DR), temperature, percent deflection (pipe ovality), and duration of exposure to external pressures. The EPR for HDPE 3408/3608 and 4710 at 23°C for DR-11 and DR-9 are shown in Table 10, and compensating factors to account for other temperatures are shown in Table 9. Compensation factors to account for pipe ovality are shown in Figure 21 and Table 11, and those to account for duration of sustained pressure on the outer wall of the HDPE pipe are shown in Table 12. Note that the 1 h correction factor is appropriate for bentonite-based grouts, whose working time is generally 30 to 45 minutes. Cement-based grouting materials usually require use of 10 or 24 h compensation factors. Contact the manu- facturer for more information. To determine the EPR at the actual working temperature of the pipe for a given ovality, multiply the EPR at 23°C by the appropriate temperature, ovality, and sustained pressure duration compensating multipliers. Additionally, the percent deflection must be lower than the limits specified in Table 11. As shown in Figure 21, HDPE EPR is very sensitive to ovality, which is determined by calculating the percentage reduction in pipe diameter along the deformed section of pipe (when applicable): OD - OD nom min Ovality, % = 100 OD nom where (32) nominal U-bend pipe diameter, mm OD nom = OD min U-bend pipe diameter along deformed section, when applicable, mm Inc. ASHRAE, 2019 user. single for Licensed | {}
8ba070a5-b85d-460a-b6f8-d8a83c2a79a9 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Geothermal Energy 35.23 Chart Type: line (0) (1) (2) (3) (4) (5) (6) (7) (8) (9) (10) (11) (12) item_01 1.0% 0.8% 0.8% 0.6% 0.6% 0.5% 0.4% 0.4% 0.3% 0.3% 0.3% 0.2% 0.2% Fig. 21 Ovality Compensation Factors for HDPE (PPI 2018) Note that any section of pipe that exhibits ovality greater than the recommended limit shown in Table 9 should be removed from the system and discarded. If exceeding the U-bend EPR becomes a concern, there are three primary ways to minimize the potential for issues to occur: · Use a heavier pipe wall thickness. Remember that thicker-walled pipe is more expensive and may not be as readily available; its use also effectively reduces the inside pipe diameter, which increases system head loss and associated pumping power requirements · Pressurize the U-bend from the surface before pumping grout into the bore to counteract external pressures during grout placement. Do not pressurize the loop above its IPR. Additionally, if the bore is completely dry, adding pressure to the loop from the surface will not be an option. Without water in the bore to counteract the pres- sure applied to the inside pipe wall, the U-bend's internal pressure rating will quickly be exceeded (burst pressure). · Reduce grout density by using graphite in place of silica sand (without sacrificing thermal performance). Densities of graphite- based mixes are typically low enough that bore collapse should no longer be a concern for common bore installation depths. Contact the grout manufacturer for additional information. Example 4. Calculate the external pressure rating of HDPE 4710 and the external hydrostatic pressure exerted on the outer pipe wall during grout placement. Assume the pipe will be DR-11 and is perfectly round (0% ovality), that a bentonite-based grouting material is used in the bore annulus, and that the 1 h apparent modulus is appropriate. Ground temperature, tg = 16°C Grout density, grout kg/m3 = 1809.4 Internal fluid (water) density, water kg/m3 = 1000 Borehole depth = 152.4 m Bore fill conductivity kgrt = 1.7 W/(m-K) Percent deflection (pipe ovality) compensation factor = 1.00 Temperature compensation factor = 1.18 EPR = (1349 kPa)(1.18) = 1591.8 kPa EWP = (0.00981)(1809.4 kPa - 1000 kPa)(152.4 m) = 1210.1 kPa The external pressure rating (EPR) exceeds the external working pressure (EWP) of the piping system during grout placement (assuming no safety factor, Ns = 1.00). Table 13 Rating Conditions for Water-to-Air Heat Pumps for Total Cooling (TC, W), Energy Efficiency Ratio (EER, W/W), Heating Capacity (HC, W) and Coefficient of Performance (COP, W/W) ¦ Entering Liquid and Air ¦ WLHP Water Loop ¦ GWHP Ground- water ¦ GLHP Ground Loop ¦ GLHP-PL (Part-Load) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ELT (sink, cooling) ¦ 30°C ¦ 15°C ¦ 25°C ¦ 20°C ¦ ¦ ELT (source, heating) ¦ 20°C ¦ 10°C ¦ 0°C ¦ 5°C ¦ ¦ EAT (db/wb, cooling) ¦ 27/19°C ¦ 27/19°C ¦ 27/19°C ¦ 27/19°C ¦ ¦ EAT (heating) ¦ 20°C ¦ 20°C ¦ 20°C ¦ 20°C ¦ Source: ANSI/ARI/ASHRAE/ISO Standard 13256-1. Required fan power to overcome external static pressure (ESP) and pump power to cir- culate liquid for piping loop not included in calculation of TC, EER, HC, and COP. Table 14 Rating Conditions for Water-to- Water Heat Pumps for Total Cooling (TC, W), Energy Efficiency Ratio (EER, W/W), Heating Capacity (HC, W) and Coefficient of Performance (COP, W/W) ¦ Entering Liquid and Air ¦ WLHP (Water Loop) ¦ GWHP (Ground- water) ¦ GLHP (Ground Loop) ¦ GLHP-PL (Part- Load) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ELT (sink) ¦ 30°C ¦ 15°C ¦ 25°C ¦ 20°C ¦ ¦ ELT (source) ¦ 20°C ¦ 10°C ¦ 0°C ¦ 5°C ¦ ¦ ELT (building) ¦ 12°C ¦ 12°C ¦ 12°C ¦ 12°C ¦ ¦ ELT (building) ¦ 40°C ¦ 40°C ¦ 40°C ¦ 40°C ¦ Source: ANSI/ARI/ASHRAE/ISO Standard 13256-2. Pump power to circulate liquid for source/sink and building loops not included in cal- culation ofTC, EER, HC, and COP. Effect of GSHP Equipment Selection on Heat Exchanger Design The ground heat exchanger must absorb the heat of compression and heat from auxiliary equipment (e.g., fans, pumps) in cooling mode. In heating mode, heat from auxiliary equipment reduces the amount of heat required from the ground. Therefore, the cooling- and heating-mode power values Wc and Wh in Equations (4) and (5) must include the auxiliary input. Rated values for GSHPs published in compliance with ANSI/ ARI/ASHRAE/ISO Standard 13256-1 do not include the auxiliary power required to circulate air and water through the distribution systems. Furthermore, the auxiliary power required to distribute chilled air (and water) can have a substantial negative effect on the equipment's cooling capacity. Table 13 summarizes the air and water temperatures used to generate the rated performance of water-to-air heat pumps. Table 14 summarizes the conditions for ANSI/ARI/ASHRAE/ISO Standard 13256-2, which rates water-to-water heat pumps. Actual heat pump performance can be substantially different from rated conditions. Designers must convert rated performance to design conditions by accounting for the effect of auxiliary power input and for design ELTs and EWTs. When water-to-water heat pumps or chillers are used in this application, corrections should include power for the pump(s) of the source/sink loop and the chilled-/hot-water loop, and power for fans in the air distribution system. Table 15 demonstrates the difference between rated GSHP efficiency and actual system efficiencies for various options when the effect of auxiliary components is considered. Note that using a high-static-pressure air handler for air distribution significantly reduces cooling efficiency. In heating, 49°C hot water also lowers heating COP compared to direct condensation and hydronic systems (e.g., in-floor heating) that use lower-temperature water. Inc. ASHRAE, 2019 user. single for Licensed | {}
51321531-b786-43b9-a399-1ec8e69975c6 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 35.24 2019 ASHRAE Handbook- -HVAC Applications (SI) ![image](/image/placeholder) 1.5 m A. ONE PIPE PER TRENCH ![image](/image/placeholder) 1. 2 m 1.2 m 1.2 m 1.2 m 1.5 m 1.8 m 1.8 m 1.8 m 1.8 m 2.1 m ○ ○ ○ B. TWO PIPES PER 0.6 m 0.6 m TRENCH C. FOUR VERTICAL PIPES D. FOUR PIPES PER E. SIX PIPES PER PER TRENCH TRENCH TRENCH Note: If frost line is greater than 0.9 m below grade, average depth of coils should be a minimum of 0.6 m below frost line and upper pipe should be a minimum of 0.3 m below frost line. Fig. 22 Horizontal Ground Heat Exchanger Configurations Table 15 Rated Efficiency, Component Power, and Corrected System Efficiency for Various GSHP Equipment Options (30°C ELT Cooling/10°C ELT Heating) ¦ GSHP Cooling Equipment and System Description ¦ Rated COP ¦ Evap. Type ¦ Fan Power, kW ¦ Cond. Pump, kW ¦ CW Pump, kW ¦ Parasitic Heat, kW ¦ System COP ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 13.6 kW WAHP, 24/17°C EAT ¦ 4.8 ¦ 7°C DX ¦ 0.63 ¦ 0.21 ¦ ¦ -0.63 (4%) ¦ 4.0 ¦ ¦ 35 kW WWHP; 1900 L/s, 1 kPa AHU ¦ 4.0 ¦ 7°C CW ¦ 3.36 ¦ 1.07 ¦ 1.07 ¦ -4.4 (12.6%) ¦ 2.3 ¦ ¦ 35 kW WWHP; four 470 L/s, 0.25 kPa FCUs ¦ 4.0 ¦ 7°C CW ¦ 1.8 ¦ 1.07 ¦ 1.07 ¦ -2.9 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ (8.0%) ¦ 2.8 ¦ ¦ 1760 kW chiller, 1 kPa AHUs, 0.5 kPa return fans, series FPVA V ¦ 7.0 ¦ 7°C CW ¦ 314 ¦ 27 ¦ 36 ¦ -350 (20%) ¦ 2.2 ¦ ¦ 1760 kW chiller, 200 to 470 L/s, 0.25 kPa FCUs ¦ 7.0 ¦ 7°C CW ¦ 90 ¦ 27 ¦ 36 ¦ -126 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ (7.2%) ¦ 3.8 ¦ ¦ ¦ Rated COP, ¦ ¦ Fan Power, ¦ Cond. Pump, ¦ CW Pump, ¦ Parasitic ¦ System ¦ ¦ GSHP Heating Equipment and System Description ¦ kJ/Wh ¦ Cond. Type ¦ kW ¦ kW ¦ kW ¦ Heat, kW ¦ COP ¦ ¦ 14 kW WAHP, 21°C EAT ¦ 5 ¦ Dir. ¦ 0.63 ¦ 0.21 ¦ ¦ -0.62 (4.4%) ¦ 4.0 ¦ ¦ 35 kW WWHP; 1900 L/s, 1 kPa AHU ¦ 4 ¦ 49°C HW ¦ 3.36 ¦ 1.07 ¦ 1.07 ¦ -4.2 (12.0%) ¦ 2.5 ¦ ¦ 35 kW WWHP; four 470 L/s, 0.25 kPa FCUs ¦ 4 ¦ 49°C HW ¦ 1.57 ¦ 1.07 ¦ 1.07 ¦ -2.4 (6.9%) ¦ 2.8 ¦ ¦ 35 kW WWHP; 1900 L/s, 1 kPa AHU ¦ 4 ¦ 38°C HW ¦ 3.36 ¦ 1.07 ¦ 1.07 ¦ -4.2 (12.0%) ¦ 3.1 ¦ ¦ 35 kW WWHP, in-floor heat ¦ 4 ¦ 38°C HW ¦ 0 ¦ 1.07 ¦ 1.07 ¦ -1.1 (3.1%) ¦ 3.7 ¦ Horizontal and Small Vertical System Design The buried pipe of a closed-loop GSHP may theoretically produce a change in temperature in the ground up to 5 m away. For all practical purposes, however, the ground temperature is essentially unchanged beyond about 1 m from the pipe loop. For that reason, the pipe can be buried relatively near the ground surface and still benefit from the moderating temperatures that the earth provides. Because the ground temperature may fluctuate as much as 5 K at a depth of 2 m, an antifreeze solution must be used in most heating-dominated regions. The critical design aspect of horizontal applications is to have enough buried pipe loop in the available land area to serve the equipment. The design guidelines for residential horizontal loop installations can be found in OSU (1988b). Limitations on selecting a horizontal loop design include the fol- lowing: · The minimum land area needed for most nonspiral horizontal loop designs for an average house is about 2000 m2. Horizontal systems are not feasible for most urban houses, which are com- monly built on smaller lots. · The larger length ofpipe buried relatively near the surface is more susceptible to being cut during excavations for other utilities. · Soil moisture content must be properly accounted for in comput- ing the required ground heat exchanger length, especially in sandy soils or on hilltops that may dry out in summer. · Rocks and other obstructions near the surface may make excava- tion with a backhoe or trencher impractical. · Multiple pipes are often placed in a single trench to reduce the land area needed for horizontal loop applications. Some common multiple-pipe arrangements are shown in Figure 22. When pipes are placed at two depths, the bottom row is placed first, and then the trench is partially backfilled before the upper row is put in place. Rarely are more than two layers of pipe used in a single trench because of the extra time needed for the partial backfilling. Higher pipe densities in the trench provide diminishing returns because thermal interference between multiple pipes reduces the heat transfer effectiveness of each pipe. The most common multiple-pipe applications are the two-pipe arrangement used with chain trenchers and the four- or six-pipe arrangements placed in trenches made with a wide backhoe bucket. An overlapping spiral configuration (Figure 23) has also been used with some success. However, it requires special attention during back- filling to ensure that soil fills all the pockets formed by the overlapping pipe.Large quantities of water must be added to compact the soil around the overlapping pipes. The backfilling must be performed in stages to guarantee complete filling around the pipes and good soil contact. The high pipe density (up to 10 m of pipe per linear metre of trench) may cause problems in prolonged extreme weather conditions, either from soil drying during cooling or from freezing during heating. This spiral design has been used in vertical trenches cut with a chain trencher as well as in laying the coil flat on the bottom of a large pit Inc. ASHRAE, 2019 user. single for Licensed | {}
4a05a332-60a0-4992-8f85-4feaa9f38116 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Geothermal Energy 35.25 ![image](/image/placeholder) TOP VIEW SIDE VIEW Fig. 23 General Layout of Spiral Earth Coil excavated with a bulldozer. Installations using the horizontal spiral coil on the bottom of a pit have generally performed better than those with spiral coils that were stood upright in a vertical trench. The extra time needed to backfill and the extra pipe length required make spiral configurations nearly as expensive to install as straight pipe configurations. However, the reduced land area needed for the more compact design may allow use on smaller residential lots that are too small for conventional horizontal-pipe ground-loop designs. The spiral pipe configuration laid flat in a horizontal pit arrangement is used commonly in the northern Midwest of the United States, where sandy soil causes vertical trenches to collapse. A large open pit is excavated by a bulldozer, and then the overlapping pipes laid flat on the bottom of the pit. The bulldozer is also used to cover the pipe, being careful to not run over them with the bulldozer tread. Although most horizontal closed-loop systems (see Figure 3) are installed with either a chain trencher or a backhoe, horizontal boring machines are also now available for this application. Developed for buried utility applications such as electric or potable water service, these devices simply bore through the ground parallel to the ground surface. A detector at the surface can show the exact point where the boring head is located underground so that the bore does not penetrate other known utilities or cross over into a neighbor's lot. Most horizontal loop installations place the pipe loops in a parallel rather than a single (series) loop to reduce pumping power (Figure 24). Splitting the flow into parallel loops increases the fluid- to-soil temperature difference and subsequent heat transfer. Parallel loops may require slightly more pipe, but may use smaller pipe and thus have smaller internal volumes, requiring less antifreeze (if needed). Also, smaller pipe is typically much less expensive for a given length, so total pipe cost should be less for parallel loops. An added benefit is that parallel loops can be flushed out with a smaller purge pump than is required for a larger single-pipe loop. A disadvantage of parallel loops is the potential for unequal flow in the loops and thus nonuniform heat exchange efficiency. The time required to install a horizontal loop is not much different from that for a vertical system. For the arrangements described, a two-person crew can typically install the ground heat exchanger for an average house in a single day. Soil characteristics are an important concern for any ground heat exchanger design. With horizontal loops, the soil type can be more easily determined because the excavated soil can be inspected and tested. EPRI (1990) lists criteria and simple test procedures that can be used to classify soil and rock for horizontal ground-loop design. Although soil type and moisture content are important consider- ations in sizing the ground heat exchanger, some design guidelines have been developed based on extensive analysis of monitored sys- tems in mostly southern climates (Kavanaugh and Calvert 1995). Table 16 gives recommended trench lengths for the various types of ![image](/image/placeholder) SERIES GROUND LOOP PARALLEL GROUND LOOP Fig. 24 Parallel and Series Ground Heat Exchanger Configurations commonly used excavation methods. Heating-mode run times ap- proaching 100% on a daily basis would be the norm at heating design conditions in heating-dominated climates. In contrast, daily run times of no more than 50% would be encountered at design cooling condi- tions in cooling-dominated climates. The combination of long run times and ice formation around the pipes makes performance of hor- izontal systems dependent on both the loop field design and how the system is matched to the building load. Though many thousands of these systems have been installed in heating climates, no comparable analysis has been performed to determine proper design guidelines. The loop length data in Table 16 for soil temperatures below 13°C are based on nominal heat pump capacity and use of supplemental resistance heat at design conditions. Ifinstalling such a system for the first time, contact several experienced contractors in the area to deter- mine successful design lengths for the local climate and soil types. Trench lengths in Table 16 are based on a minimum trench separation of 3 m and minimum horizontal loop average burial depth of the greater of 1.5 m or 0.6 m below the frost line. Bore lengths are based on a vertical bore separation of 6 m. Design ground heat exchanger temperatures are a maximum of 32°C return and 38°C entering in warm climates and a minimum of - 2°C return and -6°C entering in cold climates. Additional considerations for horizontal loop systems in colder climates arise from the potential for ice formation around the pipe loop. The loop should not pass within 0.6 m of any buried water line (potable, sewer, or rainwater). If such proximity cannot be avoided, the GCHP loop can be insulated in that area. Horizontal loops should not be placed closer than 2 m from a basement or crawl space wall when buried parallel to the wall. Heaving from ice formation could cause structural damage if placed in close proximity to the wall. Leaks in heat-fused plastic pipe are rare when attention is paid to pipe cleanliness and proper fusion techniques. Should a leak occur, it is usually best to try to isolate the leaking parallel loop Inc. ASHRAE, 2019 user. single for Licensed | {}
1ef3cd69-ac9e-4016-864d-96a89e06ecaa | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 35.26 2019 ASHRAE Handbook- -HVAC Applications (SI) Table 16 Recommended Lengths of Trench or Bore per kW for Residential GCHPs ¦ ¦ ¦ Pitchb ¦ Ground Temperature, °C ¦ Ground Temperature, °C ¦ Ground Temperature, °C ¦ Ground Temperature, °C ¦ Ground Temperature, °C ¦ Ground Temperature, °C ¦ Ground Temperature, °C ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Coil Typea ¦ ¦ m of Pipe per m Trench/Bore ¦ 7 to 8 ¦ 8 to 11 ¦ 11 to 13 ¦ 13 to 15 ¦ 15 to 17 ¦ 17 to 19 ¦ 19 to 21 ¦ ¦ Horizontal ¦ 6-Pipe/6-Pitch Spiral ¦ 6 ¦ 16 ¦ 14 ¦ 13 ¦ 14 ¦ 16 ¦ 17 ¦ 20 ¦ ¦ ¦ 4-Pipe/4-Pitch Spiral ¦ 4 ¦ 19 ¦ 17 ¦ 17 ¦ 17 ¦ 19 ¦ 22 ¦ 26 ¦ ¦ ¦ 2-Pipe ¦ 2 ¦ 26 ¦ 24 ¦ 22 ¦ 24 ¦ 26 ¦ 30 ¦ 35 ¦ ¦ Vertical U-tube ¦ 19 mm Pipe ¦ 2 ¦ 16 ¦ 15 ¦ 14 ¦ 15 ¦ 16 ¦ 17 ¦ 20 ¦ ¦ ¦ 25 mm Pipe ¦ 2 ¦ 15 ¦ 14 ¦ 13 ¦ 14 ¦ 15 ¦ 16 ¦ 19 ¦ ¦ ¦ 32 mm Pipe ¦ 2 ¦ 14 ¦ 13 ¦ 12.5 ¦ 13 ¦ 14 ¦ 15 ¦ 17 ¦ Source: Kavanaugh and Calvert (1995). aLengths based on DR1 1 high-density polyethylene (HDPE) pipe. See Figures 24 to 26 for details. bMultiply length of trench by pitch to find required length of pipe. Multiply Table 16 Values by Bold Values Below to Correct for Other Values of Ground Conductivity ¦ ¦ Ground Thermal Conductivity in W/(m·K) ¦ Ground Thermal Conductivity in W/(m·K) ¦ Ground Thermal Conductivity in W/(m·K) ¦ Ground Thermal Conductivity in W/(m·K) ¦ Ground Thermal Conductivity in W/(m·K) ¦ Ground Thermal Conductivity in W/(m·K) ¦ Ground Thermal Conductivity in W/(m·K) ¦ Ground Thermal Conductivity in W/(m·K) ¦ Ground Thermal Conductivity in W/(m·K) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ 0.7 ¦ 1.0 ¦ 1.4 ¦ 1.7 ¦ 2.1 ¦ 2.4 ¦ 2.8 ¦ 3.1 ¦ 3.5 ¦ ¦ Horizontal loop ¦ 1.22 ¦ 1.0 ¦ 0.89 ¦ 0.82 ¦ ¦ ¦ ¦ ¦ ¦ ¦ Vertical loop* ¦ ¦ ¦ 1.23 ¦ 1.10 ¦ 1.0 ¦ 0.93 ¦ 0.87 ¦ 0.83 ¦ 0.79 ¦ *Vertical loop values based on an annular fill with k = 1.5 W/(m·K). Multiply lengths by 1.2 for Kannulus = 0.7 W/(m-K) and 0.95 for kannulus = 1.9 W/(m·K). and abandon it in place. The effort required to find the source of the leak usually far outweighs the cost of replacing the defective loop. Because the loss of as little as 0.9 L of water from the system causes the system to lose pressure and shut down, leaks cannot be located by looking for wet soil, as is commonly done with water lines. Although leaks should be rare with properly thermally fused pipe, some states have adopted restrictions against the use of certain types of antifreeze mixtures in GCHP systems; check local water-quality regulations before selecting a mixture. Methanol has been used extensively because of its low cost and good physical properties when cold. Comprehensive studies by Heinonen and Tapscott (1996) and Heinonen et al. (1997) showed that propylene glycol is a good alternative when issues of flammability or environmental safety are important considerations. A more thorough discussion of antifreeze solutions is given in the Antifreeze Requirements section of this chapter. Fluid Flow and Loop Circuiting. Residential systems, like commercial applications, sometimes have excessive pumping power. This trend may result from undersized piping, excessive amounts of viscous antifreeze solutions, or conservative pump sizing. Because a 10.5 kW heat pump with an energy efficiency ratio (EER) of 15 requires a total power (compressor and fan) of 2400 W, the addition of a second 0.12 kW pump (which draws 245 W) reduces system efficiency by 10%. Table 17 provides a guideline to ensure adequate liquid flow rate with the least possible number of pumps. It should be used in conjunction with Table 16 and applies to loops with 0 to 15% propylene glycol solutions (by volume; note that caution and additional treatment may be needed for solutions lower than 20%, because of risks of corrosion and biological growth below this level). This solution has the reputation of being the most difficult of the commonly used solutions to pump when cold. However, it is no more difficult to pump than ethyl alcohol, and pumping penalties can be mitigated by adding only the required amount of antifreeze. Shorter loops may require higher levels of antifreeze solutions. See the section on Antifreeze Requirements for more details. Any exposed piping above the frost line must be insulated with closed-cell insulation with ultraviolet (UV) protection (paint or wrap). Example 5. Design the vertical ground coupling grid and the pumping loop for a 14 kW residential heat pump system. The home is located in Nashville, Tennessee, and the header pipes can be brought into the Note: Based on k = 1.0 W/(m-K) for horizontal loops and k= 2.1 W/(m-K) for vertical loops. Figures for soil temperatures < 13°C based on modeling using nominal heat pump capacity and assumption of auxiliary heat at design conditions. Table 17 Recommended Residential GCHP Piping Arrangements and Pumps ¦ ¦ Nominal Heat Pump Capacity, kW ¦ Nominal Heat Pump Capacity, kW ¦ Nominal Heat Pump Capacity, kW ¦ Nominal Heat Pump Capacity, kW ¦ Nominal Heat Pump Capacity, kW ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 7 ¦ 10.5 ¦ 14 ¦ 17.5 ¦ 21 ¦ ¦ ¦ Required Flow Rate, L/s ¦ Required Flow Rate, L/s ¦ Required Flow Rate, L/s ¦ Required Flow Rate, L/s ¦ Required Flow Rate, L/s ¦ ¦ ¦ 0.3 to 0.4 ¦ 0.5 to 0.6 ¦ 0.6 to 0.8 ¦ 0.8 to 0.90.9 ¦ to 1.1 ¦ ¦ ¦ Number of Parallel Loops ¦ Number of Parallel Loops ¦ Number of Parallel Loops ¦ Number of Parallel Loops ¦ Number of Parallel Loops ¦ ¦ ¦ Coil Type* Spiral (10 pt.) ¦ 3 to 4 ¦ 4 to 6 ¦ 6 to 9 ¦ 8 to 10 ¦ 8 to 10 ¦ ¦ 6-Pipe ¦ 3 to 4 ¦ 4 to 6 ¦ 6 to 9 ¦ 8 to 10 ¦ 8 to 10 ¦ ¦ 4-Pipe ¦ 2 to 3 ¦ 4 to 6 ¦ 5 to 8 ¦ 6 to 9 ¦ 6 to 10 ¦ ¦ 2-Pipe ¦ 2 to 4 ¦ 3 to 5 ¦ 4 to 6 ¦ 5 to 8 ¦ 6 to 10 ¦ ¦ Vertical 19 mm pipe ¦ 2 to 3 ¦ 3 to 5 ¦ 4 to 6 ¦ 5 to 8 ¦ 6 to 10 ¦ ¦ 25 mm pipe ¦ 2 to 3 ¦ 2 to 4 ¦ 3 to 5 ¦ 4 to 6 ¦ 4 to 6 ¦ ¦ 32 mm pipe ¦ 1 to 2 ¦ 1 to 2 ¦ 2 to 3 ¦ 2 to 3 ¦ 2 to 4 ¦ ¦ Trench Length ¦ Header Diameter (HDPE Pipe), mm ¦ Header Diameter (HDPE Pipe), mm ¦ Header Diameter (HDPE Pipe), mm ¦ Header Diameter (HDPE Pipe), mm ¦ Header Diameter (HDPE Pipe), mm ¦ ¦ Less than 30 m ¦ 32 ¦ 32 ¦ 38 ¦ 38 to 51 ¦ 38 to 51 ¦ ¦ 30 to 60 m ¦ 32 ¦ 38 ¦ 38 ¦ 51 ¦ 51 ¦ ¦ ¦ Size (No.) of Pumps Required ¦ Size (No.) of Pumps Required ¦ Size (No.) of Pumps Required ¦ Size (No.) of Pumps Required ¦ Size (No.) of Pumps Required ¦ ¦ ¦ 0.06 kW (1) ¦ 0.12 kW (1) ¦ 0.06 kW (2) ¦ 0.12 kW (2) ¦ 0.12 kW (2) ¦ Source: Kavanaugh and Calvert (1995). *Based on DR11 HDPE pipe. equipment room where the unit will be located. The driller can bore 115 mm holes to a depth of 53 m in the light limestone and clay at the site. The owner wants the drilling site to be located 23 m from the house. Thermally enhanced grout with thermal conductivity of 1.5 W/ (m· K) is used to fill the annular region between the U-tubes and bore- hole walls. Solution: The soil temperature is estimated to be 14.5°C in Nashville. Table 16 suggests bore lengths of 15 m/kW for 19 mm U-bends, 14 m/ kW for 25 mm, and 13 m/kW for 32 mm (bores are deep, greater than 30 m). However, 32 mm U-bends are very difficult to install in a 115 mm borehole, and are not considered. Therefore, either 210 m (15 m/kW 14 kW) of 19 mm U-bend coupling or 196 m (14 m/kW 14 kW) of25 mm coupling is required. The latter is used in this example. Also, Table 16 is based on a soil conductivity of 2.1 W/(m· K), which is an approximate Inc. ASHRAE, 2019 user. single for Licensed | {}
57e78582-fcfb-40cf-9d06-da3e8d3021a4 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Geothermal Energy 35.27 average between limestone and clay, and a bore fill (or grout) conductivity of 1.5 W/(m · K). Ifthe ground conductivity is higher (i.e., more limestone than clay), the loops should be reduced as noted in Table 16; if lower, the loops should be lengthened. Loop lengths also must be lengthened if the bore fill (or grout) conductivity is lower than 1.5 W/(m·K), as noted in Table 16. Layout is dictated by drilling conditions. The total length of 196 m requires four bores, because the driller can only drill to 53 m. This can be accomplished with four 48 to 50 m holes. Table 16 suggests between three and five parallel circuits for the grid. Three and five circuits do not divide evenly into the four U-bends. Therefore, four circuits (one per U-bend) should be used in an arrangement similar to Figure 25. Central Plant Systems Central plant GCHP systems use central water-to-water equipment (e.g., a water-cooled chiller) to move thermal energy ![image](/image/placeholder) EXAMPLE 14 kW VERTICAL GCHP SYSTEM (LENGTHS VARY: SEE TABLE FOR OTHER APPLICATIONS AND CLIMATES DESIGN) WATER-TO-AIR HEAT PUMP · EXTENDED RANGE (ELT = -5 to 40°C) · HIGH EFFICIENCY PUMP (ASHRAE STANDARD THREE-WAY PURGE VALVES 13256-1 GLHP C COOLING COP ≥4.4) 그 P/T TAP 38 mm HDPE HEADERS CLOSE HEADER 25 mm DR11 50 m 4.5 to 6 m HDPE U-TUBES MINIMUM FOUR CIRCUITS, FOUR BORES Fig. 25 Residential Design Example between a source loop (the ground coupled heat exchanger), a chilled-water loop, and a hot-water loop.Here, the term central plant implies the mechanical equipment is in one centralized location; it does not imply a campus is served, and single buildings are a common application. The central plant source loop is commonly a vertical closed-loop heat exchanger, but any combination of GCHP types may be used. The chilled- and hot- water loops may serve any HVAC distribution equipment (fan coils or radiant systems are efficient options) as long as design hot- water supply temperatures do not exceed heat pump temperature ranges (typically 54.4°C). Best practice in these applications is largely theoretical or anecdotal; research is needed on the efficacy of the various central plant GCHP applications and designers considering central plant GCHPs must be cautious. Compared to traditional unitary (water-to-air) GCHP systems, central plant systems offer the potential advantages of (1) incorporating direct heat recovery from hot-water loads to chilled- water loads, (2) sometimes allowing waterside economizing, (3) centralizing equipment maintenance, and (4) expanding retrofit opportunities. However, when such plants are connected to conventional distribution such as variable air volume (VAV), the loss of zone level heating and cooling results in large fan and reheat energy penalties. Pumping power is often higher than equivalent unitary heat pump systems. Central plants also have significantly more complex design, controls, commissioning, operational training, and maintenance. Most existing tools and methods for sizing ground heat exchangers and evaluating energy performance do not accurately represent central plant GCHP operation. As with unitary systems, central plant systems may take many forms. Figure 26 illustrates the basic building blocks of a central plant GCHP system. Any number of heat recovery chillers and heating or cooling heat pumps may be installed. Either or both of the load-side loops may be connected to the source loop to achieve direct heat transfer (water economizing). The loops may be separated by control valves or heat exchangers (as shown in Figure ![image](/image/placeholder) FREE-HEATING HEAT EXCHANGER HOT-WATER SUPPLY HOT-WATER RETURN CONDENSER CONDENSER CONDENSER HEATING COOLING HEAT HEAT HEAT RECOVERY PUMP PUMP HEAT PUMP EVAPORATOR EVAPORATOR EVAPORATOR CHILLED-WATER TO GROUND LOOP RETURN CHILLED-WATER FROM GROUND LOOP SUPPLY CONTROL VALVE FREE-COOLING (TYPICAL) HEAT EXCHANGER Fig. 26 Central Plant GCHP System Inc. ASHRAE, 2019 user. single for Licensed | {}
0a86f1d5-b85a-4c09-a276-20c725e7b9cc | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 35.28 26), but loops should be linked only by control valves where fluid type and pressure are compatible. Most central plant heat pump equipment is designed for use in one of three basic strategies: · Parallel water-to-water heat pumps: dedicated heat pumps pro- vide hot and/or chilled water in parallel. This type is often used in conjunction with unitary heat pumps or in simple applications where there is little opportunity for heat recovery or water econ- omizing. · Packaged modular heat pumps: multiple units are connected by control valves to any of the loops (source, hot water, or chilled water) such that each individual heat pump may serve for heating, cooling, or heat recovery. · Heat pump chiller: one or more large heat recovery chillers, designed to operate with a large lift, operate to maintain both hot and chilled water at required temperatures. No dedicated cooling heat pump or heating heat pump is provided. The heat exchangers (or direct valve connections between loops) provide the means to achieve heat rejection or heat absorption with the ground heat exchanger. To provide stable temperature control and part load operation, cen- tral plant GCHP systems can benefit from additional thermal capaci- tance (buffer tanks) on the load side loops. Any loop flow control methodology may be used; however, variable flow should be used to minimize pumping energy penalties where equipment allows. Con- sider using water as the working fluid wherever possible, because of the energy and capital cost associated with antifreeze solutions. Central plant designers have the option to connect hybrid heating and cooling equipment to the load side of the heat pumps instead of the source/ground side, which adds redundancy and reduces pump and compressor energy at the expense of increased controls complexity. Hybrid air-cooled chillers may serve the chilled-water loop directly, whereas evaporative cooling equipment is best placed on the source loop in series or in parallel with the ground heat exchanger. Connecting a hybrid boiler to the hot-water loop reduces thermal stress for boilers designed to operate at higher temperatures and provides direct emergency heat; connecting a hybrid boiler to the source loop reduces control interconnection/complexity and reduces heat pump faults caused by low entering water temperatures. Antifreeze Requirements Closed-loop horizontal and surface water heat exchanger systems often require antifreeze in the circulating water in locations with significant heating seasons. Antifreeze may not be needed in a comparable vertical borehole heat exchanger, because the deep ground temperature is essentially constant. At a depth of 2 m, a typical value for horizontal heat exchangers, ground temperature varies by approximately ±5 K. Even if the mean ground temperature is 15°C in late winter, ground temperature at a 2 m depth drops to 10°C. The heat extraction process lowers the temperature even further around the heat exchanger pipes, probably by an additional 5 K or more. Even with good heat transfer to the circulating water, the entering water temperature (leaving the ground heat exchanger) is around 5°C. Lakes that freeze at the surface in the winter approach 4°C at the bottom, yielding nearly the same margin of safety against freezing of the circulating fluid. An additional 5 K temperature difference is usually needed in the heat pump 's refrigerant-to-water heat exchanger to transfer heat to the refrigerant. Having a refrigerant-to-water coil surface temperature below the freezing point of water risks growing a layer of ice on the water side of the heat exchanger. In the best case, coil icing restricts and may eventually block the flow of water and cause a shutdown. In the worst case, ice could burst the tubing in the coil and require a major service expense. 2019 ASHRAE Handbook-HVAC Applications (SI) Table 18 Suitability of Selected GCHP Antifreeze Solutions Propylene Potassium Category Methanol Ethanol Glycol Acetate CMA Urea ¦ Life-cycle cost ¦ *** ¦ *** ¦ **1 ¦ **1 ¦ **1 ¦ *** ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Corrosion ¦ **2 ¦ **3 ¦ *** ¦ ** ¦ **4 ¦ *5 ¦ ¦ Leakage ¦ *** ¦ **6 ¦ **6 ¦ *7 ¦ *8 ¦ *9 ¦ ¦ Health risk ¦ *10,11 ¦ ** 10,12 ¦ ** * 10 ¦ ** * 10 ¦ *** ¦ 10 *** 10 ¦ ¦ Fire risk ¦ *13 ¦ *13 ¦ *** 14 ¦ *** ¦ *** ¦ *** ¦ ¦ Environment risk ¦ **15 ¦ **15 ¦ *** ¦ **15 ¦ **15 ¦ *** ¦ ¦ Future-use risk ¦ *16 ¦ **17 ¦ *** ¦ **18 ¦ **19 ¦ **19 ¦ ¦ Key: * Potential problems, caution in use required ** Minor potential for problems *** Little or no potential for problems ¦ Key: * Potential problems, caution in use required ** Minor potential for problems *** Little or no potential for problems ¦ Key: * Potential problems, caution in use required ** Minor potential for problems *** Little or no potential for problems ¦ Key: * Potential problems, caution in use required ** Minor potential for problems *** Little or no potential for problems ¦ Key: * Potential problems, caution in use required ** Minor potential for problems *** Little or no potential for problems ¦ Key: * Potential problems, caution in use required ** Minor potential for problems *** Little or no potential for problems ¦ Key: * Potential problems, caution in use required ** Minor potential for problems *** Little or no potential for problems ¦ ¦ Category ¦ Notes ¦ Notes ¦ Notes ¦ Notes ¦ Notes ¦ Notes ¦ ¦ Life-cycle cost ¦ 1. Higher-than-average installation and energy costs. ¦ 1. Higher-than-average installation and energy costs. ¦ 1. Higher-than-average installation and energy costs. ¦ 1. Higher-than-average installation and energy costs. ¦ 1. Higher-than-average installation and energy costs. ¦ 1. Higher-than-average installation and energy costs. ¦ ¦ Corrosion ¦ 2. High black iron and cast iron corrosion rates. 3. High black iron, cast iron, copper, and copper alloy corrosion rates. 4. Medium black iron, copper, and copper alloy corrosion rates. 5. Medium black iron, high cast iron, and extremely high copper and copper alloy corrosion rates. ¦ 2. High black iron and cast iron corrosion rates. 3. High black iron, cast iron, copper, and copper alloy corrosion rates. 4. Medium black iron, copper, and copper alloy corrosion rates. 5. Medium black iron, high cast iron, and extremely high copper and copper alloy corrosion rates. ¦ 2. High black iron and cast iron corrosion rates. 3. High black iron, cast iron, copper, and copper alloy corrosion rates. 4. Medium black iron, copper, and copper alloy corrosion rates. 5. Medium black iron, high cast iron, and extremely high copper and copper alloy corrosion rates. ¦ 2. High black iron and cast iron corrosion rates. 3. High black iron, cast iron, copper, and copper alloy corrosion rates. 4. Medium black iron, copper, and copper alloy corrosion rates. 5. Medium black iron, high cast iron, and extremely high copper and copper alloy corrosion rates. ¦ 2. High black iron and cast iron corrosion rates. 3. High black iron, cast iron, copper, and copper alloy corrosion rates. 4. Medium black iron, copper, and copper alloy corrosion rates. 5. Medium black iron, high cast iron, and extremely high copper and copper alloy corrosion rates. ¦ 2. High black iron and cast iron corrosion rates. 3. High black iron, cast iron, copper, and copper alloy corrosion rates. 4. Medium black iron, copper, and copper alloy corrosion rates. 5. Medium black iron, high cast iron, and extremely high copper and copper alloy corrosion rates. ¦ ¦ Leakage ¦ 6. Minor leakage observed. 7. Moderate leakage observed. Extensive leakage reported in installed systems. 8. Moderate leakage observed. 9. Massive leakage observed. ¦ 6. Minor leakage observed. 7. Moderate leakage observed. Extensive leakage reported in installed systems. 8. Moderate leakage observed. 9. Massive leakage observed. ¦ 6. Minor leakage observed. 7. Moderate leakage observed. Extensive leakage reported in installed systems. 8. Moderate leakage observed. 9. Massive leakage observed. ¦ 6. Minor leakage observed. 7. Moderate leakage observed. Extensive leakage reported in installed systems. 8. Moderate leakage observed. 9. Massive leakage observed. ¦ 6. Minor leakage observed. 7. Moderate leakage observed. Extensive leakage reported in installed systems. 8. Moderate leakage observed. 9. Massive leakage observed. ¦ 6. Minor leakage observed. 7. Moderate leakage observed. Extensive leakage reported in installed systems. 8. Moderate leakage observed. 9. Massive leakage observed. ¦ ¦ Health risk ¦ 10. Protective measures required with use. See Material Safety Data Sheet (MSDS). 11. Prolonged exposure can cause headaches, nausea, vomiting, dizziness, blindness, liver damage, and death. Use of proper equipment and procedures reduces risk significantly. 12. Additives make ethanol poisonous for human consumption. See Material Safety Data Sheet (MSDS). ¦ 10. Protective measures required with use. See Material Safety Data Sheet (MSDS). 11. Prolonged exposure can cause headaches, nausea, vomiting, dizziness, blindness, liver damage, and death. Use of proper equipment and procedures reduces risk significantly. 12. Additives make ethanol poisonous for human consumption. See Material Safety Data Sheet (MSDS). ¦ 10. Protective measures required with use. See Material Safety Data Sheet (MSDS). 11. Prolonged exposure can cause headaches, nausea, vomiting, dizziness, blindness, liver damage, and death. Use of proper equipment and procedures reduces risk significantly. 12. Additives make ethanol poisonous for human consumption. See Material Safety Data Sheet (MSDS). ¦ 10. Protective measures required with use. See Material Safety Data Sheet (MSDS). 11. Prolonged exposure can cause headaches, nausea, vomiting, dizziness, blindness, liver damage, and death. Use of proper equipment and procedures reduces risk significantly. 12. Additives make ethanol poisonous for human consumption. See Material Safety Data Sheet (MSDS). ¦ 10. Protective measures required with use. See Material Safety Data Sheet (MSDS). 11. Prolonged exposure can cause headaches, nausea, vomiting, dizziness, blindness, liver damage, and death. Use of proper equipment and procedures reduces risk significantly. 12. Additives make ethanol poisonous for human consumption. See Material Safety Data Sheet (MSDS). ¦ 10. Protective measures required with use. See Material Safety Data Sheet (MSDS). 11. Prolonged exposure can cause headaches, nausea, vomiting, dizziness, blindness, liver damage, and death. Use of proper equipment and procedures reduces risk significantly. 12. Additives make ethanol poisonous for human consumption. See Material Safety Data Sheet (MSDS). ¦ ¦ Fire risk ¦ 13. Pure fluid only. Little risk when diluted with water in antifreeze. 14. Very minor potential for pure fluid fire at elevated temperatures. ¦ 13. Pure fluid only. Little risk when diluted with water in antifreeze. 14. Very minor potential for pure fluid fire at elevated temperatures. ¦ 13. Pure fluid only. Little risk when diluted with water in antifreeze. 14. Very minor potential for pure fluid fire at elevated temperatures. ¦ 13. Pure fluid only. Little risk when diluted with water in antifreeze. 14. Very minor potential for pure fluid fire at elevated temperatures. ¦ 13. Pure fluid only. Little risk when diluted with water in antifreeze. 14. Very minor potential for pure fluid fire at elevated temperatures. ¦ 13. Pure fluid only. Little risk when diluted with water in antifreeze. 14. Very minor potential for pure fluid fire at elevated temperatures. ¦ ¦ Environment risk ¦ 15. Water pollution. ¦ 15. Water pollution. ¦ 15. Water pollution. ¦ 15. Water pollution. ¦ 15. Water pollution. ¦ 15. Water pollution. ¦ ¦ Future-use risk ¦ 16. Toxicity and fire concerns. Prohibited in some locations. 17. Toxicity, fire, and environmental concerns. 18. Potential leakage concerns. 19. Not currently used as GSHP antifreeze solution. May be difficult to obtain approval for use. ¦ 16. Toxicity and fire concerns. Prohibited in some locations. 17. Toxicity, fire, and environmental concerns. 18. Potential leakage concerns. 19. Not currently used as GSHP antifreeze solution. May be difficult to obtain approval for use. ¦ 16. Toxicity and fire concerns. Prohibited in some locations. 17. Toxicity, fire, and environmental concerns. 18. Potential leakage concerns. 19. Not currently used as GSHP antifreeze solution. May be difficult to obtain approval for use. ¦ 16. Toxicity and fire concerns. Prohibited in some locations. 17. Toxicity, fire, and environmental concerns. 18. Potential leakage concerns. 19. Not currently used as GSHP antifreeze solution. May be difficult to obtain approval for use. ¦ 16. Toxicity and fire concerns. Prohibited in some locations. 17. Toxicity, fire, and environmental concerns. 18. Potential leakage concerns. 19. Not currently used as GSHP antifreeze solution. May be difficult to obtain approval for use. ¦ 16. Toxicity and fire concerns. Prohibited in some locations. 17. Toxicity, fire, and environmental concerns. 18. Potential leakage concerns. 19. Not currently used as GSHP antifreeze solution. May be difficult to obtain approval for use. ¦ Source: Heinonen and Tapscott (1996). Several factors must be considered when selecting an antifreeze for a ground-loop heat exchanger; the most important are (1) effect on system life-cycle cost, (2) corrosivity, (3) leakage, (4) health risks, (5) fire risks, (6) environmental risks from spills or disposal, and (7) risk of future use (acceptability of the antifreeze over the life ofthe system). A study by Heinonen and Tapscott (1996) evaluating six antifreezes against these seven criteria is summarized in Table 18. No single material satisfies all criteria. Methanol and ethanol have good viscosity characteristics at low temperatures, yielding lower-than-average pumping power requirements. However, in con- centrated forms they both pose a significant fire hazard. Methanol is also toxic, eliminating it from consideration in areas that require nontoxic antifreeze to be used. Propylene glycol had no major concerns, with only leakage and pumping-power requirements prompting minor concerns. Potassium acetate, calcium magnesium acetate (CMA), and urea have favorable environmental and safety Inc. ASHRAE, 2019 user. single for Licensed | {}
76fab35b-1632-49de-9848-78660635db2e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Geothermal Energy 35.29 ![image](/image/placeholder) HORIZONTAL DIAGONAL VERTICAL Fig. 27 DXGCHP Ground Heat Exchanger Configurations performance, but are all subject to significant leakage problems, which has limited their use. 1.4 GROUND-COUPLED HEAT PUMP SYSTEMS USING REFRIGERANT-BASED HEAT TRANSFER FLUIDS (DIRECT EXCHANGE) Direct-exchange ground-coupled heat pumps (DXGCHPs) circulate refrigerant from the heat pump in sealed copper tubing to directly exchange heat with the ground. In heating mode, the ground loop system functions as an evaporator, absorbing heat from the ground and causing the refrigerant to change phase from liquid to vapor. In cooling mode, the ground loop system functions as a condenser, discharging heat to the ground and changing the refrigerant from vapor to liquid. DXGCHP systems are applied primarily to residential and moderately sized commercial buildings, and are ideal for installation where space is limited because of the smaller ground loop footprint and drilling equipment required. Distribution systems for DXGCHPs use conditioned air delivered through a direct-expansion air handler or cased coil, hydronic heating and cooling, or both. Potable water heating is an option. DXGCHP systems can be applied to various geological formations and typically in locations with ground temperatures of 4.5 to 26.6°C. DXGCHPs are generally sized up to 21 kW. Multiple systems are specified for higher-capacity applications. System Design The DXGCHP system operation is very similar the GCHP shown in Figure 1, except that the refrigerant is piped directly through the ground loop, the buried polyethylene tubing is replaced with copper tubing, and the water circulating pump and refrigerant-to-water heat exchanger are eliminated. DXGCHP ground heat exchanger systems can be horizontal, diagonal, or vertical (Figure 27). A typical DXGCHP distribution system illustrating the liquid and vapor manifold arrangement is shown in Figure 28. The ground heat exchangers are comprised of multiple individual ground loops, with the number of ground loops increasing with system capacity. Each loop is typically two copper tubes with a return bend connecting them at one end, and ranges in size from 6.4 to 12.7 mm OD, depending on the specific design. The tube diameter must be small to achieve high velocity, which ensures adequate oil return to the compressor, but large enough so the pressure drop does not significantly lower system performance. In addition, the selected lubricant must maintain a relatively low viscosity down to -15°C for proper oil return during the heating season. The vertical and diagonal ground loop systems in Figure 27 require drilling 76 mm minimum diameter boreholes to accommodate a ground loop and thermal grout. The horizontal earth loop system in Figure 27 can be either a trench or pit configuration. All ground loop systems, including line sets and manifolds, must be at least 2.4 m below grade or 0.5 m below the ![image](/image/placeholder) MANIFOLD PIT FOR GROUND LOOP HEAT EXCHANGER VAPOR MANIFOLD VAPOR LOOP 1.2 m DIAMETER VAPOR PIT BASE LINE 0.3 m 0.6 m LIQUID LINE LINE SET TO COMPRESSOR UNIT LIQUID LIQUID LOOP MANIFOLD (A) AERIAL VIEW BACKFILLED WITH SAND REQUIRED VAPOR 0.6 m DEPTH MANIFOLD BELOW GRADE 0.3 m LIQUID MANIFOLD 1.2 m DIAMETER PIT BASE (B) SIDE VIEW FROM TRENCH ENTRANCE Fig. 28 Typical DXGCHP Ground Heat Exchanger Distribution System local frost line, whichever is deeper, to ensure adequate year-round heat exchange with the surrounding ground. DXGCHP heat exchanger lengths and configurations are currently selected using DXGCHP manufacturers' performance tables, which are based on empirical laboratory and field test data accrued over the last 40 years. Generalized analytical techniques for the design and application of DXGCHP ground heat exchanger systems are currently being developed. Using a manufacturer's performance tables requires knowledge of the soil temperature (e.g., from Figure 10), building loads (see ACCA [2008, 2016] and Chapters 17 and 18 of the 2017 ASHRAE Handbook- - Fundamentals), and available land area and geology. Available Land Area and Geology. The available land area, geology at the site, and knowledge and experience of local excavators and drillers influence the selected configuration of the ground heat exchanger. The specifier may make a preliminary selection of the ground loop configuration before sizing the system. In general, if the job site has relatively level land and enough space is available, excavating and installing a horizontal pit or trench ground loop system is economically attractive. There must be adequate space to put the excavated earth. Horizontal ground loops can also be installed by horizontally boring (see Figure 3). If vertical ground loops are to be installed, the required drilling will disturb far less surface space than horizontal systems. Vertical systems for capacities up to 21 kW can be installed within a surface footprint of only 2.5 m diameter, which makes this configuration well suited for installation where ground surface area is limited. In addition, borehole diameters of 76 mm for each ground loop allow use of small, maneuverable drill rigs. Inc. ASHRAE, 2019 user. single for Licensed | {}
47437f84-cdec-46cc-9a71-a37357ab79ea | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 35.30 2019 ASHRAE Handbook- -HVAC Applications (SI) Site geology, including soil composition and associated thermal conductivity, is a major factor in selecting the appropriate ground loop configuration with sufficient ground loop surface area for effective heat transfer. DXGCHP manufacturers provide tables for selecting ground heat exchanger configurations and surface areas that accommodate various soil thermal conductivities. Sufficient soil samples should be taken from the ground loop field and analyzed for pH and potentially corrosive elements. If corrosive elements are present beyond the manufacturer's stated threshold levels, an alternative acceptable location for the ground heat exchanger system is required. Ground Heat Exchanger Corrosion Protection System DXGCHP ground heat exchangers are typically constructed of copper because of its high thermal conductivity and compatibility with refrigerant system pressures; annealed copper tubing is malleable, making it easy to install. Because it is a noble metal, it is almost impervious to corrosion from soils found worldwide. However, copper is still vulnerable to corrosion in aggressive soils, and must be protected. The simplest way to prevent corrosion is to apply cathodic protection by connecting the copper to another metal, typically zinc, which is more easily corroded. The sacrificial metal corrodes instead of the protected copper. Although this method of corrosion protection is low cost and easy to apply, a major drawback is that corrosion protection fades over time as the sacrificial metal deteriorates. The sacrificial metal must be replaced to maintain an adequate level of corrosion protection. A more effective means of protecting copper in aggressive soils is the impressed current cathodic protection (ICCP) system (Figure 29). This system provides an electronically regulated continuous current from a titanium anode covered with a mixed- metal oxide, to the copper ground loops, resulting in superior long- term ground heat exchanger system durability and performance. DXGCHP manufacturers design ICCP systems as integral, matched components of specific DXGCHP systems to ensure superior corrosion protection for the ground heat exchanger, thus eliminating the need for the specifier to attempt designing the ICCP system separately. Part of the specification process includes contacting local utilities to learn whether there are existing underground impressed current protection systems, and the ![image](/image/placeholder) COMPRESSOR UNIT ELECTRONIC CONTROL INSULATED ANODE CABLE TITANIUM ANODE CURRENT PROTECTED PATH EARTH LOOP (CATHODE) Fig. 29 Typical Impressed Current Protection System effective range of those systems, the proximity of which could potentially interfere with the DXGCHP ground heat exchanger protection system. 1.5 OPEN-LOOP GROUNDWATER HEAT PUMP SYSTEM COMPONENTS A groundwater heat pump system (GWHP) removes groundwater from a well and delivers it to a heat pump (or an intermediate heat exchanger) where heat is absorbed from or rejected to the water. Both unitary and central plant designs are used. In the unitary type, a large number of small water-to-air heat pumps are distributed throughout the building. The central plant design uses one or a small number of large-capacity chillers supplying hot and chilled water to a two- or four-pipe distribution system. The unitary approach is more common and tends to be more energy-efficient. Direct systems (in which groundwater is pumped directly to the heat pump without an intermediate heat exchanger) are not recommended except on the very smallest installations. Although some systems of this design have been successful, many have had serious difficulty even with groundwater of apparently benign chemistry. Thus, prudent design for commercial/industrial-scale projects isolates groundwater from the building system with a heat exchanger. The increased capital cost of installing the heat exchanger is only a small percentage of the total cost and, in view of these systems' greatly reduced maintenance requirements, is quickly recovered. Past GWHP systems sometimes used surface disposal (to rivers, lakes, drainage ditches, etc.) of the groundwater. Current standards use reinjection instead, because it eliminates the potential for negative effects on the aquifer water level over time and preserves the positive environmental character associated with GSHP systems. Regardless of the type of equipment installed in the building, the specific components for handling groundwater are similar. Primary items include (1) wells (supply and injection), (2) well pump and controls, and (3) groundwater heat exchanger. Some specifics of these items are discussed in the Direct-Use Geothermal Energy section of this chapter. In addition to those comments, the following considerations apply specifically to unitary GWHP systems using a groundwater isolation heat exchanger. w ater Wells This section includes information on water wells that is generally common to both direct-use and groundwater heat pump (GWHP) systems. Water well open-loop systems and standing column well best practices are covered in ANSI/CSA/IGSHPA Standard C448-16. An aquifer is a geologic unit that can yield groundwater to a well in sufficient quantities to be of practical use (UOP 1975). Aquifers can exist in areas where water is present in conjunction with pore spaces in the subsurface materials sufficient to allow the water to move laterally. In many projects, construction of the well (or wells) is handled through a separate contract between the owner and the driller or a hydrology/hydrogeology consultant. As a result, the engineer is not responsible for its design. However, because design of the building system depends on the wells' performance, it is critical that the engineer be familiar with water well terminology and test data. The most important consideration with regard to the wells is that they be completed and tested (for flow volume and water quality) before final system design, in much the same way that ground thermal properties testing precedes GCHP system design. Inc. ASHRAE, 2019 user. single for Licensed | {}
ad80e47e-6fd9-435b-b10f-16279caffc78 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Geothermal Energy 35.31 ![image](/image/placeholder) MOTOR GROUND LEVEL STATIC WATER LEVEL CONE OF DEPRESSION DRAWDOWN PUMPING WATER LEVEL BOWL ASSEMBLY GROUT SEAL PRODUCTION CASING SCREEN PERFORATED CASING OR OPEN HOLE GROUNDWATER (WATER INTAKE) PRODUCTION ZONE Fig. 30 Water Well Terminology Figure 30 illustrates some important well terms. Several references (Anderson 1984; Campbell and Lehr 1973; EPA 1975; Roscoe Moss Company 1985) cover well drilling and well construction in detail. Static water level (SWL) is the level that exists under static (nonpumping) conditions. In some cases, this level is much closer to the surface than that at which the driller encounters water during drilling. Pumping water level (PWL) is the level that exists under specific pumping conditions. Generally, this level is different for different pumping rates (higher pumping rates mean lower pumping levels). The difference between the SWL and the PWL is the drawdown. The well's specific capacity may be quoted in L/s per metre of drawdown. For example, for a well with a static level of 15 m that produces 30 L/s at a pumping level of 25 m, drawdown = 25 15 = 10 m; specific capacity = 30/10 = 3.0 L/s per metre. w ater entrance velocity (through the screen or perforated casing) can be an important design consideration. Velocity should be limited to a maximum of 0.03 m/s (0.015 m/s for injection wells) to avoid incrustation of the entrance openings. The pump bowl assembly (impeller housings and impellers) is always placed sufficiently below the expected pumping level to prevent cavitation at the peak production rate. For the previous example, this pump should be placed at least 30 m below the casing top (pump setting depth = 30 m) to allow for adequate submergence at peak flow. Along with any expected annual aquifer water level fluctuations, the specific NPSH pressure required for a pump varies with each application and should be carefully considered in selecting the setting depth along with any expected annual aquifer water level fluctuations. For the well pump, total pump pressure is composed of four primary components: lift, column friction, surface requirements, and injection head (pressure). Lift is the vertical distance that Table 19 Nominal Well Surface Casing Sizes ¦ Pump Bowl Diameter, mm ¦ Suggested Casing Size, mm ¦ Minimum Casing Size, mm ¦ Submersible Flow Range 3450 rpm, L/s ¦ Lineshaft Flow Range, 1750 rpm, L/s ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 100 ¦ 150 ¦ 125 ¦ 5 ¦ 3 ¦ ¦ 150 ¦ 250 ¦ 200 ¦ 5 to 22 ¦ 3 to 11 ¦ ¦ 180 ¦ 300 ¦ 250 ¦ 16 to 38 ¦ 9 to 17 ¦ ¦ 200 ¦ 300 ¦ 250 ¦ 22 to 50 ¦ 16 to 30 ¦ ¦ 230 ¦ 360 ¦ 300 ¦ 30 to 53 ¦ 17 to 34 ¦ ¦ 250 ¦ 360 ¦ 300 ¦ 30 to 63 ¦ ¦ ¦ 300 ¦ 400 ¦ 360 ¦ 57 to 82 ¦ ¦ water must be pumped to reach the surface. In the example, lift is 25 m. The additional 5 m of submergence imposes no static pump head (pressure). Column friction, the friction loss in the pump column between the bowl assembly and the surface, is calculated from pump manufacturer data in a similar manner to other pipe friction calculations (see Chapter 22 of the 2017 ASHRAE Handbook- Fundamentals). Surface pressure requirements account for friction losses through piping, heat exchangers, and controls, and in many applications are between 8 and 11 m. Injection pressure requirements are a function of well design, aquifer conditions, and water quality. In theory, an injection well penetrating the same aquifer as the production well experiences a water level rise (assuming equal flows) that mirrors the drawdown in the production well. Using the earlier example, an injection well with a 15 m static level would experience a water level rise of 10 m, resulting in a surface injection pressure of 10 15 = 5 m (i.e., a water level that remains 5 m below the ground surface). Thus, no additional pump head is required for injection in the example. In practice, injection pressure requirements usually exceed the theoretical value. With good (non-scaling) water quality, careful drilling, and little sand production, injection pressure should be near the theoretical value. For poor water quality, high sand production, or poor well construction, injection pressure may be 10 to 40% higher. The well casing diameter depends on the diameter of the pump (bowl assembly) necessary to produce the required flow rate. Table 19 presents nominal casing sizes for a range of water flow rates. In addition to the production well, most systems should include an injection well to dispose of the fluid after it has passed through the system. Injection stabilizes the aquifer from which the fluid is withdrawn by reducing or eliminating long-term drawdowns, and helps to ensure long-term productivity. Construction of injection wells differs from production wells primarily in the recommended screen velocity (0.015 m/s, or 1/2 that of production wells) and well sealing design. Injection wells, particularly those likely to be subject to positive injection pressure, should be fully cased and sealed from the top of the injection zone to the surface. It is commonly thought that wells, particularly injection wells, often fail, but failure is more often attributable to the designer than to the well itself. The most common factors in reduced water well (production and injection) performance are incrustation and biofouling of screens, formation plugging with fines, sand pumping, casing/screen collapse, and pump problems (Driscoll 1986). To a large extent, incrustation and biofouling can be reduced by minimizing drawdown through careful well design and the avoidance of excessive groundwater flows. Material selection appropriate for the water chemistry and avoidance of substandard casing and screen products can reduce or eliminate failures in these components. Sand production should be limited by screen, gravel pack, and development practices, or removed by strainers before injection. With such good practices, maintenance intervals can be reduced to approximately 10 to 15 years in favorable conditions, Inc. ASHRAE, 2019 user. single for Licensed | {}
1e07ffc0-5635-4633-934a-fd8cea87ce26 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 35.32 and 5 to 8 years in unfavorable settings. One key to successful water well operations is effective monitoring: regular testing of well yield, drawdown, specific capacity, and sand production, coupled with periodic review of trends in these parameters. Flow Testing When possible, well testing should be completed before mechanical design. Only with actual flow test data and water chemical analysis information can accurate design proceed. Flow testing can be divided into three different types of tests: rig, short-term, and long-term (Stiger et al. 1989). Rig tests are generally very short and are accomplished while the drilling rig is on site. The primary purpose of this test is to purge the well of remaining drilling fluids and cuttings and to get a preliminary indication of yield. The length of the test is generally governed by the time required for the water to run clean. The rate is determined by the available pumping equipment. Frequently, the well is blown (pumped with the drilling rig s air compressor). As a result, limited information about the well' s production characteristics is available from a rig test. If the well is air lifted, it may not be useful to collect water samples for chemical analysis because certain chemical constituents may be oxidized by the compressed air. Properly conducted, short-term, single-well tests lasting 4 to 24 h yield information about well flow rate, temperature, drawdown, and recovery. These tests are used most frequently for direct-use and GWHP applications. The test is generally run with a temporary electric submersible pump or lineshaft turbine pump driven by an internal combustion engine and are often performed by a well pump contractor. A step test (Table 20), the most common type, involves at least three production rates, the largest being equal to the design flow rate for the system served. The three points are the minimum required to determine a productivity curve for the well that relates production to drawdown (Stiger et al. 1989). The key parameters monitored during these tests are well water level and water flow. Water level and pumping rate should be stabilized at each point before flow is increased. In many cases, water level is monitored with a bubbler or an electric sounder, and flow is measured using an orifice meter. More sophisticated instrumentation (e.g., pressure transducers for water level, magnetic flow meters, data loggers) can also be used. Short-term testing is generally used for small projects and provides information on yield, drawdown, and specific capacity. Test results should reflect stable flow rates, and individual flow steps are extended until water level readings stabilize. In many cases, brief intervals of turbidity may occur at flow changes, but extensive periods of turbidity indicate instability in the near-well formation. Long-term tests of up to 30 days provide information on the reservoir. Normally, these tests involve monitoring nearby wells to evaluate interference effects. The data are useful in calculating transmissivity and storage coefficient, reservoir boundaries, and recharge areas (Stiger et al. 1989) but are rarely used for direct-use and GWHP systems. It is also important to collect background information before the test, and water level recovery data after pumping has ceased. Recovery data in particular can be used to evaluate skin effect, which is a type of well flow resistance caused by residual drilling fluids, insufficient screen or slotted liner area, or improper filter pack. Groundwater Quality The importance of groundwater quality depends on the system design. Systems using isolation heat exchangers commonly encounter no water quality issues (other than iron bacteria) that would prevent a GWHP system from operating under reasonable maintenance levels. 2019 ASHRAE Handbook-HVAC Applications (SI) Table 20 Example Well Flow Test Results SWL 21 m ¦ Time Since Pump Start, min ¦ Flow, L/s ¦ Water Level, m ¦ Comments ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 5 ¦ 7.88 ¦ 23.9 ¦ clear ¦ ¦ 10 ¦ 8.02 ¦ 24.2 ¦ clear ¦ ¦ 15 ¦ 7.88 ¦ 24.7 ¦ clear ¦ ¦ 20 ¦ 7.88 ¦ 25.0 ¦ clear ¦ ¦ 25 ¦ 7.88 ¦ 25.3 ¦ clear ¦ ¦ 30 ¦ 7.95 ¦ 25.4 ¦ clear ¦ ¦ 40 ¦ 7.88 ¦ 25.4 ¦ clear ¦ ¦ 50 ¦ 7.88 ¦ 25.4 ¦ clear ¦ ¦ 60 ¦ 7.88 ¦ 25.4 ¦ clear ¦ ¦ 65 ¦ 12.6 ¦ 27.6 ¦ cloudy ¦ ¦ 70 ¦ 12.6 ¦ 29.5 ¦ clear ¦ ¦ 75 ¦ 12.6 ¦ 30.1 ¦ clear ¦ ¦ 80 ¦ 12.6 ¦ 30.3 ¦ clear ¦ ¦ 85 ¦ 12.7 ¦ 30.4 ¦ clear ¦ ¦ 90 ¦ 12.6 ¦ 30.5 ¦ clear ¦ ¦ 100 ¦ 12.6 ¦ 30.5 ¦ clear ¦ ¦ 120 ¦ 12.6 ¦ 30.5 ¦ clear ¦ ¦ 125 ¦ 18.6 ¦ 39.8 ¦ cloudy ¦ ¦ 130 ¦ 18.9 ¦ 41.4 ¦ cloudy ¦ ¦ 135 ¦ 19.0 ¦ 42.8 ¦ clear ¦ ¦ 140 ¦ 18.9 ¦ 43.1 ¦ clear ¦ ¦ 160 ¦ 18.9 ¦ 43.4 ¦ clear ¦ ¦ 170 ¦ 18.9 ¦ 44.4 ¦ clear ¦ ¦ 180 ¦ 18.9 ¦ 44.4 ¦ clear ¦ For systems that use groundwater directly in heat pump units (e.g., standing-column systems and small residential GWHP systems), several issues are of concern. The primary water quality problem in the United States is scaling, usually of calcium carbonate (lime). Because this type of scaling is partially temperature driven, the temperature of surfaces that groundwater contacts determines the extent to which scaling will occur. In these systems, peak temperatures in the refrigerant-to-water exchanger in cooling mode are likely to be over 70°C. For the same system using an isolation plate heat exchanger, the groundwater is unlikely to encounter temperatures over 32°C. Using the plate heat exchanger reduces the propensity for scaling and limits any scale that does occur to a single heat exchanger. Rafferty (2000b) provides information on water scaling potential on a state-by-state basis. Hydrogen sulfide can destroy the oxide layer on copper, copper- nickel alloys, and stainless steels, and make these metals vulnerable to acidic corrosion. Titanium heat exchangers are recommended for hydrogen-sulfide-bearing waters. Excessive iron, particularly ferrous iron, in the water can result in coating of heat transfer surfaces if the water is exposed to air (allowing the iron to oxidize to the ferric state, a form with much lower solubility in water). Periodically removing this iron from the plates of a single heat exchanger is much less labor intensive than removing it from tens or hundreds of individual heat pump heat exchangers. Table 21 summarizes the minimum parameters that should be evaluated for a GWHP application. Particulate matter (e.g., sand) in the groundwater stream, although usually not a problem in the mechanical system, can effectively plug injection wells. Sand production should be addressed in construction of the production well (screen/gravel pack/development). Ifit must be dealt with on the surface, a screen or strainer is preferable to a centrifugal separator, which can be ineffective at start-up and shutdown and can experience variable flow (Kavanaugh and Rafferty 2014). Perforation size selection is critical to a strainer's effectiveness, and should be based on 90 to Inc. ASHRAE, 2019 user. single for Licensed | {}
eaca354b-a8a4-4e8e-b6f9-194396fe91b3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Geothermal Energy 35.33 Table 21 Water Chemistry Constituents ¦ Quality ¦ Comment ¦ ¦ --- ¦ --- ¦ ¦ pH ¦ Typical range: 6.5 to 9.0. Lower values typically associated with higher rates of general corrosion in ferrous and copper alloys; higher values associated with scaling. ¦ ¦ TDS ¦ Total dissolved solids: gross indicator of quantity of dissolved constituents. Higher levels associated with increased corrosion and/or scaling; used in calculation of scale index. ¦ ¦ Fe ¦ Iron: use care to prevent exposure to air; problems possible at 0.5 ppm. ¦ ¦ Total M alkalinity ¦ Ability of water to buffer acid; strongly linked to scale and used to calculate scaling index. Usually expressed as ppm CaCO3. ¦ ¦ Ca ¦ Calcium ion: linked to scaling of water and used to calculate scaling index. Expressed in ppm Ca X 0.5 = ppm as CaCO3. ¦ ¦ CO3/HCO3 ¦ Carbonate/bicarbonate: varies in concentration with pH. ¦ ¦ Hardness ¦ Linked to scaling and used to calculate scale index; at 100 ppm, scaling can occur. Expressed in ppm or g/m3. ¦ ¦ C1 ¦ Chloride: accelerates corrosion of carbon and stainless steels; may be elevated in coastal areas. ¦ ¦ Mn ¦ Manganese: causes black scale; possible deposits at 0.2 ppm. ¦ ¦ O2 ¦ Oxygen: dissolved gas; accelerates corrosion; promotes other reactions; test in field. ¦ ¦ H2S ¦ Hydrogen sulphide: dissolved gas; rotten egg odor 0.5 ppm; attacks copper alloys; test in field. ¦ ¦ CO2 ¦ Carbon dioxide: dissolved gas, often present at pH 7.5, test in field. GW pressurization keeps CO2 in solution. ¦ Stability index (Ryznar Originally developed to predict corrosion but used in GWHP for index) scaling prediction; calculated from temperature, Ca, TDS, alkalinity, and hardness. Must use temperature reflective of application: 29°C for systems with plate heat exchanger, 66°C Saturation index for nonisolated systems. (Langlier Similar to stability index. Originally developed to predict index) corrosion but used in GWHP for scaling prediction; calculated from temperature, Ca, TDS, alkalinity, and hardness. Must use temperature reflective of application: 29°C for systems with plate heat exchanger, 66°C for nonisolated systems BART Bacteriological activity reaction test: broad indicator of various bacteria. Most common tests are for iron-reducing (IRB), slime-forming (SLYM), and sulfate-reducing (SRB) bacteria. Source: Rafferty (2008). 100% removal of the particulate material. Particle size information can be based on the sieve analysis results of drill cuttings (used to size the well screen) or of a sample taken during well flow testing. In applications with very fine sand, multiple strainers in parallel may be necessary to control pressure drop (Rafferty 2008). Well Pumps Submersible pumps have not performed well in higher- temperature, direct-use projects. However, the submersible pump is a cost-effective option with normal groundwater temperatures, as encountered in heat pump applications. The low temperature eliminates the need to specify an industrial design for the motor/ protector, thereby greatly reducing the first cost relative to direct use. Caution should still be used for wells that are expected to produce moderate amounts of sand. The high speed (nominal 60 Hz) of most submersible pumps makes them susceptible to erosion damage. Applications with sand/particles greater than 400 to 600 m should specify sand fighter submersible pump configurations. Small groundwater systems have frequently been identified with excessive well pump energy consumption. The reasons for excessive pump energy consumption (high water flow rate, coupling to the domestic pressure tank, and low efficiency of small Table 22 Controller Range Values for Dual Set-Point Well Pump Control* ¦ ¦ Building Loop Thermal Mass in L/kW of Peak Block Cooling Load ¦ Building Loop Thermal Mass in L/kW of Peak Block Cooling Load ¦ Building Loop Thermal Mass in L/kW of Peak Block Cooling Load ¦ Building Loop Thermal Mass in L/kW of Peak Block Cooling Load ¦ Building Loop Thermal Mass in L/kW of Peak Block Cooling Load ¦ Building Loop Thermal Mass in L/kW of Peak Block Cooling Load ¦ Building Loop Thermal Mass in L/kW of Peak Block Cooling Load ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ 2.15 ¦ 4.31 ¦ 6.46 ¦ 8.61 ¦ 10.76 ¦ 12.91 ¦ 15.07 ¦ ¦ Cooling range, K ¦ 17 ¦ 9 ¦ 6 ¦ 4 ¦ 3 ¦ 3 ¦ 2 ¦ ¦ Heating range, K ¦ 10 ¦ 5 ¦ 3 ¦ 2 ¦ 2 ¦ 2 ¦ 2 ¦ Source: Rafferty (2000c). *Table values for pumps 3.7 kW. For pumps 3.7kW, three-phase range values may be reduced by 50%, submersible pumps) are generally not present in large, commercial groundwater systems. In large systems, the groundwater flow per unit capacity is frequently less than half that of residential systems. Pressure at the wellhead is not the 200 to 350 kPa typical of domestic systems, but is rather a function only of pressure losses through the groundwater loop. Finally, large well pumps have efficiencies of up to 83% compared to the 35 to 40% range for small submersible pumps. In GWHP system design, the control method for the well pump determines the extent to which the optimum relationship between well pump power and heat pump power is preserved at off-peak conditions. There are several ways the pump can be controlled. Multiple pumps can be staged to meet system loads, either with multiple wells or with multiple pumps installed in a single well. A dual set-point control similar to that used in boiler/tower systems energizes the well pump above a given temperature in cooling mode and below a given temperature in heating mode. Between those temperatures, the building loop floats without the addition of groundwater. To control well pump cycling, it is necessary to establish a temperature range (difference between pump-on and pump-off temperatures) over which the pump operates in both the heating and cooling modes. The size of this range is primarily a function of the building loop water volume in terms of litres per peak per kilowatt of peak block system load (Rafferty 2000c). Table 22 summarizes these data. In the example in Table 23, the optimum system building loop return temperature (at peak system EER) is 27.0°C. Ifthis system had a water volume of 8.61 L/kW, from Table 22, a range of 4 K in cooling mode would be required. This range would result in a well pump start temperature of 27.0 + (4/2) = 29°C and a well pump stop temperature of 27.0 - (4/2) = 25°C. A similar calculation can be made for heating mode. From Table 22, for systems with very low thermal mass, the dual set-point method of control becomes impractical because of the very large temperature range required. For these applications, an alternative method of control (variable speed, staging, etc.) is required. Well pumps may also be controlled using a variable-speed drive, which responds to building loop return temperature by varying groundwater flow to the exchanger to maintain the cooling or heating mode set point. Submersible-motor variable-speed applications are somewhat different than surface motor applications. Most manufacturers limit speed reduction to 50%, and other issues such as minimum water velocity for motor cooling, switching frequency, reactor requirement, and motor protection must be addressed. Additional information on VFD applications for submersible motors is available in Rafferty (2008). Heat Exchangers Design of a plate-and-frame heat exchanger is largely a trade- off between pressure drop, which influences pumping (operating cost), and overall heat transfer coefficient, which influences surface area (capital cost). In general, exchangers in GWHP systems can be economically selected for approach temperatures (between loop return and groundwater leaving temperatures) as low as 1.7 K. Most selections involve an approach of between 1.7 Inc. ASHRAE, 2019 user. single for Licensed | {}
a3c88fe2-ea17-46e9-ba6c-26fea93b2407 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 35.34 2019 ASHRAE Handbook-HVAC Applications (SI) and 3.9 K and a pressure drop of less than 70 kPa on the building loop side. Excessive fouling factors (>3.5 10-5 [m2.K]/W) should not be specified when selecting plate heat exchangers, which can be easily disassembled and cleaned. Heat exchanger cost may be reduced for groundwater applications by using Type 304 stainless steel plates rather than the Type 316 or titanium plates common in direct-use projects. The low temperature and generally low chloride content of heat pump fluids frequently make the less expensive Type 304 material acceptable. Chloride content of the groundwater, particularly in coastal areas, should always be compared to values in Figure 40 to determine plate material acceptability. Exchanger performance should be checked at minimum system flow rates to ensure adequate heat transfer. In some cases, very low design pressure drop selections can encounter inadequate heat transfer at minimum flows. 1.6 OPEN-LOOP GROUNDW ATER HEAT PUMP SYSTEM DESIGN Extraction Well Commercial Systems This section applies to systems with an extraction well and means to return the water elsewhere, such as reinjection wells or surface disposal. An open-loop system design must balance well pumping power with heat pump performance. As groundwater flow increases through a system, more favorable average temperatures are produced for the heat pumps. Higher groundwater flow rates, to a point, increase system EER or COP: increased well pump power is outweighed by decreased heat pump power requirements (because of the more favorable temperatures). At some point, additional increases in groundwater flow result in a greater increase in well pump power than the resulting decrease in heat pump power. The key strategy in open-loop system design is identifying the point of maximum system performance with respect to heat pump and well pump power requirements. Once this optimum relationship has been established for the design condition, the method of controlling the well pump determines the extent to which the relationship is preserved at off-peak conditions. This optimization process involves evaluating the performance of the heat pumps and well pump(s) over a range of groundwater flows. Key data necessary to make this calculation include well performance (flow and drawdown at various groundwater flows) and heat pump performance versus entering water temperatures at different flow rates. Well information is generally derived from well pump test results. Heat pump performance data are available from the manufacturer. GWHP systems employ the same type of extended-range unitary heat pumps as GCHP systems. Building loop pumping guidelines (see Table 6) in the GCHP portion of this chapter also apply to GWHP systems. In large commercial applications, the head loss associated with the isolation heat exchanger in a GWHP system is typically lower than that of an equivalently sized ground heat exchanger in a GCHP system. A guideline for building loop head loss in a GWHP system can be described as follows: Building loop head loss (kPa) = 84 + 0.01d where d = pipeline distance m from plate heat exchanger outlet to most distant heat pump unit inlet. This calculation assumes a maximum pressure loss of 4 kPa/10 m, fittings at 25% of total pressure loss, and a heat pump unit pressure loss of 36 kPa. Because of more extensive fittings, retrofits can sometimes exceed this value. For moderate-efficiency heat pumps (COP of 4), efficient loop pump design (0.016 W/W), and a heat exchanger approach of 1.5°C, Figure 31 provides curves for two different groundwater temperatures (GWT = 10 and 18°C) and two well pump situations GWHP SYSTEM EFFICIENCY WITH GROUNDWATER FLOW RATE Chart Type: line 0.5 0.6 0.7 0.8 0.9 1.0 1.1 1.2 1.3 1.4 1.5 1.6 1.7 1.8 1.9 2.0 2.1 2.2 2.3 2.4 2.5 2.6 2.7 2.8 2.9 3.0 item_01 3.2kW 3.3kW 3.4kW 3.5kW 3.6kW 3.7kW 3.8kW 3.9kW 4.0kW 4.1kW 4.2kW 4.3kW 4.4kW 4.5kW 4.6kW 4.7kW 4.4kW 4.5kW 4.4kW 4.3kW 4.3kW 4.2kW 4.1kW 4.0kW 3.9kW 3.8kW ![image](/image/placeholder) GWT = 10°C/SWL = 23 m/SC = 2L/(s-m) GWT = 10°C/SWL = 91 m/SC = 0.6 L/(sm) GWT = 18°C/SWL = 23 m/SC = 2L/(s·m) GWT = 18°C/SWL = 91 m/SC = 0.6 L/(s·m) Fig. 31 Optimum Groundwater Flow for Maximum System COP SWL is static water level in m, and SC is specific capacity of well in L/(s·m). (Kavanaugh and Rafferty 2014) (static water level [SWL] 23 m/specific capacity 2 L/[s · m] and SWL 91 m/specific capacity 0.6 L/[s · m]). The curves are plotted for constant well pump head, a situation which does not occur in practice. In reality, well pump head rises with flow but at a rate typically less than that in friction head applications. Although the four curves show a clear optimum flow, sometimes operating at a lower groundwater flow reduces well/ pump capital cost and the problem of fluid disposal. These considerations are highly project specific, but do afford the designer some latitude in flow selection. Generally, an optimum design results in a groundwater flow rate that is less than the building loop flow rate. The exception is when groundwater temperatures are less than 8.3°C or greater than 22.2°C. In these situations, the groundwater flow requirement is influenced more by avoiding excessive heat pump EWT in the cooling mode (groundwater temperatures above 22.2°C) and heat pump L WTs that could result in freezing conditions in the heating mode (groundwater temperatures less than 8.3°C). In the case of low water temperatures, some designers have found it advantageous to use antifreeze in the building loop to slightly broaden the allowable loop temperature range. Table 23 provides design data for a specific example system. Central Plant Systems Central plant systems, in which a conventional or heat recovery central chiller is connected to a four-pipe system, are the oldest type of open-loop design, having first been installed in the late 1940s. Because of the cost and energy requirements of the central plant design, these systems typically do not result in the same level of energy efficiency as unitary GWHP systems. For central plant groundwater systems, two heat exchangers are normally used: one in the chilled-water loop and one in the condenser water loop (Figure 32). The evaporator-loop exchanger provides a heat source for heating-dominated operation and the condenser-loop exchanger provides a heat sink for cooling- dominated operation. Sizing the condenser-loop exchanger is based on providing sufficient capacity to reject the condenser load in the absence of any building heating requirement. Inc. ASHRAE, 2019 user. single for Licensed Sizing the chilled-water-loop exchanger must consider two loads. The primary criterion is the load required during heating- dominant operation. The exchanger must transfer sufficient heat | {}
92cfee3f-31c4-4477-a7e5-b42692a45dc7 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Geothermal Energy 35.35 ![image](/image/placeholder) EXPANSION PLATE HEAT EXCHANGER TANK HEATING COILS 42。C CONDENSERS EXPANSION TANK r COOLING COILS 8°C 22°C EVAPORATORS VARIABLE-SPEED DRIVE PLATE HEAT INJECTION EXCHANGER WELL PRODUCTION WELL Fig. 32 Central Plant Groundwater System Table 23 Example GWHP System* Design Data ¦ Heat Pump EWT, °C ¦ Heat Pump LWT, °C ¦ Ground- ¦ Ground- ¦ Ground- ¦ Well Pump Well Head, m ¦ Pump kW ¦ Loop Pump kW System ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Heat Pump EWT, °C ¦ Heat Pump LWT, °C ¦ Heat Pump EER ¦ water LWT, °C ¦ Ground- water Flow, L/s ¦ Well Pump Well Head, m ¦ Pump kW ¦ Loop Pump kW System ¦ ¦ ¦ 16.1 ¦ 22.4 ¦ 5.2 ¦ 20.2 ¦ 18.2 ¦ 78.0 ¦ 23.7 ¦ 4.8 ¦ 3.5 ¦ ¦ 17.2 ¦ 23.6 ¦ 5.1 ¦ 21.4 ¦ 14.7 ¦ 69.7 ¦ 17.5 ¦ 4.8 ¦ 3.7 ¦ ¦ 18.3 ¦ 24.7 ¦ 5.0 ¦ 22.5 ¦ 12.4 ¦ 64.0 ¦ 13.7 ¦ 4.8 ¦ 3.8 ¦ ¦ 19.4 ¦ 25.9 ¦ 4.8 ¦ 23.7 ¦ 10.7 ¦ 60.0 ¦ 11.4 ¦ 4.8 ¦ 3.8 ¦ ¦ 20.6 ¦ 27.0 ¦ 4.7 ¦ 24.8 ¦ 9.4 ¦ 56.7 ¦ 9.7 ¦ 4.8 ¦ 3.8 ¦ ¦ 21.7 ¦ 28.2 ¦ 4.6 ¦ 25.9 ¦ 8.4 ¦ 54.4 ¦ 8.5 ¦ 4.8 ¦ 3.8 ¦ ¦ 22.8 ¦ 29.3 ¦ 4.5 ¦ 27.1 ¦ 7.6 ¦ 52.4 ¦ 7.5 ¦ 4.8 ¦ 3.8 ¦ ¦ 23.9 ¦ 30.4 ¦ 4.4 ¦ 28.2 ¦ 6.9 ¦ 50.9 ¦ 6.7 ¦ 4.8 ¦ 3.8 ¦ ¦ 25.0 ¦ 31.6 ¦ 4.4 ¦ 29.3 ¦ 6.4 ¦ 49.7 ¦ 6.0 ¦ 4.8 ¦ 3.8 ¦ ¦ 26.1 ¦ 32.7 ¦ 4.3 ¦ 30.4 ¦ 5.9 ¦ 48.5 ¦ 5.5 ¦ 4.8 ¦ 3.7 ¦ ¦ 27.2 ¦ 33.5 ¦ 4.2 ¦ 31.6 ¦ 5.6 ¦ 47.5 ¦ 5.1 ¦ 4.8 ¦ 3.6 ¦ ¦ 28.3 ¦ 34.9 ¦ 3.9 ¦ 32.7 ¦ 5.2 ¦ 46.6 ¦ 4.7 ¦ 4.8 ¦ 3.6 ¦ *Block cooling load 300 kW, 15.5°C groundwater, 23 m well static water level, 0.41 L/ (s·m) specific capacity, 11 m surface head losses, 2.2 K heat exchanger approach, 13 L/s building loop flow at 20 m pressure. (when combined with compressor heat) from the groundwater to the chilled-water loop to meet the building's space heating requirement. Depending on the relative groundwater and chilled- water temperatures and on the design temperature rise, exchangers may also provide some free cooling during cooling-dominant operation. If groundwater temperature is lower than that of chilled water returning to the exchanger, some chilled-water load can be met by the exchanger. This mode is most likely available in regions with groundwater temperatures below 15°C. Central plant chiller controls must also allow for the unique oper- ation with a groundwater source. Controls can be similar to those on a heat recovery chiller with a tower, with one important difference. In a conventional heat recovery chiller, waste heat is available only when there is a building chilled-water (or conditioning) load. In a groundwater system, a heat source (the groundwater) is available year round. To take advantage of this source during the heating sea- son, the chiller must be loaded in response to the heating load instead of the chilled-water load. That is, the control must include a heating-dominant mode and a cooling-dominant mode. Two general designs are available for this: · Chiller capacity remains controlled by chilled-water (supply or return) temperature, and groundwater flow through the chilled- water exchanger is varied in response to the heating load ![image](/image/placeholder) MOTORIZED VALVE FLOW CONTROL VALVE TO DISPOSAL HEAT PUMP TO DOMESTIC WATER SYSTEM WATER CONNECTIONS PRESSURE WITH PIT PORTS F MHFCV TANK ○ RAW GROUNDWATER FROM WELL BOILER DRAIN VALVES BALL/SHUTOFF VALVE Fig. 33 Motorized Valve Placement · Chiller capacity is controlled by the heating-water (condenser) loop temperature, and groundwater flow through the chilled- water exchanger is controlled by chilled-water temperature For buildings with a significant heating load, the former may be more attractive, whereas the latter may be appropriate for conven- tional buildings in moderate to warm climates. Extraction Well Residential Systems This section applies to systems with an extraction well and means to return the water elsewhere, such as reinjection wells or surface disposal. Residential groundwater heat pump systems have the same design considerations as commercial groundwater heat pump systems, but differ on three main items: typically they (1) are integrated with a household domestic water system, (2) are single-zone systems, and (3) do not isolate the groundwater from the heat pump unit(s). Groundwater heat pumps are a prudent choice in residential buildings on well water if the groundwater is of good quality. As such, the heat pump can be integrated into the domestic water system and considered another water-using appliance. Design care must be taken to ensure that the well and pressure tank have adequate capacity to handle the additional flow demand of the heat pump. Well pumps may be of the submersible or jet type, and the design groundwater flow rate should be chosen based on its temperature such that the system COP or EER is maximized. Flow control valves are recommended in the discharge line to ensure that the well is not over-pumped. Placement of a slow-closing motorized valve also on the discharge line ensures positive pressure on the heat pump water coil, and stops the flow of water when the heat pump is not operating (Figure 33). Flow control valves may be noisy as they meter flow. This noise can be mitigated by placing the motorized shutoff valve, with its associated pressure drop, after (downstream of) the flow control valve. The pressure tank provides water at pressure on demand without short-cycling the well pump. A prepressurized bladder tank is preferred, and it should be large enough that filling it with the well pump takes at least 1 min. Residential groundwater heat pump systems are small enough that the additional cost of an isolation heat exchanger is typically not economically justified. Raw groundwater is generally used as the heat transfer fluid, but provisions must be made (such as hose bibs or boiler drains) to allow for flushing and descaling of the heat pump water/refrigerant coil if necessary. After exiting the heat pump, groundwater should be returned to a point of discharge in accordance with best practices and/or local codes. Surface discharge to a pond or wetland, or infiltration in to a dry well may be more of an option in these smaller systems than Inc. ASHRAE, 2019 user. single for Licensed | {}
b772570a-7bd0-47fb-b44f-e5b803c539a5 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 35.36 ![image](/image/placeholder) EMERGENCY BLEED SUBMERSIBLE PUMP TAIL PIPE ALLOWS PUMP TO BE SET AT TOP OF BORE GEOTHERMAL HEAT PUMPS TYPICALLY 150 to 460 m 105 to 125 kW/BORE (MAXIMUM) Fig. 34 Commercial Standing-Column Well with larger commercial systems due to the correspondingly lower flow rates. Standing-Column Systems Standing-column systems use the same well to extract and re- inject the water (Figure 34), and consist of a borehole cased in steel or other material until competent bedrock is reached. The casing must be driven 7.5 to 15 m into, and sealed in, the competent bedrock. Bedrock sealing requirements vary by state. The remaining depth of the well is then self supporting through bedrock. Standing-column wells (SCWs) are most practical and cost effective when used in areas with near-surface (<60 m) consolidated bed rock; the long steel/PVC casing needed to reach deeper bedrock can make the systems very expensive. Though standing-column systems have been applied mostly in the northeastern United States, approximately 60% of the country is underlain by near-surface bedrock suitable for the systems. The SCW combines supply and injection wells into one, and does not depend on the presence or flow of groundwater, beyond that of the typical bleed rate of 10 to 20% of total pumped flow (based on a 0.055 L/[s.kW] design flow rate). The bleed circuit effectively extracts water from the SCW by diverting part of the water returning from the heat pump into a reinjection well, storm drain, or roof drain, but generally not into sewer or septic systems. SCWs are always augmented with a bleed circuit to monitor the entering water temperature. Further, the bleed circuit can be used to promote advective flow (bleed circuit reduces water level in SCW and therefore increases flow of groundwater, which is near the undisturbed ground temperature, into the well) to regulate the entering water temperature (Figure 34). The additional advective flow can restabilize (i.e., bring back to far-field temperatures by overflowing smaller amounts of water on command) well water temperatures that are below or above design limits because of variations in rock conductivity, building anomalies, or nonstandard weather patterns. This advective flow is a powerful short-term method of warming and cooling well columns that are beyond design limits. Additional advective flow can be promoted by drawing water from the well for domestic or commercial use. Bleed operation is most critical during winter: entering water temperatures below 4.5 to 5.5°C can result in water leaving the heat pump(s) at less than 1°C, for systems designed for flows of 0.05 L/(s.kW). Adequate control to bleed the SCW or shut the heat pump off (and instead use backup heat) must be provided to avoid freezing the water in the heat exchangers. Water being returned to the bore cannot be allowed to free fall. Free falling water entraps air, which reduces heat exchanger performance and promotes scaling and microbial corrosion. The water should be returned to the SCW using a solid drop pipe, 2019 ASHRAE Handbook-HVAC Applications (SI) typically 7.5 to 15 m below the level of the maximum static water depth. If the drop pipe contains more than 10 m of water, a perfect vacuum is formed. With a vacuum on the return line, the bleed circuit cannot release water, and air will be drawn in. Therefore, a back-pressure device should be installed in the return line between the bleed-circuit tee and the SCW, to maintain a positive gage pressure of 35 to 70 kPa at the bleed-circuit tee. For residential application, a 75 to 150 m well provides a heating/cooling capacity of 7 to 28 kW. A relatively simple SCW is used where a submersible well pump is placed at the bottom of the bore. In many jurisdictions, a single well can function with the dual use of geothermal heat transfer and domestic water. In addition to saving construction costs, this technique enhances advective heat transfer by daily use of domestic water. Dual-use wells typically require (1) the submersible pump to be at a lower elevation than the return drop pipe and (2) installation of a back- flow preventer between the heat pump and the domestic water take-off line. For commercial application, a heating capacity of 370 to 445 kW or cooling capacity of 105 to 125 kW can be expected from a single 460 m deep standing-column well. These estimated capacities assume a 10% (0.055 L/[s.kW]) on command and intermittent advective bleed flow. For deep commercial SCWs more than 152 m, a tail pipe (porter shroud assembly [PSA]) is inserted to form a conduit to draw up water, and an annulus to return water downward (ANSI/CSA/IGSHPA Standard C448-16). This tail pipe is perforated at the bottom to form a diffuser. Water is drawn into the diffuser and up the central riser pipe to the submersible pump. The well pump must be located below the water table in line with the central riser pipe. The tail pipe allows a shorter, reduced-power wire size as well as more accessible well pump service. SCW well bore configurations are based upon casing-to-bedrock size, bedrock bore size, and PSA size. The most common SCW is 400 m deep and uses an 200 mm casing into bedrock pocket, 150 mm rock bore and a 100 mm PSA. The designer can anticipate stable and slightly higher temperature from the well bottom; below 150 m ground water temperatures typically increase by 0.45 to 0.9 K per 100 m. Ideal spacing between SCWs is 15 to 28 m, to inhibit well-to-well thermal interference (Orio et al. 2005). Typically, spacing between SCWs is greater than vertical closed-loop (GCHP) boreholes. Closer spacing affects well field performance and can be evaluated with design software. Additional information on standing-column systems can be found in Spitler (2002). In practice, SCWs are a trade-off between extraction well groundwater systems and GCHPs. Flow testing requirements for SCWs are less extensive than for extraction well groundwater systems. The capacity per bore length is less than extraction well systems because SCWs are recharged by advection of only 10 to 20% of total pumped flow, rather than 100% of flow with extraction wells. The SCW capacities are larger than for closed- loop GCHPs because SCWs promote partial advection; they have lower bore thermal resistance since there is no conduction resistance from grout or plastic pipe; and well depths can be deeper without application problems related to large pressure drop in long, narrow pipes. The U.S. Environmental Protection Agency (EPA) Underground Injection Control program considers standing- column reinjection well water a Class V water use, type 5A7, noncontact cooling water for geothermal heating and cooling. The EPA and equivalent state agencies regard SCW reinjection as a beneficial use. Permitting or notice may be required, depending on average daily water flow rates. SCWs are serviced by qualified well contractors with minimal familiarization training. Inc. ASHRAE, 2019 user. single for Licensed | {}
b85c3520-6886-4eb7-9d6c-3c47e6a8c344 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Geothermal Energy 35.37 1.7 SURFACE WATER HEAT PUMPS Surface water bodies can be very good heat sources and sinks if properly used. In some cases, lakes can be the very best water supply for cooling. Various water circulation designs are possible; several of the more common are presented here. ANSI/CSA/ IGSHPA Standard C448-16 contains guidance for both open- and closed-loop surface water heat exchangers. In a closed-loop system, one or more water-to-water or water- to-air heat pumps are linked to one or more submerged coils or flat plate heat exchangers, referred to as surface water heat exchangers (SWHEs). Heat is exchanged to (cooling mode) or from (heating mode) the lake by the fluid (usually a water/ antifreeze mixture) circulating inside the SWHE. The heat pump transfers heat to or from the air in the building. In an open-loop system, water is pumped from the lake through a heat exchanger and returned to the lake some distance from the point at which it was removed. Thermal stratification of water often keeps large quantities of cold water undisturbed near the bottom of deep lakes. This water is cold enough to adequately cool buildings by simply being circulated through heat exchangers. A heat pump is not needed for cooling, and energy use is substantially reduced. Closed-loop coils may also be used in colder lakes. Heating can be provided by a separate source or with heat pumps in heating mode. As noted previously, precooling or supplemental total cooling are also allowed when water returning to the building is near or below 13°C. Heat Transfer in Lakes Heat is transferred to lakes by three primary modes: radiant energy from the sun, convective heat transfer from the surrounding air (when the air is warmer than the water), and conduction from the ground. Solar radiation, which can exceed 950 W/m2 of lake area, is the dominant heating mechanism, but it occurs primarily in the upper portion of the lake unless the lake is very clear. About 40% of solar radiation is absorbed at the surface (Pezent and Kavanaugh 1990). Approximately 93% of the remaining energy is absorbed at depths visible to the human eye. Convection transfers heat to the lake when the lake surface is cooler than the air. Wind speed increases the rate at which heat is transferred to the lake, but maximum heat gain by convection is usually only 10 to 20% of maximum solar heat gain. Conduction gain from the ground is even less than convection gain (Pezent and Kavanaugh 1990). Lakes are cooled primarily by evaporative heat transfer at the surface. Convective cooling or heating in warmer months contributes only a small percentage of the total because of the relatively small temperature difference between the air and lake surface. At night when the sky is clear, longwave radiation can account for significant amount of cooling. The relatively warm water surface radiates heat to the cooler sky. For example, on a clear night, a cooling rate of up to 160 W/m2 is possible from a lake 14°C warmer than the sky. The last mode of heat transfer, conduction to the ground, does not play a major role in lake cooling (Pezent and Kavanaugh 1990), though it does provide significant heating under winter conditions (Gu and Stefan 1990) when the surface of the lake is frozen. To put these heat transfer rates in perspective, consider a 4000 m2 lake used in connection with a 35 kW heat pump. In cooling mode, the unit rejects approximately 44 kW to the lake. This is 11 W/m2, or approximately 1% of the maximum heat gain from solar radiation in the summer. In winter, a 35 kW heat pump absorbs only about 26 kW, or 6.5 W/m2, from the lake. Chart Type: line Winter Stagnation Spring Overturning Fall Overturning Summer Stagnation Hypolimnsion item_01 1Not specified 2Not specified 3Not specified 4Not specified 1Not specified Fig. 35 Idealized Diagram of Annual Cycle of Thermal Stratification in Lakes Thermal Patterns in Lakes The maximum density of water occurs at 4.0°C, not at the freezing point of 0°C. This phenomenon, in combination with normal modes of heat transfer to and from lakes, produces temperature profiles advantageous to efficient heat pump operation. In the winter, the coldest water is at the surface. It tends to remain at the surface and freeze. The bottom of a deep lake stays 3 to 5 K warmer than the surface. This condition is referred to as winter stagnation. The warmer water is a better heat source than the colder water at the surface. As spring approaches, the surface water warms until the temperature approaches the maximum density point of 4.0°C. The winter stratification becomes unstable, and circulation loops begin to develop from top to bottom. This condition of spring overturn (Peirce 1964) causes the lake temperature to become fairly uniform. Later in the spring, as water temperatures rise above 7°C, the circulation loops are in the upper portion of the lake. This pattern continues throughout the summer. The upper portion of the lake remains relatively warm, with evaporation cooling the lake and solar radiation warming it. The lower portion (hypolimnion) of the lake remains cold because most radiation is absorbed in the upper zone. Circulation loops do not penetrate to the lower zone, and conduction to the ground is quite small. The result is that, in deeper lakes with small or medium inflows, the upper zone is 21 to 32°C, the lower zone is 4 to 13°C, and the intermediate zone (thermocline) has a sharp change in temperature in a small change in depth. This condition is referred to as summer stagnation. As fall begins, the water surface begins to cool by radiation and evaporation. With the approach of winter, the upper portion begins to cool toward the freezing point and the lower levels approach the maximum density temperature of 4.0°C. An ideal temperature- versus-depth chart is shown in Figure 35 for each of the four seasons (Peirce 1964). Inc. ASHRAE, 2019 user. single for Licensed | {}
2671cbed-f900-4e22-a5d9-e339bcbde2d2 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 35.38 2019 ASHRAE Handbook-HVAC Applications (SI) Many lakes do exhibit near-ideal temperature profiles. However, (1) high inflow/outflow rates, (2) insufficient depth for stratification, (3) level fluctuation, (4) wind, and (5) lack of enough cold weather to establish sufficient amounts of cold water necessary for summer stratification can disrupt the profile. Therefore, a thermal survey of the lake should be conducted or existing surveys of similar lakes in similar geographic locations should be consulted (Hattemer and Kavanaugh 2005). When interpreting survey data, be aware that there are annual variations in temperature profiles that will not be reflected in measurements for a single year. Shallow ponds and lakes often destratify completely. This does not preclude their use for SWHP systems, but does reduce performance in cooling mode and may require larger heat exchangers compared to lakes that remain stratified. The thermal and environmental effects of heat rejection and absorption on larger lakes and streams have been studied (Bashyum et al. 2017; Hattemer et al. 2006; Spitler and Mitchell 2016). However, the effect of SWHPs on thermal stratification profiles is not well characterized, and there is a lack of experimental data. The relative importance of heat transfer modes is not well known, especially during heating mode. There are no publicly available design tools that consider the many heat and mass flow modes of lakes, streams, and oceans. The model of unstratified ponds developed by Chiasson et al. (2000b) has been implemented in publicly available energy calculation programs, but its lack of accounting for stratification, freezing on the coil, or freezing at the surface limits its usefulness for analysis of deeper lakes and operation in heating mode. The model developed by Spitler et al. (2012) accounts for stratification and for freezing both on the coil and at the surface, but makes several approximations such as neglecting inflows, outflows, and water level variations. Furthermore, validation of all such models is necessarily limited to a small number of lakes for which experimental data are available. Therefore, some caution in using such tools is warranted. It would be ideal to have a set of statistically characterized temperature profiles (e.g., 1% and 99% design temperature profiles), but the data simply do not exist. With few exceptions, lake temperature profiles are measured infrequently, if at all. Available sources with significant quantities of data include the Consortium of Universities for the Advancement of Hydrologic Science's Hydrologic Information System (CUAHSI HIS 2017), the U.S. EPA 's STORET database (EPA 2017), and the U.S. Geological Survey (USGS 2017). Closed-Loop Lake Water Heat Pump Systems The closed-loop SWHEs shown in Figure 36 have several advan- tages over the open loop: · Fouling is reduced because clean water (or water/antifreeze solu- tion) circulates through the heat pump · Pumping-power requirement is lower because there is no eleva- tion head from the lake surface to the heat pumps · It is the only type recommended with unitary heat pumps if a lake temperature below 4°C is possible: fluid outlet temperature is about 3 K below that of the inlet at a flow of54 mL/s per kilowatt, and icing occurs on heat exchanger surfaces when the lake water temperature is in the 1 to 3°C range Disadvantages of closed-loop systems include the following: · Heat pump performance decreases slightly because circulation fluid temperature drops 2 to 7 K below lake temperature · Coils may be damaged in public lakes; thermally fused polyeth- ylene loops are much more resistant to damage than copper, glued plastic (PVC), or tubing with band-clamped joints · Fouling can occur on the outside of the lake coil, particularly in murky lakes or where coils are located on or near the lake bottom. High-density polyethylene (HDPE 3408) is recommended for in- lake piping. All connections must be either thermally socket-fused or butt-fused. These plastic pipes should also have protection from UV radiation, especially when near the surface. Polyvinyl chloride (PVC) pipe and plastic pipe with band-clampedjoints are not recommended. Plate heat exchangers are also available, and manufacturers typically provide estimated capacities for specified conditions. However, use care in applying metal heat exchangers in cold climates. For an equal temperature difference between the reservoir and fluid inside the coil, the surface temperature of metal heat exchangers is closer to the freezing point of water. The higher thermal resistance of HDPE results in a larger required surface area and a much lower heat transfer per unit of surface area. Thus, the surface temperature of an adequately designed HDPE coil tends to be higher than that of a metal tube or plate and less likely to develop ice on the coil exterior. In certain circumstances, ice build-up may occur on the closed-loop SWHE nonetheless. Use proper methods for anchoring the SWHE to resist the upward buoyant force caused by ice build-up. The piping networks of closed-loop systems resemble those used in ground-coupled heat pump systems. Both a large- diameter header between the heat pump and lake coil and several parallel loops of piping in the lake are required. Loops are spread out to limit thermal interference, hot spots, and cold pockets. Although this layout is preferred in terms of performance, installation is more time consuming. Many contractors simply unbind plastic pipe coils and submerge them in a loose bundle. Some compensation for thermal interference is obtained by making bundled coils longer than the spread coils. A diagram of this type of installation is shown in Figure 36A. Copper coils have also been used successfully. Copper tubes have a very high thermal conductivity, so coils only one-fourth to one-third the length of plastic coils are required. However, copper pipe does not have the durability of HDPE 3408, and if fouling is possible, coils must be significantly longer. Open-Loop Lake Water Heat Pump and Direct Surface Cooling Systems Open-loop surface water heat pump systems use heat pumps or chillers to provide heating and/or cooling, with surface water ![image](/image/placeholder) INSERT SPACERS (~6 mm) TO ENHANCE NATURAL CONVECTION HDPE TUBING WITH UV PROTECTION (A) HDPE LAKE COIL AIR-FILLED PLASTIC STABILIZER TUBES TO PROVIDE BUOYANCY. DURING INSTALLATION SUPPLY AND RETURN HEADER CONNECTIONS 00 FLOW PATH 000 STAINLESS STEEL (OR TITANIUM) PLATE HEAT EXCHANGERS (B) PLATE LAKE COIL Fig. 36 SWHEs: (A) HDPE Coil Type and (B) Plate Type Inc. ASHRAE, 2019 user. single for Licensed | {}
38234e07-7c8b-4549-a37d-75160e0ab9b5 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Geothermal Energy 35.39 circulating through a heat exchanger to provide the heat source and/or sink. The heat pumps may be unitary or custom built. Direct surface water cooling (DSWC) systems use cold lake or sea water to provide cooling without heat pumps. Because the total (horizontal + vertical) distance between the building(s) being cooled and the actual location of the cold water is often significant, the scale of the system that is economically feasible tends to be quite large. In cases where the lake or sea water may not be cool enough to meet all demands, hybrid systems that can provide cooling with or without heat pumps or chillers have also been used. Published descriptions of all three types of systems have been reviewed by Mitchell and Spitler (2013). As noted previously, open-loop systems with unitary heat pumps are not suitable for lake temperatures below 4.4°C because of the risk of freezing in the evaporator. However, larger installations that use custom-designed heat pumps are successfully operated in Scandinavia under even colder conditions. Their capacities can be as large as 30 MW. One such system takes water from the Baltic Sea at 3°C and returns it at 0.5°C using falling film evaporators (i.e., plate evaporators with the sea water sprayed on to the outside of the evaporator) (Mitchell and Spitler 2013). Open-loop systems are generally designed with either a submersible pump in a wet sump pit connected to the water body or with a conventional centrifugal pump in a dry sump pit. Itis also possible in some applications to place the pump Just above the water level. Small (e.g., residential) systems are sometimes installed with a submersible pump in the water body. Design guidelines for open-loop systems may be summarized as follows: · HDPE is recommended for pipelines because of its flexibility, durability, and high thermal resistance. HDPE is also fusible and floats in water, which makes it possible to connect large sections of pipe together for surface installation. · Design intakes to avoid entrainment and impingement of sedi- ment and fish. A radial wedge wire intake screen with 2 to 10 mm openings placed 2 to 3 m above the lake or seabed is recom- mended. Limit screened face velocity to 0.15 m/s. · For direct surface water cooling applications, intake water tem- perature should be no higher than 13°C for space air dehumidification. Water with higher temperatures may also be used for sensible only cooling or precooling. · Pumps may be configured in a wet-sump or dry-sump configura- tion. For wet-sump pumping designs, a large-diameter intake pipeline or a deep sump pit may be necessary to achieve the required flow rate. For dry-sump pumping configurations, avail- able net positive suction head should be calculated carefully to check against the pump specifications. Pump material should be chosen to resist corrosion and erosion. · Heat exchangers operating in salt water should be constructed from titanium; those operating in freshwater may use stainless steel. Water quality should be tested and verified. · Heat exchanger fouling may be a problem in warmer climates. Methods for addressing this concern include chlorine dosing, per- manently installed brush systems, or disassembly and cleaning. · Heat pumps for larger systems are typically custom designed units. If used for heating, multistage compression is common. · Outfall structures should discharge at a depth that will not pro- mote nutrient enhancement of the outfall area. They should also discharge near the lake or seabed and cover a large enough area so as to prevent a high thermal gradient in the source water body. 2. DIRECT-USE GEOTHERMAL ENERGY 2.1 RESOURCES Geothermal energy is the thermal energy in the earth's crust: thermal energy in rock and fluid (water, steam, or water containing large amounts of dissolved solids) that fills the pores and fractures in the rock, sand, and gravel. Calculations show that the earth, originating from a completely molten state, would have cooled and become completely solid many thousands of years ago without an energy input beyond that of the sun. It is believed that the ultimate source of geothermal energy is radioactive decay within the earth (Bullard 1973). Through plate motion and vulcanism, some of this energy is concentrated at high temperature near the surface of the earth. Energy is also transferred from deeper parts of the crust to the earth 's surface by conduction and by convection in regions where geological conditions and the presence of water allow. Because of variation in volcanic activity, radioactive decay, rock conductivities, and fluid circulation, different regions have different heat flows (through the crust to the surface), as well as different temperatures at a particular depth. The normal increase of temperature with depth (i.e., the normal geothermal gradient) is about 24 K/km of depth, with gradients of 9 to 48 K/km being common. Areas that have higher temperature gradients and/or higher-than-average heat flow rates constitute the most interesting and viable economic resources. However, areas with normal gradients may be valuable resources if certain geological features are present. Geothermal resources of the United States are categorized into the following types: Igneous point resources are associated with magma bodies, which result from volcanic activity. These bodies heat the surrounding and overlying rock by conduction and convection, as allowed by the rock permeability and fluid content in the rock pores. Hydrothermal convection systems are hot fluids near the earth 's surface that result from deep circulation of water in areas of high regional heat flow. A widely used resource, these fluids rise from natural convection between hotter, deeper formations and cooler formations near the surface. The passageway that provides for this deep convection must consist of adequately permeable fractures and faults. Geopressured resources, present widely in the Gulf Coast of the United States, consist of regional occurrences of confined hot water in deep sedimentary strata, where pressures of greater than 75 MPa are common. This resource also contains methane, which is dissolved in the geothermal fluid. Radiogenic heat sources exist in various regions as granitic plutonic rocks that are relatively rich in uranium and thorium. These plutons have a higher heat flow than the surrounding rock; if the plutons are blanketed by sediments of low thermal conductivity, an elevated temperature at the base of the sedimentary section can result. This resource has been identified in the eastern United States. Deep regional aquifers of commercial value can occur in deep sedimentary basins, even in areas of only normal temperature gradient. For deep aquifers to be of commercial value, (1) basins must be deep enough to provide usable temperature levels at the prevailing gradient, and (2) permeability in the aquifer must be adequate for flow. Thermal energy in geothermal resources exists primarily in the rocks and only secondarily in the fluids that fill the pores and frac- tures. Thermal energy is usually extracted by bringing to the surface Inc. ASHRAE, 2019 user. single for Licensed | {}
54e1170a-408d-44f0-a65d-ebacca7594d4 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 35.40 2019 ASHRAE Handbook- -HVAC Applications (SI) ![image](/image/placeholder) WA MT ME OR ND MN VT NH WI 류 MA SD NY 증 MI CT RI IA PA NV NJ NE OH MD DE IL IN UT WV [ CA VA KS MO KY NC TN ① AZ OK AR SC 00 GA AL 목 MS TX LA FL , HI 증 주류 届 · AK TEMPERATURE ABOVE 100°C TEMPERATURE BELOW 100°C Fig. 37 U.S. Hydrothermal Resource Areas (Lienau et al. 1995) the hot water or steam that occurs naturally in the open spaces in the rock. Where rock permeability is low, the energy extraction rate is low. In permeable aquifers, fluid produced may be injected back into the aquifer at some distance from the production well to pass through the aquifer again and recover some of the energy in the rock. Figure 37 indicates geothermal resource areas in the United States. Temperature The temperature of fluids produced in the earth's crust and used for their thermal energy content varies from below 5 to 360°C. As shown in Figure 37, local gradients also vary with geologic conditions. The lower value represents fluids used as the low- temperature energy source for heat pumps, and the higher temperature represents an approximate value for the HGP-A well at Hilo, Hawaii. The following classification by temperature is used in the geo- thermal industry: ¦ High temperature ¦ ¦ t ¦ 150°C ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Intermediate temperature ¦ 90°C ¦ t ¦ 150°C ¦ ¦ Low temperature ¦ ¦ t ¦ 90°C ¦ Electric generation is generally not economical for resources with temperatures below about 150°C, which is the reason for the division between high- and intermediate-temperature. However, binary (organic Rankine cycle) power plants, with the proper set of circum- stances, have demonstrated that it is possible to generate electricity economically above 110°C. In 1988, there were 86 binary plants worldwide, generating a total of 126.3 MW (Di Pippo 1988). Geothermal resources at lower temperatures are more common. The frequency by reservoir temperature of identified convective systems above 90°C is shown in Figure 38. 2.2 FLUIDS Geothermal energy is extracted from the earth through naturally occurring fluids in rock pores and fractures. Fluids produced are steam, hot water, or a two-phase mixture of both. These may contain various amounts of impurities, notably dissolved gases and dissolved solids. Geothermal resources that produce essentially dry steam are vapor-dominated. Although these are valuable resources, they are rare. Hot-water (fluid-dominated) resources are much more common and can be produced either as hot water or as a two-phase mixture of steam and hot water, depending on the pressure maintained on the production well. If pressure in the production casing or in the formation around the casing is reduced below the saturation pressure at that temperature, some of the fluid will flash, and a two-phase fluid will result. If pressure is maintained above the saturation pressure, the fluid remains single-phase. In fluid- dominated resources, both dissolved gases and dissolved solids are significant. Geothermal fluid chemistry varies over a wide range. In the Imperial valley of California, some high-temperature geothermal fluids may contain up to 300 000 mg/kg of total dissolved solids (TDS). Fluids of this character are extremely difficult to accommodate in systems design and materials selection. In fact, most low-temperature fluids contain less than 3000 mg/kg and many meet drinking water standards. Despite this, even Inc. ASHRAE, 2019 user. single for Licensed | {}
5e82aba0-62ed-47f8-8b96-7d5f60d56f2c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Geothermal Energy 35.41 Chart Type: line 90°C 100°C 150°C 200°C 250°C 300°C item_01 28Percent 16Percent 12Percent 4Percent 3Percent 1Percent Fig. 38 Frequency of Identified Hydrothermal Convection Resources Versus Reservoir Temperature (Muffler 1979) geothermal fluids of a few hundred mg/kg TDS can cause substantial problems with standard construction materials. 2.3 PRESENT USE Discoveries of concentrated radiogenic heat sources and deep regional aquifers in areas of near-normal temperature gradient indicate that 37 states in the United States have economically exploitable direct-use geothermal resources (Interagency Geothermal Coordinating Council 1980). The Geysers, in northern California, is the largest single geothermal development in the world. The U.S. Department of Energy created a database of geothermal system data (including ground resource data) for practitioners to share data about installations (NGDS 2014). The total electricity generated by geothermal development in the world was 7974 MW in 2000 (Lund et al. 2001). Direct application of geothermal energy for space heating and cooling, water heating, agricultural growth-related heating, and industrial processing represented about 15 000 MW worldwide in 2000. In the United States in 2000, direct-use installed capacity amounted to 6400 MW, providing 5.65 106 MWh. The major uses of geothermal energy in the United States are for heating greenhouse and aquaculture facilities. The principal industrial use is for food processing. 2.4 DESIGN A major goal in designing direct-use systems is capturing the most possible heat from each litre of fluid pumped. System owning and operating costs are composed primarily of well pumping and well capitalization components; maximizing system t (i.e., minimizing flow requirements) minimizes well capital cost and pump operating cost. In many cases, system design can benefit from connecting loads in series according to temperature requirements. Direct-use system design is covered in detail in Anderson and Lund (1980) and Rafferty (1989a). Direct-use systems can be divided into four subsystems: (1) production, including the producing wellbore and associated wellhead equipment; (2) transmission and distribution to transport geothermal energy from the resource site to the user site and then ![image](/image/placeholder) HEAT EXCHANGER INJECTION PRODUCTION PEAKING/ USER WELLHEAD WELLHEAD BACK-UP SYSTEM EQUIPMENT EQUIPMENT UNIT TRANSMISSION AND DISTRIBUTION OF FLUID Fig. 39 Geothermal Direct-Use System with Wellhead Heat Exchanger and Injection Disposal distribute it to the individual user loads; (3) user system; and (4) disposal, which can be either surface disposal or injection back into a formation. In a typical direct-use system, geothermal fluid is produced from the production borehole by a lineshaft multistage centrifugal pump. When the geothermal fluid reaches the surface, it is delivered to the application site through the transmission and distribution system. In Figure 39, geothermal fluid is separated from the heating system by a heat exchanger. This secondary loop is especially desirable when the geothermal fluid is particularly corrosive and/ or causes scaling. The geothermal fluid is pumped directly back into the ground without loss to the surrounding surface. 2.5 COST FACTORS The following characteristics influence the cost of energy deliv- ered from geothermal resources: · Well depth · Distance between resource location and application site · Well flow rate · Resource temperature · Temperature drop · Load factor · Composition of fluid · Ease of disposal Many of these characteristics have a major influence because the cost of geothermal systems is primarily front-end capital cost; annual operating cost is relatively low. Well Depth The cost of the wells is usually one of the larger items in the overall cost of a geothermal system, and increases with resource depth. Compared to many geothermal areas worldwide, well depth requirements in the western United States are relatively shallow; most larger geothermal systems there operate with production wells of less than 600 m, and many at less than 300 m. Distance Between Resource Location and Application Site Inc. ASHRAE, 2019 user. single for Licensed Direct use of geothermal energy must occur near the resource. The reason is primarily economic; although geothermal (or secondary) fluid could be transmitted over moderately long distances (greater than 100 km) without great temperature loss, such transmission is generally not economically feasible. Most existing geothermal projects have transmission distances ofless than 1500 m. | {}
8a83be71-6410-4fc2-8630-59cba4fdb5a1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 35.42 Well Flow Rate Energy output from a production well varies directly with the fluid flow rate. The energy cost at the wellhead varies inversely with the well flow rate. A typical good resource has a production rate of 25 to 50 L/s per production well; however, geothermal direct-use wells have been designed to produce up to 130 L/s. Resource Temperature The available temperature is fixed by the prevailing resource. The temperature can restrict applications. It often requires a reevaluation of accepted application temperatures, which were developed for uses served by conventional fuels for which the application temperature could be selected at any value in a relatively broad range. Most existing direct-use projects use fluids in the 55 to 110°C range. Temperature Drop Because well flow is limited, power output from a geothermal well is directly proportional to the temperature drop of the geothermal fluid connected to the system. Consequently, a larger temperature drop reduces operating (pumping) and capital (well and production pump) costs. Cascading geothermal fluid to uses with lower temperature requirements can help achieve a large temperature difference ( t). Most geothermal systems are designed for a t between 17 and 28 K, although one system was designed for a t of 56 K with an 88°C resource temperature. Load Factor Defined as the ratio of the average load to the design capacity of the system, the load factor effectively reflects the fraction of time that the initial investment in the system is working. Again, because geothermal cost is primarily initial rather than operating cost, this factor significantly affects a geothermal system , s viability. As the load factor increases, so does the economy of using geothermal energy. The two main ways of increasing the load factor are (1) to select applications where it is naturally high, and (2) to use peaking equipment so that the geothermal design load is not the application peak load, but rather a reduced load that occurs over a longer period. Composition of Fluid The quality of the produced fluid is site specific and may vary from less than 1000 mg/kg TDS to heavily brined. Fluid quality influences two aspects of the design: (1) material selection to avoid corrosion and scaling effects, and (2) disposal or ultimate end use of the fluid. Ease of Disposal The costs associated with disposal, particularly when injection is involved, can substantially affect development costs. Historically, most geothermal effluent was disposed of on the surface, including discharge to irrigation, rivers, and lakes. This method of disposal is considerably less expensive than constructing injection wells. Geothermal fluids sometimes contain chemical constituents that make surface disposal problematic. Some of these constituents are listed in Table 24. Most new, large geothermal systems use injection for disposal to minimize environmental concerns and ensure long-term resource reliability. If injection is chosen, the depth at which the fluid can be injected affects well cost substantially. Many jurisdictions require the fluid be returned to the same or similar aquifers; thus, it may be necessary to bore the injection well to the same depth as the production well. Direct-use injection wells are considered Class v wells under the U.S. Environmental Protection 2019 ASHRAE Handbook- -HVAC Applications (SI) Table 24 Selected Chemical Species Affecting Fluid Disposal ¦ Species ¦ Reason for Control ¦ ¦ --- ¦ --- ¦ ¦ Hydrogen sulfide (H2S) ¦ Odor ¦ ¦ Boron (B3+) ¦ Damage to agricultural crops ¦ ¦ Fluoride (F -) ¦ Level limited in drinking water sources ¦ ¦ Radioactive species ¦ Levels limited in air, water, and soil ¦ Source: Lunis (1989). Agency's Underground Injection Control (UIC) program. Water wells, along with terminology relating to the technology, are discussed in the section on Ground-Source Heat Pumps. Direct-Use Water Quality Testing Low-temperature geothermal fluids commonly contain seven key chemical species that can significantly corrode standard materials of construction (Ellis 1989). These include · Oxygen (generally from aeration) · Hydrogen ion (pH) · Chloride ion · Sulfide species · Carbon dioxide species · Ammonia species · Sulfate ion The principal effects of these species are summarized in Table 25. Except as noted, the described effects are for carbon steel. Kindle and W oodruff (1981) present recommended procedures for complete chemical analysis of geothermal well water. Two of these species are not reliably detected by standard water chemistry tests and deserve special mention. Dissolved oxygen does not occur naturally in low-temperature (50 to 100°C) geothermal fluids that contain traces of hydrogen sulfide. However, because of slow-reaction kinetics, oxygen from air inleakage may persist for some minutes. Once the geothermal fluid is produced, it is extremely difficult to prevent contamination, especially if pumps used to move the fluid are not downhole-submersible or lineshaft turbine pumps. Even if fluid systems are maintained at positive pressure, air inleakage at pump seals is likely, particularly with the low level of maintenance in many installations. Hydrogen sulfide is ubiquitous in extremely low concentrations in geothermal fluids above 50°C. This corrosive species also occurs naturally in many cooler groundwaters. For strongly affected alloys, such as cupronickel, hydrogen sulfide concentrations in the low micrograms per kilogram range may have a serious detrimental effect, especially if oxygen is also present. At these levels, the characteristic rotten egg odor of hydrogen sulfide may be absent, so field testing may be required for detection. Hydrogen sulfide levels down to 50 g/kg can be detected using a simple field kit; however, absence of hydrogen sulfide at this low level may not preclude damage by this species. Two other key species that should be measured in the field are pH and carbon dioxide concentrations. This is necessary because most geothermal fluids release carbon dioxide rapidly, causing a rise in pH. Inc. ASHRAE, 2019 user. single for Licensed Production of suspended solids (sand) from a well should be addressed during well construction with gravel pack, screen, or both. Proper selection of the screen/gravel pack is based on sieve analysis of cutting samples from drilling. Surface separation is less desirable because it requires sand to pass first through the pump, reducing its useful life. Biological fouling is largely a phenomenon of low-temperature ( 32°C) wells. The most prominent organisms are various strains (Galionella, Crenothrix) of what are commonly referred to as iron bacteria. These organisms typically inhabit water with a pH | {}
d9fa49b1-d4e1-4118-99d5-77cbbf927e77 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Geothermal Energy 35.43 Table 25 Principal Effects of Key Corrosive Species ¦ Species ¦ Principal Effects ¦ ¦ --- ¦ --- ¦ ¦ Oxygen ¦ · Extremely corrosive to carbon and low-alloy steels; 0.03 mg/kg shown to cause fourfold increase in carbon steel corrosion rate. · Concentrations above 0.05 mg/kg cause serious pitting. · In conjunction with chloride and high tempera- ture, 0.1 mg/kg dissolved oxygen can cause chloride-stress corrosion cracking (chloride- SCC) of some austenitic stainless steels. ¦ ¦ Hydrogen ion (pH) ¦ · Primary cathodic reaction of steel corrosion in air-free brine is hydrogen ion reduction. Corro- sion rate decreases sharply above pH 8. · Low pH (5) promotes sulfide stress cracking (SSC) ofhigh-strength low-alloy (HSLA) steels and some other alloys coupled to steel. · Acid attack on cements. ¦ ¦ Carbon dioxide species (dissolved carbon dioxide, bicarbonate ion, carbonate ion) ¦ · Dissolved carbon dioxide lowers pH, increasing carbon and HSLA steel corrosion. · Dissolved carbon dioxide provides alternative proton reduction pathway, further exacerbating carbon and HSLA steel corrosion. · May exacerbate SSC. · Strong link between total alkalinity and corrosion of steel in low-temperature geothermal wells. ¦ ¦ Hydrogen sulfide species (hydrogen sulfide, bisulfide ion, sulfide ion) ¦ · Potent cathodic poison, promoting SSC ofHSLA steels and some other alloys coupled to steel. · Highly corrosive to alloys containing both copper and nickel or silver in any proportions. ¦ ¦ Ammonia species (ammonia, ammonium ion) ¦ · Causes stress corrosion cracking (SCC) of some copper-based alloys. ¦ ¦ Chloride ion ¦ · Strong promoter oflocalized corrosion of carbon, HSLA, and stainless steel, as well as of other alloys. · Chloride-dependent threshold temperature for pitting and SCC. Different for each alloy. · Little if any effect on SSC. · Steel passivates at high temperature in pH 5, 6070 mg/kg chloride solution with carbon diox- ide. 133 500 mg/kg chloride destroys passivity above 150°C. ¦ ¦ Sulfate ion ¦ · Primary effect is corrosion of cements. ¦ Source: Ellis (1989). Note: Except as indicated, described effects are for carbon steel. range of 6.0 to 8.0, dissolved oxygen content of less than 5 mg/ kg, ferrous iron content of less than 0.2 mg/kg, and a temperature of 8 to 16°C (Hackett and Lehr 1985). Iron bacteria can be identified microscopically. The most common treatment for iron bacteria infestation is chlorination, surging, and flushing; success depends on maintaining proper pH (less than 8.5), dosage, free residual chlorine content (13 to 32 mg/kg), contact time (24 h minimum), and agitation or surging. Precleaning (wire brushing) of the screen and redevelopment of the well after treatment are key to effectiveness. Hackett and Lehr (1985) provide additional detail on treatment. 2.6 MA TERIALS AND EQUIPMENT For system parts exposed to the fluid, materials selection is an important part of the design process. Chemical treatment of the geothermal fluid is not an effective strategy in most cases, because of economics and environmental (disposal) considerations. Corrosion and scaling in direct-use systems are generally addressed by isolating the fluid from the majority of the system using a plate heat exchanger. Performance of Materials Carbon Steel. The Ryznar index has traditionally been used to estimate the corrosivity and scaling tendencies of potable water supplies. However, one study found no significant correlation (at the 95% confidence level) between carbon steel corrosion and the Ryznar index (Ellis and Smith 1983). Therefore, the Ryznar and other indices based on calcium carbonate saturation should not be used to predict corrosion in geothermal systems, though they remain valid for scaling prediction. In Class Va geothermal fluids [as described by Ellis (1989); 5000 mg/kg total key species (TKS), total alkalinity 207 to 1329 mg/kg as CaCO3, pH 6.7 to 7.6], corrosion rates of about 100 to 500 m per year can be expected, often with severe pitting. In Class Vb geothermal fluids [as described by Ellis (1989); 5000 mg/kg TKS, total alkalinity 210 mg/kg as CaCO3, pH 7.8 to 9.85], carbon steel piping has given good service in a number of systems, as long as system design rigorously excluded oxygen. However, introduction of 0.03 mg/kg oxygen under turbulent flow conditions causes a fourfold increase in uniform corrosion. Saturation with air often increases the corrosion rate by at least 15 times. Oxygen contamination at the 0.05 mg/kg level often causes severe pitting. Chronic oxygen contamination causes rapid failure. External surfaces of buried steel pipe must be protected from contact with groundwater. Groundwater is aerated and has caused pipe failures by external corrosion. Required external protection can be obtained by coatings, pipe-wrap, or preinsulated piping, provided the selected material resists the system operating temperature and thermal stress. At temperatures above 57°C, galvanizing (zinc coating) does not reliably protect steel from either geothermal fluid or groundwater. Hydrogen blistering can be prevented by using void- free (killed) steels. Low-alloy steels (steels containing not more than 4% alloying elements) have corrosion resistance similar, in most respects, to carbon steels. As with carbon steels, sulfide promotes entry of atomic hydrogen into the metal lattice. If the steel exceeds a hardness of Rockwell C22, sulfide stress cracking may occur. Copper and Copper Alloys. Copper-tubed fan-coil units and heat exchangers have consistently poor performance because of traces of sulfide species found in geothermal fluids in the United States. Copper tubing rapidly becomes fouled with cuprous sulfide films more than 1 mm thick. Serious crevice corrosion occurs at cracks in the film, and uniform corrosion rates of 50 to 150 m per year appear typical, based on failure analyses. Experience in Iceland also indicates that copper is unsatisfactory for heat exchange service and that most brasses (Cu- Zn) and bronzes (Cu-Sn) are even less suitable. Cupronickel often performs more poorly than copper in low-temperature geothermal service because of trace sulfide. Much less information is available regarding copper and copper alloys in non-heat-transfer service. Copper pipe shows corrosion behavior similar to copper heat exchange tubes under conditions of moderate turbulence (Reynolds numbers of 40 000 to 70 000). An internal inspection of yellow brass valves showed no significant corrosion. However, silicon bronze CA 875 (12-16Cr, 3-5Si, 0.05Pb, 0.05P), an alloy normally resistant to dealloying, failed in less than three years when used as a pump impeller. Leaded red brass (CA 836 or 838) and leaded red bronze (SAE 67) appear viable as pump internal parts. Based on a few tests at Class Va sites, aluminum bronzes have shown potential for corrosion in heavy-walled components (Ellis 1989). Inc. ASHRAE, 2019 user. single for Licensed | {}
3a384027-175d-407c-bedc-8a16ef3495d7 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 35.44 Solder is yet another problem area for copper equipment. Lead- tin solder (50Pb, 50Sn) was observed to fail by dealloying after a few years exposure. Silver solder (1Ag, 7P, Cu) was completely removed from joints in under two years. If the designer elects to accept this risk, solders containing at least 70% tin should be used. Stainless Steel. Unlike copper and cupronickel, stainless steels are not affected by traces of hydrogen sulfide. Their most likely application is heat exchange surfaces. For economic reasons, most heat exchangers are probably of the plate-and-frame type, most of which are fabricated with one of two standard alloys, Type 304 and Type 316 stainless steel. Some pump and valve trim also are fabricated from these or other stainless steels. These alloys are subject to pitting and crevice corrosion above a threshold chloride level, which depends on the chromium and molybdenum content of the alloy and on the temperature of the geothermal fluid. Above this temperature, the passivation film, which gives the stainless steel its corrosion resistance, is ruptured, and local pitting and crevice corrosion occur. Figure 40 shows the relationship between temperature, chloride level, and occurrence of localized corrosion of Type 304 and Type 316 stainless steel. This figure indicates, for example, that localized corrosion of Type 304 may occur in 27°C geothermal fluid if the chloride level exceeds approximately 210 mg/kg; Type 316 is resistant at that temperature until the chloride level reaches approximately 510 mg/kg. Because ofits 2 to 3% molybdenum content, Type 316 is always more resistant to chlorides than is Type 304. Aluminum. Aluminum alloys are not acceptable in most cases because of catastrophic pitting. Titanium. This material has extremely good corrosion resistance and could be used for heat exchanger plates in any low- temperature geothermal fluid, regardless of dissolved oxygen content. Great care is required if acid cleaning is to be performed. The vendor' s instructions must be followed. The titanium should not be scratched with iron or steel tools; this can cause pitting. Chlorinated Polyvinyl Chloride (CPVC) and Fiber-Reinforced Plastic (FRP). These materials are easily fabricated and are not adversely affected by oxygen intrusion. External protection against groundwater is not required. The mechanical properties of these materials at higher temperatures may vary greatly from those at ambient temperature, and the materials' mechanical limits should not be exceeded. The usual mode of failure is creep rupture: X-Axis: Temperature °C Y-Axis: Chloride, mg/kg Chart Type: line WATER FREEZES PASSIVITY MAINTAINED item_01 500mg/kg 100mg/kg Fig. 40 Chloride Concentration Required to Produce Localized Corrosion of Stainless Steel as Function of Temperature (Efrid and Moeller 1978) 2019 ASHRAE Handbook-HVAC Applications (SI) strength decays with time. Follow manufacturer's directions for joining to avoid premature failure ofjoints. Elastomeric Seals. Tests on O-ring materials in a low- temperature system in Texas indicated that a fluoroelastomer is the best material for piping of this nature; Buna-N is also acceptable (Ellis 1989). Neoprene, which developed extreme compression set, was a failure. Natural rubber and Buna-S should also be avoided. Ethylene-propylene terpolymer (EPDM) has been used successfully in gasket, O-ring, and valve seats in many systems. EPDM materials have swollen in some systems using oil- lubricated turbine pumps. Pumps Production well pumps are among the most critical components in a geothermal system and have been the source of much system downtime. Therefore, proper selection and design of the production well pump is extremely important. Well pumps are available for larger systems in two general configurations: lineshaft and submersible. The lineshaft type is most often used for direct-use systems (Rafferty 1989b). Lineshaft Pumps. Lineshaft pumps are similar to those typically used in irrigation applications. An aboveground driver, typically an electric motor, rotates a vertical shaft extending down the well to the pump. The shaft rotates pump impellers in the pump bowl assembly, which is positioned at such a depth in the wellbore that adequate net positive suction pressure is available when the unit is operating. Two designs for the shaft/bearing portion of the pump are available: open and enclosed. In the open lineshaft pump, the shaft bearings are supported in "spiders, , which are anchored to the pump column pipe at 1.5 to 3 m intervals. The shaft and bearings are lubricated by the fluid flowing up the pump column. In geothermal applications, bearing materials for open lineshaft designs are typically elastomer compounds. The shaft material is typically stainless steel. Experience with this design in geothermal applications has been mixed. It appears that the open lineshaft design is most successful in applications with high ( 15 m) static water levels or flowing artesian conditions. Open lineshaft pumps are generally less expensive than enclosed lineshaft pumps for the same application. In an enclosed lineshaft pump, an enclosing tube protects the shaft and bearings from exposure to the pumped fluid. A lubricating fluid is admitted to the enclosed tube at the wellhead. It flows down the tube, lubricates the bearings, and exits where the column attaches to the bowl assembly. The bowl shaft and bearings are lubricated by the pumped fluid. Oil-lubricated, enclosed lineshaft pumps have the longest service life in low- temperature, direct-use applications. These pumps typically include carbon or stainless steel shafts and bronze bearings in the lineshaft assembly, and stainless steel shafts and leaded red bronze bearings in the bowl assembly. Keyed-type impeller connections (to the pump shaft) are superior to collet-type connections (Rafferty 1989b). Because of the lineshaft bearings, lineshaft pump reliability decreases as pump-setting depth increases. Nichols (1978) indicates that, below about 240 m, reliability is questionable, even under good pumping conditions. Submersible Pumps. The electrical submersible pump consists of three primary components located downhole: the pump, the drive motor, and the motor protector. The pump is a vertical multistage centrifugal type. The motor is usually a three-phase induction type that is filled with oil for cooling and lubrication; it is cooled by heat transfer to the pumped fluid moving up the well. The motor protector is located between the pump and the motor and isolates the motor from the well fluid while allowing pressure equalization between the pump intake and the motor cavity. Inc. ASHRAE, 2019 user. single for Licensed | {}
55c5ec59-7c04-440e-9622-df877b66bda2 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Geothermal Energy 35.45 The electrical submersible pump has several advantages over lineshaft pumps, particularly for wells requiring greater pump bowl setting depths. The deeper the well, the greater the economic advantage of the submersible pump. Moreover, it is more versatile, adapting more easily to different depths. Submersible pumps have not demonstrated acceptable lifetimes in most geothermal applications. Although they are commonly used in high-temperature, downhole applications in the oil and gas industry, the acceptable overhaul interval in that industry is much shorter than in a geothermal application. In addition, most submersibles operate at 3600 rpm, resulting in greater susceptibility to erosion in aquifers that produce moderate amounts of sand. They have, however, been applied in geothermal projects where an existing well of relatively small diameter must be used. At 3600 rpm, they provide greater flow capacity for a given bowl size than an equivalent 1750 rpm lineshaft pump. Standard cold-water submersible motors can be used at temperatures up to approximately 50°C with adequate precautions. These consist primarily of ensuring adequate water velocity past the motor (minimum 0.9 m/s), which may require the use of a sleeve, and a small degree of motor oversizing (Franklin Electric 2001). Well Pump Control. Well pumps serving variable loads are often controlled using variable-speed drives (VSDs). Submersible pumps can also be controlled using VSDs, but special precautions are required. Drive-rated motors are not commonly available for these applications, so external electronic protection should be used to prevent premature motor failure. In addition, the motor manufacturer must be aware that the motor will applied in a variable-speed application. Finally, because of the large static head in many well pump applications, controls should be configured to prevent the pump from operating at no-flow conditions. Heat Exchangers Geothermal fluids can be isolated with large central heat exchangers, as in the case of a district heating system, or with exchangers at individual buildings or loads. In both cases, the principle is to isolate the geothermal fluid from complicated systems or those that cannot readily be designed to be compatible with the geothermal fluid. The main types of heat exchangers used in transferring energy from the geothermal fluid are plate and downhole. Plate Heat Exchangers. For all but the very smallest applications, plate-and-frame heat exchangers are the most commonly used design. Available in corrosion-resistant materials, easily cleanable, and able to accommodate increased loads by adding plates, these exchangers are well suited to geothermal applications. Their high performance is also an asset in many system designs. Because geothermal resource temperatures are often less than those used in conventional hot-water heating system design, minimizing temperature loss at the heat exchanger is frequently a design issue. Approach temperatures of 2 K and less are common. Materials for plate heat exchangers in direct-use applications normally include Buna-N or EPDM gaskets and 316 or titanium plates. Plate selection is often a function of temperature and chloride content of the water. For applications characterized by chloride contents of 50 mg/kg at 93°C, titanium would be used. At lower temperatures, much higher chloride exposure can be tolerated (see Figure 40). Downhole Heat Exchangers. The downhole heat exchanger (DHE) is an arrangement of pipes or tubes suspended in a wellbore (Culver and Reistad 1978). A secondary fluid circulates from the load through the exchanger and back to the load in a closed loop. The primary advantage of a DHE is that only heat is extracted from the earth, which eliminates the need to dispose of spent fluids. Other advantages are the elimination of (1) well pumps with their initial operating and maintenance costs, (2) the potential for ![image](/image/placeholder) EXPANSION CHECK TANK VALVE AIR ELIMINATOR SUPPLY CIRCULATING PUMP (OPTIONAL) RETURN PRESSURE-REDUCING VALVE PRESSURE-RELIEF DOMESTIC HOT WATER VALVE CITY WATER CASING CEMENT GROUT GRADE LEVEL PACKER WELL BORE UPPER PERFORATIONS LOWER PERFORATIONS Fig. 41 Typical Connection of Downhole Heat Exchanger for Space and Domestic Hot- Water Heating (Reistad et al. 1979) depletion of groundwater, and (3) environmental and institutional restrictions on surface disposal. One disadvantage of a DHE is the limited amount of heat that can be extracted from or rejected to the well. The amount of heat extracted depends on the hydraulic conductivity of the aquifer and well design. Because of the limitations of natural convection, only about 10% of the heat output of the well is available from a DHE in comparison to pumping and using surface heat exchange (Reistad et al. 1979). With wells of approximately 95°C and depths of 150 m, output under favorable conditions is sufficient to serve the needs of up to five homes. The DHE in low- to moderate-temperature geothermal wells is installed in a casing, as shown in Figure 41. Downhole heat exchangers with higher outputs rely on water circulation within the well, whereas lower-output DHEs rely on earth conduction. Circulation in the well can be accomplished by two methods: (1) undersized casing and (2) convection tube. Both methods rely on the difference in density between the water surrounding the DHE and that in the aquifer. Circulation provides the following advantages: · Water circulates around the DHE at velocities that, in optimum conditions, can approach those in the shell of a shell-and-tube exchanger. · Hot water moving up the annulus heats the upper rocks and the well becomes nearly isothermal. · Some of the cool water, being denser than the water in the aquifer, sinks into the aquifer and is replaced by hotter water, which flows up the annulus. Figure 41 shows well construction in competent formation (i.e., where the wellbore will stand open without a casing). An under- sized casing with perforations at the lowest producing zone (usually near the bottom) and just below the static water level is installed. A packer near the top of the competent formation allows installation of an annular seal between it and the surface. When the DHE is in- stalled and heat extracted, thermosiphoning causes cooler water inside the casing to move to the bottom, and hotter water moves up the annulus outside the casing. Inc. ASHRAE, 2019 user. single for Licensed | {}
3f314dbd-19ad-4c3e-a421-c0388fb993f9 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 35.46 Because most DHEs are used for space heating (an intermittent operation), heated rocks in the upper portion of the well store heat for the next cycle. Where the well will not stand open without casing, a convection tube can be used. This is a pipe one-half the diameter of the casing either hung with its lower end above the well bottom and its upper end below the surface or set on the bottom with perforations at the bottom and below the static water level. If a U-bend DHE is used, it can be either inside or outside the convection tube. DHEs operate best in aquifers with a high hydraulic conductivity and that provide water movement for heat and mass transfer. Valves In large ( 65 mm) pipe sizes, resilient-lined butterfly valves are preferred for geothermal applications. The lining material protects the valve body from exposure to the geothermal fluid. The rotary rather than reciprocating motion of the stem makes the valve less susceptible to leakage and build-up of scale deposits. For many direct-use applications, these valves are composed of Buna-N or EPDM seats, stainless steel shafts, and bronze or stainless steel disks. Where oil-lubricated well pumps are used, a seat material of oil-resistant material is recommended. Gate valves have been used in some larger geothermal systems but have been subject to stem leakage and seizure. After several years of use, they are no longer capable of 100% shutoff. Piping Piping in geothermal systems can be divided into two broad groups: pipes used inside buildings and those used outside, typically buried. Indoor piping carrying geothermal water is usually limited to the mechanical room. Carbon steel with grooved end joining is the most common material. For buried piping, many existing systems use some form of nonmetallic piping, particularly asbestos cement (which is no longer available) and glass fiber. With the cost of glass fiber for larger sizes ( 150 mm) sometimes prohibitive, ductile iron is frequently used. Available in sizes 50 mm, ductile iron offers several positive characteristics: low cost, familiarity to installation crews, and wide availability. It requires no allowances for thermal expansion if push-on fittings are used. Most larger-diameter buried piping is preinsulated. The basic ductile iron pipe is surrounded by a layer of insulation (typically polyurethane), which is protected by an outer jacket of PVC or high-density polyethylene (HDPE). Standard ductile iron used for municipal water systems is sometimes modified for geothermal use. The seal coat used to protect the cement lining of the pipe is not suitable for the temperature of most geothermal applications; in applications where the geothermal water is especially soft or low in pH, the cement lining should be omitted, as well. Special high-temperature gaskets (usually EPDM) are used in geothermal applications. Few problems have been encountered in using ferrous piping with low- temperature geothermal fluids unless high chloride concentration, low ( 7.0) pH, or oxygen is present in the fluid. Most cases of corrosion failure have resulted from external attack by soil moisture in buried applications. For more information on piping systems for these applications, see Chapter 12 in the 2016 ASHRAE Handbook-HVAC Systems and Equipment and ASHRAE (2013a, 2013b). 2.7 RESIDENTIAL AND COMMERCIAL BUILDING APPLICATIONS The primary applications for direct use of geothermal energy in the residential and commercial area are space and domestic water 2019 ASHRAE Handbook-HVAC Applications (SI) heating. Space cooling using the absorption process is possible but rarely applied. Space Heating Figure 42 illustrates a system that uses geothermal fluid at 75°C (Austin 1978). The geothermal fluid is used in two main equipment components for heating the buildings: (1) a plate heat exchanger that supplies energy to a closed heating loop previously heated by a natural gas boiler (the boiler remains as a standby unit) and (2) a water-to-air coil used for preheating ventilation air. In this system, proper control is crucial for economical operation. The average temperature of discharged fluid is 49 to 54°C. Geothermal fluid is used directly in the preheat coils in the buildings, which would probably not be the case if the system were designed today (Lienau 1979). Figure 43 shows a geothermal district heating system that has a unique feature: its design is based on a peak load t of 38 K using an 88°C resource. It is of closed-loop design with central heat exchangers. The production well has an artesian shut-in pressure of 170 kPa, so the system operates with no production pump for most of the year. During colder weather, a surface centrifugal pump located at the wellhead boosts the pressure. Geothermal flow from the production well is initially controlled by a throttling valve on the supply line to the main heat exchanger, which responds to a temperature signal from the supply water on the closed-loop side of the heat exchanger. When the throttling valve reaches the full-open position, the production booster pump is enabled. The pump is controlled through a variable-speed drive that responds to the same supply-water signal as the throttling valve. The booster pump is designed for a peak flow rate of 19 L/s of 88°C water. A few district heating systems have also been installed using an open distribution system. In this design, central heat exchangers (as in Figure 43) are eliminated and the geothermal water is delivered to individual building heat exchangers. When more than a few buildings are connected to the system, using central heat exchangers is normally more cost effective. Terminal equipment used in geothermal systems is the same as that used in nongeothermal heating systems. However, certain types of equipment are better suited to geothermal design than others. In many cases, buildings heated by low-temperature geothermal sources operate at lower supply water temperatures than conventional hydronic designs. Because many geothermal sources are designed to take advantage of a large t, proper ![image](/image/placeholder) BOILER PLANT 77°C 。 T SET AT T SET AT WATER 410 kPa METER 0⌀ 68°C 68°C 66°C METER 53°C 60°C GEOTHERMAL FLOW CONTROL SUPPLY MAIN VALVE PLA E HEAT EXCHANGER 0 * STANDBY BOILER AND 43°C AIR BUILDING MUI LTIZONE AIR-HANDLING OFFICE PREHEAT COIL UN BYPASS LINE 10°C PREHEATED 53°C AIR PREHEAT LABORATORY COIL TO SPRAY-COOLING POND AND -12°C OUTSIDE 38°C FINAL DISCHARGE TO RIVER AIR Fig. 42 Heating System Schematic Inc. ASHRAE, 2019 user. single for Licensed | {}
6a31506c-b722-4681-be6f-97b94b6f1cb4 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Geothermal Energy 35.47 selection of equipment for low flow and low temperature is important. Finned-coil, forced-air systems generally function best in this low-temperature/high- t situation. One or two additional rows of coil depth compensate for the lower supply water temperature. Although an increased t affects coil circuiting, it improves controllability. This type of system should be able to use a supply water temperature as low as 60°C. Radiant floor panels are well suited to very low water temperatures, particularly in industrial applications with little or no floor covering. In industrial settings, with a bare floor and a relatively low space-temperature requirement, the average water temperature could be as low as 35°C. For a higher space temperature and/or thick floor coverings, a higher water temperature may be required. Baseboard convectors and similar equipment are the least capable of operating at low supply-water temperature. At 65°C average water temperatures, derating factors for this design load may be affected. This type of equipment can be operated at low temperatures from the geothermal source to provide base-load heating, with peak load supplied by a conventional boiler. Ensure the boiler does not supply a higher fraction of the load than intended by the designer. Domestic Water Heating Domestic water heating in a district space-heating system is beneficial because it increases the overall size of the energy load, energy demand density, and load factor. For those resources that cannot heat water to the required temperature, preheating is usually possible. Whenever possible, the domestic hot-water load should be placed in series with the space-heating load to reduce system flow rates and increase t. Space Cooling Geothermal energy has seldom been used for cooling, although emphasis on solar energy and waste heat has created interest in cooling with thermal energy. The absorption cycle is most often used, and lithium bromide/water absorption machines are available in a wide range of capacities. Temperature and flow requirements for absorption chillers run counter to the general design philosophy for geothermal systems: they require high supply water temperatures and a small t on the hot-water side. Figure 44 shows the effect of reduced supply water temperature on machine performance. The machine is rated at a 115°C input temperature, so derating factors must be applied if the machine is operated below this temperature. For example, operation at a 93°C supply water temperature results in a 50% decrease in capacity, which seriously affects the economics of absorption cooling at a low resource temperature. Coefficient of performance (COP) is less seriously affected by reduced supply water temperature. The nominal COP of a single- stage machine at 115°C is 0.65 to 0.70; that is, for each kilowatt of cooling output, a heat input of 1 kW divided by 0.65, or 1.54 kW, is required. Most absorption equipment is designed for steam input (an isothermal process) to the generator section. When this equipment is operated from a hot-water source, a relatively small t must be used. This creates a mismatch between building flow requirements for space heating and cooling. For example, assume a 20 000 m2 building is to use a geothermal resource for heating and cooling. ![image](/image/placeholder) VARIABLE- MAIN THROTTLING SPEED VALVE DRIVE I 88°C . T 82°C GEOTHERMAL BOOSTER PUMP I MAIN LOOP HEAT EXCHANGERS 2200 kW EACH SIGNAL FROM DIFFERENTIAL PRESSURE SENSOR PRODUCTION WELL 170 kPa SHUT-IN PRESSURE VARIABLE-SPEED DRIVE 27°C HEAT TOTALIZER LOOP HEAT PUMP SYSTEM AT SCHOOL DOMESTIC HOT- , 32°C WATER HEAT MUNICIPAL POOL EXCHANGER COMPLEX T T ↗ SPACE HEATING FLOW METER HEAT EXCHANGER TYPICAL CUSTOMER CONNECTIONS TO SIGNAL TO CIRCULATING DISPOSAL PUMP VIA PHONE LINE DIFFERENTIAL PRESSURE SENSOR Fig. 43 Closed Geothermal District Heating System (Rafferty 1989a) Inc. ASHRAE, 2019 user. single for Licensed | {}
715ce4e1-0b8f-4e08-886e-51d495154bcc | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 35.48 Chart Type: line 75 80 85 95 100 105 110 115 item_01 10Percent 20Percent 30Percent 40Percent 50Percent 60Percent 70Percent 100Percent Fig. 44 Typical Lithium Bromide Absorption Chiller Performance Versus Temperature (Christen 1977) At 80 W/m2 and a design t of 22 K, the flow requirement for heating is 16 L/s. At 95 W/m2, a t of 8 K, and a COP of 0.65, the flow requirement for cooling is 78 L/s. Some small-capacity (10 to 90 kW) absorption equipment has been optimized for low-temperature operation in conjunction with solar heat. Although this equipment could be applied to geothermal resources, the prospects are questionable. Small absorption equipment generally competes with packaged direct- expansion units in this range; absorption equipment requires a great deal more mechanical auxiliary equipment for a given capacity. The cost of the chilled-water piping, pump, and coil; cooling-water piping, pump, and tower; and hot-water piping raises the capital cost of the absorption equipment substantially. Only in large sizes ( 35 kW) and in areas with high electric rates and high cooling requirements ( 2000 full-load hours) would this type of equipment offer an attractive investment to the owner (Rafferty 1989a). Cascading Systems Cascading geothermal systems have been used for centuries all over the world (Lund 2010). These systems typically use intermediate- (90 < t < 150°C) and low-temperature (90°C) resources, depending on the first step of the cascade. As shown in Figure 38, low-temperature resources are most frequently identified but are underused. Resources typically include hot/warm fluid well production, springs, ponds, shallow groundwater flows, and geologic features such as hot pots. The nature of the resource, temperature, volume, and chemical composition determine the heat collection method and use. In ideal cases, the thermal fluid may be used directly to heat or cool, but indirect collection methods are more common. Open water systems may use a heat exchanger immersed in the fluid. Other sources need to be pumped and a plate-and-frame heat exchanger used. The goal is to use as much heat from the fluid as possible. The designer should carefully examine fluid quality to determine the best harvesting method, system material composition, and disposal of the geothermal fluid. An example of a cascading system is a hot-water well producing 22 L/s of 68°C, low TDS, and approximately neutral pH water used for the following heat cascading temperature loads: domestic hot water at 60°C, a large spa at 40°C, a pool at 29°C, warm-water 2019 ASHRAE Handbook-HVAC Applications (SI) irrigation storage and a water feature to a pond at about 27 to 22°C, and finally through a lake plate heat exchanger in the pond serving GSHPs to heat and cool selected campus buildings. Another common application is to use a low-temperature cascading system for hydroponic and aquaculture in both remote and urban environments. 2.8 INDUSTRIAL APPLICATIONS Design philosophy for the use of geothermal energy in industrial applications, including agricultural facilities, is similar to that for space conditioning. However, these applications have the potential for much more economical use of the geothermal resource, primarily because they (1) operate year-round, which gives them greater load factors than possible with space- conditioning applications; (2) do not require extensive (and expensive) distribution to dispersed energy consumers, as is common in district heating; and (3) often require various temperatures and, consequently, may be able to make greater use of a particular resource than space conditioning, which is restricted to a specific temperature. In the United States, the primary non- space-heating applications of direct-use geothermal resources are dehydration (primarily vegetables), gold mining, and aquaculture. 3. RENEW ABILITY Geothermal energy is a renewable resource (see the section on Nonrenewable and Renewable Energy Sources in Chapter 34 of the 2017 ASHRAE Handbook-Fundamentals for discussion). Quantification of the source may be required for renewable portfolio standards, utility programs, etc.; to do this, measure or calculate the electric or thermal energy that is either generated from, or avoided by, use of the geothermal resource. Geothermal energy ultimately comes from a variety of sources, including earth heat and solar energy. Direct-use and higher- temperature geothermal resources may be considered renewable, because the heat removed is replaced by natural processes: heat is generated deep in the earth and transferred to more shallow depths. The geothermal resource must be carefully managed, however, and can eventually be depleted if used at too high of a rate. Geothermal heat pumps (GHPs) also use these sources (albeit in a more complex, indirect fashion) for building heating, cooling, and domestic hot water. Because this method of using geothermal energy does require electricity input, quantification of the renewable portion of GHP operation is to be based on the amount of electric and thermal energy that is avoided by use of GHPs. Attempts at quantifying this avoidance have been made (European Union 2013), but more work is needed before a more specific methodology can be published here. REFERENCES ACCA. 2008. Commercial load calculation. Manual N, 5th ed., Air- conditioning Contractors of America, Arlington, VA. ACCA. 2016. Residential load calculation. Manual J, 8th ed. Air- conditioning Contractors of America, Arlington, VA. Anderson, K.E. 1984. Water well handbook. Missouri Water Well and Pump Contractors Association, Belle, MD. Anderson, D.A., and J. W. Lund, eds. 1980. Direct utilization of geothermal energy: Technical handbook. Geothermal Resources Council Special Report 7. ANSI/CSA/IGSHPA. 2016. Design and installation of ground source heat pump systems for commercial and residential buildings. ANSI/CSA/ IGSHPA Standard C448 Series 16. Canadian Standards Association, Rexdale, ON ASHRAE. 2012. Water-source heat pumps-Testing and rating for perfor- mance-Part 1: Water-to-air and brine-to-air heat pumps. ANSI/ARI/ ASHRAE/ISO Standard 13256-1:1998 (RA 2012). Inc. ASHRAE, 2019 user. single for Licensed | {}
442c9e47-deb0-44f4-a5b2-e218f8b52040 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Geothermal Energy 35.49 ASHRAE. 2012. Water-source heat pumps- Testing and rating for perfor- mance Part 2: Water-to-water and brine-to-water heat pumps. ANSI/ ARI/ASHRAE/ISO Standard 13256-2:1998 (RA 2012). ASHRAE. 2013a. District heating guide. ASHRAE. 2013b. District cooling guide. Austin, J.C. 1978. A low temperature geothermal space heating demonstra- tion project. Geothermal Resources Council Transactions 2(2). Austin III, W.A., C. Yavuzturk, and J.D. Spitler. 2000. Development of an in- situ system for measuring ground thermal properties. ASHRAE Transac- tions 106(1):365-379. Bashyum, K., G. Hansen, M. Mitchell, and M. Selvakumar. 2017. Develop- ment of design tools for surface water heat pump systems. ASHRAE Research Project RP-1385, Final Report. Battocletti, E.C., and W.E. Glassley. 2013. Measuring the costs and benefits of nationwide geothermal heat pump deployment. Report DE- EE0002741. Bob Lawrence & Associates, Inc. dx.doi.org/10.2172/ 1186828; database at gdr.openei.org/submissions/180. Bernier, M.A., P. Pinel, P., multiple load R. Labib, and R. Paillot. 2004. A aggregation algorithm for annual hourly simulations of GCHP systems. International Journal ofHVAC&R Research (now Science and Technol- ogy. for the Built Environment) 10(4):471-488. Bernier, M.A., A. Chahla, and P. Pinel. 2008. Long-term ground temperature changes in geo-exchange systems. ASHRAE Transactions 114(2):342- 350. Bullard, E. 1973. Basic theories. In Geothermal energy; Review of research and development. UNESCO, Paris. Campbell, M.D., and J.H. Lehr. 1973. Water well technology. McGraw-Hill, New Y ork. Caneta Research. 1995a. Commercial/institutional ground-source heat pump engineering manual. ASHRAE. Caneta Research. 1995b. Operating experiences with commercial ground- source heat pump systems. ASHRAE TRP-863, Final Report. Caneta Research. 2001. Commissioning, preventative maintenance and troubleshooting guide for commercial GSHP systems (SP-94). ASHRAE Transactions 108(2), Paper 4554. Carlson, S. 2001. Development of equivalent full load heating and cooling hours for GCHPs applied in various building types and locations. ASHRAE TRP-1120, Final Report. Carslaw, H.S., and J.C. Jaeger. 1947. Heat conduction in solids. Claremore Press, Oxford. Carslaw, H.S., and J.C. Jaeger. 1959. Conduction of heat in solids. Oxford Science Publications. Chandler, R. V. 1987. Alabama streams, lakes, springs and ground waters for use in heating and cooling. Bulletin 129. Geological Survey of Alabama, Tuscaloosa. Chiasson, A.D., S.J. Rees, and J.D. Spitler. 2000a. A preliminary assessment of the effects of groundwater flow on closed-loop ground-source heat pump systems. ASHRAE Transactions 106(1):380-393. Chiasson, A.D., J.D. Spitler, S.J. Rees, and M.D. Smith. 2000b. A model for simulating the performance of a shallow pond as a supplemental heat rejecter with closed-loop ground-source heat pump systems. ASHRAE Transactions. 106(2):107-121. Christen, J.E. 1977. Central cooling-Absorption chillers. Oak Ridge National Laboratories, Oak Ridge, TN. Claesson, J., and G. Hellstrom. 2011. Multiple method to calculate borehole thermal resistances in a borehole heat exchanger. HVAC&R Research (now Science and Technologyfor the Built Environment) 17(6):895-911. Cooper, L. Y. 1976. Heating of a cylindrical cavity. International Journal of Heat and Mass Transfer 19:575-577. Cornell University. 2006. Lake source cooling. energyandsustainabil- http:/comell.edunufilocingproductucteBaute8.htm. CUAHSI HIS. 2017. Hydrologic information system. Consortium of Univer- sities for the Advancement ofHydrologic Science, Inc. www.cuahsi.org/. Culver, G.G., and G.M. Reistad. 1978. Evaluation and design of downhole heat exchangers for direct applications. DOE Report RLO-2429-7. Di Pippo, R. 1988. Industrial developments in geothermal power production. Geothermal Resources Council Bulletin 17(5). Driscoll, F.G. 1986. Groundwater and wells, 2nd ed. Johnson Screens, St. Paul, MN. Efrid, K.D., and G.E. Moeller. 1978. Electrochemical characteristics of 304 and 316 stainless steels in fresh water as functions of chloride concentra- tion and temperature. Paper 87, Corrosion/78, Houston. Ellis, P. 1989. Geothermal direct use engineering and design guidebook, Ch. 8: Materials selection guidelines. Oregon Institute of Technology, Geo- Heat Center, Klamath Falls. Ellis, P., and C. Smith. 1983. Addendum to material selection guidelines for geothermal energy utilization systems. Radian Corporation, Austin. Enwave. (no date). Deep water lake cooling. www.enwavetoronto.com /district_cooling_system.html. EPA. 1975. Manual of water well construction practices. EPA-570/9-75- 001. U.S. Environmental Protection Agency, Washington, D.C. www.epa.gov/nscep/. EPA. 2017. Water quality data: STORET. United States Environmental Pro- tection Agency. www.epa.gov/storet/. EPRI. 1990. Soil and rock classification for the design of ground-coupled heat pump systems. International Ground Source Heat Pump Associa- tion. Electric Power Research Institute, National Rural Electric Cooper- ative Association, Oklahoma State University, Stillwater. Eskilson, P. 1987. Thermal analysis ofheat extraction boreholes. University of Lund, Sweden. European Union. 2013. Commission decision of 1 March 2013 establishing the guidelines for member states on calculating renewable energy from heat pumps from different heat pump technologies. OfficialJournal Doc- ument 32013D0114. eur-lex. europa.eu/eli/dec/2013/114(1)/oj. Fisher, D.E., S.J. Rees, S.K. Padhmanabhan, and A. Murugappan. 2006. Implementation and validation of ground-source heat pump system mod- els in an integrated building and system simulation environment. HVAC&R Research (now Science and Technologyfor the Built Environ- ment) 12:693-710. Franklin Electric. 2001. Application manual for submersible pumps. Franklin Electric, Bluffton, IN. Gehlin, S. 1998. Thermal response test, in-situ measurements of thermal properties in hard rock. Licentiate thesis, Department of Environmental Engineering, Division of Water Resources Engineering, Lulea Univer- sity ofTechnology, Sweden. Gu, R., and H.G. Stefan. 1990. Year-round temperature simulation of cold climate lakes. Cold Regions Science and Technology 18(2):147-160. Hackel, S., and A. Pertzborn. 2011. Effective design and operation ofhybrid ground-source heat pumps: Three case studies. Energy and Buildings 43. Hackel, S., G. Nellis, and S. Klein. 2009. Optimization of cooling dominated hybrid ground-coupled heat pump systems (RP-1384). ASHRAE Trans- actions 109(1), Paper CH-09-057. Hackett, G., and J.H. Lehr. 1985. Iron bacteria occurrence problems and control methods in water wells. National Water Well Association, Worth- ington, OH. Hattemer, B.G., and S.P. Kavanaugh. 2005. Design temperature data for sur- face water HVAC systems. ASHRAE Transactions 111(1). Hattemer, B.G., S.P. Kavanaugh, and D. Williamson. 2006. Environmental impacts of surface water heat pump systems. ASHRAE Transactions 112(1). Heinonen, E. W., and R.E. Tapscott. 1996. Assessment of anti-freeze solu- tions for ground-source heat pump systems. ASHRAE Research Project RP-908, Report. Heinonen, E. W , R.E. Tapscott, M. W. Wildin, and A.N. Beall. 1997. Assess- ment of anti-freeze solutions for ground-source heat pump systems. ASHRAE BRP-90, Report. Hellstrom, G. 1989. Duct ground heat storage model: Manualfor computer code. Department of Mathematical Physics, University of Lund, Sweden. Hellstrom, G. 1991. Ground heat storage- Thermal analyses ofduct storage systems. Ph.D. dissertation. University of Lund, Sweden. IAPMO. 2015. Uniform solar electric and hydronic codeⓇ, Chs. 4: Hydronics, and 7: Geothermal Energy Systems. International Associa- tion of Plumbing and Mechanical Officials, Ontario, CA. ICC. 2015. International mechanical code�, Ch. 12: Hydronic piping. Inter- national Code Council, Washington, D.C. IGSHPA. 2017. Closed loop/geothermal heat pump systems- Design and installation standards. International Ground Source Heat Pump Associ- ation, Stillwater, OK. Ingersoll, L.R., and A.C. Zobel. 1954. Heat conduction with engineering and geological application, 2nd ed. McGraw-Hill, New York. Interagency Geothermal Coordinating Council. 1980. Geothermal energy, research, development and demonstration program. DOE Report RA0050, IGCC-5. U.S. Department of Energy, Washington, D.C. Inc. ASHRAE, 2019 user. single for Licensed | {}
f8fe607c-1a68-4a43-bad1-7e8aeeb5cadd | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 35.50 Javed, S. and J.D. Spitler. 2016. Calculation of borehole thermal resistance. Advances in Ground-Source Heat Pump Systems (May):63-95. Jenkins, J., ed. 2009. Guidelines for the construction of vertical boreholes for closed loop heat pump systems. National Ground Water Association, Westerville, OH. Kavanaugh, S.P. 1985. Simulation and experimental verification of a vertical ground-coupled heat pump system. Ph.D. dissertation, Okla- homa State University, Stillwater. Kavanaugh, S.P. 1991. Ground and water source heat pumps. Oklahoma State University, Stillwater. Kavanaugh, S.P. 1992. Ground-coupled heat pumps for commercial build- ing. ASHRAE Journal 34(9):30-37. Kavanaugh, S.P. 1998. A design method for hybrid ground-source heat pumps. ASHRAE Transactions 104(2), Paper TO-98-07-3. Kavanaugh, S.P. 2000. Field tests for ground thermal properties- Methods and impact on GSHP system design. ASHRAE Transactions 106(1), Paper DA00-13-4. Kavanaugh, S.P. 2001. Investigation of methods for determining soil forma- tion thermal characteristics from short term field tests. ASHRAE Research Project RP-1118, Final Report. Kavanaugh, S.P. 2008. A 12-step method for closed-loop ground-source heat-pump design. ASHRAE Transactions 1 14(2). Kavanaugh, S.P. 2010. Ground heat exchangers: Determining thermal resis- tance. ASHRAE Journal 52(8):72-75. Kavanaugh, S.P., and T.H. Calvert. 1995. Performance of ground source heat pumps in north Alabama. Final Report, Alabama Universities and Ten- nessee Valley Authority Research Consortium. University of Alabama, Tuscaloosa. Kavanaugh, S.P , and J.S. Kavanaugh. 2012a. Long-term commercial GSHP performance, part 3. ASHRAE Journal 54(9). Kavanaugh, S.P - and J.S. Kavanaugh. 2012b. Long-term commercial GSHP performance, part 1. ASHRAE Journal 54(6). Kavanaugh, S.P , and K. Rafferty. 2014. Geothermal heating and cooling: Design of ground-source heat pump systems. ASHRAE. Kavanaugh, S.P., S. Lambert, and D. Messer. 2002. Development of guide- lines for the selection and design of the pumping/piping subsystem for ground coupled heat pumps. ASHRAE TRP-1217, Final Report. Kavanaugh, S., M. Green, and K. Mescher. 2012. Long-term commercial GSHP performance, part 4: Installation costs. ASHRAE Journal 54(10): 26-36. Kindle, C.H., and E.M. Woodruff. 1981. Techniques for geothermal liquid sampling and analysis. Battelle Pacific Northwest Laboratory, Richland, WA. Lienau, P.J. 1979. Materials performance study of the OIT geothermal heating system. Geo-Heat Utilization Center Quarterly Bulletin, Oregon Institute ofTechnology, Klamath Falls. Lienau, P., H. Ross, and P. Wright. 1995. Low temperature resource assess- ment. Geothermal Resources Council Transactions 19(1995). Liu, X. 2005. Development and experimental validation of simulation of geothermal snow melting systems for bridges. Ph.D. dissertation, Okla- homa State University, Stillwater. Liu, X. 2008. Enhanced design and energy analysis tool for geothermal water loop heat pump systems. 9th International IEA Heat Pump Con- ference, Z�rich, Switzerland, Paper 4.54. Lund, J.W. 2010. Direct utilization of geothermal energy. Energies 3(8): 1443-1471. dx.doi.org/:10.3390/en3081443. Lund, J., T. Boyd, A. Sifford, and R. Bloomquist. 2001. Geothermal utiliza- tion in the United States- 2000. Proceedings of the 26th Annual Stan- ford Workshop-Reservoir Engineering. Stanford University. Lunis, B. 1989. Geothermal direct use engineering and design guidebook, Ch. 20: Environmental considerations. Oregon Institute of Technology, Geo-Heat Center, Klamath Falls. Means. 2014. RSMeansⓇ mechanical cost data. Reed Construction Data. Norwell, MA. Mitchell, M.S., and J.D. Spitler. 2013. Open-loop direct surface water cool- ing and surface water heat pump systems - A review. HVAC&R Research (now Science and Technologyfor the Built Environment) 19(2):125-140. Mogensen, P. 1983. Fluid to duct wall heat transfer in duct system heat stor- ages. Proceedings of the International Conference on Subsurface Heat Storage in Theory and Practice, Stockholm, pp. 652-657. Morrison, A. 1997. GS2000 software. Proceedings of the Third Interna- tional Heat Pumps in Cold Climates Conference, Wolfville, Nova Scotia, pp. 67-76. 2019 ASHRAE Handbook-HVAC Applications (SI) Muffler, L.J.P., ed. 1979. Assessment of geothermal resources of the United States-1978. U.S. Geological Survey Circular 790. NGDS. 2014. National geothermal data system. U.S. Department of Energy, Washington, D.C. www .geothermaldata.org/. NGWA. 2010. Guidelines for the construction of loop wells for vertical closed loop ground source heat pump systems, Appendix A. J.T. Jenkins, ed. National Ground Water Association, Westerville, OH. Nichols, C.R. 1978. Direct utilization of geothermal energy: DOE' s resource assessment program. Direct Utilization of Geothermal Energy: A Sym- posium. Geothermal Resources Council. Nutter, D., R. Couvillion, M.G. Sutton, K. Tan, R. Davis, and J. Hemphill. 2001. Investigation of borehole completion methods to optimize the environmental benefits of ground-coupled heat pumps (RP-1016). ASHRAE Research Project RP-1016, Final Report. Orio, C., C.N. Johnson, S.J. Rees, A. Chiasson, D. Zheng, and J.D. Spitler. 2005. A survey of standing column well installations in North America (RP-1119). ASHRAE Transactions 111(2):109-121. Oklahoma State University. 1988a. Closed-loop/ground-source heat pump systems installation guide. International Ground Source Heat Pump Association, Oklahoma State University, Division of Engineering Tech- nology, Stillwater. Oklahoma State University. 1988b. Closed loop ground source heat pump systems. Oklahoma State University, Division of Engineering Technol- ogy, Stillwater. Peirce, L.B. 1964. Reservoir temperatures in north central Alabama. Bulletin 8. Geological Survey of Alabama, Tuscaloosa. Pertzborn, A., G. Nellis, and S. Klein. 2012. Thermal storage properties of a hybrid ground source heat pump. ASHRAE Transactions 118(2), Paper SA-12-C005. Pezent, M.C., and S.P. Kavanaugh. 1990. Development and verification of a thermal model of lakes used with water-source heat pumps. ASHRAE Transactions 96(1). PPI. 2018. Handbook ofpolyethylene pipe, 2nd ed. Plastics Pipe Institute. Chs. 3 and 6. plasticpipe.org/publications/pe-handbook.html. Rafferty, K. 1989a. Geothermal direct use engineering and design guide- book, Ch. 14: Absorption refrigeration. Oregon Institute of Technology, Geo-Heat Center, Klamath Falls. Rafferty, K. 1989b. A materials and equipment review ofselected U.S. geo- thermal district heating systems. Oregon Institute of Technology, Geo- Heat Center, Klamath Falls. Rafferty, K. 2000a. A guide to online geologic information and publications for use in GSHP site characterization. Transactions of the 2000 Heat Pumps in Cold Climates Conference, Caneta Research, Missisaugua, ON, Canada. Rafferty, K. 2000b. Scaling in geothermal heat pump systems. Geo-Heat Center, Oregon Institute of Technology, Klamath Falls. Rafferty, K. 2000c. Design aspects of commercial open loop heat pump sys- tems. Transactions of the 2000 Heat Pumps in Cold Climates Confer- ence, Caneta Research, Missisaugua, ON, Canada. Rafferty, K. 2008. Design issues in commercial open loop heat pump sys- tems. ASHRAE Transactions 114(2). Reistad, G.M., G.G. Culver, and M. Fukuda. 1979. Downhole heat exchang- ers for geothermal systems: Performance, economics and applicability. ASHRAE Transactions 85(1):929-939. Remund, C. 1999. Borehole thermal resistance: Laboratory and field studies. ASHRAE Transactions 105(1). Remund, C., and R. Carda. 2014. Ground source heat pump residential and light commercial design and installation guide. International Ground Source Heat Pump Association, Stillwater, OK. Roscoe Moss Company. 1985. The engineers manualfor water well design. Roscoe Moss Company, Los Angeles. Sachs, H. 2002. Geology and drilling methods for ground-source heat pump system installations: An introduction for engineers. ASHRAE. Shonder, J.A., and J.V. Beck. 1999. Determining effective soil formation properties from field data using a parameter estimation technique. ASHRAE Transactions 105(1):458-466. Shonder, J.A., V.D. Baxter, J.W. Thornton, and P. Hughes. 1999. A new comparison of vertical ground heat exchanger design methods for resi- dential applications. ASHRAE Transactions 105(2). Shonder, J.A., V.D. Baxter, P.J. Hughes, and J. W. Thornton. 2000. A com- parison of vertical ground heat exchanger design software for commer- cial applications. ASHRAE Transactions 106(1). Inc. ASHRAE, 2019 user. single for Licensed | {}
6417437f-be54-495c-a5e6-ba2016451057 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Geothermal Energy 35.51 Singh, J.P., and G. Foster. 1998. Advantages of using the hybrid geothermal option. Proceedings of the Second Stockton International Geothermal Conference. Skouby, A., ed. 2011. Closed loop/geothermal heat pump systems design and installation standards. International Ground Source Heat Pump Association, Oklahoma State University, Stillwater, OK. Spitler, J.D. 2000. GLHEPRO-A design tool for commercial building ground loop heat exchangers. Proceedings of the Fourth International Heat Pumps in Cold Climates Conference, Aylmer, Quebec. Spitler, J.D. 2002. R&D studies applied to standing column well design, ASHRAE RP-1119, Report. Spitler, J., and M. Bernier. 2016. Vertical borehole ground heat exchanger design methods. In Advances in ground-source heat pump systems, pp. 29-61. S.J. Rees, ed. Woodhead Publishing. Spitler, J.D., and M.S. Mitchell. 2016. Surface water heat pump systems. Advances in Ground-Source Heat Pump Systems (Jan.):225-246. Spitler, J.D., S.J. Rees, and C. Yavuzturk. 1999. More comments on in-situ borehole thermal conductivity testing. The Source 12(2):4-6. Spitler, J.D, S.J. Rees, and C. Yavuzturk. 2000. Recent developments in ground source heat pump system design, modeling and applications. Proceedings of the Dublin 2000 Conference. Spitler, J.D., J.R. Cullin, K. Conjeevaram, M. Ramesh, and M. Selvakumar. 2012. Improved design tools for surface water and standing column well heat pump systems. Report DE-EE0002961. Office of Scientific and Technical Information, U.S. Department of Energy, Washington, D.C. www.osti.gov/scitech/biblio/1111113/ Stiger, S., J. Renner, and G. Culver. 1989. Geothermal and direct use engi- neering and design guidebook, Ch. 7: Well testing and reservoir evalua- tion. Oregon Institute of Technology, Geo-Heat Center, Klamath Falls. Svec, O.J. 1990. Spiral ground heat exchangers for heat pump applications. Proceedings of3rd IEA Heat Pump Conference. Pergamon Press, Tokyo. UOP. 1975. Ground water and wells. Johnson Division, UOP Inc., St. Paul, MN. USGS. 2000. Ground water atlas of the United States. U.S. Geological Survey, Reston, VA. USGS. 2017. United States Geological Survey National Water Information System. waterdata.usgs.gov/nwis. Witte, H., G. van Gelder, and J. Spitler. 2002. In-situ thermal conductivity testing: A Dutch perspective. ASHRAE Transactions 108(1). Xu, X. 2007. Simulation and optimal control of hybrid ground source heat pumps. Ph.D. dissertation, Oklahoma State University. Yavuzturk, C., and J.D. Spitler. 1999. A short time step response factor model for vertical ground loop heat exchangers. ASHRAE Transactions, 105:475-485. Zimmerman, D.R. 2000. Documentation of operation, maintenance & con- struction cost of geothermal heat pump systems in schools. Final Report EP-P3128/C1476. Electric Power Research Institute. Palo Alto, CA. BIBLIOGRAPHY Allen, E. 1980. Preliminary inventory of western U.S. cities with proximate hydrothermal potential. Eliot Allen and Associates, Salem, OR. Bernier, M.A. 2006. Closed-loop ground-coupled heat pump systems, ASHRAE Journal 48(9):12-19. Caneta Research. 1995. Operating experiences with commercial ground- source heat pumps. ASHRAE RP-863, Report. Chiasson, A. 2011. A feasibility study of a multi-source hybrid district geo- thermal heat pump system. Geo-Heat Center Quarterly Bulletin (May). Klamath Falls, Oregon 2011. Chiasson, A.D., and C. Yavusturk. 2003. Assessment of the viability of hybrid geothermal heat pump systems with solar thermal collectors. ASHRAE Transactions 109(2). Cosner, S.R., and J.A. Apps. 1978. A compilation of data on fluids from geo- thermal resources in the United States. DOE Report LBL-5936. Law- rence Berkeley Laboratory, Berkeley, CA. Hansen, G.M. 2011. Experimental testing and analysis ofspiral-helical sur- face water heat exchangers. M.S. Thesis. Oklahoma State University. Stillwater, Oklahoma. Im, P., and X. Liu. 2015. Case study for ARRA-funded ground-source heat pump demonstrations at Denver Museum of Nature and Science. Oak Ridge National Lab. Kavanaugh, S. 1991. Ground and water source heat pumps: A manual for the design and installation of ground coupled, ground water and lake water heating and cooling systems in southern climates. Energy Infor- mation Services, Tuscaloosa. Kavanaugh, S.P. 2003. Impact of operating hours on long-term heat storage and design of ground heat exchangers. ASHRAE Transactions 109(1). Kavanaugh, S., and C. Gray. 2016. A simple approach to affordable GSHPs. ASHRAE Journal 58(4). Kavanaugh, S.P , and M.C. Pezent. 1990. Lake water applications of water- to-air heat pumps. ASHRAE Transactions 96(1):813-820. Lund, J., ed. 2000. Geothermal direct use engineering and design guide- book. Geo-Heat Center, Klamath Falls. Lund, J.W. P.J. Lienau, G.G. Culver, and C. V. Higbee. 1979. Klamath Falls geothermal district heating. Geothermal Resources Council Transac- tions 3. Meline, L. 2013. How to select materials GHP piping systems. ASHRAE Journal 55(3):86-88. Mitchell, D.A. 1980. Performance of typical HVAC materials in two geo- thermal heating systems. ASHRAE Transactions 86(1):763-768. Mitchell, M.S. 2014. Experimental investigations and design tool develop- ment for surface water heat pump systems. M.S. thesis. Oklahoma State University. Stillwater. Performance Pipe. 1998. Polyethylene piping systems manual 10428-98 pip- ing manual. Performance Pipe Inc., Dallas. Phillipe, M., M. Bernier, and D. Marchio. 2010. Vertical geothermal bore- fields. ASHRAE Journal 52(7):20-28. Remund, C., and N. Paul. 2000. Groutingfor vertical geothermal heat pump systems: Engineering design andfield procedures manual. International Ground Source Heat Pump Association, Stillwater. Rogers, G.F.C., and Y.R. Mayhew. 1964. Heat transfer and pressure loss in helically coiled tubes with turbulent flow. International Journal of Heat and Mass Transfer 7(11):1207-1216. Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
7ae38e42-126a-4a4f-a3da-321bc37631f2 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 36 SOLAR ENERGY USE ¦ Quality and Quantity of Solar Energy ¦ 36.1 ¦ ¦ --- ¦ --- ¦ ¦ Solar Energy Collection ¦ 36.6 ¦ ¦ Water Heating Systems ¦ 36.10 ¦ ¦ Active and Passive Systems for Solar Heating and Cooling Systems Cooling by Nocturnal Radiation and Evaporation ¦ 36.15 ¦ ¦ Cooling by Solar Energy Sizing Solar Heating and Cooling Systems: Energy Requirements ¦ 36.16 ¦ ¦ ¦ ¦ ¦ ¦ 36.18 ¦ ¦ ¦ ¦ ¦ ¦ 36.19 ¦ THE sun radiates considerable energy onto the earth. Desire 0 put that relatively low-intensity (rarely over 950 W/m2) energy to work has led to the creation of many types of devices to convert that energy into useful forms, mainly heat and electricity. Economic valuing of that energy drives the ebb and flow of the global solar industry. This chapter discusses several different types of solar equipment and system designs for various HVAC applica- tions, as well as methods to determine availability of the solar resource. Worldwide, solar energy use varies in application and degree. In China and, to a lesser extent, Australasia, solar energy is widely used, particularly for water heating. In the Middle East, solar power is used for desalination and absorption air conditioning. Solar energy use in the United States is relatively modest, driven by tax policy and utility programs that generally react to energy shortages or the price of oil. In Europe, government incentives have fostered use of photo- voltaic and thermal systems for both domestic hot-water and space heating (solar combi systems), which have a well-established mar- ket in several countries, and solar cooling is an emerging market with a significant growth potential. Combined solar space heating/ cooling and domestic hot-water production (solar combi-plus sys- tems) may lead to both high solar fractions and economical systems because of the continuous (annual) exploitation ofthe solar collector field and other system components. Recent interest in sustainability and green buildings has led to an increased focus on solar energy devices for their nonpolluting and renewable qualities; replacing fossil fuel with domestic, renewable energy sources can also enhance national security by reducing dependence on imported energy. For more information on the use of solar and other energy sources, see the Energy Information Administration (EIA) of the U.S. Department of Energy (www.eia.gov) and the International Energy Agency (www.iea.org). 1. QUALITY AND QUANTITY OF SOLAR ENERGY Solar Constant Solar energy approaches the earth as electromagnetic radiation, with wavelengths ranging from 0. 1 �m (x-rays) to 100 m (radio waves). The earth maintains a thermal equilibrium between the annual input of shortwave radiation (0.3 to 2.0 um) from the sun and the outward flux of longwave radiation (3.0 to 30 �m). Only a lim- ited band is considered in terrestrial applications, because 99% of the sun's radiant energy has wavelengths between 0.28 and 4.96 �m. The current value of the solar constant (which is defined as the The preparation of this chapter is assigned to TC 6.7, Solar Energy Utili- zation. Installation Guidelines of Solar Thermal Collectors 36.23 Design, Installation, and Operation Checklist of Solar ¦ Heating and Cooling Systems ¦ 36.25 ¦ ¦ --- ¦ --- ¦ ¦ Photovoltaic Applications ¦ 36.27 ¦ ¦ Design and Performance of Photovoltaic ¦ ¦ Systems 36.29 ¦ Installation and Operation Guidelines for ¦ ¦ ¦ --- ¦ --- ¦ ¦ Photovoltaic Systems ¦ 36.33 ¦ ¦ Symbols ¦ 36.35 ¦ ![image](/image/placeholder) AIR OUT INDOOR COIL FAN REFRIGERANT-TO-WATER HEAT EXCHANGER AIR IN 0000 0000 COLD WATER EXPANSION DEVICE REVERSING VALVE OUTLET WATER INLET GROUND HOT LEVEL WATER AI IA in Fig. 1 Variation of Declination 8 (degrees) and Equation of Time ET as Function of Day of Year intensity of solar radiation on a surface normal to the sun's rays, just beyond the earth's atmosphere at the average earth-sun distance) is 1366.1 W/m2 (ASTM Standard E490). Chapter 14 of the 2017 ASHRAE Handbook-Fundamentals has further information on the available extraterrestrial solar radiation. Solar Angles The axis about which the earth rotates is tilted at an angle of 23.45° to the earth 's orbital plane and the sun 's equator. The earth's tilted axis results in a day-by-day variation of the angle between the earth-sun line and the earth , s equatorial plane, called the solar dec- lination 8. This angle varies with the date, as shown in Figure 1, and may be estimated by the following equation: 284 +N 8 = 23.45 sin 360° x 365 (1) where N = day of year, with January 1 = 1. The relationship between 8 and the date from year to year varies to an insignificant degree. The daily change in the declination is the primary reason for the changing seasons, with their variation in distri- bution of solar radiation over the earth's surface and the varying number ofhours of daylight and darkness. Note that the following sec- tions are based in the northern hemisphere; sites in the southern hemi- sphere will be 180° from the examples (e.g., a solar panel should face north). The earth 's rotation causes the sun 's apparent motion (Figure 2). The position of the sun can be defined in terms ofits altitude B above Inc. ASHRAE, 2019 user. single for Licensed 36.1 | {}
c05493bc-1955-43b9-ac4d-86138afbb84f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 36.2 Chart Type: pie SOUTH H B C NORTH WEST item_01 5% 1% 2% 1% 1% 1% Fig. 2 Apparent Daily Path of the Sun Showing Solar Altitude B and Solar Azimuth ⌀ the horizon (angle HOQ) and its azimuth ⌀, measured as angle HOS in the horizontal plane. At solar noon, the sun is exactly on the meridian, which contains the south-north line. Consequently, the solar azimuth ⌀ is 0°. The noon altitude BN is given by the following equation as BN = 90° - LAT + 8 where LAT = latitude. (2) Because the earth's daily rotation and its annual orbit around the sun are regular and predictable, the solar altitude and azimuth may be readily calculated for any desired time ofday when the lat- itude, longitude, and date (declination) are specified. Apparent solar time (AST) must be used, expressed in terms of the hour angle H, where H = (Number of hours from solar noon) x 15° Number of minutes from solar noon = 4 Solar Time Apparent solar time (AST) generally differs from local standard time (LST) or daylight saving time (DST), and the difference can be significant, particularly when DST is in effect. Because the sun appears to move at the rate of 360° in 24 h, its apparent rate of motion is 4 min per degree of longitude. The AST can be deter- mined from the following equation: (3) Inc. ASHRAE, 2019 user. single for Licensed AST = LST + ET + (4 min)(LST meridian - Local longitude) All standard meridians are multiples of 15° east or west of the prime meridian, which is at the Royal Observatory in Greenwich, U.K. The longitude correction is a positive value for the western hemisphere and negative for the eastern hemisphere. The longitudes of the seven standard time meridians that affect North America are Atlantic ST, 60°W; Eastern ST, 75°W; Central ST, 90°W; Mountain ST, 105°W; Pacific ST, 120°W; Alaska ST, 135°W; and Hawaii- Aleutian ST, 150°W. Starting with the prime meridian through Greenwich, many European countries define their standard meridi- ans based on legal, political, and economic, as well as purely physical or geographical, criteria. The longitudes of the three stan- dard time meridians that affect Europe are western European ST (U.K., Ireland, and Portugal), 0°; central European ST, 15°E [e.g., Spain (except for Canary Islands) to the south, Serbia to the east, and Sweden to the north]; and eastern European ST, 30°E (e.g., Greece and Cyprus to the south, Turkey to the east, Finland to the north). (4) 2019 ASHRAE Handbook- HVAC Applications (SI) The equation of time (ET) is the measure, in minutes, of the extent by which solar time, as determined by a sundial, runs faster or slower than local standard time (LST), as determined by a clock that runs at a uniform rate. The equation of time may be estimated by the following equation: ET = 9.87 sin 2B - 7.53 cos B - 1.5 sin B where B = 0.989(N - 81). (5) Example 1. Find AST at noon DST on July 21 for Washington, D.C., lon- gitude = 77°W; for Chicago, longitude = 87.6°W; and for Athens, Greece, longitude = 23.75°E. Solution: Noon DST is 11:00 AM LST. Washington is in the eastern time zone, and the LST meridian is 75°W. From Equation (5), the equa- tion of time for July 21 (N = 202) is -6.07 min. Thus, from Equation (4), noon DST for Washington is AST = 11:00 - 6.07 + 4(75 - 77) = 10:45.93 AST = 10.77 h Chicago is in the central time zone, and the LST meridian is 90°W. Thus, from Equation (4), noon central DST is AST = 11:00 - 6.07 + 4(90 - 87.6) = 11:03.53 AST = 11.06 h Athens is in the eastern European time zone, and the LST meridian 30°E. Thus, from Equation (4), noon DST is is AST = 11:00 - 6.07 - 4(30 - 23.75) = 10:28.93 AST = 10.48 h The hour angles H (see Figure 3) for these three examples are for Washington, H = (12.00 - 10.77)15° = 18.6° east for Chicago, H = (12.00 - 11.06)15° = 14.1° east for Athens, H = (12.00 - 10.48) 15° = 22.8° east To find the solar altitude B and the azimuth ⌀ when the hour angle H, latitude LAT, and declination 8 are known, the following equa- tions may be used: sin B = cos(LAT) cos 8 cos H + sin(LAT) sin 8 sin ⌀ = cos 8 sin H/cos B or cos ⌀ = (cos H cos �sin LAT - sin 8 cos LAT)/cos B (6) Incident Angle The angle between the line normal to the irradiated surface (OP' in Figure 3) and the earth-sun line OQ is called the incident angle 0. It is important in solar technology because it affects the intensity of the direct component of solar radiation striking the surface and the surface's ability to absorb, transmit, or reflect the sun's rays. To determine 0, the surface azimuth 4 and the surface-solar azi- muth Y must be known. The surface azimuth (angle POS in Figure 3) is the angle between the south-north line SO and the normal PO to the intersection of the irradiated surface with the horizontal plane, shown as line OM. The surface-solar azimuth, angle HOP, is designated by Y and is the angular difference between the solar azi- muth ⌀ and the surface azimuth 4. For surfaces facing east of south, Y= ⌀ - 4 in the morning and Y = ⌀ + V in the afternoon. For surfaces facing west of south, Y = � + Y in the morning and Y = ⌀ - 4 in the afternoon. For south-facing surfaces, 4 = 0°, so Y = � for all condi- tions. The angles 8, B, and ⌀ are always positive. (7) For a surface with a tilt angle � (measured from the horizontal), the angle of incidence 0 between the direct solar beam and the nor- mal to the surface (angle QOP in Figure 3) is given by (8) For vertical surfaces, ⌀= 90°, cos �=0, and sin � = 1.0, so Equa- tion (9) becomes cos 0 = cos B cos Y sin � + sin B cos � cos 0 = cos B cos Y (9) (10) | {}
03ca7e22-c0d9-4fab-8313-5a16167b5807 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Solar Energy Use 36.3 Chart Title: EARTH-SUN LINE Chart Type: line B C D E F G item_01 12Not explicitly defined 11Not explicitly defined 10Not explicitly defined 9Not explicitly defined 8Not explicitly defined 6Not explicitly defined Fig. 3 Solar Angles with Respect to a Tilted Surface For horizontal surfaces, � = 0°, sin � = 0, and cos � = 1.0, so Equation (9) leads to ⌀h = 90° - B Example 2. Find 0 for a south-facing surface tilted upward 30° from the horizontal at 40° north latitude at 4:00 PM, AST, on August 21. Solution: From Equation (3), at 4:00 PM on August 21, H = 4 x 15° = 60° From Equation (1) for August 21 (N = 233), 8 = 1 1.8° From Equation (6), sin B = cos 40° cos 11.8° cos 60° + sin 40° sin 11.8° B = 30.4° From Equation (7), sin � = cos 1 1.8° sin 60°/cos 30.4° ⌀ = 79.4° The surface faces south, so ⌀ = Y From Equation (9), cos 0 = cos 30.4° cos 79.4° sin 30° + sin 30.4° cos 30° 0 = 58.8° Solar Spectrum Beyond the earth , s atmosphere, the effective blackbody tempera- ture of the sun is 5760 K. The maximum spectral intensity occurs at 0.48 �m in the green portion of the visible spectrum. Thekaekara (1973) presents tables and charts of the sun 's extraterrestrial spectral irradiance from 0.120 to 100 �m, the range in which most of the sun 's radiant energy is contained. The ultraviolet portion of the spec- trum below 0.40 �m contains 8.73% of the total, another 38.15% is contained in the visible region between 0.40 and 0.70 um, and the infrared region contains the remaining 53.12%. Solar Radiation at the Earth's Surface In passing through the earth's atmosphere, some of the sun's direct radiation is scattered by nitrogen, oxygen, and other mole- cules, which are small compared to the wavelengths ofthe radiation; and by aerosols, water droplets, dust, and other particles with diam- eters comparable to the wavelengths (Gates 1966). This scattered radiation causes the sky to appear blue on clear days, and some ofit reaches the earth as diffuse radiation. Attenuation ofthe solar rays is also caused by absorption, first by the ozone in the outer atmosphere, which causes a sharp cutoff at 0.29 um of the ultraviolet radiation reaching the earth 's surface (Figure 4). In the longer wavelengths, there are series of absorption bands caused by water vapor, carbon dioxide, and ozone. The total amount of attenuation at any given location is determined by (1) the length of the atmospheric path through which the rays travel and (2) the composition of the atmosphere. The path length is expressed in terms of the air mass m, which is the ratio of the mass of atmo- sphere in the actual earth-sun path to the mass that would exist ifthe sun were directly overhead at sea level (m = 1.0). For all practical purposes, at sea level, m = 1.0/sin B. Beyond the earth's atmosphere, m = 0. Before 1967, solar radiation data were based on an assumed solar constant of 1324 W/m2 and on a standard sea-level atmosphere con- taining the equivalent depth of 2.8 mm of ozone, 20 mm of precipitable moisture, and 300 dust particles per cm3. Threlkeld and Jordan (1958) considered the wide variation of water vapor in the at- mosphere above the United States at any given time, and particularly the seasonal variation, which finds three times as much moisture in the atmosphere in midsummer as in December, January, and Febru- ary. The basic atmosphere was assumed to be at sea-level barometric pressure, with 2.5 mm of ozone, 200 dust particles per cm3, and an actual precipitable moisture content that varied throughout the year from 8 mm in midwinter to 28 mm in mid-July. Figure 5 shows the variation of the direct normal irradiation IDN with solar altitude, as estimated for clear atmospheres and for an atmosphere with variable moisture content. ( 1 1) The ASHRAE clear-sky model described in previous editions of this chapter operated under several well-known limitations. For ex- ample, the clearness number was not universally available; its value varied between 0.85 and 1.20 according to location and season in the United States, and was often taken as unity for lack of better data in other countries. The model also lacked universal applicability and the values of its coefficients had to be altered according to location. In addition, the model was derived from a very limited number of measurements, and its applicability outside the United States had never been demonstrated. Finally, clear-sky diffuse irradiance was proportional to beam irradiance, a fact that runs contrary to intuition (i.e., hazier skies should lead to less direct but more diffuse solar ir- radiation). To overcome these limitations, ASHRAE research projects RP-1363 and RP-1453 developed a significant update of the model (Thevenard and Gueymard 2010). The objectives were to ob- tain a more accurate model that could enable calculation of clear-sky radiation for any location in the world for all 12 months of the year, while retaining a relatively simple formulation. The resulting model (Gueymard and Thevenard 2013) can be found in Chapter 14 of the 2017 ASHRAE Handbook-Fundamentals, along with the tabulated parameters required at different locations. Design Values of Total Solar Irradiation The total solar irradiation Ite of a terrestrial surface of any orien- tation and tilt with an incident angle 0 is the sum of the direct component IDN cos 0 plus the diffuse component Ide coming from the sky plus whatever amount of reflected shortwave radiation Ir may reach the surface from the earth or from adjacent surfaces: Ite = IDN cos 0 + Ide Ir + The diffuse component is difficult to estimate because ofits wide variations and nondirectional nature. Figure 5 shows typical values of diffuse irradiation of horizontal and vertical surfaces. For addi- tional information on calculating clear-sky solar radiation, see Chapter 14 of the 2017 ASHRAE Handbook- -Fundamentals. (12) The maximum daily amount of solar irradiation that can be received at any given location is that which falls on a flat plate with its surface kept normal to the sun 's rays so it receives both direct and diffuse radiation. For fixed flat-plate collectors, the total amount of clear-day irradiation depends on the orientation and slope. As shown by Figure 6 for 40° north latitude, the total irradiation of horizontal surfaces reaches its maximum in midsummer, whereas vertical south-facing surfaces experience their maximum irradiation Inc. ASHRAE, 2019 user. single for Licensed | {}
b93d3dc2-59fc-42fa-a843-0284493cdc82 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 36.4 2019 ASHRAE Handbook-HVAC Applications (SI) Chart Type: line O3 U N2 H2O3 item_01 1400WK/(m2·μm) 1800WK/(m2·μm) 1600WK/(m2·μm) 200WK/(m2·μm) WAVELENGTH, �m Fig. 4 Spectral Solar Irradiation at Sea Level for Air Mass = 1.0 Chart Type: line EAST in AM, WEST in PM MOON, INDUSTRIAL ATMOSPHERE GATE5 (1966) DEC, JAN EAST in PM, WEST in AM MAR, OCT DIRECT IRRADIATION MOON'S 1940 STANDARD SEP APR MAY, AUG JUN, JUL THRELKELD AND JORDAN FEB, NOV item_01 400W/m2 300W/m2 100W/m2 100W/m2 100W/m2 100W/m2 100W/m2 100W/m2 100W/m2 100W/m2 100W/m2 100W/m2 100W/m2 100W/m2 Fig. 5 Variation with Solar Altitude and Time of Year for Direct Normal Irradiation during the winter. These curves show the combined effects of the varying length of days and changing solar altitudes. In general, flat-plate collectors are mounted at a fixed tilt angle � (above the horizontal) to give the optimum amount of irradiation for each purpose. Collectors intended for winter heating benefit from higher tilt angles than those used to operate cooling systems in summer. Solar water heaters, which should operate satisfactorily throughout the year, require an angle that is a compromise between the optimal values for summer and winter. Figure 6 shows the MJ/(day-m2) IRRADIATION, SOLAR Chart Title: TOTAL INSOLATION ON HORIZONAL SURFACE X-Axis: DAY-LONG TOTAL IRRADIATION FOR 21st DAY OF FACH MONTH Y-Axis: Count Chart Type: line LAT. - 10° LATINUDE LAT. + 10° LAT. + 20° VERTICAL SOUTH-FACING SURFACE TOTAL INSOLATION ON HORIZONAL SURFACE item_01 25Count 30Count 25Count 20Count 15Count 10Count Fig. 6 Total Daily Irradiation for Horizontal, Tilted, and Vertical Surfaces at 40° North Latitude monthly variation oftotal day-long irradiation on the 21st day of each month at 40° north latitude for flat surfaces with various tilt angles. NREL tables (rredc.nrel.gov/solan/pubs/redbook/) give the aver- age solar irradiation of each month, at latitudes 24 to 64° north, on surfaces with the following orientations: normal to the sun's rays (direct normal data do not include diffuse irradiation); horizontal; south-facing, tilted at (LAT-15), LAT, (LAT+15), and 90° from the horizontal. The day-long total irradiation for fixed surfaces is high- est for those that face south, but a deviation in azimuth of15 to 20° causes only a small reduction. Solar Energy for Flat-Plate Collectors The preceding data apply to clear days. Irradiation for average days may be estimated for any specific location by referring to pub- lications of the U.S. Weather Service. The Climatic Atlas of the Inc. ASHRAE, 2019 user. single for Licensed | {}
727c444f-118f-46ff-9bf1-71fe23901320 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Solar Energy Use 36.5 United States website (NOA 2010; www.ncdc.noaa.gov/climate atlas/) gives maps of monthly and annual values of percentage of possible sunshine, total hours of sunshine, mean solar radiation, mean sky cover, wind speed, and wind direction. The European Solar Radiation Atlas (Scharmer and Grief 2000) is a database that provides spatial and temporal climatic information for different time scales, including irradiation (global and its components), sun- shine duration, air temperature, precipitation, water vapor pressure, and air pressure for a number of stations. Chapter 14 in the 2017 ASHRAE Handbook-Fundamentals also provides several sources for obtaining solar data. The total daily horizontal irradiation data reported by the U.S. Weather Bureau for approximately 100 stations before 1964 show that the percentage of total clear-day irradiation is approximately a linear function of the percentage of possible sunshine. The irradia- tion is not zero for days when the percentage of possible sunshine is reported as zero, because substantial amounts of energy reach the earth in the form of diffuse radiation. Instead, the following relation- ship exists for the percentage of possible sunshine (ratio of day-long horizon irradiation to clear-day total horizon irradiation): Day-long actual I tH 100 = a + b Clear day I⌀H (13) where a and b are empirical constants for any specified month at any given location. See also Duffie and Beckman (2006) and Jordan and Liu (1977). Longwave Atmospheric Radiation In addition to the shortwave (0.3 to 2.0 um) radiation it receives from the sun, the earth receives longwave radiation (4 to 100 �m, with maximum intensity near 10 �m) from the atmosphere. In turn, a surface on the earth emits longwave radiation qRs in accordance with the Stefan-Boltzmann law: qRs = es⌀T4 (14) where es = surface emittance 0 = Stefan-Boltzmann constant, 5.67 x 10-8 W/(m2 - K4) Ts = absolute temperature of surface, K For most nonmetallic surfaces, the longwave hemispheric emit- tance is high, ranging from 0.84 for glass and dry sand to 0.95 for black built-up roofing. For highly polished metals and certain selec- tive surfaces, es may be as low as 0.05 to 0.20. Atmospheric radiation comes primarily from water vapor, car- bon dioxide, and ozone (Bliss 1961); very little comes from oxygen and nitrogen, although they make up 99% of the air. Approximately 90% of the incoming atmospheric radiation comes from the lowest 90 m. Thus, air conditions at ground level Tat largely determine the magnitude of the incoming radiation. Down- ward radiation from the atmosphere qRat may be expressed as 9Rat = eat⌀Tat (15) The sky emittance eat is a complex function of air temperature and moisture content. The dew point of the atmosphere near the ground determines the total amount of moisture in the atmosphere above the place where the dry-bulb (db) and dew-point (dp) tem- peratures of the atmosphere are determined (Reitan 1963). Bliss (1961) found that the sky emittance is related to the dew-point tem- perature, as shown by Table 1. is defined as the temperature The apparent sky temperature Tsky at which the sky (as a blackbody) emits radiation at the rate actually emitted by the atmosphere at ground level temperature with its actual emittance eat. Then, Table 1 Sky Emittance and Amount of Precipitable Moisture Versus Dew-Point Temperature ¦ Dew Point, °C ¦ Sky Emittance, eat ¦ Precipitable Water, mm ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ -30 ¦ 0.68 ¦ 3.3 ¦ ¦ -25 ¦ 0.70 ¦ 3.7 ¦ ¦ -20 ¦ 0.72 ¦ 4.3 ¦ ¦ -15 ¦ 0.74 ¦ 5.0 ¦ ¦ -10 ¦ 0.76 ¦ 6.2 ¦ ¦ -5 ¦ 0.78 ¦ 8.2 ¦ ¦ 0 ¦ 0.80 ¦ 11.2 ¦ ¦ 5 ¦ 0.82 ¦ 15.0 ¦ ¦ 10 ¦ 0.84 ¦ 20.3 ¦ ¦ 15 ¦ 0.86 ¦ 28.0 ¦ ¦ 20 ¦ 0.88 ¦ 38.6 ¦ Chart Type: line -20 -10 0 10 20 30 40 item_01 -23W/m2 -12W/m2 -1W/m2 100W/m2 40W/m2 20W/m2 10W/m2 Fig. 7 Radiation Heat Loss to Sky from Horizontal Blackbody ⌀Tsky = eatoTat or (16) 4 Tml T = eat sky Example 3. Consider a summer night condition when ground-level tem- peratures are 17.5°C dew point and 30°C dry bulb. From Table 1, eat at 17.5°C dew point is 0.87, and the apparent sky temperature is (17) Tsky = 0.870.25(30 + 273.15) = 292.8 K Thus, Tsky = 292.8 - 273.15 = 19.6°C, which is 10.4 K below the ground-level dry-bulb temperature. For a winter night in Arizona, when temperatures at ground level are 15°C db and -5°C dp, from Table 1, the sky emittance is 0.78, and the apparent sky temperature is 270.8 K or -2.4°C. A simple relationship, which ignores vapor pressure of the atmo- sphere, may also be used to estimate the apparent sky temperature: Inc. ASHRAE, 2019 user. single for Licensed 1.5 Tai Tsky = 0.0552 where Tis in kelvins. If the temperature of the radiating surface is assumed to equal the atmospheric temperature, the heat loss from a black surface (es = 1.0) may be found from Figure 7. (18) Example 4. For the conditions in the previous example for summer, 30°C db and 17.5°C dp, the rate of radiative heat loss is about 72 W/m2. For winter, 15°C db and -5°C dp, the heat loss is about 85 W/m2. Where a rough, unpainted roof is used as a heat dissipater, the rate of heat loss rises rapidly as the surface temperature goes up. For the summer example, a painted metallic roof, es = 0.96, at 38°C (311 K) will have a heat loss rate of | {}
7bb9b89e-2504-4f0b-a523-633e9d1c38ff | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 36.6 2019 ASHRAE Handbook- -HVAC Applications (SI) qRs = 0.96 x 5.67 x 10-8[3114 - 292.84] = 109 W/m2 This analysis shows that radiation alone is not an effective means of dissipating heat under summer conditions of high dew- point and ambient temperatures. In spring and fall, when both the dew-point and dry-bulb temperatures are relatively low, radiation becomes much more effective. On overcast nights, when cloud cover is low, the clouds act much like blackbodies at ground-level temperature, and virtually no heat can be lost by radiation. Exchange of longwave radiation between the sky and terrestrial surfaces occurs in the daytime as well as at night, but the much greater magnitude of the solar irradiation masks the longwave effects. 2. SOLAR ENERGY COLLECTION Solar energy can be converted by (1) chemical, (2) electrical, and (3) thermal processes. Photosynthesis is a chemical process that plants and other organisms use to convert CO2 to O2 and carbohy- drates. Photovoltaic cells convert solar energy to electricity. The section on Photovoltaic Applications discusses some applications for these devices. The thermal conversion process provides thermal energy for space heating and cooling, domestic water heating, power generation, distillation, and process heating. Solar Heat Collection by Flat-Plate Solar Thermal Collectors The solar irradiation calculation methods presented in the previ- ous sections may be used to estimate how much energy is likely to be available at any specific location, date, and time of day for collection by either a concentrating device, which uses only the direct rays of the sun, or by a flat-plate solar thermal collector (hereinafter called a flat-plate collector), which can use both direct and diffuse irradia- tion. Temperatures needed for space heating and cooling do not exceed 90°C, even for absorption refrigeration, and they can be attained with carefully designed flat-plate collectors. A flat-plate collector generally consists of the following compo- nents (see Figure 8): · Glazing. One or more sheets of glass or other radiation-transmitting material. · Tubes, fins, or passages. To conduct or direct the heat transfer fluid from the inlet to the outlet. · Absorber plates. Flat, corrugated, or grooved plates, to which the tubes, fins, or passages are attached. The plate may be integral with the tubes. · Headers or manifolds. To admit and discharge the heat transfer fluid. · Insulation. To minimize heat loss from the back and sides of the collector. · Container or casing. To surround the other components and pro- tect them from dust, moisture, etc. Collectors have been built in a wide variety of designs from many different materials (Figure 9). They have been used to heat fluids such as water, water plus an antifreeze additive, or air. Their major purpose is to collect as much solar energy as possible at the lowest possible total cost. The collector should also have a long effective life, despite the adverse effects of the sun 's ultraviolet radiation; corrosion or clogging because of acidity, alkalinity, or hardness of the heat transfer fluid; freezing or air binding in the case of water, or deposition of dust or moisture in the case of air; and broken glazing because of thermal expansion, hail, vandalism, or other causes. These problems can be minimized by using tempered glass. Glazing Materials Glass has been widely used to cover flat-plate solar collectors because it can transmit as much as 90% of the incoming shortwave solar irradiation while transmitting very little of the longwave radi- ation emitted outward from the absorber plate. Glass with low iron content has a relatively high transmittance for solar radiation (approximately 0.85 to 0.90 at normal incidence), but its transmit- tance is essentially zero for the longwave thermal radiation (5.0 to 50 �m) emitted by sun-heated surfaces. Note that commercially available grades of window and greenhouse glass have normal inci- dence transmittances of about 0.87 and 0.85, respectively. For direct radiation, the transmittance varies markedly with the angle of inci- dence, as shown in Table 2, which gives transmittances for single and double glazing using double-strength clear window glass. Plastic films and sheets also have high shortwave transmittance, but because most usable varieties also have transmission bands in the middle of the thermal radiation spectrum, their longwave trans- mittances may be as high as 0.40. Plastics are also generally limited in the temperatures they can sustain without deteriorating or undergoing dimensional changes. Only a few kinds of plastics can withstand the sun 's ultraviolet radi- ation for long periods. However, they are not broken by hail and other stones and, in the form of thin films, they are completely flex- ible and have low mass. The glass generally used in solar collectors may be either single- strength (2.2 to 2.5 mm thick) or double-strength (2.92 to 3.38 mm thick). The 4% reflectance from each glass/air interface is the most important factor in reducing transmission, although a gain of about 3% in transmittance can be obtained by using water-white glass. Antireflective coatings and surface texture can also improve trans- mission significantly. The effect of dirt and dust on collector glazing may be quite small, and the cleansing effect of an occasional rainfall is usually adequate to maintain the transmittance within 2 to 4% of its maximum. The glazing should admit as much solar irradiation as possible and reduce upward loss of heat as much as possible. Although glass ![image](/image/placeholder) HEADER GLAZING; TWO COVER GLASSES SHOWN FLUID TUBE ABSORBER PLATE CASING INSULATION HEADER Fig. 8 Exploded Cross Section Through Double-Glazed Solar Water Heater Inc. ASHRAE, 2019 user. single for Licensed | {}
10de73fa-f55e-4797-b6f3-31845ace6d7b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Solar Energy Use 36.7 ![image](/image/placeholder) SINGLE OR RECEIVER DOUBLE GLAZING FRAME CONCENTRATOR GLAZING REFLECTIVE TEMPERATURE-TOLERANT SURFACE EPDM OR GASKET EQUIVALENT GROMMET BOX FLOW PASSAGES TEMPERATURE-TOLERANT ABSORBER PLATE TRACKING INSULATION MECHANISM BACKING A. FLAT PLATE B. PARABOLIC TROUGH RETURN EXTRUDED MAT WITH TUBE FLOW PASSAGES GLASS ENVELOPE SUPPLY TUBE ABSORBER TUBE BOUNDARY LAYER AIR FLOW FROM MANIFOLD DRAWN THROUGH HOLES REFLECTOR THROUGH PASSAGES IN SOLAR-HEATED PLATE C. EVACUATED TUBES D. UNGLAZED EPDM COLLECTOR E. PERFORATED PLATE Fig. 9 Various Types of Solar Collectors Table2 Variation with Incident Angle ofTransmittance for Single and Double Glazing and Absorptance for Flat-Black Paint ¦ Incident Angle, Deg ¦ Transmittance ¦ Transmittance ¦ Absorptance for Flat-Black Paint ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Incident Angle, Deg ¦ Single Glazing ¦ Double Glazing ¦ Absorptance for Flat-Black Paint ¦ ¦ 0 ¦ 0.87 ¦ 0.77 ¦ 0.96 ¦ ¦ 10 ¦ 0.87 ¦ 0.77 ¦ 0.96 ¦ ¦ 20 ¦ 0.87 ¦ 0.77 ¦ 0.96 ¦ ¦ 30 ¦ 0.87 ¦ 0.76 ¦ 0.95 ¦ ¦ 40 ¦ 0.86 ¦ 0.75 ¦ 0.94 ¦ ¦ 50 ¦ 0.84 ¦ 0.73 ¦ 0.92 ¦ ¦ 60 ¦ 0.79 ¦ 0.67 ¦ 0.88 ¦ ¦ 70 ¦ 0.68 ¦ 0.53 ¦ 0.82 ¦ ¦ 80 ¦ 0.42 ¦ 0.25 ¦ 0.67 ¦ ¦ 90 ¦ 0.00 ¦ 0.00 ¦ 0.00 ¦ is virtually opaque to the longwave radiation emitted by absorber plates, absorption of that radiation causes an increase in the glass temperature and a loss of heat to the surrounding atmosphere by radiation and convection. This type of heat loss can be reduced by using an infrared-reflective coating on the underside of the glass; however, such coatings are expensive and reduce the effective solar transmittance of the glass by as much as 10%. In addition to serving as a heat trap by admitting shortwave solar radiation and retaining longwave thermal radiation, the glazing also reduces heat loss by convection. The insulating effect of the glazing is enhanced by using several sheets of glass, or glass plus plastic. Loss from the back of the plate rarely exceeds 10% of the upward loss. Absorber Plates The absorber plate absorbs as much of the irradiation as possible through the glazing, while losing as little heat as possible up to the atmosphere and down through the back of the casing. The absorber plates transfer retained heat to the transport fluid. The absorptance of the collector surface for shortwave solar radiation depends on the nature and color of the coating and on the incident angle, as shown in Table 2 for a typical flat-black paint. By suitable electrolytic or chemical treatments, selective surfaces can be produced with high values of solar radiation absorptance a and low values oflongwave emittance e. Essentially, typical selective surfaces consist of a thin upper layer, which is highly absorbent to shortwave solar radiation but relatively transparent to longwave ther- mal radiation, deposited on a substrate that has a high reflectance and a low emittance for longwave radiation. Selective surfaces are par- ticularly important when the collector surface temperature is much higher than the ambient air temperature. For fluid-heating collectors, passages must be integral with, or firmly bonded to, the absorber plate. A major problem is obtaining a good thermal bond between tubes and absorber plates without incurring excessive costs for labor or materials. Materials most fre- quently used for absorber plates are copper, aluminum, and steel. UV-resistant plastic extrusions are used for low-temperature appli- cation. If the entire absorber area is in contact with the heat transfer fluid, the material's thermal conductance is not important. Whillier (1964) concluded that steel tubes are as effective as cop- per ifthe bond conductance between tube and plate is good. Potential corrosion problems should be considered with the use of any metal. Bond conductance can range from 5700 W/(m2. K) for a securely soldered or brazed tube, to 17 W/(m2. K) for a poorly clamped or badly soldered tube. Plates of copper, aluminum, or stainless steel with integral tubes are among the most effective types available. Fig- ure 9 shows a few of the solar water and air heaters that have been used with varying degrees of success. Concentrating Collectors Temperatures far above those attainable by flat-plate collectors can be reached ifa large amount of solar radiation is concentrated on a relatively small collection area. Simple reflectors can markedly increase the amount of direct radiation reaching a collector, as shown in Figure 10A. Because ofthe apparent movement ofthe sun across the sky, con- ventional concentrating collectors must follow the sun's daily motion. There are two methods by which the sun's motion can be Inc. ASHRAE, 2019 user. single for Licensed | {}
faf590bc-73a7-49e0-9b66-0a344cb823ee | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 36.8 2019 ASHRAE Handbook HVAC Applications (SI) ![image](/image/placeholder) A. FLAT PLATE COLLECTOR WITH REFLECTIVE WINGS � ABSORBER COMPOUND PARABOLIC CONCENTRATOR ![image](/image/placeholder) B. PARABOLOIDAL CONCENTRATOR ![image](/image/placeholder) ABSORBER ![image](/image/placeholder) ABSORBER C. PARABOLIC TROUGH LENS CASING INSULATION WATER TUBE D. E. FRESNEL PARABOLIC TROUGH F. LINEAR FRESNEL CONCENTRATOR Fig. 10 Types of Concentrating Collectors readily tracked. The altazimuth method requires the tracking device to turn in both altitude and azimuth; when performed properly, this method enables the concentrator to track the sun exactly. Parabo- loidal solar furnaces (Figure 10B) generally use this system. The polar, or equatorial, mounting points the axis ofrotation at the North Star, tilted upward at the angle of the local latitude. By rotating the collector 15° per hour, it tracks the sun almost perfectly (perfectly on March 21 and September 21). Ifthe collector surface or aperture must be kept normal to the solar rays, a second motion is needed to correct for the change in the solar declination. This motion is not essential for most solar collectors. The maximum variation in the angle of incidence for a collector on a polar mount is ±23.5° on June 21 and December 21; the inci- dent angle correction then is cos 23.5° = 0.917. Horizontal reflective parabolic troughs, oriented east and west (Figure 10C), require continuous adjustment to compensate for changes in the sun 's declination. There is inevitably some morning and afternoon shading of the reflecting surface if the concentrator has opaque end panels. The necessity of moving the concentrator to accommodate the changing solar declination can be reduced by mov- ing the absorber or by using a trough with two sections of a parabola facing each other, as shown in Figure 10D. Known as a compound parabolic concentrator (CPC), this design can accept incoming radiation over a relatively wide range of angles. By using multiple internal reflections, any radiation that is accepted finds its way to the absorber surface located at the bottom of the apparatus. By filling the collector shape with a highly transparent material having an index of refraction greater than 1.4, the acceptance angle can be increased. By shaping the surfaces of the array properly, total internal reflection occurs at the medium/air interfaces, which results in a high con- centration efficiency. Known as a dielectric compound parabolic concentrator (DCPC), this device has been applied to the photovol- taic generation of electricity (Cole et al. 1977). The parabolic trough of Figure 10E can be simulated by many flat strips, each adjusted at the proper angle so that all reflect onto a common target. By supporting the strips on ribs with parabolic con- tours, a relatively efficient concentrator can be produced with less tooling than the complete reflective trough. Another concept applies this segmental idea to flat and cylindri- cal lenses. A modification is shown in Figure 10F, in which a linear Fresnel lens, curved to shorten its focal distance, can concentrate a relatively large area of radiation onto an elongated receiver. Using the equatorial sun-tracking mounting, this type of concentrator has been used to attain temperatures well above those that can be reached with flat-plate collectors. One disadvantage of concentrating collectors is that, except at low concentration ratios, they can use only the direct component of solar radiation, because the diffuse component cannot be concentrated by most types. However, an advantage of concentrating collectors is that, in summer, when the sun rises and sets well to the north of the east-west line, the sun tracker, with its axis oriented north-south, can begin to accept radiation directly from the sun long before a fixed, south-facing flat plate can receive anything other than diffuse radia- tion from the portion ofthe sky that it faces. At 40° north latitude, for example, the cumulative direct radiation available to a sun tracker (on a clear day) is 36.1 MJ/m2, whereas the total radiation falling on the flat plate tilted upward at an angle equal to the latitude is only 25.2 MJ/m2 each day. Thus, in relatively cloudless areas, the concen- trating collector may capture more radiation per unit of aperture area than a flat-plate collector. To get extremely high inputs of radiant energy, many flat mirrors or heliostats using altazimuth mounts can be used to reflect their incident direct solar radiation onto a common target. Using slightly concave mirror segments on the heliostats, large amounts of thermal energy can be directed into the cavity of a steam generator to pro- duce steam at high temperature and pressure. Inc. ASHRAE, 2019 user. single for Licensed | {}
fcb9f0f0-380b-4672-8265-54a7f6ad79ef | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Owning and Operating Costs 38.3 Table 4 Comparison of Service Life Estimates ¦ ¦ Median Service Life, Years ¦ Median Service Life, Years ¦ ¦ Median Service Life, Years ¦ Median Service Life, Years ¦ ¦ Median Service Life, Years ¦ Median Service Life, Years ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Equipment Item ¦ Abramson Akalin et al. (2005) (1978) ¦ Abramson Akalin et al. (2005) (1978) ¦ Equipment Item ¦ Abramson Akalin et al. (2005) (1978) ¦ Abramson Akalin et al. (2005) (1978) ¦ Equipment Item ¦ Abramson Akalin et al. (2005) (1978) ¦ Abramson Akalin et al. (2005) (1978) ¦ ¦ Air Conditioners ¦ ¦ ¦ Air Terminals ¦ ¦ ¦ Condensers ¦ ¦ ¦ ¦ Window unit ¦ N/A * ¦ 10 ¦ Diffusers, grilles, and registers ¦ N/A * ¦ 27 ¦ Air-cooled ¦ N/A ¦ 20 ¦ ¦ Residential single or split package ¦ N/A * ¦ 15 ¦ Induction and fan-coil units ¦ N/A * ¦ 20 ¦ Evaporative ¦ N/A* ¦ 20 ¦ ¦ Commercial through-the-wall ¦ N/A * ¦ 15 ¦ VAV and double-duct boxes ¦ N/A * ¦ 20 ¦ Insulation ¦ ¦ ¦ ¦ Water-cooled package ¦ 24 ¦ 15 ¦ Air washers ¦ N/A* ¦ 17 ¦ Molded ¦ N/A* ¦ 20 ¦ ¦ Heat pumps ¦ ¦ ¦ Ductwork ¦ N/A* ¦ 30 ¦ Blanket ¦ N/A * ¦ 24 ¦ ¦ Residential air-to-air ¦ N/A * ¦ 15 ¦ Dampers ¦ N/A* ¦ 20 ¦ Pumps ¦ ¦ ¦ ¦ Commercial air-to-air ¦ N/A * ¦ 15 ¦ Fans ¦ N/A* ¦ ¦ Base-mounted ¦ N/A * ¦ 20 ¦ ¦ Commercial water-to-air ¦ 24 ¦ 19 ¦ Centrifugal ¦ N/A* ¦ 25 ¦ Pipe-mounted ¦ N/A * ¦ 10 ¦ ¦ Roof-top air conditioners ¦ ¦ ¦ Axial ¦ N/A* ¦ 20 ¦ Sump and well ¦ N/A * ¦ 10 ¦ ¦ Single-zone ¦ N/A* ¦ 15 ¦ Propeller ¦ N/A* ¦ 15 ¦ Condensate ¦ N/A * ¦ 15 ¦ ¦ Multizone ¦ N/A * ¦ 15 ¦ Ventilating roof-mounted ¦ N/A* ¦ 20 ¦ Reciprocating engines ¦ N/A * ¦ 20 ¦ ¦ Boilers, Hot-Water (Steam) ¦ ¦ ¦ Coils ¦ ¦ ¦ Steam turbines ¦ N/A * ¦ 30 ¦ ¦ Steel water-tube ¦ 22 ¦ 24 ¦ DX, water, or steam ¦ N/A* ¦ 20 ¦ Electric motors ¦ N/A * ¦ 18 ¦ ¦ Steel fire-tube ¦ ¦ 25 ¦ Electric ¦ N/A* ¦ 15 ¦ Motor starters ¦ N/A * ¦ 17 ¦ ¦ Cast iron ¦ N/A* ¦ 35 ¦ Heat Exchangers ¦ ¦ ¦ Electric transformers ¦ N/A * ¦ 30 ¦ ¦ Electric ¦ N/A * ¦ 15 ¦ Shell-and-tube ¦ N/A* ¦ 24 ¦ Controls ¦ ¦ ¦ ¦ Burners ¦ N/A * ¦ 21 ¦ Reciprocating compressors ¦ N/A * ¦ 20 ¦ Pneumatic ¦ N/A * ¦ 20 ¦ ¦ Furnaces ¦ ¦ ¦ Packaged Chillers ¦ ¦ ¦ Electric ¦ N/A * ¦ 16 ¦ ¦ Gas- or oil-fired ¦ N/A * ¦ 18 ¦ Reciprocating ¦ N/A* ¦ 20 ¦ Electronic ¦ N/A * ¦ 15 ¦ ¦ Unit heaters ¦ ¦ ¦ Centrifugal ¦ 25 ¦ 23 ¦ Valve actuators ¦ ¦ ¦ ¦ Gas or electric ¦ N/A * ¦ 13 ¦ Absorption ¦ N/A* ¦ 23 ¦ Hydraulic ¦ N/A * ¦ 15 ¦ ¦ Hot-water or steam ¦ N/A * ¦ 20 ¦ Cooling Towers ¦ ¦ ¦ Pneumatic ¦ N/A * ¦ 20 ¦ ¦ Radiant heaters ¦ ¦ ¦ Galvanized metal ¦ 22 ¦ 20 ¦ Self-contained ¦ ¦ 10 ¦ ¦ Electric ¦ N/A * ¦ 10 ¦ Wood ¦ N/A* ¦ 20 ¦ ¦ ¦ ¦ ¦ Hot-water or steam ¦ N/A * ¦ 25 ¦ Ceramic ¦ N/A * ¦ 34 ¦ ¦ ¦ ¦ *N/A: Not enough data yet in Abramson et al. (2005). Note that data from Akalin (1978) for these categories may be outdated and not statistically relevant. Use these data with cau- tion until enough updated data are accumulated in Abramson et al. Chart Type: line 0 years 4 years 8 years 12 years 16 years 20 years 24 years 28 years 32 years 36 years 40 years 44 years 48 years item_01 100% 100% 100% 100% 100% 98% 75% 65% 55% 50% 25% 10% 5% Fig. 1 Survival Curve for Centrifugal Chillers [Based on data in Abramson et al. (2005)] Table 4 compares the estimates of median service life in Abramson et al. (2005) with those developed with those in Akalin (1978). Most differences are on the order of one to five years. Estimated service life of new equipment or components of systems not listed in Table 3 or 4 may be obtained from manufacturers, associ- ations, consortia, or governmental agencies. Because of the proprietary nature ofinformation from some of these sources, the variety of criteria used in compiling the data, and the diverse objectives in disseminating them, extreme care is necessary in comparing service life from different sources. Designs, materials, and components of equipment listed in Tables 3 and 4 have changed over time and may have altered the esti- mated service lives of those equipment categories. Therefore, establishing equivalent comparisons of service life is important. As noted, service life is a function of the time when equipment is replaced. Replacement may be for any reason, including, but not lim- ited to, failure, general obsolescence, reduced reliability, excessive maintenance cost, and changed system requirements (e.g., building characteristics, energy prices, environmental considerations). Service lives shown in the tables are based on the age of the equip- ment when it was replaced, regardless of the reason it was replaced. Locations in potentially corrosive environments and unique maintenance variables affect service life. Examples include the fol- lowing: · Coastal and marine environments, especially in tropical loca- tions, are characterized by abundant sodium chloride (salt) that is carried by sea spray, mist, or fog. Many owners require equipment specifications stating that HVAC equipment located along coastal waters will have corrosion- resistant materials or coatings. Design criteria for systems installed under these conditions should be carefully considered. · Industrial applications provide many challenges to the HVAC designer. Itis very important to know if emissions from the indus- trial plant contain products of combustion from coal, fuel oils, or releases of sulfur oxides (SO2, SO3) and nitrogen oxides (NOx) into the atmosphere. These gases typically accumulate and return to the ground in the form of acid rain or dew. Not only is it important to know the products being emitted from the industrial plant being designed, but also the adjacent upwind or downwind facilities. HVAC system design for a plant located downwind from a paper mill requires extraordinary cor- rosion protection or recognition of a reduced service life of the HVAC equipment. Inc. ASHRAE, 2019 user. single for Licensed | {}
7c81499f-b22f-4d8b-8a9b-e275838d6da1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 38.4 2019 ASHRAE Handbook-HVAC Applications (SI) · Urban areas generally have high levels of automotive emissions as well as abundant combustion by-products. Both of these con- tain elevated sulfur oxide and nitrogen oxide concentrations. · Maintenance factors also affect life expectancy. The HVAC designer should temper the service life expectancy of equipment with a maintenance factor. To achieve the estimated service life values in Table 3, HV AC equipment must be maintained properly, including good filter-changing practices and good maintenance procedures. For example, chilled-water coils with more than four rows and close fin spacing are virtually impossible to clean even using extraordinary methods; they are often replaced with multi- ple coils in series, with a maximum of four rows and lighter fin spacing. Depreciation Depreciation periods are usually set by federal, state, or local tax laws, which change periodically. Consult applicable tax laws for more information on depreciation. Interest or Discount Rate Most major economic analyses consider the opportunity cost of borrowing money, inflation, and the time value of money. Oppor- tunity cost of money reflects the earnings that investing (or lending) the money can produce. Inflation (price escalation) decreases the purchasing or investing power (value) of future money because it can buy less in the future. Time value of money reflects the fact that money received today is more useful than the same amount received a year from now, even with zero inflation, because the money is available earlier for reinvestment. The cost or value of money must also be considered. When bor- rowing money, a percentage fee or interest rate must normally be paid. However, the interest rate may not necessarily be the correct cost of money to use in an economic analysis. Another factor, called the discount rate, is more commonly used to reflect the true cost of money (see Fuller and Petersen [1996] for detailed discussions). Discount rates used for analyses vary depending on individual investment, profit, and other opportunities. Interest rates, in con- trast, tend to be more centrally fixed by lending institutions. To minimize the confusion caused by the vague definition and variable nature of discount rates, the U.S. government has specified particular discount rates to be used in economic analyses relating to federal expenditures. These discount rates are updated annually (Rushing et al. 2013) but may not be appropriate for private-sector economic analyses. Inc. ASHRAE, 2019 user. single for Licensed Periodic Costs Regularly or periodically recurring costs include insurance, property taxes, income taxes, rent, refurbishment expenses, disposal fees (e.g., refrigerant recycling costs), occasional major repair costs, and decommissioning expenses. Insurance. Insurance reimburses a property owner for a finan- cial loss so that equipment can be repaired or replaced. Insurance often indemnifies the owner from liability, as well. Financial recov- ery may include replacing income, rents, or profits lost because of property damage. Some of the principal factors that influence the total annual in- surance premium are building size, construction materials, amount and size of mechanical equipment, geographic location, and policy deductibles. Some regulations set minimum required insurance COV- erage and premiums that may be charged for various forms of insurable property. Property Taxes. Property taxes differ widely and may be col- lected by one or more agencies, such as state, county, or local governments or special assessment districts. Furthermore, prop- erty taxes may apply to both real (land, buildings) and personal (everything else) property. Property taxes are most often calculated as a percentage of assessed value, but are also deter- mined in other ways, such as fixed fees, license fees, registration fees, etc. Moreover, definitions of assessed value vary widely in different geographic areas. Tax experts should be consulted for applicable practices in a given area. Income Taxes. Taxes are generally imposed in proportion to net income, after allowance for expenses, depreciation, and numerous other factors. Special tax treatment is often granted to encourage certain investments. Income tax professionals can provide up-to- date information on income tax treatments. Other Periodic Costs. Examples of other costs include changes in regulations that require unscheduled equipment refurbishment to eliminate use of hazardous substances, and disposal costs for such substances. Replacement Costs and Salvage Value. Replacement costs and salvage value should be evaluated when calculating owning cost. Replacement cost is the cost to remove existing equipment and install new equipment. Salvage value is the value of equipment or its components for recycling or other uses. Equipment' s salvage value may be negative when removal, disposal, or decommissioning costs are considered. 2. OPERA TING COSTS Operating costs are those incurred by the actual operation of the system. They include costs of fuel and electricity, wages, supplies, water, material, and maintenance parts and services. Energy is a large part of total operating costs. Chapter 19 of the 2017 ASHRAE Handbook-Fundamentals outlines how fuel and electrical require- ments are estimated. Because most energy management activities are dictated by economics, the facility manager must understand the utility rates that apply to each facility. Electric rates are usually more complex than gas or water rates. In addition to general com- mercial or institutional electric rates, special rates may exist such as time of day, interruptible service, on-peak/off-peak, summer/winter, and peak demand. Electric rate schedules vary widely in North America. The facility manager should work with local utility com- panies to identify the most favorable rates and to understand how to qualify for them. The local utility representative can help the facility manager develop the most cost-effective methods of metering and billing. The facility manager must understand the utility rates, including the distinction between marginal and average costs and, in the case of demand-based electric rates, how demand is computed. Note that, in general, total energy consumption cannot be multi- plied by a per-unit energy cost to arrive at a correct annual utility cost, because rate schedules (especially for electricity) often have a sliding scale of prices that vary with consumption, time of day, and other factors. Future energy costs used in discounted payback analyses must be carefully evaluated. Energy costs have historically escalated at a dif- ferent rate than the overall inflation rate as measured by the consumer price index. To assist in life-cycle cost analysis, fuel price escalation rate forecasts by end-use sector and fuel type are updated annually by the National Institute of Standards and Technology and published in the Annual Supplement to NIST Handbook 135 (Rush- ing et al. 2010). There are no published projection rates for water prices for use in life-cycle cost analyses. Water escalation rates should be obtained from the local water utility when possible. Building designers should use energy price projections from their local utility in place of regional forecasts whenever possible, espe- cially when evaluating alternative fuel types. Deregulation in some areas may allow increased access to nontra- ditional energy providers and pricing structures; in other areas, traditional utility infrastructures and practices may prevail. The amount and profile of the energy used by the facility will also deter- mine energy cost. Unbundling energy services (having separate | {}
e7f8c473-1232-4470-aeb9-59e84c7b4a6c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Owning and Operating Costs 38.5 contracts for energy and for its transportation to point ofuse) may dic- tate separate agreements for each service component or may be packaged by a single provider. Contract length and price stability are factors in assessing nontraditional versus traditional energy suppliers when estimating operating costs. The degree of energy supply and system reliability and price stability considered necessary by the owner/occupants ofa building may require considerable deliberation. The sensitivity of a building's functionality to energy-related vari- ables should dictate the degree of attention allocated in evaluating these factors. Electrical Energy The total cost of electricity is determined by a rate schedule and is usually a combination of several components: consumption (megajoules), demand (kilowatts) fuel adjustment charges, special allowances or other adjustments, and applicable taxes. Of these, consumption and demand are the major cost components and the ones the owner or facility manager may be able to affect. Electricity Consumption Charges. Most electric rates have step-rate schedules for consumption, and the cost of the last unit consumed may be substantially different from that of the first. The last unit is usually cheaper than the first because the fixed costs to the utility may already have been recovered from earlier consump- tion costs. Because of this, the energy analysis cannot use average costs to accurately predict savings from implementation of energy conservation measures. A verage costs will overstate the savings possible between alternative equipment or systems; instead, mar- ginal (or incremental) costs must be used. To reflect time-varying operating costs or to encourage peak shifting, electric utilities may charge different rates for consumption according to the time of use and season, with higher costs occurring during the peak period of use. Fuel Adjustment Charge. Because of substantial variations in fuel prices, electric utilities may apply a fuel adjustment charge to recover costs. This adjustment may not be reflected in the rate schedule. The fuel adjustment is usually a charge per unit of con- sumption and may be positive or negative, depending on how much of the actual fuel cost is recovered in the energy consumption rate. The charge may vary monthly or seasonally. Allowances or Adjustments. Special discounts or rates may be available for customers who can receive power at higher voltages or for those who own transformers or similar equipment. Special rates or riders may be available for specific interruptible loads such as domestic water heaters. Certain facility electrical systems may produce a low power factor (i.e., ratio of real [active] kilowatt power to apparent [reac- tive] kVA power), which means that the utility must supply more current on an intermittent basis, thus increasing their costs. These costs may be passed on as an adjustment to the utility bill if the power factor is below a level established by the utility. When calculating power bills, utilities should be asked to provide detailed cost estimates for various consumption levels. The final calculation should include any applicable special rates, allowances, taxes, and fuel adjustment charges. Demand Charges. Electric rates may also have demand charges based on the customer' s peak kilowatt demand. Whereas consump- tion charges typically cover the utility's operating costs, demand charges typically cover the owning costs. Demand charges may be formulated in a variety of ways: · Straight charge. Cost per kilowatt per month, charged for the peak demand of the month. · Excess charge. Cost per kilowatt above a base demand (e.g., 50 kW), which may be established each month. KW Chart Type: bar Jan Feb Mar May Jun Jul Aug Sep Oct Nov Dec item_01 140kW 160kW 120kW 140kW 160kW 160kW 160kW 160kW 140kW 120kW 140kW Fig. 2 Bill Demand and Actual Demand for Atlanta Example Building, 2004 · Maximum demand (ratchet). Cost per kilowatt for maximum annual demand, which may be reset only once a year. This estab- lished demand may either benefit or penalize the owner. · Combination demand. Cost per hour of operation of demand. In addition to a basic demand charge, utilities may include further demand charges as demand-related consumption charges. The actual demand represents the peak energy use averaged over a specific period, usually 15, 30, or 60 min. Accordingly, high electrical loads of only a few minutes' duration may never be recorded at the full instantaneous value. Alternatively, peak demand is recorded as the average of several consecutive short periods (i.e., 5 min out of each hour). The particular method of demand metering and billing is important when load shedding or shifting devices are considered. The portion of the total bill attributed to demand may vary greatly, from 0% to as high as 70%. · Real-time or time-of-day rates. Cost of electricity at time of use. An increasing number of utilities offer these rates. End users who can shift operations or install electric load-shifting equipment, such as thermal storage, can take advantage of such rates. Because these rates usually reflect a utility's overall load profile and possibly the availability of specific generating resources, contact with the supplying utility is essential to determine whether these rates are a reasonable option for a specific application. Understanding Electric Rates. To illustrate a typical commer- cial electric rate with a ratchet, electricity consumption and demand data for an example building are presented in Table 5. The example building in Table 5 is on a ratcheted rate, and bill demand is determined as a percentage of actual demand in the sum- mer. How the ratchet operates is shown in Figure 2. Table 5 shows that the actual demand in the first six months of 2004 had no effect on the billing demand, and therefore no effect on the dollar amount of the bill. The same is true for the last three months of the year. Because of the ratchet, the billing demand in the first half of 2004 was set the previous summer. Likewise, billing demand for the last half of 2004 and first half of2005 was set by the peak actual demand of 180 kW in July 2003. This tells the facility manager to pay attention to demand in the summer months (June to September) and that demand is not a factor in the winter (October to May) months for this particular rate. (Note that Atlanta 's climate is hot and humid; in other climates, winter electric demand is an Inc. ASHRAE, 2019 user. single for Licensed | {}
e609fff5-fcb4-4ae4-a1f8-2bac49fe4cde | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 38.6 2019 ASHRAE Handbook-HVAC Applications (SI) Table 5 Electricity Data Consumption and Demand for ASHRAE Headquarters, 2003 to 2004 ¦ ¦ Billing Days ¦ Consumption, GJ ¦ Actual Demand, kW ¦ Billing Demand, kW ¦ Total Cost, USS ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Jan. 2003 ¦ 29 ¦ 205.6 ¦ 178 ¦ 185 ¦ 4,118 ¦ ¦ Feb. 2003 ¦ 31 ¦ 222.9 ¦ 145 ¦ 185 ¦ 4,251 ¦ ¦ Mar. 2003 ¦ 29 ¦ 216.2 ¦ 140 ¦ 185 ¦ 4,199 ¦ ¦ Apr. 2003 ¦ 29 ¦ 225.5 ¦ 154 ¦ 185 ¦ 4,271 ¦ ¦ May. 2003 ¦ 33 ¦ 264.4 ¦ 161 ¦ 185 ¦ 4,569 ¦ ¦ Jun. 2003 ¦ 26 ¦ 191.2 ¦ 171 ¦ 185 ¦ 4,007 ¦ ¦ Jul. 2003 ¦ 32 ¦ 242.4 ¦ 180 ¦ 185 ¦ 4,400 ¦ ¦ Aug. 2003 ¦ 30 ¦ 237.6 ¦ 170 ¦ 185 ¦ 4,364 ¦ ¦ Sep. 2003 ¦ 32 ¦ 230.3 ¦ 149 ¦ 171 ¦ 4,127 ¦ ¦ Oct. 2003 ¦ 30 ¦ 198.9 ¦ 122 ¦ 171 ¦ 3,865 ¦ ¦ Nov. 2003 ¦ 27 ¦ 165.7 ¦ 140 ¦ 171 ¦ 3,613 ¦ ¦ Dec. 2003 ¦ 34 ¦ 220.5 ¦ 141 ¦ 171 ¦ 4,028 ¦ ¦ Total 2003 ¦ 362 ¦ 2621.2 ¦ ¦ ¦ 49,812 ¦ ¦ Jan. 2004 ¦ 31 ¦ 212.5 ¦ 145 ¦ 171 ¦ 3,967 ¦ ¦ Feb. 2004 ¦ 29 ¦ 195.3 ¦ 159 ¦ 171 ¦ 3,837 ¦ ¦ Mar. 2004 ¦ 20 ¦ 133.5 ¦ 122 ¦ 171 ¦ 2,584 ¦ ¦ Apr. 2004 ¦ 12 ¦ 79.7 ¦ 133 ¦ 171 ¦ 1,547 ¦ ¦ May. 2004 ¦ 34 ¦ 231.3 ¦ 148 ¦ 171 ¦ 4,110 ¦ ¦ Jun. 2004 ¦ 29 ¦ 229.4 ¦ 148 ¦ 171 ¦ 4,321 ¦ ¦ Jul. 2004 ¦ 30 ¦ 248.8 ¦ 169 ¦ 169 ¦ 4,458 ¦ ¦ Aug. 2004 ¦ 32 ¦ 265.7 ¦ 170 ¦ 170 ¦ 4,605 ¦ ¦ Sep. 2004 ¦ 29 ¦ 232.2 ¦ 166 ¦ 166 ¦ 4,281 ¦ ¦ Oct. 2004 ¦ 30 ¦ 216.2 ¦ 152 ¦ 161 ¦ 3,866 ¦ ¦ Nov. 2004 ¦ 32 ¦ 236.7 ¦ 128 ¦ 161 ¦ 4,018 ¦ ¦ Dec. 2004 ¦ 31 ¦ 187.1 ¦ 132 ¦ 161 ¦ 3,646 ¦ ¦ Total 2004 ¦ 339 ¦ 2468.4 ¦ ¦ ¦ 45,240 ¦ important determinant of costs.) Consumption must be monitored all year long. Understanding the electric rates is key when evaluating the economics of energy conservation projects. Some projects save electrical demand but not consumption; others save mostly con- sumption but have little effect on demand. Electric rates must be correctly applied for economic analyses to be accurate. Chapter 56 contains a thorough discussion of various electric rates. Natural Gas Rates. Conventional natural gas rates are usually a combination of two main components: (1) utility rate or base charges for gas con- sumption and (2) purchased gas adjustment (PGA) charges. Although gas is usually metered by volume, it is often sold by energy content. The utility rate is the amount the local distribution company charges per unit of energy to deliver the gas to a particular location. This rate may be graduated in steps; the first 10 GJ of gas consumed may not be the same price as the last 10 GJ. The PGA is an adjustment for the cost of the gas per unit of energy to the local utility. It is similar to the electric fuel adjustment charge. The total cost per unit of energy is then the sum of the appropriate utility rate and the PGA, plus taxes and other adjustments. Interruptible Gas Rates and Contract/Transport Gas. Large industrial plants usually have the ability to burn alternative fuels and can qualify for special interruptible gas rates. During peak periods of severe cold weather, these customers' supply may be curtailed by the gas utility, and they may have to switch to propane, fuel oil, or some other back-up fuel. The utility rate and PGA are usually con- siderably cheaper for these interruptible customers than they are for firm-rate (noninterruptible) customers. Deregulation of the natural gas industry allows end users to negotiate for gas supplies on the open market. The customer actu- ally contracts with a gas producer or broker and pays for the gas at the source. Transport fees must be negotiated with the pipeline companies carrying the gas to the customer' s local gas utility. This can be a very complicated administrative process and is usually economically feasible only for large gas users. Some local utilities have special rates for delivering contract gas volumes through their system; others simply charge a standard utility fee (PGA is not applied because the customer has already negotiated with the sup- plier for the cost of the fuel itself). When calculating natural gas bills, be sure to determine which utility rate and PGA and/or contract gas price is appropriate for the particular interruptible or firm-rate customer. As with electric bills, the final calculation should include any taxes, prompt payment dis- counts, or other applicable adjustments. Other Fossil Fuels Propane, fuel oil, and diesel are examples of other fossil fuels in widespread use. Calculating the cost of these fuels is usually much simpler than calculating typical utility rates. The cost of the fuel itselfis usually a simple charge per unit vol- ume or per unit mass. The customer is free to negotiate for the best price. However, trucking or delivery fees must also be included in final calculations. Some customers may have their own transport trucks, but most seek the best delivered price. If storage tanks are not customer-owned, rental fees must be considered. Periodic replace- ment of diesel-type fuels may be necessary because of storage or shelf-life limitations and must also be considered. The final fuel cost calculation should include any of these costs that are applicable, as well as appropriate taxes. It is usually difficult, however, to relate usage of stored fossil fuels (e.g., fuel oil) with their operating costs. This is because pro- pane or fuel oil is bought in bulk and stored until needed, and normally not metered or measured as it is consumed, whereas nat- ural gas and power are metered and billed for as they are used. Energy Source Choices In planning for a new facility, the designer may undertake energy master planning. One component of energy master planning is choice of fuels. Typical necessary decisions include, for example, whether the building should be heated by electricity or natural gas, how service hot water should be produced, whether a hybrid heating plant (i.e., a combination of both electric and gas boilers) should be considered, and whether emergency generators should be fueled by diesel or natural gas. Decision makers should consider histories or forecasts of price volatility when selecting energy sources. In addition to national trending, local energy price trends from energy suppliers can be informative. These evaluations are particularly important where rel- ative operating costs parity exists between various fuel options, or where selecting more efficient equipment may help mitigate utility price concerns. Many sources ofhistoric and projected energy costs are available for reference. In addition to federal projections, utility and energy supplier annual reports and accompanying financial data may pro- vide insight into future energy costs. Indicators such as constrained or declining energy supply or production may be key factors in pro- jecting future energy pricing trends. Pricing patterns that suggest unusual levels of energy price volatility should be carefully ana- lyzed and tested at extreme predicted price levels to assess potential effects on system operating costs. Under conditions of rapidly evolving energy prices or new pricing options, imminent technological improvements, or pending environmental standards and mandates, the adaptability of design options must be carefully evaluated. Where appropriate, Inc. ASHRAE, 2019 user. single for Licensed | {}
1c557b75-42b4-46f3-89d7-67bf080d03b1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Owning and Operating Costs 38.7 contingency planning for accommodating foreseeable alterations to building systems may be prudent. Using diverse energy sources or suppliers in lieu of single sourcing may reduce cost of shifting en- ergy use in the event that single-source pricing becomes volatile, and may even provide negotiating leverage for facility owners. Water and Sewer Costs Water and sewer costs have risen in many parts ofthe country and should not be overlooked in economic analyses. Fortunately, these rates are usually very simple and straightforward: commonly, a charge per unit volume for water and a different charge per unit vol- ume for sewer. Because water consumption is metered and sewage is not, most rates use the water consumption quantity to compute the sewer charge. If an owner uses water that is not returned to sewer, there may be an opportunity to receive a credit or refund. Owners frequently use irrigation meters for watering grounds when the water authority has a special irrigation rate with no sewer charge. Another opportunity that is sometimes overlooked is to separately meter makeup water for cooling towers. This can be done with an irrigation meter if the costs of setting the meter can be justified; alternatively, it may be done by installing an in-line water meter for the cooling tower, in which case the owner reports the usage annu- ally and applies for a credit or refund. Because of rising costs of water and sewer, water recycling and reclamation is becoming more cost effective. For example, it may now be cost effective in some circumstances to capture cooling coil condensate and pump it to a cooling tower for makeup water. 3. MAINTENANCE COSTS The quality of maintenance and maintenance supervision can be a major factor in overall life-cycle cost of a mechanical system. The maintenance cost of mechanical systems varies widely depending upon configuration, equipment locations, accessibility, system com- plexity, service duty, geography, and system reliability requirements. Maintenance costs can be difficult to predict, because each system or facility is unique. Dohrmann and Alereza (1986) obtained maintenance costs and HVAC system information from 342 buildings located in 35 states in the United States. In 1983 U.S. dollars, data collected showed a mean HVAC system maintenance cost of $3.40/m2 per year, with a median cost of $2.60/m2 per year. Building age has a statistically significant but minor effect on HVAC maintenance costs. Analysis also indicated that building size is not statistically significant in ex- plaining cost variation. The type of maintenance program or service agency that building management chooses can also have a signifi- cant effect on total HVAC maintenance costs. Although extensive or thorough routine and preventive maintenance programs cost more to administer, they usually extend equipment life; improve re- liability; and reduce system downtime, energy costs, and overall life-cycle costs. Some maintenance cost data are available, both in the public domain and from proprietary sources used by various commercial service providers. These sources may include equipment manufactur- ers, independent service providers, insurers, government agencies (e.g., the U.S. General Services Administration), and industry-related organizations (e.g., the Building Owners and Managers Association [BOMA]) and service industry publications. More traditional, widely used products and components are likely to have statistically reliable records. However, design changes or modifications necessitated by industry changes, such as alternative refrigerants, may make histori- cal data less relevant. Newer HVAC products, components, system configurations, control systems and protocols, and upgraded or revised system applications present an additional challenge. Care is required when using data not drawn from broad experience or field reports. In Table 6 Comparison of Maintenance Costs Between Studies ¦ ¦ Cost per m2, as Reported ¦ Cost per m2, as Reported ¦ Consumer ¦ Cost per m2, 2004 Dollars ¦ Cost per m2, 2004 Dollars ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Survey ¦ Mean ¦ Median ¦ Price Index ¦ Mean ¦ Median ¦ ¦ Dohrmann and Alereza (1983) ¦ $3.44 ¦ $2.58 ¦ 99.6 ¦ $6.57 ¦ $4.95 ¦ ¦ Abramson et al. (2005) ¦ $5.06 ¦ $4.74 ¦ 188.9 ¦ $5.06 ¦ $4.74 ¦ many cases, maintenance information is proprietary or was spon- sored by a particular entity or group. Particular care should be taken when using such data. It is the user's responsibility to obtain these data and to determine their appropriateness and suitability for the application being considered. ASHRAE research project TRP-1237 (Abramson et al. 2005) developed a standardized Internet-based data collection tool and database on HVAC equipment service life and maintenance costs. The database was seeded with data on 163 buildings from around the country. Maintenance cost data were gathered for total HVAC system maintenance costs from 100 facilities. In 2004 dollars, the mean HVAC maintenance cost from these data was $5.06/m2, and the median cost was $4. 74/m2. Table 6 compares these figures with estimates reported by Dohrmann and Alereza (1983), both in terms of contemporary dollars, and in 2004 dollars, and shows that the cost per square metre varies widely between studies. Estimating Maintenance Costs Total HVAC maintenance cost for new and existing buildings with various types of equipment may be estimated several ways, using several resources. Equipment maintenance requirements can be obtained from the equipment manufacturers for large or custom pieces of equipment. Estimating in-house labor requirements can be difficult; BOMA (2003) provides guidance on this topic. Many independent mechanical service companies provide preventative maintenance contracts. These firms typically have proprietary esti- mating programs developed through their experience, and often provide generalized maintenance costs to engineers and owners upon request, without obligation. When evaluating various HVAC systems during design or retro- fit, the absolute magnitude of maintenance costs may not be as important as the relative costs. Whichever estimating method or resource is selected, it should be used consistently throughout any evaluation. Mixing information from different resources in an eval- uation may provide erroneous results. Applying simple costs per unit of building floor area for main- tenance is highly discouraged. Maintenance costs can be generalized by system types. When projecting maintenance costs for different HV AC systems, the major system components need to be identified with a required level of maintenance. The potential long-term costs of environmental issues on maintenance costs should also be considered. Factors Affecting Maintenance Costs Maintenance costs are primarily a measure oflabor activity. Sys- tem design, layout, and configuration can significantly affect the amount of time and effort required for maintenance and, therefore, the maintenance cost. Factors to consider when evaluating mainte- nance costs include the following: · Quantity and type of equipment. Each piece of equipment requires a core amount of maintenance and time, regardless of its size or capacity. A greater number of similar pieces of equip- ment are generally more expensive to maintain than larger but fewer units. For example, one manufacturer suggests the annual maintenance for centrifugal chillers is 24 h for a nominal 3500 Inc. ASHRAE, 2019 user. single for Licensed | {}
196619d1-9ee2-47a4-b1c1-2eb8be29856e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 38.8 2019 ASHRAE Handbook-HVAC Applications (SI) kW chiller and 16 h for a nominal 1800 kW chiller. Therefore, the total maintenance labor for a 3500 kW chiller plant with two 1800 kW chillers would be 32 h, or 1/3 more than a single 3500 kW chiller. · Equipment location and access. The ability to maintain equipment in a repeatable and cost-effective manner is signifi- cantly affected by the equipment' s location and accessibility. Equipment that is difficult to access increases the amount of time required to maintain it, and therefore increases mainte- nance cost. Equipment maintenance requiring erection of ladders and scaffolding or hydraulic lifts increases mainte- nance costs while likely reducing the quantity and quality of maintenance performed. Equipment location may also dictate an unusual working condition that could require more service personnel than normal. For example, maintenance performed in a confined space (per OSHA [Annual] definitions) requires an additional person to be present, for safety reasons. · System run time. The number of hours of operation for an HVAC system affects maintenance costs. Many maintenance tasks are dictated by equipment run time. The greater the run time, the more often these tasks need to be performed. · Critical systems. High-reliability systems require more mainte- nance to ensure uninterrupted system operation. Critical system maintenance is also usually performed with stringent shutdown and failsafe procedures that tend to increase the amount of time required to service equipment. An office building system can be turned off for a short time with little effect on occupants, allowing maintenance almost any time. Shutdown of a hospital operating room or pharmaceutical manufacturing HVAC system, on the other hand, must be coordinated closely with the operation of the facility to eliminate risk to patients or product. Maintenance on critical systems may sometimes incur labor premiums because of unusual shutdown requirements. · System complexity. More complex systems tend to involve more equipment and sophisticated controls. Highly sophisticated sys- tems may require highly skilled service personnel, who tend to be more costly. · Service environment. HVAC systems subjected to harsh operating conditions (e.g., coastal and marine environments) or environments like industrial operations may require more fre- quent and/or additional maintenance. · Local conditions. The physical location of the facility may require additional maintenance. Equipment in dusty or dirty areas or exposed to seasonal conditions (e.g., high pollen, leaves) may require more frequent or more difficult cleaning of equipment and filters. Additional maintenance tasks may be needed. · Geographical location. Maintenance costs for remote locations must consider the cost of getting to and from the locations. Labor costs for the number of anticipated trips and their duration for either in-house or outsourced service personnel to travel to and from the site must be added to the maintenance cost to properly estimate the total maintenance cost. · Equipment age. The effect of age on equipment repair costs var- ies significantly by type of HVAC equipment. Technologies in equipment design and application have changed significantly, affecting maintenance costs. · Available infrastructure. Maintenance costs are affected by the availability of an infrastructure that can maintain equipment, components, and systems. Available infrastructure varies on a national, regional, and local basis and is an important consider- ation in the HVAC system selection process. 4. REFRIGERANT PHASEOUTS Production phaseout of many commonly used refrigerants has required building owners to decide between replacing existing equipment or retrofitting for alternative refrigerants. Several factors must be considered, including · Initial Cost. New equipment may have a significantly higher installed cost than retrofitting existing equipment. For example, retrofitting an existing centrifugal chiller to operate on R-123 may cost 50% of the cost for a new chiller, making the installation cost ofa new chiller seem a prudent alternative. Conversely, the cost of rigging a new unit may significantly raise the installed cost, improving the first-cost advantage of refrigerant conversion. · Operating Costs. The overall efficiency of new equipment is often substantially better than that of existing equipment, depend- ing on age, usage, and level of maintenance performed over the life of the existing unit. In addition, conversion to alternative refrigerants may reduce capacity and/or efficiency of the existing equipment. · Maintenance Costs. The maintenance cost for new equipment is generally lower than that for existing equipment. However, the level of retrofit required to attain compatibility between existing equipment and new refrigerant often includes replacement or remanufacture of major unit components, which can bring the maintenance and repair costs in line with those expected of new equipment. · Equipment Useful Life. The effect of a retrofit on equipment useful life is determined by the extent of modification required. Complete remanufacture of a unit should extend the remaining useful life to a level comparable to that of new equipment. Replacing existing equipment or converting to alternative refrig- erants can improve overall system efficiency. Reduced capacity requirements and introduction of new technologies such as variable- speed drives and microprocessor-based controllers can substantially reduce annual operating costs and significantly improve a project's economic benefit. Information should be gathered to complete Table 1 for each alternative. The techniques described in the section on Economic Analysis Techniques may then be applied to compare the relative values of each option. Other Sources The DOE's Federal Energy Management Program (FEMP) (snerg/govereflimplind-potor-staprisec-efidency -programs) has up-to-date information on energy-efficient federal procurement. Products that qualify for the EP A/DOE ENERGY STAR label are listed, as are efficiency recommendations, cost effectiveness examples, and purchasing guidance. FEMP also pro- vides web-based cost-calculator tools that simplify the energy cost comparison between products with different efficiencies. The General Services Administration (GSA) has a basic ordering agreement (BOA) that offers a streamlined procurement method for some HV AC products based on lowest life-cycle cost. For chillers purchased through commercial sources, the BOA can still be used as a guide in preparing specifications. 5. OTHER ISSUES Financing Alternatives Alternative financing is commonly used in third-party funding of projects, particularly retrofit projects, and is variously called privatization, third-party financing, energy services outsourcing, performance contracting, energy savings performance contracting (ESPC), or innovative financing. In these programs, an outside party performs an energy study to identify or quantify attractive energy-saving retrofit projects and then (to varying degrees) designs, builds, and finances the retrofit program on behalf of the owner or host facility. These contracts range in complexity from Inc. ASHRAE, 2019 user. single for Licensed | {}
396e00b3-1798-49c0-9484-bec68c8fd81a | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Owning and Operating Costs 38.9 simple projects such as lighting upgrades to more detailed projects involving all aspects of energy consumption and facility operation. Alternative financing can be used to accomplish any or all of the following objectives: · Upgrade capital equipment · Provide for maintenance of existing facilities · Speed project implementation · Conserve or defer capital outlay · Save energy · Save money The benefits of alternative financing are not free. In general terms, these financing agreements transfer the risk of attaining future savings from the owner to the contractor, for which the con- tractor is paid. In addition, these innovative owning and operating cost reduction approaches have important tax consequences that should be investigated on a case-by-case basis. There are many variations of the basic arrangements and nearly as many terms to define them. Common nomenclature includes guaranteed savings (performance-based), shared savings, paid from savings, guaranteed savings loans, capital leases, municipal leases, and operating leases. For more information, see the U.S. Depart- ment of Energy's website and DOE (2007). A few examples of alternative financing techniques follow. Leasing. Among the most common methods of alternative financing is the lease arrangement. In a true lease or lease-purchase arrangement, outside financing provides capital for construction of a facility. The institution then leases the facility at a fixed monthly charge and assumes responsibility for fuel and personnel costs asso- ciated with its operation. Leasing is also commonly available for individual pieces of equipment or retrofit systems and often includes all design and installation costs. Equipment suppliers or independent third parties retain ownership of new equipment and lease it to the user. Outsourcing. For a cogeneration, steam, or chilled-water plant, either a lease or an energy output contract can be used. An energy output contract enables a private company to provide all the capital and operating costs, such as personnel and fuel, while the host facil- ity purchases energy from the operating company at a variable monthly charge. Energy Savings. Retrofit projects that lower energy usage create an income stream that can be used to amortize the investment. In paid-from-savings programs, utility payments remain constant over a period of years while the contractor is paid out of savings until the project is amortized. In shared savings programs, the insti- tution receives a percentage of savings over a longer period of years until the project becomes its property. In a guaranteed savings pro- gram, the owner retains all the savings and is guaranteed that a certain level of savings will be attained. A portion of the savings is used to amortize the project. In any type of energy savings project, building operation and use can strongly affect the amount of savings actually realized. Low-Interest Financing. In this arrangement, the supplier offers equipment with special financing arrangements at below-market in- terest rates. Cost Sharing. Several variations of cost-sharing programs exist. In some instances, two or more groups jointly purchase and share new equipment or facilities, thereby increasing use of the equipment and improving the economic benefits for both parties. In other cases, equipment suppliers or independent third parties (such as utilities) who receive an indirect benefit may share part ofthe equip- ment or project cost to establish a market foothold for the product. Alternative Property-Based Financing for Building and Energy-Related Upgrades. One common challenge for imple- menting energy-efficient upgrades (even with excellent internal rate of return or savings-to-investment parameters) is simply getting someone to commit the financing or credit line to fund the project. This is especially problematic in a building where tenant occupancy is high. Although the overall energy savings gained by the project might yield a great payback, the challenge stems from uncertainty as to how tenants will benefit and building owner concerns over not having a method for recouping the investment. Property assessment for clean energy (PACE) is a method for providing financing that is based on increasing the municipal tax base for funding energy reduction methods (ERMs). This approach can yield energy savings for the building and does not affect the building or property owner's credit rating or their ability to borrow. The goal is to offset the added tax costs with the energy savings of the ERMs. Life-cycle costs over the life ofthe funding must be care- fully considered and maintained to accepted ASHRAE standards. PACE relies on being recognized, accepted, and adopted into local tax laws. Over half the U.S. states have accepted PACE, but it is not currently well developed or even accepted in all locations. The structure and interest rate of P. ACE is a function of firms providing the PACE process and the actual funding. Currently, 16 states have approved this type of municipal tax- based funding for specifically energy-efficient upgrades in buildings. The exact mechanics for the program vary by location and by state), but typically involve an investment-grade building energy audit to ASHRAE standards. This provides a reasonably reliable method with which to pick the internal rate ofreturn (see the section on Internal Rate of Return, under Economic Analysis Tech- niques) of different ERMs. Once the different ERMs are evaluated, the life-cycle cost anal- ysis can be completed (see the section on Life-Cycle Costs, under Economic Analysis Techniques). The goal is for the ERMs to save more energy than the increase to the municipal tax base, so that the overall ownership or life-cycle costs are decreased. To pass on energy savings to a building's tenants, condo owners, and other occupants without putting a financial burden on the building owner(s), the following must be achieved: · A skillfully executed, investment-grade energy audit executed to ASHRAE standards · Selection of effective ERMs · Proper life-cycle operation · Proper maintenance of the ERMs Property owners who choose to participate in a PACE program repay their ERMs over a set period (typically 5 to 30 years) through property assessments. Such assessments are secured by the property itself and become an added payment on the owner's property tax bills or are ultimately paid for by the tenants or businesses through common-area maintenance fees or operational costs. When PACE projects are properly structured and maintained, the energy savings achieved can be greater than the costs of owning and operating the building and provide a realized monthly savings from the first year through the life of the improvement. PACE projects present a solu- tion for owners and tenants who do not want to commit credit resources to provide needed ERMs and building improvements. If the building is sold, the assessment or financing stays with the prop- erty in the form of a tax assessment. The U.S. Department of Energy (DOE) and other material in the Bibliography are good sources for more in-depth information. Note that the way PACE is administered by local municipalities changes according to location. A general sequence of PACE process is shown in Figure 3. Because the PACE assessment is a debt that is tied to the property and not the property owners, depending on state laws, the assess- ment can transfer with the building and the repayment obligation does not affect building owners. This lack of obligation for the prop- erty owner eliminates a key opposition to investing in ERMs, Inc. ASHRAE, 2019 user. single for Licensed | {}
d4e043df-345b-4453-a3af-a79519d38743 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 38.10 2019 ASHRAE Handbook- -HVAC Applications (SI) ¦ CITY OR COUNTY CREATES TYPE OF LAND- SECURED FINANCING DISTRICT OR SIMILAR LEGAL MECHANISM → ¦ PROPERTY OWNERS VOLUNTARILY SIGN UP FOR FINANCING AND INSTALL ENERGY PROJECTS ¦ THE LENDER* PROVIDES FUNDS TO PROPERTY OWNER TO PAY FOR ENERGY PROJECT ¦ PROPERTY OWNER REPAYS BOND THROUGH PROPERTY TAX BILL (UP TO 30 YEARS) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ *Depending on program structure, lender may be private capital provider or local jurisdiction. Fig. 3 PACE Process (based on DOE 2013) Table 7 Key Pros and Cons of PACE ¦ Pros ¦ Cons ¦ ¦ --- ¦ --- ¦ ¦ Allows for secure financing of com- prehensive projects over terms up to 30 years ¦ Available only to property owners; renters cannot access programs directly ¦ ¦ Repayment obligation passes with ownership, overcoming hesitancy to invest in longer payback measures ¦ Cannot finance portable items ¦ ¦ Senior lien municipal financing may lead to low interest rates ¦ Requires dedicated staff time ¦ ¦ Interest portion of assessment repayments are tax deductible ¦ High legal and administrative expenses to set up ¦ ¦ Lower transaction costs compared to private loans ¦ Not appropriate for investments below $50 000 ¦ ¦ Allows municipalities to encourage energy efficiency and renewable energy without putting their general funds at risk ¦ Some resistance by lenders whose priority in default may be reduced ¦ Source: DOE (2013). because many property owners may not own the building long enough to enjoy the savings as opposed to the initial cost. Other owners simply will be hesitant to use scarce financial resources when they might not benefit directly from lower utility bills. Table 7 summarizes the key advantages and disadvantages of PACE for property owners. Key steps local governments may follow to implement a com- mercial PACE program include the following: 1. Review and address issues: Become familiar with issues re- lated to PACE and factor their consequences into program design and implementation. 2. Establish supporting framework: Lay a solid foundation for the program in the areas of team composition, goals, legisla- tion, and assessment district formation. 3. Choose capital sourcing approach(es): Choose whether the projects will be funded using private capital, and if so, whether the program will use an open- or closed-market approach. 4. Determine whether and how to deploy credit enhancement: Decide how to achieve the best interest rates for the program and how best to apply and leverage any available funds to fit the program 's design. 5. Choose eligible property types: Select the commercial prop- erty types eligible for the program. 6. Assemble eligible project measures: Determine what types of improvements can be financed based on enabling legislation and program goals. 7. Choose energy audit requirements: Decide the types of energy audits applicants will be required to undergo to assess expected project energy/cost savings. 8. Choose program eligibility criteria: Determine the program underwriting/eligibility criteria that applicants and their prop- erties must meet. See DOE (2013) for guidance. 9. Leverage existing utility rebate/incentive programs: Inves- tigate local utility rebate/incentive programs and how best to leverage them. 10. Plan quality assurance/quality control: Decide how the pro- gram will ensure that project work meets program quality stan- dards and how to guard against fraud. 11. Design application processing procedures: Design the pro- cess for reviewing applications and either approving or reject- ing them. 12. Specify contractor requirements: Specify the requirements for energy auditors and contractors to participate in the pro- gram. 13. Market and launch program: Decide what kind of outreach will be made to property owners and contractors, and launch the program. Note that many steps are carried out concurrently and not neces- sarily in this exact order. Often, an additional step for procurement is appropriate to choose capital and/or administration entities. Note that although PACE is an alternative to traditional financ- ing, as with all energy saving or performance-based methods, the actual performance data, parameters, and assumptions of energy modeling and analysis of projected costs, along with real-world operating conditions and operators' varying skill levels, lead to changing energy and life-cycle costs. District Energy Service District energy service is increasingly available to building own- ers; district heating and cooling eliminates most on-site heating and cooling equipment. A third party produces treated water or steam and pipes it from a central plant directly to the building. The build- ing owner then pays a metered rate for the energy that is used. A cost comparison of district energy service versus on-site generation requires careful examination of numerous, often site- specific, factors extending beyond demand and energy charges for fuel. District heating and cooling eliminates or minimizes most costs associated with installation, maintenance, administration, repair, and operation of on-site heating and cooling equipment. Specifically, costs associated with providing water, water treat- ment, specialized maintenance services, insurance, staff time, space to house on-site equipment, and structural additions needed to support equipment should be considered. Costs associated with auxiliary equipment, which represent 20 to 30% of the total plant annual operating costs, should also be included. Any analysis that fails to include all the associated costs does not give a clear picture of the building owner's heating and cooling alternatives. In addition to the tangible costs, there are a number of other factors that should be considered, such as convenience, risk, environmental issues, flexibility, and back-up. On-site electrical power generation covers a broad range of applications, from emergency back-up to power for a single piece of equipment to an on-site power plant supplying 100% of the facil- ity's electrical power needs. Various system types and fuel sources are available, but the economic principles described in this chapter apply equally to all of them. Other chapters (e.g., Chapters 7 and 37 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment) may be helpful in describing system details. On-Site Electrical Power Generation An economic study of on-site electrical power generation should include consideration of all owning, operating, and maintenance costs. Typically, on-site generation is capital intensive (i.e., high first cost) and therefore requires a high use rate to produce savings Inc. ASHRAE, 2019 user. single for Licensed | {}
85e24bfc-da84-4d02-a2b5-10c75ed7c92f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Owning and Operating Costs Inc. ASHRAE, 2019 user. single for Licensed 38.11 adequate to support the investment. High use rates mean high run time, which requires planned maintenance and careful operation. Owning costs include any related systems required to adapt the building to on-site power generation. Additional equipment is required ifthe building will also use purchased power from a utility. Costs associated with shared equipment should also be considered. For example, ifthe power source for the generator is a steam turbine, and a hot-water boiler would otherwise be used to meet the HVAC demand, the boiler would need to be a larger, high-pressure steam boiler with a heat exchanger to meet the hot-water needs. Operation and maintenance costs for the boiler also are increased because of the increased operating hours. Costs of an initial investment and ongoing inventory of spare parts must also be considered. Most equipment manufacturers provide a recommended spare parts list as well as recommended maintenance schedules, typically daily, weekly, and monthly routine maintenance and periodic major overhauls. Major overhaul frequency depends on equipment use and requires taking the equipment off-line. The cost of either lost building use or the provision of electricity from an alternative source during the shutdown should be considered. 6. ECONOMIC ANALYSIS TECHNIQUES Analysis of overall owning and operating costs and comparisons of alternatives require an understanding of the cost of lost opportu- nities, inflation, and the time value of money. This process of economic analysis of alternatives falls into two general categories: simple payback analysis and detailed economic analyses (life-cycle cost analyses). A simple payback analysis reveals options that have short versus long paybacks. Often, however, alternatives are similar and have similar paybacks. For a more accurate comparison, a more compre- hensive economic analysis is warranted. Many times it is appropriate to have both a simple payback analysis and a detailed economic analysis. The simple payback analysis shows which options should not be considered further, and the detailed economic analysis determines which of the viable options are the strongest. The strongest options can be accepted or further analyzed if they include competing alternatives. Simple Payback In the simple payback technique, a projection of the revenue stream, cost savings, and other factors is estimated and compared to the initial capital outlay. This simple technique ignores the cost of borrowing money (interest) and lost opportunity costs. It also ignores inflation and the time value of money. Example 1. Equipment item 1 costs $10 000 and will save $2000 per year in operating costs; equipment item 2 costs $12 000 and saves $3000 per year. Which item has the best simple payback? ¦ Item 1 ¦ $10 000($2000/yr) = 5-year simple payback ¦ ¦ --- ¦ --- ¦ ¦ Item 2 ¦ $12 000/($3000/yr) = 4-year simple payback ¦ Because analysis of equipment for the duration ofits realistic life can produce a very different result, the simple payback technique should be used with caution. More Sophisticated Economic Analysis Methods Economic analysis should consider details of both positive and negative costs over the analysis period, such as varying inflation rates, capital and interest costs, salvage costs, replacement costs, interest deductions, depreciation allowances, taxes, tax credits, mortgage payments, and all other costs associated with a particular system. See the section on Symbols for definitions of variables. Present- v alue (Present Worth) Analysis. All sophisticated economic analysis methods use the basic principles of present value analysis to account for the time value of money. Therefore, a good understanding of these principles is important. The total present value (present worth) for any analysis is deter- mined by summing the present worths of all individual items under consideration, both future single-payment items and series of equal future payments. The scenario with the highest present value is the preferred alternative. Single-Payment Present- Value Analysis. The cost or value of money is a function of the available interest rate and inflation rate. The future value F of a present sum of money P over n periods with compound interest rate i per period is F = P(1 + i)" (1) Conversely, the present value or present worth P of a future sum of money F is given by P=F/(1+i)" (2) or P= F PWF (i,n)sgl (3) is de- where the single-payment present-worth factor PWF (i,n) sgl fined as PWF (i,n)sgl = 1/(1 +i)" (4) Example 2. Calculate the value in 10 years at 10% per year interest of a system presently valued at $10 000. F = P(1 +i)" = $10 000(1 + 0.1)10 = $25,937.42 Example 3. Using the present-worth factor for 10% per year interest and an analysis period of 10 years, calculate the present value of a future sum of money valued at $10 000. (Stated another way, determine what sum of money must be invested today at 10% per year interest to yield $10 000 10 years from now.) P = F PWF (i,n)sgl P = $10 000 1/(1 + 0. 1)10 = $3855.43 Series of Equal Payments. The present-worth factor for a series of future equal payments (e.g., operating costs) is given by n 1 +i - 1 PWF(i,n)ser = n i 1 + i (5) The present value P of those future equal payments (PMT) is then the product of the present-worth factor and the payment [i.e., P = PWF(i,n)ser PMT]. The number of future equal payments to repay a present value of money is determined by the capital recovery factor (CRF), which is the reciprocal of the present-worth factor for a series of equal payments: CRF = PMT/P (6) n i 1 + i i CRF(i,n), = = n -n 1 + i - 1 1 - 1 + i The CRF is often used to describe periodic uniform mortgage or loan payments. Note that when payment periods other than annual are to be stud- ied, the interest rate must be expressed per appropriate period. For example, if monthly payments or return on investment are being analyzed, then interest must be expressed per month, not per year, and n must be expressed in months. (7) Example 4. Determine the present value of an annual operating cost of $1000 per year over 10 years, assuming 10% per year interest rate. | {}
fc06ede0-9bbe-4ef9-aadb-9109e03c8216 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 38.12 2019 ASHRAE Handbook - HVAC Applications (SI) 10 10 PWF (i,n)ser = 1 + 0.1 - 1 0.1 1 + 0.1 = 6.14 P = $1000 6.14 = $6140 Example 5. Determine the uniform monthly mortgage payments for a loan of $100 000 to be repaid over 30 years at 10% per year interest. Because the payment period is monthly, the payback duration is 30(12) = 360 monthly periods, and the interest rate per period is 0.1/12 = 0.00833 per month. 360 360 CRF(i,n) = 0.008 33 1 + 0.008 33 1 + 0.008 33 - 1 = 0.008 773 PMT = P CRF = $100 000 0.008 773 = $877.30 per month Improved Payback Analysis. This somewhat more sophisti- cated payback approach is similar to the simple payback method, except that the cost of money (interest rate, discount rate, etc.) is considered. Solving Equation (7) for n yields the following: In CRF CRF -i n= In 1 +i (8) Given known investment amounts and earnings, CRFs can be calculated for the alternative investments. Subsequently, the number of periods until payback has been achieved can be calculated using Equation (8). Example 6. Compare the years to payback of the same items described in Example 2 if the value of money is 10% per year. Item 1 cost = $10 000 savings = $2000/year CRF = $2000/$10 000 = 0.2 n = ln[0.2/(0.2 - 0.1)]/ln(1 + 0.1) = 7.3 years Item 2 cost = $12 000 savings = $3000/year CRF = $3000/$12 000 = 0.25 n = In[0.25/(0.25 - 0.1)]/ln(1 +0.1) = 5.4 years If years to payback is the sole criteria for comparison, Item 2 is preferable because the investment is repaid in a shorter period of time. Accounting for Inflation. Different economic goods may inflate at different rates. Inflation reflects the rise in the real cost of a commodity over time and is separate from the time value of money. Inflation must often be accounted for in an economic eval- uation. One way to account for inflation is to substitute effective interest rates that account for inflation into the equations given in this chapter. The effective interest rate i , sometimes called the real rate, accounts for inflation rate j and interest rate i or discount rate id; it can be expressed as follows (Kreider and Kreith 1982): 1 + i i - i = - 1 = 1 + ] 1 +j Different effective interest rates can be applied to individual components of cost. Projections for future fuel and energy prices are available in the Annual Supplement to NIST Handbook 135 (Rush- ing et al. 2010). (9) Example 7. Determine the present worth P of an annual operating cost of $1000 over 10 years, given a discount rate of 10% per year and an infla- tion rate of 5% per year. i = 0.1 - 0.05 1 + 0.05 = 0.0476 10 1 + 0.0476 - 1 PWF(i n)ser = = 7.813 10 0.0476 1 + 0.0476 P = $1000 7.813 = $7813 The following are three common methods of present-value anal- ysis that include life-cycle cost factors (life of equipment, analysis period, discount rate, energy escalation rates, maintenance cost, etc., as shown in Table 1). These comparison techniques rely on the same assumptions and economic analysis theories but display the results in different forms. They also use the same definition of each term. All can be displayed as a single calculation or as a cash flow table using a series of calculations for each year of the analysis period. Savings-to-Investment Ratio. Most large military-sponsored work and many other U.S. government entities require a savings-to- investment-ratio (SIR) method. Simply put, SIR is the ratio of an option 's savings to its costs. This ratio defines the relative economic strength of each option. The higher the ratio, the better the economic strength. Ifthe ratio is less than 1, the measure does not pay for itself within the analysis period. The escalated savings on an annual and a special (nonannual) basis is calculated and discounted. Costs are shown on an annual and special basis for each year over the life of the system or option. Savings and investments are both discounted separately on an annual basis, and then the discounted total cumu- lative savings is divided by the discounted total cumulative investments (costs). The analysis period is usually the life of the system or equipment being considered. The SIR is the sum of a series of operation-related savings from a project alternative divided by the sum ofits additional investment- related costs. Typically, this is over a period of years (5, 10, or 20 years, or the typical expected life span). The general equation for the SIR simply rearranges these two terms as a ratio: N / SV 1 + d 1=0 SIRA:BC = N t It 1 + d t= 0 where (10) SIR A:BC = ratio of PV savings to additional PV investment costs of (mutually exclusive) alternative A to base case BC S, = savings in year t in operational costs attributable to alternative I, = investment-related costs in year t attributable to alternative t = year of occurrence (where 0 is base date) d = discount rate N = length of study A more practical SIR base-case equation for buildings is as follows: E+ W + OM&R SIR A:BC I。 + Repl - Res where (11) SIRA:BC = ratio of operational savings to investment-related additional costs computed for alternative A to base case BC E = (EBC - EA), savings in energy costs attributable to alternative relative to base case W = (WBC - WA), savings in water costs attributable to alternative OM&R = difference in OM&R costs; OM&RBC OM&RA I⌀ = additional initial investment cost required for alternative relative to base case; (IA - IBC) Repl = difference in capital replacement costs; (ReplA - ReplBC) Inc. ASHRAE, 2019 user. single for Licensed | {}
704b8a17-6cce-4848-a83f-9e8115a6fe70 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Owning and Operating Costs 38.13 Res = difference in residual value; (ResA - ResBC) where all amounts are in present values. this de- Example 8: SIR Computation. For example, the numerator and nominator are defined as follows: Numerator: PV of operational savings attributable to the alternative = $91 030 Denominator: PV of additional investment costs required for the alternative = $7239 Thus, $91 030 SIRA:BC = = 12.6 $7239 A ratio of 12.6 means that the energy-conserving design generates an average return of $12.6 for every $1 invested, over and above the minimum required rate of return imposed by the discount rate. The project alternative in this example is clearly cost effective. A ratio of 1.0 indicates that the cost of the investment equals its savings; a ratio of less than 1.0 indicates an uneconomic alternative that would cost more than it would save. Summary of SIR Method · An investment is cost effective ifits SIR is greater than 1.0; this is equivalent to having net savings greater than zero. · The SIR is a relative measure; it must be calculated with respect to a designated base case. · When computing the SIR of an alternative relative to its base case, the same study period and the same discount rate must be used. · The SIR is useful for evaluating a single project alternative against a base case or for ranking independent project alternatives; it is not useful for evaluating multiple mutually exclusive alternatives. Internal Rate of Return. The internal rate ofreturn (IRR) method calculates a return on investment over the defined analysis period. The annual savings and costs are not discounted, and a cash flow is established for each year of the analysis period, to be used with an ini- tial cost (or value of the loan). Annual recurring and special (nonannual) savings and costs can be used. The cash flow is then dis- counted until a calculated discount rate is found that yields a net present value of zero. This method assumes savings are reinvested at the same calculated rate of return; therefore, the calculated rates of return can be overstated compared to the actual rates of return. Another version ofthis is the modified or adjusted internal rate of return (MIRR or AIRR). In this version, reinvested savings are assumed to have a given rate of return on investment, and the financed moneys a given interest rate. The cash flow is then dis- counted until a calculated discount rate is found that yields a net present value of zero. This method gives a more realistic indication of expected return on investment, but the difference between alter- natives can be small. The most straightforward method ofcalculating the AIRR requires that the SIR for a project (relative to its base case) be calculated first. Then the AIRR can be computed easily using the following equation: AIRR = (1 + r)(SIR)1/N - 1 where r is the reinvestment rate and N is the number of years in the study period. Using the SIR of 12.6 from Equation (10) and a rein- vestment rate of 3% (the minimum acceptable rate of return [MARR]), the AIRR is found as follows: AIRR A:BC = (1 + 0.03)(12.6)1/20 - 1 = 0.1691 (12) Because an AIRR of 16.9% for the alternative is greater than the MARR, which in this example is the FEMP discount rate of3%, the project alternative is considered to be cost effective in this applica- tion. Life-Cycle Costs. This method of analysis compares the cumu- lative total of implementation, operating, and maintenance costs. The total costs are discounted over the life of the system or over the loan repayment period. The costs and investments are both dis- counted and displayed as a total combined life-cycle cost at the end of the analysis period. The options are compared to determine which has the lowest total cost over the anticipated project life. Example 9. A municipality is evaluating two different methods of provid- ing chilled water for cooling a government office building: purchasing chilled water from a central chilled-water utility service in the area, or installing a conventional chiller plant. Because the municipality is not a tax-paying entity, the evaluation does not need to consider taxes, allow- ing for either a current or constant dollar analysis. The first-year price of the chilled-water utility service contract is $65 250 per year and is expected to increase at a rate of 2.5% per year. The chiller and cooling tower would cost $220 000, with an expected life of 20 years. A major overhaul ($90 000) of the chiller is expected to occur in year ten. Annual costs for preventative mainte- nance ($1400), labor ($10 000), water ($2000) and chemical treatments ($1800) are all expected to keep pace with inflation, which is estimated to average 3% annually over the study period. The annual electric cost ($18 750) is expected to increase at a rate of 5% per year. The munici- pality uses a discount rate of 8% to evaluate financial decisions. Which option has the lowest life-cycle cost? Solution. Table 8 compares the two alternatives. For the values pro- vided, alternative 1 has a 20-year life-cycle cost (LCC) of $769 283 and alternative 2 has a 20-year life-cycle cost of $717 100. If LCC is the only basis for the decision, alternative 2 is preferable because it has the lower life-cycle cost. Computer Analysis Many computer programs are available that incorporate eco- nomic analysis methods. These range from simple macros devel- oped for popular spreadsheet applications to more comprehensive, menu-driven computer programs. Commonly used examples of the latter include Building Life-Cycle Cost (BLCC) and PC-ECON- PACK. BLCC was developed by the National Institute of Standards and Technology (NIST) for the U.S. Department of Energy (DOE). The program follows criteria established by the Federal Energy Management Program (FEMP) and the Office of Management and Budget (OMB). It is intended for evaluation of energy conserva- tion investments in nonmilitary government buildings; however, it is also appropriate for similar evaluations of commercial facilities. PC-ECONPACK, developed by the U.S. Army Corps of Engi- neers for use by the DOD, uses economic criteria established by the OMB. The program performs standardized life-cycle cost calcula- tions such as net present value, equivalent uniform annual cost, SIR, and discounted payback period. Macros developed for common spreadsheet programs gener- ally contain preprogrammed functions for various life-cycle cost calculations. Although typically not as sophisticated as the menu- driven programs, the macros are easy to install and learn. Reference Equations Table 9 lists commonly used discount formulas as addressed by NIST. Refer to NIST Handbook 135 (Fuller and Petersen 1996) for detailed discussions. 7. SYMBOLS ¦ AIRR = ¦ modified or adjusted internal rate of return (MIRR or AIRR) ¦ ¦ --- ¦ --- ¦ ¦ c = ¦ cooling system adjustment factor ¦ ¦ C = ¦ total annual building HVAC maintenance cost ¦ ¦ Ce = ¦ annual operating cost for energy ¦ ¦ Cs.assess ¦ assessed system value ¦ ¦ Cs,init = ¦ initial system cost ¦ Inc. ASHRAE, 2019 user. single for Licensed | {}
148e04e4-4665-4713-ab45-1bb5ce06b143 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 38.14 2019 ASHRAE Handbook-HVAC Applications (SI) Table 8 Two Alternative LCC Examples ¦ Alternative 1: Purchase Chilled Water from Utility ¦ Alternative 1: Purchase Chilled Water from Utility ¦ Alternative 1: Purchase Chilled Water from Utility ¦ Alternative 1: Purchase Chilled Water from Utility ¦ Alternative 1: Purchase Chilled Water from Utility ¦ Alternative 1: Purchase Chilled Water from Utility ¦ Alternative 1: Purchase Chilled Water from Utility ¦ Alternative 1: Purchase Chilled Water from Utility ¦ Alternative 1: Purchase Chilled Water from Utility ¦ Alternative 1: Purchase Chilled Water from Utility ¦ Alternative 1: Purchase Chilled Water from Utility ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ Year ¦ Year ¦ Year ¦ Year ¦ Year ¦ Year ¦ Year ¦ Year ¦ Year ¦ Year ¦ ¦ ¦ 0 ¦ 1 ¦ 2 ¦ 3 ¦ 4 5 ¦ 6 ¦ 7 ¦ 8 ¦ 9 ¦ 10 ¦ ¦ First costs Chilled-water costs Replacement ¦ ¦ $65 250 ¦ $66 881 ¦ $68 553 ¦ $70267 $72 024 ¦ $73 824 ¦ $75 670 ¦ $77 562 ¦ $79 501 ¦ $81 488 ¦ ¦ costs Maintenance costs ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Net annual cash flow ¦ ¦ 65 250 ¦ 66 881 ¦ 68 553 ¦ 70 267 ¦ 73 824 ¦ 75 670 ¦ 77 501 ¦ 79 501 ¦ 81 488 ¦ ¦ ¦ ¦ 60 417 ¦ ¦ ¦ 72 024 ¦ ¦ ¦ ¦ ¦ ¦ ¦ Present value of cash flow ¦ ¦ 11 ¦ 57 340 ¦ 54 420 ¦ 51 648 49 018 ¦ 46 522 ¦ 44 153 ¦ 41 904 ¦ 39 770 ¦ 37 745 ¦ ¦ Year ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 12 ¦ 13 14 ¦ 15 ¦ 16 ¦ 17 ¦ 18 ¦ 19 ¦ 20 ¦ ¦ Financing annual payments Chilled-water costs ¦ ¦ $83 526 $85 ¦ $87 754 ¦ $89 948 ¦ $92 197 ¦ $94 501 ¦ $96 864 ¦ $99 286 ¦ $101 768 ¦ $104 312 ¦ ¦ Replacement costs ¦ ¦ 614 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Maintenance costs ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 286 ¦ 101 ¦ ¦ ¦ Net annual cash flow Present value of cash flow ¦ ¦ 83 526 ¦ 85 614 87 ¦ 754 89 948 ¦ 92 197 ¦ 94 501 ¦ 96 864 ¦ 99 ¦ 768 ¦ 104 312 ¦ ¦ 20-year life-cycle cost ¦ $769 823 ¦ 35 823 ¦ 33 998 ¦ 32267 30 624 ¦ 29 064 ¦ 27 584 ¦ 26 179 ¦ 24 846 ¦ 23 581 ¦ 22380 ¦ ¦ Alternative 2: Install Chiller and Tower Year ¦ Alternative 2: Install Chiller and Tower Year ¦ Alternative 2: Install Chiller and Tower Year ¦ Alternative 2: Install Chiller and Tower Year ¦ Alternative 2: Install Chiller and Tower Year ¦ Alternative 2: Install Chiller and Tower Year ¦ Alternative 2: Install Chiller and Tower Year ¦ Alternative 2: Install Chiller and Tower Year ¦ Alternative 2: Install Chiller and Tower Year ¦ Alternative 2: Install Chiller and Tower Year ¦ Alternative 2: Install Chiller and Tower Year ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 0 ¦ 1 2 ¦ 3 ¦ 4 ¦ 5 ¦ 6 ¦ 7 ¦ 8 ¦ 9 ¦ 10 ¦ ¦ First costs Energy costs Replacement costs Maintenance costs ¦ $220 000 ¦ $18 750 $19 688 15 200 656 ¦ $20 672 15 16 126 ¦ $21 705 16 609 ¦ $22 791 17 108 ¦ $23 930 17 621 ¦ $25 127 18 150 ¦ $26 383 18 694 ¦ $27 702 19 255 ¦ $29 087 90 000 19 833 ¦ ¦ Net annual cash flow Present value of cash flow ¦ 220 000 220 000 ¦ 33 950 31 435 ¦ 35 344 ¦ 36 798 38315 29 211 28 163 ¦ 39 898 27 ¦ 41 551 26 184 ¦ 43 276 ¦ 45 077 354 ¦ 46 957 23 490 ¦ 138 920 64 347 ¦ ¦ ¦ ¦ ¦ 30 301 ¦ ¦ 154 ¦ ¦ 25 251 ¦ 24 ¦ ¦ ¦ ¦ Year ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 11 12 ¦ ¦ 13 ¦ 15 ¦ 16 ¦ 17 ¦ 18 ¦ 19 ¦ 20 ¦ ¦ Financing annual payments Energy costs Replacement costs ¦ ¦ $30 542 ¦ $32 069 ¦ 14 $35 356 ¦ $37 ¦ ¦ $40 929 ¦ $42 975 ¦ $45 124 ¦ $47 380 ¦ ¦ Maintenance costs Net annual cash flow ¦ ¦ 20 428 50 ¦ 21 040 ¦ $33 672 21 672 22322 55 344 ¦ 124 22 991 ¦ $38 980 23 681 ¦ 24 392 65 320 ¦ 25 123 ¦ 25 877 71 001 ¦ 26 653 74 ¦ ¦ Present value of ¦ ¦ ¦ ¦ 57 678 ¦ 60 115 ¦ 62 661 ¦ ¦ 68 099 ¦ ¦ 034 ¦ ¦ cash flow 20-year life-cycle cost ¦ ¦ 969 ¦ 53 109 ¦ 19 637 ¦ 18 951 ¦ 18 290 ¦ 17 654 ¦ 042 ¦ 16452 ¦ 15 ¦ ¦ ¦ $717 100 ¦ 21 860 ¦ 21 090 ¦ 20350 PWF(i,n)sgl ¦ future equal PWF ¦ ¦ ¦ 17 ¦ ¦ 884 ¦ ¦ Cs,salv = system salvage value at end of study period i effective interest rate for fuel Cy = uniform annualized mechanical system owning, operating, I insurance cost per period and maintenance costs ITC investment tax credit CRF = capital recovery factor j inflation rate per period CRF(i,n) = capital recovery factor for interest rate i and analysis = fuel inflation rate per period je period n k = end of period(s) during which replacement(s), repair(s), CRF(i ,n) = capital recovery factory for interest rate i for items other depreciation, or interest are calculated than fuel and analysis period n M = maintenance cost per period CRF(i ,n) = capital recovery factor for fuel interest rate i and analysis = number of periods under analysis n period n P = present value of a sum of money CRF(i m,n) = capital recovery factor for loan or mortgage rate i and m Pk = outstanding principle on loan at end of period k analysis period n PMT = payments d = distribution system adjustment factor = present worth factor Dk = depreciation during period k PWF(igk) = present worth factor for discount rate id at end of period k Dk,SL depreciation during period k from straight-line PWF(i ,k) = present worth factor for effective interest rate i at end of depreciation method period k Dk,SD = depreciation during period k from sum-of-digits depreciation method = single payment present worth factor F = future value of sum of money PWF(i,n)ser = present worth factor for a series of future equal payments h = heating system adjustment factor Rk = net replacement, repair, or disposal costs at end of period k i = compound interest rate per period SIR = savings-to-investment ratio id = discount rate per period Tine net income tax rate I = market mortgage rate T = property tax rate prop m I = effective interest rate for all but fuel T = tax rate applicable to salvage value of system salv ¦ Cs,salv = system salvage value at end of study period i effective interest rate for fuel Cy = uniform annualized mechanical system owning, operating, I insurance cost per period and maintenance costs ITC investment tax credit CRF = capital recovery factor j inflation rate per period CRF(i,n) = capital recovery factor for interest rate i and analysis = fuel inflation rate per period je period n k = end of period(s) during which replacement(s), repair(s), CRF(i ,n) = capital recovery factory for interest rate i for items other depreciation, or interest are calculated than fuel and analysis period n M = maintenance cost per period CRF(i ,n) = capital recovery factor for fuel interest rate i and analysis = number of periods under analysis n period n P = present value of a sum of money CRF(i m,n) = capital recovery factor for loan or mortgage rate i and m Pk = outstanding principle on loan at end of period k analysis period n PMT = payments d = distribution system adjustment factor = present worth factor Dk = depreciation during period k PWF(igk) = present worth factor for discount rate id at end of period k Dk,SL depreciation during period k from straight-line PWF(i ,k) = present worth factor for effective interest rate i at end of depreciation method period k Dk,SD = depreciation during period k from sum-of-digits depreciation method = single payment present worth factor F = future value of sum of money PWF(i,n)ser = present worth factor for a series of future equal payments h = heating system adjustment factor Rk = net replacement, repair, or disposal costs at end of period k i = compound interest rate per period SIR = savings-to-investment ratio id = discount rate per period Tine net income tax rate I = market mortgage rate T = property tax rate prop m I = effective interest rate for all but fuel T = tax rate applicable to salvage value of system salv ¦ Cs,salv = system salvage value at end of study period i effective interest rate for fuel Cy = uniform annualized mechanical system owning, operating, I insurance cost per period and maintenance costs ITC investment tax credit CRF = capital recovery factor j inflation rate per period CRF(i,n) = capital recovery factor for interest rate i and analysis = fuel inflation rate per period je period n k = end of period(s) during which replacement(s), repair(s), CRF(i ,n) = capital recovery factory for interest rate i for items other depreciation, or interest are calculated than fuel and analysis period n M = maintenance cost per period CRF(i ,n) = capital recovery factor for fuel interest rate i and analysis = number of periods under analysis n period n P = present value of a sum of money CRF(i m,n) = capital recovery factor for loan or mortgage rate i and m Pk = outstanding principle on loan at end of period k analysis period n PMT = payments d = distribution system adjustment factor = present worth factor Dk = depreciation during period k PWF(igk) = present worth factor for discount rate id at end of period k Dk,SL depreciation during period k from straight-line PWF(i ,k) = present worth factor for effective interest rate i at end of depreciation method period k Dk,SD = depreciation during period k from sum-of-digits depreciation method = single payment present worth factor F = future value of sum of money PWF(i,n)ser = present worth factor for a series of future equal payments h = heating system adjustment factor Rk = net replacement, repair, or disposal costs at end of period k i = compound interest rate per period SIR = savings-to-investment ratio id = discount rate per period Tine net income tax rate I = market mortgage rate T = property tax rate prop m I = effective interest rate for all but fuel T = tax rate applicable to salvage value of system salv ¦ Cs,salv = system salvage value at end of study period i effective interest rate for fuel Cy = uniform annualized mechanical system owning, operating, I insurance cost per period and maintenance costs ITC investment tax credit CRF = capital recovery factor j inflation rate per period CRF(i,n) = capital recovery factor for interest rate i and analysis = fuel inflation rate per period je period n k = end of period(s) during which replacement(s), repair(s), CRF(i ,n) = capital recovery factory for interest rate i for items other depreciation, or interest are calculated than fuel and analysis period n M = maintenance cost per period CRF(i ,n) = capital recovery factor for fuel interest rate i and analysis = number of periods under analysis n period n P = present value of a sum of money CRF(i m,n) = capital recovery factor for loan or mortgage rate i and m Pk = outstanding principle on loan at end of period k analysis period n PMT = payments d = distribution system adjustment factor = present worth factor Dk = depreciation during period k PWF(igk) = present worth factor for discount rate id at end of period k Dk,SL depreciation during period k from straight-line PWF(i ,k) = present worth factor for effective interest rate i at end of depreciation method period k Dk,SD = depreciation during period k from sum-of-digits depreciation method = single payment present worth factor F = future value of sum of money PWF(i,n)ser = present worth factor for a series of future equal payments h = heating system adjustment factor Rk = net replacement, repair, or disposal costs at end of period k i = compound interest rate per period SIR = savings-to-investment ratio id = discount rate per period Tine net income tax rate I = market mortgage rate T = property tax rate prop m I = effective interest rate for all but fuel T = tax rate applicable to salvage value of system salv ¦ Cs,salv = system salvage value at end of study period i effective interest rate for fuel Cy = uniform annualized mechanical system owning, operating, I insurance cost per period and maintenance costs ITC investment tax credit CRF = capital recovery factor j inflation rate per period CRF(i,n) = capital recovery factor for interest rate i and analysis = fuel inflation rate per period je period n k = end of period(s) during which replacement(s), repair(s), CRF(i ,n) = capital recovery factory for interest rate i for items other depreciation, or interest are calculated than fuel and analysis period n M = maintenance cost per period CRF(i ,n) = capital recovery factor for fuel interest rate i and analysis = number of periods under analysis n period n P = present value of a sum of money CRF(i m,n) = capital recovery factor for loan or mortgage rate i and m Pk = outstanding principle on loan at end of period k analysis period n PMT = payments d = distribution system adjustment factor = present worth factor Dk = depreciation during period k PWF(igk) = present worth factor for discount rate id at end of period k Dk,SL depreciation during period k from straight-line PWF(i ,k) = present worth factor for effective interest rate i at end of depreciation method period k Dk,SD = depreciation during period k from sum-of-digits depreciation method = single payment present worth factor F = future value of sum of money PWF(i,n)ser = present worth factor for a series of future equal payments h = heating system adjustment factor Rk = net replacement, repair, or disposal costs at end of period k i = compound interest rate per period SIR = savings-to-investment ratio id = discount rate per period Tine net income tax rate I = market mortgage rate T = property tax rate prop m I = effective interest rate for all but fuel T = tax rate applicable to salvage value of system salv ¦ Cs,salv = system salvage value at end of study period i effective interest rate for fuel Cy = uniform annualized mechanical system owning, operating, I insurance cost per period and maintenance costs ITC investment tax credit CRF = capital recovery factor j inflation rate per period CRF(i,n) = capital recovery factor for interest rate i and analysis = fuel inflation rate per period je period n k = end of period(s) during which replacement(s), repair(s), CRF(i ,n) = capital recovery factory for interest rate i for items other depreciation, or interest are calculated than fuel and analysis period n M = maintenance cost per period CRF(i ,n) = capital recovery factor for fuel interest rate i and analysis = number of periods under analysis n period n P = present value of a sum of money CRF(i m,n) = capital recovery factor for loan or mortgage rate i and m Pk = outstanding principle on loan at end of period k analysis period n PMT = payments d = distribution system adjustment factor = present worth factor Dk = depreciation during period k PWF(igk) = present worth factor for discount rate id at end of period k Dk,SL depreciation during period k from straight-line PWF(i ,k) = present worth factor for effective interest rate i at end of depreciation method period k Dk,SD = depreciation during period k from sum-of-digits depreciation method = single payment present worth factor F = future value of sum of money PWF(i,n)ser = present worth factor for a series of future equal payments h = heating system adjustment factor Rk = net replacement, repair, or disposal costs at end of period k i = compound interest rate per period SIR = savings-to-investment ratio id = discount rate per period Tine net income tax rate I = market mortgage rate T = property tax rate prop m I = effective interest rate for all but fuel T = tax rate applicable to salvage value of system salv ¦ Cs,salv = system salvage value at end of study period i effective interest rate for fuel Cy = uniform annualized mechanical system owning, operating, I insurance cost per period and maintenance costs ITC investment tax credit CRF = capital recovery factor j inflation rate per period CRF(i,n) = capital recovery factor for interest rate i and analysis = fuel inflation rate per period je period n k = end of period(s) during which replacement(s), repair(s), CRF(i ,n) = capital recovery factory for interest rate i for items other depreciation, or interest are calculated than fuel and analysis period n M = maintenance cost per period CRF(i ,n) = capital recovery factor for fuel interest rate i and analysis = number of periods under analysis n period n P = present value of a sum of money CRF(i m,n) = capital recovery factor for loan or mortgage rate i and m Pk = outstanding principle on loan at end of period k analysis period n PMT = payments d = distribution system adjustment factor = present worth factor Dk = depreciation during period k PWF(igk) = present worth factor for discount rate id at end of period k Dk,SL depreciation during period k from straight-line PWF(i ,k) = present worth factor for effective interest rate i at end of depreciation method period k Dk,SD = depreciation during period k from sum-of-digits depreciation method = single payment present worth factor F = future value of sum of money PWF(i,n)ser = present worth factor for a series of future equal payments h = heating system adjustment factor Rk = net replacement, repair, or disposal costs at end of period k i = compound interest rate per period SIR = savings-to-investment ratio id = discount rate per period Tine net income tax rate I = market mortgage rate T = property tax rate prop m I = effective interest rate for all but fuel T = tax rate applicable to salvage value of system salv ¦ Cs,salv = system salvage value at end of study period i effective interest rate for fuel Cy = uniform annualized mechanical system owning, operating, I insurance cost per period and maintenance costs ITC investment tax credit CRF = capital recovery factor j inflation rate per period CRF(i,n) = capital recovery factor for interest rate i and analysis = fuel inflation rate per period je period n k = end of period(s) during which replacement(s), repair(s), CRF(i ,n) = capital recovery factory for interest rate i for items other depreciation, or interest are calculated than fuel and analysis period n M = maintenance cost per period CRF(i ,n) = capital recovery factor for fuel interest rate i and analysis = number of periods under analysis n period n P = present value of a sum of money CRF(i m,n) = capital recovery factor for loan or mortgage rate i and m Pk = outstanding principle on loan at end of period k analysis period n PMT = payments d = distribution system adjustment factor = present worth factor Dk = depreciation during period k PWF(igk) = present worth factor for discount rate id at end of period k Dk,SL depreciation during period k from straight-line PWF(i ,k) = present worth factor for effective interest rate i at end of depreciation method period k Dk,SD = depreciation during period k from sum-of-digits depreciation method = single payment present worth factor F = future value of sum of money PWF(i,n)ser = present worth factor for a series of future equal payments h = heating system adjustment factor Rk = net replacement, repair, or disposal costs at end of period k i = compound interest rate per period SIR = savings-to-investment ratio id = discount rate per period Tine net income tax rate I = market mortgage rate T = property tax rate prop m I = effective interest rate for all but fuel T = tax rate applicable to salvage value of system salv ¦ Cs,salv = system salvage value at end of study period i effective interest rate for fuel Cy = uniform annualized mechanical system owning, operating, I insurance cost per period and maintenance costs ITC investment tax credit CRF = capital recovery factor j inflation rate per period CRF(i,n) = capital recovery factor for interest rate i and analysis = fuel inflation rate per period je period n k = end of period(s) during which replacement(s), repair(s), CRF(i ,n) = capital recovery factory for interest rate i for items other depreciation, or interest are calculated than fuel and analysis period n M = maintenance cost per period CRF(i ,n) = capital recovery factor for fuel interest rate i and analysis = number of periods under analysis n period n P = present value of a sum of money CRF(i m,n) = capital recovery factor for loan or mortgage rate i and m Pk = outstanding principle on loan at end of period k analysis period n PMT = payments d = distribution system adjustment factor = present worth factor Dk = depreciation during period k PWF(igk) = present worth factor for discount rate id at end of period k Dk,SL depreciation during period k from straight-line PWF(i ,k) = present worth factor for effective interest rate i at end of depreciation method period k Dk,SD = depreciation during period k from sum-of-digits depreciation method = single payment present worth factor F = future value of sum of money PWF(i,n)ser = present worth factor for a series of future equal payments h = heating system adjustment factor Rk = net replacement, repair, or disposal costs at end of period k i = compound interest rate per period SIR = savings-to-investment ratio id = discount rate per period Tine net income tax rate I = market mortgage rate T = property tax rate prop m I = effective interest rate for all but fuel T = tax rate applicable to salvage value of system salv ¦ Cs,salv = system salvage value at end of study period i effective interest rate for fuel Cy = uniform annualized mechanical system owning, operating, I insurance cost per period and maintenance costs ITC investment tax credit CRF = capital recovery factor j inflation rate per period CRF(i,n) = capital recovery factor for interest rate i and analysis = fuel inflation rate per period je period n k = end of period(s) during which replacement(s), repair(s), CRF(i ,n) = capital recovery factory for interest rate i for items other depreciation, or interest are calculated than fuel and analysis period n M = maintenance cost per period CRF(i ,n) = capital recovery factor for fuel interest rate i and analysis = number of periods under analysis n period n P = present value of a sum of money CRF(i m,n) = capital recovery factor for loan or mortgage rate i and m Pk = outstanding principle on loan at end of period k analysis period n PMT = payments d = distribution system adjustment factor = present worth factor Dk = depreciation during period k PWF(igk) = present worth factor for discount rate id at end of period k Dk,SL depreciation during period k from straight-line PWF(i ,k) = present worth factor for effective interest rate i at end of depreciation method period k Dk,SD = depreciation during period k from sum-of-digits depreciation method = single payment present worth factor F = future value of sum of money PWF(i,n)ser = present worth factor for a series of future equal payments h = heating system adjustment factor Rk = net replacement, repair, or disposal costs at end of period k i = compound interest rate per period SIR = savings-to-investment ratio id = discount rate per period Tine net income tax rate I = market mortgage rate T = property tax rate prop m I = effective interest rate for all but fuel T = tax rate applicable to salvage value of system salv ¦ Cs,salv = system salvage value at end of study period i effective interest rate for fuel Cy = uniform annualized mechanical system owning, operating, I insurance cost per period and maintenance costs ITC investment tax credit CRF = capital recovery factor j inflation rate per period CRF(i,n) = capital recovery factor for interest rate i and analysis = fuel inflation rate per period je period n k = end of period(s) during which replacement(s), repair(s), CRF(i ,n) = capital recovery factory for interest rate i for items other depreciation, or interest are calculated than fuel and analysis period n M = maintenance cost per period CRF(i ,n) = capital recovery factor for fuel interest rate i and analysis = number of periods under analysis n period n P = present value of a sum of money CRF(i m,n) = capital recovery factor for loan or mortgage rate i and m Pk = outstanding principle on loan at end of period k analysis period n PMT = payments d = distribution system adjustment factor = present worth factor Dk = depreciation during period k PWF(igk) = present worth factor for discount rate id at end of period k Dk,SL depreciation during period k from straight-line PWF(i ,k) = present worth factor for effective interest rate i at end of depreciation method period k Dk,SD = depreciation during period k from sum-of-digits depreciation method = single payment present worth factor F = future value of sum of money PWF(i,n)ser = present worth factor for a series of future equal payments h = heating system adjustment factor Rk = net replacement, repair, or disposal costs at end of period k i = compound interest rate per period SIR = savings-to-investment ratio id = discount rate per period Tine net income tax rate I = market mortgage rate T = property tax rate prop m I = effective interest rate for all but fuel T = tax rate applicable to salvage value of system salv ¦ Inc. ASHRAE, 2019 user. single for Licensed | {}
743a38c4-20e8-4778-b4b0-9fc09d63d710 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Owning and Operating Costs 38.15 Table 9 Commonly Used Discount Formulas ¦ Name ¦ Algebraic Forma,b ¦ Name ¦ Algebraic Forma,b ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Single compound-amount (SCA) equation Single present-value (SPV) equation Uniform sinking-fund (USF) equation Uniform capital recovery (UCR) equation ¦ 月 F = P 1 + d 1 P = F " 1 + d d A = F N 1 + d 1 " d 1 + d A = P 1 + d 1 N ¦ compound-amount Uniform (UCA) equation Uniform present-value (UPV) equation Modified uniform present-value (UPV*) equation ¦ N = A 1 + d 1 F d N 1 + d 1 P = A 1 + d n d " 1 + e 1 + e d e 1 + d P = A0 1 - ¦ where A = end-of-period payment (or receipt) in a uniform series of payments (or receipts) over n periods at d interest or discount rate A0 = initial value of a periodic payment (receipt) evaluated at beginning of study period Source: NIST Handbook 135 (Fuller and Petersen 1996). aNote that the USF, UCR, UCA, and UPV equations yield undefined answers when d = 0. The correct algebraic forms for this special case would be as follows: USF formula, A = F/N; UCR formula, A = P/N; UCA formula, F = An. The UPV* equation also yields an undefined answer when e = d. In this case, P = Aon. REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. Abramson, B., D. Herman, and L. Wong. 2005. Interactive web-based own- ing and operating cost database (TRP-1237). ASHRAE Research Proj- ect, Final Report. Akalin, M.T. 1978. Equipment life and maintenance cost survey (RP-186). ASHRAE Transactions 84(2):94-106. BOMA. 2003. Preventive maintenance and building operation efficiency. Building Owners and Managers Association, Washington, D.C. DOE. 2007. The international performances measurement and verification protocol (IPMVP). Publication No. DOE/EE-0157. U.S. Department of Energy. DOE. 2013. Commercial property-assessed clean energy (PACE) financing. Ch. 12 in U.S. Department of Energy Clean Energy Finance Guide, 3rd ed. U.S. Department of Energy, Washington, D.C. www.energy .gov subsa/pooffies20406/Wichl2_commenticii_pox__pdf Dohrmann, D.R., and T. Alereza. 1986. Analysis of survey data on HVAC maintenance costs (RP-382). ASHRAE Transactions 92(2A):550-565. Fuller, S.K., and S.R. Petersen. 1996. Life-cycle costing manual for the fed- eral energy management program, 1995 edition. NIST Handbook 135. National Institute of Standards and Technology, Gaithersburg, MD. www.mts.gomp.hillicalite-sp-ce-communneifAcom/ -managemeni-prograngran-mischandbook-1995. Hiller, C.C. 2000. Determining equipment service life. ASHRAE Journal 42(8):48-54. Kreider, J., and F. Kreith. 1982. Solar heating and cooling: Active and pas- sive design. McGraw-Hill, New York. Lovvorn, N.C., and C.C. Hiller. 2002. Heat pump life revisited. ASHRAE Transactions 108(2): 107-112. NIST. Building life-cycle cost computer program (BLCC 5.3-13). A vailable from the U.S. Department of Energy Efficiency and Renewable Energy Federal Energy Management Program, Washington, D.C. energy .gov /eere/femp.huilding-lift-cycle-cost-programa. OMB. 1992. Guidelines and discount rates for benefit-cost analysis of fed- eral programs. Circular A-94. Office of Management and Budget, Wash- ington, D.C. www.whitehouse.gov/omb/circulars/. OSHA. [Annual.] Permit-required confined spaces. Code ofFederal Regu- lations 29 CFR 1910.146. www.ecfr.gov. Rushing, A.S., Kneifel, J.D., and B.C. Lippiatt. 2013. Energy price indices and discount factors for life-cycle cost analysis-2010. Annual Supple- ment to NIST Handbook 135 and NBS Special Publication 709. NISTIR 85-3273-25. National Institute of Standards and Technology, Gaithers- burg, MD. www.leene.energy.gov/femp/pdfs/askibbi3.pdf) At = A0(1 + e)', where t = 1, · · · , n d interest or discount rate e price escalation rate per period bThe terms by which known values are multiplied are formulas for the factors found in discount factor tables. Using acronyms to represent the factor formulas, the discount- ing equations can also be written as F = P SCA, P = F SPV, A = F USF, A = P UCR, F = UCA, P = A UPV, and P = A0 UPV*. BIBLIOGRAPHY ASHRAE. 1999. HVAC maintenance costs (RP-929). ASHRAE Research Project, Final Report. ASTM. 2004. Standard terminology ofbuilding economics. Standard E833- 04. American Society for Testing and Materials, International, West Conshohocken, PA. DOE. (No date) NEPA documents. energy .gov/nepa/nepa-documents. U.S. Department of Energy, Washington, D.C. DOE. 2009. National Environmental Policy Act guide for state energy pro- gram and energy efficiency and conservation block grant projects. State Energy Program Notice 10-001 and Energy Efficiency and Conservation Block Grant Program Notice 10-003. www 1 .eere.energy gov/wip/pdfs /nepa_program_guidance_notice_ 10-003.pdf. Easton Consultants. 1986. Survey of residential heat pump service life and maintenance issues. AGA S-77126. American Gas Association, Arling- ton, VA. EECBG. 2010. Guidance for Energy Efficiency and Conservation Block Grant grantees on financing programs. Program Notice 09-002B. www.l.eere.energy.gov/wip/pdfs/eechg financing_ guidance2010_08 10.pdf. Energy Efficiency and Conservation Block Grant Program, U.S. Department of Energy, Washington, D.C. EECBG. 2010. Guidance on implementation of the Davis-Bacon Act pre- vailing wage requirement for energy efficiency and conservation block grant recipients under the American Recovery and Reinvestment Act of 2009. Program Notice 10-004A. www1.eere.energy .gov/wip/pdfs/eecbg _program_guidance_dba_ 121709 10-004_revised_april_2010.pdf. Energy Efficiency and Conservation Block Grant Program, U.S. Depart- ment of Energy, Washington, D.C. Haberl, J. 1993. Economic calculations for ASHRAE Handbook. ESL-TR- 93/04-07. Energy Systems Laboratory (esl.tamu.edu), Texas A&M University, College Station. hdl.handle.net/1969.1/2113. Kurtz, M. 1984. Handbook of engineering economics: Guide for engineers, technicians, scientists, and managers. McGraw-Hill, New York. Lovvorn, N.C., and C.C. Hiller. 1985. A study of heat pump service life. ASHRAE Transactions 91(2B):573-588. PACENation. 2017. PACEfor commercial building owners. pacenation.us/ commercial-pace/. Quirin, D.G. 1967. The capital expenditure decision. Richard D. Win, Inc., Homewood, IL. U.S. Department of Commerce, Bureau of Economic Analysis. (Monthly) Survey of current business. U.S. Department of Commerce Bureau of Economic Analysis, Washington, D.C. www.bea.gov/scb/. USA-CERL. 1998. Life cycle cost in design computer program (WinLCCID 98). Available from Building Systems Laboratory, University ofIllinois, Urbana-Champaign. U.S. Department ofLabor. 2005. Annual percent changesfrom 1913 to pres- ent. Bureau of Labor Statistics. www.bls.gov/cpi. USACE. (No date) PC-ECONPACK computer program (ECONPACK 4.0.2). U.S. Army Corps of Engineers, Huntsville, AL. www.wbdg.org /tools/econpack.php. Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
773c4a8e-13b6-474d-8c60-a95e34ddf5d0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 39 TESTING, ADJUSTING, AND BALANCING ¦ Terminology ¦ 39.1 ¦ Balancing Cooling Towers ¦ 39.29 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ General Criteria ¦ 39.1 ¦ Verification of Controls Operation ¦ 39.29 ¦ ¦ Air Volumetric Measurement Methods ¦ 39.2 ¦ Thermal Performance Verification ¦ 39.30 ¦ ¦ Instruments ¦ 39.3 ¦ Outdoor Air Ventilation Verification ¦ 39.30 ¦ ¦ Air Testing, Adjusting, and Balancing Balancing Hydronic Systems ¦ 39.10 39.14 ¦ Temperature Control Verification ¦ 39.30 ¦ ¦ Hydronic Balancing Methods ¦ 39.22 ¦ Testing for Sound and Vibration ¦ ·· 39.31 ¦ ¦ Fluid Flow Measurement ¦ 39.25 ¦ Field Survey for Energy Audit. ¦ 39.37 ¦ ¦ Balancing Steam Distribution Systems ¦ 39.28 ¦ TAB Reports ¦ 39.39 ¦ S YSTEMS that control the environment in a building change with time and use, and must be rebalanced accordingly. The designer must consider initial and supplementary testing and balancing requirements for commissioning. Complete and accurate operating and maintenance instructions that include intent of design and how to test, adjust, and balance the building systems are essen- tial. Building operating personnel must be well trained, or qualified operating service organizations must be hired to ensure optimum comfort, proper process operations, and economical operation. This chapter does not suggest which groups or individuals should perform a complete testing, adjusting, and balancing procedure. How- ever, the procedure must produce repeatable results that meet the design intent and the owner' s requirements. Overall, one source must be responsible for testing, adjusting, and balancing all systems. As part of this responsibility, the testing organization should check all equipment under field conditions to ensure compliance. Testing and balancing should be repeated as systems are reno- vated and changed. Testing boilers and other pressure vessels for compliance with safety codes is not the primary function of the test- ing and balancing firm; rather, it is to verify and adjust operating conditions in relation to design conditions for flow, temperature, pressure drop, noise, and vibration. ASHRAE Standard 111 details procedures not covered in this chapter. 1. TERMINOLOGY Testing, adjusting, and balancing (TAB) is the process of check- ing and adjusting all environmental systems in a building to produce and meet the design objectives. This process includes (1) balancing air and water distribution systems, (2) adjusting the total system to provide design quantities, (3) electrical measurement, (4) establish- ing quantitative performance of all equipment, (5) verifying auto- matic control system operation and sequences of operation, and ⑥ sound and vibration measurement. These procedures are accom- plished by checking installations for conformity to design, measur- ing the quantities of fluid that need to flow in the system to meet design specifications, and recording and reporting the results. The following definitions are used in this chapter. Refer to ASHRAE Terminology (www.ashrae.org/ashraeterms) for addi- tional definitions. Test. Determine quantitative performance of equipment. Adjust. Regulate the specified fluid flow rate and air patterns at terminal equipment (e.g., reduce fan speed, adjust a damper). Balance. Proportion flows in the distribution system (submains, branches, and terminals) according to specified design quantities. The preparation of this chapter is assigned to TC 7.7, Testing and Balancing. Balanced System. A system designed to deliver heat transfer required for occupant comfort or process load at design conditions. A minimum heat transfer of 97% should be provided to the space or load served at design flow. The flow required for minimum heat transfer establishes the system 's flow tolerance. The fluid distribu- tion system should be designed to allow flow to maintain the required tolerance and verify its performance. Bump test. A test consisting of bumping the part and measuring its response. The part will vibrate at its natural frequency, which shows up as a response peak on the analyzer. Usually the bump test is accom- plished by placing an accelerometer on the device under test (DUT) and tapping or bumping the DUT with a rubber hammer. Procedure. An approach to and execution of a sequence of work operations to yield repeatable or predictable results. Report forms. Test data sheets arranged in logical order for sub- mission and review. They should also form the permanent record to be used as the basis for future TAB work and/or system maintenance. Terminal. A point where the controlled medium (fluid or energy) enters or leaves the distribution system. In air systems, these may be variable- or constant-volume boxes, registers, grilles, diffusers, lou- vers, and hoods. In water systems, these may be heat transfer coils, fan-coil units, convectors, or finned-tube radiation or radiant panels. 2. GENERAL CRITERIA Effective and efficient TAB requires a systematic, thoroughly planned procedure implemented by experienced and qualified staff. All activities, including organization, calibration of instruments, and execution of the work, should be scheduled. Air-side work must be coordinated with water-side and control work. Preparation includes planning and scheduling all procedures, collecting necessary data (including all change orders), reviewing data, studying the system to be worked on, preparing forms, and making preliminary field in- spections. Air leakage in a duct system can significantly reduce perfor- mance, so ducts must be designed, constructed, and installed to min- imize and control leakage. During construction, all duct systems should be sealed and tested for air leakage. Water, steam, and pneumatic piping should be tested for leakage, which can harm people and equipment. Design Considerations TAB planning begins with design functions, because most of the devices required for adjustments are integral parts of the design and installation. To ensure that proper balance can be achieved, the engi- neer should show and specify a sufficient number of dampers, valves, flow measuring locations, and flow-balancing devices; these should be properly located in required straight lengths of pipe or duct whenever possible for accurate measurement. Testing depends on 39.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
4319f4cc-354b-4c03-baee-0429c2701b0c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 39.2 2019 ASHRAE Handbook- -HVAC Applications (SI) system characteristics and layout. Interaction between individual terminals varies with pressures, flow requirements, and control devices. The design engineer should specify balancing tolerances. Minimum flow tolerances are ±10% for individual terminals and branches in noncritical applications and ±5% for main air ducts. For critical water systems where differential pressures must be main- tained, tolerances of ±5% are suggested. For critical air systems, recommendations are the following: ¦ Positive zones: ¦ Positive zones: ¦ Positive zones: ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Supply air ¦ 0 to +10% ¦ 0 to +10% ¦ ¦ Exhaust and return air ¦ 0 to ¦ 10% ¦ ¦ Negative zones: ¦ Negative zones: ¦ Negative zones: ¦ ¦ Supply air ¦ 0 to ¦ 10% ¦ ¦ Exhaust and return air ¦ 0 to +10% ¦ 0 to +10% ¦ Balancing Devices. Balancing devices should be used to provide maximum flow-limiting ability without causing excessive noise. Flow reduction should be uniform over the entire duct or pipe. Single-blade dampers or butterfly balancing valves are not accept- able for use as balancing devices because of the uneven flow pattern at high pressure drops. Pressure drop across equipment is not an accurate flow measurement but can be used to determine whether the manufacturer design pressure is within specified limits. Liberal use of pressure taps at critical points is recommended. Stratification Normal design minimizes conditions causing air turbulence, to produce the least friction, resistance, and consequent pressure loss. Under some conditions, however, air turbulence is desirable and necessary. For example, two airstreams of different temperatures can stratify in smooth, uninterrupted flow conditions. In this situa- tion, design should promote mixing. Return and outdoor airstreams at the inlet side of the air-handling unit tend to stratify where enlargement of the inlet plenum or casing size decreases air veloc- ity. Without a deliberate effort to mix the two airstreams (e.g., in cold climates, placing the outdoor air entry at the top of the plenum and return air at the bottom of the plenum to allow natural mixing), stratification can be carried throughout the system (e.g., filter, coils, eliminators, fans, ducts). Stratification can freeze coils and rupture tubes, and can affect temperature control in plenums, spaces, or both. Inc. ASHRAE, 2019 user. single for Licensed Stratification can also be reduced by adding vanes to break up and mix the airstreams. No solution to stratification problems is guaranteed; each condition must be evaluated by field measure- ments and experimentation. 3. AIR VOLUMETRIC MEASUREMENT METHODS The pitot tube traverse is the generally accepted method of mea- suring airflow in ducts. The primary objective for other ways to measure airflow at individual terminals is to establish repeatable measurement procedures that correlate with the pitot tube traverse. Laboratory tests, data, and techniques prescribed by equipment and air terminal manufacturers must be reviewed and checked for accuracy, applicability, and repeatability ofresults. Conversion fac- tors that correlate field data with laboratory results must be devel- oped to predict the equipment': s actual field performance. Air Devices Airflow-measuring instruments should be field verified by com- paring to pitot tube traverses to establish correction and/or density factors. Check correction factors given by air diffuser manufacturers by field measurement and comparing them to actual flow measured by pitot tube traverse. A capture hood is frequently used to measure device airflows. Correction factors should be established by field measurement and comparison to actual flow measured by pitot tube traverse for hood measurements with varying flow and deflection settings. Rotating vane anemometers are commonly used to measure air- flow from sidewall grilles. Effective areas (correction factors) should be established with the face dampers fully open and deflec- tion set uniformly on all grilles. Correction factors are required when measuring airflow in open ducts (i.e., damper openings and fume hoods [Sauer and Howell 1990]). Duct Flow The preferred method of measuring duct volumetric flow is the pitot tube traverse average as detailed in ASHRAE Standard 1 11. When using airflow measuring stations, these airflow measure- ments should be checked against a pitot tube traverse. Power input to a fan 's driver should be used as only a guide to indicate its delivery; it may also be used to verify performance determined by a reliable method (e.g., pitot tube traverse of system 's main) that considers possible system effects. For some fans, the flow rate is not proportional to the power needed to drive them. In some cases, as with forward-curved-blade fans, the same power is required for two or more flow rates. The backward-curved-blade centrifugal fan is the only type with a flow rate that varies directly with power input. If an installation has an inadequate straight length of ductwork or no ductwork to allow a pitot tube traverse, follow Sauer and How- ell's (1990) procedure: use a vane anemometer to read air velocities at multiple points across the face of a coil to determine loss coeffi- cient. 3.1 MIXTURE PLENUMS Approach conditions are often so unfavorable that the air quan- tities comprising a mixture (e.g., outdoor and return air) cannot be determined accurately by volumetric measurements. In such cases, the mixture's temperature indicates the balance (proportions) between the component airstreams. Temperatures must be mea- sured carefully to account for stratification, and the difference between outdoor and return temperatures must be greater than 10 K. The temperature of the mixture can be calculated as follows: Qttm = Qoto + Qrtr where 외 = total measured air quantity, % Q。 = outdoor air quantity, % Qr = return air quantity, % tm = temperature of outdoor and return mixture, °C to = outdoor temperature, °C ty = return temperature, °C Pressure Measurement Measured air pressures include barometric, static, velocity, total, and differential. For field evaluation of air-handling performance, pressure should be measured per ASHRAE Standard 11 1 and ana- lyzed together with manufacturers' fan curves and system effect as predicted by AMCA Standard 210. When measured in the field, pressure readings, air quantity, and power input often do not cor- relate with manufacturers' certified performance curves and proper correction is necessary. Pressure drops through equipment such as coils, dampers, or fil- ters should not be used to measure airflow. Pressure is an acceptable means of establishing flow volumes only where itis required by, and performed in accordance with, the manufacturer certifying the equipment. | {}
aa726527-7488-41b5-82cb-ebb48e86e38b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Testing, Adjusting, and Balancing 39.3 4. INSTRUMENTS No one established procedure applies to all systems. The bibli- ography lists sources of additional information. Air Testing and Balancing Inclined Manometer. The inclined manometer is made of a single tube, inclined (usually 10:1 slope), to enlarge the reading. Alcohol or special oils are normally used in place of water. Such oils have a lower specific gravity than water which serves to further enlarge the reading. Manometers using these fluids have scales cal- ibrated in pascals corresponding to the pressure indicated on the oil of a known specific gravity. Recommended for use with pitot tubes or static pressure probes. The combination vertical-inclined manometer is constructed of an inclined fluid column with a scale of 0 to 250 or 500 Pa con- nected to a vertical fluid column with scales of 1250 or 2500 Pa. Recommended for use with pitot tubes or static pressure probes. Limitations: · Not to be used to measure air velocities less than 3 m/s. A micro- manometer, hook gage, or another sensitive instrument should be used to decrease the uncertainty of measurements between 2.3 and 3 m/s. · The manometer must be carefully leveled during use and held in a rigid position so that when zero pressure is registered, the end of the meniscus arc of the fluid exactly bisects the center of the zero line. · Calibration is required. The manometer must be verified by com- parison to a recently calibrated reference instrument. If the reading on the instrument to be verified is not within 2% of the reading on the reference instrument, then the manometer must be calibrated by an ISO-certified air speed laboratory before it can be used. Pitot Tube. A pitot tube, used in conjunction with a manometer, provides a basic method of determining the air velocity within a duct. The typical pitot tube is of a double concentric tube construc- tion, consisting of an 3.2 mm OD inner tube concentrically located inside a 7.9 mm OD outer tube that measures total pressure. The outer static tube has eight equally spaced 1.02 mm diameter holes around the circumference of the outer tube, located 63.5 mm back from the nose or open end ofthe pitot tube tip. At the base (tube con- nection) end, the inner tube is open ended, as is the head. The outer tube has a side outlet tube connector perpendicular to the outer tube, directly parallel with and in the same direction as the head end ofthe pitot static tube. Recommended for measuring an airstream's · Total pressure, by connecting the inner tube outlet connector to one side of a manometer or draft gage · Static pressure, by connecting the outer tube side outlet connector to one side of a manometer or draft gage · Velocity pressure, by connecting both the inner and outer tube connectors to opposite sides of a manometer or draft gage. When used with a manometer or micromanometer, the pitot tube is very reliable and rugged. Its use as a direct measurement tool is preferred over many other methods for the field measurement of air velocity, system total air, outdoor air, return air quantities, fan static pressure, fan total pressure, and fan outlet velocity pressures where such measured quantities may be required and within the range or capabilities of the instrument. Instruments that may be used with the pitot static tube include the following: · Micromanometer: very low pressure differential, less than 250 Pa · Inclined manometer: moderate pressure differential, 0 to 2500 Pa · U-tube manometer: medium pressure differential, greater than 2500 Pa · Diaphragm-type pressure gage · Electronic differential pressure meters Limitations: · Pitot tubes should not be used to measure velocities below 2.3 m/ S, regardless of the electronic sensors used to identify differentials in pressure, because of the inherent high uncertainties in pitot measurement. · Accuracy depends on uniformity of flow and completeness of tra- verse. · A reasonably large space is required adjacent to duct penetrations for maneuvering the instrument. · Care is needed to avoid pinching or puncturing instrument tubing. · Because of the distance between the impact and static holes, the pitot static tube cannot be used to measure flow through orifice- type openings. · Pitot static tubes are susceptible to plugging in airstreams with heavy dust or moisture loadings. · Acceptance of the standard pitot static tube rests in its accuracy on the correct determination of the static pressure. The total pressure is not affected by yaw or angularity up to approximately 8° on ei- ther side ofparallel flow. The static pressure, however, is extreme- ly sensitive to direction of flow. Accuracy offield measurement. Rigorous error analysis shows that flow rate determinations by the pitot static tube and manometer combination method can range from 5 to 10% error. Experience shows that qualified technicians can obtain measurements within 5 and 10% accuracy of actual flow under good field conditions. It has also been determined that suitable traverse conditions do not always exist, and measurements can then exceed a ±10% error rate. Chronometric Tachometer. The chronometric tachometer is a hand-held instrument that combines an accurate timer and a revolu- tion counter. After the instrument tip is placed on the rotating shaft, pushing the stopwatch button simultaneously activates the counter and the stopwatch. After the timer has run for either 3 or 6 s, the in- strument stops counting revolutions even though it is still in contact with the rotating shaft. The scale is calibrated to give readings direct- ly in rpm. Instrument accuracy is within ±0.5% offull scale. Hand ta- chometers (e.g., dial face [Eddy current], solid-state with digital readout) can produce instantaneous rpm measurement readings, with accuracy within ±1% of full scale. Tachometers are recommended for determining the speed of any shaft having a countersunk end. Limitations: · The shaft end must be accessible and countersunk. · Calibration is required. Readings must be verified with a recently calibrated chronometric tachometer on each project. If the reading is not within ±2% of the recently calibrated tachometer, have the instrument recalibrated by a qualified testing lab. Accuracy offield measurements. Accuracy is within one-half of a scale division mark. Clamp-on Volt-Ammeter. This instrument has trigger-operated, clamp-on transformer jaws that allow current readings without interrupting electrical service. Most volt-ammeters have several scale ranges, in amperes and volts. Two voltage test leads are fur- nished that may be quick-connected to the bottom of the volt- ammeter opposite the end used for measuring current. Some models have a built-in ohmmeter. Instrument accuracy is within ±3% offull scale. Recommended for measuring operating voltages and currents of electric motors and of electric resistance heating coils. Limitations: · The proper range must be selected. It is desirable for readings to occur about mid-scale. When in doubt, begin with the highest range for both voltage and current scales. Accuracy of reading Inc. ASHRAE, 2019 user. single for Licensed | {}
b63a559b-33ef-48ca-943a-8be9f0272402 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 39.4 low currents can be improved by looping the conductor wire around the jaw once and dividing the current reading by 2. · Depending on conditions at the point of measurement and the size of the volt-ammeter, access for measurement may be restrictive. Caution is required, particularly when taking measurements under confined conditions. · To avoid distortion of current readings by other fields, move the meter along the wire to verify that the reading remains constant. · Calibration is required. Readings must be verified with a recently calibrated clamp-on volt-ammeter on each project. If the reading is not within ±2% of the recently calibrated instrument, have the instrument recalibrated by a qualified testing lab. Accuracy offield measurements. Accuracy is ±3% of full scale. Anemometers. There are several types of anemometers. The deflecting vane anemometer consists of a pivoted vane enclosed in a case. As it passes through the anemometer, air exerts a pressure on the vane. Movement of the vane is resisted by a hairspring. The instrument gives instantaneous readings of directional velocities on an indicating scale, and can be supplied with various remote- and direct-connected measuring tips (jets). Recommended for measur- ing air quantities through both supply and return air terminals using the proper air terminal factor Ak (effective area) for airflow calcula- tion, as well as for indicating low velocities (0.5 to 1.5 m/s) where the instrument case itself with the appropriate probe attached is placed in the airstream. Limitations: · It should not be used in extremely hot, cold, or contaminated air. · It is affected by static electricity. · The instrument duct probe is sensitive to presence and proximity of duct walls, and tends to read high on the suction side and low on the discharge side of a fan. · Accuracy is affected by position. · Calibration is required. Readings must be verified with a recently calibrated deflecting vane anemometer on each project. If the reading is not within ±2% of the recently calibrated instrument, have the instrument recalibrated by a qualified testing lab. Accuracy offield measurements. Accuracy is within ±10% when the instrument is calibrated and used in accordance with the manu- facturers' recommendations. Air inlet and outlet device flow Ak fac- tors are a function of duct and damper conditions, which affect velocity immediately before the device. Use under conditions not identical to the manufacturers' test conditions produces measure- ment error. The instrument must be calibrated in the field for cor- rection factor by pitot tube traverse within the limitations of the system. The revolving vane or propeller anemometer can be either mechanical or direct-reading digital. For the mechanical type, a mechanical propeller or revolving vane anemometer consists of a light wind-driven wheel connected through a gear train to a set of recording dials that read the linear feet of air passing through the wheel in a measured length of time. The instrument is made in var- ious sizes, but 75, 100, and 125 mm are the most common. Each instrument requires individual calibration. The required instrument accuracy of calibration is 1 to 3% of scale (using a corrective chart). Recommended for measuring supply, return, and exhaust air quan- tities at air inlets and outlets, as well as air quantities at the faces of return air dampers or openings, total air across the filter or coil face areas, etc. The direct-reading digital type differs from the mechanical type mainly in that it uses a powered electronic circuit to convert a pulse generated by the rotating vane into a small electric current to give a meter reading calibrated directly in air velocity units. Gener- ally, these instruments have microprocessor software to compensate for any nonlinearity. Recommended for measuring supply, return, 2019 ASHRAE Handbook-HVAC Applications (SI) and exhaust air quantities at air inlets and outlets; air quantities at the faces of return air dampers or openings; total air across the filter or coil face areas, etc. Limitations: · For mechanical anemometers, each reading must be corrected by the instrument's calibration chart. · The air inlet or outlet device manufacturers' specified flow Ak factor for the device must be used in computing air quantities. · Total inlet area of the instrument must be in the measured air- stream. · It is not suitable for measurement in ducts. · It is fragile and cannot be used in dusty or corrosive air. · The instrument has a turbine wheel of very low inertia, so be cau- tious regarding reliability of readings in nonuniform, turbulent, or stratified airstreams. This is likely to occur downstream of dampers, face-and-bypass coils, or any device that causes turbu- lence in the airstream being measured. · The mechanical anemometer is not direct reading and must be timed manually. · At low velocities, the instrument's friction drag is considerable. To compensate, a gear is commonly used. Thus, the correction is additive at the lower range and subtractive at the upper range, with the least correction in the middle of the range. Most of these instruments are not sensitive enough for use below 1 m/s, although ball-bearing models claim ranges down to 0.15 m/s. The useful range is from 1 to 10 m/s. · Calibration is required. Readings must be verified with a recently calibrated instrument on each project. If the reading is not within ±2% of the recently calibrated instrument, have the anemometer recalibrated by a qualified testing lab. Accuracy offield measurements: · Smooth flow: ±5% of reading above 1 m/s. Not recommended for velocities below 1 m/s. · Nonuniform flow: ±30% (or greater, for direct-reading digital type). · The instrument must be calibrated in the field for a correction factor by pitot tube traverse within the limitations of the system. Operation of the thermal anemometer, which can be either sin- gle point or omnidirectional, depends on the fact that the resistance of a heated element changes with its temperature. As airflows over the element in the probe, the temperature of the element changes from its temperature in still air. The resistance change is indicated as a velocity on the indicating scale of the instrument. Instruments are available using a heated thermocouple, heated thermistor, or a heated wire. They have similar characteristics regarding uses, lim- itations, and accuracy. Some instruments are also provided with temperature scales that can be used by setting the proper selector button. Others can measure static pressure with provided accesso- ries. Recommended uses include measuring the following: · Very low air velocities, such as room air currents and airflow in hoods (0.05 to 3.0 m/s) · Air movement at grilles and diffusers · Velocity measurements in ducts Limitations: · The instrument probe is very directional for velocity readings and must be located at the exact location and orientation on the air inlet or outlet device, as specified by the air device manufacturer. · Probes are subject to fouling by dust and corrosive air. · The instrument probe must be used in the direction of calibration. · In general, these instruments should not be used in flammable or explosive atmosphere. However, there are special thermal ane- mometer probes available for use in these environments. Inc. ASHRAE, 2019 user. single for Licensed | {}
b33ec91e-678c-45d1-865f-869640cd9285 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Testing, Adjusting, and Balancing 39.5 · Calibration is required. Readings must be verified with a recently calibrated instrument on each project. If the reading is not within ±2% of the recently calibrated instrument, have the anemometer recalibrated by a qualified testing lab. Accuracy offield measurements. Accuracy is ±3% above 0.5 m/ s. The instrument must be calibrated in the field for correction factor by pitot tube traverse within the limitations of the system. Thermometers. Dial thermometers are of two general types: stem and flexible capillary. Their dial heads can be 45 to 125 mm, with stainless steel encapsulated temperature sensing elements. Hermetically sealed, they are rust-, dust-, and leakproof and are actuated by sensitive bimetallic helix coils. Some can be field cali- brated. Sensing elements range in length from 60 to 600 mm and are available in many temperature ranges with or without thermometer wells. Small dial thermometers usually use a bimetallic temperature- sensing element in the stem. Temperature changes cause a change in the twist of the element, and this movement is transmitted to the pointer by a mechanical linkage. The flexible capillary dial thermometer has a rather large tem- perature-sensing bulb connected to the instrument with a capillary tube. The instrument contains a Bourdon tube, the same as in pres- sure gages. The temperature sensing system, consisting of the bulb, capillary tube, and Bourdon tube, is charged with either liquid or gas. Temperature changes at the bulb cause the contained liquid or gas to expand or contract, resulting in changes in the pressure exerted within the Bourdon tube. This causes the pointer to move over a graduated scale as in a pressure gage, except that the ther- mometer dial is graduated in degrees. The advantage of this type is that it can be used to read temperature in a remote location. In using a dial thermometer, the stem or bulb must be immersed a sufficient distance to allow this part of the thermometer to reach the tempera- ture being measured. Recommended uses include checking both air and water tem- perature in ducts and pipe thermometer wells. Limitations: · Dial thermometers have a relatively long time lag, so enough time must be allowed for the thermometer to reach equilibrium and the pointer to come to rest. · Calibration is required. Readings must be verified with a recently calibrated instrument on each project. If the reading is not within ±2% of the recently calibrated instrument, have the dial thermom- eter recalibrated by a qualified testing lab. Accuracy offield measurements. Accuracy is within one-half of a scale division mark. There are four basic types of digital electronic thermometers: thermocouple, thermistor, resistance temperature detector (RTD), and diode sensors. They consist of a portable, handheld, battery- powered, digital thermometer connected by a short cable to various interchangeable probes that are designed for sensing the tempera- ture of air or other gases, immersion in liquids, or contact with a solid surface. Some instruments have a calibration reference, which allows calibrating out offsets introduced by mechanical shocks, ambient temperature variations, or component drift. Some instru- ments can switch between I-P and SI units and between resolutions of 0.1 and 1.0. Response times are 1 to 10 s for liquids and solids, and 5 to 50 s for gases. Instrument accuracy is ±0.3°C where the range is below 350°C and ±0.8°C for broader ranges. The lower- range instruments should be used unless the expected measure- ments will be out of their range. Recommended uses include all TAB temperature measurements, including air and other gases, liquids, and surfaces of pipes and other components with the appropriate probe. The manufacturers' directions must be followed regarding proper use of probe and max- imum allowable temperature for the probe and or thermometer. Equipment is available to measure from -230 to 1230°C. A com- mon range is -10 to 120°C. Limitations: · Batteries must be recharged or changed when required. · In piping applications, it should be remembered that the surface temperature of the pipe is not equal to the fluid temperature and that a relative comparison is more reliable than an absolute reli- ance on readings at a single circuit or terminal unit. · Be sure measurement is taken at least as long as response time. · Calibration is required. Readings must be verified with a recently calibrated instrument on each project. If the reading is not within ±2% of the recently calibrated instrument, have the digital elec- tronic thermometer recalibrated by a qualified testing lab. Accuracy offield measurements. When properly used, the instru- ment accuracy shall be attainable in the field. Fluid Testing and Balancing Pyrometers. Pyrometers normally used in measurements of sur- face temperatures in heating and air conditioning applications use a thermocouple as a sensing device and a millivoltmeter (or potenti- ometer) with a scale calibrated for reading temperatures directly. A variety of types, shapes, and scale ranges are available. The required instrument test accuracy is ±1% of full scale. Recommended uses include · Balancing water circuits thermally, whenever balancing with flow measurements are not practical. · For evaluation of some types of boilers, furnaces, ovens, etc., where temperatures are over 40°C. · Calibration is required. Readings must be verified with a recently calibrated instrument on each project. If the reading is not within ±2% of the recently calibrated instrument, have the pyrometer recalibrated by a qualified testing lab. Limitations. In piping applications, remember that the surface temperature of the conduit is not equal to the fluid temperature, and that a relative comparison is more reliable than an absolute depen- dence on readings at a single circuit or terminal unit. Accuracy offield measurements. Accuracy is within one-half of a scale division mark. Calibrated Pressure Gage. Test gages should be at least Grade A quality; have Bourdon tube assemblies made of stainless steel, alloy steel, monel, or bronze; and have a nonreflecting white face with black lettering conforming to ASME Standard B40.1-1985. Test gages are usually 90 to 150 mm in diameter, with bottom or back connections. Many dials are available with pressure, vacuum, or compound ranges. Minimum accuracy is within 1% of full scale. Recommended uses are checking pump pressures; coil, chiller, and condenser pressure drops; and pressure drops across orifice plates, venturis, and other flow calibrated devices. Limitations: · Anticipated working pressure range is in the middle two-thirds of the instrument's scale range, and the gage should not be exposed to pressures greater than the maximum dial reading. Where there is exposure to vacuum, use compound gage. · Reduce or eliminate pressure pulsations by installing a snubber or needle valve in waterline. · Do not mount on vibrating equipment or piping. Wall mounting is preferred; another alternative is to install pressure/temperature test ports that can be used with a portable stem probe and gage (or thermometer) through an elastic, durable, self-sealing material. Cap the test port when not in use for additional sealing security. · Calibration is required. Readings must be verified with a recently calibrated instrument on each project. Ifthe reading is not within Inc. ASHRAE, 2019 user. single for Licensed | {}
8db42add-0829-4508-87d1-9b61ca8ebbbe | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 39.6 2019 ASHRAE Handbook-HVAC Applications (SI) ±2% of the recently calibrated instrument, have the pressure gage recalibrated by a qualified testing lab. Accuracy offield measurements. Accuracy is within one-half of a scale division mark. Differential Pressure Gage. This instrument is a dual-inlet, Grade A, dual Bourdon tube pressure gage with a single indicating pointer on the dial face that indicates the pressure differential between two measured pressures. It can be calibrated in Pa or kPa. The required instrument accuracy minimum is ±1 % of full scale. At lower differential pressure ranges, recommended for use with water hose flexible connectors for water distribution balancing (similar to how a mercury U-tube manometer is used). At higher differential pressure ranges, these instruments can be used in lieu of the two combination high-pressure gages mounted on the mercury U-tube manometer board. Limitations: · Some applications require use of a snubber or needle valve. A three-valve cluster for shutoff and bypass is necessary to prevent over-pressure damage when used as a portable test gage. · Calibration is required. Readings must be verified with a recently calibrated instrument on each project. If the reading is not within ±2% of the recently calibrated instrument, have the pressure gage recalibrated by a qualified testing lab. Accuracy offield measurements. Within one-half of a scale divi- sion mark. Differential Pressure Manifold Gage. This is a single-port, Grade A, Bourdon tube, calibrated test gage attached to the bull of a tee. Each branch is fitted with a tight shutoffball valve and a length of hose, terminating in a union and nipple for attachment to a con- ventional gage port at each measuring point. Recommended use is to indicate pressure at each point by alternating valve opening and closing. Using a single gage eliminates potential error from using two separate permanently mounted gages, which are subject to pos- sible vibration damage and differences in calibration. Calibration is required. Readings must be verified with a recently calibrated instrument on each project. If the reading is not within ±2% of the recently calibrated instrument, have the pressure gage recalibrated by a qualified testing lab. Other Air or Fluid System Measurements Inc. ASHRAE, 2019 user. single for Licensed Revolution Counter (Odometer) and Timing Device. The rev- olution counter is a small handheld counting device that is pressed to the center of a rotating shaft for a period of30 to 60 s. Reasonable accuracy can be obtained by using a good watch with a sweep sec- ond hand or a digital watch if a stopwatch is not available. Recom- mended use is for determining shaft speed on any shaft having an accessible shaft end with a countersink. Limitations: · Not to be used on flat-ended shafts without the correct adaptor. Otherwise, slip and inaccurate readings are inevitable. · Some types have a clutch engagement in which a certain amount of force is required to activate the recording mechanism. · Must be used and coordinated with an accurate timepiece. · Normally cannot be reset to zero; the shaft speed measured is the difference between the initial and final instrument readings divided by the time interval. · Calibration is required. Readings must be verified with a recently calibrated instrument on each project. If the reading is not within ±2% of the recently calibrated instrument, have the odometer recalibrated by a qualified testing lab. Accuracy offield measurement. Accuracy is ±2%, when used properly. Electronic Tachometer (Stroboscope and Photoelectric). The stroboscope has a controlled high-speed electronic flashing light The solid-state photoelectric tachometer is an optional instru- ment that is pointed at the device to be measured and the revolution speed is directly read on the dial face. A reflective paint or material must be spotted on the rotating device; this spot is counted and elec- tronically integrated over time to give an instantaneous reading. The instruments usually have several ranges, and no electrical or physi- cal contact with the device is necessary. Accuracy is within ±1% of the dial scale reading when properly calibrated. whose frequency is electronically controlled and adjustable. When the frequency of the flashing light is adjusted to equal the frequency of the rotating machine, the machine appears to stand still. This unit need not be in contact with the machine during use. Instrument accuracy is generally within 1.5% of the indicated value, and within 1% if a magnetic pickup is used. Recommended use is for measuring rotational speeds when instrument contact with the rotating equipment is not feasible. Limitations: · Care must be taken to avoid reading multiples of the actual rpm when using the stroboscope. Readings must be started at the lower end of the scale. · Calibration is required. Readings must be verified with a recently calibrated instrument on each project. If the reading is not within ±2% of the recently calibrated instrument, have the tachometer recalibrated by a qualified testing lab. Accuracy offield measurements. Accuracy is within one-half of a scale division. Dual-Function Tachometer. This instrument provides both optical and contact measurements of rotation and linear motions. Many allow a choice of ranges, depending on the application. A dig- ital display always indicates the unit of measurement to identify the operating range. A memory button may be used to recall the last, maximum, minimum, and average readings. Compact size and light weight make for easy operation. Recommended use is for measur- ing rotation speeds by direct contact or by counting the speed of a reflective mark. Limitations: · Calibration is required. Readings must be verified with a recently calibrated instrument on each project. If the reading is not within ±2% of the recently calibrated instrument, have the tachometer recalibrated by a qualified testing lab. · Battery operated Accuracy offield measurements. Accuracy is within one-half of a scale division. Low-Density Fluid U-Tube Manometer. The manometer is a simple, useful way to measure partial vacuum and pressure. In its simplest form, it consists of a U-shaped glass tube partially filled with liquid; a difference in height of the two fluid columns denotes a pressure difference in the two legs. Recommended uses include measuring pressure drops above 250 Pa across filters, coils, elimi- nators, fans, grilles, and duct sections; and measuring low manifold gas pressures. Limitations: · To ensure accuracy, manometer tubes must be chemically cleaned and filled with the correct fluid. · U-tube manometers cannot be used for readings under 250 Pa. · Reading accuracy depends on the user' s ability to gage the level in each tube simultaneously; this is especially troublesome if surges occur in the flow being measured. Diaphragm-Type Differential Pressure Gage. A dry diaphragm-operated differential pressure gage that uses a calibrated spring-loaded horseshoe magnet lever operated from the differential pressure on the diaphragm, causing rotation of a highly magnetic permeable helix that positions a pointer on the pressure scale. The | {}
1bf4c49f-1b25-469c-a724-bd79a6315208 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Testing, Adjusting, and Balancing 39.7 pressure gage is operated by magnetic field linkage only, so it is extremely sensitive and accurate; its construction design makes it resistant to shock and vibration. The helix rotates on antishock- mounted sapphire bearings. A zero-calibration screw is located on the plastic cover. Common ranges are 0 to 125, 250, or 1250 Pa. There are approximately 30 available pressure ranges. The minimum accuracy of the instrument is ±2% of full dial range. Rec- ommended for use with pitot tube or with static probe, or with spe- cially constructed induction unit primary air total pressure measuring tip for primary air distribution balancing on high- pressure induction systems. Limitations: · Should not be used in preference to liquid or electronic manometer. · Readings should be made in mid-scale of range. · Should not be mounted on a vibrating surface. · Should be held in same position as when zeroed · Should be checked against a known pressure source with each use · Calibration is required. Readings must be verified with a recently calibrated instrument on each project. If the reading is not within ±2% of the recently calibrated instrument, have the pressure gage recalibrated by a qualified testing lab. Smoke Devices. These devices are generally used in special studies of airflow and duct leakage. Candles are available in various sizes and durations of burning time. The chemical element in the smoke is zinc chloride. Sticks are activated by crushing the end of the device, releasing a smoke stream approximately double that of a cigarette. Guns generally use a chemical that readily combines with atmospheric moisture. A cartridge produces 500 to 1000 puffs of smoke, or releases the same quantity in a steady stream. Borazine guns emit dense white clouds of smoke that tend to remain suspended in air for some time. A valve adjustment regulates the discharge. Recommended uses include determining the direction and observing the velocity and pattern of airflow in room studies, hoods, filters, etc. Discharge patterns from exhaust systems, driers, hoods, and stacks can be identified. Limitations: · Some smoke devices may be toxic, and protective apparatus may be required. After extreme use, special removal efforts may be necessary. · Smoke devices may activate fire and or smoke alarms in ductwork, computer rooms, or critical areas of the building; or cause panic if occupants are not notified. Flow Capture Hoods. A conical or pyramid shaped hood may be used to collect the airflow from a terminal and guide it over a flow measuring system which reads directly in litres per second. The instrument can be a swinging vane anemometer, differential pres- sure air gage (diaphragm type), manometer, or thermal anemometer. The balancing cone should be tailored for the particular job. The large end ofthe cone should be sized to fit over the complete air inlet or outlet device and should have a seal to eliminate air leakage. The cone should terminate in a straight section with factory designed and calibrated pressure grids, straighteners, and instruments. Recommended uses include proportionally balancing air distri- bution devices. Limitations: · Should not be used where discharge velocities exceed 10 m/s. · Recognize that the device generally redirects the normal pattern of air discharge and that it contributes an artificially imposed pres- sure drop in the branch of the air terminal being measured. These may result in a decrease in the delivered airflow of the outlet. · Contact the air inlet and outlet device manufacturer for details in using this instrument with their devices. · The instrument must be calibrated for the intended use. For use with supply distribution devices, the instrument should have been calibrated in the supply mode. For use with return distribution devices, the instrument should have been calibrated in the return mode. · Calibration is required. Flow-measuring instrument and hood assembly should be field checked with a velocity traverse. Read- ings must be verified with a recently calibrated instrument on each project. If the reading is not within ±2% of the recently cal- ibrated instrument, have the pressure gage recalibrated by a qual- ified testing lab. Accuracy offield measurements. If the hood is properly shaped and positioned at the air terminal, accuracy of field measurements will be within the limitations of the flow reading instrument. Micromanometer (Hook Gage). These instruments are designed to read small differences in air pressure accurately and usually have a wide scale range. Most scales read pressures of 0 to 1000 Pa, in hundredths of 10 Pa on the vertical scale, and thou- sandths of 1 Pa on a vernier scale. Different versions of this instrument exist. The most common type contains two glass vials about 50 to 75 mm in diameter. A pointed needle or hook is positioned by a micrometer adjustment until the point dimples the water surface but does not break the sur- face tension. The difference in level is determined in micrometer readings. Another variation of this instrument has a single vial or well and an inclined scale. The well is positioned by a micrometer or vernier adjustment. It is very important that all micromanometers, including the electronic units, be accurately leveled. The solid-state electronic hook gage will measure positive, neg- ative, or differential pressures to ±0.0625 Pa over a 0 to 500 Pa range. It can also be used with pitot tubes for accurate measurement of air velocities as low as 2.3 m/s. Recommended uses include read- ings at hoods, perforated ceilings, etc.; calibrating other instru- ments; and measurements of velocities between 2.3 and 3.0 m/s, when used with a standard pitot tube. Limitations: · Difficult to use with pulsating pressures. · Stability and leveling requirements make the instrument difficult to use in the field. · Generally not as sensitive as thermal anemometers below 3 m/s, when used with a standard pitot tube. Double Reverse Tube. Other names for this device include impact reverse tube, combined reverse tube, and type s tube. It con- sists of two stainless steel tubes approximately 9.5 mm OD, perma- nently joined lengthwise. The tubes open facing opposite directions at the probe end with open ends at the base for connection to a manometer. (See Figure 1 .) Recommended for use in dirty or wet airstreams where the amount of particulate matter in the airstream impairs the use of a pitot static tube. The instrument can be used to measure total pressure, static pressure, and obtain velocity pressure. Limitations: · Requires a large (19 mm) duct hole for insertion. · The tube requires calibration and must be used in the same orien- tation as calibrated. The flow direction should be marked on the tube. · The tube cannot be used to measure static pressure directly. It must be connected to two manometers and static pressure must be calculated. · Tube ends must be kept smooth, clean, and free of burrs. Accuracy offield measurements. Accuracy for field use of the combination of a double reverse tube with manometers is ±10%. Inc. ASHRAE, 2019 user. single for Licensed | {}
3fa04d95-016f-4e69-ada1-628df933d6c1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 39.8 2019 ASHRAE Handbook-HVAC Applications (SI) Clamp-On AC Power Meter (Wattmeter). The clamp-on type power meter has trigger-operated, clamp-on transformer jaws, like a voltammeter. This instrument measures true rms voltage and cur- rent, in addition to power in single phase or balanced three phase circuits. Compared with mean value measurement, true rms mea- surement is especially valuable for distorted waves, such as noise and multiplexed signals. Typical ranges are 20 to 600 v rms, 2 to 200 A rms, and 2 to 200 kW; or 20 to 600 V rms, 0.2 to 20 A rms, and 0.2 to 20 kW. Recommended uses include measurement of single, split-phase, and three-phase power sources. Given motor efficiency and power factor, power draw can be related to motor power on a fan or pump curve and the operating point determined. Limitations: · Caution is required, particularly when taking measurements under confined conditions. · Readings below 10% of input range are not recommended. · Batteries must be checked before use. · Calibration is required. Readings must be verified with a recently calibrated instrument on each project. If the reading is not within ±2% of the recently calibrated instrument, have the pressure gage recalibrated by a qualified testing lab. Accuracy of field measurements. Accuracy is within ±1% of reading plus 0.5% of range Recording Instruments. Recording instruments exist in wide variety, available to record any measurement taken by an instru- ment, such as dry-bulb temperature, wet-bulb temperature, relative humidity, and operating periods of cycling electrical equipment. The recording charts may be either continuous strip or circular, with chart rotation once every 24 h or 7 days. Some instruments are avail- able with one or more remote bulbs. Recommended for obtaining round-the-clock data on the operation or performance of equipment. They are particularly useful for studying and diagnosing question- able operation in refrigerators, greenhouses, processing rooms, ovens, and comfort air conditioning systems. Limitations. Some judgment must be used in the application of recording instruments. There are great differences in quality, accu- racy, and cost. Care must be used to start the instrument at the cor- rect time of day, and on the right day when a seven-day chart is used. Calibration is required. Readings must be verified with a recently calibrated instrument on each project. If the reading is not within ±2% of the recently calibrated instrument, have the pressure gage recalibrated by a qualified testing lab. Accuracy offield measurements. Carefully study the manufac- turer catalog data for instrument accuracy. Itis important to read and observe specific operating instructions to obtain the published accu- racy from a given instrument. Humidity-Measuring Devices. A number of instruments are available to measure the level of moisture in air, including · Battery-powered hygrometer · Powered dew point indicator · Powered psychrometer with built in pump and fan · Digital psychrometer with built-in reservoir and fan Calibration is required. Readings must be verified with a recently calibrated instrument on each project. If the reading is not within ±2% ofthe recently calibrated instrument, have the instrument reca- librated by a qualified testing lab. Recommended use varies by type; hygrometers give direct, rapid relative humidity readings, and digital psychrometers provide dry- and wet-bulb depression within approximately 30 s. Accuracy offield measurements. Hygrometers have an accuracy of ±2 to 3% rh in the 20 to 95% rh range. Psychrometer thermometer readings have an accuracy of ±0.3 K. Barometer. A barometer measures atmospheric pressure, which is required to correct all airflow readings to standard conditions. A Bourdon tube type with accuracy of 1% of full scale should be used. Barometric pressure information may also be obtained from weather radio stations or airports in the immediate vicinity. Actual pressure at local elevation must be used for air density calculations. Fluid System Digital Electronic Differential Pressure Meter. This instrument measures the differential pressure across an ele- ment in a system when flow is present, providing digital readings in the range of 1 to 150 kPa. Some instruments include a temperature probe for a range of 0 to 120°C, hoses with snap-on fittings, and automatic air purging. A computer is available for calculating the flow in a range of0.01 to 300 L/s and computing the hand wheel set- ting of compatible valves by proportional balancing procedures. Maximum working pressures can be up to 2060 kPa (gage). Recommended uses include measurement offluid flow, tempera- ture, and differential pressure, as well as computing the setting of compatible valves by proportional balancing procedures. Limitations: · The computing feature is limited to compatible valves. · Calibration is required. Readings must be verified with a recently calibrated instrument on each project. If the reading is not within ±2% of the recently calibrated instrument, have the instrument recalibrated by a qualified testing lab. Accuracy offield measurements. Accuracy of differential pres- sure within 3 kPa or 2% of valve readout (whichever is greater). This same accuracy is true for measurement of flow, done via the com- puting feature. Electronic Differential Pressure Meter. This instrument is a portable device which measures differential pressure and gives a digital readout directly in pressure or velocity. Some instruments are also available with adapters and probes to measure flow and tem- perature. Typical ranges are 0 to 25 kPa for low-density fluids, and 0 to 600 kPa or 0 to 700 kPa for high-density fluids. Temperatures can be measured from -48 to 120°C. Recommended for use with a pitot tube, static probe, flow grid, orifice plate, or special balancing valve. Some instruments can also be combined with a flow- measuring hood. Many instruments have memories, averaging capabilities, and printers. Limitations: · When air velocities are below 3 m/s, a micromanometer or hook gage should be used. Some instruments of this type have micro- manometer accuracies. · These instruments are battery powered and require checking bat- teries and replacing or recharging them. · Some instruments should not be stored below -10°C or operated below 0°C. · Calibration is required. Readings must be verified with a recently calibrated instrument on each project. If the reading is not within ±2% of the recently calibrated instrument, have the instrument recalibrated by a qualified testing lab. Accuracy offield measurements. Experience shows that qualified technicians can obtain measurements that range between ±5 and 10% accuracy under good field conditions. However, good field conditions do not always exist, and measurements can easily exceed ±10% error. Inc. ASHRAE, 2019 user. single for Licensed Ultrasonic Flowmeters. This is a device that determines flow through the use of acoustic signals, measured in design units (e.g., litres per second). The ultrasonic flow metering station is either an integral part of the piping system or a strap-on meter. In either case, there is no intrusion into the pipe or liquid flow that would generate a pressure drop. There are no moving parts in the flow to maintain or service. Two distinct types of ultrasonic flow meters exist: a transit-time device for HVAC or clear water measurement, and a | {}
fcbd7e7e-df4e-410b-9e7d-d224efd46fc4 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Testing, Adjusting, and Balancing 39.9 Doppler-effect device for flows containing a required volume of particulate in the liquid. Recommended use includes measurement of flow in full pipes; these devices are excellent when low or non- existent pressure drop is a requirement. These are best for larger pipes, and most manufacturers' specifications are based on flows of 0.3 m/s or greater. Limitations: · For Doppler flow meters, liquid must contain particulate or gas bubbles. · Transit-time flowmeters require liquid to be acoustically transpar- ent (implies low particulate content [e.g., typical lake or river water or cleaner]). · Portable (strap-on) flowmeters require that pipe details (e.g., diameter, wall thickness, material of construction) are known or determinable. Pipe must be acoustically transparent (both con- crete and lined pipe are not). · Calibration is required. Readings must be verified with a recently calibrated instrument on each project. If the reading is not within ±2% of the recently calibrated instrument, have the instrument recalibrated by a qualified testing lab. Accuracy offield measurements. Doppler Flowmeters: · Typically within 3 to 5% for strap-on transducers · Typically within 2 to 3% for integral transducers Transit- Time Flowmeters: · Typically within 2 to 3% for strap-on transducers · Typically within 1 to 2% for integral transducers · Typically within 0.5 to 1% for integral transducers mounted to a calibrated flow tube Turbine Flowmeter. This mechanical device uses a wheel placed in the path of the flow. Liquid causes the wheel to turn at speeds relative to the velocity, generating a signal and providing flow information directly in design units (e.g., litres per second) or a milliamp output. Recommended for measurement of flow in pipes with clean fluid flow. Limitations: · Care must be exercised to maintain the turbine flowmeter, be- cause wear may affect the wheel bearings. · Bearings may drag if impurities lodge in them. · Debris can clog or break the wheel. · Calibration is required. Readings must be verified with a recently calibrated instrument on each project. If the reading is not within ±2% of the recently calibrated instrument, have the instrument recalibrated by a qualified testing lab. Accuracy offield measurements. Accuracy is within 2%. Permanently Installed Airflow Measuring Stations. There are two main types of permanent airflow measuring stations. The veloc- ity pressure array comprises a fixed array of velocity pressure measuring devices. Recommended uses. These stations measure the fan total airflow and distribution of air in branch ducts. Other useful measurements include those of outdoor, return, and relief airflow. Limitations: · The required length of straight sections upstream and downstream of the measuring device depends on both velocity of airflow and the effects of the nearest obstruction. The location of the airflow measuring station must be in accordance with the manufacturer's recommendations. · Inlet velocity magnitude, profile temperature, dust, moisture, and gas products may limit the use of airflow measuring stations. Accuracy of field measurements. Under ideal conditions, a velocity pressure airflow measuring station should produce an accu- racy of ±5% plus the error rate of the pressure sensor. Because of sensitivity to disturbances and duct conditions, the manufacturer's duct placement recommendations or ASHRAE Handbook-Funda- mentals requirements for measurement with technologies based on velocity-pressure equalizing principles should be observed. The thermal dispersion array airflow measuring station ob- tains velocity measurements directly using independent measure- ment points in a fixed array before averaging. Communications options allow technicians to download instantaneous point velocity and temperature data independently from the control system. A re- mote traverse without time lag between samples is possible either using an infrared reading device or over an RS-485 network using BACnetTM or ModbusⓇ protocols. The independent nature of the sensor data allows for accurate duct area averaging. Recommended uses: · Direct measurement of outdoor airflow rates (low flow sensitivity and accuracy, wide operating velocity range, wide temperature range, fewer space restrictions) · Maintaining fixed volumetric differentials for space pressuriza- tion control, using its high repeatability · As a reference for other velocity and temperature instruments be- cause of their stability and factory calibration (higher precision) · Any conditioned air velocity, volume, or temperature averaging application that would benefit from highly repeatable measure- ment Limitations: · Performance depends on local conditions, velocity sensor density (number/unit area), and type of the nearest obstructions (upstream and downstream). · Avoid placement downstream of modulating dampers or immedi- ately upstream of a damper that may close completely. · The discharge side of duct silencers can be problematic when the measuring station is within the absorption distance of a humidi- fier or wet coil face. Accuracy offield measurements. Accuracy should be within ±3% of reading, when placement is within the manufacturer's guidelines. Multifunction Portable Instruments. Digital electronic instru- ments are available with a wide selection of probes that can be fitted into the various channel ports of a single handheld meter with vari- ous uses, accuracies, and limitations. These uses can be singular (e.g., thermohygrometers for temperature and relative humidity) or many. Types of measurements include temperature of air, gas, and liquids with a wide choice of sensing elements, such as thermocou- ples or RTDs; pressure of air, gas, and liquids with manometers or pitot tubes; differential air pressure, static pressure, or barometric pressure; and differential water pressure or gage pressure. Amongst the specific tools used are wind vane, hot wire, or pitot tube ane- mometers; optical, inductive, and rotational tachometers; and water and air quality attachments for pH, conductivity, salinity, and mV, O2, and ion concentration. Some instruments have both battery and plug-in AC power; recording memory for downloading onto computers or transmission over RS-232 or RS-500 interface; hold, alternating, and averaging circuits for applications as traverses; relative humidity calibrating devices; and other features. Individual manufacturers must be consulted for details of accu- racy, limitations, usage, and response times of the individual mea- surements. Instruments should be calibrated in accordance with ASHRAE Standard 11 1 to verify their accuracy and repeatability before use in the field. Inc. ASHRAE, 2019 user. single for Licensed | {}
c3aa2859-8d8f-4fb9-867f-2b5bd698f032 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 39.10 5. AIR TESTING, ADJUSTING, AND BALANCING This section sets forth requirements for system preparation, obtaining data, and system testing and adjusting. These require- ments apply to both new and existing HVAC supply, return, and exhaust systems. System Preparation Before air system testing, adjusting, and balancing, obtain and verify the following: · Obtain updated construction drawings, specifications, approved shop drawings and submittals, addenda, bulletins, and change orders related to air systems. · Prepare field data forms to record testing and balancing process. · Obtain system leakage rate data where duct leak testing is speci- fied. · Verify that fans are installed, rotating correctly with proper rpm, controlled to supply the required airflow rate, and that all instal- lation, start-up, lubrication, and safety requirements have been met. · Check for clean filters properly mounted and sealed. · Fire, smoke, automatic, and volume control dampers are opera- ble, accessible, and are in an open or normal position. · Controls are installed, operable, and calibrated. · Air terminal devices are installed, operable, and accessible. · Air outlet and inlet devices are installed and accessible. · Access doors are installed and secured. Perform the following in accordance with design documents before beginning air system testing, adjusting, and balancing: · Verify that all dampers are in an open position and all air terminal devices or automatic air volume control devices are in an accept- able mode. · Verify that all air inlet or outlet deflectors are in the position indi- cated by the manufacturer when using Ak factors to determine air- flow rate, and obtain correction factors for all velocity measuring instruments. · Verify that all automatic controls in the system are set in the testing mode and all computer programs have been properly loaded (where applicable) and parameters set. Inc. ASHRAE, 2019 user. single for Licensed Air System Testing and Adjusting Perform the following tests and adjustments before beginning the air system balancing: · Record nameplate data on fan, motor, and air handling cabinet. Also, record sizes of sheaves, belts, and shafts. · Test and record fan rate to confirm rated speed. · Measure and record motor-running amperes and voltages. · Set system in minimum outdoor air mode, then perform a pitot tube velocity traverse of main ducts and adjust fan speeds for total design supply and return airflow rates. Total design flow must include estimated duct leakage plus 5% of system total to allow for balancing effects. Minimum outdoor air quantities, estab- lished by pitot tube velocity traverse or other methods, must be maintained during all system modes. · For special systems such as variable-air-volume or constant- volume pressure-independent air terminal devices, set system static pressure and proceed to test and balance all of the air terminal devices and their downstream air inlet or outlet devices, ensuring that air terminal device inlet pressure is in the correct range. Air terminal device adjustments must be done per manu- facturer literature. 2019 ASHRAE Handbook- -HVAC Applications (SI) The following steps occur after all air terminal devices and related air inlet or outlet devices are balanced: · Measure and record the static pressure resistance of the duct system and the static pressure drop across coils, filters, etc., in the cabinet or out in the duct system. · Measure and record the pressures at fan suction and discharge per the pressure rating required, either static or total. · After the system is balanced, test the system in the maximum out- door air mode. If motor overloads or airflow rates are excessive, adjust manual dampers to obtain the same conditions as recorded with minimum outdoor air. · Measure and record outdoor, return, and supply air temperatures with the system set at minimum outdoor air mode at design air- flow or diversity and cooling or heating medium set for design flow. Verify coil capacities using the following formulas: Sensible Heat Btu/h = cfm 1.08 T where 1.08 = constant, 60 min/h 0.075 Ib/ft3 0.24 Btu/lb·oF T = dry-bulb temperature difference between air entering and air leaving the coil. In applications where cfm to conditioned space must be calculated, Tis the difference between supply air dry- bulb temperature and room dry-bulb temperature Total Heat Air-Side Btu/h t = cfm 4.5 ht⌀t where Btu/h = gpm x 500 x Tw 4.5 = conversion factor, 60 min/h 0.075 1b/ft3 htot = change in total heat content of supply air (enthalpy), in Btu/lb (from wet-bulb temperatures and psychrometric chart or table of properties of mixtures of air and saturated water vapor) Total Heat Water-Side where 500 = conversion factor, 60 min/h 8.33 lbs/gallon 1 Btu/lb·oF Tw = temperature difference between the entering and leaving water Air System Balancing Traverse Procedure. After the air system has been prepared, balance by the procedures set forth. Note: When system character- istics prevent design flow rates, balance the system components to equal percentages of design unless otherwise instructed by the design engineer. Balancing Submain Air Ducts. · Perform a pitot tube velocity traverse of each submain duct to determine flow rate through each. · Adjust the main volume control dampers to provide the required flow through each submain air duct. Balancing Branch Air Ducts. Balance the airflow in each branch duct by the following procedure: · Beginning at the submain duct closest to the fan, or with the high- est percentage of required flow, perform a pitot tube velocity tra- verse of each branch on that submain duct run. · Proceeding from the branch with the highest percentage of required flow, adjust the branch volume control dampers to pro- vide the required flow through each branch duct. · Proceed to the submain duct with the next highest percentage of required flow, and traverse and adjust each branch per the preceding steps. | {}
7fff3b75-7b21-4d5a-a66d-31a7ed2c153a | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Testing, Adjusting, and Balancing 39.11 · Continue until all branches are balanced. Balancing Air Terminal Device Flow Rates. After obtaining the required airflow rates in submain and branch ducts, balance each air terminal device by the following procedures: · Starting at the air terminal device with the highest percentage of design flow and ending with the air terminal device having the lowest percentage of design flow, adjust the air terminal device volume control to provide an airflow rate within 10% of design. Note: If balanced properly without excess pressure, then at least one air terminal device on each branch should have the volume control damper fully open. Branch dampers may require readjust- ment. · Continue until all air terminal devices are balanced to within 10% of design. Final Adjusting and Balancing. Upon completion of the preceding steps, obtain final measurements as follows: · Measure and record the final airflow rates at each air terminal device. If adjusting airflow rate through an air terminal device by 5% or less is required to achieve the final setting within 10% of design, it is not necessary to adjust nearby air terminal devices which have been final measured. Otherwise, nearby air terminal devices should be remeasured and adjusted as required. · Secure, mark, seal, and record the final setting positions of all vol- ume control dampers installed in submain or branch ducts. · Measure and record the final airflow rates at velocity traverses in main, submain, and branch ducts. Do not adjust related volume control dampers. · Measure and record the data, as outlined in Section 9. 4 (b), (c), (f), and (g). · Reset all controls for normal operations. Air-Side Systems. In addition to the applicable procedures al- ready detailed, the following air-side systems require additional bal- ancing procedures as indicated. Note: For systems using fan volume controls, balance at less than 100% volume setting to allow for fu- ture pressure loss of wet coils, damper movement, or dirty filter, or simulate pressure losses with volume controls at 100%. Single-Duct, Pressure-Dependent Systems: · Operate all associated fans. · Set the air terminal devices being testing on full cooling or for diversity and read all air outlet devices on the system. · Take static pressures at all system components. · Proportionally balance the air terminal devices. Start with the air terminal device with the highest percent of design airflow, and proportionally balance all V A V air terminal devices. This is done by setting the air terminal devices to full cooling (maximum air- flow) and adjusting the manual volume damper in the inlet to the air terminal device. There must be adequate static pressure at all times in the primary air duct. · Proportionally balance the air inlet or outlet devices. · Measure and record the final total airflow rate by pitot tube tra- verse with system set for maximum airflow. · Measure and record the data as detailed in Section 8.4 (b), (c), (f), (g), and ①, plus the duct static pressure sensed by the static pres- sure probe for automatic control of supply duct pressure existing when fan is at design flow rate. · Reset all controls for normal operation. · At the completion of balancing, - The inlet manual damper to at least one VAV air terminal device in the system will be fully open. - At least one damper in each branch duct will be fully open. . At least one air inlet or outlet device on each branch duct will be fully open. Multizone Systems: · Operate all fans (supply, return, and exhaust) associated with the system at or near design speeds. · Take initial static pressure measurements at all system compo- nents. · Take total air measurements. Determine total airflow quantity for each zone by pitot tube traverse unless impractical to do so. Take traverses as close to the unit as practical. Where the quantity can- not be obtained by pitot tube traverse, use the sum of the outlet quantities as the total airflow of the zones. Record this informa- tion on the report forms. Ifthe system has diversity, determine the diversity ratio and keep the proportion of cooled air to total- volume constant during the balance by setting enough zones to full cooling to equal the design flow through the cooling coil. The remaining zones will be set to minimum flow. · Check zone damper operation. Modulate the zone mixing damp- ers and measure the supply fan's motor amperage to ensure that motor overloading does not occur. Check amperage with the system in full cooling, full heating, and economizer modes to determine where maximum brake power occurs. Check that the unit's mixing dampers are operating correctly with minimal leak- age. Depending on circumstances, this should be done visually by reading temperatures or using static pressure drops. Also verify that all zone mixing dampers are controlled by the proper space thermostat. · Set zones being tested on full cooling or for diversity. · Proportionally balance the zones. Using the data from the pitot tube traverses or reading the outlets, determine which zones are over or under design airflow. If any zone is especially low, inves- tigate and correct for any blockages. To balance the zones, start with the highest zone and adjust each zone's manual balancing damper until the airflow is within 10% of the desired amount. · To balance the branches, start with the highest branch and adjust the branch damper until the airflow is within 10% of the desired amount. Use the total of the air inlet or outlet devices on the branch or balance with the traverses. After the highest branch is adjusted to within 10% of desired flow, go to the next highest branch and adjust it accordingly. Continue adjusting each branch from the highest to the lowest. After all the branches have been adjusted, go back and recheck each branch, because there is usu- ally some interaction between branches, and readjustment may be necessary. · After all the branches are adjusted to within 10% of desired air- flow, proceed with balancing the air inlet or outlet devices. Read all the air inlet or outlet devices and determine which air inlet or outlet devices have excessively great airflow and adjust them first, regardless of their location. Continue balancing until all the air inlet or outlet devices have been adjusted. Make one or more passes until an acceptable balance is obtained. · As all the air inlet or outlet devices have been proportionally bal- anced to each other by branch, an adjustment at the branch damper will increase or decrease all the air inlet or outlet devices on that branch proportionally. · Measure and record the final total airflow rate by pitot tube tra- verses in the heating and cooling mode with system set for max- imum duct airflow. · Measure and record the data required in Section 8.4 (b), (c), (f), (g), and (i), plus the duct static pressure sensed by the static pres- sure probe for automatic control of supply duct pressure existing when fan is at design flow rate. · Reset all controls for normal operation. · At the completion of balancing, - At least one air inlet or outlet device balancing damper will be fully open on every zone. - At least one zone balancing damper will be fully open. Inc. ASHRAE, 2019 user. single for Licensed | {}
b5419d3f-7c4a-4e1a-8538-745a7cb1309e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 39.12 2019 ASHRAE Handbook-HVAC Applications (SI) - Reset the system to normal operating conditions. Single-Duct, Fan-Powered Pressure- Systems: Fan configurations vary among air terminal devices in fan- powered systems. The internal fan may be in series with the pri- mary air for continuous airflow, or it may be in parallel with the primary air for intermittent airflow. Airflow from these fans is controlled by various methods, such as multiple wiring for three-speed control, silicon-controlled rectifiers (SCR) for multiple-speed control, or manual dampers at the fan dis- charge. Consult the air terminal device manufacturer for the proper operation and setting of the flow control. · Operate all associated fans. · Set the air terminal devices being tested on full cooling or for diversity. · Take static pressures at all system components. · Proportionally balance all air terminal devices. Start with the air terminal device with the highest percent of design airflow, and proportionally balance all VA v air terminal devices. This is done by setting the air terminal devices to full cooling (maximum air- flow) and adjusting the manual volume damper in the inlet to the air terminal device. There must be adequate static pressure at all times in the primary air duct. · Proportionally balance all air outlet devices. · Measure and record the final total airflow rate by pitot tube with system set for maximum duct airflow. · Measure and record the data noted in Section 8.4 (b), (c), (f), (g), and (i plus the duct static pressure sensed by the static pressure probe for automatic control of supply duct pressure existing when fan is at design flow rate. · Reset all controls for normal operation. · At the completion of balancing, 、 The inlet manual damper to at least one VAV air terminal device on each branch duct will be fully open. 、 At least one damper in each branch duct will be fully open. - Reset the system to normal operating conditions. Single-Duct, Fan-Powered Pressure-Independent Systems: Fan configurations and airflow control for these devices are the same as described in the Single-Duct, Fan-Powered Pressure- Dependent Systems section. Consult the terminal manufacturer for the proper operation and setting of the flow control. · Operate all associated fans · Set the air terminal devices being tested on full cooling or for diversity · Take static pressures at all systemic components · Proportionally balance all air terminal devices. Consider each air terminal device and associated downstream low-pressure duct- work as a separate, independent system. Verify the action of the thermostat (direct or reverse acting) and the volume damper posi- tion (normally closed or normally open). Verify the range of the damper motor as it responds to the velocity controller. Consult the air terminal device manufacturer's data for the required pressure drop range across the air terminal device. The total required inlet static pressure is this drop plus the downstream resistance. Take the static pressure drop across the air terminal device and the inlet static pressure. These readings should be within the required range. Verify that the air terminal device will operate at maximum flow when the inlet static pressure to the air terminal device is within the proper operating range by reading the downstream air outlet devices. · Proportionally balance all air outlet devices. · Test the VA V air terminal device for both maximum and minimum airflow as applicable. Consult the manufacturers' recommenda- tions on the proper procedure for setting the velocity controllers if required. Include both quantities on the report. · Measure and record the final total airflow rate by pitot tube tra- verses with system set for maximum duct airflow. · Measure and record the data required in Section 8.4 (b), (c), (f), (g), and ①, plus the duct static pressure sensed by the static pres- sure probe for automatic control of supply duct pressure existing when fan is at design flow rate. · Reset all controls for normal operation. · At the completion of balancing, - The inlet manual damper to at least one VAV air terminal device on each branch duct will be fully open. - At least one damper in each branch duct will be fully open. - Reset the system to normal operating conditions. Dual-Duct, Pressure-Independent Systems: This type of system uses control schemes that supply a varying quantity of heated or cooled air to the space. The hot duct and cold duct each have their own volume controller. · Operate all associated fans. · Set the air terminal devices being tested on full cooling or for diversity. · Take static pressures at all systemic components. · If all of the air terminal devices are constant volume, set thermo- stats to obtain all the airflow through the cold ducts. Traverse the main ducts if more than 10% of the rated fan airflow is measured in the hot duct. During the balancing process, find and correct hot valve leakage or crossed box supplies. · If the air terminal devices have a variable-volume feature, then adjust to full flow via thermostats so the sum total airflow rate of the air terminal devices equals the fan design flow rate during the balancing procedures. · Test the inlet static pressure at several of the most difficult-to- supply air terminal devices and make system adjustments for ade- quate pressure at the air terminal device inlet (CV or VA V) to pro- vide the required flow rate through the air terminal device and downstream ductwork. · With the air terminal device set for 100% cold air delivery and with the hot-duct temperature at least 11 K warmer than the cold duct, test the air terminal device for hot-valve leakage. Measure the temperature of the cold inlet duct air and the supply air tem- perature at two air outlet devices. If the duct splits at the dis- charge, measure the temperature at an air outlet device on each branch. If the average supply air temperature at the air outlet device is higher than the cold inlet duct temperature by more than 5% ofthe difference between cold duct and hot duct temperatures, request the installer to correct the deficiency. Also test for, report, and correct any air mixing deficiencies that result in 1.6 K or more difference between air outlet device supply temperatures and those supplied by an air terminal device. · Proportionally balance all air outlet devices. Consider each air ter- minal device and associated downstream low-pressure ductwork as a separate, independent system. Verify the action of the ther- mostat (direct or reverse acting) and the volume damper position (normally closed or normally open). Verify the range of the damper motor as it responds to the velocity controller. Consult the air terminal device manufacturer's data for the required pressure drop range across the air terminal device. The total required inlet static pressure is this drop plus the downstream resistance. Record the static pressure drop across the air terminal device and the inlet static pressure. These readings should be within the required range. Verify that the air terminal device will operate at maximum flow when the inlet static pressure to the air terminal device is within the proper operating range by reading out the downstream air outlet devices. · Proportionally balance all air outlet devices. · Test the VA v air terminal device for both maximum and minimum flow as applicable. Consult the manufacturer recommendations Inc. ASHRAE, 2019 user. single for Licensed | {}
7e133fcd-d605-4342-8701-307fe492c31f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Testing, Adjusting, and Balancing 39.13 on the proper procedure for setting velocity controllers if re- quired. Include both quantities on the report. · Measure and record the final total airflow rate that velocity tra- verses in the hot and cold ducts with system set for maximum cold duct airflow. · Measure and record the data required in Section 8.4 (b), (c), (f), (g), and (1), plus the duct static pressure sensed by the static pres- sure probe for automatic control of supply duct pressure existing when fan is at design flow rate. · Reset all controls for normal operation. · At the completion of balancing, - The inlet manual damper to at least one VA v air terminal de- vice on each branch duct will be fully open. . At least one damper in each branch duct will be fully open. - Reset the system - to normal operating conditions. Laboratory Testing and Balancing: The first three steps are written as for laboratories where room pressure is negative. The exhaust and supply airflow percentages will switch when the laboratories are designed to be positive pressure. · For each fume hood, verify by pitot tube traverse that the airflow is between 100 and 1 10% of design. Design airflow is the volume of exhaust that produces the required face velocity at sash opening (i.e., face velocity area). · For each laboratory balance, the supply airflow should be be- tween 90 and 100% of design. Avoid any direct velocity from the ceiling diffuser toward the fume hoods. Verify airflow measure- ments by establishing correction factors from pitot tube traverses. · Balance the general exhaust system airflow to between 100 and 110% of design. When flow hoods are used to measure general exhaust airflow rates, care should be taken when reading multiple exhaust grilles that the flow hood does not add restriction, forcing the air to another exhaust grille. · After the correct airflow for the hood has been established and all exhaust and supply air systems have been balanced, verify that the face velocities do not fall below the design face velocity as directed by the safety officer. Face velocities should be taken at equal areas as described in ASHRAE Standard 110. · Make a sketch of the tested hood indicating each face velocity, the sash opening dimensions (height, width, and area), the position of the internal baffles, the traversed airflow rate, the laboratory room number, and exhaust system number. After the face velocities have been determined to be within the established limits, observe smoke flows into the hood to determine that no reverse flows are present. · A sticker indicating the inspection test result should be placed on the side of the hood, at the maximum sash height measured, indi- cating (1) height of sash (in mm), (2) average velocity (m/s), (3) highest velocity (m/s), (4) lowest velocity (m/s, (5) person per- forming the test, and ⑥ date of test. Note in the sketch that all face readings are for reference only. The flow is established by pitot tube traverse. At the present time, there is no way to take the average velocity multiplied by the face area to determine total flow. Each velocity-measuring instrument will require different correction factors, and these corrections are often different for different size hoods of the same type. If the hood does not pass this requirement a caution tag must be placed on the sash. The caution tag should be a fluorescent orange tag stating that the hood does not meet specified flow requirements, with the date. Tracking the laboratory control can be done in the following manner by establishing airflows for each air terminal device: · All hood sashes open, minimum cooling. · All hood sashes closed, minimum cooling. · All hood sashes closed, maximum cooling. · Note velocity at the door during the preceding steps. · Identify the point at which the hood face velocity falls below its target velocity. (Any time a minimum airflow is set, the hood will track linearly until it reaches the minimum airflow point; face velocity will then increase). · Indicate flows on a drawing of the laboratory at maximum and minimum conditions and velocities (to be posted at the door). · Track the entire exhaust system from maximum to minimum flow by observing the static pressure entering the most remote hood exhaust air terminal device and the exhaust fan static pressure controller maintains set point. · Track the entire supply system from maximum flow to minimum flow, observing the static pressure entering the most remote sup- ply air terminal device. The supply air static pressure controller maintains set point. Report Information To be of value to the consulting engineer and owner's mainte- nance department, the air-handling report should consist of at least the following items: 1. Design · Air quantity to be delivered · Fan static pressure · Motor power installed or required · Percent of outdoor air under minimum conditions · Fan speed · Input power required to obtain this air quantity at design static pressure 2. Installation · Equipment manufacturer (indicate model and serial numbers) · Size of unit installed · Arrangement of air-handling unit · Nameplate power and voltage, phase, cycles, and full-load amperes of installed motor 3. Field tests · Fan speed · Power readings (voltage, amperes of all phases at motor termi- nals) · Total pressure differential across unit components · Fan suction and fan discharge static pressure (equals fan total pressure) · Plot of actual readings on manufacturer's fan performance curve to show the installed fan operating point · Measured airflow rate It is important to establish initial static pressures accurately for the air treatment equipment and duct system so that the vari- ation in air quantity caused by filter loading can be calculated. It enables the designer to ensure that the total air quantity is never less than the minimum requirements. Because the design air quantity for peak loading of the filters has already been cal- culated, it also serves as a check of dirt loading in coils. 4. Terminal Outlets · Outlet by room designation and position · Manufacture and type · Size (using manufacturer's designation to ensure proper factor) · Manufacturer's outlet factor (where no factors are available, or field tests indicate listed factors are incorrect, a factor must be determined in the field by traverse of a duct leading to a single outlet); this also applies to capture hood readouts [see ASH- RAE Standard 1 1 1]) · Adjustment pattern for every air outlet Inc. ASHRAE, 2019 user. single for Licensed | {}
4e244fcb-8f7e-4763-9d15-7a2775edb8d1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 39.14 2019 ASHRAE Handbook-HVAC Applications (SI) 5. Additional Information (if applicable) · Air-handling units - Belt number and size - Drive and driven sheave size - Belt position on adjusted drive sheaves (bottom, middle, and top) · Motor speed under full load - Motor heater size - Filter type and static pressure at initial use and full load; time to replace - Variations of velocity at various points across face of coil · Existence of vortex or discharge dampers, or both · Distribution system - Unusual duct arrangements · Branch duct static readings in double-duct and induction system - Ceiling pressure readings where plenum ceiling distribution is used; tightness of ceiling - With wind conditions outdoor less than 2.2 m/s, relationship of building to outdoor pressure under both minimum and maximum outdoor air · Induction unit manufacturer and size (including required air quantity and plenum pressures for each unit) and test plenum pressure and resulting primary air delivery from manufacturer's listed curves · All equipment nameplates visible and easily readable Many independent firms have developed detailed procedures suitable to their own operations and the area in which they function. These procedures are often available for information and evaluation on request. 6. BALANCING HYDRONIC SYSTEMS Testing, adjusting, and balancing of hydronic systems has one core principle for functionality: conditioned water (fluid) must be provided to the heat transfer device (coil) so that at design condi- tions 97% of the coil heat transfer is achieved, while not allowing flow to have a larger tolerance than ±1 0% of design flow. Itis at part load that the designer must take care to assure that a similar type of performance is attainable if desired. Many designers make the assumption that at part load a system will stay balanced. This implies proportionality, which is only ensured if all connected sys- tem terminals have the same head loss with respect to the pump. This can, and does, vary based on the type of device used to make adjustments. The condition also varies based on how other devices that affect system flow and head are operated; specifically, variable- speed pumping can have a major impact on how well fluid gets where it is intended by a distribution system at design and part load. When other design options (e.g., diversity) are used, and where the pump (and possibly the piping system) are not sized to provide connected flow load as based on the required design flow rate for each connected terminal, the designer must analyze the system flow under varying load and control conditions and specify a sequence and methodology of test, with expected results, to ensure system operation. The evolution of system design criteria to incorporate higher t, reduce required flow rates, and incorporate advanced con- trol strategies (e.g., variable-speed pumping) has increased the sen- sitivity of the system to slight variations from design. This necessitates additional calculation and analysis to achieve the com- fort and energy efficiency conditions required, while protecting the system from potential hazards (e.g., mold growth) and that might in part be affected by a lack of performance in the system operation. This should not imply that there was or is anything wrong with the fundamentals of earlier system design and field adaptation. Those fundamentals provide the basis to apply design principles with modern knowledge, for efficient, well-operated systems. The rela- X-Axis: Design FLOW, % Y-Axis: Design Heat Transfer, % Chart Type: line Discharge Air Temp At = 22 K item_01 66.7% 55.6% Fig. 1 Effects of Flow Variation on Heat Transfer from Hydronic Terminal X-Axis: Design Ex Y-Axis: Design Flow, % Chart Type: line Heating Cooling 10°C 14°C 60°C 82°C 104°C 127°C 150°C item_01 60% 70% 80% 70% 60% 75% 80% 85% 90% Fig. 2 Percent of Design Flow Versus Design t to Maintain 90% Terminal Heat Transfer for Various Supply Water Temperatures tionship between flow and heat transfer is at the root of this under- standing. Heat Transfer at Reduced Flow Rate The traditional heating-only hydronic terminal (90°C, 11 K t) gradually reduces heat output as flow is reduced (Figure 1 ). Decreasing waterflow to 20% of design reduces heat transfer to 65% of that at full design flow. The control valve must reduce waterflow to 10% to reduce heat output to 50%. This relative insen- sitivity to changing flow rates is because the governing coefficient for heat transfer is the air-side coefficient; a change in internal or water-side coefficient with flow rate does not materially affect the overall heat transfer coefficient. This means (1) heat transfer for water-to-air terminals is established by the mean air-to-water tem- perature difference, (2) heat transfer is measurably changed, and (3) a change in mean water temperature requires a greater change in waterflow rate. Figure 1 shows the relationship between water-side design criteria and heat transfer. The coil was selected for an entering water temperature of 82°C, and design water temperature drops tofll K and 33 K. The design exit air temperature of the coil is 50°C. Note that with waterflow twice that of design, there is a reasonable amount of temperature difference to indicate overflow. Acceptable industry practice has been to allow for only 10% overflow, and in that case a 20° t coil yields a negligible increase in heat transfer (101%) and an equally tough to measure 0.42 K change in departing air temperature. Sim- ilarly, the coil with 60° thas only 104% of design heat transfer with a 2° increase in leaving air temperature. The designer should not Inc. ASHRAE, 2019 user. single for Licensed | {}
2e6c4577-e898-468b-b9f8-d64d2933398f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Testing, Adjusting, and Balancing 39.15 assume that a temperature control system will be able to adequately control any overflows based on sensing the increase in temperature. Though possible if great care is taken to match the control valve to the coil and tune the control loop for proper control, more often than not, this is rarely attained in implementation. Tests ofhydronic coil performance show that when flow is throt- tled to the coil, the water-side differential temperature of the coil increases with respect to design selection. This applies to both con- stant-volume and variable-volume air-handling units. In constantly circulated coils that control temperature by changing coil entering water temperature, decreasing source flow to the circuit decreases the water-side differential temperature. A secondary concern applies to heating terminals. Hot water can be supplied at a wide range of temperatures. Inadequate heating capacity caused by actual conditions varying from design or insuf- ficient flow can sometimes be overcome by raising supply water temperature. Designs below the 120°C limit (ASME Boiler and Pressure Vessel Code) often add enhanced flexibility to make this adjustment if there is adequate source capacity. Figure 2 shows the flow variation when 90% terminal capacity is acceptable. Note that heating tolerance decreases with temperature and flow rates and that chilled-water terminals are much less toler- ant of flow variation than hot-water terminals. A third concern also needs to be considered when dual-tempera- ture heating/cooling hydronic systems are employed. These systems are sometimes first started during the heating season. Adequate heating ability in the terminals may suggest that the system is bal- anced. However, when operated in cooling mode, capacity may vary greatly from that required. Figure 2 shows that 40% of design flow through the terminal provides 90% of design heating with 60°C sup- ply water and a 5 K temperature drop. Increased supply water tem- perature establishes the same heat transfer at terminal flow rates of less than 40% design. Sometimes, dual-temperature water systems have decreased flow during the cooling season because of chiller pressure drop; this could cause a flow reduction of 25%. For example, during the cooling season, a terminal that heated satisfactorily would only receive 30% of the design flow rate. Although the example of reduced flow rate at t = 10 K only affects heat transfer by 10%, this reduced heat transfer rate may have the following negative effects: · Object ofthe system is to deliver (or remove) heat where required. When flow is reduced from design rate, the system must supply heating or cooling for a longer period to maintain room tempera- ture. · As load reaches design conditions, the reduced flow rate is unable to maintain room design conditions. · Control valves with average range ability (30:1) and reasonable authority ( = 0.5) may act as on/off controllers instead of throt- tling flows to the terminal. The resultant change in riser friction loss may cause overflow or underflow in other system terminals. Attempting to throttle may cause wear on the valve plug or seat because of higher velocities at the vena contracta of the valve. In extreme situations, cavitations may occur. Table 1 Load Flow Variation ¦ Load Type ¦ % Design Flow at 90% Load ¦ Other Load, Order of % ¦ Other Load, Order of % ¦ Other Load, Order of % ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Load Type ¦ % Design Flow at 90% Load ¦ Sensible ¦ Total ¦ Latent ¦ ¦ Sensible ¦ 65 ¦ 90 ¦ 84 ¦ 58 ¦ ¦ Total ¦ 75 ¦ 95 ¦ 90 ¦ 65 ¦ ¦ Latent ¦ 90 ¦ 98 ¦ 95 ¦ 90 ¦ Note: Dual-temperature systems are designed to chilled flow requirements and often operate on a 5 K temperature drop at full-load heating. Terminals with lower water temperature drops have greater tol- erance for unbalanced conditions. However, larger waterflows are necessary, requiring larger pipes, pumps, and pumping cost. System balance becomes more important in terminals with a large temperature difference. Less waterflow is required, which reduces the size of pipes, valves, and pumps, as well as pumping costs. A more linear emission curve gives better system control. If flow varies by more than 5% at design flow conditions, heat transfer can fall off rapidly, ultimately causing poorer control of the wet- bulb temperature and potentially decreasing system air quality. Heat Transfer at Excessive Flow Increasing the flow rate above design in an effort to increase heat transfer requires careful consideration. Figures 1 and 3 both show that increasing the flow to 200% of design only increases heat transfer by 6 to 20%. However, the excess flow increases resistance or pressure drop four times and, more importantly, energy draw by a factor of eight using the cube of the original power (from the pump laws). Generalized Chilled Water Terminal: Heat Transfer Versus Flow Heat transfer for a typical chilled-water coil in an air duct versus waterflow rate is shown in Figure 4. The curves are based on AHRI rating points: 7.2°C inlet water at a 5.6 K rise with entering air at 26.7°C db and 19.4°C wb. The basic curve applies to catalog ratings for lower dry-bulb temperatures providing a consistent entering-air moisture content (e.g., 24°C db, 18°C wb). Changes in inlet water temperature, temperature rise, air velocity, and dry- and wet-bulb temperatures cause terminal performance to deviate from the curves. Figure 4 is only a general representation and does not apply to all chilled-water terminals. Comparing Figure 4 with Figure 1 indicates the similarity of nonlinear heat transfer and flow for both the heating and cooling terminals. Table 1 shows that if the coil is selected for the load and flow is reduced to 90% ofload, three flow variations can satisfy the reduced load at various sensible and latent combinations. Note that the reduction in flow will not maintain a chilled-water design differen- tial when coil velocity drops below 0.5 m/s. This affects chiller loading and unloading. 옹 OUTPUT, HEAT Chart Type: line 0 50 100 150 200 250 item_01 0% 80% 100% 105% 110% 110% Fig.3 Typical Heating-Coil Heat Transfer v ersus w ater Flow Inc. ASHRAE, 2019 user. single for Licensed | {}
ef211e59-171b-46cc-a769-ee9fe2fc8c33 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 39.16 2019 ASHRAE Handbook- -HVAC Applications (SI) X-Axis: Design FLOW, % Y-Axis: Total Heat Transfer, % Chart Type: line 0 20 40 60 80 100 item_01 20% 40% 60% 80% 90% 100% X-Axis: Design FLOW, % Y-Axis: Temperature Rise °C Chart Type: line (0) (20) (40) (60) (80) (100) item_01 12°C 11°C 9°C 8°C 6°C 5°C Fig. 4 Chilled Water Terminal Heat Transfer Versus Flow The coil characteristic shown in Figure 5 is for air that is always recirculated within a space, such as in a fan-coil. Another common (but nonstandard) approach in chilled-water systems is for airflow volume across the coil to vary according to load. Static pressure in the supply duct is controlled by VA v box dampers opening and closing, and some percentage of outdoor air is introduced at enter- ing conditions. With these control modifications, the coil starts to appear more linear, depending on air turndown (determined by load) and variations in dry- and wet-bulb temperatures of the air being introduced. In some cases, as sensible design conditions are approached, reasonable variance in wet-bulb temperature can sig- nificantly change heat transfer across the coil. If enthalpy is the con- trol set point, fluid flow may vary by 40% or more of design at the same entering dry-bulb temperature. These common characteristics make fluid flow measurement of a coil (rather than using surrogate indicators such as water-side t) important in indicating the system balance. Flow Tolerance and Balance Procedure The design procedure rests on a design flow rate and an allow- able flow tolerance. The designer must define both the terminal's flow rates and feasible flow tolerance, remembering that the cost of balancing rises with tightened flow tolerance. Any overflow increases pumping cost, and any flow decrease reduces the maxi- mum heating or cooling at design conditions. Water-Side Balancing Minimum Design Requirements for Hydronic System Instal- lation. Given the effect of flow on heat transfer, comfort, and energy efficiency, each coil must have some form of verifiable flow mea- surement to enable measurement and verification to properly verify system operation (even if no adjustments are planned). Tradition- ally, this function was performed by balancing valves, and the required performance was communicated in the written specifica- tion and in schematic drawings like the one shown in Figure 6. X-Axis: Design FLOW, % Y-Axis: Design Heat Transfer, % Chart Type: line Water Sensible Latent Water-side at K Total Air item_01 30% 33% 3.3% 4.4% 5.6% 8.9% Fig. 5 Chilled Water Terminal Heat Transfer v ersus Flow for VAV Unit with 20% Outdoor Air ![image](/image/placeholder) 2-WAY ATC VALVE EXCEPT WHERE 3-WAY MIXING VALVES THERMOMETER (TYPICAL) ARE SHOWN ON PLANS REDUCER (TYPICAL) MANUAL AIR VENT (TYPICAL) BALANCE VALVE NC BALL VALVE OR BUTTERFLY NO VALVE (TYPICAL) * RETURN PROVIDE BYPASS LINE WITH BALANCE VALVE ON 3-WAY VALVE INSTALLATION SUPPLY UNION (TYPICAL) STRAINER WITH BLOW-OFF 19 mm DRAIN VALVE WITH THREADED HOSE CONNECTION Fig. 6 Example of Coil Schematic The example is not meant to endorse any particular method of control or specification. For example, having thermometers entering and leaving the coil is a nice feature, especially when work- ing on large coils and air-handling units. However, most terminal unit coils (e.g., fan-coils, terminal reheat coils) serving a small tem- perature control zone have flow rates of 0.03 to 0.63 L/s, and there are many coils. In that instance, the expense of thermometers is not justified. Alternatively, a measurement device could be installed that allows for the insertion and removal of a temperature sensor into the fluid stream to make a measurement. Note that many fittings and devices are shown. It is very common to find specialty devices installed as an alternative to the specification drawing at the request of the installer, with the object of providing functional performance while increasing the installation efficiency. Typically these are Inc. ASHRAE, 2019 user. single for Licensed | {}
47cbc015-66f6-4758-a4c2-2c170b414da7 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Testing, Adjusting, and Balancing 39.17 ![image](/image/placeholder) AIR VENT ACCESSORY UNION P/T MEASUREMENT PORT BALL VALVE, UNION TAIL AND DRAIN DRAIN VALVE Fig. 7 Typical Coil Kit Components called hook-up kits or coil kits and are installed with the TAB device and the control valve. Figure 7 shows the three most common types of devices applied; note that the market can drive subtle variances of their design. There are a few things that are important in applying these devices: · They should be described in detail in the written specification and shown on the drawings with the required features called out. These devices are not specifically covered by manufacturing stan- dards such as MSS or ANSI standards as other valves and fittings are, and that leaves much open to interpretation. · Note the required quantity and placement of pressure or tempera- ture (P/T) measurement ports and the minimum required quantity ofauxiliary mounting locations (e.g., the strainer valve, which has a P/T port installed, as well as a strainer blowdown and drain valve; in addition, it has a larger auxiliary port for assistance in piping the three-way valve bypass, as well as several alternative ports for relocation of the P/T, additional P/T ports, or other devices that might fit within the constraints of the thread size). · The devices should specifically be checked for their specific application as a balance device. The devices shown in Figure 7 are all auxiliary piping devices. They provide the functions of shutoff valves, strainers, pressure, and temperature measurement loca- tions or other functions, but they do not provide the calibration of a balancing device for flow measurement or if required adjust- ment. Balancing devices are distinct, and while the balancing device may serve the purpose of a shutoff valve for one side of the coil (based on code or performance requirements), the auxiliary device does not serve this purpose unless specifically designed to do so. Balancing Devices. Traditional balancing valves are of two basic styles: static or dynamic. In addition, a simple flow measure- ment device such as an orifice or venturi could serve the same func- tion, but these are often integrated into the balance valve Static Balance Valves. Varieties exist for both operation and mea- surement. This valve is typically set to a position by a technician and does not self-adjust in operation. Typically, the simplest type of valve has a throttling device able to measure pressure entering and exiting the throttling orifice. Manufacturers publish the perfor- mance data associated with the valve using a standardized valve test, such as ISA Standard 75.02.01, with adjustment to compensate for the valve design and measurement points. In this manner, the bal- ancing device uses a variable orifice for flow calculation based on the orifice flow coefficient cv at the operating position. This device generally provides an acceptable flow measurement when wide open, but if care is not exercised to carefully match the differential pressure measurement device range to the flow coefficient of the valve, flow accuracy declines as the valve is closed. A modified type of static valve uses a fixed orifice for flow cal- culation combined with a variable orifice for flow adjustment. The fixed orifice may be a simple orifice, venturi profile, or nozzle. Vari- able orifice measurement requires knowing where the device is set to calculate flow, which may require having to adjust a measure- ment device each reading. The fixed orifice, on the other hand, does not change each reading, thus giving a direct readout on flow if the measurement device incorporates this calculation and the measure- ment range is adequate for the measured flow. Remember the square relationship of flow to pressure drop: if 0.06 L/s is being measured at a pressure drop of 6.9 kPa, then reducing the flow to half gives a measured pressure drop of 1.7 kPa. These pressures can become quite small, and finding the proper range sensor is difficult unless care is taken in sizing and design to allow for enough pressure drop to calculate a reasonably accurate flow. Measuring at design flow is important and should be relatively easy to accomplish. However, if the intent is to check the system at part load, especially at flows less than 50% of design, this must be taken into account when selecting the design pressure drop for the measurement device, to make sure the signal is of enough magnitude as to be measurable by the avail- able devices. The built-in benefit ofa static balancing valve is that, when prop- erly field adjusted, all system flow paths have the same head loss (the same as the design head loss calculated for the selection of the pump). This system is therefore proportionally balanced; if flow is too great, all circuits have the same overflow, and if flow is too small, all circuits receive the same percentage of flow. This can be highly advantageous for some system designs. Note that in a system that is properly proportionally balanced, at least one of the balancing valves will be open, providing only the pressure drop required to provide an adequate differential pressure signal for flow calculation. There are no parasitic head losses in the system, because all paths have the same head loss, and maximum flow is limited, reducing flow to only that of design, thus saving pump motor power and energy. Dynamic Devices (Automatic Flow Limiters). The process of adjusting the maximum flow in a circuit can be expensive or labo- rious, but there will be varying differential pressures at each branch that cause excessive flows at design, especially when control valves are selected with little care for required pressure drop at the point of system application. The dynamic device incorporates a system- powered regulator to either vary the open orifice area to keep no more than a specific set point flow, or control the differential pres- sure across a fixed orifice to accomplish the same function. Like all regulators, these devices rely on machined control areas and engi- neered springs to set a specific range of operation, and therefore exhibit proportional control ofthe regulator for the flow, but not pro- portional regulation of the controlled system (as does the static valve). Typically, these valves operate over a fixed range of differ- ential pressure (e.g., 14 to 220, 14 to 415, or 35 to 415 kPa [differ- ential]). A drawback is that these valves do not definitively know the position, and thus the flow coefficient, where the regulator is oper- ating. They also often do not allow for the correct pressures to estab- lish flow. As a result, these devices cannot be used to measure flow at the design condition, and the manufacturer's statement of flow must be taken at face value. Performance is generally reasonable, but there are occasions when suspended construction material can obstruct the working apparatus, blocking flow and giving no indi- cation that there is an issue. It is recommended that when these types of devices are installed, a properly sized fixed orifice device be installed to allow for positive flow measurement. Pressure Regulators. Regulators are some of the earliest auto- matic control devices, using various materials and approaches to Inc. ASHRAE, 2019 user. single for Licensed | {}
95dbd464-62bd-457c-81da-5f34b436cb60 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 39.18 2019 ASHRAE Handbook-HVAC Applications (SI) control specific processes. For example, the simple bimetallic ele- ment, which has two physically bonded strips of metal with different coefficients of expansion and contraction, is harnessed into the ther- mostat, so that when the element heats or cools, the corresponding physical movement of the element actuates a switch or provides con- trol of air pressure to actuate a damper motor or valve. For TAB, sys- tem water pressure is directed to both sides of a diaphragm-operated actuator, to open or close a valve. Using a spring on the actuator, a specific pressure set point can be controlled for either a static or dif- ferential pressure; by adding other system-powered devices, this basic function can be turned into a flow regulator or other type of control element. Use of regulators on hydronic systems is returning to popularity, with widespread application of variable-speed pumping and designs that attempt to recreate proportional control. (The application of variable speed pumping will be handled sepa- rately.) A differential pressure regulator is typically used, and it is applied either as an independent device across an individual branch, a temperature control valve, or a multiterminal branch. A subset of P regulators is the pressure-independent control valve, which incorporates the P regulator into the body of the temperature con- trol valve to control the pressure drop across the control orifice. In that specific application, whenever system differential pressure at the point of the controlled valve exceeds the regulator pressure set point, the fixed P set point is kept constant. This mimics the same conditions applied when a TC control valve is given the standard flow capacity test, and consequently the valve characteristic is maintained without deviation, because of system hydraulics. The regulator P is normally less than the pressure drop across the valve assembly as prescribed by the flow capacity test. Manufac- turers normally state the controlled range of flow of the valve and the operating P range, and often of the regulator. If the manufacturer states a specific flow coefficient Av for the valve, this should imply the entire assembly's pressure drop per the standard test method. Whether these devices can be used for flow measurement or verifi- cation varies with manufacturer. In some cases, manufacturers pro- vide the ability to measure pressure drop across some portion of the valve. It is common to designate three critical pressures: P1 (upstream pressure), P2 (regulator pressure), and P3 (downstream pressure). If only P1 and P3 are measurable, flow verification cannot be performed because the drop around the controlled orifice is unknown. If P2 and P3 are known and the flow coefficient for the applied position is known (published), it may be possible to verify flow. Some manufacturers incorporate fixed-flow orifices specifi- cally for flow verification. Similar to automatic flow limiters, it is recommended that when these types of devices are installed, a prop- erly sized fixed orifice device be installed (ifnot included in the valve assemblage) to allow positive flow measurement. Normal Instrumentation for Field Measurement Hydronic system measurement tools can be categorized by func- tion: electrical (to deal with pumps), pressure and differential pres- sure (to establish system settings, pressure losses, and calculate flow rates), temperature (to establish performance levels), and direct-flow instruments (e.g., a strap-on instrument such as a dop- pler effect type of meter to measure flow directly). In addition, it is useful to apply thermal imagers and vibration analyzers when testing for improper operation and, if the TAB technician is desig- nated to perform alignments, an alignment analyzer. Electrical Measurements. As a result of the wide application of variable-speed drives to pumps, both a portable oscilloscope and a digital multimeter with required test probes and safety gear and pro- cedures are required to take reasonable and repeatable measure- ments and establish power use. The oscilloscope is required to measure the voltage and current leaving the drive to the motor and entering the motor and check for imbalance. There are several other measurements that are useful but may not be part of the designated TAB technician 's responsibility. The majority of motors applied to large commercial systems are three-phase motors, and when attached to a speed drive, the fre- quency of the drive operation is too fast for a digital multimeter. In addition, both the scope and the digital multimeter (DMM) should incorporate a low-pass filter to filter out high frequencies associated with the drive. Note the instrument manufacturer, model, and whether the device includes a low-pass filter measurement docu- mentation. If readings are taken by other technicians at a later time, using meters without the low-pass filter, there may be substantial difference in the reported measurement when no difference actually exists. Because of the function of the drive, voltage measurements can be significantly greater than the nominal 480 V assumed to being measured. Instruments should be rated for 750 to 1000 V to be safe. Analog meters are unacceptable for making these measure- ments because they lack the required electrical protections and capability to handle power transients. Note that power analyzers may not be substituted for oscilloscopes. Power analyzers are designed to measure supply power lines, but are incapable of mea- suring drive output power because of the frequencies encountered. The oscilloscope also allows for checking (1) drive setup for output versus load; (2) whether there are overvoltage reflections on the line, which could cause motor winding damage; (3) motor shaft voltages; (4) bearing currents, which can cause fluting of the bear- ing raceway leading to excess vibration and noise and ultimately leading to reduced motor life; and (5) if there is motor leakage cur- rent, which can interfere with control system data acquisition and communications. The digital multimeter is inadequate for many of these measurements, though there are other measurements for which it is very appropriate. Regardless, it too should have the low pass filter to deal with any high frequencies which could lead to errors in measurement. Pressure Measurement. A broad variety of gages, transmitters, and digital meters exist for the purposes of pressure and differential pressure measurement. The use of the tube-filled manometers was the traditional standard of care, however the indicating fluid was mercury (now a banned substance), so these should never be seen in field application. Most commonly applied still would appear to be a basic mechanical, diaphragm separated dial gage, the device could also be liquid filled. In some cases these might be advantageous due to the inherent simplicity of the device, but what is important is care- fully matching the gage range to the expected range of reading, and to ensuring that overpressurization does not influence or damage the gage. The most common problem of the field application of these types of devices is that a user will apply a gage with a reading of 0 to 300 kPa on a device providing a signal in the range of0 to 2.5 kPa. Digital manometers are also used. In these units, a semiconduc- tor differential pressure sensor or matched pair of gage pressure sen- sors is used, with either electronic analog circuitry or an application-specific microprocessor to convert the electrical signal from the sensor into usable data by the technician. In many cases, the manufacturers will apply some user adaptability to enter field data that might display the differential pressure, and convert that sensed value to a calculated flow. In other cases, the applied micro- processor has a far greater set of operations, from device databases to instructional methods on making system adjustments. Most important to the balancing process is that an accurate, precise, and appropriate range sensor is applied to the measurement device, and that it is properly compensated for temperature of the working fluid. All sensing devices rely on some electrical interpretation of the physical movement of an object (e.g., diaphragm) in response to changing pressure. The same technologies that are applied to free- standing sensors used in the control process are also applied in the test instrumentation used by balancers. Digital manometers should minimally offer a capability of zeroing the sensor and electrical Inc. ASHRAE, 2019 user. single for Licensed | {}
6a9ae961-43d4-4a06-a6bc-a4b6db241a7e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Testing, Adjusting, and Balancing 39.19 signal before measurement of the test specimen, and may also offer connection methods to the test specimen that balance the pressure across the device until reading to prevent sensor damage, and ensure that the physical connection device (e.g., tubes) are filled with liquid and vented of air. Test instruments should be regularly checked against a traceable reference standard; allow for regular calibration as required. Temperature Measurement. Careful system design should always allow for a sensor to be placed directly into a fluid stream, not externally mounted to the pipe. There are a wide variety of mechanical temperature sensing methodologies, such as the tradi- tional liquid-filled thermometer, and bimetallic or vapor-filled ele- ments with a calibrated dial indicator or electronic sensing through RTD, thermistor, or other type of sensing element. Electronic sens- ing also implies semiconductor devices and implementations that can be quite small, allowing for the carrying or sheathing element to be equally small: the tube that carries the physical sensing device and wires can be diametrically as small as a hypodermic needle (1.5 mm diameter), or the more traditional instant-read type of dial indi- cator probe, which is slightly greater than 3.6 mm in diameter. Probe size should be checked to ensure that it can be injected into the fluid stream as far as possible (as this may be restricted by entry point). Temperature instruments should be regularly checked against a traceable reference standard, and allow for regular calibration as required and capable. Less commonly applied, and appropriate for specific applica- tions, are thermographic imagers, which may be handheld and have digital imaging. Though inappropriate for direct fluid temperature measurement, they are invaluable for extra measurements such as showing the face of a heat transfer coil or to indicate faulty points of insulation. On devices such as pumps, they can provide valuable data on motor and bearing operation. Flow Sensing. The noninvasive flow sensor typically uses a form of ultrasonic detection to establish flow on the interior of a pipe. This is a nontraditional instrument in balancing for several reasons, including setup time and the data required to translate the signal into waterflow. However, in certain application instances, such as mea- suring main distribution piping, there can be value in spot checking flow rates. In all of these device categories, there is a wide variety of other technologies which may be applied, especially when those applica- tions are permanent to system operation. However, it is this perma- nence that makes them less applicable to field testing for TAB. A fluid flow turbine meter may be very good for getting a flow mea- surement, but adding and then removing the device to the fluid stream (aside from the piping complications) also substantively changes the system pressure drop and flow rate, making the overall readings and adjustments less accurate. This should be accounted for in design. If there are specific devices that the designer feels are more appropriate to the goals that they wish to accomplish, specific mechanical installation techniques and equipment should be incor- porated into the design to accommodate those measurements. For example, a removable section of piping could allow for physical checking of the interior pipe surfaces to ensure accuracy for an ul- trasonic device. Expect sensing errors, and the associated error in rational units (e.g. P into volume-per-unit-time flow). Expect that, when the accounting is complete, a gross reading at one point in the system will not be the same as all the individual unit flows when added. When attempting to establish the validity of the reported numbers, it may be necessary to recheck not only the installed devices but also the pipes and fittings. Expect problems, and provide simple logical points of measurement opportunity that allow the anomaly to be traced until satisfaction can be established with the data. Anecdotal evidence supports the necessity of these precautions. In a 60 story office tower in Chicago, it was known for years that the chilled-water system did not seem to work right and that, in particu- lar, the pumps did not develop the required system flow. After check- ing all of the installed devices, the building owners eventually installed extra measurement points that allowed enough data to be taken to track anomalies. Eventually, these measurements led to a specific section of pipe. The system was shut down for maintenance, drained, and the suspect pipe was cut open only to find it stuffed with tubes of conduit. Apparently the electrician thought it was a conve- nient storage spot during construction, and the pipefitters never rec- ognized that it was a mistake, not some form of flow straightener in the pipe, welding it in. These types of errors can (and do) occur with regularity. Catching errors such as this is not the purpose ofTAB, but the principles of TAB measurements can be used to address func- tional problems, as well as the normal system hydraulics. System Calculation and Specification Water-side balancing adjustments should be made with a thor- ough understanding of piping friction loss calculations and mea- sured system pressure losses. It is good practice to show expected losses of pipes, fittings, and terminals, and expected pressures in operation on schematic system drawings (as recommended in ASHRAE Standard 111). Designers often use schematic drawings to provide functional representation of a system design, in addition to the dimensional piping plans associated with the building layout drawings. It is suggested that one of these schematics be drawn in a flat connection or ladder-type diagram, as shown in Figure 8. Con- ceptually, the schematic allows main distribution paths, branch con- nections, major devices, and the pump, without any piping lines crossing. The drawing serves several purposes: allowing all paths and various system interactions to be easily seen, evaluating oppor- tunities for reverse or gravity flows, easily translating to a spread- sheet for sizing and analysis calculations, quickly and efficiently establishing the required balance adjustments and identifying dif- ferences between installed versus design differences (done by the TAB technician), and establishing and communicating more detailed sequences of operation for the control system. The power of commonly available spreadsheets allows designers to create a straightforward calculation procedure that is easily veri- fiable by the firm using it. The spreadsheet approach also allows analysis to be performed while sticking to the basics of a system operating at the intersection of its pump and system curves. The accuracy of these methods is reasonably good, and the implementa- tion complexity can be left to the designer of the spreadsheet. For example, to achieve a higher degree of precision in the calculations for fittings, the spreadsheet can account for the influences of geo- metric plane interaction (as shown by ASHRAE research and detailed in the 2017 ASHRAE Handbook-Fundamentals). How- ever, if this is ofless concern, the spreadsheet can implement some- thing as simple as K factors or fitting TEL. Using Figure 8 as an example, a simple spreadsheet was established to provide design analysis, shown in Figure 9. The spreadsheet allows calculation ofthe system flow coefficient (analogous to a valve flow coefficient Cv, and outlined in Chapter 47 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment) for showing how various branches will operate. In any pumped piping system, the system will operate at the intersection of the pump and system curve. The system curve is a composite of many system curves, which represent all of the individual paths of water- flow in the system. Each individual path flow coefficient is an indi- rect sum of the individual component (pipe, fittings, valves, coils, etc.) flow coefficients which may be either implied from calculation or tested under standard test procedures. The math of the spreadsheet is expressed through algebraic rear- rangement of the basic flow equation: Inc. ASHRAE, 2019 user. single for Licensed | {}
a8e8fef3-b07c-4d59-a45a-c3546f2ac926 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 39.20 2019 ASHRAE Handbook HVAC Applications (SI) ![image](/image/placeholder) A B 1 1 1 SEGMENT 2 3 2 3 2 3 2 3 FLOW RATE 8 7 6 5 4 3 2 1 PIPE FRICT. SIZE RATE ■ LENGTH FRICTION 5 4 5 4 5 4 5 4 LOSS 6 6 6 6 H F E Fig. 8 Example of Flat System Schematic Drawing and Labeling for Devices 2 = Cv or 용 = P and Pis h P (1) Given that the system head loss in a closed-loop hydronic system is the total of the single largest path s head loss of pipe, fittings, etc., the sum of the head losses can be rearranged into the requisite com- ponents of flow and flow coefficient as shown. As the flow is the same in all paths, the term drops out and an equation that can be solved for the system flow coefficient from the components is real- ized. 2 2 2 2 용 = 용 + 용 + 용 Tot Pipe Coil Elbows 2 2 2 + 2 8, + gv 옹 + 온 Tees Gate Bal Cont 1 1 1 1 + + (2) CV-Tot CV-Pipe Cv-Coil CV-Elbow 1 1 1 1 + + + + Cv-Tee Cv-Gate CV-Bal Cv-Cont 1 1 1 1 + + + CV-Tot Cv-1 Cv-2 C V-n Each individual segment in a flow path will have a path flow rate equal to the design flow rate of the served heat transfer device, and the unique or shared head loss in a segment for that flow. For instance, Coil Path 3 has a flow rate of 100, but the distribution pip- ing segment A-B has a design flow 800 for all eight circuits (only three are shown in Figure 9) and design head loss of 4.03. Using hydronic design principles, all paths see the bulk head loss, and the pump must provide enough energy to overcome these losses, so cal- culation of the path flow coefficient is as shown in the equation above. All that is being illustrated is the addition of the head losses in each flow path, but doing so as the X form of the equation, the flow divided by the flow coefficient squared. Parallel-path flow coefficients are simply additive, and when used to develop a system curve, they can be plotted to a specific pump curve and the intersection point calculated. This allows for the requirements of the first pass of system adjustment to be determined. Note that there will be differences in actual measured pressures and those calculated. In keeping with the Bernoulli principles, when fittings and devices are fitted to an installed system, they do not always behave in a perfectly theoretical way. Sometimes there are greater or fewer losses of a combined device, influenced by changes in velocity head and velocity head recovery and exhibited in things like the vicinity of a change in flow direction, and changes in the X, Y, and Z planes of the pipe. These losses can only be tested for, and examples of these influences are demonstrated in ASHRAE research project RP-968 (Rahmeyer 1998) (partially published in Tables 3, 4, and 5 and Figures 2 and 3 in Chapter 22 of the 2017 ASHRAE Handbook-Fundamentals). However, this should not be used as a reason not to calculate. The first step should always be to have a more rational quantitative approach by which to direct and decide. One of the by-products of this type of analysis is the calculation of control valve authority, or the authority of any device used to throttle flow. Simply put, valve authority is the ratio of control valve pressure drop to the maximum pressure drop of the system that it serves. For a constant-speed pump, P maximum is the pump head, in a variable-speed pumping system, the pressure drop P maximum is the controlled set-point pressure for the pump speed controller The indexing number offers a simple indication of how the valve will perform, but is fairly useless for calculating what the flow would be. However, treated as flow coefficients, the equivalent system flow coefficient is determined as follows. Cv-1 Cv-2 = CV-SYST 2 2 N Cv-2 + Cv-1 When the system flow coefficient is calculated for each valve position's flow coefficients, the deviation of a given valve's flow control characteristic may be graphically shown. Figure 10 shows the graphical result for a modified equal-percentage valve at various valve authorities. In the field there may be deviations from this, though the deviation has also been seen in operating systems. Through application of this method of analysis, the effects of bal- ancing the system can be demonstrated for relative effect. It has been anecdotally maintained that application of balancing valves degrades control valve performance, and an example shows this to be partially true, with an unbalanced valve having 22% authority, compared to the same circuit balanced, which has 16%. If the con- trol valve completely opens, under the applied pump differential of 200 kPa, that is higher than that required for the design flow. (3) Inc. ASHRAE, 2019 user. single for Licensed | {}
56b24570-7605-4dd4-bbd6-9bb66982900b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Testing, Adjusting, and Balancing 39.21 ¦ CIRCUIT 1 ¦ A ¦ B ¦ C ¦ D ¦ 1-2 ¦ 2-3 ¦ COIL ¦ ATC VALVE ¦ BAL VALVE ¦ 4-5 ¦ 5-6 ¦ E ¦ F ¦ G ¦ H ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ FLOW ¦ 100 ¦ 100 ¦ 100 ¦ 100 ¦ 100 ¦ 100 ¦ 100 ¦ 100 ¦ 100 ¦ 100 ¦ 100 ¦ 100 ¦ 100 ¦ 100 ¦ 100 ¦ ¦ ¦ ¦ PIPE SIZE ¦ 6 ¦ 5 ¦ 5 ¦ 4 ¦ 4 ¦ 3 ¦ ¦ 2 ¦ ¦ 3 ¦ 4 ¦ 4 ¦ 5 ¦ 5 ¦ 6 ¦ ¦ ¦ ¦ FRICTION ¦ 4.03 ¦ 5.87 ¦ 2.71 ¦ 2.27 ¦ 2.27 ¦ 2.39 ¦ ¦ ¦ ¦ 2.39 ¦ 2.27 ¦ 2.27 ¦ 5.87 ¦ 2.71 ¦ 4.03 ¦ ¦ ¦ ¦ LENGTH ¦ 100 ¦ 100 ¦ 100 ¦ 100 ¦ 50 ¦ 50 ¦ ¦ ¦ ¦ 100 ¦ 100 ¦ 100 ¦ 100 ¦ 50 ¦ 50 ¦ ¦ ¦ ¦ HEAD LO55 ¦ 4.03 ¦ 5.87 ¦ 2.71 ¦ 2.27 ¦ 1.135 ¦ 1,195 ¦ 15 ¦ 10.82 ¦ 2.31 ¦ 2.39 ¦ 2.27 ¦ 2.27 ¦ 5.87 ¦ 1.355 ¦ 2.015 ¦ ¦ ¦ ¦ CV ¦ 75.7 ¦ 62.7 ¦ 92.3 ¦ 100.9 ¦ 142.7 ¦ 139.0 ¦ 39.2 ¦ 46.2 ¦ 100.0 ¦ 98.3 ¦ 100.9 ¦ 100.9 ¦ 62.7 ¦ 130.6 ¦ 107.1 ¦ ¦ PATH Cv ¦ ¦ 1/CV2 ¦ 0.0001745 ¦ 0.0002541 ¦ 0.0001173 ¦ 9.827E-05 ¦ 4.913E-05 ¦ 5.173E-05 ¦ 0.0006494 ¦ 0.0004685 ¦ 0.0001 ¦ 0.0001035 ¦ 9.827E-05 ¦ 9.827E-05 ¦ 0.0002541 ¦ 5.866E-05 ¦ 8.723E-05 ¦ 0.0026629 ¦ 19.378683 ¦ ¦ CIRCUIT 2 ¦ A ¦ B ¦ C ¦ D ¦ 1-2 ¦ 2-3 ¦ COIL ¦ ATC VALVE ¦ BAL VALVE ¦ 4-5 ¦ 5-6 ¦ E ¦ F ¦ G ¦ H ¦ ¦ ¦ ¦ FLOW ¦ 100 ¦ 100 ¦ 100 ¦ 100 ¦ 100 ¦ ¦ 100 ¦ 100 ¦ 100 ¦ ¦ 100 ¦ 100 ¦ 100 ¦ 100 ¦ 100 ¦ ¦ ¦ ¦ PIPE SIZE ¦ 6 ¦ 5 ¦ 5 ¦ 4 ¦ 4 ¦ ¦ ¦ 2 ¦ ¦ ¦ 4 ¦ 4 ¦ 5 ¦ 5 ¦ 6 ¦ ¦ ¦ ¦ FRICTION ¦ 4.03 ¦ 5.87 ¦ 2.71 ¦ 2.27 ¦ 2.27 ¦ ¦ ¦ ¦ ¦ ¦ 2.27 ¦ 2.27 ¦ 5.87 ¦ 2.71 ¦ 4.03 ¦ ¦ ¦ ¦ LENGTH ¦ 100 ¦ 100 ¦ 100 ¦ 100 ¦ 50 ¦ ¦ ¦ ¦ ¦ ¦ 100 ¦ 100 ¦ 100 ¦ 50 ¦ 50 ¦ ¦ ¦ ¦ HEAD LO55 ¦ 4.03 ¦ 5.87 ¦ 2.71 ¦ 2.27 ¦ 1.135 ¦ ¦ 15 ¦ 10.82 ¦ 2.31 ¦ ¦ 2.27 ¦ 2.27 ¦ 5.87 ¦ 1.355 ¦ 2.015 ¦ ¦ ¦ ¦ CV ¦ 75.7 ¦ 52.7 ¦ 92.3 ¦ 100.9 ¦ 142.7 ¦ ¦ 39.2 ¦ 46.2 ¦ 100.0 ¦ ¦ 100 9 ¦ 100.9 ¦ 52.7 ¦ 130.6 ¦ 107.1 ¦ ¦ PATH Cv ¦ ¦ 1/CV2 ¦ 0.0001745 ¦ 0.0002541 ¦ 0.0001173 ¦ 9:827E-05 ¦ 4,913E-05 ¦ ¦ 0.0006494 ¦ 0 .0004685 ¦ 0.0001 ¦ ¦ 9.827E-05 ¦ 9.827E-05 ¦ 0.0002541 ¦ 5.866E-05 ¦ 8.723E-05 ¦ 0.0025077 ¦ 19.969333 ¦ ¦ CIRCUIT 3 ¦ A ¦ B ¦ C ¦ D ¦ 1-2 ¦ 2-3 ¦ COIL ¦ ATC VALVE ¦ BAL VALVE ¦ 4-5 ¦ 5-6 ¦ E ¦ F ¦ G ¦ H ¦ ¦ ¦ ¦ FLOW ¦ 100 ¦ 100 ¦ 100 ¦ ¦ 100 ¦ 100 ¦ 100 ¦ 100 ¦ 100 ¦ 100 ¦ 100 ¦ ¦ 100 ¦ 100 ¦ 100 ¦ ¦ ¦ ¦ PIPE SIZE ¦ 6 ¦ 5 ¦ 5 ¦ ¦ 4 ¦ 3 ¦ ¦ 2 ¦ ¦ 3 ¦ 4 ¦ ¦ 5 ¦ 5 ¦ 6 ¦ ¦ ¦ ¦ FRICTION ¦ 4.03 ¦ 5.87 ¦ 2.71 ¦ ¦ 2.27 ¦ 2.39 ¦ ¦ ¦ ¦ 2.39 ¦ 2.27 ¦ ¦ 5.87 ¦ 2.71 ¦ 4.03 ¦ ¦ ¦ ¦ LENGTH ¦ 100 ¦ 100 ¦ 100 ¦ ¦ 50 ¦ 50 ¦ ¦ ¦ ¦ 100 ¦ 100 ¦ ¦ 100 ¦ 50 ¦ 50 ¦ ¦ ¦ ¦ HEAD LO55 ¦ 4.03 ¦ 5.87 ¦ 2.71 ¦ ¦ 1.135 ¦ 1.195 ¦ 15 ¦ 10.82 ¦ 2.31 ¦ 2.39 ¦ 2.27 ¦ ¦ 5.87 ¦ 1,355 ¦ 2.015 ¦ ¦ ¦ ¦ CV ¦ 75.7 ¦ 62.7 ¦ 92.3 ¦ ¦ 142.7 ¦ 139.0 ¦ 39.2 ¦ 45.2 ¦ 100.0 ¦ 98.3 ¦ 100.9 ¦ ¦ 62.7 ¦ 130.6 ¦ 107.1 ¦ ¦ PATH Cv ¦ ¦ 1/CV2 ¦ 0.0001745 ¦ 0.0002541 ¦ 0.0001173 ¦ ¦ 4.913E-05 ¦ 5.173E-05 ¦ 0.0006494 ¦ 0.0004685 ¦ 0.0001 ¦ 0.0001035 ¦ 9.827E-05 ¦ ¦ 0.0002541 ¦ 5.866E-05 ¦ 8.723E-05 ¦ 0.0024663 ¦ 20.136005 ¦ Fig. 9 Example Spreadsheet Though perfect for the most significant path that the pump was selected for, unbalanced and closer to the pump there will be about 15% overflow. This is shown in Figure 10, based on the example. This overflow is very likely not to be recognized by the valves tem- perature controller, and the beginning result is that there will be excess pump energy used until the controller is able to respond and reduce flow. For the controls technician, adjusting the proportional setting is harder. In the extreme, controller hunting will occur, con- tinuously opening and closing the valve, over and underflowing. Balancing the poorly sized control valve at reduces the maximum opening overflow. Reduced flow at this condition saves pump energy. Tuning the control loop, however, can only be fixed by selecting the temperature control valve with a better valve authority, which means more design pressure drop, and indirectly increases the design pump head. From the perspective of cost, reducing flow always saves oper- ating expense (relatively). The use of a balancing device will gen- erally save 10 to 15% (more for systems that have paid little or no attention to the hydronic system details, or that have pumps that pro- vide more head than absolutely required) of the pump energy. Poor control valve authority has a larger energy penalty than balancing maximum flow, because the tuning that is possible leads to valves that generally react to disturbances sooner than the load requires (more flow at load), and at each valve position, more flow is deliv- ered than would be indicated by the characteristic. Pumping costs can be significantly reduced by being able to maintain control valve characteristic (on the order of 50%) with even more energy when considering the operation cost of the source energy provider. In that regard, applying hydronic design options, such as properly zoned secondary pumping, zone differential pressure control, or pressure- independent control valves (PICV) for zone pressure control adds operating benefit. Per CSI Standard 2305.93, TAB specification requires direct section implementation of equipment, procedures, and specialists. In addition, coordination should be noted in sections on controls, pumps, any installation sections, etc. Hydronic systems should be tested by direct flow measurement. This method is accurate because it deals with system flow as a func- % FLOW, VALVE Chart Type: line VAIVE LIFT HOW SYSTEM FLOW CHANGES VALVE CHARACTERISTIC item_01 70% 10% 90% Fig. 10 System Flow and Valve Characteristics tion of differential pressures, and avoids compounding errors intro- duced by temperature difference procedures. To achieve this, each circuit should have some form of inexpensive yet accurate producer of differential pressure related to flow, such as the pre- viously outlined static balancing valve, or a small venturi or ori- fice measuring station. This requirement could also be a direct reading sensor (as these prices reach competitive levels, or the importance of the measured path requires). Measuring flow at each terminal enables verification of the system operation and, where required, proportional balancing. It also allows matching pump head and flow to actual system requirements and reducing excess flows by trimming the pump impeller or reducing pump speed. Often, reducing pump operating cost pays for the cost of water-side balancing. Inc. ASHRAE, 2019 user. single for Licensed | {}
29c6ad01-5f30-4915-bf23-91a56da1c669 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 39.22 Equipment Proper equipment selection and preplanning are needed to suc- cessfully balance hydronic systems. Circumstances sometimes dic- tate that flow, temperature, and pressure be measured. The designer must specify the waterflow balancing devices and measurement points for installation during construction and use in testing during hydronic system measurement and adjustment. In addition, the designer is well served by specifying the minimum acceptable level for test equipment, which should include full-scale range and accu- racy and required calibration. In so specifying, simplicity should be the order of the day. Temperature sensors should be able to fit into the specified measurement ports. Pressure and differential pressure sensing devices should be capable of providing accuracy that, when converted to system flow, falls within the specified tolerance for flow adjustment. Note that (as typical ofall HVAC equipment) there is a broad range of implementation for specific instrumentation devices. Record Keeping Balancing requires accurate record keeping while making field measurements. Dated and signed field test reports help the designer or customer in work approval, and the owner has a valuable refer- ence when documenting future changes. Sizing Balancing Valves and Flow Measurement Devices Flow measurement devices and balancing valves are placed in the system to measure flow and, where required, adjust waterflow to a terminal, branch, zone, riser, or main. These should be located on the leaving side of the hydronic branch, following the temperature control valve and prior to isolation or service valves. General branch layout is from takeoff to entering service valve and strainer, then to the coil, control valve, and balancing/service valve. Pressure is thereby left on the coil, helping keep dissolved air in solution and preventing false balance problems resulting from collected air and improper pressure references. An improper but commonly applied sizing method is to select the valve or device for line size. These devices should be selected to pass design flows when near or at their fully open position with the differential pressure required to accurately represent flow for the measurement range desired. Although a small pressure drop may allow determination of design flow, it should be remembered that measurements will almost always be taken at reduced flows. The square relationship between flow and head will greatly reduce the available differential pressure for measurement. If a minimum dif- ferential pressure of 7 kPa is used for sizing, measurement at 50% design flow means measured P will be 1.8 kPa; conversely, twice the flow will be a drop of28 kPa. This factors into the practical and available instrumentation used in field measurement. If a manufac- turer publishes a minimum accuracy of 0.5 kPa} and it was desired to read a flow of 0.06 L/s with an uncorrected valve flow coefficient of 1, then a 7 kPa drop would produce that reading at 0.02 L/s, or ±30%. If the designer is specifying a flow tolerance of ±10%, then sizing of devices and matching them to instrumentation become very important. A bare minimum 7 kPa pressure drop is suggested; more pressure drop for basic measurements is recommended. Many balancing valves and measuring meters give an accuracy of ±5% of range down to a pressure drop of 3 kPa with the balancing valve wide open. Too large a balancing valve pressure drop affects the per- formance and flow characteristic of the control valve. Too small a pressure drop affects its flow measurement accuracy as it is closed to balance the system. Equation (5) may be used to determine the flow coefficient Av for a balancing valve or to size a control valve. The flow coefficient Av is defined as the number of cubic metres per second that flows through a wide-open valve with a pressure drop of 1 Pa. This is shown as 2019 ASHRAE Handbook-HVAC Applications (SI) Q = A P (4) where 0 = design flow for terminal or valve, m3/s = density of fluid, kg/m3 SG = specific gravity of fluid P = pressure drop across valve, Pa The inch-pound equivalent of Av is Cv, measured in gallons per minute; Cv can be converted by the following factor: Av =24 10-6 Cv (5) 7. HYDRONIC BALANCING METHODS Various techniques are used to balance hydronic systems. Bal- ance by temperature difference and water balance by proportional method are the most common. Preparation. Minimally, preparation before balancing should include collecting the following: 1. Pump submittal data; pump curves, motor data, etc. 2. Starter sizes and overload protection information 3. Control valve Av ratings and temperature control diagrams 4. Chiller, boiler, and heat exchanger information; flow and head loss 5. Terminal unit information; flow and head loss data 6. Pressure relief and reducing valve setting 7. Flowmeter calibration curves 8. Other pertinent data System Preparation for Static System 1. Examine piping system: Identify main pipes, risers, branches and terminals on as-built drawings. Check that flows for all bal- ancing devices are indicated on drawings before beginning work. Check that design flows for each riser equal the sum of the design flows through the terminals. 2. Examine reducing valve 3. Examine pressure relief valves 4. Examine expansion tank 5. For pumps, confirm · Location and size · Vented volute · Alignment · Grouting · Motor and lubrication · Nameplate data · Pump rotational direction 6. For strainers, confirm · Location and size · Mesh size and cleanliness 7. Confirm location and size of terminal units 8. Control valves: · Confirm location and size · Confirm port locations and flow direction · Set all valves open to coil · Confirm actuator has required force to close valve under loaded conditions Inc. ASHRAE, 2019 user. single for Licensed 9. Ensure calibration of all measuring instruments, and that all calibration data are known for balancing devices 10. Remove all air from piping; all high points should have air vents Pump Start-Up 1. Start pump and confirm rotational direction; if rotation is incor- rect, have corrected. 2. Read differential head and apply to pump curve to observe flow approximates design. | {}
12b6663e-5bcd-4257-8d98-ddbe3d6fecb8 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Testing, Adjusting, and Balancing 39.23 3. Slowly close pump (if pump is under 20 kW) throttle valve to shutoff. Read pump differential head from gages. · If shutoff head corresponds with published curve, the previ- ously prepared velocity head correction curve can be used as a pump flow calibration curve. · A significant difference between observed and published shut- off head can be caused by an unvented volute, a partially plugged impeller, or by an impeller size different from that specified. Confirmation of System Venting 1. Confirm tank location and size. 2. Shut off pump; record shutoff gage pressure at tank junction. 3. Start pump and record operating pressure at tank junction. 4. Compare operating to shutoff pressures at tank junction. If there is no pressure change, the system is air-free. 5. Eliminate free air. · No air separation: Shut off pump and revent. Retest and revent until tank junction pressure is stable. · Air separation: Operate system until free air has been sepa- rated out, indicated by stable tank junction pressure. Balancing For single-, multiple-, and parallel pump systems, after pump start-up and confirmation of system venting, 1. Adjust pump throttle until pump head differential corresponds to design. 2. Record pump motor voltage and amperage, and pump strainer head, at design flow. 3. Balance equipment room piping circuit so that pumped flow remains constant over alternative flow paths. 4. Record chiller and boiler circuits (for multiple-pump systems, requires a flowmeter installed between header piping). For multiple-pump systems only, 5. Check for variable flow in source circuits when control valves are operated. 6. Confirm · Pump suction pressure remains above cavitations range for all operating conditions. · Pump flow rates remain constant. · Source working pressures are unaffected. For parallel-pump systems, follow steps (1) to (4), then shut off pumps alternately and 7. Record head differential and flow rate through operating pump, and operating pump motor voltage and current. 8. Confirm that operational point is satisfactory (no overload, cav- itation potential, etc.). Balance by Temperature Difference This common balancing procedure is based on measuring the water temperature difference between supply and return at the ter- minal. The designer selects the cooling and/or heating terminal for a calculated design load at full-load conditions. At less than full load, which is true for most operating hours, the temperature drop is proportionately less. Figure 11 demonstrates this relationship for a heating system at a design t of 10 K for outdoor design of -20°C and room design of 20°C. For every outdoor temperature other than design, the balancing technician should construct a similar chart and read off the t for balancing. For example, at 50% load, or -1°C outdoor air, the t required is 5 K, or 50% of the design drop. This method is a rough approximation and should not be used where great accuracy is required. It is not accurate enough for cooling systems. Chart Type: line -20 -15 -10 -5 0 5 10 15 20 item_01 80°C 80°C 70°C 60°C 50°C 40°C 30°C 20°C 10°C Fig. 11 Water Temperature Versus Outdoor Temperature Showing Approximate Temperature Difference Water Balance by Proportional Method Preset Method. A thorough understanding of the pressure drops in the system riser piping, branches, coils, control valves, and bal- ancing valves is needed. Generally, several pipe and valve sizes are available for designing systems with high or low pressure drops. A flow-limiting or trim device will be required. Knowing system pres- sure losses in design allows the designer to select a balancing device to absorb excess system pressures in the branch, and to shift pres- sure drop (which might be absorbed by a balancing device nearly close to achieve balance) to the pipes, coils, and valves so the bal- ancing device merely trims these components' performance at design flow. It may also indicate where high-head-loss circuits can exist for either relocation in the piping network, or hydraulic isola- tion through hybrid piping techniques. The installed balancing device should never be closed more than 40 to 50%; below this point flow reading accuracy falls to 20 to 30%. Knowing a starting point for setting the valve (preset) allows the designer to iterate system piping design. This may not always be practical in large systems, but minimizing head and flow saves energy over the life of the facility and allows for proper temperature control. In this method, 1. Analyze the piping network for the largest hydraulic loss based on design flow and pipe friction loss. The pump should be selected to provide the total of all terminal flows, and the head required to move water through the hydraulically greatest cir- cuit. Balance devices in this circuit should be sized only for the loss required for flow measurement accuracy. Trimming is not required. 2. Analyze differences in pressure drop in the pumping circuit for each terminal without using a balancing device. The difference between each circuit and the pump head (which represents the drop in the farthest circuit) is the required drop for the balancing device. 3. Select a balancing device that will achieve this drop with mini- mum valve throttling. If greater than two pipe sizes smaller, shift design drop into control valve or coil (or both), equalizing pres- sure drop across the devices. 4. Monitor system elevations and pressure drops to ensure air man- agement, minimizing pocket collections and false pressure ref- erences that could lead to phantom balancing problems. 5. Use proportional balancing methods as outlined for field testing and adjustment. Inc. ASHRAE, 2019 user. single for Licensed | {}
8cd6bfe4-4b5c-4edd-85ae-f547499e61cd | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 39.24 Proportional Balancing Proportional water-side balancing may use design data, but relies most on as-built conditions and measurements and adapts well to design diversity factors. This method works well with multiple-riser systems. When several terminals are connected to the same circuit, any variation of differential pressure at the circuit inlet affects flows in all other units in the same proportion. Circuits are proportionally balanced to each other by a flow quotient: Actual flow rate Flow quotient Design flow rate (6) To balance a branch system proportionally, 1. Fully open the balancing and control valves in that circuit. 2. Adjust the main balancing valve for total pump flow of 100 to 110% of design flow. 3. Calculate each riser valve's quotient based on actual measure- ments. Record these values on the test form, and note the circuit with the lowest flow quotient. Note: When all balancing devices are open, flow will be higher in some circuits than others. In some, flow may be so low that it cannot be accurately measured. The situation is complicated because an initial pressure drop in series with the pump is necessary to limit total flow to 100 to 110% of design; this decreases the available dif- ferential pressure for the distribution system. After all other risers are balanced, restart analysis of risers with unmeasurable flow at step (2). Identify the riser with the highest flow ratio. Begin balancing with this riser, then continue to the next highest flow ratio, and so on. When selecting the branch with the highest flow ratio, · Measure flow in all branches of the selected riser. · In branches with flow higher than 150% of design, close the bal- ancing valves to reduce flow to about 110% of design. · Readjust total pump flow using the main valve. · Start balancing in branches with a flow ratio greater than or equal to 1. Start with the branch with the highest flow ratio. Inc. ASHRAE, 2019 user. single for Licensed The reference circuit has the lowest quotient and the greatest pressure loss. Adjust all other balancing valves in that branch until they have the same quotient as the reference circuit (at least one valve in the branch should be fully open). When a second valve is adjusted, the flow quotient in the refer- ence valve also changes; continued adjustment is required to make their flow quotients equal. Once they are equal, they will remain equal or in proportional balance to each other while other valves in the branch are adjusted or until there is a change in pressure or flow. When all balancing valves are adjusted to their branches' respec- tive flow quotients, total system waterflow is adjusted to the design by setting the balancing valve at the pump discharge to a flow quo- tient of 1. Pressure drop across the balancing valve at pump discharge is produced by the pump that is not required to provide design flow. This excess pressure can be removed by trimming the pump impel- ler or reducing pump speed. The pump discharge balancing valve must then be reopened fully to provide the design flow. As in variable-speed pumping, diversity and flow changes are well accommodated by a system that has been proportionately bal- anced. Because the balancing valves have been balanced to each other at a particular flow (design), any changes in flow are propor- tionately distributed. Balancing the water side in a system that uses diversity must be done at full flow. Because components are selected based on heat transfer at full flow, they must be balanced to this point. To accom- plish full-flow proportional balance, shut off part of the system while balancing the remaining sections. When a section has been 2019 ASHRAE Handbook- -HVAC Applications (SI) balanced, shut it off and open the section that was open originally to complete full balance of the system. When balancing, care should be taken if the building is occupied or if load is nearly full. Variable-Speed Pumping. To achieve hydronic balance, full flow through the system is required during balancing, after which the sys- tem can be placed on automatic control and the pump speed allowed to change. After the full-flow condition is balanced and the system differential pressure set point is established, to control the variable- speed pumps, observe the flow on the circuit with the greatest resis- tance as the other circuits are closed one at a time. The flow in the observed circuit should remain equal to, or more than, the previously set flow. Waterflow may become laminar at less than 0.6 m/s, which may alter the heat transfer characteristics of the system. Other Balancing Techniques Flow Balancing by Rated Differential Procedure. This pro- cedure depends on deriving a performance curve for the test coil, comparing water temperature difference tw to entering water tem- perature tew minus entering air temperature tea. One point of the desired curve can be determined from manufacturer's ratings, which are published as (tew - tea). A second point is established by observing that the heat transfer from air to water is zero when (tew - tea) is zero (consequently, tw = 0). With these two points, an approximate performance curve can be drawn (Figure 12). Then, for any other (tew - tea), this curve is used to determine the appropriate tw. The basic curve applies to catalog ratings for lower dry-bulb temperatures, providing consistent entering air moisture content (e.g., 24°C db, 18°C wb). Changes in inlet water temperature, tem- perature rise, air velocity, and dry- and wet-bulb temperatures cause terminal performance to deviate from the curves. The curve may also be used for cooling coils for sensible transfer (dry coil). Flow Balancing by Total Heat Transfer. This procedure deter- mines waterflow by running an energy balance around the coil. From field measurements of airflow, wet- and dry-bulb temperatures up- and downstream of the coil, and the difference tw between entering and leaving water temperatures, waterflow can be determined by the following equations: AIR Qw = Q/4180 tw ENTERING = 1.20�a(h1 - h2) 9 cooling MINUS WATER ENTERING (7) (8) X-Axis: WATER TEMPERATURE DIFFERENTIAL (Mt.) Y-Axis: Elevation (m.) Chart Type: line 0 1 2 3 4 5 6 7 8 item_01 0Elevation (m.) 0Elevation (m.) 10Elevation (m.) 20Elevation (m.) 30Elevation (m.) 40Elevation (m.) 50Elevation (m.) 60Elevation (m.) 70Elevation (m.) Fig. 12 Coil Performance Curve | {}
83972d15-b47f-4910-bb56-44d196956c95 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Testing, Adjusting, and Balancing 39.25 qheating = 1.23�g(t1 - t2) (9) where ¦ Qw = ¦ waterflow rate, L/s ¦ ¦ --- ¦ --- ¦ ¦ 9 = ¦ load, W ¦ ¦ qcooling = ¦ cooling load, W ¦ ¦ qheating = ¦ heating load, W ¦ ¦ Qa = ¦ airflow rate, L/s ¦ ¦ h = ¦ enthalpy, kJ/kg ¦ ¦ t = ¦ temperature, °C ¦ Example 1. Find the waterflow for a cooling system with the following characteristics: Test data ¦ tewb ¦ = entering wet-bulb temperature = 20.3°C ¦ ¦ --- ¦ --- ¦ ¦ tlwb ¦ = leaving wet-bulb temperature = 11.9°C ¦ ¦ Qa ¦ = airflow rate = 10 000 L/s ¦ ¦ tlw ¦ = leaving water temperature = 15.0°C ¦ ¦ tew ¦ = entering water temperature = 8.6°C ¦ From psychrometric chart h1 = 76.52 kJ/kg h2 = 52.01 kJ/kg Solution: From Equations ⑤ and (6), 1.20 10 000 76.52 - 52.01 Qw = 11.0 L/s 4180 15.0 - 8.6 The desired waterflow is achieved by successive manual adjust- ments and recalculations. Note that these temperatures can be greatly influenced by the heat of compression, stratification, bypassing, and duct leakage. General Balance Procedures All the variations ofbalancing hydronic systems cannot be listed; however, the general method should balance the system and mini- mize operating cost. Excess pump pressure (operating power) can be eliminated by trimming the pump impeller. Allowing excess pressure to be absorbed by throttle valves adds a lifelong operating- cost penalty to the operation. The following is a general procedure based on setting the balance valves on the site: 1. Develop a flow diagram if one is not included in the design draw- ings. Illustrate all balance instrumentation, and include any addi- tional instrument requirements. 2. Compare pumps, primary heat exchangers, and specified termi- nal units, and determine whether a design diversity factor can be achieved. 3. Examine the control diagram and determine the control adjust- ments needed to obtain design flow conditions. Balance Procedure: Primary and Secondary Circuits 1. Inspect the system completely to ensure that (1) it has been flushed out, it is clean, and all air is removed; (2) all manual valves are open or in operating position; (3) all automatic valves are in their proper positions and operative; and (4) the expan- sion tank is properly charged. 2. Place controls in position for design flow. 3. Examine flow diagram and piping for obvious short circuits; check flow and adjust the balance valve. 4. Take pump suction, discharge, and differential pressure read- ings at both full and no flow. For larger pumps, a no-flow con- dition may not be safe. In any event, valves should be closed slowly. 5. Read pump motor amperage and voltage, and determine ap- proximate power. 6. Establish a pump curve, and determine approximate flow rate. 7. If a total flow station exists, determine the flow and compare with pump curve flow. 8. If possible, set total flow about 10% high using the total flow station first and the pump differential pressure second; then maintain pumped flow at a constant value as balance proceeds by adjusting the pump throttle valve. 9. Any branch main flow stations should be tested and set, start- ing by setting the shortest runs low as balancing proceeds to the longer branch runs. 10. With primary and secondary pumping circuits, a reasonable balance must be obtained in the primary loop before the second- ary loop can be considered. The secondary pumps must be run- ning and terminal units must be open to flow when the primary loop is being balanced, unless the secondary loop is decoupled. 8. FLUID FLOW MEASUREMENT Flow Measurement Based on Manufacturer's Data Any component (terminal, control valve, or chiller) that has an accurate, factory-certified flow/pressure drop relationship can be used as a flow-indicating device. The flow and pressure drop may be used to establish an equivalent flow coefficient as shown in Equation (3). According to the Bernoulli equation, pressure drop varies as the square of the velocity or flow rate, assuming density is constant: 02 02 = h1/ h2 (10) For example, a chiller has a certified pressure drop of 80 kPa at 10 L/s. The calculated flow with a field-measured pressure drop of 90 kPa is Q2 = 10 V 90 80 = 10.6 L/s (11) Flow calculated in this manner is only an estimate. The accuracy of components used as flow indicators depends on the accuracy of (1) cataloged information concerning flow/pressure drop relation- ships and (2) pressure differential readings. As a rule, the compo- nent should be factory-certified flow tested if it is to be used as a flow indicator. Pressure Differential Readout Gages or digital differential pressure manometers are used to read differential pressures. Accurate readout is diminished when two separate devices are used, especially when the two are gages that are permanently mounted. When applying a single pressure gage for differential readout, follow the example of Figure 13. This gage should be alternately valved to the high- and low-pressure side to establish the differential. A single gage needs no static height cor- rection, and excess coordinated errors caused by disparate gage cal- ibration are eliminated. ![image](/image/placeholder) VALVED TAP POINTS SINGLE GAGE CHILLER OR OTHER SYSTEM FLOW DEVICE (TERMINAL, BOILER ETC.) GAGE VALVES Fig. 13 Single Gage for Reading Differential Pressure Inc. ASHRAE, 2019 user. single for Licensed | {}
3ff0543f-67cc-4405-87ec-88c05ffb3c6f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 39.26 2019 ASHRAE Handbook- -HVAC Applications (SI) Differential pressure can also be read from differential gages, thus eliminating the need to subtract outlet from inlet pressures to establish differential pressure. Differential pressure gages are usually dual gages mechanically linked to read differential pressure. Conversion of Differential Pressure to Head Gages may be calibrated to metres of fluid head, which, histori- cally, refers to the height of water above a point in the fluid circuit. Head is a function of density and is related to pressure by the hydro- static law as h = pl g (12) where h = fluid head, m p = pressure, Pa = density, kg/m3 g = standard force of gravity = 9.806 65 N/kg Because the calibration only applies at one density (typically at a standard temperature of 15°C), the reading of head may require cor- rection when the gage is applied to high-temperature water with a significantly lower density. The relationship between head and pressure as a function of density is shown in Table 2. Table 2 Differential Pressure Conversion to Head ¦ Fluid Density, kg/m3 ¦ Approximate Corresponding Water Temperature, °C ¦ Metre Fluid Head Equal to 1 kPa* ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 1500 ¦ ¦ 0.680 ¦ ¦ 1400 ¦ ¦ 0.0728 ¦ ¦ 1300 ¦ ¦ 0.0784 ¦ ¦ 1200 ¦ ¦ 0.0850 ¦ ¦ 1100 ¦ ¦ 0.0927 ¦ ¦ 1000 ¦ 10 ¦ 0.1020 ¦ ¦ 980 ¦ 65 ¦ 0.104 ¦ ¦ 960 ¦ 95 ¦ 0.106 ¦ ¦ 940 ¦ 125 ¦ 0.108 ¦ ¦ 920 ¦ 150 ¦ 0.111 ¦ ¦ 900 ¦ 170 ¦ 0.113 ¦ ¦ 800 ¦ ¦ 0.127 ¦ ¦ 700 ¦ ¦ 0.146 ¦ ¦ 600 ¦ ¦ 0.170 ¦ ¦ 500 ¦ ¦ 0.204 ¦ *Differential kPa readout is multiplied by this number to obtain metres fluid head when gage is calibrated in kPa. X-Axis: FLOW RATE, L/s Y-Axis: METRES HEAD Chart Type: line PUMP CURVE INDEPENDENT OF DENSITY FALSE FLOW TRUE FLOW FALSE HEAD item_01 30METRES 7.6METRES 5.4METRES 25METRES Fig. 14 Fluid Density Correction Chart for Pump Curves For example, a manufacturer may test a boiler control valve with 40°C water. Differential pressures from another test made in the field at 120°C may be correlated with the manufacturer's data by using Equation (8) to account for the density differences of the two tests. When differential heads are used to estimate flow, a density correc- tion must be made because of the shape of the pump curve. For example, in Figure 15 the uncorrected differential reading for pumped water with a density of900 kg/m3 is 25 m; the gage conver- sion was assumed to be for water with a density of 999 kg/m3. The uncorrected or false reading gives a 40% error in flow estimation. Differential Head Readout with Manometers Manometers are used for differential pressure readout, especially when very low differentials, great precision, or both, are required. But manometers must be handled with care; they should not be used for field testing because fluid could blow out into the water and rap- idly deteriorate the components. A proposed manometer arrange- ment is shown in Figure 15. Figure 15 and the following instructions provide accurate manometer readings with minimum risk of blowout. 1. Make sure that both legs of manometer are filled with water. 2. Open purge bypass valve. 3. Open valved connections to high and low pressure. 4. Open bypass vent valve slowly and purge air here. 5. Open manometer block vents and purge air at each point. 6. Close needle valves. The columns should zero in if the manom- eter is free of air. If not, vent again. 7. Open needle valves and begin throttling purge bypass valve slowly, watching the fluid columns. Ifthe manometer has an ade- quate available fluid column, the valve can be closed and the dif- ferential reading taken. However, ifthe fluid column reaches the top of the manometer before the valve is completely closed, insufficient manometer height is indicated and further throttling will blow fluid into the blowout collector. A longer manometer or the single gage readout method should then be used. An error is often introduced when converting millimetres of gage fluid to the pressure difference (in kilopascals) of test fluid. The conversion factor changes with test fluid temperature, density, or both. Conversion factors shown in Table 2 are to a water base, and the counterbalancing water height H (Figure 15) is at room temperature. ![image](/image/placeholder) BYPASS PURGE BYPASS VALVE VENT VALVE NEEDLE NEEDLE VALVE VALVE VENT MERCURY H BLOWOUT COLLECTOR WATER GAGE FLUID Fig. 15 Fluid Manometer Arrangement for Accurate Reading and Blowout Inc. ASHRAE, 2019 user. single for Licensed | {}
9b8d415e-9427-4595-b823-a0347ea0a556 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Testing, Adjusting, and Balancing 39.27 Orifice Plates, Venturi, and Flow Indicators Manufacturers provide flow information for several devices used in hydronic system balance. In general, the devices can be classified as (1) orifice flowmeters, (2) venturi flowmeters, (3) velocity impact meters, (4) pitot-tube flowmeters, (5) bypass spring impact flowme- ters, (6) calibrated balance valves, (7) turbine flowmeters, and (8) ultrasonic flowmeters. The orifice flowmeter is widely used and is extremely accurate. The meter is calibrated and shows differential pressure versus flow. Accuracy generally increases as the pressure differential across the meter increases. The differential pressure readout instrument may be a manometer, differential gage, or single gage. The venturi flowmeter has lower pressure loss than the orifice plate meter because a carefully formed flow path increases velocity head recovery. The venturi flowmeter is placed in a main flow line where it can be read continuously. Velocity impact meters have precise construction and calibra- tion. The meters are generally made of specially contoured glass or plastic, which allows observation of a flow float. As flow increases, the flow float rises in the calibrated tube to indicate flow rate. Veloc- ity impact meters generally have high accuracy. A special version of the velocity impact meter is applied to hy- dronic systems. This version operates on the velocity pressure dif- ference between the pipe side wall and the pipe center, which causes fluid to flow through a small flowmeter. Accuracy depends on the location of the impact tube and on a velocity profile that corre- sponds to theory and the laboratory test calibration base. Generally, the accuracy of this bypass flow impact or differential velocity pressure flowmeter is less than a flow-through meter, which can op- erate without creating a pressure loss in the hydronic system. The pitot-tube flowmeter is also used for pipe flow measure- ment. Manometers are generally used to measure velocity pressure differences because these differences are low. The bypass spring impact flowmeter uses a defined piping pressure drop to cause a correlated bypass side branch flow. The side branch flow pushes against a spring that increases in length with increased flow. Each individual flowmeter is calibrated to relate extended spring length position to main flow. The bypass spring impact flowmeter has, as its principal merit, a direct readout. However, dirt on the spring reduces accuracy. The bypass is opened only when a reading is made. Flow readings can be taken at any time. The calibrated balance valve is an adjustable orifice flowmeter. Balance valves can be calibrated so that a flow/pressure drop relationship can be obtained for each incremental setting of the valve. A ball, rotating plug, or butterfly valve may have its setting expressed in percent open or degree open; a globe valve, in percent open or number of turns. The calibrated balance valve must be man- ufactured with precision and care to ensure that each valve of a par- ticular size has the same calibration characteristics. The turbine flowmeter is a mechanical device. The velocity of the liquid spins a wheel in the meter, which generates a 4 to 20 mA output that may be calibrated in units of flow. The meter must be well maintained, because wear or water impurities on the bearing may slow the wheel, and debris may clog or break the wheel. The ultrasonic flowmeter senses sound signals, which are cali- brated in units of flow. The ultrasonic metering station may be installed as part ofthe piping, or it may be a strap-on meter. In either case, the meter has no moving parts to maintain, nor does it intrude into the pipe and cause a pressure drop. Two distinct types of ultra- sonic meter are available: (1) the transit time meter for HVAC or clear-water systems and (2) the Doppler meter for systems handling sewage or large amounts of particulate matter. If any of the above meters are to be useful, the minimum dis- tance of straight pipe upstream and downstream, as recommended ![image](/image/placeholder) 15x PIPE DIAMETER* 15x PIPE DIAMETER* MINIMUM UPSTREAM DISTANCE MINIMUM M DOWNSTREAM METER DISTANCE ANY FITTING OR VALVE ANY FITTING OR VALVE *Or as indicated by manufacturer Fig. 16 Minimum Installation Dimensions for Flowmeter ![image](/image/placeholder) STRAINER GAGE GAGE PUMP DISCHARGE VALVE GAGE VALVE Fig. 17 Single Gage for Differential Readout Across Pump and Strainer by the meter manufacturer and flow measurement handbooks, must be adhered to. Figure 16 presents minimum installation sugges- tions. Using Pump as Indicator Although the pump is not a meter, it can be used as an indicator of flow together with the other system components. Differential pressure readings across a pump can be correlated with the pump curve to establish the pump flow rate. Accuracy depends on (1) ac- curacy of readout, (2) pump curve shape, (3) actual conformance of the pump to its published curve, (4) pump operation without cavita- tion, (5) air-free operation, and (6) velocity pressure correction. When a differential pressure reading must be taken, a single gage with manifold provides the greatest accuracy (Figure 17). The pump suction to discharge differential can be used to establish pump dif- ferential pressure and, consequently, pump flow rate. The single gage and manifold may also be used to check for strainer clogging by measuring the pressure differential across the strainer. Ifthe pump curve is based on fluid head, pressure differential, as obtained from the gage reading, needs to be converted to head, which is pressure divided by the density and gravity. The pump dif- ferential head is then used to determine pump flow rate (Figure 18). As long as the differential head used to enter the pump curve is expressed as head of the fluid being pumped, the pump curve shown by the manufacturer should be used as described. The pump curve may state that it was defined by test with 30°C water. This is unim- portant, because the same curve applies from 15 to 120°C water, or to any fluid within a broad viscosity range. Generally, pump-derived flow information, as established by the performance curve, is questionable unless the following precautions are observed: 1. The installed pump should be factory calibrated by a test to establish the actual flow/pressure relationship for that particular pump. Production pumps can vary from the cataloged curve because of minor changes in impeller diameter, interior casting tolerances, and machine fits. 2. When a calibration curve is not available for a centrifugal pump being tested, the discharge valve can be closed briefly to estab- lish the no-flow shutoff pressure, which can be compared to the published curve. If the shutoff pressure differs from that Inc. ASHRAE, 2019 user. single for Licensed | {}
8e0cb3ef-266d-4ebe-b293-f2fec66398d0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 39.28 Chart Type: line Differential Pressure Subtoff Pressure Determines Start of Curve Capacity Curve Low Rate item_01 90Feet 8Feet 2Feet 1Feet Fig. 18 Differential Pressure Used to Determine Pump Flow published, draw a new curve parallel to the published curve. Though not exact, the new curve usually fits the actual pumping circumstance more accurately. Clearance between the impeller and casing minimizes the danger of damage to the pump during a no-flow test, but manufacturer verification is necessary. 3. Differential pressure should be determined as accurately as pos- sible, especially for pumps with flat flow curves. 4. The pump should be operating air-free and without cavitation. A cavitating pump will not operate to its curve, and differential readings will provide false results. 5. Ensure that the pump is operating above the minimum net posi- tive suction pressure. 6. Power readings can be used (1) as a check for the operating point when the pump curve is flat or (2) as a reference check when there is suspicion that the pump is cavitating or providing false readings because of air. 7. The flow determined by the pump curve should be compared to the flow measured at the flowmeters, flow measured by pressure drops through circuits, and flow measured by pressure drops through exchangers. 8. The pump flow derived from the pressure differential at the suc- tion and discharge connections is only an indicator of the actual flow; it cannot be used to verify the test and balance measure- ments. If pump flow is to be used for balancing verification, it needs to be determined using the Hydraulic Institute procedure or by measuring the flow through a properly installed metering station 15 to 20 straight pipe diameters downstream from the pump discharge. Power draw should be measured in watts. Ampere readings cannot be trusted because of voltage and power factor problems. If motor efficiency is known, the wattage drawn can be related to pump brake power (as described on the pump curve) and the oper- ating point determined. For existing installations, establishing accurate thermal load pro- files is of prime importance because it establishes proper primary chilled-water supply temperature and flow. In new installations, actual load profiles can be compared with design load profiles to obtain valid operating data. Central Plant Chilled- w ater Systems To perform proper testing and balancing, all interconnecting points between the primary and secondary systems must be de- signed with sufficient temperature, pressure, and flow connections so that adequate data may be indicated and/or recorded. Water Flow Instruments As indicated previously, proper location and use of instruments is vital to accurate balancing. Instruments for testing temperature 2019 ASHRAE Handbook- -HVAC Applications (SI) Table 3 Instruments for Monitoring a Water System ¦ Point of Information ¦ Manifold Gage ¦ Single Gage ¦ Ther- mometer ¦ Test Well ¦ Pressure Tap ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Pump: Suction, discharge ¦ X ¦ ¦ ¦ ¦ ¦ ¦ Strainer: In, out ¦ ¦ ¦ ¦ ¦ X ¦ ¦ Cooler: In, out ¦ ¦ X ¦ X ¦ ¦ ¦ ¦ Condensers: In, out ¦ ¦ X ¦ X ¦ ¦ ¦ ¦ Concentrator: In, out ¦ ¦ X ¦ X ¦ ¦ ¦ ¦ Absorber: In, out ¦ ¦ X ¦ X ¦ ¦ ¦ ¦ Tower cell: In, out ¦ ¦ ¦ ¦ X ¦ X ¦ ¦ Heat exchanger: In, out ¦ X ¦ ¦ X ¦ ¦ ¦ ¦ Coil: In, out ¦ ¦ ¦ ¦ X ¦ X ¦ ¦ Coil bank: In, out ¦ ¦ X ¦ X ¦ ¦ ¦ ¦ Booster coil: In, out ¦ ¦ ¦ ¦ ¦ X ¦ ¦ Cool panel: In, out ¦ ¦ ¦ ¦ ¦ X ¦ ¦ Heat panel: In, out ¦ ¦ ¦ ¦ X ¦ X ¦ ¦ Unit heater: In, out ¦ ¦ ¦ ¦ ¦ X ¦ ¦ Induction: In, out ¦ ¦ ¦ ¦ ¦ X ¦ ¦ Fan-coil: In, out ¦ ¦ ¦ ¦ ¦ X ¦ ¦ Water boiler: In, out ¦ ¦ ¦ X ¦ ¦ ¦ ¦ Three-way valve: All ports ¦ ¦ ¦ ¦ ¦ X ¦ ¦ Zone return main ¦ ¦ ¦ X ¦ ¦ ¦ ¦ Bridge: In, out ¦ ¦ ¦ X ¦ ¦ ¦ ¦ Water makeup ¦ ¦ X ¦ ¦ ¦ ¦ ¦ Expansion tank ¦ ¦ X ¦ ¦ ¦ ¦ ¦ Strainer pump ¦ ¦ ¦ ¦ ¦ X ¦ ¦ Strainer main ¦ X ¦ ¦ ¦ ¦ ¦ ¦ Zone three-way: All ports ¦ ¦ ¦ ¦ X ¦ X ¦ and pressure at various locations are listed in Table 3. Flow- indicating devices should be placed in water systems as follows: · At each major heating coil bank (0.6 L/s or more) · At each major cooling coil bank (0.6 L/s or more) · At each bridge in primary-secondary systems · At each main pumping station · At each water chiller evaporator · At each water chiller condenser · At each water boiler outlet · At each floor takeoff to booster reheat coils, fan coil units, induc- tion units, ceiling panels, and radiation (do not exceed 25 termi- nals off of any one zone meter probe) · At each vertical riser to fan coil units, induction units, and radiation · At the point of tie-in to existing systems 9. BALANCING STEAM DISTRIBUTION SYSTEMS Procedures for Steam Balancing Variable Flow Systems Steam distribution cannot be balanced by adjustable flow- regulating devices. Instead, fixed restrictions built into the piping in accordance with carefully designed pipe and orifice sizes are used to regulate flow. It is important to have a balanced distribution of steam to all por- tions of the steam piping at all loads. This is best accomplished by properly designing the steam distribution piping, which includes carefully considering steam pressure, steam quantities required by each branch circuit, pressure drops, steam velocities, and pipe sizes. Just as other flow systems are balanced, steam distribution systems are balanced by ensuring that the pressure drops are equalized at design flow rates for all portions of the piping. Only marginal bal- ancing can be done by pipe sizing. Therefore, additional steps must be taken to achieve a balanced performance. Steam flow balance can be improved by using spring-type pack- less supply valves equipped with precalibrated orifices. The valves should have a tight shutoff between 80 to 400 kPa (gage). These valves have a nonrising stem, are available with a lockshield, and have a replaceable disk. Orifice flanges can also be used to regulate Inc. ASHRAE, 2019 user. single for Licensed | {}
3628a16b-8702-42f1-8adc-b8978417cca9 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Testing, Adjusting, and Balancing 39.29 and measure steam flow at appropriate locations throughout the system. The orifice sizes are determined by the pressure drop required for a given flow rate at a given location. A schedule should be prepared showing (1) orifice sizes, (2) valve or pipe sizes, (3) required flow rates, and (4) corresponding pressure differentials for each flow rate. It may be useful to calculate pressure differentials for several flow rates for each orifice size. Such a schedule should be maintained for future reference. After the appropriate regulating orifices are installed in the proper locations, the system should be tested for tightness by seal- ing all openings in the system and applying a vacuum of 35 kPa (absolute), held for 2 hours. Next, the system should be readied for warm-up and pressurizing with steam following the procedures out- lined in Section VI of the ASME Boiler and Pressure Vessel Code. After the initial warm-up and system pressurization, evaluate system steam flow, and compare it to system requirements. The ori- fice schedule calculated earlier will now be of value should any of the orifices need to be changed. Steam Flow Measuring Devices Many devices are available for measuring flow in steam piping: (1) steam meters, (2) condensate meters, (3) orifice plates, (4) ven- turi fittings, ⑤ steam recorders, and ⑥ manometers for reading differential pressures across orifice plates and venturi fittings. Some of these devices are permanently affixed to the piping system to facilitate taking instantaneous readings that may be necessary for proper operation and control. A surface pyrometer used in conjunc- tion with a pressure gage is a convenient way to determine steam saturation temperature and the degree of superheat at various loca- tions in the system. This information can be used to evaluate perfor- mance characteristics. Steam Pressure Regulation Many large steam systems generate steam at higher pressures (for distribution efficiencies) than what is required by the building systems, and then modulate the pressure using pressure-reducing valves (PRVs). To aid in stable pressure control at low loads, many engineers install two PRVs sized for 1/3 and 2/3 of the design flow rate. To aid in stable pressure control during moderate loads, verify that the 2/3 PRV does not open until the 1/3 PRV is full open. 10. BALANCING COOLING TOWERS Field-testing cooling towers is demanding and difficult. ASME Standard PTC 23 and CTI Standard Specification ATC-105 estab- lish procedures for these tests. Certain general guidelines for testing cooling towers are as follows. Waterflow from condenser to cooling tower should be the same flow. There may be basins and bypasses in the path that affect this pattern. Flow measurements should be made at both locations. For accurate flow measurements and good quality of flow, meters are required to be installed in the supply piping to each cooling tower and to each condenser. The condenser supply is from the cooling tower. This is a requirement even if there is more than one chiller or more than one cooling tower per system. Measurements and Verification Process 1. Measure waterflow both into and out of the condenser. 2. Measure waterflow in the cooling tower and balance each cooling tower for design flow. 3. Measure flow of makeup water to each tower basin. Set over- flow to zero during test so the evaporation rate can be deter- mined. During test, isolate make up water. 4. Verify control valves are operating properly. 5. Verify the entire condenser water system is operating correctly by allowing the system to go to full cooling. Not all chillers need to run with adequate flow meters, but the controls must allow full flow through the condenser and cooling tower. Take final flow measurements and record for the final report. 6. Measure and record the temperatures on and off the cooling towers. 7. Measure and record outdoor wet-bulb temperature. 8. If the cooling tower has nozzles and pressure gages installed, take pressure measurements on each line to the nozzles at full flow and record. 9. Measure power usage including nameplate data. Include motor amperage, voltage, hertz, safety factor, overload protection, manufacturer, and rating. List nameplate motor power and actual brake power. 10. List cooling tower airflow from brake power and manufactur- ers' data. Calculations and Verification 1. Calculate heat rejection of cooling tower as follows. Flow t factor/rate = heat rejection kilowatts Example: 63 L/s 11.1 tK 4.2/4.396 kW = 668 kilowatts 2. Verify and record data that each cooling tower is operating within manufacturers' design. Verify · Waterflow · Airflow · Power · Makeup water · Overflow water · Water treatment (with data from water treatment contractor) 3. If standby cooling towers and equipment are in the system, start up the standby units and shut down the tested units and repeat test. 11. VERIFICATION OF CONTROLS OPERATION The performance of the HVAC system's automatic controls should be inspected and tested in each seasonal mode. In addition, the performance of all life safety devices and their interface with the HV AC systems should be verified and reported. In general, the TAB technician is responsible for verifying that the control system is operating as specified, and for reporting any installation problems discovered. Basically, this means (1) setting controls to a proper fixed mode to prevent changes during balancing, and (2) verifying proper operation. Actual adjusting, moving, or recalibrating con- trols is normally the responsibility of the control contractor. How- ever, TAB technicians should work closely with the control contractor to ensure system operation within design limitations, identify and correct any problems, and ensure the safety of the system and its components, fulfilling the following steps: 1. Verify that controllers, including limiting controllers (e.g., fire stats and freeze stats), are calibrated and in control. 2. Verify that controller set points meet design intent. 3. Confirm that the sequences of operation for any control mode are in compliance with the approved drawings. 4. Check that the control terminations are in accordance with the approved drawings. 5. Verify the settings, operation, and adjustment of all end switches, mercury switches, solenoid valves, contractors, etc. 6. Check the operation of lockout or interlock systems. 7. Check the operation of all valve and damper actuators. 8. Determine that all controlled devices are properly connected. Inc. ASHRAE, 2019 user. single for Licensed | {}
e6db6fa2-c91c-4227-9c9a-41c0399c515c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 39.30 2019 ASHRAE Handbook- -HVAC Applications (SI) 9. Verify the operation of pilot positioners. 10. Confirm that all controlled devices are operated by the intended controller and note any overlap of controlled devices. 11. Prove that all controlled devices are in the position indicated by the controller (either open, closed, or modulating). 12. Determine the integrity of all controlled devices with regard to tightness of close-off and full-open positions. This includes dampers in multizone units, mixing boxes, and VAV air terminal devices. 13. Ensure that all controlled devices have free travel. 14. Verify that all controlled devices are properly installed in the distribution system with respect to direction of flow and loca- tion. 15. Confirm the proper operation of all controlled devices as appli- cable to normally open or normally closed. 16. Test the fail-safe modes of all controlled devices. 17. Examine the span of controls from a normally open position to a normally closed position, observing any dead bands, exces- sive pressures, and leading or lagging of simultaneously or sequentially controlled devices. 18. Check the location and installation of all sensors to determine if they will sense only the intended temperatures, humidities, or pressures. 19. Also check for potential erratic operation because of outdoor influences such as sunlight, drafts, outdoor walls, etc. For pneumatic systems: 1. Check main supply air for proper pressures. 2. Observe the operation of the compressor and dryer. For electronic systems: 1. Confirm that the control voltage is correct. 2. With the system in normal operation, test each control loop at both ends of its control range to verify that all control loops and their individual field points are responding correctly. 3. Check the calibration of all field sensors. 4. Verify the calibration and response time of all transducers. 5. Determine if the system has lightning protection and battery back-up. For direct digital systems: 1. Confirm that the control voltage is correct. 2. With the system in normal operation, test each control loop at both ends of its control range to prove that all control loops and their individual field points are responding correctly. 3. Check the calibration of all field sensors. 4. Verify the calibration and response time of all transducers. 5. Determine if the system has lightning protection and battery back-up. 6. Confirm the application and accuracy of the software algorithms for each control loop. 7. Test the operation of the phone modem. 12. THERMAL PERFORMANCE VERIFICATION After performing all preceding procedures, the system shall be set to simulate design conditions. Measure and record a complete set of dry-bulb and wet-bulb temperatures for air entering and leav- ing coils and heat exchangers, air leaving terminal devices (diffus- ers), and air in conditioned rooms or spaces. If conditions cannot be simulated and this affects verification, it should be documented in the testing and balancing report. 13. OUTDOOR AIR VENTILA TION VERIFICATION After completion of the balancing procedures, the system out- door air rate should be verified. This is necessary to ensure that the design minimum outdoor air is being supplied to the occupied spaces. Obtain the minimum outdoor air rate and the appropriate balance conditions from the design documents. Determine the total system actual flow rate by traverse or other approved method and the return air rate by the same method. If adequate space is not avail- able to perform a proper traverse, use the temperature ratio method if the outdoor temperature is at least 1 1 K above or below the return air temperature. Adjust the outdoor air rate to equal the required flow rate by balancing the return air system to allow sufficient out- door air to enter the system. This setting should be locked in and marked as the minimum outdoor air setting. After setting the out- door air rate, recheck the total system flow to make sure that it has not changed. 14. TEMPERA TURE CONTROL VERIFICATION The test and balance technician should work closely with the tem- perature control installer to ensure that the project is completed cor- rectly. The balancing technician needs to verify proper operation of the control and communicate findings back to the agency responsible for ensuring that the controls have been installed correctly. This is usually the HVAC system designer, although others may be involved. Generally, the balancing technician does not adjust, relocate, or calibrate the controls. However, this is not always the case, and dif- ferences do occur with VA V terminal unit controllers. The balancing technician should be familiar with the specifications and design intent of the project so that all responsibilities are understood. During the design and specification phase of the project, the designer should specify verification procedures for the controls and responsibilities for the contractor who installs the temperature controls. It is important that the designer specify the (1) degree of coordination between the installer of the control and the balancing technician and (2) testing responsibilities of each. Verification of control operation starts with the balancing tech- nician reviewing the submitted documents and shop drawings of the control system. In some cases, the controls technician should instruct the balancing technician in the operation of certain control elements, such as digital terminal unit controllers. This is followed by schedule coordination between the control and balancing tech- nicians. In addition, the balancing and controls technicians need to work together when reviewing the operation of some sections of the HV AC system, particularly with VAV systems and the setting of the flow measurement parameters in digital terminal unit control- lers. Major mechanical systems should be verified after testing, adjusting, and balancing is completed. The control system should be operated in stages to prove it can match system capacity to varying load conditions. Mechanical subsystem controllers should be veri- fied when balancing data are collected, considering that the entire system may not be completely functional at the time of verification. Testing and verification should account for seasonal variations; tests should be performed under varying outdoor loads to ensure opera- tional performance. Retesting a random sample of terminal units may be desirable to verify the control technician 's work. Suggested Procedures The following verification procedures may be used with either pneumatic or electrical controls: 1. Obtain design drawings and documentation, and become well acquainted with the design intent and specified responsibilities. 2. Obtain copies of approved control shop drawings. 3. Compare design to installed field equipment. 4. Obtain recommended operating and test procedures from man- ufacturers. 5. Verify with the control contractor that all controllers are cali- brated and commissioned. Inc. ASHRAE, 2019 user. single for Licensed | {}
4719dda1-11e3-4a08-8155-6c8f8b1d7a51 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Testing, Adjusting, and Balancing 39.31 6. Check location of transmitters and controllers. Note adverse conditions that would affect control, and suggest relocation as necessary. 7. Note settings on controllers. Note discrepancies between set point for controller and actual measured variable. 8. Verify operation of all limiting controllers, positioners, and relays (e.g., high- and low-temperature thermostats, high- and low-differential pressure switches, etc.). 9. Activate controlled devices, checking for free travel and proper operation of stroke for both dampers and valves. Verify nor- mally open (NO) or normally closed (NC) operation. 10. Verify sequence of operation of controlled devices. Note line pressures and controlled device positions. Correlate to air or waterflow measurements. Note speed ofresponse to step change. 11. Confirm interaction of electrically operated switch transducers. 12. Confirm interaction of interlock and lockout systems. 13. Coordinate balancing and control technicians' schedules to avoid duplication of work and testing errors. Pneumatic System Modifications 1. Verify main control supply air pressure and observe compressor and dryer operation. 2. For hybrid systems using electronic transducers for pneumatic actuation, modify procedures accordingly. Electronic Systems Modifications 1. Monitor voltages of power supply and controller output. Deter- mine whether the system operates on a grounded or nongrounded power supply, and check condition. Although electronic controls now have more robust electronic circuits, improper grounding can cause functional variation in controller and actuator perfor- mance from system to system. 2. Note operation of electric actuators using spring return. Gener- ally, actuators should be under control and use springs only upon power failure to return to a fail-safe position. Direct Digital Controllers Direct digital control (DDC) offers nontraditional challenges to the balancing technician. Many control devices, such as sensors and actuators, are the same as those in electronic and pneumatic systems. Currently DDC is dominated by two types of controllers: fully programmable or application-specific. Fully programmable controllers offer a group of functions linked together in an appli- cations program to control a system such as an air-handling unit. Application-specific controllers are functionally defined with the programming necessary to carry out the functions required for a system, but not all adjustments and settings are defined. Both types of controllers and their functions have some variations. One of the functions is adaptive control, which includes control algo- rithms that automatically adjust settings of various controller functions. The balancing technician must understand controller functions so that they do not interfere with the test and balance functions. Lit- eracy in computer programming is not necessary, although it does help. When testing the DDC, 1. Obtain controller application program. Discuss application of the designer's sequence with the control programmer. 2. Coordinate testing and adjustment of controlled systems with mechanical systems testing. Avoid duplication of efforts be- tween technicians. 3. Coordinate storage (e.g., saving to central DDC database and controller memory) of all required system adjustments with con- trol technician. In cases where the balancing agency is required to test discrete points in the control system, 1. Establish criteria for test with the designer. 2. Use reference standards that test the end device through the en- tire controller chain (e.g., device, wiring, controller, communi- cations, and operator monitoring device). An example would be using a dry block temperature calibrator (a testing device that allows a temperature to be set, monitored, and maintained in a small chamber) to test a space temperature sensor. The sensor is installed with extra wire so that it may be removed from the wall and placed in the calibrator chamber. After the system is ther- mally stabilized, the temperature is read at the controller and the central monitor, if installed. 3. Report findings of reference and all points of reading. Refer to ASHRAE Standard 1 1 1 for further details on HVAC TAB. 15. TESTING FOR SOUND AND VIBRA TION Testing for sound and vibration ensures that equipment is oper- ating satisfactorily and that no objectionable noise and vibration are transmitted to the building structure and occupied space. Although sound and vibration are specialized fields that require expertise not normally developed by the HVAC engineer, the procedures to test HV AC are relatively simple and can be performed with a minimum of equipment by following the steps outlined in this section. Although this section provides useful information for resolving common noise and vibration problems, consult Chapter 49 for details on problem solving or the design of HVAC. Testing for Sound Present technology does not test whether equipment is operating within rated sound levels; field tests can only determine sound pres- sure levels, and equipment ratings are almost always in terms of sound power levels. Until new techniques are developed, the testing engineer can only determine (1) whether sound pressure levels are within desired limits and (2) which equipment, systems, or compo- nents are the source of excessive or disturbing transmission. Sound-Measuring Instruments. Although an experienced lis- tener can often determine whether systems are operating in an acceptably quiet manner, sound-measuring instruments are neces- sary to determine whether system noise levels are in compliance with specified criteria, and if not, to obtain and report detailed infor- mation to evaluate the cause of noncompliance. Instruments nor- mally used in field testing are as follows. The precision sound level meter is used to measure sound pres- sure level. The most basic sound level meters measure overall sound pressure level and have up to three weighted scales that provide lim- ited filtering capability. The instrument is useful in assessing out- door noise levels in certain situations and can provide limited information on the low-frequency content of overall noise levels, but it provides insufficient information for problem diagnosis and solution. Its usefulness in evaluating indoor HVAC sound sources is thus limited. Proper evaluation ofHV AC sound sources requires a sound level meter capable of filtering overall sound levels into frequency incre- ments of one octave or less. Sound analyzers provide detailed information about sound pressure levels at various frequencies through filtering networks. The most popular sound analyzers are the octave band and one third octave band center frequency analyzers, which break the sound into the eight octave bands or twenty-four third octave bands of audible sound. Octave band or narrower sound analyzers are required where specifications are based on noise criteria (NC) and room criteria (RC) curves or similar frequency criteria and for problem jobs where knowledge of frequency is necessary to determine proper corrective action. Personal computers are a versatile sound-measuring tool. Soft- ware used on portable computers has all the functional capabilities Inc. ASHRAE, 2019 user. single for Licensed | {}
233d9272-78c2-4b08-a72f-e18b32475b3d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 39.32 2019 ASHRAE Handbook-HVAC Applications (SI) described previously, plus many that previously required a fully equipped acoustical laboratory. This type of sound-measuring sys- tem is many times faster and much more versatile than conventional sound level meters. With suitable accessories, it can also be used to evaluate vibration levels. Accuracy and calibration to applicable standards are of concern for software. Regardless of which sound-measuring system is used, it should be calibrated before each use. Some systems have built-in calibration, while others use external calibrators. Much information is available on the proper application and use of sound-measuring instruments. Air noise, caused by air flowing at a velocity of over 5 m/s or by winds over 19 km/h, can cause substantial error in sound measure- ments because of wind effect on the microphone. For outdoor mea- surements or in drafty places, either a wind screen for the microphone or a special microphone is required. When in doubt, use a wind screen on standard microphones. Sound Level Criteria. Without specified values, the testing engineer must determine whether sound levels are within acceptable limits (Table 1 in Chapter 49 Note that a complete absence of noise is seldom a design criterion, except for certain critical locations such as sound and recording studios. In most locations, a certain amount of noise is desirable to mask other noises and provide speech pri- vacy; it also provides an acoustically pleasing environment, because few people can function effectively in extreme quiet. Table 1 in Chapter 8 of the 2017 ASHRAE Handbook-Fundamentals lists typical sound pressure levels. Most field sound-measuring instru- ments and techniques yield an accuracy of ±3 dB, the smallest dif- ference in sound pressure level that the average person can discern. A reasonable tolerance for sound criteria is 5 dB. The measured sound level of any location is a combination of all sound sources present, including sound generated by HVAC equip- ment, as well as sound from other sources such as plumbing systems and fixtures, elevators, light ballasts, and outdoor noises. In testing for sound, all sources from other than HVAC equipment are consid- ered background or ambient noise. Background sound measurements generally have to be made (1) when the specification requires that the sound levels from HVAC equipment only, as opposed to the sound level in a space, not exceed a certain specified level; (2) when the sound level in the space exceeds a desirable level, in which case the noise contributed by the HVAC system must be determined; and (3) in residential locations where little significant background noise is generated during the evening hours and where generally low allowable noise levels are specified or desired. Because background noise from outdoor sources such as vehicular traffic can fluctuate widely, sound mea- surements for residential locations are best made in the normally quiet evening hours. Procedures for residential sound measure- ments can be found in ASTM Standard E1574, Measurement of Sound in Residential Spaces. Sound Testing. Ideally, a building should be completed and ready for occupancy before sound level tests are taken. All spaces in which readings will be taken should be furnished with whatever drapes, carpeting, and furniture are typical because these affect the room absorption, which can affect sound levels and the subjective quality of the sound. In actual practice, because most tests must be conducted before the space is completely finished and furnished for final occupancy, the testing engineer must make some allowances. Because furnishings increase the absorption coefficient and reduce by about 4 dB the sound pressure level that can be expected between most live and dead spaces, the following guidelines should suffice for measurements made in unfurnished spaces. Ifthe sound pressure level is 5 dB or more over the specified or desired criterion, it can be assumed that the criterion will not be met, even with the increased absorption provided by furnishings. If the sound pressure level is under 4 dB greater than the specified or desired criterion, recheck when the room is furnished to determine compliance. Follow this general procedure: 1. Obtain a complete set of accurate, as-built drawings and specifi- cations, including duct and piping details. Review specifications to determine sound and vibration criteria and any special instruc- tions for testing. 2. Visually check for noncompliance with plans and specifications, obvious errors, and poor workmanship. Turn system on for aural check. Listen for noise and vibration (especially duct leaks and loose fittings). 3. Adjust and balance equipment, as described in other sections, so that final acoustical tests are made with the HVAC system oper- ating as designed. It is desirable to perform acoustical tests for both summer and winter operation, but where this is not practical, make tests for the summer operating mode, as it usu- ally has the potential for higher sound levels. Tests must be made for all mechanical equipment and systems, including standby. 4. Check calibration of instruments. 5. Measure sound levels in all areas as required, combining mea- surements if equipment or systems must be operated separately. Before final measurements are made in any particular area, survey the area using an A-weighted scale reading (dBA) to determine the location of the highest sound pressure level. Indi- cate this location on a testing form, and use it for test measure- ments. Restrict the preliminary survey to determine location of test measurements to areas that can be occupied by standing or sitting personnel. For example, measurements would not be made directly below a diffuser located in the ceiling, but would be made as close to the diffuser as standing or sitting personnel might be situated. In the absence of specified sound criteria, the testing engineer should measure sound pressure levels in all occupied spaces to determine compliance with criteria indicated in Table 1 in Chapter 49 and to locate any sources of excessive or disturbing noise. With octave band sound level measurements, overall NC and RC values can be determined using measure- ments in the 125 Hz to 8000 Hz range. 6. Determine whether background noise measurements must be made. · If specification requires determining sound level from HVAC equipment only, background noise readings must be taken with HVAC equipment turned off. · If specification requires compliance with a specific noise level or criterion (e.g., sound levels in office areas not to exceed 35 dBA), ambient noise measurements must be made only if the noise level in any area exceeds the specified value. · For residential locations and areas requiring very low noise, such as sound recording studios and locations used during the normally quieter evening hours, it is usually desirable to take sound measurements in the evening and/or take ambient noise measurements. 7. For outdoor noise measurements to determine noise radiated by outdoor or roof-mounted equipment such as cooling towers and condensing units, the section on Sound Control for Outdoor Equipment in Chapter 49, which presents proper procedure and necessary calculations, should be consulted. Noise Transmission Problems. Regardless of precautions taken by the specifying engineer and installing contractors, situations can occur where the sound level exceeds specified or desired levels, and there will be occasional complaints of noise in completed installa- tions. A thorough understanding of Chapter 49 and the section on Testing for Vibration in this chapter is desirable before attempting to resolve any noise and vibration transmission problems. The following is intended as an overall guide rather than a detailed prob- lem-solving procedure. All noise transmission problems can be evaluated in terms of the source-path-receiver concept. Objectionable transmission can be Inc. ASHRAE, 2019 user. single for Licensed | {}
7c0c0e91-9f09-4c65-b1f6-6d574e836a49 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Testing, Adjusting, and Balancing 39.33 resolved by (1) reducing noise at the source by replacing defective equipment, repairing improper operation, proper balancing and adjusting, and replacing with quieter equipment; (2) attenuating paths of transmission with silencers, vibration isolators, and wall treatment to increase transmission loss; and (3) reducing or masking objectionable noise at the receiver by increasing room absorption or introducing a nonobjectionable masking sound. The following dis- cussion includes ways to identify actual noise sources using simple instruments or no instruments and possible corrections. When troubleshooting in the field, the engineer should listen to the offending sound. The best instruments are no substitute for careful listening, because the human ear has the remarkable ability to identify certain familiar sounds such as bearing squeak or duct leaks and can discern small changes in frequency or sound character that might not be apparent from meter readings only. The ear is also a good direction and range finder; noise generally gets louder as one approaches the source, and direction can often be determined by turning the head. Hands can also identify noise sources. Airjets from duct leaks can often be felt, and the sound of rattling or vibrating pan- els or parts often changes or stops when these parts are touched. In trying to locate noise sources and transmission paths, the engi- neer should consider the location of the affected area. In areas remote from equipment rooms containing significant noise producers but adjacent to shafts, noise is usually the result of structure-borne trans- mission through pipe and duct supports and anchors. In areas adjoining, above, or below equipment rooms, noise is usually caused by openings (acoustical leaks) in the separating floor or wall or by improper, ineffective, or maladjusted vibration isolation systems. Unless the noise source or path of transmission is quite obvious, the best way to identify it is by eliminating all sources systemati- cally as follows: 1. Turn off all equipment to make sure that the objectionable noise is caused by the HVAC. If the noise stops, the HVAC components (compressors, fans, and pumps) must be operated separately to determine which are contributing to the objectionable noise. Where one source of disturbing noise predominates, the test can be performed starting with all equipment in operation and turning off components or systems until the disturbing noise is eliminated. Tests can also be performed starting with all equipment turned off and operating various component equipment singularly, which permits evaluation of noise from each individual component. Any equipment can be termed a predominant noise source if, when the equipment is shut off, the sound level drops 3 dBA or if, when measurements are taken with equipment operating indi- vidually, the sound level is within 3 dBA ofthe overall objection- able measurement. When a sound level meter is not used, itis best to start with all equipment operating and shut off components one at a time because the ear can reliably detect differences and changes in noise but not absolute levels. 2. When some part ofthe HVAC system is established as the source of objectionable noise, try to further isolate the source. By walk- ing around the room, determine whether the noise is coming through air outlets or returns, hung ceiling, or floors or walls. 3. If the noise is coming through the hung ceiling, check that ducts and pipes are isolated properly and not touching the hung ceiling supports or electrical fixtures, which would provide large noise radiating surfaces. If ducts and pipes are the source of noise and are isolated properly, possible remedies to reduce noise include changing flow conditions, installing silencers, and/or wrapping the duct or pipe with an acoustical barrier or lagging such as a lead blanket or other materials suitable for the location (see Chapter 49). 4. If noise is coming through the walls, ceiling, or floor, check for any openings to adjoining shafts or equipment rooms, and check vibration isolation systems to ensure that there is no structure-borne transmission from nearby equipment rooms or shafts. 5. Noise traced to air outlets or returns usually requires careful eval- uation by an engineer or acoustical consultant to determine the source and proper corrective action (see Chapter 49). In general, air outlets can be selected to meet any acoustical design goal by keeping the velocity sufficiently low. For any given outlet, sound level increases with an increase in airflow velocity and doubling the velocity can increase this the sound level by 12 to 15 dB. Ap- proach conditions caused by improperly located control dampers or improperly sized diffuser necks can increase these sound levels by 10 to 20 dB. Using variable-frequency drive (VFD) speed controllers on air-handling units can help evaluate air ve- locity concerns. Dampers used to limit airflow typically increase these sound levels. A simple, effective instrument that aids in locating noise 6. sources is a microphone mounted on a pole. It can be used to localize noises in hard-to-reach places, such as hung ceilings and behind heavy furniture. If noise is traced to an air outlet, measure the A-weighted sound level close to it but with no air blowing against the microphone. Then, remove the inner assembly or core of the air outlet and repeat the reading with the meter and the observer in exactly the same position as before. If the second reading is more than 3 dB below the first, a significant amount of noise is caused by airflow over the vanes of the diffuser or grille. In this case, check whether the system is balanced properly. As little as 10% too much air increases the sound generated by an air outlet by 2 dB. As a last resort, a larger air outlet could be substituted to obtain lower air velocities and hence less turbulence for the same air quality. Before this is considered, however, the air approach to the outlet should be checked. Noise far exceeding the normal rating of a diffuser or grille is generated when a throttled damper is installed close to it. Air jets impinge on the vanes or cones of the outlet and produce edge tones similar to the hiss heard when blowing against the edge of a ruler. The material of the vanes has no effect on this noise, although loose vanes may cause additional noise from vibration. When balancing air outlets with integral volume dampers, consider the static pressure drop across the damper, as well as the air quantity. Separate volume dampers should be installed suffi- ciently upstream from the outlet so that there is no jet impinge- ment. Plenum inlets should be brought in from the side, so that jets do not impinge on the outlet vanes. 7. If air outlets are eliminated as sources of excessive noise, inspect the fan room. Ifpossible, change fan speed by about 10%. If res- onance is involved, this small change can make a significant difference. 8. Sometimes fans are poorly matched to the system. If a belt- driven fan delivers air at a higher static pressure than is needed to move the design air quantity through the system, reduce fan speed by changing sheaves. Ifthe fan does not deliver enough air, consider increasing fan speed only after checking the duct system for leakage. Turbulence in the air approach to the fan inlet increases fan sound generation and decreases its air capac- ity. Other parts that may cause excessive turbulence are dampers, duct bends, and sudden enlargements or contractions of the duct. When investigating fan noise, seek assistance from the fan sup- plier or manufacturer. 9. If additional acoustical treatment is to be installed in the ductwork, obtain a frequency analysis. This involves the use of an octave-band analyzer and should generally be left to a trained engineer or acoustic consultant. Inc. ASHRAE, 2019 user. single for Licensed | {}
aa36e1cf-1b2d-42b8-9266-c16d8d6d49f0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 39.34 Testing for Vibration Vibration testing is necessary to ensure that (1) equipment is operating within satisfactory vibration levels and (2) objectionable vibration and noise are not transmitted to the building structure. Although these two factors are interrelated, they are not necessarily interdependent. A different solution is required for each, and it is essential to test both the isolation and vibration levels of equip- ment. When measured routinely at the same location, vibration can be used for predictive maintenance. General Procedure. 1. Verify final system balancing is complete. 2. Make a visual check of all equipment for obvious errors that must be corrected immediately. 3. Make sure all isolation is free-floating and not short-circuited by obstruction between equipment or equipment base and building structure. 4. Conduct bump test to determine the natural frequency. 5. Energize the system for an aural check of any obviously rough operation. Checking bearings with vibration measurement in- strumentation is especially important because bearings can be- come defective in transit and/or if equipment was not properly stored, installed, or maintained. Defective bearings should be re- placed immediately to avoid damage to the shaft and other com- ponents. 6. Set or drive equipment and systems so that final vibration tests are made on equipment as it will actually be operating. 7. Test equipment vibration. Instruments. Although instruments are not required to test vi- bration isolation systems, they are essential to test equipment vibra- tion properly. Sound-level meters and computer-driven sound-measuring systems are the most useful instruments for measuring and evalu- ating vibration. Usually, they are fitted with accelerometers or vi- bration pickups for a full range of vibration measurement and analysis. Other instruments used for testing vibration in the field are described as follows. Reed vibrometers are relatively inexpensive and are often used for testing vibration, but their relative inaccuracy limits their usefulness. Vibrometers are moderately priced and measure vibration am- plitude by means of a light beam projected on a graduated scale. Vibrographs are moderately priced mechanical instruments that measure both amplitude and frequency. They provide a chart recording amplitude, frequency, and actual wave form of vibration. They can be used for simple, accurate determination of the natural frequency of shafts, components, and systems by a bump test. Reed vibrometers, vibrometers, and vibrographs have largely been supplanted by electronic meters that are more accurate and have become much more affordable. Vibration meters are moderately priced, relatively simple-to- use modern electronic instruments that measure the vibration ampli- tude. They provide a single broadband (summation of all frequen- cies) number identifying the magnitude of the vibration level. Both analog and digital readouts are common. Vibration analyzers are relatively expensive electronic instru- ments that measure amplitude and frequency, usually incorporating a variable filter. Strobe lights are often used with many of the other instruments for analyzing and balancing rotating equipment. Stethoscopes are available as inexpensive mechanic's type (basi- cally, a standard stethoscope with a probe attachment), relatively in- expensive models incorporating a tunable filter, and moderately priced powered types that electronically amplify sound and provide some type of meter and/or chart recording. 2019 ASHRAE Handbook-HVAC Applications (SI) The choice of instruments depends on the test. Vibrometers and vibration meters can be used to measure vibration amplitude as an acceptance check. Because they cannot measure frequency, they cannot be used for analysis and primarily function as a go/no-go instrument. The best acceptance criteria consider both amplitude and frequency. Anyone seriously concerned with vibration testing should use an instrument that can determine frequency as well as amplitude, such as a vibrograph or vibration analyzer. Vibration measurement instruments (both meters and analyzers) made specifically for measuring machinery vibration typically use moving coil velocity transducers, which are sizable and rugged. These are typically limited to a lower frequency of 500 cycles per minute (cpm) [8.33 Hz] with normal calibration. If measuring very-low-speed machinery such as large fans, cooling towers, or compressors operating below this limit, use an adjustment factor provided by the instrument manufacturer or use an instrument with a lower low-frequency limit, which typically uses a smaller accel- erometer as the vibration pickup transducer. Testing Vibration Isolation. 1. Ensure that equipment is free-floating by applying an unbal- anced load, which should cause the equipment to move freely and easily. On floor-mounted equipment, check that there are no obstructions between the base or foundation and the building structure that would cause transmission while still permitting equipment to rock relatively free because of the application of an unbalanced force (Figure 19). On suspended equipment, check that hanger rods are not touching the hanger. Rigid connections such as pipes and ducts can prohibit mounts from functioning properly and from providing a transmission path. Note that the fact that the equipment is free floating does not mean that the isolators are functioning properly. For example, a 500 revolu- tions per minute (rpm) fan on isolators with a natural frequency of 500 cpm (8.33 Hz) could be free-floating but would actually be in resonance, resulting in transmission to the building and excessive movement. 2. Determine whether isolators are adjusted properly and providing desired isolation efficiency. All isolators supporting a piece of equipment should have approximately the same deflection (i.e., they should be compressed the same under the equipment). If not, they have been improperly adjusted, installed, or selected; this should be corrected immediately. Note that isolation effi- ciency cannot be checked by comparing vibration amplitude on equipment to amplitude on the structure (Figure 20). The only accurate check ofisolation efficiencies is to compare vibration measurements of equipment operating with isolators to measurements of equipment operating without isolators. Be- cause this is usually impractical, it is better to check whether the isolator's deflection is as specified and whether the specified or desired isolation efficiency is being provided. Figure 21 shows natural frequency of isolators as a function of deflection and indicates the theoretical isolation efficiencies for various fre- quencies at which the equipment operates. ![image](/image/placeholder) EQUIPMENT OBSTRUCTION ROD HITTING HANGER BOX Fig. 19 Obstructed Isolation Systems Inc. ASHRAE, 2019 user. single for Licensed | {}
dfcf9267-e068-459d-a06e-28183feb9b64 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Testing, Adjusting, and Balancing 39.35 Although it is easy to determine the deflection of spring mounts by measuring the difference between the free heights with a ruler (information as shown on submittal drawings or available from a manufacturer), these measurements are difficult with most pad or rubber mounts. Further, most pad and rubber mounts do not lend themselves to accurate determination of natural frequency as a func- tion of deflection. For these mounts, the most practical approach is to check that there is no excessive vibration of the base and no notice- able or objectionable vibration transmission to the building structure. Ifisolators are in the 90% efficiency range and there is transmis- sion to the building structure, either the equipment is operating roughly or there is a flanking path of transmission, such as connecting piping or obstruction, under the base. Testing Equipment Vibration. Testing equipment vibration is necessary as an acceptance check to determine whether equipment is functioning properly and to ensure that objectionable vibration and noise are not transmitted. Although a person familiar with equipment can determine when it is operating roughly, instruments are usually required to determine accurately whether vibration lev- els are satisfactory. Vibration Tolerances. Vibration tolerance criteria are listed in Table 45 of Chapter 49. These criteria are based on equipment in- ![image](/image/placeholder) 200 Jum WRONG EQUIPMENT 20 Jum THIS IS NOT 10% TRANSMISSION. , MEASUREMENTS HAVE NO RELATIONSHIP TO EACH OTHER IN TERMS OF EFFICIENCY. 200 Jum MEASUREMENT WITHOUT ISOLATORS OR RIGHT EQUIPMENT SYSTEM BLOCKED 20 �m MEASUREMENT WITH ISOLATORS IN PLACE AND ADJUSTED 10% TRANSMISSION Fig. 20 Testing Isolation Efficiency X-Axis: Disturbing Frequency (f = Cycles Per Minute) Y-Axis: Natural Frequency (m, Cycles Per Minute) Chart Type: line Static Deflection & Structure Peak Aviation Chemical Production Rice Station 100 Work of 200 Work onwards Preventionation (m) Reduction for 800 Processoration (m) item_01 250m 75m 100m 75m 50m 75m 100m 100m 50m 25m Fig. 21 Isolator Natural Frequencies and Efficiencies stalled on vibration isolators and can be met by any reasonably smoothly running equipment. Note that values in Chapter 49 are based on root-mean-square (RMS) values; other sources often use peak-to-peak or peak values, especially for displacements. For sinu- soid responses, it is simple to obtain peak from RMS values, but in application the relationship may not be so straightforward. The main advantage of RMS is that the same instrumentation can be used for both sound and vibration measurements by simply changing the transducer. Also, there is only one recognized refer- ence level for the decibel used for sound-pressure levels, but for vi- bration levels there are several recognized ones but no single standard. A common mistake in interpreting vibration data is mis- understanding the reference level and whether the vibration data are RMS, peak-to-peak, or peak values. Use great care in publishing and interpreting vibration data and converting to and from linear ab- solute values and levels in decibels. Procedure for Testing Equipment Vibration. 1. Determine operating speeds of equipment from nameplates, drawings, or a speed-measuring device such as a tachometer or strobe, and indicate them on the test form. For any equipment where the driving speed (motor) is different from the driven speed (e.g., fan wheel, rotor, impeller) because of belt drive or gear reducers, indicate both driving and driven speeds. 2. Determine acceptance criteria from specifications, and indicate them on the test form. If specifications do not provide criteria, use those shown in Chapter 49. 3. Ensure that the vibration isolation system is functioning properly (see the section on Testing Vibration Isolation). 4. Conduct bump test to determine the natural frequency. This can be accomplished by placing the accelerometer and taping or bumping the bearing or motor with a rubber hammer. 5. Energize equipment and make visual and aural checks for any apparent rough operation. Any defective bearings, misalign- ment, or obvious rough operation should be corrected before proceeding further. If not corrected, equipment should be con- sidered unacceptable. 6. Measure and record vibration at bearings of driving and driven components in horizontal, vertical, and, if possible, axial direc- tions. At least one axial measurement should be made for each rotating component (fan motor, pump motor). 7. Evaluate measurements. Evaluating Vibration Measurements. Amplitude Measurement. When specification for acceptable equipment vibration is based on amplitude measurements only, measurements can be made with an instrument that measures only amplitude (e.g., a vibration meter or vibrometer), · No measurement should exceed specified values or values shown in Tables 45 or 46 of Chapter 49, taking into consideration reduced values for equipment installed on inertia blocks · No measurement should exceed values shown in Tables 45 or 46 of Chapter 49 for driving and driven speeds, taking into consider- ation reduced values for equipment installed on inertia blocks. For example, with a belt-driven fan operating at 800 rpm and hav- ing an 1800 rpm driving motor, amplitude measurements at fan bearings must be in accordance with values shown for 800 cpm (13.3 Hz), and measurements at motor bearings must be in accor- dance with values shown for 1800 cpm (30 Hz). If measurements at motor bearings exceed specified values, take measurements of the motor only with belts removed to determine whether there is feedback vibration from the fan. · No axial vibration measurement should exceed maximum radial (vertical or horizontal) vibration at the same location. Amplitude and Frequency Measurement. When specification for acceptable equipment vibration is based on both amplitude and fre- Inc. ASHRAE, 2019 user. single for Licensed | {}
dadbb46c-7acc-4d6d-8723-3b71316f03c3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 39.36 2019 ASHRAE Handbook-HVAC Applications (SI) Chart Type: line Operating Speed Equipment operating just above resonance Multide sharply increases just before or as equipment reaches operating speed item_01 100 100 100 Fig. 22 Vibration from Resonant Condition quency measurements must be made with instruments that measure both amplitude and frequency (e.g., a vibrograph or vibration ana- lyzer), · Amplitude measurements at driving and driven speeds should not exceed specified values or values shown in Tables 45 or 46 of Chap- ter 49, taking into consideration reduced values for equipment installed on inertia blocks. Measurements that exceed acceptable amounts may be evaluated as explained in the section on Vibration Analysis. · Axial vibration measurements should not exceed maximum radial (vertical or horizontal) vibration at the same location. · The presence of any vibration at frequencies other than driving or driven speeds is generally reason to rate operation unacceptable; this vibration should be analyzed as explained in the section on Vibration Analysis. Vibration Analysis. The following guide covers most vibration problems that may be encountered. Axial Vibration Exceeds Radial Vibration. When the amplitude of axial vibration (parallel with shaft) at any bearing exceeds radial vibration (perpendicular to shaft, vertical or horizontal), it usually indicates misalignment, most common on direct-driven equipment because flexible couplings accommodate parallel and angular mis- alignment of shafts. This misalignment can generate forces that cause axial vibration, which can cause premature bearing failure, so misalignment should be checked carefully and corrected promptly. Other possible causes of large-amplitude axial vibration are reso- nance, defective bearings, insufficient rigidity of bearing supports or equipment, and loose hold-down bolts. Vibration Amplitude Exceeds Allowable Tolerance at Rotational Speed. The allowable vibration limits established by Table 41 of Chapter 49 are based on vibration caused by rotor imbalance, which results in vibration at rotational frequency. Although vibration caused by imbalance must be at the frequency at which the part is rotating, a vibration at rotational frequency does not have to be caused by imbalance. An unbalanced rotating part develops centrif- ugal force, which causes it to vibrate at rotational frequency. Vibra- tion at rotational frequency can also result from other conditions such as a bent shaft, an eccentric sheave, misalignment, and reso- nance. If vibration amplitude exceeds allowable tolerance at rota- tional frequency, the following steps should be taken before performing field balancing of rotating parts: 1. Check vibration amplitude as equipment goes up to operating speed and as it coasts to a stop. Any significant peaks at or near operating speed, as shown in Figure 22, indicate probable reso- nance (i.e., some part having a natural frequency close to the Chart Type: line Oceanic speed Encending or bent shaft item_01 0Amplitude 200Amplitude Fig. 23 Vibration Caused by Eccentricity ![image](/image/placeholder) OR Fig. 24 Bent Shafts operating speed, resulting in greatly amplified levels of vibra- tion). A bent shaft or eccentricity usually causes imbalance that re- sults in significantly higher vibration amplitude at lower speeds, as shown in Figure 23 whereas vibration caused by imbalance generally increases as speed increases. 2. 3. If a bent shaft or eccentricity is suspected, check the dial indi- cator. A bent shaft or eccentricity between bearings as shown in Figure 24A can usually be compensated for by field balancing, although some axial vibration might remain. Field balancing cannot correct vibration caused by a bent shaft on direct- connected equipment, on belt-driven equipment where the shaft is bent at the location of sheave, or if the sheave is eccentric (Figure 24B). This is because the center-to-center distance of the sheaves fluctuates, each revolution resulting in vibration. For belt- or gear-driven equipment where vibration is at motor driving frequency rather than driven speed, it is best to discon- nect the drive to perform tests. If the vibration amplitude of the motor operating by itself does not exceed specified or allowable values, excessive vibration (when the drive is connected) is prob- ably a function of bent shaft, misalignment, eccentricity, reso- nance, or loose hold down bolts. Vibration caused by imbalance can be corrected in the field by firms specializing in this service or by testing personnel if they have appropriate equipment and experience. Vibration at Other than Rotational Frequency. Vibration at fre- quencies other than driving and driven speeds is generally consid- ered unacceptable. Table 4 shows some common conditions that can cause vibration at other than rotational frequency. Resonance. If resonance is suspected, determine which part of the system is in resonance. Isolation Mounts. The natural frequency of the most commonly used spring mounts is a function of spring deflection, as shown in Figure 25, and it is relatively easy to calculate by determining the difference between the free and operating height of the mount, as explained in the section on Testing Vibration Isolation. This tech- nique cannot be applied to rubber, pad, or fiberglass mounts, which have a natural frequency in the 300 to 3000 cpm (5 to 50 Hz) range. Natural frequency for such mounts is determined by a bump test. Any resonance with isolators should be immediately corrected because it results in excessive movement of equipment and more Inc. ASHRAE, 2019 user. single for Licensed | {}
a92abec9-00f7-4ef0-84ba-5eda34ff40ad | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Testing, Adjusting, and Balancing 39.37 Table 4 Common Causes of Vibration Other than Unbalance at Rotation Frequency ¦ Frequency ¦ Frequency ¦ Source ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 0.5 ¦ rpm ¦ Vibration at approximately 0.5 rpm can result from improperly loaded sleeve bearings. This vibration will usually disappear suddenly as equipment coasts down from operating speed. ¦ ¦ 2 ¦ rpm ¦ Equipment is not tightly secured or bolted down. ¦ ¦ 2 ¦ rpm ¦ Misalignment of couplings or shafts usually results in vibration at twice rotational frequency and generally a relatively high axial vibration. ¦ ¦ Many ¦ rpm ¦ Defective antifriction (ball, roller) bearings usually result in low-amplitude, high-frequency, erratic vibration. Because defective bearings usually produce noise rather than any significantly measurable vibration, it is best to check all bearings with a listening device. ¦ ![image](/image/placeholder) NATURAL FREQUENCY fn, Hz 2.0 3.0 1 1.25 1.50 1.75 2.5 3.5 200 150 100 75 50 25 10 250 STATIC DEFLECTION 8st, mm 1 fn = 2元 Vg/8st = 15.76V1/8sl Fig. 25 Natural Frequency of Vibration Isolators transmission to the building structure than if equipment were attached solidly to the building (installed without isolators). Components. Resonance can occur with any shaft, structural base, casing, and connected piping. The easiest way to determine natural frequency is to perform a bump test with a vibration spec- trum analyzer. Checking for Vibration Transmission. The source of vibration transmission can be checked by determining frequency with a vibra- tion analyzer and tracing back to equipment operating at this speed. However, the easiest and usually best method (even if test equipment is being used) is to shut off components one at a time until the source of transmission is located. Most transmission problems cause disturb- ing noise; listening is the most practical approach to determine a noise source because the ear is usually better than instruments at distinguishing small differences and changes in character and amount of noise. Where disturbing transmission consists solely of vibration, an instrument will probably be helpful, unless vibration is signifi- cantly above the sensory level ofperception. Vibration below sensory perception is generally not objectionable. If equipment is located near the affected area, check isolation mounts and equipment vibration. If vibration is not being transmit- ted through the base, or if the area is remote from equipment, the probable cause is transmission through connected piping and/or ducts. Ducts can usually be isolated by isolation hangers. However, transmission through connected piping is very common and pres- ents many problems that should be understood before attempting to correct them (see the following section). Vibration and Noise Transmission in Piping. Vibration and noise in connected piping can be generated by either equipment (e.g., pump or compressor) or flow (velocity). Mechanical vibration from equipment can be transmitted through the walls of pipes or by a water column. Flexible pipe connectors, which provide system flexibility to permit isolators to function properly and protect equip- ment from stress caused by misalignment and thermal expansion, can be useful in attenuating mechanical vibration transmitted through a pipe wall. However, they rarely suppress flow vibration ![image](/image/placeholder) TIE RODS Fig. 26 Typical Tie Rod Assembly and noise and only slightly attenuate mechanical vibration as trans- mitted through a water column. Tie rods are often used with flexible rubber hose and rubber expansion joints (Figure 26). Although they accommodate thermal movements, they hinder vibration and noise isolation. This is because pressure in the system causes the hose or joint to expand until resilient washers under tie rods are virtually rigid. To isolate noise adequately with a flexible rubber connector, tie rods and anchor piping should not be used. However, this technique generally cannot be used with pumps on spring mounts, which would still permit the hose to elongate. Flexible metal hose can be used with spring-isolated pumps because wire braid serves as tie rods; metal hose controls vibration but not noise. Problems of transmission through connected piping are best resolved by changes in the system to reduce noise (improve flow characteristics, reduce impeller size) or by completely isolating pip- ing from the building structure. Note, however, that it is almost impossible to isolate piping completely from the structure, because the required resiliency is inconsistent with rigidity requirements of pipe anchors and guides. Chapter 49 contains information on flexible pipe connectors and resilient pipe supports, anchors, and guides, which should help resolve any piping noise transmission problems. 16. FIELD SURVEY FOR ENERGY AUDIT An energy audit is an organized survey of a specific building to identify and measure all energy uses, determine probable sources of energy losses, and list energy conservation opportunities. This is usually performed as a team effort under the direction of a qualified energy engineer. The field data can be gathered by firms employing technicians trained in testing, adjusting, and balancing. Procedures for energy audits can be found in ASHRAE (2011). Instruments To determine a building's energy use characteristics, existing conditions must be accurately measured with proper instruments. Accurate measurements point out opportunities to reduce waste and provide a record of the actual conditions in the building before energy conservation measures were taken. They provide a compila- tion of installed equipment data and a record of equipment perfor- mance before changes. Judgments will be made based on the information gathered during the field survey; that which is not accu- rately measured cannot be properly evaluated. Generally, instruments used for testing, adjusting, and balancing are sufficient for energy conservation surveying. Possible additional instruments include a power factor meter, light meter, combustion testing equipment, refrigeration gages, and equipment for recording temperatures, fluid flow rates, and energy use over time. Only high- quality instruments should be used. Observation of system operation and any information the techni- cian can obtain from the operating personnel pertaining to the oper- ation should be included in the report. Inc. ASHRAE, 2019 user. single for Licensed | {}
6b7e7aa0-1ffc-4378-a993-0642466182c0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 39.38 Data Recording Data sheets for energy conservation field surveys contain differ- ent and, in some cases, more comprehensive information than those used for testing, adjusting, and balancing. Generally, the energy engineer determines the degree of fieldwork to be performed; data sheets should be compatible with the instructions received. Organized record keeping is extremely important. A camera is also helpful. Photographs of building components and mechanical and electrical equipment can be reviewed later when the data are analyzed. Building Systems The most effective way to reduce building energy waste is to identify, define, and tabulate the energy load by building system. For this purpose, load is defined as the quantity of energy used in a building, or by one ofits subsystems, for a given period. By follow- ing this procedure, the most effective energy conservation opportu- nities can be achieved more quickly because high priorities can be assigned to systems that consume the most energy. A building can be divided into nonenergized and energized sys- tems. Nonenergized systems do not require external energy sources such as electricity and fuel. Energized systems (e.g., mechanical and electrical systems) require external energy. Energized and non- energized systems can be divided into subsystems defined by func- tion. Nonenergized Systems. Nonenergized subsystems include building site, envelope, and interior; building use; and building operation. Building Site, Envelope, and Interior. These subsystems should be surveyed to determine how they can be modified to reduce the building load that the mechanical and electrical systems must meet (without adversely affecting the building': s appearance). It is import- ant to compare actual conditions with conditions assumed by the designer, so that mechanical and electrical systems can be adjusted to balance their capacities to satisfy actual needs. Building Use. These loads can be classified as people occu- pancy or operation loads. People occupancy loads are related to schedule, density, and mixing of occupancy types (e.g., process and office). People operation loads are varied and include opera- tion of manual window shading devices; setting of room thermo- stats; and conservation-related habits such as turning off lights, closing doors and windows, turning off energized equipment when not in use, and not wasting domestic hot or chilled water. Building Operation. This subsystem consists of the operation and maintenance of all the building subsystems. The load on the building operation subsystem is affected by factors such as the time at which janitorial services are performed, janitorial crew size and time required to clean, amount oflighting used to perform janitorial functions, quality of equipment maintenance program, system oper- ational practices, and equipment efficiencies. Energized Systems. Energized subsystems of a building gener- ally include plumbing, heating, ventilating, cooling, space condi- tioning, control, electrical, and food service. Although these systems are interrelated and often use common components, logical organization of data requires evaluating the energy use of each sub- system as independently as possible. In this way, proper energy con- servation measures for each subsystem can be developed. Process Loads In addition to building subsystem loads, the process load in most buildings must be evaluated by the energy field auditor. Most tasks not only require energy for performance, but also affect the energy consumption of other building subsystems. For example, if a pro- cess releases large amounts of heat to the space, the process con- sumes energy and also imposes a large load on the cooling system. 2019 ASHRAE Handbook-HVAC Applications (SI) Guidelines for Developing Field Study Form The following checklist outlines requirements for a field study form, needed to conduct an energy audit. Inspection and Observation of All Systems. Record physical and mechanical condition of the following: · Fan blades, fan scroll, drives, belt tightness, and alignment · Filters, coils, and housing tightness · Ductwork (equipment room and space, where possible) · Strainers · Insulation ducts and piping · Makeup water treatment and cooling tower Interview of Physical Plant Supervisor. Record answers to the following survey questions: · Is the system operating as designed? If not, what changes have been made to ensure its performance? · Have there been modifications or additions to the system? · If the system has had a problem, list problems by frequency of occurrence. · Are any systems cycled? If so, which systems, when, and would building load allow cycling systems? Recording System Information. Record the following system/ equipment identification: · Type of system. Single-zone, multizone, dual-duct, low- or high- velocity, reheat, variable-volume, or other · System arrangement. Fixed minimum outdoor air, no relief, grav- ity or power relief, economizer gravity relief, exhaust return, or other · Air-handling equipment. (Supply, return, and exhaust) manufac- turer, model, size, type, and class of fans; dampers (vortex, scroll, or discharge); motors manufacturer, power requirement, full-load amperes, voltage, phase, and service factor · Chilled- and hot-water coils. Area, tubes on face, fin spacing, and number of rows (coil data necessary when shop drawings are not available) · Terminals. High-pressure mixing box manufacturer, model, and type (reheat, constant-volume, variable-volume, induction); grilles, registers, and diffusers manufacturer, model, style, and correction factor to convert field-measured velocity to flow rate · Main heating and cooling pumps, over 3.5 kW. Manufacturer, pump service and identification, model, size, impeller diameter, speed, flow rate, head at full flow, and head at no flow; motor data (power, speed, voltage, amperes, and service factor) · Refrigeration equipment. Chiller manufacturer, type, model, serial number, nominal tons, input power, total heat rejection, motor (kilowatts, amperes, volts), chiller pressure drop, entering and leaving chilled water temperatures, condenser pressure drop, condenser entering and leaving water temperatures, running amperes and volts, no-load running amperes and volts · Cooling tower. Manufacturer, size, type, nominal cooling capacity, range, flow rate, and entering wet-bulb temperature · Heating equipment. Boiler (small through medium) manufac- turer, fuel, energy input (rated), and heat output (rated) Recording Test Data. Record the following test data: · Systems in normal mode of operation (ifpossible). Fan motor run- ning amperes and volts and power factor (over 3.5 kW; fan speed, total air (pitot tube traverse where possible), and static pressure (discharge static minus inlet total); static profile drawing (static pressure across filters, heating coil, cooling coil, and dampers); static pressure at ends of runs of the system (identifying loca- tions). · Cooling coils. Entering and leaving dry- and wet-bulb tempera- tures, entering and leaving water temperatures, coil pressure drop (where pressure taps permit and manufacturer's ratings can be Inc. ASHRAE, 2019 user. single for Licensed | {}
f8c42b02-9f21-4218-8de9-1474a581584c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Testing, Adjusting, and Balancing 39.39 obtained), flow rate of coil (when other than fan), outdoor wet and dry bulb, time of day, and conditions (sunny or cloudy). · Heating coils. Entering and leaving dry-bulb temperatures, entering and leaving water temperatures, coil pressure drop (where pressure taps permit and manufacturer's ratings can be obtained), and flow rate through coil (when other than fan). · Pumps. No-flow head, full-flow discharge pressure, full-flow suc- tion pressure, full-flow differential pressure, motor running amperes and volts, and power factor (over 3.5 kW). · Chiller (under cooling load conditions). Chiller pressure drop, entering and leaving chilled water temperatures, condenser pres- sure drop, entering and leaving condenser water temperatures, running amperes and volts, no-load running amperes and volts, chilled water on and off, and condenser water on and off. · Cooling tower. Waterflow rate in tower, entering and leaving water temperatures, entering and leaving wet bulb, fan motor (amperes, volts, power factor [over 3.5 kW], and ambient wet bulb). · Boiler (full fire). Input energy (if possible), percent CO2, stack temperature, efficiency, and complete Orsat test on large boilers. · Boiler controls. Description of operation. · Temperature controls. Operating and set-point temperatures for mixed air controller, leaving air controller, hot-deck controller, cold-deck controller, outdoor reset, interlock controls, and damper controls; description of complete control system and any malfunctions. · Outdoor air intake versus exhaust air. Total airflow measured by pitot tube traverses ofboth outdoor air intake and exhaust air sys- tems, where possible. Determine whether an imbalance in the exhaust system causes infiltration. Observe exterior walls to determine whether outdoor air can infiltrate return air (record out- door air, return air, and return air plenum dry- and wet-bulb tem- peratures). The greater the differential between outdoor and return air, the more evident the problem will be. 17. TAB REPORTS This section sets forth an outline for the procedures and forms which make up the final report of operating conditions. Supervising personnel should use a logical approach in preparing forms and recording data. This section will list form titles and entries commonly used, allowing for design suited to each par- ticular job. All entries will not be required in every situation. Many excellent forms have been developed by various associations but are available for use by their members only. Accuracy in preparing the final report forms is important for sev- eral reasons: · They provide a permanent record of system operating conditions after the last adjustments have been made. · They confirm that prescribed procedures have been followed. · They will serve as a reference that can be used by the owner for maintenance. · They provide the designer with a system operational check and could serve as an aid in diagnosing problems. All forms shall include identification of project, system/unit, location, date, technician, page number, and remarks. General Items The report should contain the following, as applicable: Title page: · Name and address ofTAB firm · Project name · Location · Architect · Engineer · Contractor · Report date · Signature of TAB firm person who approved report Summary of comments: · Design versus final performance · Notable characteristics of system · Description of systems operation sequence · Summary of outdoor and exhaust flows to indicate amount of building pressurization Nomenclature sheet: · Codes for boxes, reheat coils, terminals, etc. (with data on manufacturer, type, size, fittings, etc.) · Notes that explain in detail why certain final data in the body of the report deviate from design values Test conditions (to be stated on the fan or pump performance form): · Setting of outdoor, return, and exhaust dampers · Condition of filters · Cooling coil wet or dry · Face and bypass damper setting at coil · Fan drive setting (indicate setting · percentage of maximum pitch diameter) · Set points of variable flow controller · Setting of supply air static pressure controller · Other systems operating which affect performances System Diagram A single line diagram for schematic layout of air distribution sys- tems and hydronic systems is highly recommended to ensure sys- tematic and efficient procedures. Quantities of outdoor air, return air, relief air; sizes and airflow rates for main ducts; sizes and air- flow rates for all air terminal devices, dampers, and other regulating devices should be shown. All air terminals should be numbered before filling out the air terminal device report. Though diagrams are suggested, the use of this form is not mandatory. Air Apparatus Test Report The performance of air handling apparatus with coils is to be reported. Motor voltage and amperage for three-phase motors should be reported for all three legs (T1, T2, and T3). If the design engineer did not specify a design quantity for any item in the test data section, place an X in the space for the design quantity and record the actual quantity. If available, include equipment manufac- turer ratings in the design columns when design quantity is unknown. If motor ratings differ from design, provide an explana- tion at the bottom of the page. If there are split coils, record data for each airstream. Unit Data Inc. ASHRAE, 2019 user. single for Licensed · Make/type · Model number/size · Serial number · Arrangement/class · Discharge · Sheave make · Sheave size/bore · Number of belts/make/size · Number of filters/type/size · Make/frame · W/Rad/s · Volts/phase/hertz · Full load amps/service factor · Sheave make · Cooling coil differential static · Heating coil differential static pressure pressure · Outdoor airflow rate · Return airflow rate | {}
b8990e50-8622-4e2e-a8e8-09125d1ab5f6 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 39.40 · Outdoor air damper position · Return air damper position · Vortex damper position Motor Data Sheave size/bore Sheave adjustment · Test Data (list design and actual for each) · Total airflow rate · Total system static pressure · Fan Hz · Motor volts, T1-T2, T2-T3, T3-T1 · Motor amps, A1, A2, A3 · Discharge static pressure · Filter differential static pressure · Preheat coil differential static pressure Apparatus Coil Test Report: The performance of chilled water, hot water, steam, or DX coils, and for runaround heat recovery systems is to be reported. Coil Data: · System number · Location · Coil type · Number of rows/fins · Make/model · Face area · Tube size · Tube/fin material · Circuiting Test Data: (list design and actual for each) ¦ · Airflow rate ¦ · ¦ Air velocity ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ · Air pressure drop ¦ · ¦ Entering/leaving air (db/wb) ¦ ¦ · Waterflow rate ¦ · ¦ Water pressure differential ¦ ¦ · Entering/leaving water temperature ¦ · ¦ Exp. valve/refrigeration ¦ ¦ · Refrigeration suction pressure ¦ · ¦ Refrigeration suction temperature ¦ · Inlet steam pressure Gas/Oil Fired Heat Apparatus Test Report Inc. ASHRAE, 2019 user. single for Licensed Data for gas- or oil-fired devices, (e.g., unit heaters, duct fur- naces, etc.) will be recorded. This report is not intended to be used in lieu of a factory startup equipment report, but could be used as a supplement. All available design data should be reported. Some information could apply to the burner motor, burner fan motor, unit air fan motor, etc., depending on the application or equipment. Therefore, designate the motor of the recorded data. Unit Data: · System number · Location · Make/type · Model number/size · Serial number · Type fuel/input · Output/W · Ignition type · Burner control · Volts/phase/hertz · W/Rad/s · Full load amps/service factor · Sheave data Test Data: (list design and actual for each) · Airflow rate · Entering/leaving air temperature · Entering/leaving air pressure · Low fire input · High fire input · Manifold pressure/CFH · High limit setting · Operating set point · Voltage, T1-T2, T2-T3, T3-T1 · Amps, A1, A2, A3 · Heating value of fuel 2019 ASHRAE Handbook-HVAC Applications (SI) Electric Coil/Duct Heater Test Report Data for electric furnaces or for electric coils installed in built-up units or ducts will be recorded. "Minimum air velocity" is as rec- ommended by manufacturers. Unit Data: · System/location · Coil number · kW · Stages · Volts/phase/Hertz · Amps · Airflow rate · Face area · Minimum air velocity Test Data: (list design and actual for each) · kW · Air velocity · Airflow rate · Entering air temperature · Leaving air temperature · Voltage, T1-T2, T2-T3, T3-T1 · Amps, A1, A2, A3 · Fan Test Report The performance of all supply, return, and exhaust fans should be recorded. · · · Fan Data: System number Make/type Serial number Sheave make · · Location · Model number/size · Arrangement/class · Sheave size/bore · · W/Rad/s · · Full load amps · · Sheave make Motor Data: Make/frame Volts/phase/Hertz Service factor Sheave size/bore Sheave centerline distance and adjustment · · Number of belts/make/size · · Test Data: (list design and actual for each) · Airflow rate · Fan Hz · Suction static pressure · Amps, Al, A2, A3 · Total system static pressure · Discharge static pressure · Voltage, T1 T2, T2 T3, T3 T1 Duct Traverse Report The results of a pitot tube traverse in all rectangular, round, and oval ducts shall be recorded. For rectangular duct traverses, make a grid representing the duct cross section with a box for each test point and its distance from sides of duct. It is recommended that the velocity pressures be recorded in one half of each box provided and then converted to velocities in the other half of the box at a later time. The velocities should be averaged, but do not average the velocity pressures. For round duct traverses, make a circle repre- senting the duct cross section. Make columns with a number for each test point, along with its distance from sides of duct, and for velocity pressures or velocities taken at points across three diame- ters at a 60° angles to each other. For oval duct traverses, make col- umns with a number for each test point, its dimension along the major and minor axis, and velocity pressures or velocities taken at points across the two axes of the duct, or show on a traverse sheet the horizontal reading. Data Reported: · System/unit number · Traverse air temperature · Location/zone · Duct static pressure | {}
30a311d9-07e1-41af-94e8-c73b820a06b2 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Testing, Adjusting, and Balancing 39.41 · Duct size · Design velocity · Actual average velocity · Barometric pressure · Duct area · Design flow rate · Actual flow rate Air Terminal Device Report The flow rate of all air terminal devices should be recorded. Ifthe final adjusted flow rate of any air terminal device deviates from design by more than ±10%, a note indicating the amount of variance shall be recorded in the "remarks" section of the report to provide known or potential reasons for such deviation. All correction factors should be shown in the remarks column for all velocity measure- ment instruments. Data Reported: · System/unit number · Location/zone · Test apparatus · Area served · Air terminal device number · Air terminal device type/ (from system diagram) model · Air terminal device size · Design flow rate · Design velocity · Preliminary velocity (as needed) · Make preliminary flow rate (as · Final velocity needed) · Final volume · Ar/effective area System Coil Report The performance of reheat coils or the water coil on terminal units should be recorded. Equipment Data: · System/unit number · Location/zone · Room number/riser number · Coil make · Model/size · Design flow rate · Design water supply temperature. Flow meter type/size Test Data: · Flow meter reading (if available). · Entering water pressure · Actual pressure drop · Entering/leaving water temperature · Design air pressure drop Design pressure drop · Leaving water pressure · Design water temperature drop · Actual water temperature drop · Entering/leaving air static · Actual air static pressure drop · Design air temperature drop · Entering/leaving air temperature · Actual air temperature drop pressure Packaged Chiller Test Report (cooling coil [db, wb] heating The control settings and the entering and leaving conditions at the chiller should be recorded. This data should be substantially completed and verified by the manufacturers' representatives and/or the equipment owner or installing contractor before the HVAC dis- tribution systems are balanced. Temperature and pressure differen- tial readings of the chiller unit evaporator and condenser should be recorded during the TAB procedures. Describe the flow measuring device when used. coil [db]) (List design and actual quantities where appropriate.) Unit Data: · Make/type · Model number/size · Serial number · Capacity refrigerant · Starter · Refrigerant · Heater size Condenser Data: · Condenser pressure/temperature · Entering/leaving water pressure · Water pressure drop · Entering/leaving water temperature · Entering/leaving air temperature · Actual air temperature drop · Water drop temperature Evaporator Data: · Evaporator pressure/temperature · Water pressure drop · Water temperature drop Compressor Data: · Make/model · Entering/leaving water pressure · Entering/leaving water temperature · Waterflow rate · Suction pressure/temperature · Serial number · Discharge pressure/ temperature · Voltage, T1-T2, T2-T3, T3-T1 · Kilowatt input · Chilled-water control setting · Low-pressure cutout setting · Oil pressure/temperature · Amps, A1, A2, A3 · Crankcase heater amps · Cond. water control setting · High-pressure cutout setting Refrigeration Data: · Oil level checked · Oil failure sw. diff. · Refrigeration level checked · Relief valve setting · Unloader set points · Percent cylinders unloaded · Purge operation checked · Bearing temperature · Vane position · Demand limit · Low-temperature cutout setting Package Rooftop/Heat Pump A/C Unit Test Report Test data from package units of all types shall be recorded. Ifthe unit has components other than the evaporator fan, DX coil, and compressor and condenser fan(s), use the appropriate report forms for: water or steam coils, direct fired heaters, electric coils, or return air fans. Unit Data: · Make/model number · Type/size · Serial number · Filter type/size · Fan sheave make · Fans sheave diameter/bore · Number, make, and size ofbelts · Type of heating section (use other appropriate form) · Make/frame · Volts/phase/hertz · Sheave make · Sheave centerline distance and adjustment · W/Rad/s · Full-load amps/SF · Sheave diameter/bore Motor Data: Evaporator Test Data: (list design and actual) · Total airflow rate · Total static pressure · Discharge static pressure · Suction static pressure · Outdoor airflow rate · Outdoor air db/wb Inc. ASHRAE, 2019 user. single for Licensed | {}
568f8c69-ff93-4280-a23e-92231b293927 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 39.42 · Return airflow rate · Return airflow db/wb · Make/type · Entering air db/wb · Leaving air db/wb · Serial number · Fan rpm · Voltage, T1-T2, T2-T3, T3-T1 · Refrigerant · Amps, A1, A2, A3 Condenser Test Data: (list design and actual) · Refrigerant mass · Compressor manufacturer/ number · Compressor model/serial number. Low ambient control · Suction pressure/temperature · Condenser pressure/ temperature · Crankcase motor amps · Compressor volts, T1-T2, T2- T3, T3-T1 · Compressor amps, A1, A2, A3 · Low-/high-pressure cutout setting · Number of fans/rpm · Condenser fan power/airflow rate · Condenser fan volts/amps/phase Compressor and/or Condenser Test Report Control settings, as well as entering and leaving conditions at the compressor and/or condenser, should be recorded. Because the bal- ancing firm is not necessarily responsible for startup or the proper operation of the machine, this form does not attempt to indicate the performance or efficiency of the machine except as may be deter- mined by the design engineer from the data contained therein. These data should be substantially completed and verified by the manufacturers' representatives and/or the equipment owner or installing contractor before the HVAC distribution systems are bal- anced. Temperature and pressure differential readings of the unit should be recorded during the TAB procedures. This report may also be used to record data for the refrigerant side of unitary systems, bare compressors, separate air-cooled con- densers, or separate water-cooled condensers. Unit Data: · Unit make · · Compressor make · Refrigerant mass · · Unit model/serial number · Compressor model/serial number · Low ambient control Test Data: (list design and actual for each) · Duct inlet/outlet static · Entering/leaving air db pressure · Cond. water temperature in/out · Cond. water pressure in/out · Control setting · Unloader set points · Low-/high-pressure cutout · Suction pressure/temperature setting · Cond. pressure temperature · Oil pressure/temperature · Voltage, T1 T2, T2 T3, T3 T1 · Amps, A1, A2, A3 · Kilowatt input · Crankcase heater amps · Number of fans/fan rpm/airflow · Fan motor make/frame/power rate · Fan motor volts/amps Cooling Tower or Condenser Test Report This data should be substantially completed and verified before the system is balanced. The pump data section is to be used for the recirculating pump in evaporative condensers, not the system used with cooling towers. Unit Data: 2019 ASHRAE Handbook- -HVAC Applications (SI) · Model number/size · Nominal capacity · Water treatment Pump Data: · Make/model · Motor make/frame · Volts/phase/hertz · Pump serial number · Motor W/Rad/s · Waterflow rate Fan Data: · Number of fan motors · Motor W/Rad/s · Motor sheave diameter/bore · Sheave centerline distance · Motor make/frame · Volts/phase/hertz · Fan sheave diameter/bore · Number of belts/make/size Air Data: (list design and actual for each) · Duct airflow rate · Duct inlet static pressure · Duct outlet static pressure · Average entering/leaving wb · Ambient wb Water Data: (list design and actual for each) · Entering/leaving water pressure · Water pressure drop · Entering/leaving water · Water temperature drop temperature · Water flow rate · Bleed waterflow rate Heat Exchanger/Converter Test Report The record final conditions for steam or hot water heat exchangers should be recorded. Unit Data: · Location · Service · Make/type · Model number/size · Serial number · Rating Steam Test Data: (list design and actual for each) Pressure · Flow rate Primary Test Data: (list design and actual for each) · Entering/leaving temperature · Temperature drop Entering/leaving pressure · Pressure drop Waterflow rate · Secondary Test Data: (list design and actual for each) Inc. ASHRAE, 2019 user. single for Licensed · Entering/leaving temperatures · Temperature differential · Entering/leaving pressure · Pressure differential · Waterflow rate · Control set point Pump Test Report · Circuiting type The final data on each pump is to be recorded. The actual impeller diameter entry is that indicated by plotting the head curve based on a no-flow head test or by actual field measurement where possible. Net positive suction head (NPSH) is important for pumps in open circuits and for pumps handling fluids at elevated temperatures. Design Data: · Service/location · Make · Model number · Serial number · Waterflow rate/head · Required NPSH · Pump rpm · Impeller diameter · Motor make/frame · Motor W/Rad/s | {}
1797be6d-76bb-457c-b317-a450b168b881 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Testing, Adjusting, and Balancing 39.43 · Volts/phase/hertz · Seal type · Full-load amps/SF Actual Test Data: · Number of flow heads · Actual impeller diameter · Full open head · Full open flow rate · Final discharge pressure · Final suction pressure · Final head · Final flow rate · Voltage, T1-T2, T-T3, T3-T1 · Amps, A1, A2, A3 Boiler Test Report The control settings and the entering and leaving conditions at the boiler should be recorded. Because the balancing firm is not nec- essarily responsible for start-up or the proper operation of the machine, these data do not attempt to indicate the performance or efficiency of the boiler except as may be determined by the design engineer from the data contained therein. This report should be substantially completed and verified by the manufacturers' representatives and/or the installing contractor before the HVAC distribution systems are balanced. Temperature and/or pressure readings ofthe boiler should be entered during TAB procedures. A flue gas analysis normally is not in the scope of TAB proce- dures, but data could be added in a commentary section if available and required by the engineer/owner. Unit Data: · Location/service · Model number/size · Fuel/input · Ignition type · Volts/phase/hertz · Make/type · Serial number · Number of passes · Burner control Test Data: (list design and actual for each) · Operating pressure/temperature · Entering/leaving temperature · Number of safety valves/size · Safety valve settings · High limit setting · Operating control setting · High fire set point · Low fire set point · Voltage, T1-T2, T2-T3, T3-T1 · Amps, A1, A2, A3 · Draft fan volts/amps · Manifold pressure · Safety controls check Instrument Calibration Report This report is to document the application and date of the most recent calibration test or calibration for each instrument used in the testing, adjusting, and balancing work. Data Reported: · Instrument/make · Serial number · Application · Dates of use · Date(s) of calibration Component Failure Report This report is intended to provide sufficient information to deter- mine cause of failure and provide feedback to the manufacturer, designer, or installer. This report should be used as soon as a prob- lem has occurred, and its inclusion in the final report is at the dis- cretion of the balancer. It should be noted on the report, if appropriate, that the analysis and recommendations are not to be considered final or expert. Data Reported: · Project · Component · System · Manufacturer · Serial number · Model number · Date · Architect/engineer · Contractor · Submittal data · Description and problem · Field test results · Probable cause · Recommendations Reports should comply with ASHRAE Standard 111, be com- plete, and include the location of test drawings. An instrument list including serial numbers and current and future calibration dates should also be provided. REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. AMCA. 1999. Laboratory methods of testing fans for rating. Standard 210- 99/ASHRAE Standard 51-1999. Air Movement and Control Associa- tion, Arlington Heights, IL. ASHRAE. 2016. Methods of testing performance of laboratory fume hoods. ANSI/ASHRAE Standard 110-2016. ASHRAE. 2017. Measurement, testing, adjusting and balancing of build- ing HVAC systems. Standard 111-2008 (RA 2017). www.ashrae.org /ashraeterms. ASHRAE. 2011. Proceduresfor commercial building energy audits, 2nd ed. ASME. 2003. Atmospheric water cooling equipment. Standard PTC 23-03 (RA 2014). American Society of Mechanical Engineers, New York. ASME. 2010. Boiler and pressure vessel code, Section VI. American Society of Mechanical Engineers, New York. ASTM. 2006. Standard test method for measurement of sound in residential spaces. Standard E1574-98 (RA 2014). American Society for Testing and Materials, West Conshohocken, PA. CTI. 2000. Standard specifications for thermal testing of wet/dry cooling towers. Standard Specification ATC-105. Cooling Tower Institute, Houston. ISA. 2008. Control valve capacity test procedures. ANSI/ISA Standard 75. 02.01-2008. Rahmeyer, W.J. 1998. Validation of design data on pressure loss coefficients of constant diameter pipe fittings, and development of design data on pressure loss coefficients of reducing fittings (RP-968). ASHRAE Re- search Project, Final Report. Sauer, H.J., and R.H. Howell. 1990. Airflow measurements at coil faces with vane anemometers: Statistical correction and recommended field mea- surement procedure. ASHRAE Transactions 96(1):502-511. BIBLIOGRAPHY AABC. 2002. National standards for total system balance, 6th ed. Associ- ated Air Balance Council, Washington, D.C. AABC. 2004. Test and balance procedures. Associated Air Balance Council, Washington, D.C. AMCA. 201 1. Fan application manual. Air Movement and Control Associ- ation, Arlington Heights, IL. Armstrong Pump. 1986. Technology of balancing hydronic heating and cooling systems. Armstrong Pump, North Tonawanda, NY. ASA. 2006. Specification for sound level meters. Standard 1.4-83 (R 2006). Acoustical Society of America, New York. ASHRAE. 2013. The HVAC commissioning process. Guideline 1.1-2007. ASHRAE. 2010. Energy standard for buildings except low-rise residential buildings. ANSI/ASHRAE/IES Standard 90.1-2010. ASHRAE. 2011. ASHRAE procedures for commercial building energy audits, 2nd ed. Griggs, E.I., W.B. Swim, and H.G. Yoon. 1990. Duct velocity profiles and the placement of air control sensors. ASHRAE Transactions 96(1):523- 541. NEBB. 2008. Procedural standards for testing, balancing and adjusting of environmental systems, 8th ed. National Environmental Balancing Bureau, Vienna, VA. NEBB. 1997. Testing, adjusting, balancing manual for technicians, 2nd ed. National Environmental VA. Inc. ASHRAE, 2019 user. single for Licensed Balancing Bureau, Vienna, | {}
2b95d1f9-ca1d-4b35-9675-c98f1c53ef59 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 39.44 2019 ASHRAE Handbook-HVAC Applications (SI) SMACNA. 2006. HVAC systems-Testing, adjusting and balancing, 4th ed. Sheet Metal and Air Conditioning Contractors' National Association, Merrifield, VA. SMACNA. 2002. HVAC air duct leakage test manual, 2nd ed. Sheet Metal and Air Conditioning Contractors' National Association, Merrifield, VA. Trane Company. 2007. Trane air conditioning manual revised. Trane, LaCrosse, WI. Inc. ASHRAE, 2019 user single for Licensed Related Commercial Resources | {}
30de2789-58e2-4641-b493-957674fea4f2 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 40 OPERATION AND MAINTENANCE MANAGEMENT ¦ Operation and Maintenance as Part of Life-Cycle Costs ¦ 40.1 ¦ ¦ --- ¦ --- ¦ ¦ Operating a Facility for Optimal Performance ¦ 40.2 ¦ ¦ Maintenance Strategies for Optimal Performance ¦ 40.3 ¦ ¦ Documentation ¦ 40.7 ¦ ¦ Staffing ¦ 40.8 ¦ ¦ Managing Changes in Buildings ¦ 40.10 ¦ 0 PERA TING a building, like operating any piece of machinery, entails dynamic assessment of when to turn systems on and what the set points of those systems should be. Examples include determining what level of lighting is needed for particular spaces and times, or how much ventilation air is necessary in certain rooms. Building operations also include deciding whether and when to turn those systems off or to a reduced level of output if they are no longer needed. Building maintenance involves performing any tasks designed to ensure that building systems are functionally available at acceptable levels when needed. Both operation and maintenance impact building performance, which is the building's ability to fulfill its design intent. As buildings age, their performance (particularly energy perfor- mance) drifts from design. Even new buildings can experience deg- radation in the first few years of operation due to errors in design or construction, manufacturing defects in equipment, or human activity (e.g., adjusting thermostat set points, adding plug loads, leaving things on when not in use). A Lawrence Berkeley National Labora- tory study (Mills 2009) found that retro- or recommissioning activ- ities that reset operating parameters to meet current facility requirements can improve existing building performance by 7 to 29%. Given the unavoidability of building system wear and perfor- mance drift, it is clear that active management of both the operation and maintenance is necessary to maintain the desired levels of building performance. Managing operation and maintenance (O&M) includes planning, implementing, and evaluating the outcomes of both operation and maintenance activities. More specifically, this consists of setting per- formance goals; developing strategies to achieve the established per- formance goals; communicating both the goals and the results to the building managers, operators, and users; and then providing direc- tion to building operators and maintenance staff, coordinating their efforts based on available resources, and supervising their work. This is all done with the end of achieving and maintaining the estab- lished building performance targets. Buildings may have several per- formance goals, including condition, availability, functionality, system reliability, water use, and indoor environmental quality. Energy use and energy cost are also two key parameters by which the performance of many buildings is measured. This chapter presents a general discussion of how buildings may be operated to minimize these. It also outlines various approaches to maintenance, as well as strategies, tools, and required documentation for both operations and maintenance management programs. 1. OPERATION AND MAINTENANCE AS PART OF LIFE-CYCLE COSTS Building life-cycle cost is the sum total of costs associated with owning and operating a building over its lifetime. Chapter 38 offers The preparation of this chapter is assigned to TC 7.3, Operation and Main- tenance Management. ![image](/image/placeholder) · ENERGY AND WATER · DESIGN · PERIODIC UPGRADES · ENGINEERING · INSURANCE AND TAXES · CONSTRUCTION · BUSINESS STAFF SALARIES · INSTALLATION · OTHER COSTS OF · FINANCING DOING BUSINESS ACQUISITION OPERATION DECOMMISSION MAINTENANCE IN-HOUSE OR CONTRACT · DEMOLITION STAFF · DISPOSAL · TRAINING · RESALE · SPARE PARTS · SALVAGE · TOOLS Fig. 1 Typical Building Life-Cycle Cost Categories a detailed discussion of life-cycle costs specific to operating and maintaining buildings. Figure 1 identifies the major categories of building life-cycle cost as acquisition, operation, maintenance, and decommissioning. The costs involved with each of these components depend on many factors, such as the nature, size, location, and management of the facility. However, several studies have found that, although the costs of operations and maintenance tend to be dwarfed by the costs of beneficial use and staff salaries, they exceed the costs of design and construction many times over. For example, Romm (1994) found that, over a 30-year period, operations and maintenance costs are about three times the cost of design and construction, and Yates (2001) found that operational costs are approximately five times construction costs over a 60-year building life. Results of the Building Owners and Management Association (BOMA) 2008 Experience Exchange Report indicate that, specifically for office buildings, operation and maintenance costs are approximately 11 times that ofinitial design and construction costs. Figure 2 shows the results ofBOMA 's 2017 analysis of office buildings: utilities, main- tenance, and repair accounted for more than 50% of typical operat- ing expenditures, further underscoring the need to prioritize building operations and maintenance management. Although the weight of cost elements clearly varies depending on the time period of study, type of facility, and other factors, it is generally understood that utility, maintenance, and repair costs are significant contributors to building life-cycle costs and that building performance cannot be optimized without also optimizing these principal factors. 2. OPERATING A FACILITY FOR OPTIMAL PERFORMANCE In essence, there are as many ways to operate a facility as there are facilities to be operated. During planning phases, the building de- sign team develops the building attributes (e.g., operating set points, schedules, sequences) to meet the owner's project requirements 40.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
b13dff30-9355-4d33-89fe-c83535b6f025 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 40.2 2019 ASHRAE Handbook- -HVAC Applications (SI) Table 1 Examples of General Operating Principles in Practice ¦ ¦ Building System ¦ Building System ¦ Building System ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Operating Principle ¦ HVAC ¦ Lighting ¦ Domestic Hot Water ¦ ¦ Turn systems on only when needed ¦ Heat and cool spaces no more than needed to maintain set points. Start morning warm-up/cool-down as late as possible while meeting IEQ set points upon occupancy. ¦ Turn lighting on only when spaces are occupied. ¦ Lower storage temperatures when building is unoccupied for extended periods. ¦ ¦ Turn systems on only to extent needed and optimize system output with available free sources ¦ Use economizers to offset need for mechanical cooling. Use recovered heat for preheating. Ventilate spaces based on demand. Reset working chilled- and heating-water temperatures based on outdoor air conditions. Use set-point setback and setups during unoccupied hours. ¦ Use multilevel general lighting and task lighting. Coordinate lighting power with available daylighting ¦ Use lowest storage temperature such that delivery temperature to farthest faucet matches design temperature. Use recovered heat to preheat hot water. ¦ ¦ Turn systems off when no longer needed ¦ When spaces are unoccupied for extended periods, reset cooling set points to maximal values and reset heating and ventilation set points to minimal values. As early as possible, allow system to coast to unoccupied set points, while maintaining IEQ set points during occupancy. ¦ Turn lighting off when spaces are unoccupied. ¦ Lower storage temperatures when building is unoccupied for extended periods. ¦ Chart Type: pie Utilities Repair and Maintenance Administration Cleaning and Grounds Upkeep Security item_01 25% 25% 10% 20% 5% Fig. 2 Facility Operating Expenditures for Typical Office Building (Adapted from the 2017 EER [BOMA]) (OPR), including those for energy performance. Thus, buildings should generally be operated in accordance with their design. How- ever, over the course oftime, building uses may evolve. Likewise, so do standards of thermal comfort and indoor environmental quality. Frequently, building operation schemes do not reflect current build- ing needs or the current state of technological advancement. Re- search has shown that many buildings have the potential to reduce energy consumption by 10 to 40% by modifying outdated operation strategies (Landsberg et al. 2009). In general, there are three guiding principles to optimize facility operation for energy performance: (1) only turn systems on when needed, (2) only turn systems on to the extent needed, and (3) turn systems off or to minimum acceptable output levels when accept- able. These three operating principles can be applied to all building systems that consume energy, including those for occupant convey- ance and service water. Table 1 provides examples of the principles in practical applications. Often these principles are instituted with the aid of existing control algorithms, though sometimes additional equipment is also required. Implementation of these principles varies with specific spaces. For example, consider two enclosed offices, one on the perimeter and one on the interior of a building. Both offices require an average illuminance level of 430 lx when occupied. However, whereas the interior office will likely always require the entire amount of in- stalled lighting power to achieve the required illuminance level, there will likely be times when artificial lighting in the perimeter of- fice can (and should) be offset by natural daylight to reduce energy consumption. There may even be times when the perimeter office needs no artificial lighting. Any electric lighting used during such times would constitute wasted energy and degrade building perfor- mance. Similar guidance applies to HVAC systems; spaces should be cooled, heated, and ventilated only when necessary; cooled just to the maximum acceptable temperature; and heated to the coolest acceptable temperature. Additionally, cooling, heating, and venti- lation should be coordinated with occupancy needs, outdoor condi- tions, and the availability of non-energy-consuming alternatives, such as economizer air to offset mechanical cooling. As an illustration, consider a space-heating boiler designed to provide 175 MW with 82°C water on a design day of -18°C. On winter days when the outdoor temperature is -4°C, the facility will still require heating, but it will not require the full 175 MW. An older way of modulating boiler output is to simply periodically fire the boiler and allow it to deliver 82°C water to the radiators. With this approach, the space may experience wide and uncomfortable temperature swings. Additionally, off-design-day system losses would be similar to design-day losses (i.e., they would be maximal). A more efficient method of modulation is to reduce the boiler output, low- ering the hot-water temperature as the outdoor temperature rises. This advanced operating method limits temperature swings and fur- ther improves system performance by reducing stack and distribu- tion losses. ASHRAE Guideline 36 provides more comprehensive guidance on operating facilities in a manner that improves building perfor- mance. It includes a list of detailed standardized sequences of op- eration specific to HVAC systems, which can be used to reduce energy consumption while improving indoor air quality. The se- quences are also designed to elevate fault detection from lagging to real-time, which can help reduce downtime. Inc. ASHRAE, 2019 user. single for Licensed | {}
b7bcebfa-6c2d-4b17-8714-43bb26fa6d9f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Operation and Maintenance Management 40.3 3. MAINTENANCE STRA TEGIES FOR OPTIMAL PERFORMANCE Maintenance tasks can include inspecting, adjusting, lubricating, cleaning, nondestructively testing, and repairing or re- placing components. These activities are designed to minimize the risk of failures and to preserve the performance of building assets, thus enabling them to be used effectively to meet owner and occu- pant requirements for thermal comfort, indoor environmental qual- ity, and energy efficiency. They also allow for the evaluation of conditions that can indicate the probability of acceptable future per- formance. These condition indicators can be evaluated by obser- vation, as with fan belt wear, or by measurement, as with compressor amperage draw. As soon as condition indicators suggest unacceptable future performance, remedial actions should be expe- dited to avoid failures or excessive repair costs. Thus, to ensure ac- ceptable building performance, condition indicators should be monitored and reviewed regularly. The time interval between successive assessments of a particular condition indicator defines the maintenance task frequency. Tasks may be performed once per shift, daily, weekly, monthly, quarterly, semiannually, annually, or at other intervals. For example, ASHRAE Standard 180 recommends that variable-speed drives on air handlers be checked for proper operation every six months and corrected if necessary. Task frequencies are typically derived from manufac- turers' recommendations, which are based on failure mode effect analyses, average time between failures, and other reliability data. However, these frequencies can (and should) be adjusted based on actual field conditions and data. For example, if acceptable condition indicators are found on three successive inspections of heat exchanger tubes, the interval between tube inspections can be ex- tended. Similarly, if unacceptable conditions are found in two suc- cessive inspections, the interval should be shortened, and in this case, depending on the criticality of the component, a systematic root cause analysis may need to be undertaken to identify and remedy the cause of unacceptable performance. Condition indicators, maintenance tasks, and task frequencies are developed based on the building performance objectives, which are the desired outcomes measured in terms of equipment and system deliverables. Primary deliverables are typically occupant thermal comfort, building energy consumption, and indoor environ- mental quality. Other deliverables may include system uptime, mean time between failures, mean time to repair, and normalized cost data. Building performance objectives should be quantitative, and efforts should be made to define any qualitative objectives in quantitative terms that can be more easily and objectively measured. Maintenance activities can be planned or unplanned, active or reactive but in general, there are three basic maintenance strategies that define when maintenance activities are performed. In run-to- failure maintenance, minimal or no resources are invested in main- tenance until equipment or systems break down. Once breakdown occurs, the equipment is repaired or replaced. This strategy is most often used when the cost of maintenance or repair exceeds the costs of replacement and acceptable losses in the event of a failure. The equipment may or may not be monitored for proper operation, depending on the consequences of a loss of beneficial use. For example, instead of repairing a vibrating window air conditioner, it may be operated until failure, then replaced with a new unit. Other types of equipment for which this strategy might be suitable are light bulbs; batteries; baseboard, wall, and other types of electric heaters; some valves; and fractional power recirculating pumps. Run-to-failure maintenance can be planned or unplanned. If unplanned, replacements are treated reactively with levels of urgency that depend on the criticality of the equipment and the sys- tem it supports. If planned, spare parts, components, or equipment $/hp/yr YEAR, PER HORSEPOWER PER DOLLARS RELATIVE ![image](/image/placeholder) 120 100 RUN-TO-FAILURE MAINTENANCE 80 PREVENTIVE MAINTENANCE 60 40 20 0 Fig. 3 Relative Maintenance Cost for General Industrial Rotating Equipment (Adapted from Hudacheck and Dodd 1976) are on hand to replace failed units so that interruptions of service are minimized. Preventive maintenance is planned and scheduled, either by equipment run time or by calendar. In this strategy, maintenance tasks are performed at frequencies recommended by the manufac- turer, industry standard, or as adapted to field conditions. This pro- active strategy is typically used for essential building equipment such as pumps, air handlers, boilers, ductwork, elevators, and trans- formers. One ofthe disadvantages of preventive maintenance is that it can lead to excessive maintenance costs because tasks are per- formed on schedule regardless of whether the equipment requires them. Thus, though preventive maintenance is currently the most common maintenance strategy, strategies specifically designed to optimize maintenance intervals continue to grow in popularity. Predictive maintenance uses measurements of the condition and/or performance quality of equipment and systems to guide main- tenance activities. Current conditions and performance can be com- pared to benchmarks determined by industry standards or facility historical performance. Rates and types of component wear and/or performance degradation are used to predict when failure is likely to occur. Corrective maintenance action can then be planned and sched- uled to take place, just in time before failure or loss of beneficial use. By basing maintenance actions on analysis of actual field data, both excessive and too infrequent maintenance can be avoided, thereby minimizing downtime and maintenance costs, maximizing mainte- nance personnel productivity, and optimizing plant reliability. As shown in Figure 3, Hudacheck and Dodd (1976) found that using a predictive maintenance strategy for general industrial rotating machinery can reduce maintenance costs by almost 60%. An evolving subcategory of predictive maintenance strategies re- ferred to under various names (e.g., condition-based maintenance, reliability-centered maintenance, benefit-based maintenance) is also in use. Each iteration focuses on a particular performance index to determine when and what maintenance should be performed. All forms of predictive maintenance, however, rely on nondestructive testing and observation to obtain the data on which future perfor- mance is predicted. Future failure predictions can be based on nearly any indicator of performance degradation that changes gradually over time. Typical nondestructive diagnostics include tools and tech- niques such as (1) thermal infrared imaging of electrical connections to determine whether mechanical joints are tight; (2) electrical cur- rent analysis to diagnose motor winding faults; (3) vibration analysis to identify imbalances, bearing wear, and misalignment in rotating Inc. ASHRAE, 2019 user. single for Licensed | {}
c25a2e4f-d615-420b-821a-0d372cfa7f61 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 40.4 2019 ASHRAE Handbook-HVAC Applications (SI) Table 2 Basic Maintenance Strategies ¦ ¦ Basic Maintenance Strategy ¦ Basic Maintenance Strategy ¦ Basic Maintenance Strategy ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ Run-to-Failure ¦ Preventive ¦ Predictive ¦ ¦ Principal objective ¦ Minimize maintenance tasks and expenses ¦ Minimize failure and maintain durability, reliability, efficiency, and safety ¦ Cost-effectively minimize failure and maintain durability,reliability, efficiency, and safety ¦ ¦ Key advantages ¦ Minimal staff requirements Minimal planning ¦ Extends asset life Maintains energy efficiency Reduces unplanned downtime ¦ All preventive strategy benefits Prevents unnecessary maintenance Optimizes maintenance costs Optimizes building performance Optimizes staff productivity Enhances ability to troubleshoot and identify root causes ¦ ¦ Key disadvantages ¦ Downtime costs Inability to plan Increased capital spending High inventory costs to minimize downtime ¦ Does not consider asset wear, which can lead to unnecessary maintenance expense ¦ Requires highly skilled staff to interpret data Requires monitoring and diagnostic equipment ¦ equipment; (4) chemical analysis of oil and grease for contamina- tion; (5) measurement of pressure differentials across filter banks and heat exchangers to determine optimum change or cleaning fre- quency; (6) measurement of temperature differentials to indicate proper performance of chillers and air-handling equipment; (7) sonic testing to measure material thickness at critical wear points in piping; (8) dye testing to identify cracks in components; (9) eddy current testing to evaluate the integrity of chiller heat exchanger tubes; and (10) visual inspection of fan belts to identify and characterize wear. Condition and performance measurements can be completed ei- ther continuously or periodically. Periodic measurements tend to be performed manually by operators on routine patrols or while per- forming other tasks. For example, the condition of water or glycol in hydronic loops can be checked by sampling fluids while cleaning strainer baskets and changing filters. Visually checking fan belts for wear or using ultrasonic microphones to detect leaks in steam or compressed air systems or to detect dry motor bearings can easily be incorporated into regular patrols. Although using manual patrols to detect faults does alert main- tenance staff to the presence of some issues that require attention (e.g., burned-out lamps), there may be a lag between the fault oc- currence and its detection. Depending on the equipment and its crit- icality, this lag could have a significant impact on performance. Additionally, there are some faults (e.g., failed outdoor air dampers) that are not easily discovered by patrol. Continuous monitoring pro- vides more information and enables identification of failures as they occur. Advancements in this area, coupled with building automation systems (BAS) and controls, have given rise to automated fault de- tection and diagnosis (AFDD). This software-based tool can keep operations and maintenance staff better apprised of the conditions of HV AC&R equipment and systems and can help manage both equipment-level and system-level maintenance activities. With AFDD, system performance indicators are automatically moni- tored, measured, and compared to expected values. The expected values may be input into the AFDD tool manually, or they may be extracted from a building information model (BIM), a computer- based tool increasingly used during building design and construc- tion. Discrepancies are identified and analyzed for root causes using algorithms based on engineering principles and empirical data, and a list of facility-specific recommended corrective action is generat- ed. AFDD greatly improves the operating energy efficiency of com- mercial HV AC systems, and its benefits have been validated in part by studies that document a wide variety of detected operating faults in common HVAC equipment (Breuker and Braun 1998; Breuker et al. 2000; Comstock et al. 2002; House et al. 2001, 2003; Jacobs et al. 2003; Katipamula et al. 1999; Proctor 2004; Rossi 2004; Seem et al. 1999). The immense value of AFDD lies principally in its ability to identify unwanted operating conditions that waste energy and that are not easily discoverable by cursory observation. This is particu- larly true for equipment that may be installed in locations without easy access (e.g., on roofs, above ceilings, in walls) that are inspected infrequently. Examples of detected faults include economizers in packaged air conditioners and heat pumps not operating properly; low or high (depending on the season) refrigerant charges; condenser and filter fouling; faulty sensors and controls; electrical problems; and air-handling units with too little or too much outdoor-air venti- lation, poor economizer control, failed outdoor-air dampers, and other problems. For a detailed explanation of AFDD, see Chapter 63. Choosing the Best Combination of Maintenance Strategies The ideal maintenance program preserves the required asset reliability and availability at the lowest cost by identifying and implementing actions that reduce the probability of failure to an acceptable level. It is unlikely that a single strategy will satisfy the availability, reliability, performance, and economic criteria for all assets in a facility. Thus, optimal maintenance programs generally incorporate all three basic strategies selectively. For example, a program might use a run-to-failure replacement strategy for light- ing, windows, and door weatherstripping; a preventive strategy for water heaters; and a predictive strategy for chillers and air handlers. Each basic strategy has advantages, disadvantages, and cost impli- cations that should be considered when defining a maintenance program. Table 2 provides a simple characterization of the basic strategies. When developing a maintenance program, the needs of each asset class or system should be considered separately. For each asset, an economic analysis weighing the costs and benefits of the three basic strategies should be performed. Because maintenance takes place over the life of an asset, the economic analysis will need to determine the net present values of costs and benefits. For details on performing net present value calculations, see Chapter 38. The economic evaluation may include many factors; however, those that are essential to strategy selection include · Owner and occupant requirements for availability and perfor- mance of the asset · Criticality of the asset function, both stand-alone and within any applicable systems · Cost to purchase the asset · Cost to replace the asset · Life-cycle labor costs for maintenance associated with the asset · Effects and consequences of failure Inc. ASHRAE, 2019 user. single for Licensed | {}
033ac87e-86ac-47d4-859f-fa08346f5a87 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Operation and Maintenance Management 40.5 · Cost of downtime resulting from asset failure · Safety issues related to asset failure · Cost of required staff training to maintain the asset · Cost of required instrumentation and diagnostic tools to maintain the asset Other factors may include benefits, such as productivity im- provements, improved indoor environmental quality, and enhanced occupant comfort and satisfaction. Qualitative benefits such as these do not have simple monetary values and will need to be assigned monetary worth. To reduce subjectivity, it is recommended that for- mulas be developed for valuing non-monetary benefits. Once the costs and benefits have been determined and summed, they can be compared to determine which of the three strategies has the greatest benefits, or the least cost. This information can then be used to more objectively select the optimal maintenance strategy for each asset, asset class, or system. Elements of Effective Operations and Maintenance Programs Simply put, building operation is the engaging, disengaging, and modulation ofbuilding systems, and building maintenance is the se- ries ofactivities performed to keep those building systems in accept- able working order. Often, the function of many building systems is largely automated, though building operators are still tasked with ensuring that those systems function correctly as intended. Addi- tionally, all building maintenance activities are performed by peo- ple. Thus, building operations and maintenance management is essentially management of the people who operate and maintain buildings. A general definition of management is the planning, or- ganizing, and control of a process or activity to achieve a certain outcome. A successful O&M management program can, therefore, be defined as one that manages the activities of the people who op- erate and maintain buildings, achieving effective use and preserva- tion of assets. Organization Whether for a single building or a facility complex of buildings, operations and maintenance management is a team effort. It de- mands the participation of the building owner, occupants, facility manager, and various other staff. A successful program requires (at least) · Senior management's commitment, in both form and action, to support the program · A shared understanding and appreciation of both the quantitative and qualitative benefits of operations and maintenance activities · A written program with clear objectives, methods, and targets that are directly tied to owner and occupant requirements and to busi- ness objectives · Development and integration of long- and short-term performance goals, objectives, and plans along with the tactical, day-to-day operational activities · Sufficiently budgeted resources (including people, training, and tools) to fulfill duties · Regular evaluation of performance, progress and outcomes with course corrections implemented as necessary · A well-organized system for maintaining records The importance of senior management': s commitment to operation and maintenance cannot be overstated. Senior management provides direction and leadership, and sets the course for the organization on every front. Without management support, operation and mainte- nance initiatives will lack adequate resource allocation and fail. Demonstrated support necessarily takes several forms, including · Establishing a policy statement that aligns facility performance with business performance · Assigning an accountable O&M advocate · Establishing a team to track facility performance that includes representatives from finance and human resources departments as well as the operations and maintenance functional group · Budgeting resources to support the program · Measuring and reviewing performance on a regular basis, recog- nizing and rewarding success. Ultimately, the implementation team will be responsible for per- forming the operation and maintenance tasks. The challenge for management personnel is to harmonize the two functions of opera- tions and maintenance to deliver an effective and cohesive program. Communication is also critical to success and best achieved through documentation of the program. The level of detail should allow each team member to comprehend his/her individual role, re- sponsibilities, and objectives, as well as how his/her contributions complement those of others. This helps ensure that everyone is working toward a common end and facilitates continuity when members leave or join the team. An essential aspect of the written program is specifying the rela- tionship between asset and building performance and the organiza- tion 's productivity. Communicating how the facility's performance fits into the organization 's mission and success makes it easier for business managers to make budget and resource allocation deci- sions that support facility operation and maintenance objectives. Like a building, the O&M management program is dynamic; it should be considered a living document. Over the life of a building, performance objectives are likely to change, as for example, when building tenants change or building systems are upgraded. At regular intervals and most especially at times of significant change, the O&M management program should be re-evaluated and updated to ensure that it continues to be aligned with building owner and occupant objectives. O&M Goals and Targets Setting goals is a process that begins with the end in mind and bridges the gap between the desired outcome and the point of origin. Objectives are broad statements describing fundamental desired outcomes, and goals are statements that describe the intermediate steps or achievements necessary to support the larger objective. For example, an organization 's senior management might establish an objective of being recognized amongst its peers for sustainability. To support this objective, several operations-related goals might be established, such as reducing water consumption by 2% annually, reducing energy waste by 15% by the end of the year, or achieving a total energy utilization index (EUI) of 1760 MJ/(m2.yr) in two years. The measurable parts of the goals are the targets. To be ef- fective, all goals must have targets. Targets should be clearly defined and specifically linked to building systems and equipment perfor- mance parameters. They should also be attainable by the equipment and systems to which they pertain; be results oriented and relevant to the overall objective; and establish a time frame to create an ap- propriate sense of urgency. Many facility goals will be related to the operation and perfor- mance of the building as a whole or to certain building systems. However, the maintenance program is generally established to mit- igate the degradation and failure of specific assets while enabling assets to deliver the required performance. Therefore, the mainte- nance program also needs goals and targets specific to maintaining equipment reliability: the probability that equipment or a system will perform its intended function for a specified period of time when used under specific conditions and environment. A related concept is durability, or the average expected service life. Manu- facturers quantify durability as design life, which is the average Inc. ASHRAE, 2019 user. single for Licensed | {}
73c86060-b855-407d-8f46-a20f0d4314d6 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 40.6 number of hours or years of operation before failure, extrapolated from accelerated life tests and from stressing critical components to economic destruction. Chapter 38 tabulates median years of equipment service life for many typical pieces of HV AC equip- ment. A common goal for a maintenance program is to have equip- ment attain or exceed its design life. Another common reliability-related maintenance goal focuses on uptime, the percentage of time the equipment is operable when needed. For example, the reliability of data centers is often defined, in part, by uptime, with target values ranging from 99.671% uptime (an allowable downtime of 28.8 h per year) to 99.995% uptime (an allowable downtime of26 min per year). Other related concepts that are more qualitative include capability, the ability of a system to satisfactorily provide the required level of service; and maintain- ability, which is a singular, calculated value representing the ease, accuracy, safety, and economy of performing maintenance. The term sustainability is also increasingly used in relation to operation and maintenance programs. In recent years, the term has been used generally to mean providing for the needs of the present while not compromising the ability of future generations to meet their own needs. However, when applied to operation and mainte- nance practices, its historical definition (able to be maintained at a certain level) is more useful. ASHRAE Guideline 32 suggests using the term to indicate that the performance level of operation and maintenance practices can be upheld and that they can keep building systems operating at their intended levels of performance. By adding a measurable target to any of these reliability-related concepts, they can be converted into a goal suitable for the mainte- nance group. When establishing maintenance goals, consideration must also be given to available financial and human resources, the age of equipment and systems, and capital projects planned for the near future. Additionally, maintenance goals must balance the cri- teria of building operating plans and the criticality of equipment and systems. For example, in systems for which continuous operation is a critical requirement, procedures must be established to perform maintenance while equipment is operating, or redundant capacity may be needed to allow for off-line maintenance without interrup- tion of operation of the equipment or system. Reviewing Performance Data Equipment- and system-level data should be reviewed regularly to ensure that all equipment is operating as intended. These data reviews can be thought of as an extension of the maintenance inspections. The frequency of the review should be such that any necessary adjustments to the equipment or system can be made within a reasonable time after discovery to minimize energy waste. In a facility equipped with a building automation system (BAS), it is important that operation and maintenance staff spend time each day looking at the system 's alarm history and analyzing the data it presents. Dillenbeck and Sheppard (2018) suggest conducting the alarm review during a daily meeting, during which the operator's log from the previous shift is reviewed line by line. The log should include the entry date and item number, location and description of the fault, action taken, and follow-up action recommended or requested. The log should also include a space for system specialists to indicate their notes, additional findings, actions taken or planned, and whether any additional follow-up by the operator is required. Automated fault detection and diagnosis (AFDD) software can be a valuable tool here because some fault conditions are not individu- ally alarmed. For example, consider an outdoor air damper that has failed in the open position. A BAS may not alarm this specific con- dition, but the fault can be inferred by knowledgeable and attentive operators from the unusually low (or high, depending on the season) temperature in the mixed air stream as compared to return and sup- ply air temperatures. 2019 ASHRAE Handbook-HVAC Applications (SI) In reviewing the daily log, pay special attention to any parame- ters that are not within allowable tolerances, because this can help to identify system correction or improvement opportunities. Regard- less of the nature of the poor performance, a thorough analysis should be conducted to ensure that the root causes of any problems have been identified. Only then can proper solutions be devised and implemented. There are a variety of analysis methodologies that may be used to pinpoint sources of poor performance. In selecting a problem-solving approach, care must be taken that the rigor of the analysis be commensurate with the scale and scope of the problem. Although daily logs are an important tool for the operations and maintenance team, they should not be viewed in isolation. Data trends are equally important. Trended data can help predict future performance in advance of potentially unwanted conditions, and this advance notice can often help to save energy as well. Commissioning Before, During, and After Turnover Commissioning is a quality assurance strategy that goes far be- yond equipment check/test/start procedures or the testing and bal- ancing of distribution systems. It is a formal process for integrating all project requirements throughout all the phases of building devel- opment. Commissioning verifies and documents that the facility and its systems are planned, designed, constructed and/or installed, tested, operated, and able to be maintained in order to meet the owner' s project requirements. It includes the development and doc- umentation of the owner's project requirements (OPR), the re- quired function of the facility and how its success will be determined, and regular reviews to ensure the OPRs are continuously met as the project progresses. Chapter 44 provides an overview of commissioning for HVAC systems. ASHRAE Stan- dard 202 and Guideline 0 offer guidance and define the standard of care that should be taken in delivering a commissioning project with all the major systems typical of a complete facility. Ideally, the systems and equipment of every new construction, addition, and alteration project should be commissioned before turning over the facility to the operations and maintenance team. This helps to ensure that a fully functioning and high-quality facility is delivered and that the facility management team is adequately trained and prepared to operate and maintain it. Commissioning facility projects also helps to enhance communication and reduce misunderstandings, reduce the number of change orders, reduce the total cost of project delivery, and improve the delivered quality and value for the building owner and occupants. Commissioning activities take place through the project delivery process, and a well-written commissioning specification will include provisions for the commissioning authority (CxA), the entity con- tracted to manage the commissioning process, to provide quality as- surance services through the warranty period or first year of occupancy. In addition to ensuring that systems continue to function without issue, involvement of the CxA through the initial occupancy period ensures that the building operators and maintenance team are adequately prepared to fulfill their duties as planned. The commis- sioning authority': s continued participation also helps to identify and address deficiencies in operator or maintenance personnel training. With the growing introduction of building controls and the fast pace of technological advancement, this benefit cannot be overestimated. Periodically, existing buildings may need to be commissioned. Over time, equipment performance may drift from design or build- ing function may change. Both recommissioning systems that were previously commissioned and retrocommissioning systems that have not previously undergone commissioning largely follow the same process as the commissioning of a new facility. However, there are some key differences. For example, in commissioning, the OPR are provided to the commissioning authority as part of the design documents that establish acceptable performance levels. However, in retro or recommissioning, the commissioning authority Inc. ASHRAE, 2019 user. single for Licensed | {}
d308a861-c1db-4047-8f64-779ab4e67632 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Operation and Maintenance Management 40.7 must develop and define the current facility requirements in con- junction with the building owner and occupants. Guidance for facil- ity retrocommissioning and recommissioning is provided in ASHRAE Guideline 0.2 Both recommissioning and retrocommissioning have a high po- tential to reset system performance to near original levels. However, drift from initial performance is a naturally occurring eventuality. To better ensure that building systems remain optimal throughout the facility service life, a policy of ongoing commissioning (OCx) should be considered. Ongoing commissioning is a continuation of the commissioning process throughout the service life of the build- ing. With ongoing commissioning, the original owner's project re- quirements are dynamically updated as they change. These updated requirements are referred to as the current facility requirements (CFR). Ongoing commissioning is cyclical and activities are re- peated at intervals appropriate for the facility, its use, and its man- agement team. Guidance for ongoing commissioning is also provided in ASHRAE Guideline 0.2 4. DOCUMENTATION Information on the facilities, systems, and equipment is essential for appropriate and informed operation and maintenance. It also aids in staff training; troubleshooting; updating program elements such as schedules and operating strategies; updating maintenance approaches; budgeting; assessing and communicating performance; and managing facility upgrade and retrofit projects. ASHRAE Guidelines 0 and 4 provide detailed guidance on preparing accurate, relevant operation and maintenance documentation that is easy to use and update. Additionally, ASHRAE Standard 90.1 includes documentation requirements for specific systems, such as building envelope, lighting, power, HVAC, service hot water, conveyance, and others. The design and commissioning team should ensure that a comprehensive systems manual (as outlined in these guidelines) is provided to the owner. For new construction, the design team should establish operation and maintenance documentation requirements as part of the owner's project requirements. Deliverables should support the expected maintenance strategy, skills ofthe maintenance and operations staff, and anticipated resources to be committed to performing operations and maintenance tasks. The requirements for operation and mainte- nance programs developed for existing facilities are the same, but the O&M staff may play a larger role in developing the documents (rather than the design team). O&M Documents For projects involving new equipment, it is critical that all infor- mation required to operate and maintain the systems and equipment be compiled before project turnover to the owner's staff. Moreover, it is essential that the information be made available to the entire fa- cilities department so that everyone responsible and accountable for operating and/or maintaining equipment has sufficient information to successfully perform their role. Whether operation and mainte- nance documentation is being assembled by the design team or by the facilities team, it is a good practice to compile the information into a series of interrelated manuals as it becomes available. In ad- dition to being used by the facilities team to operate and maintain the building, this information can be used to support design and con- struction activities, commissioning, initial training of O&M staff, and facility start-up. A complete operation and maintenance library includes a docu- ment directory, an emergency information and procedures manual, a facility operating manual with operating procedures and as-built construction documents for all major systems, and a facility main- tenance manual with detailed maintenance procedures and com- missioning test reports for all major systems and equipment. Recommended contents for each manual are provided in Table 3. The O&M library will serve the facility for the building's lifespan. It contains many documents and manuals that will likely evolve and grow in number over time. During this time, staff turnover may also occur any number of times. An operation and maintenance docu- ment directory lists and identifies the location of all the information and documents held by the facilities team. A directory that is well organized and current facilitates quick reference by both existing and new technicians and operators. Additionally, regardless of building type, function, or size, it is imperative that emergency information be directly distributed to emergency response personnel. Including this critical information in the operation and maintenance library ensures that it is immedi- ately available when needed by nontechnical persons (e.g., security and medical responders), as well as by technical persons (e.g., building operators, utility personnel, firefighters). Documentation Methods There are two basic methods for collecting and archiving opera- tion and maintenance documents: (1) hard-copy paper documents and (2) soft-copy, electronic documents maintained in a computer database. The chosen method should be aligned with maintenance program complexity and scope, as well as the accessibility needs of facility management and the skill level of maintenance staff. Both methods allow staff to enter, archive, update, and evaluate informa- tion on building systems and assets efficiently and effectively. How- ever, with advances in communications technology and the prevalence of computers and other smart devices, many staff mem- bers find it easier to maintain, access, and update documents elec- tronically and, at times, remotely. Nevertheless, in general, operators of small, single, and simple buildings still tend to rely on paper documents whereas operators oflarge, complex buildings and facilities are more inclined to use computer-based documentation methods. Regardless of which method is used, it is important that O&M staff be provided adequate time to regularly collect and doc- ument the required performance information. Otherwise, the data collected may not be of the quality or accuracy needed to support effective decision making. A computerized maintenance management system (CMMS) is a software tool to · Plan, schedule, and track maintenance activities · Store maintenance histories and asset inventory information · Communicate building operation and maintenance information · Generate reports to quantify maintenance productivity. It can be used by facility managers, maintenance technicians, third-party maintenance service providers, and asset managers to track the status, asset condition, and cost of day-to-day maintenance activities. The number and type of modules used in a CMMS are specified by the facility management team, depending on the facil- ity's needs and the management team ' s goals. Typical CMMS modules include provisions for requesting, generating, and tracking the progress of work orders; inventory control; maintenance plan- ning; equipment histories; maintenance contracts; and key perfor- mance indicator (KPI) tracking, analyzing, and reporting. Although a CMMS is not required to manage maintenance activ- ities, they are becoming more commonly used (Sapp 2016). When implementing a CMMS in a new or existing facility or upgrading an existing CMMS, the requirements of the tool, as well as communi- cation protocols and interfaces, must be carefully planned. Although using a CMMS has the potential to increase the facility management team 's efficiency and serve as a historical maintenance archive, more than 50% ofCMMS implementations fail (Berger 2009). One reason for failure is inadequate data population. To overcome this challenge, especially when new buildings and major renovations are designed Inc. ASHRAE, 2019 user. single for Licensed | {}
533a4c36-0141-4b74-9347-491e1684ece1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 40.8 2019 ASHRAE Handbook-HVAC Applications (SI) Table 3 Recommended Tables of Contents for Manuals Forming O&M Documentation Library ¦ Operating Manual ¦ Safety Manual ¦ Maintenance Manual ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ · General information - Building function - Building description with as-built construction documents - Energy budget - Operating standards with sequences of operation, set points, and acceptable ranges of values - Operating logs - Communication requirements: (1) performance, progress, and status reporting to management, and (2) advising occupants of seasonal changes and other alterations · Technical information - System descriptions, including as-built drawings - Seasonal start-up and shut-down procedures - Operating routines and procedures - Seasonal shutdown procedures - Emergency procedures - Other special procedures, for example operation during extreme weather - Basic troubleshooting Required testing - List of systems requiring testing, along with required test frequencies and procedures (e.g., fire protection system, boilers and pressure vessels, etc.) - Log of test dates and results - Contact information for contractors providing third-party testing ¦ · Communication protocols · Objectives · Key performance indicators (KPIs) · Regulations · Responsibilities and accountabilities · Building and building maintenance related hazards · Training requirements for emergency topics, type, and frequency · Required safety measures - Safe work practices - Engineering controls - Administrative controls - PPE · What to do in the event of an emergency, including the following, as applicable - - Fire - Security breach - Flood - Gas - Power outage - Plumbing overflow - Elevator - HVAC - Refrigerant release - Chemical spill ¦ · Equipment inventory - Equipment description, function, and associated system - Data sheets (approved submittals) with operating and nameplate data - Purchase date and warranty information - Equipment location · Maintenance program and procedure information - Maintenance plan with KPIs - Manufacturer installation, operation, and maintenance (IOM) instructions - Spare parts information (may be in the IOMs) - Corrective and planned maintenance task lists with frequencies, as applicable - Health and safety plan (HASP) - Required personal protective equipment (PPE) - Emergency procedures - Reports for air and water distribution systems testing, adjusting, and balancing (TAB); systems commissioning; factory tests; etc. - Repair histories ¦ and constructed using building information modeling (BIM), open information exchanges should be used. A supplement in the ASH- RAE Handbook Online version of this chapter provides a brief over- view of what open information exchange standards are, followed by a descriptive list of current and developing open information ex- change standards. Selecting the right software does not guarantee that using a CMMS will improve maintenance productivity, so it is important to evaluate, document, and align facility management pro- cesses with how the CMMS will be used. When implementing or up- grading a CMMS, adequate time should be allocated to design new processes and develop a set of system requirements, using a partici- patory approach that includes all stakeholders (Berger 2009). 5. STAFFING In addition to maintaining building assets in acceptable working order, it is important for maintenance staff to be able to provide good customer service. This means responding effectively to service requests and complaints from building occupants. The level of cus- tomer service provided, and how that service is perceived, are both determinants of success and continued support for the maintenance organization. Thus, determining quantity and necessary skills of staff is critical. Questions that every operation and maintenance depart- ment must answer include · How many persons are needed to operate the facility? How many are needed to maintain the facility? · What skills must the operations and maintenance teams possess? · Should the facility operation and/or the facility maintenance be self-performed or contracted with a service provider? One of the first steps in estimating staff size requirements is to translate the maintenance plan into a series of tasks and then to esti- mate the time necessary to perform each task, considering the num- ber and frequency of all tasks, as well as when they can or need to be completed. The size of the staff should be such that work loads are appropriate and that personnel can perform their assigned main- tenance tasks and duties both safely and within acceptable time limits. References, such as APPA (2011), provide standard labor units for maintenance tasks to help develop projections of time requirements. Facility operating hours also affect staff sizing. For example, hospital maintenance staff need to be on site around the clock to ensure building systems and other critical systems are functioning properly and to address any operational issues that may arise. Other considerations for staff sizing include available funding, staff sourcing, labor agreement provisions, vacations, sick days, when maintenance is likely to be required, and business imperatives. As with other organizational departments, the maintenance department should be staffed by people with a variety of talents. The nature of the job tasks dictates the required levels of skill staff mem- bers must possess to perform the work. For example, facilities with large central heating plants may require stationary operating engi- neers, and industrial facilities with large centrifugal chillers requiring a compressor teardown to inspect bearings every five years require a different level of skilled maintenance than a facility served by a single residential-style furnace or small packaged roof- top unit. Factors to consider when defining needed skill sets include the complexity and criticality of the equipment and systems to be maintained, the rigor of the maintenance program, the actual main- tenance tasks that must be performed, and whether any special skills or certifications are required to perform them. In addition to tradespeople and regardless of facility size, equip- ment type, or system complexity, there are certain roles that every Inc. ASHRAE, 2019 user. single for Licensed | {}
e2609f81-39cc-46a3-8f9a-760bbfa409bd | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Operation and Maintenance Management 40.9 Table 4 Common Roles Within Operations and Maintenance Department ¦ Role or Job Function ¦ Key Responsibilities: ¦ ¦ --- ¦ --- ¦ ¦ Shift Operator ¦ · Provide patrols and respond to emergent issues, including BAS alarms · Document condition indicators as required · Document conditions and issues requiring resolution or further attention · Attend each day's roundup meeting ¦ ¦ Equipment or system specialist ¦ · Triage reports from operators · Determine skills, tools, etc. required to resolve outstanding issues · Prioritize work · Ensure that corrective work is not dropped, waylaid, or misinterpreted · Work with site trades · Manage service contracts · Manage special system requirements (such as water treatment) for performance and safety ¦ ¦ BAS and controls programmers and technicians Planner/scheduler ¦ · Diagnose and resolve issues with the BAS instruments, electronic components, and computer code · Review operator and system reports · Issue work requests · Plan and schedule work · Review and update task descriptions ¦ ¦ Project leader ¦ · Work with stakeholders to develop project scopes · Maintain a prioritized list of proposed projects · Develop and execute capital funded projects · Assist in bidding work and securing contractors · Work with the contractors to execute the work ¦ ¦ Project comptroller ¦ · Track operating, maintenance, and capital project costs · Prepare regular reports for business management ¦ ¦ Facility manager, head of section, or department head ¦ · Oversee the BAS/HVAC section. · Provide guidance and direction to the department staff · Mange operating and capital budgets · Communicate facility and departmental needs and performance to senior management ¦ operation and maintenance department needs to fulfill. In large orga- nizations, the roles may be discrete; in small organizations, individual staff members may need to take on multiple responsibilities. Exact titles vary depending on the preference of the defining organization, but the essential functions, adapted from Dillenbeck and Sheppard (2018), include operators, specialists, planners, project leaders and department heads. Table 3 provides a summary of each role. Training To be effective and efficient, operation and maintenance man- agement staff must have both technical and managerial skills. Man- agerial skills include providing direction, guidance, correction, and coaching to the personnel who operate and maintain the facility. Facility management responsibilities may include developing oper- ation and maintenance strategies; determining program goals and objectives; and administering contracts with tenants, service provid- ers, and labor unions. Even when specialized contract maintenance companies provide certain services, the facility manager needs to be skilled in these areas to be a smart consumer of services. Technical skills include the ability to understand how mechanical and electrical systems operate and how equipment maintenance is performed, as well as the analytical problem solving expertise of a physical plant engineer. Additionally, because the in- terest in sustainable, high-performance buildings continues to grow, itis also suggested that staff be trained in how to recommission and/ or retrocommission systems. Doing so will help ensure continued efficient system operation, minimal operation and maintenance costs, and occupant satisfaction. The training program should be established with a written training plan. Ideally, the training plan would originate in the pre- design phase of a construction project and be incorporated into the project commissioning plan and construction documents. However, the training plan can be a stand-alone document and can be initiated at any time in the life of the facility. The plan should identify the knowledge and skills necessary for everyone with a stake in the facility. This includes the owner, facility managers, building opera- tors, and occupants. However, all stakeholders will not require the same degree or amount of training. Facility managers and operators will require in-depth systems and equipment training, whereas the training requirements for occupants will be more cursory and sim- ply provide a general awareness of how occupant behavior can impact facility performance. The plan will necessarily evolve over time. It should always be reviewed annually and define · The skills, knowledge, and performance expected to meet the key responsibilities of each job (refer to Table 4 for key responsibili- ties for some technical jobs) · Who needs to be trained, what current knowledge and skill levels are, and the budget and other resources allocated for training · The training schedule and how it fits into the larger project · The duration of initial training and requirements for refresher courses and/or continuous education · Specifications for trainers as well as training materials, delivery methods, and archives of reference materials · Specifications for documentation, verification, and records of training efforts and accomplishments For construction projects, training should incorporate the owner' s project requirements; for existing facilities, it should integrate the current facility requirements. Training for the facility management team should cover all the building systems and equipment, including mechanical, electrical, plumbing, controls, conveyance, and any spe- cial or unique systems (e.g., those for laboratories and cleanrooms) in the facility. As appropriate to specific job duties, training should cover the OPR and/or current facility requirements, as well as routine operation and maintenance. It should also include simple and major repairs, overhauls, failure modes, system interactions, and emergen- cy operations and procedures. ASHRAE Guideline 1.3-2018 pro- Inc. ASHRAE, 2019 user. single for Licensed | {}
94ec605d-dd7a-4659-bc31-ec85c35dd6d8 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 40.10 2019 ASHRAE Handbook-HVAC Applications (SI) vides additional guidance for development and implementation of training programs that support acceptable building performance. Self-Performance Versus Contract For most enterprises with large facilities, maintenance organiza- tions are not usually part of the core business, and economic con- siderations become an important factor in determining whether maintenance will be self-performed or provided by a contractor. For self-performance, another cost factor to consider is the cost of train- ing for development and training for various credentials. Wage structures, the available labor pool, staff skills, and ability to per- form specialized tasks are among the other factors considered when deciding to self-perform or contract facility O&M. Often, owners of (one or even several) small buildings cannot justify the expense of employing in-house maintenance personnel. Thus, they may decide to contract out all operations and mainte- nance work. In these cases, it is important that the contract specifies that the work to be carried out is consistent with the recommenda- tions in this chapter as well as industry standards and guidelines such as ASHRAE Standards 180 and 100 and ASHRAE Guidelines 4 and 36. The contract should also specify periodic operational checks of equipment operating schedules, set points, and indoor air quality. There should also be provisions to protect key building owner intellectual property and ensure it is available for continued use beyond the service provider's contract. Such intellectual prop- erty includes · Equipment tagging database and equipment tags installed in the field · Preventive maintenance task list and schedule for each piece of equipment · Operator's log books and electronic logs · Records of inspections and preventive and corrective mainte- nance performed · End-of-life and capital upgrade plans · BAS and other programmable system hardware and software, including all passwords and access permissions When the owner employs in-house operations and maintenance staff, responsibilities should include operation checks and mainte- nance duties (as needed and within staff capabilities), in addition to responding to occupant complaints and overseeing corrective ac- tions. At minimum, it is reasonable to expect changing filters, belts, and motors; lubricating bearings; and similar routine maintenance. In many buildings, particularly larger ones or campuses, in-house maintenance staff may include specialized expertise, reducing the need to retain contractors. However, whenever the operator cannot service and repair the systems or components installed, the owner should ensure that qualified contractors and technicians perform the work. Additionally, when there are regulatory or certification re- quirements to perform specialized work, the owner's in-house staff must either possess the certification, or the work must be contracted out to someone who does possess the required certification. Commonly, a mix of the two approaches is used: routine perfor- mance checks and inspection tasks are self-performed, and repairs to major equipment are contracted to factory-authorized service providers. This approach can reduce expenses associated with the tools and training necessary for infrequently needed maintenance activities. Often, with the mixed approach, cost-plus service agreements (in which the service provider is paid for all allowed expenses, plus a fee for profit) are used because they make it easy to begin work when only a partial scope of required work is known, especially in cases where costs can unexpectedly increase, such as with emergen- cy repairs. Where maintenance programs are well defined, and thus conducive to firm, fixed-price contracts, alternative contracting methods can be used. These agreements may have some form ofin- definite-quantity, indefinite-delivery provisions to cover unplanned maintenance or repair requirements. Recently, performance incen- tives such as savings sharing, extending the contract term, and award fees have been provided to contractors. 6. MANAGING CHANGES IN BUILDINGS For building projects, the owner should always work with the de- sign team to clearly define facility requirements. Even so, some of those requirements will likely evolve during the facility's life. Ex- isting building systems and equipment are based on the technology available to planners and designers at the time of preparation, con- struction, and installation. Data from the Energy Information Agen- cy's 2012 Commercial Building Energy Consumption Survey suggest that, in the United States, the median age of commercial buildings in use is over 40 years. In 2009, new buildings represented only about 2% of construction costs across the United States (Hol- ness 2009). Thus, even though operation and maintenance programs for targeted building performance may be followed, new technolo- gies (e.g., high-efficiency equipment, better control systems, sus- tainability advances) with the potential to increase overall building performance are likely to become available. Additionally, owner- ship, occupants, or building function may change, or the building footprint may be expanded. Satisfactory performance may even be redefined. Undoubtedly, such changes will also impact operation and maintenance programs. Managing such changes is key to continued acceptable building performance. Operation, maintenance, and maintainability of all building systems for the service life of the building should be con- sidered during the initial design. A facility with adequate space to inspect, repair, and replace components and equipment should be part of the owner's project requirements. The owner and designer must agree on the criticality of each system and establish criteria for access, redundancy, and component isolation. This work helps pre- pare for future replacements, upgrades, and renovations. Many renovation and retrofit projects will necessarily occur while the facilities are still operation. Construction projects in occu- pied buildings require a higher level of planning. Operation during construction can impact system design and create challenges for project scheduling. Often, this necessitates a phased installation. In these cases, it is generally helpful to select the construction team before design completion. This allows the expertise of all parties to contribute to discussions of constructability, maintainability, budget consequences, and other concerns before the design is finalized. See Chapter 60 for information on integrated teams. In all projects in existing buildings, but especially those retrofit projects that involve major conversions to new technologies, the value of the project should be assessed in terms of life-cycle costs. In addition to life-cycle factors of acquisition, operating, and main- tenance costs, other important considerations include (1) indirect costs of conversion, including potential revenue losses from associ- ated downtime; (2) service life of the retrofitted equipment or sys- tem; and (3) remaining service life of the building and whether it will be extended by the new system. After the renovation or retrofit project has been implemented, the new equipment and all building systems affected by it should be commissioned in accordance with ASHRAE Guideline 0. This quality assurance strategy helps ensure that all is operating as intended and delivering the expected results. Following the recom- mended commissioning process also ensures that the documenta- tion library is updated to reflect the most current operating protocols, parameter set points, and safety and maintenance require- ments and procedures. If a CMMS is in place, its database should also be updated to reflect the current equipment inventory. If BIM Inc. ASHRAE, 2019 user. single for Licensed | {}
7df2a6eb-1221-4c11-b836-59d669f308d1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Operation and Maintenance Management 40.11 was used in the original facility design, the building information housed in its database should also be updated. Properly commissioning a retrofit or renovation project also involves providing training to facility operations and maintenance personnel so that they know how to efficiently operate and effec- tively maintain the new equipment. This helps to preserve its bene- fits for enhanced building performance throughout the service life. As with new construction projects, much of the training material will be derived from the installing contractor's submittals, as-built record drawings, and test records. Training materials for HVAC sys- tems should be prepared in accordance with ASHRAE Guideline 1.3. Training materials for other building systems may follow the principles detailed in Guideline 1.3 but should align with the system manufacturer recommendations and fulfill the facility operating and maintenance staff knowledge needs. REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. APPA. 2011. Operational guidelines for educational facilities: Mainte- nance, 2nd ed. APPA, Alexandria, VA. ASHRAE. 2013. The commissioning process. ASHRAE Guideline 0-2013. ASHRAE. 2015. Commissioning process for existing systems and assem- blies. ASHRAE Guideline 0.2-2015. ASHRAE. 2018. Building operations and maintenance training for the HVAC&R commissioning process. ASHRAE Guideline 1.3-2018. ASHRAE. 2013. Preparation of operating and maintenance documentation for building systems. ASHRAE Guideline 4-2008 (RA 2013). ASHRAE. 2018. Sustainable high-performance operations and mainte- nance. ASHRAE Guideline 32-2018. ASHRAE. 2018. High-performance sequences of operation for HVAC sys- tems. ASHRAE Guideline 36-2018. ASHRAE. 2016. Energy standard for buildings except low-rise residential buildings. ANSI/ASHRAE/ACCA Standard 90.1-2016. ASHRAE. 2018. Energy efficiency in existing buildings. ANSI/ASHRAE/ ACCA Standard 100-2018. ASHRAE. 2018. Standard practice for inspection and maintenance of com- mercial building HV AC systems. ANSI/ASHRAE/ACCA Standard 1 80- 2018. ASHRAE. 2018. Commissioning process for buildings and systems. ANSI/ ASHRAE/ACCA Standard 202-2018. Berger, D. 2009. 2009 CMMS/EAM review: Power up a winner-How to find the right asset management system for your plant. Plant Services. April 13, 2009. www plantservices.com/aricles/2009/066//stage=Live BOMA. 2008. Experience exchange report (EER). Building Owners and Managers Association International, Washington, D.C. BOMA. 2017. Experience exchange report (EER). Building Owners and Managers Association International, Washington, D.C. Breuker, M.S., and J.E. Braun. 1998. Common faults and their impact for rooftop air conditioners. HVAC&R Research (now Science and Technol- ogy. for the Built Environment) 4(3):303-318. Breuker, M.S., T. Rossi, and J. Braun. 2000. Smart maintenance for rooftop units. ASHRAE Journal 42(11):41-47. Comstock, M.C., J.E. Braun, and E.A. Groll. 2002. A survey of common faults for chillers. ASHRAE Transactions 108(1):819-825. Dillenbeck, O., and D. Sheppard. 2018. The BAS/HVAC office: Organizing people to use the BAS to optimize building performance. ASHRAE Win- ter Conference, Paper CH-18-C016. EIA. 2012. Commercial buildings energy consumption survey (CBECS). Energy Information Administration, Washington, D.C. www.eia.gov /consumption/commercial/. Holness, G.H. 2009. Preface. In Energy efficiency guide for existing com- mercial buildings: The business case for building owners and managers. pp. xi-xii, D.R. Landsberg, M.R. Lord, S. Carlson, and F.S. Goldner, vol- ume authors. ASHRAE. House, J.M., H. Vaezi-Nejad, and J.M. Whitcomb. 2001. An expert rule set for fault detection in air-handling units. ASHRAE Transactions 107(1): 858-871. House, J.M., K.D. Lee, and L.K. Norford. 2003. Controls and diagnostics for air distribution systems. ASME Journal of Solar Energy Engineering 125(3):310-317. Hudacheck and Dodd. 1976. Jacobs, P., V. Smith, C. Higgins, and M. Brost. 2003. Small commercial rooftops: Field problems, solutions and the role of manufacturers. Pro- ceedings of the 2003 National Conference on Building Commissioning, Portland Energy Conservation, Portland, OR. Katipamula, S., R.G. Pratt, D.P. Chassin, Z.T. Taylor, K. Gowri, and M.R. Brambley. 1999. Automated fault detection and diagnosis for outdoor-air ventilation systems and economizers: Methodology and results from field testing. ASHRAE Transactions 105(1):555-567. Landsberg, D.R., M.R. Lord, S. Carlson, and F. Goldner. 2009. Energy effi- ciency guides for existing commercial buildings: The business case for building owners and managers. ASHRAE. Mills, E. 2011. Building commissioning: A golden opportunity for reducing energy costs and greenhouse gas emissions in the United States. Energy Efficiency 4(2): 145-173. Proctor, J. 2004. Residential and small commercial air conditioning Rated efficiency isn't automatic. ASHRAE Public Session, Winter Meeting, Anaheim, CA. Romm, J.J. 1994. Lean and clean management: How to boost profits and productivity by reducing pollution. Kodansha USA, New York. Rossi, T.M. 2004. Unitary air conditioning field performance. Proceedings of the Tenth International Refrigeration and Air Conditioning Confer- ence at Purdue, pp. R146. 1-R146.9. Sapp, D. 2016. Computerized maintenance management systems (CMMS). Whole Building Design Guide, National Institute of Building Sciences, Washington, D.C. www.wbdg.org/om/cmms.php. Seem, J.E., J.M. House, and R.H. Monroe. 1999. On-line monitoring and fault detection of control system performance. ASHRAE Journal 41(7): 21-26. Yates, A. 2001. Quantifying the business benefits ofsustainable buildings- Summary of existing researchfindings (extracts); Draftfor discussion. Building Research Establishment (BRE), Waterford England. www 1igho.orghts://shinkWice/EHENENEWAHIN@WNSe2020 Benefits.pdf. BIBLIOGRAPHY ASHRAE. 2007. HV AC&R technical requirements for the commissioning process. ASHRAE Guideline 1.1-2007. ASHRAE. 2010. ASHRAE green guide: The design, construction, and oper- ation ofsustainable buildings, 3rd ed. Blanchard, B.S., D. Verma, and E.L. Peterson. 1995. Maintainability: A key to effective serviceability and maintenance management. John Wiley & Sons, New York. Brambley, M.R., S. Katipamula, and P. O'Neill. 2005. Facility energy man- agement via a commercial web service. Ch. 18 in Information technology for energy managers, vol. II: Web based energy information and control systems case studies and applications, pp. 229-240, B.L. Capehart and L.C. Capehart, eds. Fairmont/CRC, Lilburn, GA. Braun, J.E. 1999. Automated fault detection and diagnostics for the HVAC&R industry. HVAC&R Research (now Science and Technology for the Built Environment) 5(2):85-86. Campbell, J.D. 1995. Uptime, strategiesfor excellence in maintenance man- agement. Productivity Press, Portland, OR. Fuchs, S.J. 1992. Complete building equipment maintenance desk book. Prentice Hall, Englewood Cliffs, NJ. House, J.M., J.E. Braun, T.M. Rossi, and G.E. Kelly. 2001. Section D: Eval- uation of FDD tools. In Final report: Demonstrating automated fault detection and diagnosis methods in real buildings, A. Dexter and J. Pakanen, eds. International Energy Agency on Energy Conservation in Buildings and Community Systems, Annex 34. VTT Technical Research Centre of Finland, Espoo, Finland. IFMA. 2009. Operations and maintenance benchmarks. Research Report 32. International Facility Management Association, Houston. IFMA. 2009. Eleven core competencies of facility managers. International Facility Management Association, Houston. cdn ifma.org/sfcdn /knowledge-base/ifmas-l I-core-competencies.poli'sfvsn=Omaintentence programs. APPA, Alexandria, VA. bokoms.appa.org/pdfs/131-05281612 .pdf. Inc. ASHRAE, 2019 user. single for Licensed | {}
79c831f0-048d-4e1d-a26e-b6b48e190226 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 40.12 2019 ASHRAE Handbook-HVAC Applications (SI) Kaiser, H. 2009. Capital renewal and deferred maintenance programs. APPA, Alexandria, VA. bokcms.appa.org/pdfs/131-05281612.pdf Katipamula, S., and M.R. Brambley. 2005. Methods for fault detection, diagnostics and prognostics for building systems-A review, part I. HVAC&R Research (now Science and Technologyfor the Built Environ- ment) 11(1):3-25. Katipamula, S., and M.R. Brambley. 2004. Methods for fault detection, diagnostics and prognostics for building systems-A review, part II. International Journal ofHVAC&R Research (now Science and Technol- ogy for the Built Environment) 11(2):169-187. Kats, G. 2003. The costs andfinancial benefits of green buildings: A report to California 's sustainable building task force. www3.cec.org/island cr-pl://dambanandjp/f/mintrx21/44Mance-eNvice-Blvvc pdf. Landsberg, D.R., S. Carlson, F.S. Goldner, J.M. MacDonald, and R.B. Slos- berg. 2011. Energy efficiency guide for existing commercial buildings: Technical implementation. ASHRAE. Li, H., and J.E. Braun. 2007. An overall performance index for characteriz- ing the economic impact of faults in direct expansion cooling equipment. International Journal of Refrigeration 30(2):299-310. Li, H., and J.E. Braun. 2007. An economic evaluation of the benefits asso- ciated with application of automated fault detection and diagnosis in rooftop air conditioners. ASHRAE Transactions 113(2):200-210. Li, H., and J.E. Braun. 2007. A methodology for diagnosing multiple- simultaneous faults in vapor compression air conditioners. HVAC&R Re- search (now Science and Technologyfor the Built Environment) 13(2): 369-395. Moubray, J. 1997. Reliability-centered maintenance, 2nd ed. Industrial Press, New York. NCMS. 1999. Reliability and maintainability guideline for manufacturing machinery and equipment, 2nd ed. National Center for Manufacturing Sciences, Ann Arbor, MI. National Academy of Sciences. 1998. Stewardship offederal facilities: A proactive strategy for managing the nation 's public assets. National Academy, Washington, D.C. NIBS. 1998. Excellence in facility management: Five federal case studies. Publication 5600-1. Facility Maintenance and Operations Committee, National Institute of Building Sciences, Washington, D.C. NRC. 1990. Committing to the cost of ownership: Maintenance and repair of public buildings. National Research Council, National Academy Press, Washington D.C. www.nap.cll.icatalog/9807/comminiting-host -of-ownership-maintenance-and-repain-of. Smith, A.M. 1993. Reliability-centered maintenance. McGraw-Hill, New York. Stum, K. 2000. Compilation and evaluation of information sources for HVAC&R system operations and maintenance procedures. ASHRAE Research Project RP-1025, Report. Whitestone. 2012. The Whitestone facility operations cost reference 2012- 2013, North American version. 6th ed., p. 292. Whitestone Research, Santa Barbara. Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
25508180-ab0a-407b-bf29-acbc688974a8 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 41 COMPUTER APPLICATIONS ¦ INTRODUCTION TO COMPUTING TECHNOLOGIES ¦ 41.1 ¦ Basic Cybersecurity Practices ¦ 41.5 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Software Availability ¦ 41.1 ¦ SOFTWARE APPLICATIONS ¦ 41.6 ¦ ¦ Custom Programming ¦ 41.2 ¦ Example Software Applications ¦ 41.7 ¦ ¦ Programming Languages ¦ 41.2 ¦ BIM and Data Interoperability ¦ 41.8 ¦ ¦ BIG DATA ¦ 41.2 ¦ BUILDING AUTOMATION AND CONTROL ¦ 41.8 ¦ ¦ HVAC Applications ¦ 41.3 ¦ Application and Purpose ¦ 41.8 ¦ ¦ CLOUD COMPUTING ¦ 41.3 ¦ Network Architecture and Components ¦ 41.8 ¦ ¦ MOBILE COMPUTING ¦ 41.3 ¦ Control Communication Protocols ¦ 41.9 ¦ ¦ Mobile Applications in the HVAC Industry ¦ 41.4 ¦ BAS Security ¦ 41.10 ¦ ¦ CYBERSE CURITY ¦ · 41.5 ¦ ASHRAE Resources for BAS System Design ¦ 41.10 ¦ COMPUTERS are used in a wide variety of applications in the industry. Rapid technological advances and the decreasing cost of computing power, memory, and secondary storage have changed many aspects of the HVAC industry. New HVAC design tools allow optimal solutions to be found in engineer- ing applications. Building operations benefit from low-cost net- working to achieve multivendor control system interoperability. Consulting engineers can search manufacturers' equipment and specifications online. Designers can collaborate from remote loca- tions. More powerful applications that are also easier to use are now affordable by a wider segment of the industry; many HVAC calcu- lations, such as heating and cooling loads, can be performed easily and automatically. Business applications and infrastructure have also positively affected the HVAC industry. Open communications standards and internetworking allow fast, efficient communications throughout company and industry circles. HVAC design, manufacture, installa- tion, and maintenance functions benefit as businesses build computing infrastructure through corporate information services (IS) or information technology (IT). Many cloud computing advances in the business community have been adopted by the HV AC industry as de facto standard practice. 1. INTRODUCTION TO COMPUTING TECHNOLOGIES Because of rapid advances in computer technology, computers offer tremendous power at very low cost. However, the total cost of ownership of a personal computer is not limited to the cost of the computer hardware. Software, network connectivity, support, and maintenance expenses quickly surpass the initial cost of hardware. Selecting a computer platform includes a wide variety of issues, such as · Analysis of application needs · Corporate computer support architecture and standards · Vendor support, including guaranteed response time · Central processing unit (CPU) power, random-access memory (RAM), graphics processing units (GPUs), and secondary or hard disk storage capacity · System compatibility and interoperability between vendors · Ease of use and required training · Data back-up strategy: how will the data on the computer be restored in the event of a system failure? · Security issues: what data will be accessible, and how will data be protected from unauthorized access? The preparation of this chapter is assigned to TC 1.5, Computer Applications. · Network communications capability and compatibility · Technical support live and/or online, including driver update support · Information system infrastructure/interoperability requirements · Technology reliability and obsolescence · Total cost of ownership Virtually all personal computers and laptop computers now have more than enough speed for basic business applications such as word processing and spreadsheets. Personal computers differ in their ability to handle multimedia graphics and sound, which are useful in advanced software applications. More recently, cloud computing solutions with subscription models have become common in the industry for agile development and deployment of software applica- tions and business services. An information system comprised of computer networks depends on the ability of computers to communicate with each other in a stan- dard architecture. Technological advances have resulted in computer systems becoming obsolete in less than five years. Therefore, it is important to plan for compatibility with future business computer requirements. Software and hardware must match the needs of the user, and be consistent with the business system architecture. System architecture standards from organizations such as the Institute of Electrical and Electronics Engineers (IEEE), the Amer- ican National Standards Institute (ANSI), and the International Organization for Standardization (ISO) have resulted in well- defined standards such as Ethernet, TCP/IP, and HTTP. The combi- nation of popular standards has resulted in network and Internet accessibility from local computers, and the adoption of cloud com- puting using remote computer resources. 1.1 SOFTW ARE AV AILABILITY Software can be purchased from manufacturers, distributors, rep- resentatives, discount stores, and computer specialty stores. Soft- ware price, support, return policies, and distribution vary from vendor to vendor. During installation, most software displays a detailed software license granting use rather than ownership of the software program. This license gives specific restrictions on how the software is to be used. Most high-volume software does not offer direct support, but many software companies offer pay-per-incident and other fee arrangements if desired. Many applications have online discussion groups or message boards, where solutions to problems may be found. With the advent of cloud computing, soft- ware subscription services are becoming more common, allowing users to purchase access to software for a period of time rather than purchase a physical product. Besides proprietary software tools, HVAC applications are widely available as open source software. Following are some of the open source licensing types. 41.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
95396fec-cba1-4295-b638-493eda19011d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 41.2 2019 ASHRAE Handbook-HVAC Applications (SI) Freeware is copyrighted software that is free. The user can run the software, but must obey the copyright restrictions. Public domain software is available to the public for little or no charge. Public domain software, which is not copyrighted, is often confused with freeware, which is copyrighted. Public domain soft- ware can be used without the restrictions associated with copy- righted software. Shareware is software available for users to try before buying it; after the trial period, users are expected to register or stop using the application. There is usually a nominal registration fee. 1.2 CUSTOM PROGRAMMING Using an existing software package is usually preferable to designing a custom application, which is much more expensive and potentially riskier. This is especially true for large, mission-critical software such as client-server applications. If, after careful evalua- tion, prepackaged software will not suffice, the choice must be made between in-house and outside development. Custom software can be (1) contracted out to a specialized firm, (2) developed solely by internal staff, or (3) developed by internal staff with consultation help by an outside firm. Contracting to an outside firm involves hiring a specialized outside party to define, estimate, schedule, and create the software. Funds should be budgeted for the outside organization to support modifications or enhancements not specifically covered in the con- tract. Contracting outside is suitable for an organization that does not have the resources or expertise to accomplish the project. Dis- advantages of this approach include the expense and lack of control over the program. Licensing and ownership issues must be defined in the contract. Developing the program internally is viable only if the skills and resources are available. Internal projects are easier to control because the people involved are co-located. Consultation help from an outside firm involves a skilled out- side party assisting internal staff, who may have insufficient skill in the area on their own. Outside firms can provide expertise to get a project going quickly. Long-term support and maintenance of the software are done in-house. Specifications are key to the success of a software project. Cal- culations, human interface, reports, user documents, and testing procedures should be carefully detailed and agreed on by all parties before development begins. Software testing should be specified at the beginning of the project to avoid the common problem of low quality resulting from hasty and inadequate testing. Design testing should address the human interface, a wide range of input values including improper input, the various functions, and output to screen, disk, or other media. Field tests should include conditions experienced by the final users of the software. With any development approach, good, understandable docu- mentation is required. If for any reason the software cannot be adequately supported, the program will have to be replaced at sub- stantial cost. 1.3 PROGRAMMING LANGUAGES HVAC application software is written in a variety of computer languages. Most commercial software is written in C++, C#, or C, to allow fast speed and efficient use of resources. In addition, there are several programming and scripting languages such as Python, JavaScript, Ruby, Perl, and Swift used for web and mobile comput- ing and customized software applications. The choice of program- ming language depends on several factors, including the programming paradigm (e.g., compiled versus interpreted, proce- dural versus functional versus object oriented), operating system, memory requirements, development environment, and user- interface features. The targeted deployment platform (e.g., stand- alone desktop, web-based application, a combination of both) often determines the programming language used. It is also more common to see several programming languages used to develop independent components of a software application and then inte- grated to deliver an end-user software tool. For example, energy simulation software tools use a procedural programming language to perform the calculations but use a different programming lan- guage for multiplatform user-interface development. In addition, there are special application programming lan- guages, such as MATLAB and R, used for mathematical program- ming and analysis of large amounts of data. 2. BIG DATA The term "big data" is often used to reference related concepts, such as business intelligence and data mining, but differs in that it refers to data sets that are so voluminous and complex that tradi- tional data processing application software is inadequate to deal with them. Big data challenges include capturing data, storage, analysis, search, sharing, transfer, visualization, querying, updating, and information privacy. There are four recognized dimensions of big data: velocity, volume, variety, and veracity (Figure 1). Data sets grow rapidly, in part because they are increasingly gathered by cheap and numerous information-sensing Internet of things (IoT) devices, such as mobile devices, aerial (remote sensing) devices, software logs, cameras, microphones, radio-frequency identification (RFID) readers, and wireless sensor networks. The world's technological per-capita capacity to store information has roughly doubled every 40 months since the 1980s; as of 2012, 2.5 exabytes (2.5 1018) of data are generated each day. By 2025, mar- ket intelligence advisors predict data will exceed 160 zettabytes (1021). One question for large enterprises is who should own big data initiatives that affect the entire organization. Relational database management systems, desktop statistics software, and visualization packages often have difficulty handling big data. The work may require massively parallel software running on tens, hundreds, or even thousands of servers. What counts as big data varies depending on the capabilities of the users and their tools. Expanding data collection capabilities and maturing software tools make big data a moving target. Big data entails a shift of analytical focus, from descriptive analyt- ics to predictive and prescriptive analytics. Descriptive analytics han- dle questions about what happened in the past, typically in the form of reporting; predictive analytics tend to address what might happen next, and prescriptive analytics attempt to develop a response. The main benefits ofbig data analytics are to (1) draw insight from data, (2) make better decisions based on that insight, and (3) automate those decisions and formulate them into a process. A big data solution may address a particular problem; it is valuable that a given solution · · · · · · · · · · · · Inc. ASHRAE, 2019 user. single for Licensed ![image](/image/placeholder) BATCH · TERABYTES NEAR TIME · RECORDS REAL TIME · TRANSACTION LIVE STREAM · TABLES RATE OF VELOCITY VOLUME · FILES ANALYSIS BIG AUTHENTICITY DATA AVAILABILITY ACCOUNTABILITY TRUSTWORTHY VERACITY VARIETY ORIGIN · UNSTRUCTURED REPUTATION · SEMI-STRUCTURED CLEANSED ● STRUCTURED Fig. 1 Four Vs of Big Data (Courtesy of Ennovision, ennovision.co.uk/) | {}
0b43ca04-9b5a-487f-bfd6-1afddcd906de | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Computer Applications 41.3 is rooted in the original problem. For example, user churn prediction should reduce user churn and therefore avert a decline in revenue from subscriptions. Building a business case for big data analytics starts with a defined problem, not with data or technology. 2.1 HVAC APPLICATIONS In the context of HVAC&R, big data tends to refer to the use of predictive analytics, user behavior analytics, sentiment analytics, operational analytics, or certain other advanced data analytics methods that extract value from data. Analysis of data sets can find new correlations to spot use trends, equipment interoperability problems, and so on. With the explosive growth of the IoT, there are more connected devices offering more information than ever before. The ability to analyze this data has also vastly improved. Intelligent analytics tools have meant that data sets that previously would have been far too large to analyze for traditional methodologies are now a valuable source of insight into how to improve systems and behaviors. For instance, facility managers are now able to gather information from thousands of data points in a building. The installation of a vast array of information-gathering and intelligence/analytical technologies (e.g., smart sensors, smart meters, smart breakers) to inform opera- tional decisions can be crucial to operator oversight of a facility. Using data analytics, large volumes ofbuilding data can be trans- formed into actionable information that targets underlying problems and creates opportunities for energy savings. This type of manage- ment can save up to 20% annually on maintenance and energy costs by refining service programs and achieving optimal building perfor- mance and cost effectiveness. For example, with smart HVAC sys- tems and the right sensors, a building manager can be made aware of system leakages where cool air may be migrating from the build- ing, causing energy loss overnight. Sustainability This same technology can simultaneously assist in driving envi- ronmental sustainability. For example, by checking carbon dioxide levels to see if people are in the room, a building management system (BMS) can manage the HV AC systems to respond to presence appro- priately, saving energy where possible. If someone is detected, a BMS may turn on ventilation to bring in fresh air, turn more lights on, and adjust the temperature out of a power-conserving deep set- back. When people leave, everything goes back to an energy-saving state. Major drivers for investment in technology and building design are commonly a combination of saving operational cost, the need for innovation, increased productivity, and talent attraction/retention. Economic Benefits There are maintenance-cost benefits to getting equipment man- agement right with big data and analytics. Smart systems offer embedded analytics, including automated fault detection and diag- nostics (FDD). By automating detection and diagnosis of equipment health, FDD can help organizations better predict the timing of costly equipment failure. This allows them to make informed decisions when it comes to addressing problems and repairing equipment before critical failure. Problems such as unnecessary equipment operation, suboptimal strategies, faulty equipment, or poorly tuned loops that are undiagnosed and creating energy wastage and comfort issues, can be addressed by these analytical techniques. For facility managers, the return on investment (ROI) ofa project is often of primary concern. Though one-off investments in infra- structure may appear to be simple solutions, their long-term ROI is often uncertain. A new solar panel may promise a reduced energy bill; however, without proper analysis, it may not properly address a facility's underlying energy inefficiency issues. When decisions are made without proper guidance by data and intelligence, those investments may prove troublesome or expensive. Guided by experience and insight, the optimal use of an invest- ment can be identified. When choices range from repairing/ replacing existing and outdated infrastructure to analyzing and resolving system inefficiencies and/or recommending new infra- structure where necessary, the best ROI will be found by someone with extensive training and knowledge of the latest trends and tech- nologies. 3. CLOUD COMPUTING Since 2010, cloud computing has become a very common, cost- effective solution to access high-performance computing infrastruc- ture and services on an as-needed basis. The National Institute of Science and Technology (NIST) defines cloud computing as "a model for enabling convenient, on-demand network access to a shared pool of configurable computing resources (e.g., networks, servers, storage, applications, and services) that can be rapidly pro- visioned and released with minimal management effort or service provider interaction. " Essential Characteristics · On-demand self-service: provision computing capabilities such as servers, network storage, and databases · Broad network access: accessibility of cloud resources from mobile devices, laptops, workstations, etc. · Resource pooling: pooling resources to serve multiple customers independent of location of the physical resource · Rapid elasticity: rapidly and elastically provide the computing resources automatically as needed · Measured service: monitor, control, and report resource usage with a metering capability Service Models · Software as a service (SaaS): application software running on a cloud infrastructure, accessible over Internet · Platform as a service (PaaS): tools for consumers to develop and deploy application software · Infrastructure as a service (IaaS): capability provided to consumer for computer servers, storage, and resources Deployment Models · Private cloud: provided for exclusive use by a single organization comprising multiple users · Community cloud: provided for exclusive use by a specific com- munity, either on or off site · Public cloud: provided for open use by general public · Hybrid cloud: a composition of two or more of the preceding models that remain entities, but work together unique Several leading cloud service providers have developed multiple data centers that provide a full range of cloud computing resources and infrastructure to support all these deployment models. HVAC industry applications have begun to adopt cloud computing for most aspects of design, documentation, data storage, and mobile device access to all building design and operational data. Big data and cloud computing together have enabled collection and analysis of BAS data for improving building operations and automation of fault detection and diagnosis. 4. MOBILE COMPUTING There are two distinct, common types of mobile applications: web-based and native. Web-based means, as the name implies, that a web site has been designed to be functional and visually appealing on a smaller (mobile) screen such as a cell phone or tablet. For this reason, these applications require Internet access via Wi-Fi or cellular data because they are just a user interface for the full web site. Native mobile applications, though still designed to operate and Inc. ASHRAE, 2019 user. single for Licensed | {}
520f1e72-b7d0-4d77-a760-a79ae6c15502 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 41.4 2019 ASHRAE Handbook-HVAC Applications (SI) be user friendly on a smaller screen, operate via a device's operating system, so Internet access is not required to use the application. There are benefits and drawbacks to each type of mobile application. w eb-based applications are most common: examples include apps on a phone (e.g., navigation, social media). These are easy to use and easy to maintain. Computing does not require as much memory or computing space, and these applications typically work across all operating systems. This allows owners of the app to main- tain updates more easily; updates can be sent out to all users at one time. However, with any web-based application, users are at a higher security and privacy risk because all data is being sent out through the web. Some of these risks can be mitigated with privacy settings, but these could limit the application': s full operating abilities. Even common privacy settings, such as limiting access to location or pho- tos and data, can prevent the application from functioning at its full capability. Native applications are typically purchased or sold alongside another product and operate using a mobile device's operating system. These are typically designed to work on one type of oper- ating system. These apps rely on a device's operating system, so they may not require Internet access (i.e., can operate at all times), and data is typically more secure. These applications are typically designed by industry experts (including but not limited to HVAC), so the user can be confident in the data/results provided. However, because the data uses a phone 's operating system, backing up data can be challenging. Users must also be cautious in using these applications, because apps can be written in any lan- guage or for any operating system. In the case ofHVAC design, ifa designer is using more than one company to design a system (e.g., chillers and cooling towers), this potentially forces the user to design one subsystem at a time. This limits the designer to subsys- tem efficiencies, a disadvantage. Some of this can be avoided if the user is aware of the operating systems up front. Companies that design mobile applications and mobile applica- tion platform software have also created hybrid mobile applications. Hybrid mobile applications are designed at a variety of levels that take the best of each application type. To choose the right application, various questions need to be addressed. As with any technology, those of greater capability also require more time and cost to develop and involve more difficult maintenance. Important questions to ask are Inc. ASHRAE, 2019 user. single for Licensed · What is the budget? · What is the (or the customer's) required security level? · How much time is available to implement a solution? · How much does the end user know about mobile applications? · What is the end user's operating device capability? · How user friendly/easily accessible should the mobile application be? · How many end users will there be? If outsourcing, there are various companies that provide enter- prise mobile application solutions (i.e., mobile applications designed for more complex projects that are typically associated with enterprise-size projects, with the complexity determined by the Many applications today are designed to have a combination of both web-based and native application traits. Some companies even have a mobile application platform advanced enough to take multiple native applications and provide a means of operating all applications at once. Once the selection questions are answered for a given project, the appropriate route can be taken. For those in HVAC looking to add mobile app development to a business, there are a couple of options. As with most business concepts, solutions can either be developed in house or outsourced to an expert. This depends on the complexity of the project and the software develop- ment capability at a given company. answers to the questions previously listed). Complexity increases with the number of users, or more back-end data analysis (native application capabilities) is needed. Lack of time for a solution or a high first-cost, more user-friendly application both increase com- plexity. When outsourcing, look for products/platforms that can · Allow a designer to build a mobile application · Design multiple levels of hybrid native/web-based mobile appli- cations · Combine mobile apps that a company already has available The best option is not the same for every company or project, and it is up to the project lead or company managers to determine the best course of action. However, a clearly defined goal and project specifications help optimize use of mobile applications. 4.1 MOBILE APPLICATIONS IN THE HVAC INDUSTRY HVAC companies often develop their own mobile application plat- form for their employees. However, to provide HV AC industry mem- bers with tools necessary to the industry, ASHRAE has supported development of several mobile applications. The applications are intended provide members with tools that can be used quickly in the field to check compliance with ASHRAE standards and equipment performance. The following is a brief introduction into some of the most commonly used ASHRAE supported applications. Psychrometric App. The ASHRAE HV AC Psychrometric App is designed for users to easily view a psychrometric map while out in the field. This app allows users to plot points and processes on a fully customizable psychrometric map. Then, if necessary, results from the points can be shared via e-mail for later use. Figure 2 shows the standard home page of an example psychrometric chart. Cross hairs enable the user to know exactly where the cursor is pointing on the map. To plot, users double-tap on a point in point mode. Because it is only available on iPadⓇ or iPhoneⓇ this application , is intended for users who are in the field or in a conversation with a customer when full use oftheir tools is not available. For this reason, both individual point processes and a PDF of a psychrometric chart can be e-mailed using the e-mail icon. Duct Fitting Database. This application, based on ASHRAE's desktop Duct Fitting Database tool, allows users to produce pres- sure loss calculations for the more than 240 ASHRAE duct fittings from the field. Calculations can be in SI or I-P units and can easily be shared via e-mail for further use or analysis. 90.1 Energy Cost Budget Application. This ASHRAE-sponsored tool enables users to model compliance with ASHRAE Standard 90.1-2010. This application follows the energy cost budget form in the User 's Manual (ASHRAE 2016a) and allows users to enter all available site details and then export the data into the energy cost budget report in ExcelⓇ. This application is web based, and the data can be accessed via any device that has Internet access. HVAC ASHRAE 62.1. This application allows users to perform calculations from the 2007 and 2013 versions of ASHRAE Stan- dard 62.1, Ventilation for Acceptable Indoor Air Quality. It loosely follows the 62MZCalc.xls ExcelⓇ spreadsheet from the ASHRAE (2016b) 62. 1 User 's Manual for each project; however, as with most applications, the capabilities exceed that of manual entry docu- ments. Users can create an unlimited number of projects. Each proj- ect can be created quickly, and calculation results can be shared via e-mail for a detailed analysis when the user is no longer in the field. HVAC PT Chart Application. This application makes quick cal- culations of refrigerant properties in the field. Users can choose the refrigerant and units they are interested in to obtain refrigerant pres- sure or temperature. | {}
1f49aebb-dfe9-4eef-81e4-471dcb8323f2 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Computer Applications 41.5 HVAC Duct Sizer Mobile Application. This application is sim- ple compared to some of the others described here, which involve more intricate calculations. However, it is still useful for easy field calculations: it allows users to size ducts based on airflow and or dimension. To get to these calculations, the user simply follows the appropriate prompt. 5. CYBERSECURITY Computer security requires sound planning and continuous maintenance and monitoring. Mail servers can scan for viruses before users open e-mail, and individual virus software loaded on individual machines serves as a second layer of protection. Always save attached files to a safe directory and scan with antivirus soft- ware before using. Typically, information services (IS) and informa- tion technology (IT) staff have a dedicated support person and strategy to maintain security. Traditional cybersecurity involves protecting computer systems, their contents, and their communications from harm, including theft, undesired access, or undesired modifications. Often, cybersecurity attacks involve malware (malicious software). Cybersecurity related to control systems has greater significance because its failure can neg- atively impact the physical world in ways that range from minor inconvenience, to damaged equipment, or even physical harm to peo- ple. As with other types of security, to be effective it must be multi- layered and constantly evolving to respond to new threats. All users of computer systems need to be aware (to some degree) of cybersecurity. Industry guidelines for cybersecurity exist for computer system administrators and for network administrators. These guidelines are relevant to the network portion of networked HVAC systems. The latest versions of these guidelines can be found online. One source, NIST Standard SP 800-82, Guide to Industrial Control Systems (ICS) Security, contains guidance that is more relevant to HV AC systems and is based on NIST Standard SP 800-53, Security and Privacy Con- trols for Federal Information Systems and Organizations. More information can be obtained from the Department of Homeland Security's Industrial Control Systems- Computer Emergency Response Team (ICS-CERT), whose mission it is to reduce the risk of systemic cybersecurity and communications chal- lenges in cyber defense and incident response. ICS-CERT, aligned under the National Cybersecurity and Communications Integration Center (NCCIC), offers a free tool that provides a systematic approach for evaluating a system 's security posture using the selected security controls listed in NIST Standard SP 800-53. The Cyber Security Evaluation Tool (CSET) is a desktop software tool that guides owners and operators through a step-by-step process to evaluate their system security practices. Physical building security measures are discussed in Chapter 61. ASHRAE Guideline 13 also has guidance on physical and cyberse- curity measures. 5.1 BASIC CYBERSECURITY PRACTICES Keeping devices that support HVAC control systems secure requires some basic security practices and procedures. These proce- dures can be used for company-owned devices but are also applicable for personally owned devices. The best practices for all electronic devices (e.g., PCs, laptops, tablets, phones) are very similar. Listed here are some tips to improve the security posture of these devices. Chart Type: line Dry-Bub Temp Humidity Ratio Relative Humidity Wet-Bub Temp Partial Pressure Enthaloy Specific Volume Dew Point Temp item_01 97.6Not explicitly visible 0.0196Not explicitly visible 50.9Not explicitly visible 81.3Not explicitly visible 0.449Not explicitly visible 45.0Not explicitly visible 14.483Not explicitly visible 76.3Not explicitly visible Fig. 2 Psychrometric Chart Example Inc. ASHRAE, 2019 user. single for Licensed | {}
43832b6d-94ad-4a6e-b318-f05f3e7da0ce | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 41.6 2019 ASHRAE Handbook-HVAC Applications (SI) Users should not connect to untrusted networks or systems. Many control systems have been connected to the Internet to pro- vide convenient, 24/7 operation and maintenance support, remote monitoring capabilities, and data collection for analysis. However, most control systems have not been designed to operate in the cyber- contested environments that have had negative effects on critical infrastructures throughout the world. Until control systems have robust security measures integrated throughout the equipment stack, it is recommended that these systems remain in an isolated network environment that connects only to trusted, secure networks. If circumstances do not allow isolation, then remote connections or any other connections from or into the control system network to other networks should be through a protected communications channel such as a virtual private network (VPN). It is important to use an appropriate account. Everyday web browsing does not require administrative privileges. Using an account with security privileges that are too high creates greater vul- nerability. Only dedicated devices should be used for control systems. To save money, many devices are used for multiple purposes and are connected across multiple networks. However, this introduces inherent risk that can propagate viruses, ransomware, and other malware across multiple systems. Due to the lack of cybersecurity resilience, it is recommended that users avoid this practice to mini- mize potential contamination of the control system environment. Users can take the following steps to increase security: · A strong password is crucial. · Use a screen lock (password, fingerprint, facial recognition) on smartphones. A simple password is better than no password. · The strength of a password is determined by both the length and range of characters used. A short password, with a few lowercase letters, is very weak. A long password, with 9 or more characters, including numbers, uppercase letters, and symbols would be strong. Length is the more important factor: it would be better to have a long password with only a few numbers or symbols, than a short password with many. A short phrase may be easier to remember than a long password, and more difficult for an attacker to break. Generally, the longer the password the better. · Ifitis in the dictionary, do not put it in a password. Except in a long passphrase, dictionary words should be modified by replacing characters with numbers/symbols or by inserting numbers/sym- bols in the word. Avoid any use of common words like "password" or sequences like "123" or "qwerty". If replacing letters with sym- bols, do not use a predictable substitution, such as @ for a. · Do not use any personally identifiable information, such as birth- day, social security number, address, etc., as part of a password. · Do not use the same password for different important web sites, such as e-mail and financial services. · Consider using a password manager. These are applications that can generate secure passwords for you, and use them to help you log in to web sites. Users then only need to remember one pass- word. For detailed guidance, consult the NIST Standard SP 800-63-3, Digital Identity Guidelines. Software updates are important to install. They are usually pro- vided to fix problems with a current version ofthe software that may lead to poor performance or put the device at risk. Ifa device is com- pany owned, there should be guidelines or policy governing updates. If a program is no longer supported and is not being updated, it should be removed from the device. System updates update the software that runs a device. Devices may be configured to tell users when these are available, if connected to the Internet (not recommended practice). Application updates update a specific application or suite of applications. Many applications inform users of available updates, but some may require periodic checks if connected to the Internet (again, not rec- ommended practice). Only software from known sources should be installed. Random apps should not be installed, because they may disguise malware. Programs or apps to be installed should also be approved by IT per- sonnel. It is essential to have antivirus software installed (often for little to no cost). Back-up is also critical; in the event of a ransomware attack (wherein files are encrypted and a price demanded to regain owner access), it is the best method to recover files. Only dedicated devices and software services for control system operations should be used. Avoid software services such as e-mail and personal web browsing. These two services are the primary attack vectors into private sys- tems such as control system networks. Removing these two services will greatly enhance the security of the system. If web browsing or e-mail cannot be disabled, precautions are recommended. Web Browser Security The functionality of web browsers can be increased by installing extensions, which are small add-ons that often act like a utility pro- gram; they may help with bookmarks, tabs, or security. This section discusses some types of extension that improve security. Note that, although most web sites are safe, caution is always advised. Ad Blocker. One common method for malware distribution is malicious links hidden in online advertising. Some methods only require the user to move their mouse cursor over an advertisement. Ad blocker extensions stop or limit the downloading of advertise- ments and are highly recommended. JavaScript Blocker. JavaScript is a computer language used to add functionality to web pages. As with any tool, it is also often mis- used. A JavaScript blocker extension allows users to specify which web sites are allowed to run JavaScript on the browser. This can be selective, with the JavaScript required to display a page allowed and the type of JavaScript that downloads blocked. This type of exten- sion is highly recommended. Other types of extensions include pri- vacy, which are designed to keep personal information controlled, and security, which provide antivirus or VPN capabilities. Safe Browsing. It is important to be wary when following links, especially those found in chatrooms or search results. Malware dis- tributors post links in chatrooms, or design pages to match common searches. Use of encrypted pages allows greater security. Almost every web site allows users to request an encrypted version by changing the "http" in the address to "https. This is important ifthe page contains forms with personal data. Many web sites now use https by default. Browser extensions can also be installed to enforce use of https. E-mail Security Various types of cybersecurity threats are delivered through e- mail, including scams, malicious links, and phishing. Phishing involves an attempt to steal personal information through imperson- ation. Any e-mail requesting personal or business information should be treated with suspicion. Other flags include an unknown sender address, links that appear strange, and grammar or spelling errors. There are other resources available on control systems cyberse- curity that can provide specific, detailed guidance for implementing cybersecurity in HV AC systems. The International Society ofAuto- mation 's ISA/IEC Standard 62443 addresses cybersecurity stan- dards for industrial control systems. 6. SOFTW ARE APPLICATIONS Computer software applications have revolutionized work pro- cesses and practices in the building industry. From drafting tables, to HVAC load calculations, to duct fabrication, software applica- Inc. ASHRAE, 2019 user. single for Licensed | {}
35628456-4136-49a4-9fc9-9f8a6be32aa6 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Computer Applications 41.7 tions have transformed the tasks performed by designers, construc- tion managers, and building operators from manual to automated ways of working. Computerization of work processes promises improved productivity and quality along with decreased cost and time. Computerization also brings learning curves, disruption of time-honored practices, and its own set of issues to be resolved. This section discusses a range of software applications currently in use in the buildings industry, as well as some emerging trends. It is not meant to be an exhaustive listing of applications, nor a com- prehensive discussion of their use. Rather, this is meant as a broad introduction to the variety of software applications currently avail- able, and as a starting point to further reading and exploration. 6.1 EXAMPLE SOFTW ARE APPLICA TIONS Numerous software applications are currently used in the cycle of building/facility design, construction, and operations and main- tenance. These software applications are tools that support practi- tioners in their work processes in each of these stages. The extent to which these tools are adopted is based on industry segment, com- pany/firm, and individual practitioner methods. However, the overall trend is toward increased use and more rapid change both in individual tools and in industry practices. Design Architectural Design (Massing, Space Layout, Rendering). Simplified energy simulation tools can provide easy and quick per- formance analysis at early stages of design, thus assisting designers and architects in making decisions. Simple tools do not require much detailed information as inputs, instead using standard defaults and modeling processes in place of building specifications that might not be available at the early design stage (e.g., schedules, internal loads). Simple tools can be very useful for preliminary energy performance prediction and for informing early design decisions. MEP Design (HVAC Sizing, Selection, Layout; Electrical, Plumbing). There are several mechanical, electrical, and plumbing (MEP) design software solutions that can integrate building infor- mation models (BIM) and calculations in an intelligent computer- aided design (CAD) environment. These can help engineers design, detail, estimate, fabricate, and install MEP building systems more quickly and accurately. Software can either have an integrated BIM capability or provide a capability to import BIM models created by other tools, by reading the file itself or through a Green Building XML (gbXML; www.gbxml. org) import. These tools can read the physical properties of the BIM objects to calculate the HVAC loads space by space. They can also help define air duct and piping networks, taking into consideration flow rates, pressure drops, and other parameters and provide the ability to develop piping/ducting networks in two and three dimensions. Some tools even provide complete documentation, including detailed calculation sheets, technical reports, bill of materials, bids, and more. Energy Simulation. Whole-building energy simulation tools are used for characterizing energy flows and analyzing the impact of building characteristics, thermal loads, and system performance on building energy consumption, thermal comfort of occupants, etc. A building energy simulation tool allows a user to provide inputs for local weather; building geometry; building envelope characteristics; internal heat gains from lighting, people, and plug loads; heating, ventilation, and cooling (HVAC) system specifications; operation schedules; and control strategies. The simulation engine then calcu- lates the building energy performance using complex physics-based models to determine thermal load, resulting energy use, and related metrics such as occupant thermal comfort and carbon emissions. Code Compliance. Numerous jurisdictions (within the United States and elsewhere) require energy code compliance of building designs prior to issuing building permits. Many code compliance software applications have been developed to assist in the process of testing and documenting energy code compliance. Some of these applications focus on so-called prescriptive approaches to compli- ance that provide rules for various aspects of a building design, such as minimum window performance characteristics and window- area-to-floor-area ratios. More sophisticated performance-based approaches rely on energy performance simulation to test and doc- ument code compliance. In all instances, each jurisdiction will pro- vide a list of approved code compliance software applications. Construction Construction Document Production. The use of architectural and MEP design applications during the design phase can greatly aid the production of construction document (CD) packages. This has been true since the development of two-dimensional design tools, but has become even more common and productive since the development and adoption of three-dimensional and BIM-based design applications. These models, if created following best- practice standardized techniques, can easily generate CD packages for hand-off to construction planners and managers. Construction Planning and Execution. BIM and 3D building models created during design that include MEP systems details and physical layout and architectural features (e.g., walls, floors, rooms) can be used for applications beyond that of CD production. Automated clash detection is one such application, in which piping, ducts, and electrical runs that interfere spatially (either with each other or with architectural features) can be detected and brought to the attention of designers and contractors for resolution before actual construction. Even more sophisticated applications, such as four-dimensional construction planning, also are possible with well-developed three- dimensional/BIM building models. Four-dimensional construction planning involves applications that add the dimension of time to a model, supporting construction sequencing for complex projects where trade coordination and materials delivery are critical. Facility Handover. The true benefit of BIM is the capture of accurate building information that can be more easily updated throughout design and construction to create up-to-date as-built building models, which can be handed over to building owners and facility managers and operators for use in the longest phase of the building life cycle: occupancy. These building models, if kept accu- rate, can be used for a variety of applications, including occupancy space planning, space rent assessment, asset (e.g., furniture, move- able equipment, fixed equipment) management, maintenance scheduling, work order tracking, and more. Energy Simulation. Value engineering often occurs during the construction phase. This process, along with change orders and rede- sign, can significantly impact the eventual energy and occupant com- fort performance of the constructed building. Energy simulation applications can be used during these processes to assess the perfor- mance impact of changes from the original design and provide important feedback to ensure desired whole-building performance. Operations and Maintenance Software applications to be used during the operations and main- tenance (O&M) phase of a building life cycle are generally less abun- dant than those for other phases. This may be due to the less computationally intensive nature of O&M work processes, but the computerization of these work processes promises substantial and longer-lasting benefits due to the duration of the O&M phase. Much of the application of software to this phase revolves around informa- tion management tasks such as asset (equipment) management, space and change management, occupant comfort (hot and cold calls), and maintenance work order management. However, newer applications such as fault detection and diagnostics, energy demand Inc. ASHRAE, 2019 user. single for Licensed | {}
6a781f0b-10d9-49b2-8f8b-691183612d2b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 41.8 2019 ASHRAE Handbook-HVAC Applications (SI) management, and continuous commissioning, along with the peri- odic use of energy simulation for HVAC system optimization and building audits and renovation (design and code compliance), pres- ents many further opportunities for computerization. Building Automation Systems. Building automation systems (BASs) provide both manual and automatic centralized control of a building's HVAC, lighting, and other systems, using a network of sensors and activators accessed and programmed through the BAS. The objectives of building automation include improved occupant comfort, efficient operation of building systems, and reduction in energy consumption and operating costs. Computerized Maintenance and Management Systems. Computerized maintenance and management systems (CMMS) (also called facility management, enterprise asset management, or computer-aided facility management) are software tools that main- tain a database of information about a building/facility and provide work order scheduling, asset and space tracking, and other capabil- ities to support O&M activities in buildings. These tools also often provide dashboards (high-level display of information in an orga- nized format) and more sophisticated report generation capabilities. Continuous Commissioning, Fault Detection, and Diagnos- tics. Building automation systems can also support enhanced ana- lytics that use the continuously collected building system data to perform continuous commissioning and detect and diagnose faulty system operation. These analytics can lead to alarm notifications that allow building operators to identify energy- and cost-saving opportunities, occupant comfort issues, and mechanical system fail- ures or inefficient operation. Demand Management and Response. BASs also provide access to the real-time building energy use data and building system control, as well as access to outside information regarding utility grid energy use, required to perform active demand management and demand response control operations. Energy Simulation. Energy simulation tools can also be used for a number of applications during the O&M phase of a building. This includes prediction of savings from building-audit-identified energy efficiency measures, design optimization and code compli- ance during renovation, ongoing HV AC system optimization, fault detection and diagnostics, and demand management and response. 6.2 BIM AND DATA INTEROPERABILITY As evidenced by the (incomplete) list of software applications provided, ASHRAE members and other professionals in the build- ings industry use a wide variety of computer software applications. Historically, these applications have generally been stand-alone desktop tools, using unique custom, and often proprietary, data models to describe the information they require. Moving from one application to another (e.g., between architectural and mechanical design and energy simulation) has required manual recreation of often similar building information in different formats. This process consumes considerable time and effort and invites error in the dif- ferent models of the same building. BIM technologies and procedures have been developed over the past several decades to address this problem. The benefits of auto- mated data exchange between disparate software tools, often referred to as data interoperability, have been recognized for years, but such exchange has still not reached a level of wide adop- tion. However, BIM has recently been gaining traction, especially in the design and construction stages of the building life cycle. ASHRAE resources on BIM and data interoperability include the following: · Multidisciplinary Task Group (MTG) BIM: Building Information Modeling · An Introduction to Building Information Modeling (BIM): A Guidefor ASHRAE Members (ASHRAE 2009; cms.ashrae.biz/bim /pdf/BIMGuide_Rev_110309.pdf) · Guideline 20 · Standards Project Committee (SPC) 205: Standard Representa- tion of Performance Simulation Data for HVAC&R and Other Facility Equipment (spc205.ashraepcs.org) · SPC 224: Standard for the Application of Building Information Modeling 7. BUILDING AUTOMATION AND CONTROL Controls systems perform functions such as monitoring sensors, controlling equipment, scheduling, alarm reporting, energy use monitoring, and trend logging. Systems may use pneumatic or elec- tronic control systems to perform some of these functions, but most modern systems use computers or controllers in direct digital con- trols (DDC). Common types of DDC systems and their functions include the following: · Building automation system (BAS): automating monitoring and control · Energy monitoring and control system (EMCS): conserving energy by both automatic and manual control with the aid of energy monitoring · Energy management system (EMS): conserving energy by spe- cific automatic control programs · Facility management system (FMS): HVAC control of a subset of multiple subsystems or buildings, including fire, security, eleva- tor, or manufacturing systems BAS has become the most popular term for description of a com- puterized control system that may provide one or more of these functions and is the term adopted by ASHRAE Guideline 13. 7.1 APPLICA TION AND PURPOSE BASs can be applied to achieve several different goals and out- comes, often simultaneously. Example applications include · Control for energy efficiency/optimization · Occupancy conditions and comfort, such as outlined in ASHRAE Standard 55 · Equipment and ventilation scheduling · Lighting control · Security · Life safety · Code compliance · Utility-based demand load shedding · Fault detection and diagnostics for preservation of capital and utility expenses · Trending of building and building equipment conditions and operation · Remote access 7.2 NETWORK ARCHITECTURE AND COMPONENTS BAS components are usually arranged and interconnected in a hierarchical structure that can be described in four tiers (Figure 3). Inc. ASHRAE, 2019 user. single for Licensed Tier 1 comprises enterprise and site connectivity devices, which includes web servers, user interfaces, trend databases, time sched- ules, analytics, demand response, load shed protocols, IP Backbone, VLAN, and the Web. This tier is often the point of connection for remote access and for data sharing with external optimization services. This is also the point that represents a cybersecurity risk from outside the network and requires coordination with building | {}
516dc1ce-8725-45cf-8695-b62b69312272 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Computer Applications 41.9 ![image](/image/placeholder) Enterprise Level BuildingLevel EquipmentLevel Sensors and Actuators Tier1 Tier2 Tier3 Sensor Wiring Site IT LAN Application Sensors IT Enterprise LAN BAS Specific (4-20mA or Internet/VPN LAN to WAN EthernetWiring Building PANEL Controller [w] Connectivity AHU 0-10VDC) BAS toLAN Router Corporate Fire/Life Safety Application Sensors Server or Interface Specific (4·20mA or Cloud Systems BASControl Controller Unit Heateri 0 10VDC NetworkWiring Energy Metering Application Sensors System Specific (4-20mA or Interface Controller 0-10VDC Gas Detection Wall Tyee_AHU System Interface Sensors Application (4-20mA or Specific 0 10VDC Water System Controller Fired MUA Direct Interface Free Lighting System Programmable Relays Various Sensors Interface Controller ExhaustFan Actuators End Devices Relays Vanous Sensors Actuators End Devices Pump Free Relays Various Enterprise LAN/WAN/VPN Sensors Programmable Actuators End Devices Site/Building LAN - Ethernet Controller UnitHeater BAS ControlNetwork Wiring Field Device Wiring Fig. 3 Tiers of BAS (ASHRAE Guideline 13) network personnel to maintain security while allowing the neces- sary connectivity. Tier 2 is the building infrastructure and includes components that bridge Tiers 1 and 2. This may include routers that interconnect building systems such as HVAC and lighting for access to Tier 1. This tier is usually IP based and may also contain network control- lers that operate equipment directly, such as a variable speed drive or programmable controllers. This is also the tier where open building control protocols such as BACnetTM or LON WORKSⓇ originate to connect subsystem components. Tier 3 contains application-specific controllers (ASCs) that con- trol equipment or subsystems. ASCs can interconnect to other system components through the building control network but are generally used as the main controller of equipment and may include the point of connectivity to system sensors. The last tier contains sensors and end devices such as relays and actuators. In general, components on this level do not contain any control logic and are either input or output devices. The advent of network sensors and other devices may alter the structure whereby the devices connect from the last tier directly to Tier 2. 7.3 CONTROL COMMUNICATION PROTOCOLS In the past, because all major HVAC equipment required some type of control system, control points were duplicated. Adoption of communication standards has greatly reduced total control costs and increased functionality by providing information (e.g., part- load performance criteria) to users that was previously only avail- able from manufacturer testing. As the functionality of component control increases and associated cost decreases, component-level interaction makes building-wide system integration less critical. HVAC manufacturers use DDC microprocessors to create pow- erful, low-cost controls and feature-rich equipment. In the past, many control devices were proprietary and information was not shared between manufacturers. With standard communication pro- tocols, diverse applications such as HVAC, energy, security, lighting, and fire controls in large buildings can use a single inte- grated control system. Standard protocols allow application-specific component control systems designed for particular HVAC equipment to be included in building-wide strategies. For example, low-cost componentized DDCs provide operation, safety, maintenance, and even self- diagnostic information and control functions. Making a chiller or a variable-speed drive controller a part of a cohesive, building-wide control system is now possible because of standard protocols. Standard communication protocols are developed in committee by professional societies, open protocols are created by manufactur- ers but available for all to use, and proprietary protocols are devel- oped by manufacturers but not freely distributed. User needs should be determined before selecting a particular protocol for a given application. There are two major standard protocols used in HVAC building automation today: BACnetTM and LONW ORKSⓇ BACnet is the ASHRAE Standard 135 Building Automation and Control Networks Protocol. It provides mechanisms by which computerized equipment for a variety ofbuilding control functions may exchange information, regardless of the particular building service it performs. As a result, the BACnet protocol may be used by head-end computers, general-purpose direct digital controllers, and application-specific or unitary controllers. Working groups represented in BACnet include lighting, life safety, elevators, smart grid, security, network security, utility integration, wireless net- working, and XML applications. BACnet is based on a four-layer collapsed architecture that corresponds to the physical, data link, network, and application layers of the ISO/OSI (International Orga- nization for Standardization Open Systems Interconnection) model. The application layer and a simple network layer are defined in the BACnet standard. The physical layer provides a means of connecting devices and transmitting the electronic signals that convey the data. BACnet devices often use Ethernet networking, and can coexist with PCs on the same network. Inc. ASHRAE, 2019 user. single for Licensed | {}
55c8f31d-9b50-40c1-bc64-06b536c9f5d0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 41.10 2019 ASHRAE Handbook-HVAC Applications (SI) The data link layer organizes the data into frames or packets, regulates access to the medium, provides addressing, and handles some error recovery and flow control. Functions provided by the network layer include translation of global addresses to local addresses, routing messages through one or more networks, accommodating differences in network types and in the maximum message size permitted by those networks, sequencing, flow control, error control, and multiplexing. BACnet is designed so that there is only one logical path between devices, thus eliminat- ing the need for optimal path routing algorithms. The presentation layer provides a way for communicating part- ners to negotiate the transfer syntax used to conduct the communi- cation. This transfer syntax is a translation from the abstract user view of data at the application layer to sequences of octets treated as data at the lower layers. The application layer of the protocol provides the communica- tion services required by the applications to perform their functions, in this case monitoring and control of the HVAC&R and other building functions. LON W ORKS defines a protocol for interoperability between con- trol and automation devices. Task groups represented in LONMARK include HVAC, fire, industrial, lighting, vertical transportation (ele- vators), automated food service equipment, home/utility, network tools, refrigeration, router, security, semiconductor, sunblinds, system integration, and transportation. Building automation system networks are local area networks, even though some applications must exchange information with devices in a very distant building. 7.4 BAS SECURITY BAS designs have many vectors for manipulation by unautho- rized personal. These include physical access to equipment and controls and access through the BAS control networks. Security measures must be weighed against the risk associated with unau- thorized manipulation. Physical building security measures are dis- cussed in Chapter 61. ASHRAE Guideline 13 also has guidance on physical and cybersecurity measures. 7.5 ASHRAE RESOURCES FOR BAS SYSTEM DESIGN · Chapter 7 of the 2017 ASHRAE Handbook Fundamentals focuses on automatic control system concepts and common devic- es. · Chapter 48 of this volume focuses on the application of controls systems of specific HVAC systems (air handlers, chillers, boilers, etc.). · Chapter 65 of this volume addresses occupant-centric controls. · ASHRAE Guideline 13 provides guidance for the designer to pre- pare a specification of a BAS for bidding to installation contrac- tors based on the CSI specification format. The guideline includes discussion of system designs, integration of different systems, common sequences of operation, security measures, and a sample specification. · ASHRAE Guideline 36 establishes a set of standardized sequenc- es of operation intended to offer energy efficiency and ease of im- plementation for BAS designers, programmers, and operators. REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. ASHRAE. 2017. Thermal environmental conditions for human occupancy. ANSI/ASHRAE Standard 55-2017. ASHRAE. 2016. Ventilation for acceptable indoor air quality. ANSI/ ASHRAE Standard 62.1-2016. ASHRAE. 2010. Energy standard for buildings except low-rise residential buildings. ANSI/ASHRAE/IES Standard 90.1-2010. ASHRAE. 2008. BACnet�: A data communications protocol for building automation and control networks. ANSI/ASHRAE Standard 135-2008. ASHRAE. 2015. Specifying building automation systems. ASHRAE Guide- line 13-2015. ASHRAE. 2016. Documenting HVAC&R work processes and data ex- change requirements. ASHRAE Guideline 20-2010 (RA 2016). ASHRAE. 2018. High-performance sequences of operation for HVAC sys- tems. ASHRAE Guideline 36-2018. ASHRAE. 2009. An introduction to building information modeling (BIM): A guidefor ASHRAE members. cms. ashrae.biz/bim/pdf/BIMGuide_Rev _110309.pdf. ASHRAE. 2016a. Standard 90.1 user 's manual. ASHRAE. 2016b. Standard 62. I user 's manual. NIST. 2011. Guide to Industrial Control Systems (ICS) Security. SP 800-82 (withdrawn). National Institute of Standards and Technology. Gaithers- burg, MD. NIST. 2013. Security and Privacy Controls for Federal Information Systems and Organizations. SP 800-53 Rev. 4 (R 2015). National Institute of Standards and Technology. Gaithersburg, MD. Ryan, C. 2017. HVAC and big data. Facility Management Magazine, Mel- bourne, Australia. BIBLIOGRAPHY Abtahi, H., T.L. Wong, andJ. Villanueva, III. 1986. Computer aided analysis in thermodynamic cycles. Proceedings of the 1986 ASME International Computers in Engineering Conference 2. ASHRAE. 1997. Thermal comfort tool CD. Badger, L., T. Grance, R. Patt-Corner, and J. Voas. 2012. Cloud computing synopsis and recommendations. NIST Special Publication 800-146. National Institute of Standards and Technology, Gaithersburg, MD. Berners-Lee, T. 1996. Presentation to CDA challenge by CDT et al. www .w3.org/People/Berners-Lee/9602affi.html BuildingSMART. 2002. Home page. www.buildingsmart.com. Diamond, S.C., C.C. Cappiello, and B.D. Hunn. 1985. User-effect validation tests ofthe DOE-2 building energy analysis computer program. ASHRAE Transactions 91(2B):712-724. Fitzgerald, N. 1995. Virus-L/comp. virus FAQ v2.00. www .faqs.org/faqs /computer-virus/faq/. Judkoff, R., D. Wortman, and B. O'Doherty. 1981. A comparative study of four building energy simulations, phase II: DOE-2. 1, BLAST-3.0, SUN- CAT-2.4 and DEROB. Solar Energy Research Institute Report SERI/TP- 721-1326 (July). Kusuda, T., and J. Bean. 1981. Comparison of calculated hourly cooling load and indoor temperature with measured data for a high mass building tested in an environmental chamber. ASHRAE Transactions 87(1):1232- 1240. Lemmon, E.W., M.L. Huber, and M.O. McLinden. 2007. NIST standard reference database 23: Reference fluid thermodynamic and transport properties⌀ REFPROP, V. 8.0. National Institute ofStandards and Tech- nology, Gaithersburg, MD. Li, K. W., W.K. Lee, and J. Stanislo. 1986. Three-dimensional graphical rep- resentation ofthermodynamic properties. Proceedings ofthe 1986 ASME International Computers in Engineering Conference 1. Martocci, J. 2008. BACnet unplugged. ASHRAE Journal 50(6):42-46. McGowan, J.J. 2002. DDC 's future. www.automated buildings.com/news /jan01/articles/mcg/mcg.htm. McQuiston, F.C., and J.D. Spitler. 1992. Cooling and heating load calcula- tion manual. ASHRAE. Mills, R.B. 1989. Why 3D graphics? In Computer Aided Engineering. Pen- ton Publishing, Cleveland, OH. Olgyay, V. 1963. Design with climate: Bioclimatic approach to architectural regionalism. Princeton University Press, Princeton, NJ. Potter, C.D. 1987. CAD in construction. Penton Publishing, Cleveland, OH. Rabl, A. 1988. Parameter estimation in buildings: Methods for dynamic analysis of measured energy use. ASME Journal of Solar Energy, Engi- neering 110. Sinclair, K. 2002. The componentization era is here! www.automated hullings.com/haw/marldaridesconpertandompor.htm. Sorrell, F., T. Luckenback, and T. Phelps. 1985. Validation ofhourly building energy models for residential buildings. ASHRAE Transactions 91(2). Inc. ASHRAE, 2019 user. single for Licensed | {}
8e9bdc85-39f8-451e-9880-b5e51c2eb34a | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Computer Applications 41.11 Spielvogel, L.G. 1975. Computer energy analysis for existing buildings. ASHRAE Journal 7(August):40. Spitler, J.D. 2008. Load calculation applications manual. ASHRAE. Tanenbaum, A.S. 1996. Computer networks. Prentice Hall, New York. Yuill, G. 1985. Verification of the BLAST computer program for two houses. ASHRAE Transactions 91(2B):687-700. FURTHER INTERNET RESOURCES BACnetTM www.bacnet.org BACnet Manufacturers www.bacnetassociation.org Association LONMARK� Interoperability www.lonmark.org Association Building Energy Software Tools www.buildingenergysoftwaretools.com/ Directory Green Building XML www.gbxml.org Inc. ASHRAE, 2019 user single for Licensed Related Commercial Resources | {}
6b9a0321-9bdc-4ca2-af85-5e8f5a533ff3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 42 BUILDING ENERGY AND WATER MONITORING ¦ Reasons for Energy or Water Monitoring ¦ 42.1 ¦ ¦ --- ¦ --- ¦ ¦ Small Projects ¦ 42.3 ¦ ¦ Protocols for Performance Monitoring ¦ 42.4 ¦ ¦ Common Monitoring Issues ¦ 42.6 ¦ ¦ Steps for Project Design and Implementation ¦ 42.7 ¦ B UILDING energy monitoring was conducted on a large scale in the 1980s and 1990s. Project requirements were often not ad- dressed adequately in these projects, and this chapter was developed to address these and capture new insights. The intent of monitoring projects is to provide realistic, empirical information from field data to enhance understanding of actual building energy performance and help quantify changes in performance over time. Although different building energy monitoring projects can have different objectives and scopes, all have several commonalities that allow methodologies and procedures (monitoring protocols) to be standardized. This chapter provides guidelines for developing building monitor- ing projects that provide the necessary measured data at acceptable cost. The intended audience includes building owners, building energy monitoring practitioners, and data end users such as energy and energy service suppliers, energy end users, building system designers, public and private research organizations, utility program managers and evaluators, equipment manufacturers, and officials who regulate residential and commercial building energy systems. The scope of this chapter has been expanded to include water, water monitoring, and associated water efficiency project measurement and verification. A section on small projects is also included, to show how the methodology can be simplified. Monitoring projects can be uninstrumented (i.e., no additional instrumentation beyond the utility meter) or instrumented (i.e., bill- ing data supplemented by additional sources, such as an installed instrumentation package, portable data loggers, or building automa- tion system [BAS]). Uninstrumented approaches are generally simpler and less costly, but they can be subject to more uncertainty in interpretation, especially when changes made to the building represent a small fraction of total energy or water use. It is important to deter- mine the accuracy needed to meet objectives, the type of monitoring needed to provide the desired accuracy, and whether the such accuracy justifies the cost of an instrumented approach. Instrumented field monitoring projects generally involve a data acquisition system (DAS), which is typically comprised of sensors and data-recording devices (e.g., data loggers) or a suitably equipped BAS. Projects may involve a single building or hundreds of build- ings and may be carried out over periods ranging from weeks to years. Most monitoring projects involve the following activities: · Project planning · Site installation and calibration of data acquisition equipment (if required) · Ongoing data collection and verification · Data analysis and reporting These activities often require support by several professional dis- ciplines (e.g., engineering, data analysis, management) and con- struction trades (e.g., electricians, controls technicians, pipe fitters). Useful building energy performance data cover whole buildings, lighting, HVAC equipment, water heating, meter readings, utility The preparation of this chapter is assigned to TC 7.6, Building Energy Per- formance. demand and load factors, excess capacity, controller actuation, and building and component lifetimes. Useful building water performance data cover whole buildings and end use component breakdowns, pota- ble fixtures, HVAC equipment (makeup water), water heating (boiler feed water), meter readings, utility demand and load factors, excess capacity, controller actuation, and building and component lifetimes. Current monitoring practices vary considerably. For example, a utility load research project may characterize the average performance of buildings with relatively few data points per building, whereas a test of new technology performance may involve monitoring hundreds of parameters in a single facility. Monitoring projects range from broad research studies to very specific, contractually required savings veri- fications carried out by performance contractors. Auditing examines energy performance using observations and measured data, which are detailed in ASHRAE (2011). BSR/ASHRAE/ACCA Standard 211- 2018 specifies minimum requirements for such audits. All practitioners should use accepted standards and protocols of monitoring practices to communicate results. Key elements in this monitoring process are (1) classifying the types of project monitor- ing and (2) developing consensus on the purposes, approaches, and problems associated with each type (Haberl et al. 1990; Misuriello 1987). For example, energy or water savings from energy service performance contracts can be specified on either a whole-building or component basis. Monitoring requirements for each approach vary widely and must be carefully matched to the specific project. Proce- dures in ASHRAE Guideline 14-2014 and the IPMVP (2014) can be used to determine monitoring requirements. Performance measure- ment protocols for commercial buildings (new or retrofit construction), including energy, water, and indoor environmental quality, are presented in ASHRAE (2010). Best practices for perfor- mance measurement are given in ASHRAE (2012). 1. REASONS FOR ENERGY OR WATER MONITORING Monitoring projects can be broadly categorized by their goals, ob- jectives, experimental approach, level of monitoring detail, and uses (Table 1). Other factors, such as resources available, data validation and analysis procedures, duration and frequency of data collection, and instrumentation, are common to most, if not all, projects. Energy or Water End Use Assessment 42.1 Energy or water end use assessment projects typically focus on individual energy or water systems in a particular market sector or building type. Monitoring usually requires separate meters or data collection channels for each end use, and analysts must account for all factors that may affect energy or water use. Examples of this approach include detailed utility load research efforts, energy or water audits, evaluation of utility incentive programs, and end use calibration of computer simulations. Depending on the project objectives, the frequency of data collection may range from one- time measurements of full-load operation to continuous time-series measurements. Inc. ASHRAE, 2019 user. single for Licensed | {}
ed39220a-349e-4119-a410-0ee6010fae4e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 42.2 2019 ASHRAE Handbook-HVAC Applications (SI) Table 1 Characteristics of Major Monitoring Project Types ¦ Project Type ¦ Goals and Objectives ¦ General Approach ¦ Level of Detail ¦ Uses ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Energy or water end use assessment ¦ Determine characteristics of specific energy or water end uses in building. ¦ Often uses large, statistically designed sample. Monitor or water demand or energy use profile of each end use of interest. ¦ Detailed data on end uses metered. Collect building and operating data that affect end use. ¦ Load forecasting by end use. Ener- gy or water audit to identify and confirm energy or water conserva- tion or demand-side management opportunities. Simulation calcula- tions. Rate design. ¦ ¦ Specific technology assessment ¦ Measure field performance of building system technology or retrofit measure in individual buildings. ¦ Characterize individual build- ing or technology, occupant behavior, and operation. Account and correct for varia- tions. ¦ Uses detailed audit, sub- metering, indoor temperature, on-site weather, and occupant surveys. May use weekly, hourly, or short-term data. ¦ Technology evaluation. Retrofit performance. Validate models and predictions. ¦ ¦ Energy or water savings measurement and verification ¦ Estimate the impact of retrofit, commissioning, or other building alteration to serve as basis for payments or benefits calculation. ¦ Pre-retrofit consumption is used to create baseline model. Post-retrofit consumption is measured; the difference between the two is savings. ¦ Varies substantially, includ- ing verification of potential to provide savings, retrofit isola- tion, or whole-building or cal- ibrated simulation. ¦ Focused on specific campus, build- ing, component, or system. Amount and frequency of data var- ies widely between projects. ¦ ¦ Building operation and diagnostics ¦ Solve problems. Measure phys- ical or operating parameters that affect energy or water use or that are needed to model build- ing or system performance. ¦ Typically uses one-time and/or short-term measurement with special methods, such as infra- red imaging, flue gas analysis, blower door, or flow measure- ment. ¦ Focused on specific building component or system. Amount and frequency of data vary widely between projects. ¦ Energy or water audit. Identify and solve operation and maintenance, indoor air quality, or system prob- lems. Provide input for models. Building commissioning. ¦ Specific Technology Assessment Specific technology assessment projects monitor field perfor- mance of particular equipment or technologies that affect building energy or water use, such as envelope retrofit measures, major end use system loads or savings from retrofits (e.g., light- ing, plumbing fixtures), or retrofits to, or performance of, mechanical equipment. The typical goal of retrofit performance monitoring projects is to estimate savings resulting from the retrofit despite potentially significant variation in indoor/outdoor conditions, building charac- teristics, and occupant behavior unrelated to the retrofit. The frequency and complexity of data collection depend on project objectives and site-specific conditions. Projects in this category assess variations in performance between different buildings or for the same building before and after the retrofit. Field tests of end use equipment are often characterized by detailed monitoring of all critical performance parameters and operational modes. In evaluating equipment performance or improvements to energy/water efficiency, it is preferable to measure in situ performance. Although manufacturers and laboratory perfor- mance measurements can provide excellent data for sizing and selecting equipment, installed performance can differ significantly from that at design conditions. The project scope may include reli- ability, maintenance, design, energy or water efficiency, sizing, and environmental effects (Phelan et al. 1997a, 1997b). Savings Measurement and Verification (M& V) Accountability is increasingly necessary in energy and water performance retrofits, whether they are performed as part of energy savings performance contracting (ESPC) or directly by the owner. In either case, savings measurement and verification (M& V) is an important part of the project. Because the actual energy or water savings cannot be measured directly, the appropriate role of energy or water monitoring methodology is to · Ensure that appropriate data are available, including pre-retrofit data if retrofits are installed · Accurately define baseline conditions and assumptions · Confirm that proper equipment and systems were installed and have the potential to generate the predicted energy or water sav- ings · Take post-retrofit measurements · Estimate the savings achieved Proper assessment of a retrofit involves comparing before and af- ter energy or water use, and adjusting for all non-retrofit changes that affected that use. Weather and occupancy are examples of factors that often change. To assess the effectiveness ofthe retrofit alone, the influence of these other complicating factors must be removed as best possible. To do so, relationships must be found between and these factors and energy or water use. These relationships are usually determined through data analysis, not textbook equations. Because data analysis can be conducted in an infinite number of ways, there can be no absolute certainty about a given relationship. The need for accuracy must be carefully balanced with measurement and analysis costs, recognizing that absolute certainty is not achievable. Among the numerous sources of uncertainty are instrumentation or measure- ment error, normalization or model error, sampling error, and errors of assumption. Each source can be minimized (to varying degrees) by using more sophisticated measurement equipment, analysis methods, sample sizes, and assumptions. However, more certain sav- ings determinations generally follow the law of diminishing returns, where further increases in certainty come at progressively greater ex- pense. Total certainty is seldom achievable, and even less frequently cost-effective (ASHRAE Guideline 14). Other resources are also available. One of the widest known is the International Performance Measurement and Verification Pro- tocol (IPMVP 2014). The IPMVP is more general than ASHRAE Guideline 14-2014 but provides important background for under- standing the larger context of M& V efforts. Building Operation and Diagnostics Diagnostic projects measure physical and operating parameters that determine the energy or water use of buildings and systems. Usually, the project goal is to determine the cause of problems, model or improve energy or water performance of a building or system(s), or isolate effects of components. Diagnostic tests fre- quently involve one-time measurements or short-term monitoring. To give insight, the frequency of measurement must be several times faster than the rate of change of the effect being monitored. Some diagnostic tests require intermittent, ongoing data collection. Inc. ASHRAE, 2019 user. single for Licensed | {}
1126da99-0099-4d67-9fff-b498d84835ae | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Building Energy and Water Monitoring 42.3 The most basic energy or water diagnostic for buildings is deter- mining rate of use or demand for a specific period, ranging from a single point in time to a few weeks. The scope of measurement may include the whole building or only one component. The purpose can range from measurement system parameter estimation to verifica- tion of nameplate information. Daily or weekly profiles may also be of interest. A large number of diagnostic procedures are used for energy and water measurements in residential (particularly single-family) build- ings. Typical measurements for single-family residences include (1) flue gas and other analysis procedures to determine steady-state furnace combustion efficiency and the efficiency of other end uses, such as air conditioners, refrigerators, and water heaters; (2) fan pres- surization tests to measure and locate building envelope air leakage (ASTM Standard E779) and tests to measure airtightness of air distribution systems (Modera 1989; Robison and Lambert 1989); (3) infrared thermography to locate thermal defects in the building envelope and other methods to determine overall building envelope parameters (Subbarao 1988); and (4) faucet and shower flow meter bags. Energy and water systems in multifamily buildings can be much more complex than those in single-family homes, but the types of diagnostics are similar: combustion equipment diagnostics, air leak- age measurements, flow meter bags, and infrared thermography to identify thermal defects or moisture problems (DeCicco et al. 1995). Some techniques are designed to determine the operating efficiency of steam and hot-water boilers, identify plumbing leaks, and measure air leakage between apartments. Diagnostic techniques have also been created to measure the over- all airtightness of office building envelopes and the thermal performance of walls (Armstrong et al. 2001; Persily et al. 1988; Sell- ers et al. 2004). Practicing engineers also use a host of monitoring techniques to aid in diagnostics and analysis of equipment energy performance. Portable data loggers are often used to collect time- synchronized distributed data, allowing multiple data sets (e.g., chiller performance and ambient conditions) to be collected and quickly analyzed. Similar short-term monitoring procedures are used to provide more detailed and complete commercial building system commissioning. Short-term, in situ tests have also been developed for pumps, fans, and chillers (Phelan et al. 1997a, 1997b). Diagnostics are also well suited to support development and implementation of building energy or water management programs (see Chapter 37). Long-term diagnostic measurements support improvements (Liu et al. 1994). Diagnostic measurement projects can generally be designed using procedures adapted to specific proj- ect requirements (see the section on Steps for Project Design and Implementation). Equipment for diagnostic measurement may be installed tempo- rarily or permanently to aid energy and water management efforts. Designers should consider providing permanent or portable check metering of major electrical loads and plumbing fixtures in new building designs. Building automation systems also can be used to collect the data required for diagnostics. The same concept can be extended to fuel and thermal energy use. 2. SMALL PROJECTS Most metering projects are done on a small scale, and the project steps described in this chapter are simplified and compacted. This section briefly describes how to apply the information in this chap- ter to a small project. Small projects are potentially impacted by the issues described here, but if only a small group of people are involved, they can choose what to address and how to handle the project requirements. Table 2 relates small-project approaches to the material in this chapter. Table 2 Comparison of Small Projects to Overall Methodology Inc. ASHRAE, 2019 user. single for Licensed ¦ Project Characteristic ¦ Small Project Approach ¦ Overall Methodology Coverage ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Project problem areas ¦ · Project goals and resources are iteratively evaluated in short time. Only one to possibly a few people involved. Small group allows more informal procedures and high interaction as needed. · Data products loosely defined. Data collection starts. Initial and ongoing analysis indicates any data management or quality control issues. · Data products refined over time as needed, based on analysis. · Accuracy evaluated on the fly as data are collected. · Commitment is to finish the work. · Advice still sought where needed. ¦ Project goals, project costs and resources, data products, data management, data quality control, commitment, accuracy requirements, advice. ¦ ¦ Building and occupant characteristics ¦ Typically, only one to a few buildings included; work is reason- ably local. Characteristic data collected on site, at convenience of project person(s), depending on project location. Return trips likely needed for simplified data collection approach; supporting data can be collected on return trips. ¦ Fairly extensive data structure (e.g., a characteristic database) and definition of levels of detail may be needed to handle possibly many buildings and improve ability to report results. With many buildings, only one trip per building may be acceptable. ¦ ¦ Project design ¦ Project personnel usually know what they want to measure and report, and may not want to be confused by complex approach in this chapter. Knowledge of experimental approaches may also be understood minimally but still applied successfully, without specific declaration, to small project. ¦ Three higher-level general approaches: (1) fewer buildings or systems with more detailed measurements, (2) many buildings or systems with less detailed measurements, or (3) many buildings or systems with more detailed measurements. Six major experimental design approaches: on/off, before/after, test/reference, simulated occupancy, nonexperimental reference, engineering field test. ¦ ¦ Reporting ¦ Reporting is informal to somewhat formal (more like straightforward engineering project than research project). Reported results are often minimal but provide key information. ¦ Research project report is likely required, possibly hundreds of pages long, with multiple appendices. Extensive databases likely generated and must be quality checked and corrected for use by others. Data user access procedures may have to be developed. Databases must be maintained over years in many cases and must be well documented. Extensive research results may have been generated and should be reported. For exam- ple, Fracastoro and Lyberg (1983) discussion of guiding prin- ciples for residential projects is 300 pages long. ¦ | {}
2f722d67-8d15-4ab8-855d-d300d4685c8c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 42.4 2019 ASHRAE Handbook-HVAC Applications (SI) How to Use This Chapter for Small Projects 1. Skim through the chapter and make a few notes on items that may apply for the project in question. 2. Generate a brief project plan to ensure major issues that could cause problems are not overlooked. 3. Generate a brief checklist from the item notes for final check-off during or at the end of project. 4. Clarify what building or site characteristics data may be needed, and be sure to collect those data. 5. Analyze data from the start, to make sure there are no quality or data issues. 6. Consider whether any data should be made available to others at the end of the project, and if so, develop a data format for ex- change. 7. Skim through the chapter again when the report is being pre- pared to gather ideas about what to include in the report. 3. PROTOCOLS FOR PERFORMANCE MONITORING ASHRAE (2010) gives protocols for performance monitoring of commercial buildings (energy, water, thermal comfort, indoor air quality, lighting, and acoustics) at three levels (basic, intermediate, and advanced). These protocols apply to both retrofit and new building projects and identify what to measure, how to measure (in- strumentation and spatial resolution), and how often to measure. Implementation of these protocols for the same six elements, at three levels (basic evaluation, diagnostic measurement, and advanced analysis) is discussed in ASHRAE (2012). Examples of procedures (protocols) for evaluating energy or water savings for projects in- volving retrofit of existing building systems are presented here. These protocols should also be useful to those interested in more general building energy or water monitoring. Building monitoring has been significantly simplified and made more professional in recent years by the development of these fairly standardized monitoring protocols. Although there may be no way to define a protocol to encompass all types of monitoring applications, repeatable and understandable methods of measuring and verifying retrofit savings are needed. However, following a pro- tocol does not replace adequate project planning and careful assessment of project objectives and constraints. Residential Retrofit Monitoring Protocols for monitoring residential building retrofit performance can answer specific questions associated with actual measured per- formance. For example, Ternes (1986) developed a single-family retrofit monitoring protocol, a data specification guideline that identifies important parameters to be measured. Both one-time and time-sequential data parameters are covered, and parameters are defined carefully to ensure consistency and comparability between experiments. Discrepancies between predicted and actual perfor- mance, as measured by the energy or water bills, are common. This protocol improves on billing data methods in two ways: (1) internal temperature is monitored, which eliminates a major unknown variable in data interpretation; and (2) data are taken more frequently than monthly, which potentially shortens monitoring duration. Utility bill analysis generally requires a full season of pre- and post-retrofit data. The single-family retrofit protocol may require only a single season. Ternes (1986) identified both a minimum set of data, which must be collected in all field studies that use the protocol, and optional extensions that can be used to study additional issues. See Table 3 for details. Szydlowski and Diamond (1989) developed a similar method for multifamily buildings. The single-family retrofit monitoring protocol recommends a before/after experimental design, and the minimum data set allows Table 3 Data Parameters for Residential Retrofit Monitoring ¦ ¦ Recording Period ¦ Recording Period ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ Minimum ¦ Optional ¦ ¦ Basic Parameters ¦ ¦ ¦ ¦ House description ¦ Once ¦ Once ¦ ¦ Space-conditioning system description ¦ Once ¦ Once ¦ ¦ Entrance interview information ¦ Once ¦ Once ¦ ¦ Exit interview information ¦ Once ¦ Once ¦ ¦ Pre- and post-retrofit infiltration rates ¦ Once ¦ Once ¦ ¦ Metered space-conditioning system performance ¦ Once ¦ Once ¦ ¦ Retrofit installation quality verification ¦ Once ¦ Once ¦ ¦ Heating and cooling equipment energy consumption ¦ Weekly ¦ Hourly ¦ ¦ Weather station climatic information ¦ Weekly ¦ Hourly ¦ ¦ Indoor temperature ¦ Weekly ¦ Hourly ¦ ¦ House gas or oil consumption ¦ Weekly ¦ Hourly ¦ ¦ House electricity consumption ¦ Weekly ¦ Hourly ¦ ¦ Wood heating use ¦ ¦ Hourly ¦ ¦ Domestic hot water energy consumption ¦ Weekly ¦ Hourly ¦ ¦ Optional Parameters ¦ ¦ ¦ ¦ Occupant behavior ¦ ¦ ¦ ¦ Additional indoor temperatures ¦ Weekly ¦ Hourly ¦ ¦ Heating thermostat set point ¦ ¦ Hourly ¦ ¦ Cooling thermostat set point ¦ ¦ Hourly ¦ ¦ Indoor humidity ¦ Weekly ¦ ¦ ¦ Microclimate ¦ ¦ ¦ ¦ Outdoor temperature ¦ Weekly ¦ Hourly ¦ ¦ Solar radiation ¦ Weekly ¦ Hourly ¦ ¦ Outdoor humidity ¦ Weekly ¦ Hourly ¦ ¦ Wind speed ¦ Weekly ¦ Hourly ¦ ¦ Wind direction ¦ Weekly ¦ Hourly ¦ ¦ Shading ¦ Once ¦ Once ¦ ¦ Shielding ¦ Once ¦ Once ¦ ¦ Distribution system ¦ ¦ ¦ ¦ Evaluation of ductwork infiltration ¦ Once ¦ Once ¦ Source: Ternes (1986). performance to be measured on a normalized basis with weekly time-series data (some researchers recommend daily). The protocol also allows hourly recording intervals for time-integrated parame- ters, an extension ofthe basic data requirements in the minimum data set. The minimum data set may also be extended through optional data parameter sets for users seeking more information. Data parameters in this protocol have been grouped into four data sets: basic parameters, occupant behavior, microclimate, and distribution system (Table 3). The minimum data set consists of a weekly option of the basic data parameter set. Time-sequential measurements are monitored continuously during the field study. These are all time-integrated parameters (i.e., appropriate average values of a parameter over the recording period, rather than instan- taneous values). This protocol also addresses instrumentation installation, accuracy, measurement frequency, and expected ranges for all time- sequential parameters (Table 4). The minimum data set (weekly option of the basic data) must always be collected. At the user's dis- cretion, hourly data may be collected, which allows two optional parameters to be monitored. Parameters from the optional data sets may be chosen, or other data not described in the protocol added, to arrive at the final data set. This protocol standardizes experimental design and data collec- tion specifications, enabling independent researchers to compare project results more readily. Moreover, including both minimum and optional data sets and two recording intervals accommodates projects of varying financial resources. Commercial Retrofit Monitoring Several related guidelines have been created for evaluating retrofit savings (measurement and verification [M& V]). Inc. ASHRAE, 2019 user. single for Licensed | {}
d20bf5c3-0b79-483b-b92c-30c799e77e1b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Building Energy and Water Monitoring 42.5 Table 4 Time-Sequential Parameters for Residential Retrofit Monitoring ¦ ¦ ¦ ¦ ¦ Scan Rateb ¦ Scan Rateb ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Data Parameter ¦ Accuracya ¦ Range ¦ Stored Value per Recording Period ¦ Option 1 ¦ Option 2 ¦ ¦ Basic Parameters ¦ ¦ ¦ ¦ ¦ ¦ ¦ Heating/cooling equipment energy consumption ¦ 3% ¦ ¦ Total consumption ¦ 15 s ¦ 15 s ¦ ¦ Indoor temperature ¦ 0.5 K ¦ 10 to 35°C ¦ Average temperature ¦ 1 h ¦ 1 min ¦ ¦ House gas or oil consumption ¦ 3% ¦ ¦ Total consumption ¦ 15 s ¦ 15 s ¦ ¦ House electricity consumption ¦ 3% ¦ ¦ Total consumption ¦ 15 s ¦ 15 s ¦ ¦ Wood heating use ¦ 0.5 K ¦ 10 to 450°C ¦ Average surface temperature or total use time ¦ ¦ 1 min ¦ ¦ Domestic hot water ¦ 3% ¦ ¦ Total consumption ¦ 15 s ¦ 15 s ¦ ¦ Optional Data Parameter Sets ¦ ¦ ¦ ¦ ¦ ¦ ¦ Occupant behavior ¦ ¦ ¦ ¦ ¦ ¦ ¦ Additional indoor temperatures ¦ 0.5 K ¦ 10 to 35°C ¦ Average temperature ¦ 1 h ¦ 1 min ¦ ¦ Heating thermostat set point ¦ 0.5 K ¦ 10 to 35°C ¦ Average set point ¦ ¦ 1 min ¦ ¦ Cooling thermostat set point ¦ 0.5 K ¦ 10 to 35°C ¦ Average set point ¦ ¦ 1 min ¦ ¦ Indoor humidity ¦ 5% rh ¦ 10 to 95% rh ¦ Average humidity ¦ 1 h ¦ ¦ ¦ Microclimate ¦ ¦ ¦ ¦ ¦ ¦ ¦ Outdoor temperature ¦ 0.5 K ¦ -40 to 50°C ¦ Average temperature ¦ 1 h ¦ 1 min ¦ ¦ Solar radiation ¦ 30 W/m2 ¦ 0 to 1100 W/m2 ¦ Total horizontal radiation ¦ 1 min ¦ 1 min ¦ ¦ Outdoor humidity ¦ 5% rh ¦ 10 to 95% rh ¦ Average humidity ¦ 1 h ¦ 1 min ¦ ¦ Wind speed ¦ 0.2 m/s ¦ 0 to 10 m/s ¦ Average speed ¦ 1 min ¦ 1 min ¦ ¦ Wind direction ¦ 5° ¦ 0 to 360° ¦ Average direction ¦ 1 min ¦ 1 min ¦ Source: Ternes (1986). aAll accuracies are stated values. ASHRAE Guideline 14-2014 provides methods for effectively and reliably measuring the energy, water and demand savings due to building improvement projects. The guideline defines a minimum ac- ceptable level of performance in measuring energy, water, and demand savings from conservation measures in residential, commer- cial, or industrial buildings. These measurements can serve as the ba- sis for commercial transactions between energy services providers and customers who rely on measured energy or water savings as the basis for financing payments. Three approaches are discussed: whole building, retrofit isolation, and calibrated simulation. The guideline includes an extensive resource on physical measurement, uncertainty, and regression techniques. Example M& V plans are also provid- ed. The International Performance Measurement and Verification Protocol (IPMVP 2014) provides guidance to buyers, sellers, and financiers of energy projects on quantifying energy savings perfor- mance of energy retrofits. The Federal Energy Management Pro- gram has produced guidelines specific to federal projects, which include many procedures applicable to calculating retrofit savings in nonfederal buildings (FEMP 2015). On a more detailed level, ASHRAE research project RP-827 resulted in separate guidelines for in situ testing of chillers, fans, and pumps to evaluate installed energy efficiency (Phelan et al. 1996, 1997a, 1997b). The guidelines specify the physical characteristics to be measured; number, range, and accuracy of data points required; methods of artificial loading; and calculation equations with a rigorous uncertainty analysis. In addition to these specialized protocols for particular monitoring applications, a number of specific laboratory and field measurement standards exist, and many monitoring source books are in circulation. Finally, MacDonald et al. (1989) developed a protocol for field monitoring studies of energy improvements (retrofits) for commer- cial buildings. Similar to the residential protocol, it addresses data requirements for monitoring studies. Commercial buildings are more complex, with a diverse array of potential efficiency improvements. Consequently, the approach to specifying measurement procedures, describing buildings, and determining the range of analysis must dif- fer. The strategy used for this protocol is to specify data requirements, analysis, performance data with optional extensions, and a building core data set that describes the field performance of efficiency improvements. This protocol requires a description of the approach bApplicable scan rates if nonintegrating instrumentation is used. used for analyzing building energy or water performance. The neces- sary performance data, including identification of a minimum data set, are outlined in Table 5. Commercial New Construction Monitoring New building construction offers the potential for monitoring building subsystem energy consumption at a reasonable cost. Infor- mation obtained by monitoring operating hours or direct energy consumption can benefit building owners and managers by · Verifying design intent · Highlighting inefficient or improper operation of equipment · Providing data that can be useful in determining benefits of alter- native operating strategies or replacement equipment · Evaluating costs of operation for extending occupancy hours for special conditions or event · Demonstrating effects of poor maintenance or identifying when maintenance procedures are not followed · Diagnosing and fixing comfort and other space condition prob- lems · Diagnosing power quality problems · Submetering tenants · Verifying/improving savings of a performance contract · Maintaining persistence of energy or water savings To provide data necessary to improve building systems opera- tion, monitoring should be considered for boilers, chillers, cooling towers, heat pumps, air-handling unit fans, large fan-coil units, major exhaust fans, major pumps, comfort cooling compressors, lighting panels, electric heaters, receptacle panels, substations, motor control centers, major feeders, service water heaters, plumb- ing systems, process loads, and computer rooms. Guidance on energy monitoring to determine energy savings for new construction design modifications is available in IPMVP (2014). Construction documents may include provisions for various meters to monitor equipment and system operation. Some equipment can be specified to have factory-installed hour meters that record actual operating hours of the equipment. Hour meters can also be easily field-installed on any electrical motor. More sophisticated power-monitoring systems, with electrical switchgear, substations, switchboards, and motor control centers, can be specified. These systems can monitor energy demand, energy consumption, power factor, neutral current, etc., and can be linked to Inc. ASHRAE, 2019 user. single for Licensed | {}
41706cf3-2101-491d-aef3-9b993ca06a14 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 42.6 2019 ASHRAE Handbook-HVAC Applications (SI) Table 5 Performance Data Requirements of Commercial Retrofit Protocol ¦ Projects with Submetering ¦ Projects with Submetering ¦ Projects with Submetering ¦ Projects with Submetering ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ Before Retrofit ¦ After Retrofit ¦ ¦ ¦ Utility billing data (for each fuel) Submetered data (for all recording intervals) ¦ 12 month minimum All data for each major end use, up to 12 months Type ¦ 3 month minimum (12 months if weather normalization required) All data for each major end use, up to 12 months Recording Interval ¦ Period Length ¦ ¦ Temperature data (daily maximum and minimum must be provided for any periods without integrated averages) ¦ Maximum and minimum or- Integrated averages ¦ Daily or- Same as for submetered data but not longer than daily ¦ Same as billing data length or- Length of submetering ¦ ¦ Projects Without Submetering ¦ Projects Without Submetering ¦ Projects Without Submetering ¦ Projects Without Submetering ¦ ¦ ¦ Before Retrofit ¦ After Retrofit ¦ ¦ ¦ Utility billing data (for each fuel) ¦ 12 month minimum Type ¦ 12 month minimum Recording Interval ¦ Period Length ¦ ¦ T emperature data ¦ Maximum and minimum or Integrated averages ¦ Daily ¦ Same as billing data length ¦ a computer. These same systems can be installed on circuits to exist- ing or retrofit fans, chillers, lighting panels, etc. Some equipment commonly used for improving system efficiency, such as variable- frequency drives, can be provided with capability to monitor kilowatt output, kilowatt-hours consumed, and other variables. Using direct digital control (DDC) or BAS for monitoring is par- ticularly appropriate in new construction. These systems can monitor, calculate, and record system status, water use, energy use at the main meter or of particular end-use systems, demand, and hours of operation; as well as start and stop building systems, con- trol lighting, and report alarms when systems do not operate within specified limits. Initial specification of the new control system should include specific requirements for sensors, calculations, and trend logging and reporting functions. Special issues related to sen- sors and monitoring approaches can be found in Piette et al. (2000). 4. COMMON MONITORING ISSUES Field monitoring projects require effective management of var- ious professional skills. Project staff must understand the building systems being examined, quality control of data, data management, data acquisition, and sensor technology. In addition to data collec- tion, processing, and analysis, the logistics of field monitoring projects require coordinating equipment procurement, delivery, and installation. Key issues include the accuracy and reliability of collected data. Projects have been compromised by inaccurate or missing data, which could have been avoided by periodic sensor calibration and ongoing data verification. Planning Many common problems in monitoring projects can be avoided by effective and comprehensive planning. Project Goals. Project goals and data requirements should be established before hardware is selected. Unfortunately, projects are often driven by hardware selection rather than by project objectives, either because monitoring hardware must be ordered several months before data collection begins or because project initiation procedures are lacking. As a result, the hardware may be inappropriate for the particular monitoring task, or critical data points may be overlooked. Project Costs and Resources. After goal setting, the feasibility of the anticipated project should be reviewed in light of available resources. Projects to which significant resources can be devoted usually involve approaches different from those with more limited resources. This issue should be addressed early on and reviewed throughout the course of the project. Although it is difficult at an early stage to assess with certainty the cost of an anticipated project, rough estimates can be quite helpful. Data Products. It is important to establish the type and format of the final results calculated from data before selecting data points. Failure to plan these data products may lead to failure to answer crit- ical questions. Data Management. Failure to anticipate the typically large amounts of data collected can lead to major difficulties. The computer and personnel resources needed to verify, retrieve, ana- lyze, and archive data can be estimated based on experience with previous projects. Data Quality Control. Itis also important to validate the quality and plausibility of data before use. Failure to use some type of qual- ity control often results in data errors and invalid results. Commitment. Many projects require long-term commitment of personnel and resources. Project success depends on long-term, daily attention to detail and staff continuity. Accuracy Requirements. The required accuracy of data prod- ucts and accuracy of the final data and experimental design needed to meet these requirements should be determined early on. After the required accuracy is specified, the sample size (number of build- ings, control buildings, or pieces of equipment) must be chosen, and the required measurement precision (including error propagation into final data products) must be determined. Because trade-offs must usually be made between cost and accuracy, this process is often iterative. It is further complicated by a large number of inde- pendent variables (e.g., occupants, operating modes) and the stochastic nature of many variables (e.g., weather). Advice. Expert advice should be sought from others who have experience with the type of monitoring envisioned. Implementation and Data Management The following steps can facilitate smooth project implementa- tion and data management: · Calibrate sensors before installation. Spot-check calibration on site. During long-term monitoring projects, recalibrate sensors periodically. Appropriate procedures and standards should be used in all calibration procedures (see ASHRAE Guideline 14-2014 and IPMVP [2014]). · Track sensor performance regularly. Quick detection of sensor failure or calibration problems is essential. Ideally, this should be an automated or a daily task. The value of data is high, because they may be difficult or impossible to reconstruct. Inc. ASHRAE, 2019 user. single for Licensed | {}
e7e48235-0c69-49db-a100-695e0ed0f828 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Building Energy and Water Monitoring 42.7 · Generate and review data on a timely, periodic basis. Problems that often occur in developing final data products include missing data from failed sensors, data points not installed because of plan- ning oversights, and anomalous data for which there are no ex- planatory records. If data products are specified as part of general project planning and produced periodically, production problems can be identified and resolved as they occur. Automating the pro- cess of checking data reliability and accuracy can be invaluable in keeping the project on track and in preventing sensor failure and data loss. · Occupancy surveys are generally used as subjective measures to assess indoor environmental quality (thermal comfort, IAQ, light- ing, acoustics). Surveys such as those of the Center for the Built Environment at the University of California at Berkeley (CBE 2008), can be administered in paper or electronic form, and pro- vide comparison of sampled results with those of peer buildings. These measurements can be taken over time to determine any changes in occupant satisfaction. Data Analysis and Reporting For most projects, the collected data must be analyzed and reported. Because the objective of the project is to translate these data into information, and ultimately into knowledge and action, the importance of this step cannot be overemphasized. Clear, conve- nient, and informative formats should be devised in the planning stages and adhered to throughout the project. Data analysis should be carefully defined before the project begins. Close attention must be paid to resource allocation to ensure that adequate resources are dedicated to verification, management, and analysis of data and to ongoing maintenance of monitoring equipment. As a quality control procedure and to make data analysis more manageable, these activities should be ongoing. 5. STEPS FOR PROJECT DESIGN AND IMPLEMENTATION This section describes methodology for designing effective field monitoring projects that meet desired goals with available project resources. The task components and relationships among the nine activities constituting this methodology are identified in Figure 1. The activities fall into four categories: project management, proj- ect development, resolution and feedback, and production quality and data transfer. Field monitoring projects vary in terms of resources, goals and objectives, data product requirements, and other variables, affecting how methodology should be applied. Nonetheless, the methodology provides a proper framework for advance planning, which helps minimize or prevent implementa- tion problems. An iterative approach to planning activities is best. The scope, accuracy, and techniques can be adjusted based on cost estimates and resource assessments. The initial design should be performed simply and quickly to estimate cost and evaluate resources. If costs are out of line with resources, such as when desired levels of instru- mentation exceed the resources available, adjustments are needed. Planning should identify and resolve any trade-offs necessary to execute the project in a given budget. Examples include reducing the scope of the project versus relaxing instrumentation specifica- tions or accuracy requirements. These decisions often depend on what questions the project must answer and which questions can be eliminated, simplified, or narrowed. One frequent oversight in project planning is failing to reserve sufficient time and resources for later analysis and reporting of data. Unanticipated additional costs associated with data collection and problem resolution should not jeopardize these resources. Documenting the results of project planning should cover all nine parts of the process. This report can be a useful part of an over- ![image](/image/placeholder) Part One PROJECT MANAGEMENT Evaluate Resources and Identify Project Goals Set Objectives, Priorities, and Constraints Part Two Part Three Part Four Part Five Part Six PROJECT Specify Specify Specify Specify Data Specifty DEVELOPMENT Building Data Monitoring Analysis Field Data Characteristics Products Design Procedures Monitoring Approach and Points Algorithms Part Seven RESOLUTION AND FEEDBACK Resolve Project Accuracy Requirements Part Eight Part Nine PRODUCTION QUALITY Specify Verification Specify Data Recording AND DATA TRANSFER and QA Procedures and Exchange Formats Fig. 1 Methodology for Designing Field Monitoring Projects all project plan that may document other important project informa- tion, such as resources to be used, schedule, etc. Part One: Identify Project Objectives, Resources, and Constraints Start with a clear understanding ofthe decision or action that the project will inform. The goals and objectives statement determines the overall direction and scope of the data collection and analysis effort. The statement should also list questions to be answered by empirical data, noting the error or uncertainty associated with the desired result. Realistic assessment of error is needed because requiring too small an uncertainty leads to an overly complex and expensive project. It is important in monitoring projects that a data acquisition plan be developed and followed with a clear idea of the research questions to be answered. Resource requirements for equipment, personnel, and other items must feed into budget estimates to determine expected funding need- ed for different project objectives. Scheduling requirements must also be considered, and project constraints defined and considered. Trade-offs on budget and objectives require that priorities be estab- lished. Even if a project is not research-oriented, it is attempting to obtain information, which can be expressed in the form of questions. Re- search questions can have varying scopes and levels of detail, addressing entire systems or specific components. Examples of re- search questions include · Measurement and verification: Have contractors fulfilled their responsibilities of installing equipment and improving systems to achieve the agreed-upon energy or water savings? · Classes of buildings: How much energy or water has been saved by using the building construction/performance standard man- dated in the jurisdiction? · Particular buildings: Has a lapse in building maintenance caused energy or water performance to degrade? · Particular components: What is the average reduction in demand charges during summer peak periods because of the installation of an ice storage system in this building? Research questions vary widely in technical complexity, gener- ally taking one of the following three forms: · How does the building/component perform? · Why does the building/component perform as it does? Inc. ASHRAE, 2019 user. single for Licensed | {}
2c93c319-2d84-42c8-9933-48bee4defd33 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 42.8 · Which building/component should be targeted to achieve optimal cost effectiveness? The first form of question can sometimes be answered generi- cally for a class of typical buildings without detailed monitoring and analysis, although planning and thorough analysis are still required. The second and third forms usually require detailed monitoring and analysis and, thus, detailed planning. In general, more detailed and precise goal statements are better. They ensure that the project is constrained in scope and developed to meet specific accuracy and reliability requirements. Usually, projects attempt to answer more than one research question, and often consider both primary and secondary questions. All data col- lected should have a purpose of helping to answer a project question; the more specific the questions, the easier it becomes to identify required data. Part Two: Specify Building and Occupant Characteristics Measured energy or water data will not be meaningful to people who were not involved in the project unless the characteristics ofthe building being monitored, and its use, have been documented. To meet this need, a data structure (e.g., a characteristic database) can be developed to describe the buildings. Building characteristics can be collected at many levels of detail, depending on the type of monitoring project and the parameters that affect results. For projects that determine whole-building perfor- mance, it is important to provide at least enough detail to document the following: · General building type, use, configuration, and envelope (particu- larly energy-related aspects) · Building occupant information (number, occupancy schedule, activities) · Internal loads · HVAC system descriptive information characterizing key param- eters affecting HVAC system performance · Type and quantity of other energy-using systems, especially light- ing · Type and quantity of potable water fixtures · Any building changes that occur during the monitoring project · Entrance interview information focusing on energy or water- related behavior of building occupants before monitoring · Exit interview information documenting physical or lifestyle changes at the test site that may affect data analysis Inc. ASHRAE, 2019 user. single for Licensed The minimum level of detail is known as summary character- istics data. Simulation-level characteristics (detailed information collected for hourly simulation model input) may be desirable for some buildings. Regardless of the level of detail, the data should provide a context for analysts, who may not be familiar with the project, to understand the building and its energy use. Part Three: Specify Data Products and Project Output The objective of a monitoring project is not to merely produce data, but to answer a question. However, the data must be of high quality and must be presented to key decision makers and analysts in a convenient, informative format. The specific data products (scope, format, and content of data needed to meet project goals and objectives) must be identified and evaluated for feasibility and usefulness in answering project questions identified in Part One. Final data products must be clearly specified, together with the min- imum acceptable data requirements for the project. Itis important to clearly define an analysis path showing what will be calculated and what data are necessary to achieve desired results; assurance should be given that the resources needed to analyze the data, once col- lected, are available. Clear communication is critical to ensure that 2019 ASHRAE Handbook-HVAC Applications (SI) project requirements are satisfied and factors contributing to moni- toring costs are understood. Evaluation results can be presented in many forms, often as in- terim and final reports (possibly by heating and/or cooling season), technical notes, or technical papers. These documents must convey specific results of the field monitoring clearly and concisely. They should also contain estimates of the accuracy of the results. The composition of data presentations and analysis summaries should be determined early to ensure that all critical parameters are identified (Hough et al. 1987). For instance, mock-ups of data tables, charts, and graphs can be used to identify requirements. Pre- viously reported results can be used to provide examples of useful output. Data products should also be prioritized to accommodate possible cost trade-offs or revisions resulting from other steps in the process such as error analysis (see Part Seven). Although requirements for the minimum acceptable data results can often be specified during planning, data analysis typically reveals further requirements. Thus, budget plans should include allowances and optional data product specifications to handle addi- tional or unique project output requirements uncovered during data analysis. Longer-term goals and future information needs should be antic- ipated and explained to project personnel. For example, a project may have short- and long-term data needs (e.g., demonstrating reductions in peak electrical demand versus demonstrating cost effectiveness or reliability to a target audience). Initial results on demand reduction may not be the ultimate goal, but rather a step toward later presentations on cost reductions achieved. Thus, it is prudent to consider long-term and potential future data needs so that additional supporting information, such as photographs or testimo- nials, may be identified and obtained. Part Four: Specify Design of Monitoring A general monitoring design must be developed that defines three interacting factors: the number of buildings in the study, the moni- toring approach (or experimental design), and the level of detail in the data being measured. A less detailed or precise approach can be considered if the number of buildings is increased, and vice versa. If the goal is related to a specific product, the monitoring design must isolate the effects of that product. Haberl et al. (1990) discuss mon- itoring designs. For example, for retrofit M& V, protocols have been written allowing a range of monitoring methods, from retrofit verifi- cation to retrofit isolation (ASHRAE Guideline 14-2014; FEMP 2015; IPMVP 2014). Some monitoring approaches are better suited than others to larger numbers of buildings. Specifying the approach is particularly important because total building performance is a complex function of several variables, changes in which are difficult to monitor and to translate into per- formance. Unless care is taken with measurement organization and accuracy, uncertainties, errors (noise), and other variations (e.g., weather) can make it difficult to detect performance changes of less than 20% (Fracastoro and Lyberg 1983). In some cases, judgment may be required in selecting the number of buildings involved in the project. If an owner seeks in- formation about a particular building, the number of buildings in the experiment is fixed at one. However, for other monitoring ap- plications, such as drawing conclusions about effects in a sample population of buildings, some selection is involved. Generally, er- ror in the derived conclusions decreases as the square root of the number of buildings increases (Box 1978). A specific project may be directed at · Fewer buildings or systems with more detailed measurements · Many buildings or systems with less detailed measurements · Many buildings or systems with more detailed measurements | {}
2c3473d2-4946-42ab-a5b1-fbdbd27bd244 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Building Energy and Water Monitoring 42.9 For projects of the first type, accuracy requirements are usually resolved initially by determining expected variations of measured quantities (dependent variables) about their average values in re- sponse to expected variations of independent variables. For buildings, a typical concern is the response of heating and cooling loads to changes in temperature or other weather variables. The re- sponse of lighting energy use to daylighting is another example of the relationship between dependent and independent variables. Fluctuations in response are caused by (1) outside influences not quantified by measured energy use data and (2) limitations and un- certainties associated with measurement equipment and procedures. Thus, accuracy must often be determined using statistical methods to describe mean tendencies of dependent variables. For projects of the second and third types, the increased number of buildings improves confidence in the mean tendencies of the dependent response(s) of interest. Larger sample sizes are also needed for experimental designs with control groups, which adjust for some outside influences. For more information, see Box (1978), Fracastoro and Lyberg (1983), and Hirst and Reed (1991). Projects can also use more complex, multilevel measurement and modeling approaches to handle an array of technologies or to improve confi- dence in results (Hughes and Shonder 1998). Most monitoring procedures use one or more of the following general experimental approaches: Before/After. Building, system, or component energy consump- tion is monitored before and after a new component or retrofit improvement is installed. Changes in factors not related to the ret- rofit, such as the weather and building operation, must be accounted for, often requiring a model-based analysis (Fels 1986; Hirst et al. 1983; Kissock et al. 1992; Robison and Lambert 1989; Sharp and MacDonald 1990). This experimental design is the primary concern of most current building energy monitoring documents (ASHRAE Guideline 14-2014; FEMP 2015; IPMVP 2014). Test/Reference. The building energy consumption data of two "identical" buildings, one with the product or retrofit being inves- tigated, are compared. Because buildings cannot be absolutely identical (e.g., different air leakage distributions, insulation effec- tiveness, temperature settings, and solar exposure), measurements should be taken before installation as well, to allow calibration. Once the product or retrofit is installed, any deviation from the calibration relationship can be attributed to the product or retrofit (Fracastoro and Lyberg 1983; Levins and Karnitz 1986). On/Off. If the retrofit or product can be activated or deactivated at will, energy consumption can be measured in a number of repeated on/off cycles. On-period consumption is then compared to off-period consumption (Cohen et al. 1987; W oller 1989). Simulated Occupancy. In some cases, the desire to reduce noise can lead the experimenter to postulate certain standard profiles for temperature set points, internal gains, moisture release, or window manipulation and to introduce this profile into the building by com- puter-controlled devices. The reference is often given by the test/ reference design. In this case, both occupant and weather variations are held constant in the comparison (Levins and Karnitz 1986). Nonexperimental Reference. A reference for assessing the performance of a building can be derived nonexperimentally using (1) a normalized, stratified performance database, such as energy use per unit area classified by building type (MacDonald and Was- serman 1989) or (2) a representative standard (peer) building, sim- ulated by a calculated hourly or bin-method calibrated building energy performance model subject to the same weather, equipment type, and occupancy as the monitored building. This design, also called calibrated simulation, is a secondary concern of current building energy monitoring documents (ASH- RAE Guideline 14-2014; FEMP 2015; IPMVP 2014). Engineering Field Test. When an experiment focuses on testing a particular piece of equipment, actual (in situ) performance in a building is often of interest. The building provides a realistic envi- ronment for testing the equipment for reliability, maintenance requirements, and comfort and noise levels, as well as energy or water usage. Because energy consumption of mechanical equip- ment is significantly affected by the system control strategy testing procedures should be designed to incorporate the control strategy of the equipment and its system (Phelan et al. 1997a, 1997b). This type of monitoring and testing can also be used to calibrate computer simulation models of as-built and as-operated buildings, which can then be used to evaluate whole-building energy consumption. The equipment may be extensively instrumented. Some of the general advantages and disadvantages of these approaches are listed in Table 6 (Fracastoro and Lyberg 1983). Combining monitoring design choices can been successful (e.g., the before/after and test/reference approaches). ¦ Mode ¦ Advantages ¦ Disadvantages ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Before/after ¦ No reference building required. Same occupants implies smaller occupant variations. Modeling processes are mostly identical before/after. ¦ Weather different before/after. More than one heating/cooling season may be needed. Model is required to account for weather and other changes. ¦ ¦ Test/reference ¦ One season of data may be adequate. Small climate difference between buildings. ¦ Reference building required. Calibration phase required (may extend testing to two seasons). Occupants in either or both buildings can change behavior. ¦ ¦ On/off ¦ No reference building required. One season may be adequate. Modeling processes are mostly identical before/after. Most occupancy changes are small. ¦ Requires reversible product. Cycle may be too long if time constants are large. Model is required to account for weather differences in cycles. Dynamic model accounting for transients may be needed. ¦ ¦ Simulated occupancy ¦ Noise from occupancy is eliminated. A variety of standard schedules can be studied. ¦ Not "real" occupants. Expensive apparatus required. Extra cost of keeping building unoccupied. ¦ ¦ Nonexperimental reference ¦ Cost of actual reference building eliminated. With simulation, weather variation is eliminated. ¦ Database may be lacking in strata entries. Simulation errors and definition of reference problematic. With database, weather changes usually not possible. ¦ ¦ Engineering field test ¦ Information focused on product of interest. Minimal number of buildings required. Same occupants during test. ¦ Extensive instrumentation of product processes required. Models required to extrapolate to other buildings and climates. Occupancy effects not determined. ¦ Table 6 Advantages and Disadvantages of Common Experimental Approaches Source: Partially based on Fracastoro and Lyberg (1983). Inc. ASHRAE, 2019 user. single for Licensed | {}
99e37111-2fca-4539-a954-f8091c6a7c8d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 42.10 2019 ASHRAE Handbook-HVAC Applications (SI) Questions to be considered in choosing a monitoring approach include the following: · Can the building alteration being investigated be turned on and off at will? · Are occupancy and occupant behavior critical? Changes in build- ing tenants, use schedules, internal gains, temperature set points, and natural or forced ventilation practices should be considered because any one of these variables can ruin an experiment if not held constant or accounted for. · Are critical baseline energy or water performance data available? In before/after designs, time must be allotted to characterize the before case as precisely as the after case. For instances in which heating and cooling systems are evaluated, data may be required for a wide range of anticipated ambient conditions. · Is it a test of an individual technology, or are multiple technolo- gies installed as a package being tested? If the effects of individual technologies are sought, detailed component data and careful model-based analyses are required. · Does the technology have a single mode or multiple modes of operation? Can the modes be controlled to suit the experiment? If many modes are involved, it is necessary to test over a variety of conditions and conduct model-based analysis (Phelan et al. 1997a, 1997b). Part Five: Specify Data Analysis Procedures and Algorithms Data are useless unless they are distilled into meaningful prod- ucts that allow conclusions to be drawn. Too often, data are col- lected and never analyzed. This planning step focuses on specifying the minimum acceptable data analysis procedures and algorithms and detailing how collected data will be processed to produce desired data products. In this step, monitoring practitioners should · Determine the independent variables and analysis constants to be measured in the field (e.g., fan power, lighting and receptacle power, indoor air temperature). · Develop engineering calculations and equations (algorithms) nec- essary to convert field data to end products: this may include use of statistical methods and simulation modeling. · Specify detailed items, such as the frequency of data collection, the required range of independent variables to be captured in the data set, and the reasons certain data must be obtained at different intervals. For example, 15 min interval demand data may be assembled into hourly data streams to match utility billing data. Determine proper National Institute of Standards and Technol- ogy (NIST)-traceable calibration standards for each sensor type to be used. For details, see the references in ASHRAE Guideline 14- 2014 and IPMVP (2014) for specific types of sensors. However, it is often impractical to implement standards in the field. For example, maintaining the length of straight ductwork required for an airflow sensor is usually difficult, requiring compromise. Algorithm inputs can be assumed values (e.g., energy value of a unit volume of natural gas), one-time measurements (e.g., leakage area of a house), or time-series measurements (e.g., fuel consumption and outdoor and indoor temperatures at the site). The algorithms may pertain to (1) utility level aggregates of build- ings, (2) whole-building performance of particular buildings, or (3) performance of instrumented components. Chapter 19 of the 2017 ASHRAE Handbook-Fundamentals con- tains a lengthy discussion on modeling procedures, and readers should consult this material for more information on modeling. In this chapter, the discussion is categorized differently, with a view toward procedures and issues related to field energy monitoring projects. Table 7 provides a guide to selecting an analysis method. The error quotations are rough estimates for a single-building scenario. Empirical Methods. Although analysis methods based on mea- sured data are the simplest, they can have large uncertainty and may generate little or no information for small sample sizes. The sim- plest empirical methods are based on annual consumption values, tracking annual numbers and looking for degradation. Questions about building performance relative to other buildings are based on comparing certain performance indices between the building and an appropriate (peer) reference. The ENERGY STAR tools (www.energystar.gov) are probably the best-known performance comparison tools. The ASHRAE Building Energy Quotient (Build- ing EQ) tool has also been developed to not just provide perfor- mance comparison (benchmarking), but also streamline the energy audit process to include improvement measures in the report gener- ated from Building EQ. For commercial buildings, the most common comparison index is the energy utilization index (EUI), which is annual consumption, either by fuel type or summed over all fuel types, divided by the gross floor area (see MacDonald and W asserman [1989] for a discussion of indices). Comparison is often made only on the basis of general building type, which can ignore potentially large variations in how much floor area is heated or cooled, climate, number of workers in a building, number and type of computers in a building, and HVAC systems. Variations can be accommodated somewhat by stratifying the database from which the reference EUI is chosen. Computer sim- ulations are often used to set reasonable comparison values. The Commercial Buildings Energy Consumption Survey (CBECS) database (summarized in Chapter 37) has been used to develop ENERGY STAR and Building EQ energy use benchmarking meth- ods for several building types in the United States. Many of the building tools use 2003 data and are updating to the 2012 CBECS survey data Building types covered as of June 2009 include · Offices (general offices, financial centers, bank branches, and courthouses) Table 7 Whole-Building Analysis Guidelines ¦ ¦ Class of Method ¦ Class of Method ¦ Class of Method ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Project Goal ¦ Empirical (Billing Data)* ¦ Time-Integrated Model* ¦ Dynamic Model ¦ ¦ Building evaluation ¦ Yes, but expect monthly fluctuations in 20 to 30% range. ¦ Yes, extra care needed beyond 15% uncertainty. ¦ Yes, extra care needed beyond 10% uncertainty. ¦ ¦ Building retrofit evaluation ¦ Not generally applicable using monthly data, unless large samples are used. Requires daily data and various normalization techniques for reasonable accuracy. ¦ Yes, but difficult beyond 15% uncer- tainty. Method cannot distinguish multiple retrofit effects. ¦ Y es, can resolve 5% change with short-term tests. Can estimate multiple retrofit effects. ¦ ¦ Component evaluation ¦ Not applicable. ¦ Not applicable unless submetering is done to supplement. ¦ Y es, about 5% accuracy, but best with submetering. ¦ ¦ Note: Error figures are approximate for total energy use in a single building. All methods improve with selection of more buildings. ¦ Note: Error figures are approximate for total energy use in a single building. All methods improve with selection of more buildings. ¦ * Accuracy can be improved by decreasing time step to weekly or daily. These methods are of little use when outdoor temperature approaches balance temperature. ¦ * Accuracy can be improved by decreasing time step to weekly or daily. These methods are of little use when outdoor temperature approaches balance temperature. ¦ Inc. ASHRAE, 2019 user. single for Licensed | {}
81ed3725-2b46-42a6-88f4-f7003f74af18 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Building Energy and Water Monitoring 42.11 · K-12 schools · Supermarkets/grocery stores · Hospitals (acute care and children's) · Medical offices and clinics · Hotels/motels · Residence halls/dormitories · Retail stores · Warehouses (refrigerated and nonrefrigerated) For some of these building types, some secondary spaces are allowed: · Computer data centers · Garages and parking lots · Swimming pools Initial work in this area covered only electricity use for office buildings (Sharp 1996), but the methods have been extended to cover all fuels for the listed building types and water. Results show that electricity use of office buildings is most significantly explained by the number of workers in the building, number of computers, whether the building is owner-occupied, and number of operating hours each week. Only a subset of these parameters might be used to determine a benchmark within a specific census division. ENERGY STAR documentation on current tools and the perfor- mance normalization factors for a range of building types can be found at www.energystar.gov/buildings. Simple empirical methods applied to retrofit applications should include at least some periods of data on daily energy or water use and average daily temperature (recorded locally) to account for vari- ations in occupancy and building schedules. Monthly EUI or billing data provide more information for empirical analysis and can be used for extended analysis of energy impacts of retrofit applica- tions, for example, in conditional demand analysis (Hirst and Reed 1991). Monthly data can also be used to detect billing errors, improper equipment operation during unoccupied hours, and sea- sonal space condition problems (Haberl and Komor 1990a, 1990b). Daily data are often used in these analyses, and raw hourly total building consumption data, when available, provide more detailed information on occupied versus unoccupied performance. Hourly, daily, monthly, and annual EUI across buildings can be directly compared when reduced to average power per unit area (power den- sity). To avoid false correlations, the method of analysis should have statistical significance that can be traced to realistic parameters (Haberl et al. 1996). ASHRAE (2012) gives best-practice protocols for measurements at different time periods. Model-Based Methods. These techniques allow a wide range of additional data normalization to potentially improve the accu- racy of comparisons and provide estimates of cause-and-effect relations. The analyst must carefully define the system and postu- late a useful form of the governing energy balance/system perfor- mance equation or system of equations, as often embodied in hour- by-hour simulation programs. Explicit terms are retained for equipment or processes of particular interest. As part of the data analysis, whole-building data (driving forces and thermal or energy response) are used to determine the model' s significant parameters. The parameters themselves can provide insight, although parame- ter interpretation can be difficult, particularly with time-integrated billing data methods. The model can then be used for normalization as well as future diagnostic and control applications. Two general classes of models are used in analysis methods: time-integrated methods and dynamic techniques (Balcomb et al. 1993). Simula- tion modeling results used for design of new buildings may not cover all energy used in a building and thus could be difficult to compare with empirical data. Time-Integrated Methods. Based on algebraic calculation of the building energy balance, time-integrated methods are often used before data comparison to correct annual consumption for variations in outdoor temperature, internal gains, and internal temperature (ASHRAE 2002; Fels 1986; Haberl and Claridge 1987). This type of calibrated model is essential for most retrofit applications. Time-integrated methods can be used with whole-building en- ergy consumption data (billing data) or with submetered end-use data. For example, standard time-integrated methods are often used to separately analyze end-use consumption data on heating, cool- ing (Ternes and Wilkes 1993), domestic water heating, and others for comparison and analysis. Time-integrated methods are generally reliable, as long as the following three conditions are ac- counted for: · Appropriate time step. Generally, the time step should be as long as or longer than the response time of the building or building sys- tem for which energy use is being integrated. For example, the response of daylighting controls to natural illumination levels can be rapid, allowing short time steps for data integration. In con- trast, the response of cooling system energy use to changes in cooling load can be comparatively slow. In this instance, either a time step long enough to average over these slow variations or a dynamic model should be used. In general, an appropriate time step should account for the physical behavior of the energy sys- tem(s) and the expression of this behavior in model parameters. · Linearity of model results. Generally, time-integrated models should not be applied to data used to estimate nonlinear effects. Air infiltration, for example, is nonlinear when estimated using wind speed and indoor/outdoor temperature difference data in certain models. Estimation errors result if these parameters are independently time-integrated and then used to calculate air infil- tration. These nonlinear effects should be modeled at each time step (each hour, for example). · End-use uniformity within data set. End-use data sets should be uniform (i.e., should not inadvertently contain observations with measurements of end uses other than those intended). During mild weather, for example, HVAC systems may provide both heating and cooling over the course of a day, creating data observations of both heating and cooling measurements. In a time-integrated model of heating energy use, these cooling energy observations lead to error. These observations should be identified or otherwise flagged by their true end use. For whole-building energy consumption data (billing data), rea- sonable results can be expected from heating analysis models when the building is dominantly responsive to indoor/outdoor tempera- ture differences. Billing data analysis yields little of interest when internal gains are large compared to envelope loads, as in large com- mercial buildings and industrial applications. Daily, weekly, and monthly whole-building heating season consumption integration steps can been used (Claridge et al. 1991; Fels 1986; Sharp and MacDonald 1990; Ternes 1986). Cooling analysis results have been less reliable because cooling load is not strictly proportional to vari- able-base cooling degree-days (Fels 1986; Haberl et al. 1996; Kissock et al. 1992). Problems also arise when solar gains are dom- inant and vary by season. Dynamic Techniques. Dynamic models, both macrodynamic (whole-building) or microdynamic (component-specific), offer great promise for reducing monitoring duration and increasing con- clusion accuracy. Furthermore, individual effects from multiple measures and system interactions can be examined explicitly. Dynamic whole-building analysis is generally accompanied by detailed instrumentation of specific technologies. Dynamic techniques create a dynamic physical model for the building, adjusting model parameters to fit experimental data (Duffy et al. 1988; Subbarao 1988). In residential applications, computer- controlled electric heaters can be used to maintain a steady interior temperature overnight, extracting from these data an experimental Inc. ASHRAE, 2019 user. single for Licensed | {}
e7e13907-1317-4719-8d98-5f2e32accf87 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 42.12 2019 ASHRAE Handbook-HVAC Applications (SI) value for the building steady-state load coefficient. A cooldown period can also be used to extract information on internal building mass thermal storage. Daytime data can be used to renormalize the building response (computed from a microdynamic model) to solar radiation, which is particularly appropriate for buildings with glaz- ing areas over 10% of the building floor area (Subbarao et al. 1986). Once the data with electric heaters have been taken, the building can be used as a dynamic calorimeter to assess the performance of aux- iliary heating and cooling systems. Similar techniques have been applied to commercial buildings (Burch et al. 1990; Norford et al. 1985). In these cases, delivered energy from the HVAC system must be monitored directly in lieu of using electric heaters. Because ventilation is a major variable in the building energy balance, outdoor airflow rate should also be moni- tored directly. Simultaneous heating and cooling (common in large buildings) requires a multizone treatment, which has not been ade- quately tested in any of the dynamic techniques. Equipment-specific monitoring guidelines using dynamic mod- eling have been successfully tested in a variety of applications. For fans and pumps, relatively simple regression techniques from short- term monitoring provided accurate estimates of annual energy consumption when combined with an annual equipment load pro- file. For chillers, a thermodynamic model used with short-term monitoring captured the most important operating parameters for estimating annual chiller energy performance. In all cases, the key to accurate model results was capturing a wide enough range of the independent load variable in monitored data to reflect annual oper- ating characteristics (Phelan et al. 1997a, 1997b). Part Six: Specify Field Data Monitoring Points Careful specification offield monitoring points is critical to iden- tifying variables that need to be measured to produce required data. The analysis method determines the data to be measured. The simplest methods require no on-site instrumentation. As methods become more complex, data channels increase. For engineering field tests conducted with dynamic techniques, up to 100 data chan- nels may be required. Because metering projects are often conducted in buildings with changing conditions, special consideration must be given to identi- fying and monitoring significant changes in climate, systems, and operation during the monitoring period. Additional monitoring points may be required to measure variables that are assumed to be constant, insignificant, or related to other measured variables to draw sound conclusions from the measurements. Because the necessary data may be obtained in several ways, data analysts, equipment installers, and data acquisition system engineers should work together to develop tactics that best suit the project require- ments. It is important to anticipate the need for supplemental measurements in response to project needs that may not become apparent until equipment is installed. The cost of data collection is a nonlinear function of the number, accuracy, and duration of measurements considered while planning within budget constraints. Costs per data point typically decrease as the number of points increases, but increase with accuracy require- ments. Duration of monitoring can have many different effects. Ifthe extent of data applications is unknown, such as in research projects, the value of other concurrent measurements should be considered, because the incremental cost of additional analyses may be small. For any project involving large amounts of data, data quality ver- ification (see Part Eight) should be automated (Lopez and Haberl 1992). Although this may require adding monitoring points to facil- itate energy balances or redundancy checks, the added costs are likely to be offset by savings in data verification. If multiple sites are to be monitored, common protocols for selecting and describing all field monitoring points should be estab- lished so data can be more readily verified, normalized, compared, and averaged. Protocols, such as those recommended in ASHRAE (2010), also add consistency in selecting monitoring points. Pilot installations should be conducted to provide data for a test of the system and to ensure that the necessary data points have been prop- erly specified and described. Monitoring Equipment. General considerations in selecting monitoring equipment include · Evaluating equipment thoroughly under actual test conditions before committing to large-scale procurement. Particular atten- tion should be paid to any sensitivity to power outages and to protection against power surges and lightning. · Considering local setup and testing of complex data acquisition systems that are to be installed in the field. · Avoiding unproven data acquisition equipment (Sparks et al. 1992). Untested equipment, even if donated, may not be a good value. · Considering costs and benefits of remote data interrogation and programming. · Evaluating quality and reliability of data loggers and instrumen- tation; these issues may be more important than cost, particularly when data acquisition sites are distant. · Verifying vendor claims by calling references or obtaining perfor- mance guarantees. · Considering portable battery-powered data loggers in lieu of hard-wired loggers if the monitoring budget is limited and the length of the monitoring period is less than a few months. · Ensure that monitoring equipment and installation methods are consistent with prevailing laws, building codes, and standards of good practice. Using a building energy management system or direct digital con- trol systems for data acquisition may decrease costs. This should be considered only when the sensors and their accuracy and limitations (scan rate, etc.) are thoroughly understood. When merging data from two data acquisition systems, problems may arise such as differing reliability and low data resolution (e.g., 1 kW resolution of a circuit that draws 10 kW fully loaded). These problems can often be avoided, however, by adding appropriate sensors and setting up custom log- ging or calculations with point, memory, and programming capacity. Once the required field data monitoring points are specified, these requirements should be clearly communicated to all members of the project team to ensure that the actual monitoring points are accurately described. This can be accomplished by publishing hand- books for measurement plan development and equipment installation and by outlining procedures for diagnostic tests and technology assessments. Because hardware needs vary considerably by project, specific selection guidelines are not provided here. However, general char- acteristics of data acquisition hardware components are shown in Table 8. Some typical concerns for selecting data acquisition hardware are outlined in Table 9. In general, data logger and instru- mentation hardware should be standardized, with replacements available in the event of failure. Also consider redundant measure- ments for critical data components that are likely to fail, such as modems, flowmeters, shunt resistors on current transformers, and devices with moving parts (O'Neal et al. 1993). Some measurements that are more difficult to obtain accurately because of instrumenta- tion limitations are summarized in Table 10. Safety must be considered in equipment selection and installa- tion. Installation teams of two or more individuals reduce risks. When contemplating thermal metering, the presence of asbestos insulation on water piping should be determined. Properly licensed trades personnel, such as an electrician or welder, should be a funda- mental part of any team installing electrical monitoring equipment. To prevent inadvertent tampering, occupants and maintenance personnel should be carefully briefed on what is being done and the Inc. ASHRAE, 2019 user. single for Licensed | {}
00abe980-033c-4064-b3ed-2e6d7cb5520e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Building Energy and Water Monitoring 42.13 Table 8 General Characteristics of Data Acquisition System (DAS) ¦ Types of DAS ¦ Typical Use ¦ Typical Data Retrieval ¦ Comments ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Manual readings ¦ Total energy or water use ¦ Monthly or daily written logs ¦ Human factors may affect accuracy and reading period. Data must be manually entered for computer analysis. ¦ ¦ Pulse counter, solid state (1, 4, or 8 channels) ¦ Total energy or water use (some end use) ¦ Polled by telephone to mainframe or minicomputer ¦ Computer hardware and software are needed for transfer and conversion of pulse data. Can be expensive. Can handle large numbers of sites. User-friendly. ¦ ¦ Stick-on battery powered logger ( 1 to 8 channels) ¦ Diagnostics, technology assessment, end use ¦ Monthly manual download to PC ¦ Very useful for remote sites. Can record pulse counts, temperature, etc., up to thousands of records. ¦ ¦ Plug-in A/D boards for PCs ¦ Diagnostics, technology assessment, control ¦ On-site real-time collection and storage ¦ Usually small-quantity, unique applications. PC programming capability needed to set up data software and configure boards. ¦ ¦ Simple field DAS (usually 16 to 32 channels) ¦ Technology assessment, residential end use (some diagnostics) ¦ Phone retrieval to host computer for primary storage (usually daily to weekly) ¦ Can use PCs as hosts for data retrieval. Good A/D conversion available. Low cost per channel. Requires programming skills to set up field unit and configure communications for data transfer. ¦ ¦ Advanced field DAS (usually >40 channels/ units) ¦ Diagnostics, energy control systems, commercial end use ¦ On-site real-time collection and data storage, or phone retrieval ¦ Usually designed for single buildings. Can be PC-based or stand-alone unit. Can run applications/diagnostic programs. User-friendly. ¦ ¦ Direct digital control or building automation system ¦ On-site diagnostics, energy measurement and verification ¦ Proprietary data collection pro- cedures, manual or automated export to spreadsheet. ¦ Requires significant coordination with building operation personnel. Sensor accuracy, calibration, and installation require confirmation. Good for projects with limited instrumentation budget. ¦ Table 9 Practical Concerns for Selecting and Using Data Acquisition Hardware ¦ Components ¦ Field Application Concerns ¦ ¦ --- ¦ --- ¦ ¦ Data logger unit and peripherals ¦ · Select equipment for field application. Flexible or adaptable input capabilities desirable. · Equipment should store data electronically for easy transfer to a computer. · Remote programming capability should be avail- able to minimize on-site software modifications. · Avoid equipment with cooling fans. · Use high-quality, reliable communication devices or methods. · Make sure logger/computer and communication reset after power outage. ¦ ¦ Cabling and interconnection hardware ¦ · Use only signal-grade cable: shielded, twisted-pair with drain wire for analog signals. · Mitigate sources of common mode and normal mode signal noise. ¦ ¦ Sensors ¦ · Use rugged, reliable sensors rated for field applica- tion. · Use a signal splitter if sharing existing sensors or signals with other recorders or energy management control system (EMCS). · Select ranges so sensors operate at 50 to 75% of full scale. · Choose sensors that do not require special signal conditioning or power supply, if possible. · Calibrate sensors and recalibrate periodically. · When possible, use redundant channels to cross- check critical channels that can drift. ¦ purpose of sensors and equipment. Data loggers should have a dedicated (non-occupant-switchable), hard-wired power supply to prevent accidental power loss. Sensors. Sensors should be selected to obtain each measurement on the field data list. Next, conversion and proportion constants should be specified for each sensor type, and the accuracy, resolu- tion, and repeatability of each sensor should be noted. Sensors should be calibrated before they are installed, preferably with a NIST-traceable calibration procedure. They should be checked periodically for drift, recalibrated, and then post-calibrated at the Table 10 Instrumentation Accuracy and Reliability ¦ Instrument ¦ Problems ¦ ¦ --- ¦ --- ¦ ¦ Hygrometers ¦ Drift, saturation, and accuracy over time; need for cali- bration to remove temperature dependence; aspirated systems need to be cleaned periodically. Chilled-mirror systems require frequent maintenance. ¦ ¦ Flowmeters ¦ Need for calibration, reliability (especially for steam flow). Moving parts prone to failure. Pipe size must be verified before calibration or installation. ¦ ¦ Heatflow meters ¦ 60 Hz noise from surroundings, calibration. ¦ ¦ Single-ended voltage ¦ Grounding problems, spurious line voltages, 60 Hz noise. ¦ ¦ Outdoor air temperature sensor ¦ Must be properly shielded from solar radiation. Aspira- tion may reduce solar radiation effects but decrease long- term reliability. ¦ ¦ RTD sensors ¦ Signal wire length affects readings. ¦ ¦ Power meters ¦ Polarity of current transducers (CTs) often marked incor- rectly, problems with shunt resistors and CT output. Devices should be checked before installation. ¦ conclusion of the experiment (Haberl et al. 1996). Instrument cali- bration is particularly important for flow and power measurement. Particular attention must be paid to sensor location. For example, if the method requires an average indoor temperature, examine the potential for internal temperature variation; data from several tem- perature sensors must often be averaged. Alternatively, temperature sensors adjacent to HVAC thermostats detect the temperature to which the HVAC equipment reacts. For temperature or pitot tube flow measurements the location must be sufficiently downstream of louvers, filters, and pipe turns to obtain accurate results. Scanning and Recording Intervals. Measurement frequency and data storage can affect the accuracy of results. Scanning differs from storage in that data channels may be read (scanned) many times per second, for example, whereas average data may be record- ed and stored every 15 min. Most data loggers maintain temporary storage registers, accumulating an integrated average of channel readings from each scan. The average is then recorded at the speci- fied interval. After the channel list is compiled and sensor accuracy require- ments established, scan rates should be assigned. Some sensors, such as indoor and outdoor temperature sensors, may require low Inc. ASHRAE, 2019 user. single for Licensed | {}
f01a9b07-9448-48ae-803e-b02f603f447e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 42.14 2019 ASHRAE Handbook-HVAC Applications (SI) (2) scan rates (once every 5 min). Others, such as total electric sensors, may contain high-frequency transients that require rapid sampling (many times per second). The scan rate must be fast enough to ensure that all significant effects are monitored. The maximum sampling rate is usually programmed into the log- ger, and averages are stored at a specified time step (e.g., hourly). Some loggers can scan different channels at different rates. The logger's interrupt capability can also be used for rapid, infrequent transients. Interrupt channels signal the data logger to start monitor- ing an event only once it begins. In some cases, online computation of derived quantities must be considered. For example, ifheating or cooling flow in an air duct is required, it can be computed from a dif- ferential temperature measurement multiplied by an air mass flow rate determined from a one-time measurement. However, it should be computed and totaled only when the fan is operating. Data collected by monitoring equipment are usually used for the following purposes: Part Seven: Resolve Project Data Accuracies · Direct reporting of primary measurement data · Reporting of secondary or deduced quantities (e.g., thermal ener- gy consumed by a building, found by multiplying mass flow rate and temperature difference) · Subsequent interpretation and analyses (e.g., to develop a statis- tical model of energy used by a building versus outdoor dry-bulb temperature) In all three cases, the value of the measurements is dramatically increased if the associated uncertainty can be quantified. Basic Concepts. Uncertainty can be better understood in terms of confidence limits, which define the range of values that can be expected to include the true value with a stated probability (ASH- RAE Guideline 2). Thus, a statement that the 95% confidence limits are 5.1 to 8.2 implies that the true value is between 5.1 and 8.2 in 19 out of 20 observations or, more loosely, that we are 95% confident that the true value lies between 5.1 and 8.2. For a given set of n observations with normal (Gaussian) error distribution, the total variance about the mean predicted value X , provides a direct indi- cation of the confidence limits. Thus the "true" mean value X' ofthe random variable is bounded as follows: Inc. ASHRAE, 2019 user. single for Licensed 2 X 土 (t�/2,n-1 N 0 /n ) (1) where a = level of significance X = mean predicted value of random variable X ta/2.n-1 = /-statistic with probability of 1 - a/2 and n - 1 degrees of freedom (tabulated in most statistical textbooks) n = number of observations, with Gaussian error distribution 2 o = estimated measurement variance The terms accuracy and precision are often used to distinguish between bias errors and random errors. A set of measurements with small bias errors is said to have high accuracy, and a set of measure- ments with small random errors is said to have high precision. In repeated measurements of a given sample by the same technique (single-sample data), each measurement has the same bias. Bias er- rors include those that are (1) known and can be removed by calibration, (2) negligible and are ignored, and (3) estimated and are included in the uncertainty analysis. Itis usually difficult to estimate bias limits, and this effect is often overlooked. However, a proper error analysis should include bias error, which is usually written as a plus-minus error. ASME Standard PTC 19.1 has a more complete discussion. Because bias errors bm and random errors Em are usually uncor- related, measurement variance �2 can be expressed as For further information on uncertainty, see Chapter 37 of the 2017 ASHRAE Handbook-Fundamentals. For more information on uncertainty calculation methods related specifically to building energy savings monitoring, see ASHRAE Guideline 14-2014, An- nex B. 2 o (b m' Em) = �2(bm) + �2(�m) meas Primary Measurement Uncertainty. Sensor and measuring equipment manufacturers usually specify measurement variances; frequent recalibration minimizes bias errors. As indicated by Equa- tion (1), increasing the number of measurements n reduces the uncertainty bounds. Uncertainty in Derived Quantities. Once a specific algorithm or equation for obtaining final data from physical measurements has been established, standard techniques can be used to incorporate primary measurement uncertainties into the final data product. For random errors, the Kline and McClintock (1953) error propagation method, based on a first-order Taylor series expansion, is widely used to determine measurement uncertainties in derived variables in single-sample experiments. Bias errors are difficult to account for; the usual practice is to remove them through calibration and exclude them from the uncertainty analysis. Uncertainty in Statistical Regression Models. Statistical re- gression models developed from measured data are usually used for predictive purposes. Measurement errors are much smaller than model errors, which arise because the regression model is imper- fect; that is, it is unable to explain the entire variation in the regression variable (Box 1978). Measurement error is inherently in- cluded in the identified model, so total prediction variance is simply given by the model prediction uncertainty. Determining prediction errors from regression models is subject to different types of problems. The sources of error can be classified into three categories (Reddy et al. 1998): · Model misspecification errors occur because the functional form of the regression model is usually an approximation of the true driving function of the response variable. · Model prediction errors occur because a model is never perfect. · Model extrapolation errors occur when a model is used for pre- diction outside the region covered by the data from which the model was developed. Models developed from short data sets, which do not satisfactorily represent the annual behavior of the system, are subject to this error. This error cannot be quantified in statistical terms alone, but certain experimental conditions are likely to lead to accurate predictive models. This falls under the purview of experimental design (Box 1978). Misspecification and extrapolation errors are likely to introduce bias and random error. If ordinary least-squares regression is used for parameter estimation, and if the model is subsequently used for prediction, model prediction will be purely random. Thus, models identified from short data sets and used to predict seasonal or annual energy use are affected by misspecification and extrapola- tion errors. The least-squares method of calculating linear regression coeffi- cients cannot produce unbiased estimators of slope and intercept if there are errors associated with measuring the predictor variable. The uncertainty analysis methodology developed for in situ equip- ment testing uses standard linear regression practices to find the functional relationship and then estimates the increased uncertainty in the regression prediction because of random and bias errors in both variable measurements (Phelan et al. 1996). Experimental Design. Errors can also be estimated based on his- torical experience (e.g., using results from previous similar projects). Alternatively, a pilot study can obtain an estimate of potential errors in a proposed analysis. Some estimate of potential error must be | {}
a903a3e5-617e-48c9-a339-b74159e701e8 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Building Energy and Water Monitoring 42.15 available to determine whether project goals and objectives are rea- sonable. Estimating data uncertainty is one part of the iterative procedure associated with proper experimental design. Ifthe final data product uncertainty determined using the given evaluation procedure is unacceptable, uncertainty can be reduced in one or more of the fol- lowing ways: · Reducing overall measurement uncertainty (improving sensor precision) · Increasing the duration of monitoring to average out stochastic variations · Increasing the number of buildings tested (sample size) On the other hand, if simulations or estimates indicate that the expected bias in the final data product is unacceptable, the bias may be reduced by one or more of the following steps: · Adding sensors to get an unbiased measurement of the quantity · Using more detailed models and analysis procedures · Increasing data acquisition frequency, combined with a more detailed model, to address biases from sensor or system nonlin- earities. Accuracy Versus Cost. The need for accuracy must be carefully balanced against measurement and analysis costs. Accuracy loss can stem from instrumentation or measurement error, normalization or model error, sampling or statistical error, and errors in assump- tions. Each of these sources can be controlled to varying degrees. However, in general, more accurate methods follow the law of diminishing returns, in which further reductions in error come at progressively greater expense. Because ofthis trade-off, the optimal measurement solution is usu- ally found by an iterative approach, where incremental improvements in accuracy are assessed relative to the increase in measurement cost. Such optimization requires that a value be placed on increasing levels of accuracy. One method of evaluating the uncertainty of a proposed method is to calculate results using the highest and lowest values in the confidence interval. The difference between these values can be translated into a monetary amount that is at risk. The question that must be answered is whether further measurement investment is war- ranted to reduce this risk. Part Eight: Specify Verification and Quality Assurance Procedures Establishing and using data quality assurance (QA) proce- dures can be very important to the success of a field monitoring project. The amount and importance of the data to be collected help determine the extent and formality ofQA procedures. For most projects, the entire data path, from sensor installation to procedures that generate results for the final report, should be considered for verification tests. In addition, the data flow path should be checked routinely for failure of sensors or test equipment, as well as unex- pected or unauthorized modifications to equipment. QA often requires complex data handling. Building energy mon- itoring projects collect data from sensors and manipulate those data into results. Data handling in a project with only a few sensors and required readings can consist of a relatively simple data flow on paper. Computers, which are generally used in one or more stages of the process, require a different level of process documentation because much of what occurs has no direct paper trail. Computers facilitate collection of large data sets and increase project complexity. To maximize automation, computers require development of specific software. Often, separate computers are involved in each step, so passing information from one computer to another must be automated in large projects. To move data as smoothly as possible, an automated data pipeline should be developed; this minimizes the delay from data collection to results production and maximizes the cost-effectiveness ofthe entire project. Because collected data are valuable, data back-up procedures must also be part of QA. At a minimum, the basic data, either raw or first-level processed, should be stored in at least one, and preferably two, different back-up locations, apart from the main data storage location, to allow data recovery in case of hardware failure, fire, vandalism, etc. Back-ups should occur at regular intervals, probably not less than weekly for larger projects. Frequent data acquisition (preferably automated), with a quality control review of summarized and plotted data, is essential to ensure that reliable data are collected. Verification procedures should be performed at frequent intervals (daily or weekly), depending on the importance of missing data. This minimizes data loss due to equipment failure and/or changes at a building site. It also allows processed information to be applied quickly. The following QA actions should take place: · Calibrate hardware and establish a good control procedure for collection of data. Use NIST-traceable calibration methods. · Verify data, check for reasonableness, and prepare a summary report to ensure data quality after collection. · Perform initial analysis of data. Significant findings may lead to changes in procedures for checking data quality. · Thoroughly document and control procedures applied to remedy problems. These procedures may entail changes in hardware or collected data (such as data reconstruction), which can have a fun- damental effect on the results reported. · Archive raw data obtained from the site to ensure project integrity. Three aspects of a monitoring project that require QA are shown in Table 11 : hardware, engineering data, and characteristics data. Table 11 Quality Assurance Elements ¦ Time Frame ¦ Hardware ¦ Engineering Data ¦ Characteristics Data ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Initial start-up ¦ Bench calibration (1) Field calibration (1) Installation verification ( 1 ) ¦ Installation verification (1) Collection verification (1, 2) Processing verification ( 1, 2) Result production (1, 2) ¦ Field verification (1) Completeness check (1) Reasonableness check ( 1, 2) Result production (1, 2) ¦ ¦ Ongoing ¦ Functional testing (1) Failure mode diagnosis (3) Repair/maintenance (4) Change control (1) ¦ Quality checking (2) Reasonableness checking (2) Failure mode diagnosis (3) Data reconstruction (4) Change control (1) ¦ Problem diagnosis (3) Data reconstruction (4) Change control (1) ¦ ¦ Periodic ¦ Preventive maintenance (1) Calibration (1) ¦ Summary report preparation and review (2) ¦ Scheduled updates/resurveys (1) Summary report preparation and review (2) ¦ (1) Actions to ensure good data. (2) Actions to check data quality. (3) Actions to diagnose problems. (4) Actions to repair problems. Inc. ASHRAE, 2019 user. single for Licensed | {}
dadfc779-b46e-4829-b476-6623ad4193c8 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 42.16 2019 ASHRAE Handbook-HVAC Applications (SI) Three QA reviews are necessary for each aspect: (1) initial QA con- firms that the project starts correctly; (2) ongoing QA confirms that information collected by the project continues to satisfy quality requirements; and (3) periodic QA involves additional checks, established at the beginning of the project, to ensure acceptable per- formance quality. Information about data quality and the QA process should be readily available to data users. Otherwise, significant analytical resources may be expended to determine data quality, or the analy- ses may never be performed because of uncertainties. Part Nine: Specify Recording and Data Exchange Formats This step specifies the formats in which data are supplied to the end user or other data analysts. Both raw and processed (adjusted for missing data or anomalous readings) data formats should be speci- fied. In addition, if supplemental analyses are planned, the medium and format to be used (type of storage, possibly magnetic tape type, spreadsheet, character encoding standard) should be specified. These requirements can be determined by analyzing the software data for- mat specifications. Common formats for raw data are comma- and blank-delimited American Standard Code for Information Exchange (ASCII), which do not require data conversion. Data documentation is essential for all monitoring projects, especially when several organizations are involved. Data usability is improved by specifying and adhering to data recording and exchange formats. Most data transfer problems are related to inadequate documentation. Other problems include hardware or software incompatibility, errors in electronic storage media, errors or inconsis- tencies in the data, and transmittal of the wrong data set. The following precautions can prevent some of these problems: · Provide documentation to accompany the data transfer (Table 12). Because these guidelines apply to general data, models, pro- grams, and other types of information, items listed in Table 12 may not apply to every case. · Provide documentation of transfer media, including the computer operating system, software used to create the files, media format (e.g., ASCII, application-specific), and media characteristics (note that many CD-ROM formats exist, some of which are proprietary and not widely used, so care should be taken to use commonly available methods). · Provide procedures to check the accuracy and completeness of data transfer, including statistics or frequency counts for variables and hard-copy versions ofthe file. Test input data and correspond- ing output results for models on other programs. · Keep all raw data, including erroneous records. · Convert and correct data; save routines for later use. · Limit equipment access to authorized individuals. · Check incoming data soon after they are collected, using simple time-series and x-y inspection plots. · Automate as many routines as possible to avoid operator error. REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. Armstrong, P.R., D.L. Hadley, R.D. Stenner, and M.C. Janus. 2001. Whole- building airflow network characterization by a many-pressure-states (MPS) technique. ASHRAE Transactions 107(2):645-657. ASHRAE/BSR/ACCA. 2018. Standard for commercial building energy audits. ASHRAE Standard 211-2018 ASHRAE. 2005. Engineering analysis of experimental data. ASHRAE Guideline 2-2005. Table 12 Documentation Included with Computer Data to Be Transferred 1. Title and/or acronym 2. Contact person (name, address, phone number) 3. Description of file (file format, number of records, geographic cover- age, spatial resolution, time period covered, temporal resolution, sam- pling methods, uncertainty/reliability) 4. Definition of data values (variable names, units, codes, missing value representation, location, method of measurement, variable derivation, variable formats) 5. Original uses of file 6. Size of file (number of records, bytes) 7. Original source (person, agency, citation) 8. Pertinent references (complete citation) on materials providing addi- tional information 9. Appropriate reference citation for the file 10. Credit line (for use in acknowledgments) 11. Restrictions on use of data/program 12. Disclaimer, such as · Unverified data; use at your own risk. · Draft data; use with caution. · Clean data to the best of our knowledge. Please let us know of any possible errors or questionable values. · Program under development. · Program tested under the following conditions (conditions specified by author). ASHRAE. 2002. Measurement of energy and demand savings. ASHRAE Guideline 14-2014. ASHRAE. 2011. Proceduresfor commercial building energy audits, 2nd ed. ASHRAE. 2012. Performance measurement protocols for commercial buildings: Best practices guide. ASHRAE/CIBSE/USGBC. 2010. Performance measurement protocols for commercial buildings. ASHRAE, in collaboration with the Chartered In- stitute of Building Engineers, London, U.K., and U.S. Green Building Council, Washington, D.C. ASME. 1998. Measurement uncertainty: Instruments and apparatus. ANSI/ ASME Standard PTC 19.1-98 (R2004). American Society of Mechanical Engineers, New York. ASTM. 2003. Test method for determining air leakage rate by fan pressur- ization. Standard E779-03. American Society for Testing and Materials, West Conshohocken, PA. Balcomb, J.D., J.D. Burch, and K. Subbarao. 1993. Short-term energy mon- itoring of residences. ASHRAE Transactions 99(2):935-944. Box, G.E.P. 1978. Statistics for experimenters: An introduction to design, data analysis and model-building. John Wiley & Sons, New York. Burch, J.D., K. Subbarao, A. Lekov, M. Warren, L. Norford, and M. Krarti. 1990. Short-term energy monitoring in a large commercial building. ASHRAE Transactions 96(1):1459-1477. CBE. 2008. Occupant indoor environmental quality (IEQ) surveyTM. Center for the Built Environment. www.che.berkeley.edu/ressxnch/survey.htm. Claridge, D.E., J.S. Haberl, W.D. Turner, D.L. O'Neal, W. M. Heffington, C. Tombari, M. Roberts, and S. Jaeger. 1991. Improving energy conserva- tion retrofits with measured savings. ASHRAE Journal 33(10):14-22. Cohen, R.R., P. W. O'Callaghan, S.D. Probert, N.M. Gibson, D.J. Nevrala, and G.F. Wright. 1987. Energy storage in a central heating system: Spa school field trail. Building Service Engineering Research Technology 8:79-84. DeCicco, J., R. Diamond, S.L. Nolden, J. DeBarros, and T. Wilson. 1995. Improving energy efficiency in apartment buildings. Proceedings ACEEE, Washington, D.C., pp. 234-236. Duffy, J.J., D. Saunders, and J. Spears. 1988. Low-cost method for evalua- tion of space heating efficiency of existing homes. Proceedings of the 12th Passive Solar Conference, ASES, Boulder, CO. Fels, M.F., ed. 1986. Measuring energy savings: The scorekeeping ap- proach. Energy and Buildings, vol. 9. Inc. ASHRAE, 2019 user. single for Licensed | {}
b3445c53-6d02-4300-adf7-1ad403eb3a38 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Building Energy and Water Monitoring 42.17 FEMP. 2015. M&V guidelines: Measurement and verification for federal energy projects. Federal Energy Management Program, U.S. Department of Energy, Washington D.C. www.energy.gov/sites/prod/files/2016 01/f28/mv _guide_ 4_0.pdf. Fracastoro, G. V., and M.D. Lyberg. 1983. Guiding principles concerning design of experiments, instruments, instrumentation, and measuring techniques. Swedish Council for Building Research, Stockholm. www. ecbcs.org/Data/publications/ECB _Annex_03 guiding_principles.pdf. Haberl, J.S., and D.E. Claridge. 1987. An expert system for building energy consumption analysis: Prototype results. ASHRAE Transactions 93(1): 979-998. Haberl, J.S., and P.S. Komor. 1990a. Improving energy audits: How annual and monthly consumption data can help. ASHRAE Journal 32(8):26-33. Haberl, J.S., and P.S. Komor. 1990b. Improving energy audits: How daily and hourly data can help. ASHRAE Journal 32(9):26-36. Haberl, J., D.E. Claridge, and D. Harrje. 1990. The design of field experi- ments and demonstration. Proceedings of the IEA Field Monitoringfor a Purpose Workshop (Chalmers University, Gothenburg, Sweden, April), pp. 33-58 (Available from Energy Systems Lab, Texas A&M University). Haberl, J.A., Reddy, D. Claridge, D. Turner, D. O'Neal, and W. Heffington. 1996. Measuring energy-saving retrofits: Experiences from the Texas LoanSTAR Program. ORNL Report ORNL/Sub/93-SP090-1. Oak Ridge National Laboratory, Oak Ridge, TN. Hirst, E., and J. Reed, eds. 1991. Handbook of evaluation of utility DSM programs. ORNL Report ORNL/CON-336, Oak Ridge National Labo- ratory, Oak Ridge, TN. Hirst, E., D. White, and R. Goeltz. 1983. Comparison of actual electricity savings with audit predictions in the BPA residential weatherization pilot program. ORNL Report ORNL/CON-142. Oak Ridge National Labora- tory, Oak Ridge, TN. Hough, R.E., P.J. Hughes, R.J. Hackner, and W.E. Clark. 1987. Results-ori- ented methodology for monitoring HVAC equipment in the field. ASHRAE Transactions 93(1):1569-1579. Hughes, P.J., and J.A. Shonder. 1998. The evaluation of a 4000-home geo- thermal heat pump retrofit at Fort Polk, Louisiana: Final report. ORNL Report ORNL/CON-460. Oak Ridge National Laboratory, Oak Ridge, TN. IPMVP. 2014 International performance measurement and verification pro- tocol, vol. III: Concepts and practices for determining energy savings in new construction. EVO 30000-1 .2014. Efficiency Valuation Organiza- tion, Washington, D.C. www.evo-world.org. IPMVP. 2014. International performance measurement and verification protocol, vol. I, Concepts and options for determining energy and water savings. EVO 10000-1.2014. Efficiency Valuation Organization, Wash- ington, D.C. www.evo-world.org. Kissock, J.K., D.E. Claridge, J.S. Haberl, and T.A. Reddy. 1992. Measuring retrofit savings for the Texas LoanSTAR program: Preliminary method- ology and results. Solar Engineering 1992-Proceedings of the 1992 ASME-JSES-KSES International Solar Engineering Conference, Maui, pp. 299-308. Kline, S., and F.A. McClintock, 1953. Describing uncertainties in single- sample experiments, Mechanical Engineering 75:2-8. Levins, W.P - and M.A. Karnitz. 1986. Cooling-energy measurements of un- occupied single-family houses with attics containing radiant barriers. ORNL Report ORNL/CON-200. Oak Ridge National Laboratory, Oak Ridge, TN (See also ORNL Report ORNL/CON-213). Liu, M., J. Houcek, A. Athar, A. Reddy, D. Claridge, and J. Haberl. 1994. Identifying and implementing improved operation and maintenance measures in Texas LoanSTAR buildings. Proceedings of the 1994 ACEEE Summer Study on Energy Efficiency in Buildings 5:153. Lopez, R., and J.S. Haberl. 1992. Data processing routines for monitored building energy data. Solar Engineering 1992-Proceedings of the 1992 ASME-JSES-KSES International Solar Engineering Conference, Maui, pp. 329-336. MacDonald, J.M., and D.M. Wasserman. 1989. Investigation of metered data analysis methods for commercial and related buildings. ORNL Report ORNL/CON-279. Oak Ridge National Laboratory, Oak Ridge, TN. ehenal.comi.gov/CommenialPoducs/ORXI-O2N427Apdf MacDonald, J.M., T.R. Sharp, and M.B. Gettings. 1989. A protocol for mon- itoring energy efficiency improvements in commercial and related build- ings. ORNL Report ORNL/CON-291. Oak Ridge National Laboratory, Oak Ridge, TN. Misuriello, H. 1987. A uniform procedure for the development and dissem- ination of monitoring protocols. ASHRAE Transactions 93(1):1619- 1629. Modera, M.P. 1989. Residential duct system leakage: Magnitude, impacts, and potential for reduction. ASHRAE Transactions 95(2):561-569. Norford, L.K, A. Rabl, and R.H. Socolow. 1985. Measurement of thermal characteristics of office buildings. ASHRAE Conference on the Thermal Performance of Building Envelopes III, Clearwater Beach, FL. O'Neal, D.L., J. Bryant, C. Boecker, and C. Bohmer. 1993. Instrumenting buildings to determine retrofit savings: Murphy 's law revisited. ESL- PA93/03-02. Energy Systems Lab, Texas A&M University. Persily, A.K., R. Grot, J.B. Fan, and Y.M. Chang. 1988. Diagnostic tech- niques for evaluating office building envelopes. ASHRAE Transactions 94(1):987-1006. Phelan, J., M. Brandemuehl, and M. Krarti. 1996. Methodology development to measure in-situ chiller, fan and pump performance. JCEM TR/96/3. Joint Center for Energy Management, University of Colorado, Boulder. ASHRAE Research Project RP-827, Final Report. Phelan, J., M. Brandemuehl, and M. Krarti. 1997a. In-situ performance test- ing of chillers for energy analysis. ASHRAE Transactions 103(1):290- 302. Phelan, J., M. Brandemuehl, and M. Krarti. 1997b. In-situ performance test- ing of fans and pumps for energy analysis. ASHRAE Transactions 103(1):318-332. Piette, M.A., S.K. Khalsa, and P. Haves. 2000. Use of an information mon- itoring and diagnostic system to improve building operations. Proceed- ings of the 2000 ACEEE Summer Study on Energy Efficiency in Buildings, Efficiency and Sustainability. Lawrence Berkeley National Laboratory Report LBNL-45567. Reddy, T.A., J.K. Kissock, and D.K. Ruch. 1998. Regression modelling in determination of retrofit savings. ASME Journal of Solar Energy Engi- neering 120:185. Robison, D.H., and L.A. Lambert. 1989. Field investigation of residential infiltration and heating duct leakage. ASHRAE Transactions 95(2):542- 550. Sellers, D., H. Friedman, L. Luskay, and T. Haasl. 2004. Commissioning and envelope leakage: Using HVAC operating strategies to meet design and construction challenges. Proceedings of the 2004 ACEEE Summer Study on Energy Efficiency in Buildings, pp. 3.287-3.299. www.eceee.org /library/conference _proceedings/ACEEE_ buildings/2004/Panel 3 /p3_24. Sharp, T. 1996. Energy benchmarking in commercial office buildings. Pro- ceedings of the 1996 ACEEE Summer Study on Energy Efficiency in Buildings, pp. 4.321-4.329. aceee.org/files/proceedings/1 996/data/papers /SS96_Panel4 _Paper33.pdf. Sharp, T.R., and J.M. MacDonald. 1990. Effective, low-cost HVAC controls upgrade in a small bank building. ASHRAE Transactions 96(1):1011- 1017. Sparks, R., J.S. Haberl, S. Bhattacharyya, M. Rayaprolu, J. Wang, and S. Vadlamani. 1992. Use of simplified system models to measure retrofit energy savings. Solar Engineering 1992-Proceedings of the 1992 ASME-JSES-KSES International Solar Engineering Conference, Maui, pp. 325-328. Subbarao, K. 1988. PSTAR A unified approach to building energy simula- tions and short-term monitoring. SERI/TR-254-3175. Solar Energy Research Institute, Golden, CO. Subbarao, K., J.D. Burch, and H. Jeon. 1986. Building as a dynamic calorim- eter: Determination of heating system efficiency. SERI/TR-254-2947. Solar Energy Research Institute, Golden, CO. Szydlowski, R.F., and R.C. Diamond. 1989. Data specification protocolfor multifamily buildings. LBL-27206. Lawrence Berkeley Laboratory, Berkeley. Ternes, M.P. 1986. Single-family building retrofit performance monitoring protocol: Data specification guideline. ORNL Report ORNL/CON-196. Oak Ridge National Laboratory, Oak Ridge, TN. Ternes, M.P., and K.E. Wilkes. 1993. Air-conditioning electricity savings and demand reductions from exterior masonry wall insulation applied to Arizona residences. ASHRAE Transactions 99(2):843-854. Woller, B.E. 1989. Data acquisition and analysis of residential HVAC alter- natives. ASHRAE Transactions 95(1):679-686. Inc. ASHRAE, 2019 user. single for Licensed | {}
de6453ef-0441-457a-af8e-95ed38b1143a | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 42.18 2019 ASHRAE Handbook-HVAC Applications (SI) BIBLIOGRAPHY ASHRAE. 2012. Performance measurement protocols for commercial buildings: Best practices guide. ASHRAE/CIBSE/USGBC. 2010. Performance measurement protocols for commercial buildings. ASHRAE, Chartered Institute of Building Ser- vices Engineers, and U.S. Green Building Council. ASTM. 2005. Guide for developing energy monitoring protocols for com- mercial or institutional buildings or facilities. ASTM Standard E1464-92 (RA2005). IPMVP. 2014. International performance measurement and verification protocol, vol. II, Concepts and practices for improved indoor environ- mental quality. www.evo-world.org. MacDonald, J.M. 2004. Commercial sector and energy use. In Encyclopedia of energy. Elsevier. Inc. ASHRAE, 2019 user single for Licensed Related Commercial Resources | {}
59a7f42e-37b5-4523-8c52-7c57188aec62 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 43 SUPERVISORY CONTROL STRATEGIES AND OPTIMIZATION ¦ TERMINOLOGY ¦ 43.1 ¦ Sequencing and Loading Multiple Chillers ¦ 43.16 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ METHODS ¦ 43.3 ¦ Simplified Static Optimization of Cooling ¦ ¦ ¦ Control Variables ¦ 43.3 ¦ Plants ¦ 43.20 ¦ ¦ Supervisory Control Strategies ¦ 43.4 ¦ Dynamic Optimization for Cooling Using Discrete ¦ ¦ ¦ Static Optimization ¦ 43.4 ¦ Storage ¦ 43.27 ¦ ¦ Dynamic Optimization ¦ 43.5 ¦ Forecasting Diurnal Cooling and Whole-Building ¦ ¦ ¦ CONTROL STRATEGIES AND OPTIMIZATION ¦ 43.8 ¦ Demand Profiles ¦ 43.36 ¦ ¦ Control Strategies for Cooling Tower Fans ¦ 43.8 ¦ Predictive HVAC Control Strategies ¦ 43.38 ¦ ¦ Chilled- Water Reset with Fixed-Speed ¦ ¦ Control Strategies for Heating Systems ¦ 43.40 ¦ ¦ Pumping ¦ 43.12 ¦ Control Strategies for Air-Handling Units ¦ 43.43 ¦ ¦ Chilled- Water Reset with Variable-Speed Pumping ¦ 43.13 ¦ Control Strategies for Building Zones ¦ 43.44 ¦ COMPUTERIZED building and energy management and con- systems provide a variety of effective ways to reduce utility costs and energy consumption associated with maintaining environ- mental conditions and thermal comfort in buildings. These systems can incorporate advanced control strategies that respond to inputs including changing weather, building conditions, occupancy levels and utility rates to minimize operating costs, energy consumption and greenhouse gas emissions while also enhancing occupant comfort. This chapter focuses on the opportunities and control strategies asso- ciated with using supervisory control strategies and optimization methods applied to cooling systems, heating systems, air handling units and zone equipment. HVAC and other building energy systems are typically controlled using a hierarchical control structure where two or more levels of control, from local through to supervisory level, are combined to form a sophisticated control system designed to achieve particular high-level functions or objectives, such as maintaining temperature within a space. With this control philosophy, controller intelligence increases from lower to higher levels within the hierarchy. The low- est control level typically exists only to provide local-loop control of a single set point through manipulation of one or more actuators. For example, the supply air temperature discharged from a cooling coil is controlled by adjusting the opening of a valve that provides chilled water to the coil, or by adjusting mixing dampers and the coil valve. The upper control level, typically called supervisory control, specifies the set points and other modes of operation that are time dependent. System performance monitoring capabilities may also be provided at this level. Ideally, the supervisory control level would determine optimal set points and operating modes that minimize operating cost and/or energy consumption, maximize comfort, and may also identify potential faults or alarms in the control system. Distributed control structures have also been applied to building energy systems, although further research is required to determine their efficacy and the benefits they may provide over more tradi- tional and well-understood control systems. Performance of large, commercial HVAC systems can be im- proved through better local-loop and supervisory control. Proper tuning of local-loop controllers can enhance comfort, reduce energy use, and increase component life. Systems that are properly commis- sioned or tuned, such as through a recommissioning process or the use of automated fault detection and diagnostics software, ensure that The preparation of this chapter is assigned to TC 7.5, Smart Building Systems. theoretical performance gains from supervisory control strategies are realized. Set points and operating modes for cooling or heating plant equipment can be adjusted by supervisory control strategies or static optimization to maximize overall operating efficiency. Dynamic op- timization strategies for ice or chilled-water storage systems can significantly reduce on-peak electrical energy and demand costs to minimize total utility costs. Similarly, thermal storage inherent in a building's structure can be dynamically controlled to minimize utility costs, for example, with the use of thermally activated building sys- tems (TABS). In general, strategies that take advantage of thermal storage work best when dynamic optimization is applied using fore- casts of future energy requirements. Significant increases in computational power and communica- tions capabilities mean that both supervisory and distributed control systems are now able to incorporate many new data streams and si- multaneously co-optimize a number of performance metrics. Rather than simply regulating temperature, the supervisory control system may manage thermal comfort while minimizing utility cost, energy consumption, and greenhouse gas emissions. Ubiquitous consumer electronics, such as smart phones, tablets, and laptops, mean that di- rect feedback of occupant preferences may be obtained rather than relying on inferred statistical models. Building thermal response and internal gain forecast models (e.g., learned by the controller) allow optimal start-up, night-purge, and economy modes as well as poten- tial participation in utility demand response programs and cost re- ductions in demand and capacity charges. Where resources are constrained by equipment sizing, mainte- nance, or imposed through energy targets or demand charges, a coordinated approach to resource allocation is required to ensure an equitable balance of comfort for all building occupants. This is in- creasingly likely to be an important control scheme design consid- eration with increased focus on energy efficiency, demand response, and the uptake of intermittent renewable generation, requiring ener- gy users to respond to resource variability. New energy pricing models will substantially reward users who have this flexibility, but may also adversely impact those without the capability to dynami- cally manage loads. 1. TERMINOLOGY Air distribution system: includes terminal units (variable-air- volume [VA V] boxes, etc.), air-handling units (AHUs), ducts, and controls. In each AHU, ventilation air is mixed with return air from the zones and fed to the cooling/heating coil. 43.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
5744c40f-0ead-4704-b9f5-e6dab27c6b90 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 43.2 Air-side economizer control: used to select between minimum and maximum ventilation air, depending on the condition of the outdoor air relative to the conditions of return air. Under certain out- door air conditions, AHU dampers may be modulated to provide a mixed air condition that can satisfy the cooling load without the need for mechanical cooling. Building thermal mass storage: storing energy in the form of sensible heat in building materials, interior equipment, and furnish- ings. Capacity: heating or cooling output at design or rating condition or, in certain contexts, at current operating condition. CAV systems: air-handling systems that have fixed-speed fans and provide no feedback control of airflow to the zones. Zone tempera- ture is controlled to a set point using a feedback controller that regulates the amount of local reheat applied to the air entering each zone. Charging: storing cooling capacity by removing heat from a cool storage device; or storing heating capacity by adding heat to a heat storage device. Chilled-/hot-water/steam loop: consists of pumps, pipes, valves, and controls. Two different types of pumping systems are consid- ered in this chapter: primary and primary/secondary. With a primary pumping system, a single piping loop is used and water that flows through the chiller or boiler also flows through the cool- ing or heating coils. When steam is used, a steam piping loop sends steam to a hot-water converter, returning hot condensate back to the boiler. Another piping loop then carries hot water through the heat- ing coils. Often, fixed-speed pumps are used with their control ded- icated to chiller or boiler control. Dedicated control means that each pump is cycled on and off with the chiller or boiler that it serves. Systems with fixed-speed pumps and two-way cooling or heating coil valves often incorporate a water bypass valve to main- tain relatively constant flow rates and reduce system pressure drop and pumping costs at low loads. The valve is typically controlled to maintain a fixed pressure difference between the main supply and return lines. This set point is termed the chilled- or hot-water loop differential pressure. Sometimes, primary systems use one or more variable-speed pumps to further reduce pumping costs at low loads. In this case, water bypass is not used and pumps are con- trolled directly to maintain a water loop differential pressure set point. Inc. ASHRAE, 2019 user. single for Licensed Chiller or boiler plant: one or more chillers or boilers, typically arranged in parallel with dedicated pumps, provide the primary source of cooling or heating for the system. Individual feedback controllers adjust the capacity of each chiller or boiler to maintain a specified supply water temperature (or steam header pressure for steam boilers). Additional control variables include the number of chillers or boilers operating and the relative loading for each. For a given total cooling or heating requirement, individual chiller or boiler loads can be controlled by using different water supply set points for constant individual flow or by adjusting individual flows for identical set points. Chiller priority: control strategy for partial storage systems that uses the chiller to directly meet as much ofthe load as possible, nor- mally by operating at full capacity most of the time. Thermal storage is used to supplement chiller operation only when the load exceeds the chiller capacity. Condenser water loop: consists of cooling towers, pumps, piping, and controls. Cooling towers reject heat to the environment through heat transfer and possibly evaporation (for wet towers) to the ambient air. Typically, large towers incorporate multiple cells sharing a common sump, with individual fans having two or more speed settings. Often, a feedback controller adjusts tower fan speeds to maintain a temperature set point for water leaving the cooling tower, termed the condenser water supply temperature. Typically, condenser water pumps are dedicated to individual 2019 ASHRAE Handbook-HVAC Applications (SI) chillers (i.e., each pump is cycled on and off with the chiller it serves). COP: heating or cooling output divided by electrical power input; may include chilled-water (CW) pump and tower fan as well as compressor power (see also System COP). Demand limiting: a partial storage operating strategy that limits the capacity of the cooling system during the on-peak period. The cooling system capacity may be limited based on its cooling capacity, its electric demand, or the facility demand. Discharge capacity: maximum rate at which cooling can be supplied from a cool storage device. Discharging: using stored cooling capacity by adding thermal energy to a cool storage device or removing thermal energy from a heat storage device. Ice storage: types of ice storage systems include the following. An ice harvester is a machine that cyclically forms a layer ofice on a smooth cooling surface, utilizing the refrigerant inside the heat exchanger, then delivers it to a storage container by heating the sur- face of the cooling plate, normally by reversing the refrigeration process and delivering hot gases inside the heat exchanger. In ice- on-coil-external melt, tubes or pipes (coil) are immersed in water and ice is formed on the outside of the tubes or pipes by circulating colder secondary medium or refrigerant inside the tubing or pipes, and is melted externally by circulation the unfrozen water outside the tubes or pipes to the load. Ice-on-coil-internal melt is similar, except the ice is melted internally by circulating the same secondary coolant or refrigerant to the load. Load leveling: a partial storage sizing strategy that minimizes storage equipment size and storage capacity. The system operates with the refrigeration equipment running at full capacity for 24 h to meet the normal cooling minimum load profile and, when the load is less than the chiller output, the excess cooling is stored. When the load exceeds the chiller capacity, the additional cooling requirement is obtained from the thermal storage system. Load profile: compilation of instantaneous thermal loads over a period of time, normally 24 hours. Nominal chiller capacity: (1) chiller capacity at standard ARI (Standard 550/590) rating conditions, or (2) chiller capacity at a given operating condition selected for the purpose of quick chiller sizing selections. Partial storage: a cool storage sizing strategy in which only a portion of the on-peak cooling load is met from thermal storage, with the remainder of the load being met by operating the chilling equipment. Precooling: a thermal energy storage (TES) strategy that allows a properly designed chiller system to operate more efficiently with lower condensing temperatures (low night ambient temperature) higher evaporating temperatures (15 to 20°C chilled water) and at or near its most efficient part-load point. Precooling can be applied to the conditioned space, or directly to mass by passing chilled air or water through building elements such as concrete floor decks. Primary/secondary chilled- or hot-water systems: systems designed specifically for variable-speed pumping. In the primary loop, fixed-speed pumps provide a relatively constant flow of water to the chillers or boilers. This design ensures good chiller or boiler performance and, for chilled-water systems, reduces the risk of freezing on evaporator tubes. The secondary loop incorpo- rates one or more variable-speed pumps that are controlled to maintain a water loop differential pressure set point. The primary and secondary loops may be separated by a heat exchanger. How- ever, it is more common to use direct coupling with a common pipe. Storage capacity: the maximum amount of cooling (or heating) that can be achieved by the stored medium in the thermal storage device. Nominal storage capacity is a theoretical capacity of the thermal storage device. In many cases, this may be greater than | {}
6c810ba0-38c6-45b3-bcee-b5be8e57dd59 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Supervisory Control Strategies and Optimization 43.3 usable storage capacity. This measure should not be used to com- pare usable capacities of alternative storage systems. Storage cycle: a period (usually one day) in which a substantial charge and discharge of a thermal storage device has occurred, beginning and ending at the same state or same time of day. Storage efficiency: the ratio of useful heating or cooling ex- tracted during the discharge cycle to that imparted to storage during the charging cycle. One may also define an exergic efficiency that accounts for mixing and thermal destratification as well as conduc- tion losses. Storage inventory: the amount of usable heating or cooling capacity remaining in a thermal storage device. Storage priority: a control strategy that uses stored cooling to meet as much of the load as possible. Chillers are operated only if the load exceeds the storage system s available cooling capacity. Supply air temperature: temperature of air leaving an AHU or package unit. The temperature supplied to the zones may differ from the supply air temperature because of heat transfer in the ductwork and local reheat. A local-loop controller adjusts the flow of water through the air handler cooling/heating coil using a two- or three-way valve to maintain a specified set-point temperature for the air downstream of the cooling/heating coil. The value of the supply air temperature set-point will affect energy consumption and can be adjusted by the supervisory control system. System capacity: maximum amount of cooling that can be sup- plied by the entire cooling system, which may include the chillers and the thermal storage. Usable storage capacity is the total amount of beneficial cooling able to be discharged from a thermal storage device. (This may be less than the nominal storage capacity, because the distribution header piping may not allow discharging the entire cooling capacity of the thermal storage device.) System COP: ratio of cooling rate (kW to system input thermal) electric) required to operate all distribution fans and power (kW pumps as well as compressors and condenser or cooling tower fans and pumps. Temperature set point: zone temperature set points are typi- cally fixed values within the comfort zone during the occupied time, and zone humidity is allowed to "float" within a range dictated by the system design and choice of the supply air set-point tempera- ture. Night setup is often used in summer to raise the zone tempera- ture set points during unoccupied times and reduce the cooling requirements. Similarly, night setback is often used in winter to lower the zone temperature set points during unoccupied times and reduce the heating requirements. Setup and setbacks can also be used during occupied periods to temporarily curtail energy con- sumption. Thermal energy storage (TES): thermal energy storage sys- tems are of three general types. Discrete TES uses a tank of water (usually stratified), packed bed ofrock or phase-change material, or a tank of ice and water with immersed coil. Intrinsic (or passive) TES uses the thermal capacitance of the building fabric, such as concrete columns, beams and decks, or wall board, possibly aug- mented by phase-change material. Thermally activated building systems (TABS): floors or other elements are cooled directly with embedded pipes or ducts, giving storage capacity and efficiency substantially greater than can achieved by passive TES. Total cooling load: integrated thermal load that must be met by the cooling plant over a given period of time. Variable-air-volume (V A V) systems: systems that use a feed- back controller that regulates the airflow to each zone to maintain zone temperature set point. The zone airflows are regulated using dampers located in VAV boxes in each zone. VA v systems also incorporate feedback control of the primary airflow through various means of fan capacity control. Typically, inputs to a fan outlet damper, inlet vanes, blade pitch, or variable speed motor are adjusted to maintain a duct static pressure set point in the supply duct, as described in Chapter 48. 2. METHODS 2.1 CONTROL VARIABLES Systems and Controls Figures 1 and 2 show schematics of typical centralized cooling and heating systems for which control strategies are presented in this chapter. For cooling systems, the strategies in this chapter gen- erally assume that the equipment is electrically driven and that heat is rejected to the environment by cooling towers. For heating systems, boilers may be fired by a variety of fuels or powered by electricity, but are typically fired from either natural gas or #2 or #6 fuel oil. However, some strategies apply to any type of system (e.g., return from night setup or setback). For describing different systems and controls, it is useful to divide the system into the subsystems depicted in Figures 1 and 2: air distribution system, chilled-/hot- water loop, chiller/boiler plant, condenser water loop. A variant of the chilled-water system shown in Figure 1 uses chilled water directly for sensible cooling by radiant panels, chilled beams, or radiant floors. Similar strategies can be applied to variable-speed controls for air-cooled chiller condenser fans. VAV cooling system controls (Figure 1) respond to changes in building cooling requirements. As the cooling load increases, the zone temperature rises as energy gains to the zone air increase. The zone controller responds to higher temperatures by increasing local flow of cool air by opening the damper in the VAV unit. Opening the damper reduces static pressure in the primary supply duct, which ![image](/image/placeholder) CONDENSER WATER LOOP CHILLED-WATER LOOP SUPPLY AIR FANS COILS TOWER(S) CHILLER(S) ZONE(S) COOLING AIR ::: MAKEUP CONDENSER PUMP(S) CHILLED-WATER PUMP(S) VENTILATION EXHAUST CHILLER AIR AIR PLANT AIR DISTRIBUTION SYSTEM Fig. 1 Schematic of Chilled- w ater Cooling System ![image](/image/placeholder) HOT-WATER LOOP SUPPLY AIR FAN(S) HEATING BOILER(S) ZONE(S) COILS HOT-WATER PUMP VENTILATION AIR EXHAUST AIR BOILER PLANT AIR DISTRIBUTION SYSTEM Fig. 2 Schematic of Hot-Water Heating System Inc. ASHRAE, 2019 user. single for Licensed | {}
80c65936-b5c6-4a84-b96d-01f62d6aba92 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 43.4 causes the fan controller to create additional airflow. With greater airflow, the supply air temperature of the cooling coils increases, which causes the air handler feedback controller to increase the water flow by further opening the cooling coil valves. This increases the chilled-water flow and/or the chilled water return temperature (i.e., increases the cooling load). Control of a radiant cooling system (a variant of Figure 1 ) re- sponds directly to zone load by increasing the chilled-water flow rate. The chilled-water temperature may be controlled by the zone with greatest demand or by an open-loop control. Control of a hot-water heating system (Figure 2) is similar. As the heating load increases, the zone temperature falls as energy gains to the zone air decrease. The zone controller responds to lower temperatures by opening a control valve and increasing the flow of hot water through the local reheat coil. The supply airflow rate is usually maintained at its minimum value when a VA V system is in heating mode. Increasing water flow through the reheat coils reduc- es the temperature of the water returned to the boiler. With lower return water temperature, the supply water temperature drops, which causes the feedback controller to increase the boiler firing rate to maintain the desired supply water temperature. For both heating and cooling modes, an increase in the building load results in an increase in water flow rate, which is ultimately propagated through the central heating/cooling system. For fixed- speed chilled- or hot-water pumps, the differential pressure controller closes the chilled- or hot-water bypass valve and keeps the overall flow relatively constant. For variable-speed pumping, the differential pressure controller increases pump speed. In a chilled- water system, the return water temperature and/or flow rate to the chillers increases, leading to an increase in the chilled-water supply temperature. The chiller controller responds by increasing the chiller cooling capacity to maintain the chilled-water supply set point (and match the cooling coil loads). The increased energy removed by the chiller increases the heat rejected to the condenser water loop, which increases the temperature of water leaving the condenser. The increased water temperature entering the cooling tower increases the water temperature leaving the tower. The tower controller responds to the higher condenser water supply tempera- ture and increases the tower airflow. At some load, the current set of operating chillers is not sufficient to meet the load (i.e., maintain the chilled-water supply set points) and an additional chiller is brought online. For a hot-water system, the return water tempera- ture and/or flow rate to the boilers decreases, leading to a decrease in the hot-water supply temperature. The boiler controller responds by increasing the boiler heating capacity to maintain the hot-water supply set point (and match the heating coil loads). For all-electric cooling without thermal storage, minimizing power at each point in time is equivalent to minimizing energy costs. Therefore, supervisory control variables should be chosen to maxi- mize the coefficient of performance (COP) of the system at all times while meeting the building load requirements. The system COP is defined as the ratio of total cooling load to total system power con- sumption. In addition to the control variables, the COP depends primarily on the cooling load and the ambient wet- and dry-bulb tem- peratures. Often, the cooling load is expressed in a dimensionless form as a part-load ratio (PLR), which is the cooling load under a given condition divided by the design cooling capacity. For cooling or heating systems with thermal storage, perfor- mance depends on the time history of charging and discharging. In this case, controls should minimize operating costs integrated over the billing period or storage cycle. In addition, safety features that minimize the risk of prematurely depleting storage capacity may be important. 2019 ASHRAE Handbook HVAC Applications (SI) 2.2 SUPERVISORY CONTROL STRA TEGIES For any of the scenarios listed previously, several local-loop controllers respond to load change to maintain specified set points. A supervisory controller establishes modes of operation and chooses (or resets) values of set points. At any given time, cooling or heating needs can be met with various combinations of modes of operation and set points. This chapter discusses several methods for determining supervisory control variables that provide good overall performance, including resetting set points such as chilled- or hot-water supply temperature, supply air temperatures, differen- tial pressure on water loops, and supply air static pressure. Another form of supervisory control includes sequencing equipment such as chillers, boilers, pumps, and fans to achieve energy-efficient operation. Optimization may be applied to cost, energy, or comfort constraints. Sampling Intervals for Reset Controls Proper sampling intervals are required when resetting the set point for proportional-integral (PI) feedback control loops to pre- vent oscillation of the process variable in those loops. In general, the sampling time interval between reset commands should be greater than the settling time for the loop. For example, resetting both the chilled-water supply temperature set point and cooling coil dis- charge air temperature set point is necessary for optimal control. In this case, resetting the set points for chilled-water supply tempera- ture and cooling coil discharge air temperature should not occur simultaneously, but at staggered intervals; the interval of reset for either loop should be greater than the settling time for the coil (the time for the discharge air temperature of the coil to reach a new steady-state temperature). For cascaded loops, the sampling interval between reset com- mands should be greater than the settling time for the faster inner loop. An example of a cascaded loop is a VA V box controller with its flow set point determined from the space temperature of its associ- ated zone, and the box damper controlled to maintain the flow set point. For example, in resetting static pressure set point on a variable- speed air-handler fan based on VAV box damper position, the interval between resets should be greater than the settling time of the flow control loop in a pressure-independent VAV box. (Settling time in this example is the time for the flow rate to reach a new steady- state value.) 2.3 STATIC OPTIMIZA TION Optimal supervisory control of building systems involves deter- mining the control that minimizes the total operating cost. Static optimization addresses the problem of optimizing the operation of a system at a given instant in time by operating each component of the system at the conditions which achieve an optimal result, such as min- imal cost. Static optimization techniques applied to a general simula- tion can be used to determine optimal supervisory control variables. The simulation may be based on physical (Hiller and Glicksman 1977; Stoecker 1980) or empirical models. However, for control vari- able optimization, empirical and semiempirical models (where model parameters are estimated from measurements) are often used. This section presents methods for static optimization useful in determining optimal control for various applications. General Static Optimization Problem Figure 3 depicts the general nature of the static optimization problem for a system of interconnected components. Each compo- nent in a system is represented as a separate set of mathematical relationships organized into a computer model. Its output variables and operating cost are functions of parameters, input, output, and uncontrolled and controlled variables. The structure of the system of Inc. ASHRAE, 2019 user. single for Licensed | {}
124cd544-3345-4040-835f-58c206051e6e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Supervisory Control Strategies and Optimization 43.5 ![image](/image/placeholder) fn M n' un yn Xn COMPONENT n x1 V1 f⌀ M1, u1 COMPONENT n 1 J 2 y1 COMPONENT 2 X2 y2 f2, M2, u2 Fig. 3 Schematic of Modular Optimization Problem equations to be solved is dictated by the manner in which the com- ponents are interconnected. A typical optimization problem is formally stated as the minimi- zation of the sum of the operating costs of each component Ji with respect to all discrete and continuous controls, or Minimize n J(f, M, u) = Ji(xpyp fp Mi, u) i=1 with respect to M and u, subject to equality constraints of the form g1 f1, M1, u1, x1, y1 g2 f2, M2, u2, X2, y2 g(f, M, u) = = 0 · gn fm Mn un, Xm y n and inequality constraints of the form (1) h1 f1, M1, u1, X1, y1 h2 f2, M2, u2, X2, y2 h(f, M, u) = 0 . hn f M m ur y n Xn n' (2) (3) where, for any component i, Xi = vector of input stream variables yi = vector of output stream variables fi = vector of uncontrolled variables Mi = vector of discrete control variables ui = vector of continuous control variables Ji = operating cost gi = vector of equality constraints hi = vector of inequality constraints Typical input and output stream variables for thermal systems are temperature and mass flow rate. Uncontrolled variables are quantities that may not be controlled, but that affect component per- formance and/or costs, such as ambient dry- and wet-bulb tempera- ture. Both equality and inequality constraints arise in the optimization ofHV AC systems. One example of an equality constraint that arises when two or more chillers are in operation is that the sum of their capacities must equal the total load. The simplest type of inequality constraint is a bound on a control variable. For example, lower and upper limits are necessary for the chilled-water set temperature, to avoid freezing in the evaporator and to provide adequate dehumid- ification for the zones. Any equality constraint may be rewritten in the form of Equation (2) such that when it is satisfied, the constraint equation is equal to zero. Similarly, inequality constraints may be expressed as Equation (3), so that the constraint is satisfied when the result is greater than or equal to zero. Braun (1988) and Braun et al. (1989a) presented a component- based nonlinear optimization and simulation tool and used it to investigate optimal performance. Each component is represented as a separate subroutine with its own parameters, controls, inputs, and outputs. The optimization problem is solved efficiently by using second-order representations of costs. Applying component-based optimization led to many guidelines for control and a simplified system-based optimization methodology. In particular, the results showed that optimal set points could be correlated as linear func- tions of load and ambient wet-bulb temperature. Zakula et al. (2011, 2012) show that, for chillers with high part- load efficiency over a wide range of compressor speed, optimal condenser fan speed and chilled-water specific flow rate are highly nonlinear functions of cooling load, and without optimal control, transport power can be much greater than compressor power at part- load and low-lift conditions. Gayeski et al. (2012) demonstrated an empirical method for deriving near-optimal control laws from mea- sured performance. Cumali (1988, 1994) presented a method for real-time global optimization ofHVAC systems, including the central plant and asso- ciated piping and duct networks. The method uses a building load model for the zones, based on a coupled weighting-factor method similar to that used in DOE-2 (Winkelman et al. 1993). Variable time steps are used to predict loads over a 5 to 15 min period. The models are based on thermodynamic, heat transfer, and fluid mechanics fun- damentals and are calibrated to match actual performance, using data obtained from the building and plant. Pipe and duct networks are rep- resented as incidence and circuit matrices, and both dynamic and static losses are included. Fluid energy transfers are coupled with zone loads using custom weighting factors calibrated for each zone. The resulting equations are grouped to represent feasible equipment allocations for each range of building loads, and solved using a non- linear solver. The objective function is the cost of delivering or removing energy to meet the loads, and is constrained by the comfort criteria for each zone. The objective function is minimized using the reduced gradient method, subject to constraints on comfort and equipment operation. Optimization starts with the feasible points as determined by a nonlinear equation solver for each combination of equipment allocation. The values of set points that minimize the objective function are determined; the allocation with the least cost is the desired operation mode. Results obtained from this approach have been applied to high-rise office buildings in San Francisco with central plants, VAV, dual-duct, and induction systems. Electrical demand reductions of 8 to 12% and energy savings of 18 to 23% were achieved. 2.4 DYNAMIC OPTIMIZA TION Whereas static optimization addresses operation of a building system at a given point in time, accounting for the operating char- acteristics of each component, dynamic optimization addresses control of buildings systems over time. As such, dynamic optimiza- tion must account for the possibility that future conditions (e.g., weather, utility prices) may affect present optimal control decisions, and that present control decisions will affect operating conditions and optimal control decisions in the future. Established methods of Inc. ASHRAE, 2019 user. single for Licensed | {}
76aeecc7-23f4-4f6a-bee4-59e714ffcf5c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 43.6 optimal control (e.g., model-predictive control, dynamic program- ming) may be used to implement dynamic optimization of a build- ing system. Daily, monthly, and annual cooling costs are particularly sensitive to time of use. Specific methods of dynamic optimization presented here are relevant to the applications in this chapter, with a focus on cooling systems largely because of the highly weather- and load-dependent nature of optimal cooling sys- tem controls. Cooling Systems with Discrete Storage Optimal supervisory control for cooling systems with discrete storage, such as water- or ice-storage, is a function of several factors including utility rate structure, load profile, chiller characteristics, storage characteristics, and weather. For a utility rate structure that includes both time-of-use energy and demand charges, the optimal strategy can depend on variables that extend over a monthly time scale. The overall problem of minimizing the utility cost over a billing period (e.g., a month) can be mathematically described as follows: Minimize N J = EkP k Max1 k N(DkPk) + k=1 with respect to the control variables (u1,u2, · · · ,UN) and subject to the following constraints for each stage k: (4) umin,k uk umax,k Xk = f(xk-1, uk k) Xmin Xk Xmax (5) XN= x⌀ (8) where J is the utility cost associated with the billing period (e.g., a month); is the stage time interval (typically equal to the time window over which demand charges are levied, e.g., 0.25 h); Nis the number of time stages in a billing period, and for each stage k, P is the average building electrical power (kW); E is the energy cost rate or cost per unit of electrical energy ($/kWh); D is the demand charge rate or cost per peak power rate over the billing period ($/kW); u is the control variable that regulates the rate of energy removal from or is the maximum value for u; addition to storage over the stage; Umax is the minimum value for u; x is the state of storage at the end umin of the stage; Xmax maximum admissible state of storage; Xmin is the is the minimum admissible state of storage; andfis a state equation that relates the state of storage at stage k to the previous state and current control. (6) (7) The first and second terms in Equation (4) are the total cost of energy use and building demand for the billing period. Both energy and demand cost rates can vary with time, but typically have two values associated with on- and off-peak periods. An even more com- plex cost optimization results ifthe utility includes ratchet clauses in which the demand charge is the maximum of the monthly peak demand cost and some fraction of the previous monthly peak demand cost during the cooling season. With real-time pricing, the demand charge (the second term in Equation [4] might not exist and the hourly energy rates would vary over time according to gen- eration and transmission costs. For ice or chilled-water storage systems, the control variable could be the rate at which energy is added or removed from storage. In this case, the constraint given by Equation (5) arises from capac- ity limits of the chiller and storage heat exchanger and can also depend on the state of storage. For use of building thermal mass, the control variable could be the zone temperature(s) and the constraint of Equation (5) would be associated with comfort considerations or 2019 ASHRAE Handbook-HVAC Applications (SI) capacity constraints. Different comfort limits would probably apply for occupied and unoccupied periods. In this general formulation the state equation, Equation (6), is treated as an equality constraint. The state of storage at any stage k is a function of the previous state Xk-1, the control uk and other time- dependent factors (e.g., ambient temperature). For lumped storage systems (e.g., ice), the state of storage can be characterized with a single-state variable. However, for a distributed storage (e.g., a building structure), multiple-state equations may be necessary to properly characterize the dynamics. The state of storage may be constrained to always lie between states corresponding to full dis- charge and full charge [Equation (7)]. The constraint of Equation (8) forces a steady-periodic solution to the problem. This constraint becomes less important as the length of analysis (control horizon) increases. To determine a control strategy for charging and discharging stor- age that minimizes utility cost, Equation (4) must be minimized over the entire billing period because of the influence of the demand charge. Alternatively, the optimization problem can be posed as a series of shorter-term (e.g., daily or weekly) optimizations with a con- straint on the peak demand charge according to the following: Minimize N J = EkP k + TDC Inc. ASHRAE, 2019 user. single for Licensed (9) k=1 with respect to the control variables (u1, U2, · · · , uN) and a billing period target demand cost (TDC) and subject to the constraints of Equations (5) to (8) and the following additional constraint: which arises from the form of the cost function chosen for Equation (9). At each stage, the demand cost must be less than or equal to the peak demand cost for the billing period. The peak or target demand cost TDC is an optimization variable that affects both energy and demand costs. Using Equation (9) rather than Equation (4) simpli- fies the numerical solution. DkPk TDC (10) Two types of solutions to the optimization problem are of inter- est: (1) minimum billing-period operating cost and (2) minimum energy cost for a specified TDC and short-term horizon (e.g., a day). The first problem is useful for benchmarking the best control and minimum cost through simulation, but is not useful for online con- trol because forecasts beyond a day are unreliable. Mathematical models of the building, equipment, and storage can be used to esti- mate load requirements, power, and state of storage. The second solution can be used for online control in conjunction with a system model and a forecaster. For minimum operating costs (first optimization problem), N + 1 variables must be determined to minimize the cost function of Equation (9) over the length of the billing period. For a given value ofTDC, minimization of Equation (9) with respect to the N charging (and discharging) control variables may be accomplished using dynamic programming (Bellman 1957) or some other direct search method. The primary advantages of dynamic programming are that it handles constraints on both state and control variables in a straight- forward manner and also guarantees a global minimum. However, the computation becomes excessive ifmore than one state variable is needed to characterize storage. The N-variable optimization problem is resolved at each iteration of an outer loop optimization for TDC. Brent's (1973) algorithm is a robust method for solving the one- dimensional optimization for the demand target because it does not require derivative information. This is important because TDC appears as an inequality constraint in the dynamic programming solution and may not always be triggered. For shorter-term optimizations (second optimization problem), dynamic programming can still be used to minimize Equation (9) | {}
fd2bb388-a364-4e95-9f08-c9c21e04c166 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Supervisory Control Strategies and Optimization 43.7 with respect to the N charging (and discharging) control variables for a specified TDC. However, an optimal value for TDC cannot be determined when demand charges are imposed. For ice storage, Drees and Braun (1996) found that a simple and near-optimal approach is to set TDC to zero at the beginning of each billing period. Therefore, the optimizer minimizes the demand cost for the first opti- mization period (e.g., a day) and then uses this demand as the target for the billing period unless it is exceeded. For online optimization, the optimization problem can be resolved at regular intervals (e.g., 1 h) during each day's operation. Ice Storage Control Optimization. Several researchers have studied optimal supervisory control of ice storage systems. Braun (1992) solved daily optimization problems for two limiting cases: minimum energy (i.e., no demand charge) and minimum demand (no energy charge). Results of the optimizations for different days and utility rates were compared with simple chiller-priority and load-limiting control strategies (see the section on Supervisory Control Strategies). For the ice-on-pipe system considered, load- limiting control was found to be near optimal for both energy and demand costs with on-peak to off-peak energy cost ratios greater than about 1.4. Drees and Braun (1996) solved both daily and monthly optimization problems for a range of systems with internal-melt area-constrained ice storage tanks. The optimization results were used to develop rules that became part of a rule-based, near-optimal controller presented in the section on Supervisory Control Strate- gies. For a range of partial-storage systems, load profiles, and utility rate structures, the monthly electrical costs for the rule-based con- trol strategy were, on average, within about 3% of the optimal costs. Henze et al. (1997a) developed a simulation environment that determines the optimal control strategy to minimize operating cost, including energy and demand charges, over the billing period. A modular cooling plant model was used that includes three compres- sor types (screw, reciprocating, and centrifugal), three ice storage media (internal melt, external melt, and ice harvester), a water- cooled condenser, central air handler, and all required fans and pumps. The simulation tool was used to compare the performance of chiller-priority, constant-proportion, storage-priority, and optimal control. Henze et al. (1997b) presented a predictive optimal controller for use with real-time pricing (RTP) structures. For the RTP structure considered, the demand term of Equation (9) disappears and the optimization problem only involves a 24 h period. The controller calculates the optimal control trajectory at each time step (e.g., 30 min), executes the first step of that trajectory, and then repeats that process at the next time step. The controller requires a model of the plant and storage, along with a forecast of the future cooling loads. To apply the optimization approach described in the previous section, models for storage, system power consumption, and building loads are needed. For online optimization, simple empiri- cal models that can be trained using system measurements are appropriate. However, physically based models would be best for simulation studies. The optimization studies that have been performed for ice storage assumed that the state of storage could be represented with a single- state variable. Assuming negligible heat gains from the environment, the relative state of charge (i.e., fraction of the maximum available storage capacity) for any stage k is uk t Xk = Xk-1 + C s where Cs is the maximum change in internal energy of the storage tank that can occur during a discharge cycle and uk is the storage charging rate. The state of charge defined in this manner must be between zero and one. ( 1 1) The charging rate for storage depends on the storage heat exchanger area, secondary fluid flow rate and inlet temperature, and the thickness ofice. At any stage, the maximum charging rate can be expressed as = mf,maxCf(ts - thi) uk, max c,k,max (12) where is the heat transfer effectiveness for charging at the c,k,max current state of storage if the secondary fluid flow rate were at its maximum value of Mf,max⌀ cfis the secondary fluid specific heat, tfi is the temperature of secondary fluid inlet to the tank, and ts is the temperature at which the storage medium melts or freezes (e.g., 0°C). The minimum charging rate is actually the negative of the max- imum discharging rate and can be given by = mf.maxcf(ts-tf,i) uk,min d,k,max (13) where is the heat transfer effectiveness for discharging at the d,k,max current state of storage if the secondary fluid flow rate were at its maximum value of mf.max. In general, the heat transfer effectiveness for charging and dis- charging at the design flow can be correlated as a function of state of charge using manufacturers' data (e.g., Drees and Braun 1995). A model for the total building power is also needed. At any time P = P + P + P noncooling plant dist (14) where P is the building electrical use that is not associated noncooling is the power needed to with the cooling system (e.g., lights), Pplant operate the cooling plant, and P dist is the power associated with the distribution of secondary fluid and air through the cooling coils. The models used by Henze et al. (1997a) predict cooling plant and dis- tribution system power with a component-based simulation that is appropriate for simulation studies. Alternatively, for online optimi- zation, plant and distribution system power can be represented with empirical correlations. Drees (1994) used curve-fits of plant power consumption in terms of cooling load and ambient wet-bulb tem- perature. At any time, the cooling requirement for the chiller is the difference between the building load requirement and the storage discharge rate. The chiller supply temperature is then determined from an energy balance on the chiller and used to evaluate the limits on the storage charging and discharging rates in Equations (12) and (13). The chiller cooling rate must be greater than a minimum value for safe operation and less than the chiller capacity. Drees (1994) correlated the maximum cooling capacity as a function of the ambi- ent wet-bulb temperature and the chiller supply temperature. For simulation studies, a building model may be used to estimate building cooling loads. For online optimization, a forecaster would provide estimates of future building cooling loads. Cooling Systems with Thermally Activated Building Systems Optimal supervisory control for precooling building mass usu- ally requires transient thermal response models of the conditioned zones, because the state of charge cannot be measured and the fully charged and discharged states are not well defined. For passive TES, Equation (4) is retained as the objective function and Equation (14) also applies, with Pplant a function of capacity uk and conditions that affect system COP. One of these conditions is chilled-water return temperature, which is in turn a function of current and past capaci- ties and zone temperatures and past return temperatures: essentially, a conduction transfer function. The constraint on plant capacity (Equation [5]) is retained as well. Inc. ASHRAE, 2019 user. single for Licensed | {}
8749a954-0498-4fac-804c-9b3304ddad26 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 43.8 Equation ⑥ is replaced by a transient thermal response model that expresses room temperature Xk in terms of current and past weather, direct heating and cooling (including direct solar and and in terms of past internal gains), and control actions uk ④ · - uk-n, Seem et al. s (1989a) comprehen- room temperatures Xk-1 · · · Xk-n. sive room transfer function (CRTF) is such a model. Methods and results of training a CRTF have been reported by Armstrong et al. (2000, 2006a, 2006b) and Gayeski et al. (2012). Equation (7) serves to constrain room temperature during occupied hours, and Equation (8) is not normally needed if time step 0 is assigned to an occupied hour. Note that, for TABS, the supervisory control cannot generally be expressed in terms of zone temperature set points. Equation (4) may involve only the chiller power used to meet sensible load, P = u/COP(u,t). It is possible (e.g., with liquid desic- cant storage or ice storage) to shift latent load. However, with enthalpy recovery (see Chapter 26 of the 2016 ASHRAE Hand- book-HVAC Systems and Equipment), latent loads are a small frac- tion of total load and not usually considered to be attractive for peak shifting; in this case, DOAS system power may be treated as part of the non-cooling power term in Equation (14). Setting E = 1 and D = 0 in Equation (4) will produce the highest energy savings. 3. CONTROL STRATEGIES AND OPTIMIZATION 3.1 CONTROL STRATEGIES FOR COOLING TOWER FANS Figure 4 shows a schematic of the condenser loop for a typical chilled-water unit consisting of centrifugal chillers, cooling towers, and condenser water pumps. Typically, the condenser water pump control is directed by the chiller control to provide relatively con- stant flow for individual chillers. However, the cooling tower cells may be independently controlled to maximize system efficiency. Typically, cooling tower fans are controlled using a feedback controller that attempts to maintain a temperature set point for the water supplied to the chiller condensers. Often, the condenser water supply temperature set point is held constant. However, a better strategy is to maintain a constant temperature difference between the condenser water supply and the ambient wet bulb (constant ap- proach). Additional savings are possible through optimal control. With a single feedback controller, the controller output signal must be converted to a specific fan sequence that depends on the ![image](/image/placeholder) COOLING TOWER CELLS CONDENSER WATER PUMPS CONDENSER CONDENSER CHILLER CONDENSERS RETURN WATER SUPPLY WATER Fig. 4 Condenser Water Loop Schematic 2019 ASHRAE Handbook-HVAC Applications (SI) number of operating cells and the individual fan speeds. Typically, with the discrete control associated with one- or two-speed tower fans, the set point cannot be realized, resulting in the potential for oscillating tower fan control. Fan cycling can be reduced by using dead bands, "sluggish" control parameters, and/or lower limits for on and off periods. Braun and Diderrich (1990) demonstrated that feedback control for cooling tower fans could be eliminated by using an open-loop supervisory control strategy. This strategy requires only measuring chiller loading to specify the control and is inherently stable. The tower fan control is separated into two parts: tower sequencing and optimal airflow. For a given total tower airflow, general rules for op- timal tower sequencing are used to specify the number of operating cells and fan speeds that give the minimum power consumption for both the chillers and tower fans. The optimal tower airflow is esti- mated with an open-loop control equation that uses design information for the cooling tower and chiller. The computational procedure is presented in this section, and the control strategy is summarized in a set of steps and sample calculations. The proce- dures can be adapted to applications where fan and cell performance characteristics vary among cells. Near-Optimal Tower Fan Sequencing For variable-speed fans, minimum power consumption results when all cooling tower cells are operated under all conditions. Tower airflow varies almost linearly with fan speed, whereas the fan power consumption varies approximately with the cube of the speed. Thus, for the same total airflow, operating more cells in parallel allows for lower individual fan speeds and lower overall fan power consump- tion. An additional benefit associated with full-cell operation is lower water pressure drops across the spray nozzles, which results in lower pumping power requirements. However, at very low pressure drops, inadequate spray distribution may adversely affect the thermal performance of the cooling tower. Most cooling towers use multiple-speed rather than continuously adjustable variable-speed fans. In this case, itis not optimal to oper- ate all tower cells under all conditions. The optimal number of cells operating and individual fan speeds depend on the system charac- teristics and ambient conditions. However, simple relationships exist for the best sequencing of cooling tower fans as capacity is added or removed. When additional tower capacity is required, Braun et al. (1989b) showed that, in almost all practical cases, the speed of the tower fan operating at the lowest speed (including fans that are off) should be increased first. The rules for bringing cell fans online are as follows: · All variable-speed fans: Operate all cells with fans at equal speeds. · Multiple-speed fans: Activate lowest-speed fans first when adding tower capacity. Reverse for removing capacity. · Variable/multiple-speed fans: Operate all cells with variable- speed fans at equal speeds. Activate lowest-speed fans first when adding tower capacity with multiple-speed fans. Add multiple- speed fan capacity when variable-speed fan speeds match the fan speed associated with the next multiple-speed fan increment to be added. Similarly, for removing tower capacity, the highest fan speeds are the first to be reduced and sequences defined here are reversed. These guidelines were derived by evaluating incremental power changes for fan sequencing. For two-speed fans, incremental power increase associated with adding a low-speed fan is less than that for increasing one to high speed if the low speed is less than 79% of the high fan speed. In addition, if the low speed is greater than 50% of the high speed, then the incremental increase in airflow is greater (and therefore thermal performance is better) for adding the low- speed fan. Most commonly, the low speed of a two-speed cooling Inc. ASHRAE, 2019 user. single for Licensed | {}
a9e2f9e2-9e97-41b4-97ee-98ea8a509161 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Supervisory Control Strategies and Optimization 43.9 kW POWER, Chart Type: line 0.2 0.4 0.6 0.8 1.0 item_01 2100kW 1800kW 1700kW 1500kW 1600kW Fig.5 Trade-Offs Between Chiller Power and Fan Power with Tower Airflow tower fan is between one-half and three-quarters of full speed. In this case, tower cells should be brought online at low speed before any operating cells are set to high speed. Similarly, the fan speeds should be reduced to low speed before any cells are brought off- line. For three-speed fans, low speed is typically greater than or equal to one-third of full speed, and the difference between the high and intermediate speeds is equal to the difference between the interme- diate and low speeds. In this situation, the best sequencing strategy is to activate the lowest fan speeds first when adding tower capacity and deactivate the highest fan speeds first when removing capacity. Typ- ical three-speed combinations that satisfy these criteria are (1) one- third, two-thirds, and full speed or (2) one-half, three-quarters, and full speed. Another issue related to control of multiple cooling tower cells with multiple-speed fans concerns the distribution of water flow to individual cells. Typically, water flow is divided equally among operating cells. Even though the overall thermal performance of the cooling tower is best when the flow is divided such that the ratio of water-to-airflow rates is identical for all cooling tower cells, equal water flow distribution results in near-optimal performance. Near-Optimal Tower Airflow Figure 5 shows the trade-off between the chiller and cooling tower fan power associated with increasing tower airflow for variable-speed fans given a chilled-water load. As airflow increases, fan power increases with a cubic relationship. Atthe same time, there is a reduction in the temperature of the water supplied to the con- denser of the chiller, resulting in lower chiller power consumption. The minimum total power occurs at a point where the rate ofincrease in fan power with airflow is equal to the rate of decrease in chiller power. Near the optimum, the total power consumption is not very sensitive to the control. This "flat" optimum indicates extreme accu- racy is not needed to determine the optimum control. In general, it is better to have too high rather than too low a fan speed. Braun et al. (1989b) showed that the tower control that mini- mizes a cooling plant' s instantaneous power consumption varies as a near-linear function of the load over a wide range of conditions. Although optimal control depends on the ambient wet-bulb tem- perature, this dependence is small compared to the load effect. Figure 6 shows an example of how the optimal tower control varies for a specific plant. The tower airflow as a fraction of the design capacity is plotted as a function of load relative to design load for two different wet-bulb temperatures. For a 10 K change in wet-bulb AIRFLOW TOWER RELATIVE OPTIMAL Chart Type: bar 0.2 0.4 0.6 0.8 1.0 OPTIMAL 0.3 0.49 0.51 0.72 0.76 NEAR-OPTIMAL 0.48 0.52 0.58 0.76 0.78 Fig. 6 Example of Optimal Tower Fan Control Gtwr Fig. 7 Fractional Tower Airflow Versus Part-Load Ratio X-Axis: PLR Y-Axis: ΔGtwr Chart Type: line ΔPLR ΔGtwr item_01 0.25 1 temperature, the optimal control varies by only about 5% of the tower capacity. This difference in control results in less than a 1% difference in the plant power consumption. Figure 6 also shows that linear functions work well in correlating the optimal control over a wide range of loads for the two wet-bulb temperatures. Given the insensitivity to wet-bulb temperature and the fact that the load is highly correlated with wet bulb, a single linear relationship is ade- quate in correlating the optimal tower control in terms of load. Figure 7 depicts the general form to determine tower airflow as a function of load. The (unconstrained) relative tower airflow is computed as a linear function of the part-load ratio as Gtwr = 1 - (PLRtwr.cap - PLR) for 0.25 PLR 1.00 (15) twr where Gtwr = optimal tower airflow divided by maximum airflow with all cells operating at high speed PLR = chilled-water load divided by design total chiller plant cooling capacity (part-load ratio) PLR = part-load ratio (value of PLR) at which tower operates at its twr.cap capacity (Gtwr = 1) = slope of relative tower airflow (Gtwr) versus part-load ratio twr (PLR) function Inc. ASHRAE, 2019 user. single for Licensed | {}
a1072fb8-1ce5-4e37-94a4-111d1e8c6d56 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 43.10 Table 1 Parameter Estimates for Near-Optimal Tower Control Equation ¦ Parameter ¦ One-Speed Fans ¦ Two-Speed Fans ¦ Variable-Speed Fans ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ PLR twr.cap ¦ PLR0 ¦ V2PLR0 ¦ V3PLR0 ¦ ¦ ¦ 1 ¦ 2 ¦ 1 ¦ ¦ twr ¦ PLR twr,cap ¦ 3PLR twr,cap ¦ 2PLR twr,cap ¦ Note: PLR0 1 P ch,des S atwr,des twr,des + r 시 P cwr,des twr,des The linear relationship between the optimal airflow and load is only valid for loads greater than about 25% of the design load. For many installations, chillers do not operate at these small loads. However, for those situations in which chiller operation is necessary below 25% of full load, the tower airflow should be reduced to zero as the load goes to zero according to Gtwr twr (PLR twr,cap 0.25)] for PLR 0.25 (16) = 4PLR [1 - - The results of either Equation (15) or (16) must be constrained between 0 and 1. This fraction oftower capacity is then converted to a tower control using the sequencing rules of the section on Near- Optimal Tower Fan Sequencing. The variables of the open-loop linear control Equation (15) that yield near-optimal control depend on the system , s character- istics. Detailed measurements may be taken over a range of con- ditions and used to accurately estimate these variables. However, this requires measuring component power consumption along with considerable time and expertise, and may not be cost effec- tive unless performed by on-site plant personnel. Alternatively, simple estimates of these parameters may be obtained using design data. Open-Loop Parameter Estimates Using Design Data. Good estimates for the parameters ofEquation (15) may be determined an- alytically using design information as summarized in Table 4. These estimates were derived by Braun and Diderrich (1990) by applying optimization theory to a simplified mathematical model ofthe chiller and cooling tower, assuming that the tower fans are sequenced in a near-optimal manner. In general, these estimates are conservative in that they should provide greater rather than less than the optimal tower airflow. The results given in Table 1 for variable-speed fans should also provide adequate estimates for three-speed fans. Design factors that affect the parameter estimates given in Table 1 are the (1) ratio of chiller power to cooling tower fan power at design conditions P (2) sensitivity of chiller power to ch,desP twr,des' changes in condenser water return temperature at design conditions S cwr.des' and (3) sum of the tower approach and range at design con- ditions (atwr,des + rtwr.des). Chiller power consumption at design conditions is the total power consumption of all plant chillers oper- ating at their design cooling capacity. Likewise, the design tower fan power is the total power associated with all tower cells operating at high speed. As the ratio of chiller power to tower fan power increases, it becomes more beneficial to operate the tower at higher airflows. This is reflected in a decrease in the part-load ratio PLRtwr.cap at which the tower reaches its capacity. If the tower air- flow were free (i.e., zero fan power), then PLRtwr.cap go to would zero, and the best strategy would be to operate the towers at full capacity independent of the load. A typical value for the ratio of the chiller power to the cooling tower fan power at design conditions is 10. 2019 ASHRAE Handbook-HVAC Applications (SI) The chiller sensitivity factor S cwr.des is the incremental increase in chiller power for each degree increase in condenser water tempera- ture as a fraction of the power, or Change in chiller power Scwr,des Change in cond. water return temp. Chiller power (17) If the chiller power increases by 2% for a 0.5 K increase in con- is equal to 0.04/K. A large denser water temperature, Scwr.des sensitivity factor means that the chiller power is very sensitive to the cooling tower control favoring operation at higher airflow rates (low PLR The sensitivity factor should be evaluated at design twr.cap). conditions using chiller performance data. Typically, the sensitivity factor is between 0.02 and 0.06/K. For multiple chillers with dif- ferent performance characteristics, the sensitivity factor at design conditions may be estimated by (18) Nch S P ch,des,i cwr. ,des,i i=1 Scwr,des Nch = P ch,des,i i=1 where Scwr,des,i is the sensitivity factor and P is the power con- ch,des,i sumption for the ith chiller at the design conditions, and Nch is the total number of chillers. is the temperature dif- The design approach to wet bulb atwr.des ference between the condenser water supply and the ambient wet bulb for the tower, operating at its air and water flow capacity at is the water tem- plant design conditions. The design range rtwr,des perature difference across the tower at these same conditions (con- denser water return minus supply temperature). The sum of atwr.des is the temperature difference between the tower inlet and and rtwr,des the ambient wet bulb and represents a measure of the tower's capa- bility to reject heat to ambient relative to the system requirements. A small temperature difference (tower approach plus range) results from a high tower heat transfer effectiveness or high water flow rate and yields lower condenser water temperatures with lower chiller power consumption. Typical values for the design approach and range are 4 and 6 K. The part-load ratio PLRtwr.cap associated with the tower operating at full capacity may be greater than or less than one. Values less than unity imply that, from an energy point of view, the tower is not sized for optimal operation at design load conditions and that it should operate at its capacity for a range of loads less than the design load. Values greater than one imply that the tower is oversized for the design load and that it should never operate at its capacity. For multiple chillers with very different performance character- istics, different open-loop parameters may be used for any combi- nation of operating chillers. The sensitivity factors and chiller design power used to determine the open-loop control parameters in Table 1 should be estimated for each combination of operating chillers, and the part-load ratio used in Equation (15) should be determined using the design capacity for the operating chillers (not all chillers). In this case, Nch in Equation (18) represents the number of operating chillers. Open-Loop Parameter Estimates Using Plant Measurements. Energy consumption may be somewhat further reduced by deter- mining the open-loop control parameters from plant measurements. However, this results in additional complexity associated with im- plementation. One method for estimating the open-loop control parameters of Equation (16) from plant measurements involves per- forming a set of one-time trial-and-error experiments. At a given set of conditions (i.e., cooling load and ambient conditions), the opti- mal tower control is estimated by varying the fan settings and mon- itoring the total chiller and fan power consumption. Each tower Inc. ASHRAE, 2019 user. single for Licensed | {}
ab6cc12d-56b7-4415-924b-cfdc7a39c740 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Supervisory Control Strategies and Optimization 43.11 control setting and load condition must be maintained for a suffi- cient time for the power consumption to approach steady state and to hold the chilled-water supply temperature constant. The control setting that produces the minimum total power consumption is deemed optimal. This set of experiments is performed for a number of chilled-water cooling loads and the best-fit straight line through the resulting data points is used to estimate the parameters of Equa- tion (15). As initial control settings for each load, Equation (15) may be used with estimates from design data as summarized in the pre- vious section. Another method for estimating the variables of Equation (15) uses an empirical model for total power consumption that is fit to plant measurements. The control that minimizes the power con- sumption associated with the model is then determined analytically. The section on Simplified Static Optimization of Cooling Plants describes a general method for determining linear control relations in this manner using a quadratic model. For cooling tower fan con- trol, chiller and fan power consumption are correlated with load and tower airflow for a constant chilled-water supply temperature using a quadratic function as follows: P = ao + a1PLR + a2PLR2 + a3Gtwr + a4G2 twr + a5PLR G twr where ao to a5 are empirical constants determined through linear regression applied to measurements. For the quadratic function of Equation (19), the tower airflow that results in minimum power is a linear function of the PLR. The parameters of the open-loop control Equation (15) are then a3 + 2a4 PLRtwr,cap = a5 (19) a5 - twr 2a4 (20) (21) For multiple chillers with very different performance character- istics, different open-loop parameters can be determined for any combination of operating chillers. In this case, separate correlations for near-optimal airflow or power consumption must be determined for each chiller combination. Overrides for Equipment Constraints The fractional tower airflow as determined by Equations (15) or (16) must be bounded between 0 and 1 according to the physical constraints ofthe equipment. Additional constraints on the tempera- ture of the supply water to the chiller condensers are necessary to avoid potential chiller maintenance problems. Many (older) chillers have a low limit on the condenser water supply temperature that is necessary to avoid lubrication migration from the compressor. A high-temperature limit is also necessary to avoid excessively high pressures in the condenser, which can lead to compressor surge in centrifugal chillers. If condenser water temperature falls below the low limit, then it is necessary to override the open-loop tower con- trol and reduce tower airflow to go above this limit. Similarly, if the high limit is exceeded, then tower airflow should be increased as required. Implementation Before commissioning, the parameters of the open-loop control Equation (15) must be specified. These parameters are estimated using Table 1 After the system is in operation, these parameters may be fine-tuned with measurements as outlined previously. If multiple chillers have significantly different performance characteristics, it may be advantageous to determine different parameters for Equation (15), depending on the combination of operating chillers. The relative tower airflow must be converted to a specific set of tower fan settings using the sequencing rules defined previously. This involves defining a relationship (i.e., table) for fan settings as a function of tower airflow. The table is constructed by defining the best fan settings for each possible increment of airflow. The conver- sion process between the continuous output of Equations (15) or (16) and the fan control involves choosing the set of discrete fan set- tings from the table that produces a tower airflow closest to the desired flow. However, in general, it is better to have greater rather than less than the optimal airflow. A good general rule is to choose the set of discrete fan controls that results in a relative airflow that is closest to, but not more than 10% less than, the output of Equa- tions (15) or (16). With the parameters of Equation (15) specified, the following procedure is applied at each decision interval (e.g., 15 min) to deter- mine the tower control: 1. Ifthe temperature of supply water to the chiller condenser is less than the low limit, then reduce tower airflow by one increment according to the near-optimal sequencing rules and exit the algo- rithm. Otherwise go to step 2. 2. If the temperature of supply water to the chiller condenser is greater than the high limit, then increase tower airflow by one increment according to the near-optimal sequencing rules and exit the algorithm. Otherwise go to step 3. 3. Determine the chilled-water load relative to the design load. 4. If the chilled-water load has changed by a significant amount (e.g., 10%) since the last control change, then go to step 5. Other- wise, exit the algorithm. 5. If the part-load ratio is greater than 0.25, then compute the near- optimal tower airflow as a fraction of tower capacity Gtwr with Equation (15). Otherwise, determine Gtwr with Equation (16). 6. Limit Gtwr to keep the change from the previous decision interval less than a minimum value (e.g., less than 0.1 change). 7. Restrict the value of Gtwr between 0 and 1. 8. Convert the value of Gtwr a specific set of control functions for to each of the tower cell fans according to the near-optimal se- quencing rules. This procedure requires some estimate of the chilled-water load, along with a measurement of the condenser water supply tempera- ture. However, accuracy of the load estimates is not extremely critical. In general, near-optimal control determined with load esti- mates that are accurate to within 5 to 10% results in total power consumption that is within 1% ofthe minimum. The best method for determining the chilled-water load is from the product of the mea- sured chilled-water flow rate and the temperature difference between the chilled-water return and supply. For systems that use constant- flow pumping to the chillers, flow rates may be estimated from design data for the pumps and system pressure-drop characteristics. Example 1. Consider an example plant consisting of four 2000 kW chillers with four cooling tower cells, each having two-speed fans. Each chiller consumes approximately 340 kW at design capacity, and each tower fan uses 42 kW at high speed. At design conditions, the chiller power in- creases approximately 12.2 kW for a 1 K increase in condenser water temperature, giving a sensitivity factor of 12.2/340 or 0.036/K. The tower design approach and range from manufacturer's data are 4 and 6 K. Solution: The first step in applying the open-loop control algorithm to this problem is determining the parameters of Equation (15) from the design data. From Table 1, the part-load ratio at which operation of the tower is at its capacity is estimated for the two-speed fans as 1 PLRtwr.cap = 0.83 4 340 kW 12 0.036 K 4 + 6 4 42 kW Inc. ASHRAE, 2019 user. single for Licensed | {}
31a278ba-1675-4fea-bcf2-a764a5b8bebf | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 43.12 2019 ASHRAE Handbook-HVAC Applications (SI) and the slope of the fractional airflow versus part-load ratio is esti- mated to be 2 = 0.80 twr 0.83 3 Given these parameters and the part-load ratio, the fractional tower airflow is estimated as IF (PLR > 0.25) THEN Gtwr = 1 - twr(PLRtwr.cap - PLR) ELSE G twr 4PLR[1 - twr (PLR twr.cap = - 0.25)] Gtwr = MIN[1, MAX(0, Gtwr)] To convert Gtwr into a specific tower control, the tower sequencing must be defined. The following table gives this information in a form that specifies the relationship between Gtwr and tower control for this example. Cooling Tower Fan Sequencing for Example 1 ¦ Sequence No. ¦ Gtwr ¦ Tower Fan Speeds ¦ Tower Fan Speeds ¦ Tower Fan Speeds ¦ Tower Fan Speeds ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Sequence No. ¦ Gtwr ¦ Cell #1 ¦ Cell #2 ¦ Cell #3 ¦ Cell #4 ¦ ¦ 1 ¦ 0.125 ¦ Low ¦ Off ¦ Off ¦ Off ¦ ¦ 2 ¦ 0.250 ¦ Low ¦ Low ¦ Off ¦ Off ¦ ¦ 3 ¦ 0.375 ¦ Low ¦ Low ¦ Low ¦ Off ¦ ¦ 4 ¦ 0.500 ¦ Low ¦ Low ¦ Low ¦ Low ¦ ¦ 5 ¦ 0.625 ¦ High ¦ Low ¦ Low ¦ Low ¦ ¦ 6 ¦ 0.750 ¦ High ¦ High ¦ Low ¦ Low ¦ ¦ 7 ¦ 0.875 ¦ High ¦ High ¦ High ¦ Low ¦ ¦ 8 ¦ 1.000 ¦ High ¦ High ¦ High ¦ High ¦ For a specific chilled-water load, the fan control should be the sequence of tower fan settings from the table that results in a value of Gtwr that is closest to, but not more than 10% less than, the output of Equations (15) or (16). Note that this example assumes that proper water flow can be maintained over all cooling tower cells. 3.2 CHILLED-WATER RESET WITH FIXED-SPEED PUMPING Figure 8 shows a common configuration using fixed-speed chilled-water pumps with two-way valves at the cooling coils. A two-way bypass valve controlled to maintain a fixed pressure differ- ence between the main supply and return lines is used to ensure relatively constant flow through chiller evaporators and reduce pres- sure drop and pumping costs at low loads. However, additional pump and chiller power savings can be realized by adjusting the chilled-water supply temperature to keep some cooling coil valves open and thereby minimize the bypass flow. Inc. ASHRAE, 2019 user. single for Licensed ![image](/image/placeholder) EVAPORATOR BUILDING #2 EVAPORATOR #1 BYPASS VALVE CHILLER CHILLER CHILLED-WATER PUMPS Fig. 8 Typical Chilled-Water Distribution for Fixed-Speed Pumping Ideally, the chilled-water temperature should be adjusted to maintain all discharge air temperatures with a minimal number of cooling-coil control valves in a saturated (fully open) condition. The procedure described in this section is designed to accomplish this goal in a reliable and stable manner that reacts quickly to changing conditions. Pump Sequencing In plants where one chilled-water pump is dedicated to each chiller, the sequencing of chilled-water pumps is defined by the sequencing of chillers. In some installations, the chiller pumps are not dedicated to chillers, but instead are arranged in parallel, sharing common headers. In this case, the order for bringing pumps online and off-line and the conditions for adding or removing chilled-water pump capacity must be specified. For pumps of different capacities, the logical order for bringing pumps online is from small to large. For pumps of similar capacity, the most efficient pumps should be brought online first and taken off-line last. Optimal Chilled- W ater Temperature One method for determining the optimal chilled-water tempera- ture is to monitor the water control valve positions of "representative" air handlers and to adjust the set temperature incre- mentally at fixed decision intervals until a single control valve is fully open. The representative air handlers should be chosen to include load diversity at all times and ensure reliable data. One dif- ficulty of this control approach is that valve position data are often unreliable. The valve could be stuck open or the saturation indicator could be faulty. This problem can be overcome by also monitoring discharge air temperatures, using them as a consistency check on valve position data. If a valve is unsaturated, this implies that the coil has sufficient capacity to maintain the discharge air temperature near the set point. Conversely, if a valve remains saturated at 100% open, the discharge air temperature should ultimately increase above the set point. These considerations lead to the following sim- ple rules for increasing or decreasing the chilled-water set point in response to valve position and discharge air temperature data. · If all water valves are unsaturated or the discharge air tempera- tures associated with all saturated valves are lower than the set point, increase the chilled-water set temperature. · If more than one valve is saturated at 100% open and their corre- sponding discharge air temperatures are greater than their set points, decrease the chilled-water temperature. In implementing these rules, a fixed increment for increasing or decreasing the chilled-water temperature must be chosen. A small increment results in more stable control, but also results in a slow response to sudden changes in load or supply air temperature set points. Using a first-order approximation, the chilled-water tem- perature can be reset in response to sudden changes in load and supply air temperature set point according to (22) PLR (tas,o - tchws,o) tchws = tas PLR。 where new chilled- water set-point temperature tchws tas = current supply air set-point temperature PLR = current part-load ratio (chiller load divided by total design load for all chillers) = chilled-water set point associated with last control decision = tchws,o tas.o supply air set point associated with last control decision PLRO = part-load ratio associated with last control decision Equation (22) assumes that the chilled-water temperature asso- ciated with the last control decision was optimal. As a result, it only applies to anticipating the effects of significant changes in the load | {}
ec2e9e9d-a91a-4f66-81f1-b1644498c43c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Supervisory Control Strategies and Optimization 43.13 and supply air set-point temperature on the optimal chilled-water set point. The "bump-and-wait" strategy fine-tunes the chilled- water supply temperature when the load and supply air set point are stable. For a variable-air-volume system, the supply air set points are most often constant and identical for all air-handling units. However, for a constant-air-volume system, these set points may vary with different air handlers. In this case, the supply air set point to use in Equation (22) should be a capacity weighted average value for the representative air handlers. Equation (22) indicates that the optimal chilled-water supply tem- perature increases with increasing supply air temperature and de- creasing load. This is because these changes cause the cooling-coil valves to close; optimal control involves keeping at least one valve open. Increasing supply air temperature causes the cooling-coil valves to close somewhat because of a larger average temperature difference for heat transfer between the water and air. A lower load requires smaller air-to-water temperature differences, which also leads to control valves closing. Overrides for Equipment and Comfort Constraints For a given chiller load, the chilled-water temperature has both upper and lower limits. The lower limit is necessary to avoid ice formation on the evaporator tubes of the chiller. This limit depends primarily on the load in relation to the size of the evaporator or, in other words, the temperature difference between the chilled water and refrigerant. At small temperature differences (large area or small load), the evaporator can tolerate a lower chilled-water tem- perature to avoid freezing than at large temperature differences. The lower limit on the chilled-water set point should be evaluated at the design load, because the overall system performance is improved by increasing chilled-water temperature above this limit for loads less than design. This lower limit can range from 3 to 7°C when chilled water is used for dehumidification, to 13°C for TABS, and as high as 15.6°C for chilled water serving radiant or chilled-beam cooling systems. An upper limit on the chilled-water temperature arises from comfort constraints associated with the zones and the possibility of microbial growth associated with high humidities. For the available flows, the chilled-water temperature should be low enough to pro- vide discharge air at a temperature and humidity sufficient to maintain all zones in the comfort region and avoid microbial growth. This upper limit varies with both load and entering air con- ditions and is accounted for by monitoring the zone conditions to ensure that they are in the comfort zone. If zone temperatures or humidities are not within reasonable bounds, then the discharge air temperature set point should be lowered. For radiant panel, chilled- beam, or TAB systems, there is no specific upper chilled-water limit as long as the load is satisfied. Implementation At each decision interval (e.g., 5 min), the following algorithm would be applied for determining the optimal chilled-water set- point temperature: 1. Determine the time-averaged total chilled-water load for the pre- vious decision interval. 2. If the chilled-water load or supply air set-point temperature has changed by a significant amount (e.g., 10%) since the last con- trol change, then estimate a new optimal chilled-water set point with Equation (22) and go to step 6. Otherwise, go to step 3. 3. Determine the time-averaged position of (or controller output for) the cooling-coil water valves and corresponding discharge air temperatures for representative air handlers. 4. If more than one valve is saturated at 100% open and their corre- sponding supply air temperatures are greater than set point (e.g., ![image](/image/placeholder) 0 DIRECT COUPLING EVAPORATOR PIPING BUILDING 饼 EVAPORATOR #1 CHILLER CHLLER CHILLED-WATER PUMPS 수 个 Fig. 9 Typical Chilled- w ater Distribution for Primary/ Secondary Pumping 0.5 K), then decrease the chilled-water temperature by a fixed amount (e.g., 0.25 K) and go to step 6. Otherwise, go to step 5. 5. If all water valves are unsaturated or the supply air temperatures associated with all valves that are saturated are lower than the set point, then raise the chilled-water set temperature by a fixed amount (e.g., 0.25 K). Otherwise, exit the algorithm with the chilled-water set point unchanged. 6. Limit the chilled-water set-point temperature between the upper and lower limits dictated by comfort, humidity, and equipment safety. Implementing this algorithm requires some estimate of the chilled-water load, along with a measurement of the discharge air temperatures and control valve positions. However, a highly accu- rate estimate of the load is not necessary. 3.3 CHILLED-WATER RESET WITH V ARIABLE-SPEED PUMPING Figure 9 shows a common configuration for systems using variable-speed chilled-water pumps with primary/secondary water loops. The primary pumps are fixed speed and are generally sequenced with chillers to provide a relatively constant flow of water through the chiller evaporators. The secondary chilled-water pumps are variable speed and are typically controlled to maintain a specified set point for pressure difference between supply and return flows for the cooling coils. Although variable-speed pumps are usually used with primary/ secondary chilled-water loops, they may also be applied to systems with a single chilled-water loop. In either case, variable-speed pumps offer the potential for a significant operating cost saving when both chilled-water and pressure differential set points are optimized in response to changing loads. This section presents an algorithm for determining near-optimal values of these control variables. Optimal Differential Pressure Set Points In practically all variable-speed chilled-water pumping applica- tions, pump speed is controlled to maintain a constant pressure differential between the main chilled-water supply and return lines. However, this approach is not optimal. To maintain a constant pressure differential with changing flow, the control valves for the air-handling units must close as the load (i.e., flow) is reduced, resulting in an increase in the flow resistance. The best strategy for a given chilled-water set point is to reset the differential pressure set point to maintain all discharge air temperatures with at least one control valve in a saturated (fully open) condition. This results in a Inc. ASHRAE, 2019 user. single for Licensed | {}
46a2f4f0-e68e-4539-bf72-da7c7565f429 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 43.14 relatively constant flow resistance and greater pump savings at low loads. With variable differential pressure set points, optimizing the chilled-water loop is described in terms of finding the chilled-water temperature that minimizes the sum of chiller and pumping power, with pump control dependent on set point and load. Near-Optimal Chilled- Water Set Point The optimal chilled-water supply temperature at a given load results from a trade-off between chiller and pumping power, as shown in Figure 10. As the chilled-water temperature increases, chiller power is reduced because of a reduction in the lift require- ments of the chiller. For a higher set temperature, more chilled-water flow is necessary to meet the load requirements, and the pumping power requirements increase. The minimum total power occurs at a point where the rate ofincrease in pumping power with chilled-water temperature is equal to the rate of decrease in chiller power. This optimal set point moves to lower values as the load increases. Braun et al. (1989b) demonstrated that the optimal chilled-water set point varies as a near-linear function of both load and wet-bulb temperature entering cooling coils over a wide range of conditions. Chart Type: line 5 6 7 8 9 10 item_01 0kW 0kW 0kW 0.3kW 0.5kW 1000kW Fig. 10 Trade-off of Chiller and Pump Power with Chilled- Water Set Point X-Axis: RELATIVE CHILLED-WATER LOAD Y-Axis: OPTIMAL CHILLED-WATER SET POINT, °C Chart Type: line HIGH WET BULB LOW WET BULB OPTIMAL NEAR-OPTIMAL item_01 27°C 16°C 16°C 4°C Fig. 11 Comparisons of Optimal Chilled- w ater Temperature 2019 ASHRAE Handbook- -HVAC Applications (SI) Figure 1 1 shows an example of how the optimal set point varies for a specific plant. The set point is plotted as a function of load relative to design load for two different wet-bulb temperatures. In general, the optimal chilled-water temperature decreases with load because pump power becomes a larger fraction of total power. A lower set-point limit is set to avoid conditions that could form ice on evap- orator tubes or too high a chiller "lift, " and an upper limit is established to ensure adequate cooling-coil dehumidification. For a given load, the chilled-water set point increases with wet-bulb tem- perature because energy transfer across each cooling coil is propor- tional to the difference between its entering air wet-bulb temperature and the entering water temperature (the chilled-water set point). For a constant load, this temperature difference is constant and the chilled-water supply temperature increases linearly with entering air wet-bulb temperature. The results in Figure 11 were obtained for a system where both the chilled-water supply and supply air set points to the zones were optimized. For this case, the supply air temperatures varied between 13°C at high loads and 16°C at low loads. More typically, supply air temperatures are constant at 13°C, and the variation in chilled-water supply temperature is smaller than that shown in Figure 10. Figure 12 depicts the general form for an algorithm to determine chilled-water supply set points as a function of load and the average wet-bulb temperature entering the cooling coils. A normalized dif- ference between the entering air wet-bulb temperature and the chilled-water supply temperature is shown as a linear function ofthe part-load ratio. The (unconstrained) chilled-water set point is deter- mined as tchws = tmx, wb - 「(tmx, wb,des - tchws,des) (23) where 「 = 1 - 3. chws (PLRchws.cap - PLR) (24) tchws supply temperature set point = chilled-water tmx,wb = average or "representative" wet-bulb temperature of air entering cooling coils tchws,des = chilled-water supply temperature at design conditions tmx, wb,des wet-bulb temperature of air entering cooling coils at design = conditions PLR = chilled-water load divided by the total chiller cooling capacity (part-load ratio) PLRchws.cap part-load ratio (value of PLR) at which 「 = 1 �chws slope of the 「 versus part-load ratio (PLR) function Chart Type: line Red Line Green Line item_01 1 1 Fig. 12 Dimensionless Chilled- Water Set Point Versus Part-Load Ratio Inc. ASHRAE, 2019 user. single for Licensed | {}
7ded97ec-7046-4a62-93c1-ea861b4b272d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Supervisory Control Strategies and Optimization 43.15 Table 2 Parameter Estimates for Near-Optimal Chilled- w ater Set Point Equation ¦ Parameter ¦ Estimate ¦ ¦ --- ¦ --- ¦ ¦ PLR chws,cap ¦ 1 P ch,des S t mx,wb,des tchws,des 3 P chws,des 시 chwp,des ¦ ¦ chws ¦ 0.5 PLRchws,cap ¦ For radiant ceiling panel (RCP) and chilled-beam systems that provide sensible cooling only, replace tmx, wb and tmx, wb.des by the corresponding zone operative temperatures. The result of Equation (23) must be constrained between upper and lower limits dictated by equipment safety (evaporator freezing), machine operating enve- lope, and comfort and humidity concerns. The variables of Equation (24) that yield near-optimal control depend on the system characteristics. Detailed measurements over a range of conditions may be used to estimate these parameters. How- ever, this requires measuring component power consumption along with considerable time and expertise, and may not be cost effective unless performed by on-site plant personnel. Alternatively, simple estimates of these parameters may be obtained using design data. Open-Loop Parameter Estimates Using Design Data. Rea- sonable estimates of the parameters of Equation (24) may be determined analytically using design information as summarized in Table 2. These estimates were derived by applying optimization theory to a simplified mathematical model ofthe chiller and second- ary-loop water pumps, assuming that a differential pressure reset strategy is used, pump efficiencies are constant, and the supply air temperature is not varied in response to changes in chilled-water supply temperature. In general, these parameter estimates are con- servative in that they should provide a relatively low estimate of the optimal chilled-water set point. The design factors that affect the parameter estimates given in Table 2 are the (1) ratio of the chiller power to chilled-water pump ch,des/P (2) chiller power's sen- power at design conditions P chwp,des' sitivity to changes in chilled-water temperature at design conditions Schws,des, and (3) difference between design entering air wet-bulb temperature to the cooling coil and the chilled-water supply tem- perature (tmx,wb,des tchws.des). - Chiller power consumption at design conditions is the total power consumption of all plant chillers operating at their design cooling capacity. Likewise, the design pump power is the total power associated with all secondary chilled-water supply pumps operating at high speed. As the ratio of chiller power to pump power increases, it becomes more beneficial to operate the chillers at higher chilled-water temperatures and the pumps at higher flows. If chiller power were This is reflected in an increase in PLRchws.cap. free, then PLRchws.cap would go to zero, and the best strategy would be to operate the chillers at the minimum possible set point, result- ing in low chilled-water flow rates. Typical values for the ratio of chiller power to pump power at design conditions are between 10 and 20, depending mainly on whether primary/secondary pumping is used. Chiller sensitivity factor S chws,des is the incremental increase in chiller power for each degree decrease in chilled-water temperature as a fraction of the power: Increase in chiller power Scwr,des Decrease in chilled-water return temp. Chiller power If chiller power increases by 2% for a 0.5 K decrease in chilled- is equal to 0.04/K. A large sensi- water temperature, then Schws.des tivity factor means that chiller power is very sensitive to the set point control favoring operation at higher set point temperatures and flows (higher PLRchws,cap). The sensitivity factor should be evalu- ated at design conditions using chiller performance data. Typically, the sensitivity factor is between 0.02 and 0.06/K. For multiple chillers with different performance characteristics, the sensitivity factor at design conditions is estimated as (26) ![image](/image/placeholder) Nch S chws,des,iP ch,des,i i=1 Schws,des Nch = P ch,des,i i=1 where S is the sensitivity factor and P is the power con- ch,des,i chws, des,i is the total sumption for the ith chiller at design conditions, and Nch number of chillers. The design difference between coil inlet air wet-bulb tempera- ture and entering water temperature should be evaluated for a typical air handler operating at design load and flows. A small temperature difference results from a high coil heat transfer effectiveness or high water flow rate, allowing higher chilled-water temperatures with lower chiller power consumption. This is evident from Equation (23), where chilled-water set point decreases linearly with (tmx,wb,des - tchws,des) for a given 「, and 「 is inversely related to the square root of (tmx,wb,des - tchws,des). Typically, this temperature difference is about 10 K. Example 2. Consider an example plant with primary/secondary chilled- water pumping. There are four 2000 kW chillers, each with a dedicated primary pump. Each chiller consumes approximately 340 kW at design capacity. At design conditions, chiller power increases approximately 2.2 kW for a 0.5 K decrease in chilled-water temperature, giving a sen- sitivity factor of 2.2/340 or 0.04/K. The design chilled-water set point is 5°C, and the coil entering wet-bulb temperature is 16°C at design con- ditions. The secondary loop uses three identical 45 kW chilled-water pumps: one with a variable-speed and two with fixed-speed motors. Solution: The first step in applying the open-loop control algorithm to this problem is determining the parameters of Equation (24) from the design data. From Table 2, the part-load ratio at which the chilled-water temperature reaches a minimum (with the design entering wet-bulb temperature to the coils) is 1 4 340 PLRchws,cap N 3 3 45 = 0.036 K 11 = 1.15 and the slope of the set point versus part-load ratio is estimated to be 0.5 = 0.43 chws 1.15 Given these parameters and the part-load ratio, the unconstrained chilled-water set-point temperature is then tchws = tmx, wb - [1 - 0.43(1.15 - PLR)](11°C) Pump Sequencing Variable-speed pumps are sometimes used in combination with fixed-speed or other variable-speed pumps. Pump sequencing in- volves determining both the order and point that pumps should be brought online and off-line. (25) Pumps should be brought online in an order that allows a contin- uous variation in flow rate and maximized operating efficiency of the pumps at each switch point for the specific pressure loss char- acteristic. For a combination of fixed- and variable-speed pumps, at least one variable-speed pump should be brought online before any fixed-speed pumps. For single-loop systems (i.e., no secondary loop) with variable-speed pumps, the pressure drop characteristics Inc. ASHRAE, 2019 user. single for Licensed | {}
25f78e71-cbcc-4dd9-b0a0-b901a56ba134 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 43.16 2019 ASHRAE Handbook- -HVAC Applications (SI) change when chillers are added or removed and the optimal se- quencing of pumps depends on the sequencing of chillers. An additional pump should be brought online whenever the cur- rent set of pumps is operating at full capacity and can no longer satisfy the differential pressure set point. This situation can be detected by monitoring the differential pressure or the controller output signal. Insufficient pump capacity leads to extended periods with differential pressures that are less than the set point and a controller output that is saturated at 100%. A pump may be taken off-line whenever the remaining pumps have sufficient capacity to maintain the differential pressure set point. This condition can be determined by comparing the current (time-averaged) controller output with the controller output (time-averaged) at the point just after the last pump was brought online. The pump can be brought off-line when the current output is less than the switch point value by a specified dead band (e.g., 5%). Overrides for Equipment and Comfort Constraints The chilled-water temperature is bounded by upper and lower limits dictated by comfort, humidity, and equipment safety con- cerns. However, within these bounds, the chilled-water temperature may not always be low enough to maintain supply air set-point tem- peratures for the cooling coils. This situation might occur at high loads when the chilled-water flow is at a maximum and is detectable by monitoring the coil discharge air temperatures. Limits on the minimum pressure differential set point might also be imposed to ensure adequate controllability of the cooling-coil control valves. Implementation Before commissioning, the parameters of the open-loop control for chilled-water set point (Equation [24]) must be estimated using the results of Table 2. After the system is in operation, these param- eters may be fine-tuned with measurements as outlined in the section on Simplified Static Optimization of Cooling Plants. With the parameters specified, the control algorithm is separated into two reset strategies: chilled-water temperature and pressure differential. Chilled- w ater Temperature Reset. The chilled-water supply temperature set point is reset at fixed decision intervals (e.g., 15 min) using the following procedure: 1. Determine the time-averaged position of (or controller output for) the cooling-coil water valves and corresponding discharge air temperatures for "representative" air handlers over the previ- ous decision interval. 2. If more than one valve is saturated at 100% open and their cor- responding discharge air temperatures are greater than set point (e.g., 0.5 K), then decrease the chilled-water temperature by a fixed amount (e.g., 0.25 K) and go to step 5. Otherwise, go to step 3. 3. Determine the total chilled-water flow and load. 4. Estimate an optimal chilled-water set point using static optimi- zation. Increase or decrease the actual set point in the direction of the near-optimal value by a fixed amount (e.g., 0.5 K). 5. Limit the new set point between upper and lower constraints dic- tated by comfort and equipment safety. Pump Sequencing. Secondary pumps should be brought online or off-line at fixed decision intervals (e.g., 15 min) with the following logic: 1. Evaluate the time-averaged pump controller output over the pre- vious decision interval. 2. If the pump controller is saturated at 100%, then bring the next pump online. Otherwise, go to step 3. 3. Ifthe pump control output is significantly less (e.g., 5%) than the value associated with the first time interval after the last pump was brought online, then bring that pump off-line. Differential Pressure Reset. The set point for differential pressure between supply and return lines should be reset at smaller time intervals than the supply water temperature reset and pump sequencing strategies (e.g., 5 min) using the following procedure: 1. Check the water valve positions (or controller output) for "rep- resentative" air handlers and determine the time-averaged values over the last decision interval. 2. If more than one valve has been saturated at 100% open, then increase the differential pressure set point by a fixed value (e.g., 5% ofthe design value) and go to step 4. Otherwise, go to step 3. 3. If none of the valves have been saturated, then decrease the dif- ferential pressure set point by a fixed value (e.g., 5% of the design value). 4. Limit the differential pressure set point between upper and lower constraints. 3.4 SEQUENCING AND LOADING MULTIPLE CHILLERS Multiple chillers are normally configured in parallel and typi- cally controlled to give identical chilled-water supply temperatures. In most cases, controlling for identical set temperatures is the best and simplest strategy. With this approach, the relative loading on operating chillers is controlled by the relative chilled-water flow rates. Typically, the distribution of flow rates to heat exchangers for both chilled and condenser water are dictated by chiller pressure drop characteristics and may be adjusted through flow balancing, but are not controlled using a feedback controller. In addition to the distribution of chilled and condenser water flow rates, the chiller sequencing affects energy consumption. Chiller sequencing defines the conditions under which chillers are brought online and off-line. Simple guidelines may be established for each of these controls to provide near-optimal operation. Near-Optimal Condenser w ater Flow Distribution In general, the condenser water flow to each chiller should be set to give identical leaving condenser water temperatures. This condi- tion approximately corresponds to relative condenser flow rates equal to the relative loads on the chillers, even if the chillers are loaded unevenly. Figure 13 shows results for four sets oftwo chillers operated in parallel. The curves represent data from chillers at three different installations: (1) a 19 300 kW variable-speed chiller at the Dallas-Ft. Worth airport, Texas (Braun et al. 1989b); (2) a 1930 kW fixed-speed chiller at an office building in Atlanta (Hackner et al. 1984, 1985); and (3) a 4400 kW fixed-speed chiller at a large office building in Charlotte, North Carolina (Lau et al. 1985). The capac- ities of the chillers in the two office buildings were scaled up for comparison with the Dallas-Ft. Worth airport chiller. The overall chiller coefficient of performance (COP) is plotted versus the difference between the condenser water return tempera- tures for equal chiller loading. For multiple chillers having similar performance characteristics (either variable- or fixed-speed), it is best to distribute the condenser water flow rates so that each chiller has the same leaving condenser water temperature. For situations where chillers do not have identical performance, equal leaving condenser water temperatures result in chiller performance that is close to the optimum. Even for variable- and fixed-speed chiller combinations that have very different performance characteristics, the penalty asso- ciated with using identical condenser leaving-water temperatures is small. To achieve equal condenser leaving-water temperatures, it is necessary to properly balance the condenser water flow rates at design operating conditions. Optimal Chiller Load Distribution Assuming identical chilled-water return and chiller supply tem- peratures, the relative chilled-water load for each parallel chiller Inc. ASHRAE, 2019 user. single for Licensed | {}
d1f0016d-b5cf-4212-9add-119afe12148c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Supervisory Control Strategies and Optimization 43.17 (load divided by total load) that is operating could be controlled by its relative chilled-water flow rate (flow divided by total flow). To change the relative loadings in response to operating conditions, the individual flow rates must be controlled. However, this is typically not done and it is probably sufficient to establish the load distribu- tions based on design information and then balance the flow rates to achieve these load distributions. Alternatively, the individual chiller loads can be precisely controlled through variation of individual chiller supply water set points. Chillers with Similar Performance Characteristics. Braun et al. (1989b) showed that, for chillers with identical design COPs and part-load characteristics, a minimum or maximum power con- sumption occurs when each chiller is loaded according to the ratio of its capacity to the total capacity of all operating chillers. This is equivalent to each chiller operating at equal part-load ratios (load divided by cooling capacity at design conditions). For the ith chiller, the optimal chiller loading is then Qload Qch, des,i ⌀ch,i N �ch,des,i i=1 where Qload is total chiller load, 2ch,des,i is cooling capacity of the ith chiller at design conditions, and N is the number of chillers operating. (27) The loading determined with Equation (27) could result in either minimum or maximum power consumption. However, this solution gives a minimum when the chillers are operating at loads greater than the point at which the maximum COP occurs (i.e., chiller COP decreases with increased loading). Typically, the maximum COP occurs at loads that are less than chiller design capacity. Figure 14 shows the effect of relative loading on chiller COP for different sets of identical chillers loaded at approximately 70% of their total capacities. Three of the chiller sets have maximum COPs when evenly loaded (matching the criterion of Equation [27]), whereas the fourth (Dallas-Ft. Worth fixed-speed) obtains a mini- mum at that point. The part-load characteristic of the Dallas-Ft. Worth fixed-speed chiller is unusual in that the maximum overall COP occurs at its maximum capacity. This chiller was retrofitted with a different refrigerant and drive motor, which derated its capacity from 30 6000 to 19 300 kW. As a result, the evaporators Chart Type: line -6 -4 -2 0 2 4 6 item_01 5.0 5.0 5.5 5.8 5.7 5.5 5.0 Fig. 13 Effect of Condenser Water Flow Distribution for Two Chillers In Parallel and condensers are oversized for its current capacity. Overall, the penalty associated with equally loading the Dallas-Ft. Worth fixed- speed chillers is small compared with optimal loading, and this strategy is probably appropriate. However, a slight reduction in energy consumption is possible if one of the two chillers operates at full capacity. The loading criterion of Equation (27) also works well for many combinations of chillers with different performance characteristics. To achieve specified relative chiller loadings with equal chilled- water set points, chilled-water flow rates must be properly balanced. The relative loadings of Equation (27) only depend on design infor- mation, and flow balancing can be achieved through proper design and commissioning. Chillers with Different Performance Characteristics. For the general case of chillers with significantly different part-load char- acteristics, a point of minimum or maximum overall power occurs where the partial derivatives of the individual chiller's power con- sumption with respect to their loads are equal: for all i and j P P ch,i ch,j 0 Q ch,j ch,i (28) and subject to the constraint that N ⌀chi = 0 load i=1 (29) is the where �ch,i is the cooling load for the ith chiller and Qload total cooling load. In general, the power consumption of a chiller can be correlated as a quadratic function of cooling load and difference between the leaving condenser water and chilled-water supply temperatures according to 2 P = ao⌀ alj tcwr,i - tchws,i a2j tcwr,i - tchwsj + + ch,i + a3i⌀chi + a4 i⌀chi + 0 ch,i asj tewr,i - tchws,i (30) is the leaving condenser water tem- where, for the ith chiller, tcwr is the chilled-water supply temperature. The coef- perature and tchws ficients of Equation (30) (ao,i to a5.i) can be determined for each Chart Type: line 0.3 0.4 0.5 0.6 0.7 item_01 6.0RELATIVE LOAD ON FIRST CHILLER 6.5RELATIVE LOAD ON FIRST CHILLER 6.5RELATIVE LOAD ON FIRST CHILLER 6.0RELATIVE LOAD ON FIRST CHILLER 5.8RELATIVE LOAD ON FIRST CHILLER Fig. 14 Effect of Relative Loading for Two Identical Parallel Chillers Inc. ASHRAE, 2019 user. single for Licensed | {}
334bc572-86ce-4313-8881-1f27c202502c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 43.18 2019 ASHRAE Handbook- HVAC Applications (SI) chiller through regression applied to measured or manufacturers' data. If each chiller has identical leaving condenser and chilled-water supply temperatures, the criterion of Equation (28) applied to the correlation of Equation (30) leads to + 2a4.i⌀ch.i + as,i tewr - tchws a3,i (31) tcwr - tchws i 1 a3,j + 2a4.j ⌀ch,j + as⌀ for is the optimal load for the ith chiller. where ⌀chi Equations (29) and (31) represent a system of N linear equations in terms of N chiller loads that can be solved to give minimum (or possibly maximum) power consumption. For a given combination of chillers, the solution depends on the operating temperatures and total load. However, the individual chiller loads must be constrained to be less than the maximum chiller capacity at these conditions. If an individual chiller load determined from these equations is greater than its cooling capacity, then this chiller should be fully loaded and Equations (29) and (31) should be resolved for the remaining chillers (Equation [31] should only include unconstrained chillers). To control individual chiller loads with identical chilled-water supply temperatures, individual chilled-water flow rates need to be controlled with two-way valves, which is not typical. However, the distribution of chiller loads could be changed for a fixed-flow dis- tribution by using different chilled-water set-point temperatures. For a given flow and load distribution, the individual chiller set point for parallel chillers is determined according to 0 ch,i * tchws,i tchwr tchws = tchwr - fFi⌀load (32) where fFi is the flow for the ith chiller divided by total flow, t chws is the chilled-water supply temperature set point for the combina- tion of chillers determined using the previously defined reset is the temperature of water returned to chillers strategies, and tchwr from the building. Substituting Equation (32) into Equation (30) and then applying the criterion of Equation (28) leads to the following: Inc. ASHRAE, 2019 user. single for Licensed Ai + Bi⌀chj = Aj + Bj�chj for i 1 (33) where tchwr - tchws A i a3,i avi 2a2,i tcwr - tchwr + + = fF,i⌀ load + asj tcwr - tchws * 2 tchwr - t tchwr t chws chws Bi = 2 a4,i asj a2,i + + ff⌀ 0 load fFi 0 load Optimal chiller loads are determined by solving the linear system of equations represented by Equations (33) and (29). The individual chiller set points are then evaluated with Equation (32). If any set points are less than the minimum or greater than the maximum set point, then the set point should be constrained and Equations (33) and (29) should be resolved for the remaining chillers (Equation [33] should only include unconstrained chillers). Example 3. Determine the optimal loading for two chillers using the three methods outlined in this section. Table 3 gives the design cool- ing capacities and coefficients of the curve-fit of Equation (30) for the two chillers. The chillers are operating with a total cooling load of Table 3 Chiller Characteristics for Optimal Loading Example 3 ¦ Variable ¦ Units ¦ Chiller 1 ¦ Chiller 2 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 0 ch,des,i ¦ kW ¦ 4396 ¦ 1934 ¦ ¦ ao.i ¦ kW ¦ 106.4 ¦ 119.7 ¦ ¦ a1.i ¦ kW/K ¦ 11.06 ¦ 0.3376 ¦ ¦ a2.i ¦ kW/K2 ¦ 0.5806 ¦ 0.1552 ¦ ¦ a3.i ¦ kW/kW ¦ -0.0208 ¦ -0.1045 ¦ ¦ a4j ¦ kW/kW2 ¦ 0.000 010 7 ¦ 0.000 043 04 ¦ ¦ asj ¦ kW/(kW ·K) ¦ -0.000 516 3 ¦ 0.004 364 ¦ COP X-Axis: LOAD RELATIVE TO DESIGN LOAD Y-Axis: Score Chart Type: line 0.4 0.5 0.6 0.7 0.8 0.9 1.0 1.1 item_01 2.8 3.8 4.0 4.2 4.4 5.0 5.8 6.0 Fig. 15 Chiller COP for Two Chillers 5064 kW, condenser water return temperature of 29°C, an overall chilled-water supply temperature set point of 7°C, and a chilled-water return temperature of 13°C. Figure 15 shows the COPs for the two chillers as a function load relative to their design loads for the given operating temperatures. Chiller 1 is more efficient at higher part-load ratios and less efficient at lower part-load ratios as compared with chiller 2. Solution: First, consider operating the chillers at equal part-load ratios. The ratio of the cooling load to the cooling capacity of the operating chillers is 5064/(4396 + 1934) = 0.8. From Equation (27), the individ- ual chiller loads are ⌀cha = 0.8(4396 kW) = 3517 kW 0 = 0.8(1934 kW) = 1547 kW ch,2 The power for each chiller is computed for the specified operating conditions with Equation (30) and the coefficients of Table 3. For the case of equal part-load ratios, the total chiller power consumption is Pch + Pch,2 = 649.7 kW + 292.2 kW = 941.9 kW = Pch,1 A second solution is determined for optimal chiller loads for the case of equal chilled-water temperature set points and controllable flow for each chiller. In this case, algebraic manipulation of Equa- tions (29) and (31) produces the following results for the individual chiller loads: a3,2 a3.1 +2a4,20load + a5.2 - a5.1 tcwr - tchws ⌀ch.1 2 a4.1 + a4,2 = 4277 kW ⌀ch.2 ch,1 = Qload Q = 787 kW | {}
e8184386-ffd4-43b5-a95b-a49398948d68 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Supervisory Control Strategies and Optimization 43.19 The resulting power consumption is then Pch ch,1 ch,2 = 688.9 kW + 222.2 kW = 910.8 kW = P + P Optimal loading of the chillers reduces overall chiller power con- sumption by about 4% through heavier loading of chiller 1 and lighter loading of chiller 2 (see Figure 15). Finally, optimal chiller loading is determined for the case where the individual loadings are controlled by using different chilled-water temperature set points (individual flow is not controllable). To apply Equations (32) and (33), the relative chilled-water flow rate for each chiller must be known. For this example, the relative flow for the ith chiller is assumed to be equal to the ratio of its design capacity to the design capacity for the operating chillers, so that 0 ch,des,1 4396 fFA = = 0.694 0 ch,des,1 + 0 4396 + 1934 ch,des,2 Q ch,des,2 4396 fF.2 = = 0.306 4396 + 1934 0 + Q ch,des,1 ch,des,2 Then, solving Equations (29) and (32) leads to the following results for the individual chiller loads: A2 -A1 + B2Q load ⌀"cha = = 4034 kW B1 + B2 ⌀ch,2 = Qload - �ch,1 = 1030 kW These loads lead to a total chiller power consumption of Pch ch,1 ch,2 = P + P = 705.8 kW + 216.4 kW = 922.2 kW Individual chilled-water set points are determined from Equation (32) and are 6.1 and 9°C for chillers 1 and 2, respectively. Power consump- tion has increased slightly from the case of identical chiller set points and variable flow. Note that changing either flows or chilled-water set points compli- cates overall system control as compared with loading the chillers with fixed part-load ratios, and leads to relatively small savings. Order for Bringing Chillers Online and Off-Line For chillers with similar efficiencies, the order in which chillers are brought online and off-line may be dictated by their cooling capacities and the desire to provide even runtimes. However, when- ever beneficial and possible, chillers should be brought online in an order that minimizes the incremental increase in energy consump- tion. At a given condition, the power consumption of any chiller can be evaluated using the correlation given by Equation (30), where the coefficients are determined using manufacturers' data or in situ measurements. Then, the overall power consumption for all operat- ing chillers is N P = P ch ch,i i=1 (34) When additional chiller capacity is required (see the section on Load Conditions for Bringing Chillers Online or Off-Line), the pro- jected power of all valid chiller combinations should be evaluated using Equation (30), with the projected load determined by Equation (27) for chillers with similar performance characteristics, or the solu- tion of Equations (28) subject to the constraint in Equation (29) for chillers with significantly different performance characteristics. Valid chiller combinations involve chillers that are not in alarm or locked out, and with load ratios between a low limit (e.g., 30%) and 100%. The best chiller combination to bring on line should result in the smallest increase (or largest decrease) in overall chiller power consumption as estimated with Equations (34) and (30) with chiller loading determined as outlined in the previous section. For systems with dedicated chilled-water and condenser water pumps and/or cooling towers, the associated power of this equipment should be added to Equation (30) to estimate the load of the chiller plus its aux- iliary equipment. It is recommended that these estimates be per- formed online using in-situ measurements of each chiller' s discharge chilled-water temperature and entering condenser water temperature, and the projected load of the chiller. A chiller should be shut down when its load drops below the spare capacity load ofthe current num- ber of online chillers; for a primary/secondary chilled-water system, the primary chilled-water flow will remain above the secondary chilled-water flow once the chiller is shut down. (The spare capacity load is equal to the rated capacity of the online chillers minus the actual measured load of the online chillers.) For chillers with similar design cooling capacities, a simpler (although suboptimal) approach can be used for determining the order for bringing chillers online and off-line. In this case, the chiller with the highest peak COP can be brought online first, fol- lowed by the second most efficient chiller, etc., and then brought off-line in reverse order. The maximum COP for each chiller can be evaluated using manufacturers' design and part-load data or from curve-fits to in-situ performance. The chiller load associated with maximum COP for each chiller can be determined by applying a first-order condition for a maximum, using Equation (30) and the definition of COP. For this functional form, the maximum (or possibly minimum) COP occurs for 2 + a2,i tewr aoj + alj tewr - tchws - tchws 0 ch,i N a4,i (35) The load determined from Equation (35) yields a maximum COP whenever it is real and bounded between upper and lower limits. Otherwise, it can be assumed that the maximum COP occurs at full load conditions. Typically, the maximum COP for centrifugal chillers occurs between about 40 and 80% and, for small multi- compressor or inverter drive chillers, between 15 and 40% of design load. COP increases as the temperature difference between the con- denser leaving water and chilled-water supply decreases. Equation (35) could be applied online to determine the rank ordering of chillers to bring online as a function of operating temperatures. However, itis often sufficient to use Equation (35) at the design tem- perature difference and establish a chiller sequencing order at the design or commissioning stage. Example 4. Determine the loads for maximum COP for two different chillers at a chilled-water set point of 7°C and a condenser water return temperature of 27°C. Table 4 gives the design cooling capacities and coefficients of the curve-fit of Equation (30) for the two chillers. Figure 16 shows the COPs of the two chillers determined from the correlations as a function of relative load (PLR) and temperature difference (tewr - tchws). These chillers have identical performance at design conditions, but very different part-load characteristics because of different methods used for capacity control. Solution: Loading associated with the maximum COP for each chiller is deter- mined using Equation (35) and the coefficients of Table 4. Power for each chiller is then determined using Equation (30) and the COP fol- lows directly. Results of the calculations are given in Table 5. The maximum COP for chiller A is about 20% greater than that for chiller B at the specified operating temperatures and should be brought online first. Inc. ASHRAE, 2019 user. single for Licensed | {}
814f7250-28a2-4818-8ad4-80f09731171d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 43.20 2019 ASHRAE Handbook- -HVAC Applications (SI) Chart Title: CHILLER A X-Axis: PLR Y-Axis: COP Chart Type: line 0.30 0.40 0.50 0.60 0.70 0.80 0.90 1.00 item_01 1.0Kelvin (K) 2.0Kelvin (K) 4.0Kelvin (K) 5.0Kelvin (K) 6.0Kelvin (K) 7.0Kelvin (K) 8.0Kelvin (K) 9.0Kelvin (K) Fig. 16 Chiller A and B Performance Characteristics for Maximum COP, Example 4 Table 4 Chiller Characteristics for Maximum COP, Example 4 ¦ Variable ¦ Unit ¦ Chiller A ¦ Chiller B ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 0 ch,des,i ¦ MW ¦ 19.07 ¦ 19.07 ¦ ¦ aoj ¦ kW ¦ 262.6 ¦ 187.2 ¦ ¦ alj ¦ kW/K ¦ -45.65 ¦ 173.1 ¦ ¦ a2.i ¦ kW/K2 ¦ 3.149 ¦ -1.398 ¦ ¦ a3.i ¦ kW/kW ¦ -0.007 301 ¦ -0.1227 ¦ ¦ a4,i ¦ kW/kW2 ¦ 0.000 003 271 ¦ 0.000 008 944 ¦ ¦ as.i ¦ kW/(kW·K) ¦ 0.002 707 ¦ -0.002 322 ¦ Table 5 Results for Maximum COP, Example 4 ¦ Variable ¦ Chiller A ¦ Chiller B ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 0 ch,i ¦ 13.65 MW ¦ 18.59 MW ¦ ¦ PLRi ¦ 0.716 ¦ 0.975 ¦ ¦ Pch.i ¦ 1857 kW ¦ 3038 kW ¦ ¦ COPi ¦ 7.35 ¦ 6.12 ¦ Load Conditions for Bringing Chillers Online or Off-Line In general, chillers should be brought online at conditions where the total power (including pumps and tower or condenser fans) of operating with the additional chiller would be less than without it. Conversely, a chiller should be taken off-line when the total power of operating with that chiller would be less than with it. In practice, the switch point for bringing a chiller online should be greater than that for bringing that same chiller off-line (e.g., 10%), to ensure sta- ble control. The optimal sequencing of chillers depends primarily on their part-load characteristics and the manner in which the chiller pumps are controlled. Dedicated Pumps. Where individual condenser and chilled- water pumps are dedicated to the chiller, Braun et al. (1989b) and Hackner et al. (1985) showed that a chiller should be brought online when the operating chillers reach their capacity. This conclusion is the result of considering both the chiller and pumping power in de- termining optimal control. Ifpumping power is ignored, the optimal chiller sequencing occurs when chiller efficiency is maximized at each load. Because maximum efficiency often occurs at part-load conditions, the optimal point for adding or removing chillers may occur when chillers are operating at less than their capacity. How- ever, the additional pumping power required for bringing additional pumps online with the chiller usually offsets any reductions in over- all chiller power consumption associated with part-load operation. When pumps are dedicated to chillers, situations may arise where chillers are operating at less than their capacity but chilled- water flow to the cooling coils is insufficient to meet the building load. This generally results from inadequate design or improper maintenance. Under these circumstances, either some zone condi- tions need to float to reduce the chilled-water set point (if possible), or an additional chiller needs to be brought online. Monitoring the zone air-handler conditions is one way to detect this situation. If (1) the chilled-water set point is atits lower limit, (2) any air-handler water control valves are saturated at 100% open, and (3) their cor- responding discharge air temperatures are significantly greater (e.g., 1 K) than set point, then the chilled-water flow is probably insufficient and an additional chiller/pump combination could be brought online. One advantage of this approach is that it is consis- tent with the reset strategies for both fixed- and variable-speed chilled-water systems. Chillers can be brought online or off-line with the following logic: 1. Evaluate the time-averaged values of the chilled-water supply temperature and overall cooling load over a fixed time interval (e.g., 5 min). 2. If the chilled-water supply temperature is significantly greater than the set point (e.g., 0.5 K), then bring the next chiller online. Otherwise, go to step 3. 3. Determine the time-averaged position of the cooling-coil water valves and corresponding discharge air temperatures for "repre- sentative" air handlers. 4. If (a) the chilled-water supply set point is at its lower limit, (b) more than one valve is saturated at 100% open, and (c) their cor- responding discharge air temperatures are significantly greater than set point (e.g., 0.5 K), then bring another chiller/pump com- bination online. Otherwise, go to step 5. 5. Ifthe cooling load is significantly less (e.g., 10%) than the value associated with the first time interval after the last chiller was brought online, then take that chiller off-line. Nondedicated Pumps. For systems without dedicated chiller pumps (e.g., variable-speed primary systems), the optimal load conditions for bringing chillers online or off-line do not generally occur at full chiller capacity. In determining optimal chiller switch points, ideally both chiller and pumping power should be consid- ered because pressure drop characteristics and pumping change when a chiller is brought online or off-line. However, approximate values of optimal switch points may be estimated by considering only chiller power. A chiller should be brought online whenever it would reduce the overall chiller power or if the current chillers can no longer meet the Inc. ASHRAE, 2019 user. single for Licensed | {}
ed96fc1e-211a-48b6-b082-40a5e0343dd9 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Supervisory Control Strategies and Optimization load (see previous section). A chiller should be added if the power consumption associated with (N + 1) chillers is significantly less (e.g., 5%) than the current N chillers, with both conditions evaluated using Equation (34) with correlations of the form given in Equation (30), and sequencing and loading determined as outlined in previous sections. Conversely, a chiller should be removed if the power con- sumption associated with the (N - 1) chillers is significantly less (e.g., 5%) than the current N chillers. The decision to add or remove chillers is readily determined using the current load and operating temperatures. 3.5 SIMPLIFIED STATIC OPTIMIZA TION OF COOLING PLANTS Optimal supervisory control of cooling equipment may involve determining the control that minimizes the total operating cost. For an all-electric system without significant storage, cost optimization leads to minimization of power at each instant in time. Optimal control depends on time, albeit indirectly through changing cooling requirements and ambient conditions. In this section, the static optimization methods described in the Methods section are simpli- fied and applied to cooling. Simplified System-Based Optimization Approach The component-based optimization method presented by Braun et al. (1989a) described in the Methods section was used to develop a simpler method for determining optimal control. The method involves correlating overall cooling plant power consumption using a quadratic functional form. Minimizing this function leads to linear control laws for control variables in terms of uncontrolled variables. The technique may be used to tune parameters of the cooling tower and chilled-water reset strategies presented in the section on Super- visory Control Strategies. It may also be used to define strategies for supply air temperature reset for VA V systems and flow control for variable-speed condenser water pumps. In the vicinity of any optimal control point, plant power con- sumption may be approximated as a quadratic function of the continuous control variables for each of the operating modes (i.e., discrete control mode). A quadratic function also correlates power consumption in terms of uncontrolled variables (i.e., load, ambient temperature) over a wide range of conditions. This leads to the fol- lowing general functional relationship between overall cooling plant power and the controlled and uncontrolled variables: J(f, M, u) = uT Au + bTu + f『Cf+ dTf+ fT Eu + g where J is the total plant power, u is a vector of continuous and free control variables, fis a vector of uncontrolled variables, M is a vec- tor of discrete control variables, and the superscript T designates the transpose operator. A, C, and E are coefficient matrices, b and d are coefficient vectors, and g is a scalar. The empirical coefficients of this function depend on the operating modes so that these constants must be determined for each feasible combination of discrete con- trol modes, M. (36) A solution for the optimal control vector that minimizes power may be determined analytically by applying the first-order condi- tion for a minimum. Equating the Jacobian of Equation (36) with respect to the control vector to zero and solving for the optimal con- trol set points gives where u* = k + Kf k =-A-1b/2 K =-A-1E/2 (37) The cost associated with unconstrained control of Equation (37) is (38) (39) 43.21 J* = f T f + T f + T (40) where = KT Ak + EK + C (41) = 2KAk + Kb + Ek + d T = KT Ak + bT k + g The control defined by Equation (37) results in a minimum power consumption if A is positive definite. If this condition holds and if the system power consumption is adequately correlated with Equation (36), then Equation (37) dictates that the optimal continuous, free control variables vary as a nearly linear function of the uncontrolled variables. However, a different linear relationship (i.e., different A, C, E, b, d, and g) applies to each feasible combi- nation of discrete control modes defined by M. The minimum cost associated with each mode combination must be computed from Equation (40) and compared to identify the global minimum. Uncontrolled v ariables. As mentioned, optimal control variables primarily depend on ambient wet-bulb temperature (or dry-bulb temperature in the case of air-cooled chillers) and total chilled-water load. The load affects the heat transfer requirements for all heat exchangers, whereas the wet-bulb temperature affects chilled- and condenser water temperatures necessary to achieve a given heat transfer rate. As discussed in the section on Supervisory Control Strategies, cooling coil heat transfer depends on the coil entering wet-bulb temperature. However, this reduces to an ambi- ent wet-bulb temperature dependence for a given ventilation mode (e.g., minimum outdoor air or economizer) and fixed zone condi- tions. Thus, separate cost functions are necessary for each ventilation mode, with load and ambient wet bulb as uncontrolled variables. Alternatively, for a specified ventilation strategy (e.g., the economizer strategy from the section on Supervisory Control Strategies), three uncontrolled variables could be used for all ven- tilation modes: load, ambient wet-bulb temperature, and average cooling-coil inlet wet-bulb temperature. For radiant cooling systems, if latent cooling is handled by pack- age dehumidifying equipment (e.g., a dedicated outdoor air system), the chilled-water set point can be raised well above what is needed for dehumidification and the main chiller will operate more efficient- ly. Gayeski et al. (2011a) and Katipamula et al. (2010a) show that part-load efficiency may benefit greatly from using optimal chilled- water flow rate and temperature in response to part-load ratio. Additional uncontrolled variables that could be important if var- ied over a wide range are the individual-zone latent-to-sensible load ratios and the ratios of individual sensible zone loads to the total sensible loads for all zones. However, these variables are difficult to determine from measurements and are of secondary importance. (42) (43) Free Control Variables. The number of independent or "free" control variables in the optimization can be reduced significantly by using the simplified strategies presented in the section on Supervi- sory Control Strategies. For instance, the optimal static pressure set point for a VA v system should keep at least one VA v box fully open and should not be considered as a free optimization variable. Simi- larly, supply air temperature for a constant-air-volume (CAV) system should be set to minimize reheat. Additional near-optimal guidelines were presented for sequencing of cooling tower fans, sequencing of chillers, loading of chillers, reset of pressure differ- ential set point for variable-speed pumping, and chilled-water reset with fixed-speed pumping. Furthermore, Braun et al. (1989b) showed that using identical supply air set points for multiple air han- dlers gives near-optimal results for VA v systems. For all variable-speed auxiliary equipment (i.e., pumps and fans), the free set-point variables to use in Equation (1) could be reduced to the following: (1) supply air set temperature, (2) chilled-water set Inc. ASHRAE, 2019 user. single for Licensed | {}
a9ad1808-a429-4cbc-b3ce-3aa865f78a05 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 43.22 temperature, (3) tower airflow relative to design capacity, and (4) condenser water flow relative to design capacity. All other continu- ous supervisory control variables are dependent on these variables with the simplified strategies presented in the section on Supervisory Control Strategies. Some of the dependent control variables may be discrete control variables. For instance, variable-flow pumping may be imple- mented with multiple fixed- and variable-speed pumps, where the number of operating pumps is a discrete variable that changes when a variable-speed pump reaches its capacity. These discrete changes could lead to discrete changes in cost because of changes in overall pump efficiency. However, this has a relatively small effect on over- all power consumption and may be neglected in fitting the overall cost function to changes in the control variables. Some discrete control variables may also be independent vari- ables. In general, different cost functions arise for all operating modes consisting of each possible combination of discrete control variables. With all variable-speed pumps and fans, the only signifi- cant discrete control variable is the number of operating chillers. Then, optimization involves determining optimal values of only four continuous control variables for each of the feasible chiller modes. A chiller mode defines which of the available chillers are to be online. The chiller mode giving the minimum overall power con- sumption represents the optimum. For a chiller mode to be feasible, the specified chillers must operate safely within their capacity and surge limits. In practice, avoid abrupt changes in the chiller modes; large chillers should not be cycled on or off except when the savings associated with the change are significant. Using fixed-speed equipment reduces the number of free contin- uous control variables. For instance, supply air temperature is removed as a control variable for CA v systems, and chilled-water temperature is not included for fixed-speed chilled-water pumping. However, for multiple chilled-water pumps not dedicated to chillers, the number of operating pumps can become a free discrete control variable. Similarly, for multiple fixed-speed cooling tower fans and condenser water pumps, each of the discrete combinations can be considered as a separate mode. However, for multiple cool- ing tower cells with multiple fan speeds, the number of possible combinations may be large. A simpler approach that works satisfac- torily is to treat relative flows as continuous control variables during the optimization and to select the discrete relative flow that is closest to the optimal value. At least three relative flows (discrete flow modes) are necessary for each chiller mode to fit the quadratic cost function. The number of possible sequencing modes for fixed-speed pumps is generally much more limited than that for cooling tower fans, with two or three possibilities (at most) for each chiller mode. In fact, with many current designs, individual pumps are physically coupled with chillers, and it is impossible to operate more or fewer pumps than the number of operating chillers. Thus, it is generally best to treat the control of fixed-speed condenser water pumps with a set of discrete control possibilities rather than use a continuous control approximation. Training. The coefficients of Equation (36) must be determined empirically, and a variety of approaches have been proposed. One approach is to apply regression techniques directly to measurements oftotal power consumption. Because the cost function is linear with respect to the empirical coefficients, linear regression techniques may be used. A set of experiments can be performed over the expected range of operating conditions. Large amounts of data that include the entire range must be taken to account for measurement uncertainty. The regression could possibly be performed online using least-squares recursive parameter updating (Ljung and Soder- strom 1983). However, precautions should be taken to ensure that the matrix A is positive definite, which guarantees a minimum. If system power is relatively "flat, automated methods could generate 2019 ASHRAE Handbook-HVAC Applications (SI) coefficients that produce a maximum in power consumption rather than a minimum (Brandemuehl and Bradford 1998). Rather than fitting empirical coefficients ofthe system-cost func- tion of Equation (36), the coefficients of the optimal control Equa- tion (37) and the minimum-cost function of Equation (40) may be estimated directly. At a limited set of conditions, optimal values of the continuous control and free variables may be estimated through trial-and-error variations. Only three independent conditions are necessary to determine coefficients of the linear control law given by Equation (37) if the load and wet bulb are the only uncontrolled variables. The coefficients of the minimum cost function can then be determined from system measurements with the linear control law in effect. The disadvantage of this approach is that there is no direct way to handle physical constraints on the controls. Summary and Constraint Implementation. The methodology for determining the near-optimal control of a chilled-water system may be summarized as follows: 1. Change the chiller operating mode if system operation is at the limits of chiller operation (near surge or maximum capacity). 2. For the current set of conditions (load and wet bulb), estimate the feasible modes of operation M that avoid operating the chiller and condenser pump at their limits. 3. For the current operating mode, determine optimal values of the continuous controls using Equation (37). 4. Determine a constrained optimum if controls exceed their bounds. 5. Repeat steps 3 and 4 for each feasible operating mode. 6. Change the operating mode if the optimal cost associated with the new mode is significantly less than that associated with the current mode. 7. Change the values of the continuous control variables. When treating multiple-speed fan control with a continuous variable, use the discrete control closest to the optimal continuous value. Ifthe linear optimal control Equation (37) is directly determined from optimal control results, then the constraints on controls may be handled directly. Otherwise, a simple solution is to constrain the individual control variables as necessary and neglect the effects of the constraints on the optimal values of the other controls and the minimum cost function. The variables of primary concern for con- straints are the chilled-water and supply air set temperatures. These controls must be bounded for proper comfort and safe operation of the equipment. On the other hand, cooling tower fans and condenser water pumps should be sized so the system performs efficiently at design loads, and constraints on control of this equipment should only occur under extreme conditions. The optimal value of the chilled-water supply temperature is coupled to the optimal value ofthe supply air temperature, so decou- pling these variables in evaluating constraints is generally not justified. However, optimization studies indicate that when either control is operated at a bound, the optimal value of the other free control is approximately bounded at a value that depends only on the ambient wet-bulb temperature. The optimal value of this free control (either chilled-water or supply air set point) may be esti- mated at the load at which the other control reaches its limit. Coupling between optimal values of the chilled-water and con- denser water loop controls is not as strong; interactions between constraints on these variables may be neglected. Case Studies. Braun et al. (1987) correlated the power consump- tion of the Dallas-Ft. Worth airport chiller, condenser pumps, and cooling tower fans with the quadratic cost function given by Equation (40) and showed good agreement with data. Because the chilled-water loop control was not considered, the chilled-water set point was treated as a known uncontrolled variable. The discrete con- trol variables associated with the four tower cells with two-speed fans and the three condenser pumps were treated as continuous con- trol variables. The optimal control determined by the near-optimal Inc. ASHRAE, 2019 user. single for Licensed | {}
6aec470d-f3b7-4f2e-9d26-002433fb9446 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Supervisory Control Strategies and Optimization 43.23 Equation (37) also agreed well with that determined using a nonlin- ear optimization applied to a detailed simulation of the system. In subsequent work, Braun et al. (1989a) considered complete system simulations (cooling plant and air handlers) to evaluate the performance of the quadratic, system-based approach. Several dif- ferent system characteristics were considered. Figures 6, 11, 17, and 18 show comparative results between the controls as deter- mined with the component- and system-based methods for a range of loads, for a relatively low and high ambient wet-bulb tempera- ture (16 and 27°C). In Figures 11 and 17, optimal values of the chilled-water and supply air temperatures are compared for a system with variable air and water flow. The near-optimal control equation provides a good fit to the optimization results for all conditions considered. The chilled-water temperature was constrained between 3 and 13°C, while the supply air set point was allowed to float freely. Figures 11 and 17 show that, for the conditions where the chilled-water tem- perature is constrained, the optimal supply air temperature is also nearly bounded at a value that depends on the ambient wet bulb. X-Axis: Relative Chilled-Water Load Y-Axis: Optimal Supply Air Temperature, °C Chart Type: line OPTIMAL NEAR-OPTIMAL LOW WET BULB HIGH WET BULB item_01 16°C 14°C 12°C 10°C Fig. 17 Comparisons of Optimal Supply Air Temperature X-Axis: RELATIVE CHILLED-WATER LOAD Y-Axis: OPTIMAL RELATIVE CONDENSER WATER FLOW Chart Type: line Black Red Green Blue item_01 0.2 0.3 0.4 0.8 Fig. 18 Comparisons of Optimal Condenser Pump Control Optimal relative cooling tower air and condenser water flow rates are compared in Figures 6 and 18 for a system with variable- speed cooling tower fans and condenser water pumps. Although the optimal controls are not exactly linear functions of the load, the linear control equation provides an adequate fit. The differences in these controls result in insignificant differences in overall power consumption, because, as discussed in the background section, the optimum is extremely flat with respect to these variables. The nonlinearity of the condenser loop controls is partly caused by the constraints imposed on the chilled-water set temperature. However, this effect is not very significant. Figures 6 and 18 also suggest that the optimal condenser loop control is not very sensitive to ambient wet-bulb temperature. Static Optimization for Cooling Plants The cooling system shown in Figure 1 depicts multiple chillers, cooling towers, and pumps providing chilled water to air-handling units to cool air that is supplied to building zones. Although cooling needs at any given time may be met with different modes of operation and set points only one set of controls and mode results in minimum power consumption. This optimal control point results from trade-offs between the energy consumption of dif- ferent components. Forinstance, increasing the number of cooling towercells (or increasing fan speeds) increases fan power but reduces chiller power because the temperature of the water supplied to the chiller's condenser is decreased. Similarly, increasing condenser water flow by adding pumps (or increasing pump speed) decreases chiller power but increases pump power. Similar trade-offs exist for the chilled-water loop variables of systems with variable-speed chilled-water pumps and air handler fans. For instance, increasing the chilled-water set point reduces chiller power but increases pump power because greater flow is needed to meet the load. Increasing the supply air set point increases fan power, but decreases pump power. Figure 19 shows the sensitivity ofthe total power consumption to condenser water-loop controls (from Braun et al. [1989b]) for a single chiller load, ambient wet-bulb temperature, and chilled-water supply temperature. Contours of constant power consumption are plotted versus cooling tower fan and condenser water pump speed for a system with variable-speed fans and pumps. Near the optimum, power consumption is not sensitive to either of these con- trol variables, but increases significantly away from the optimum. The rate of increase in power consumption is particularly large at low condenser pump speeds. A minimum pump speed is necessary X-Axis: RELATIVE CONDENSER PUMP SPEED Y-Axis: RELATIVE COOLING TOWER PAN SPEEDS Chart Type: line (5) > MINIMUM (1) > MINIMUM (10) > MINIMUM (25) > MINIMUM item_01 0.9 0.6 0.4 1.0 Fig. 19 Example Chiller Plant Power Contours for Condenser-Loop Control Variables Inc. ASHRAE, 2019 user. single for Licensed | {}
9bffcb39-2de0-4496-9d29-059bb8e00af1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 43.24 Chart Type: line (10) > MINIMUM (25) > MINIMUM (1) > MINIMUM MINIMUM (5) > MINIMUM item_01 10°C 12°C 15°C 13°C 10°C Fig. 20 Example Chiller Plant Power Contours for Chilled- Water and Supply Air Temperatures to overcome the static pressure associated with the height of the water discharge in the cooling tower above the sump. As the pump speed approaches this value, condenser flow approaches zero and chiller power increases dramatically. A pump speed that is too high is generally better than one that is too low. The broad area near the optimum indicates that, for a given load, the optimal setting does not need to be accurately determined. However, optimal settings change significantly when there are widely varying chiller loads and ambi- ent wet-bulb temperature. Figure 20 shows the sensitivity of power consumption to chilled- water and supply air set-point temperatures for a system with variable-speed chilled-water pumps and air handler fans (Braun et al. 1989b). Within about 2 K of the optimum values, power consump- tion is within 1% of the minimum. Outside this range, sensitivity to the set points increases significantly. The penalty associated with operation away from the optimum is greater in the direction of smaller differences between the supply air and chilled-water set points. As this temperature difference is reduced, the required flow of chilled water to this coil increases and the chilled-water pumping power is greater. For a given chilled-water or supply air temperature, the temperature difference is limited by the heat transfer characteris- tics of the coil. As this limit is approached, the required water flow and pumping power would become infinite if the pump speed were not constrained. It is generally better to have too large rather than too small a temperature difference between the supply air and chilled- water set points. For constant chilled-water flow, trade-offs in energy use with chilled-water set point are very different than for variable-flow systems. Increasing the chilled-water set point reduces chiller power consumption, but has little effect on chilled-water pumping energy. Therefore, the benefits of chilled-water temperature reset are more significant than for variable-flow systems (although variable-flow systems use less energy). For constant chilled-water flow, the minimum-cost strategy is to raise the chilled-water set point to the highest value that will keep all discharge air tempera- tures at their set points and keep zone humidities within acceptable bounds. For constant-volume (CAV) air-handling systems, trade-offs in energy use with supply air set point are also very different than for variable-air-volume systems. Increasing the supply air set point for cooling reduces both the cooling load and reheat required, but does not change fan energy. Again, the benefits of supply air temperature 2019 ASHRAE Handbook-HVAC Applications (SI) X-Axis: RELATIVE CHILLED-WATER LOAD Y-Axis: OPTIMAL SYSTEM COP Chart Type: line 0. 0.2 0.3 0.4 0.5 0.6 0.7 0.8 0.9 1.0 item_01 5.5 5.0 4.8 4.5 3.8 3.4 3.5 3.2 2.8 2.5 Fig. 21 Example of Effect of Chiller and Pump Sequencing on Optimal Performance reset for CAV systems are more significant than for VAV systems (although VAV systems use less energy). In general, the set point for a CA v system should be at the highest value that will keep all zone temperatures at their set points and all humidities within acceptable limits. In addition to the set points used by local-loop controllers, some operational modes can affect performance. For instance, significant energy savings are possible when a system is properly switched over to an economizer cycle. At the onset of economizer operation, return dampers are closed, outdoor air dampers are opened, and the maximum possible outdoor air is supplied to cooling coils. Two dif- ferent types of switchover are typically used: (1) dry-bulb and (2) enthalpy. With a dry-bulb economizer, the switchover occurs when the ambient dry-bulb temperature is less than a specified value, typ- ically between 13 and 18°C. With an enthalpy economizer, the switchover typically happens when the outdoor enthalpy (or wet- bulb temperature) is less than the enthalpy (or wet-bulb temperature) of the return air. Although the enthalpy economizer yields lower overall energy consumption, it requires wet-bulb tem- perature or dry-bulb and relative humidity measurements. Another important operation mode is the sequencing of chillers and pumps. Sequencing defines the order and conditions associated with bringing equipment online or off-line. Optimal sequencing depends on the individual design and part-load performance char- acteristics of the equipment. For instance, more-efficient chillers should generally be brought online before less-efficient ones. Fur- thermore, the conditions where chillers and pumps should be brought online depend on their performance characteristics at part- load conditions. Figure 21 shows an example of optimal system performance (i.e., optimal set-point choices) for different combinations of chillers and fixed-speed pumps in parallel as a function of load relative to the design load for a given ambient wet-bulb temperature. For this system (from Braun et al. [1989b]), each component (chillers, chilled-water pumps, and condenser water pumps) in each parallel set is identical and sized to meet half ofthe design requirements. The best performance occurs at about 25% of the design load with one chiller and pump operating. As load increases, system COP decreases because of decreasing chiller COP and a nonlinear increase in the power consumption of cooling tower and air handler fans. A second chiller should be brought online at the point where the overall COP ofthe system is the same with or without the chiller. For this system, this optimal switch point occurs at about 38% of the total design load or about 75% of the individual chiller's capacity. The Inc. ASHRAE, 2019 user. single for Licensed | {}
b4b5dea4-3216-49a2-8956-562b0b5d6efc | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Supervisory Control Strategies and Optimization 43.25 optimal switch point for bringing a second condenser and chilled- water pump online occurs at a much higher relative chilled load (0.62) than the switch point for adding or removing a chiller (0.38). However, pumps are typically sequenced with chillers (i.e., they are brought online together). In this case, Figure 21 shows that the opti- mal switch point for bringing a second chiller online (with pumps) is about 50% of the overall design load or at the design capacity of the individual chiller. This is generally the case for sequencing chillers with dedicated pumps. In most cases, zone humidities are allowed to float between upper and lower limits dictated by comfort (see Chapter 9 of the 2017 ASHRAE Handbook-Fundamentals). However, VAV systems can control zone humidity and temperature simultaneously. For a zone being cooled, equipment operating costs are minimized when the zone temperature is at the upper bound of the comfort region. How- ever, operating simultaneously at the upper limit of humidity does not minimize operating costs. Figure 22 shows an example compar- ison of system COP and zone humidity associated with fixed and free-floating zone humidity as a function of the relative load (from Braun et al. [1989b]). Over the range of loads, allowing the humidity to float within the comfort zone produces a lower cost and zone humidity than setting the humidity at the highest acceptable value. The largest differences occur at the highest loads. Operation with the zone at the upper humidity bound results in lower latent loads than with a free-floating humidity, but this humidity control constraint requires a higher supply air temperature, which in turn results in greater air-handler power consumption. For minimum energy costs, the humidity should be allowed to float freely within the bounds of human comfort. Effects of Load and Ambient Conditions on Optimal Super- visory Control. When the ratio ofindividual zone loads to total load does not change significantly with time, the optimal control variables are functions of the total sensible and latent gains to the zones and of the ambient dry- and wet-bulb temperatures. For systems with wet cooling towers and climates where moisture is removed from condi- tioned air, the effect of the ambient dry-bulb temperature alone is small because air enthalpy depends primarily on wet-bulb tempera- ture, and the performance of wet-surface heat exchangers is driven primarily by the enthalpy difference. Typically, zone latent gains are on the order of 15 to 25% of the total zone gains, and changes in X-Axis: Relative Chilled-Water Load Y-Axis: Optimal System Cop Chart Type: line 0.3 0.4 0.5 0.6 0.7 0.8 0.9 0.10 item_01 5.5 5.0 4.5 4.0 3.5 3.0 2.5 2.0 Fig. 22 Example Comparison of Free-Floating and Fixed Humidity latent gains have a relatively small effect on performance for a given total load. Consequently, in many cases optimal supervisory control variables depend primarily on ambient wet-bulb temperature and total chilled-water load. However, load distributions between zones may also be important if they change significantly over time. Generally, optimal chilled-water and supply air temperatures decrease with increasing load for a fixed ambient wet-bulb tempera- ture and increase with increasing ambient wet-bulb temperature for a fixed load. Furthermore, optimal cooling tower airflow and con- denser water flow rates increase with increasing load and ambient wet-bulb temperature. Performance Comparisons for Supervisory Control Strate- gies. Optimization of plant operation is most important when loads vary and when operation is far from design conditions for a signifi- cant period. Various strategies are used for chilled-water systems at off-design conditions. Commonly, the chilled-water and supply air set-point temperatures are changed only according to the ambient dry-bulb temperature. In some systems, cooling tower airflow and condenser water flow are not varied in response to changes in the load and ambient wet-bulb temperature. In other systems, these flow rates are controlled to maintain constant temperature differences between cooling tower outlet and ambient wet-bulb temperature (approach) and between cooling tower inlet and outlet (range), re- gardless of load and wet-bulb temperature. Although these strategies seem reasonable, they do not generally minimize operating costs. Figure 23 shows a comparison of the COPs for optimal control and three alternative strategies as a function ofload for a fixed ambi- ent wet-bulb temperature. This system (from Braun et al. [1989b]) incorporated the use of variable-speed pumps and fans. The three strategies are · Fixed chilled-water and supply air temperature set points (4.5 and 11°C, respectively), with optimal condenser-loop control · Fixed tower approach and range (3 and 6.5 K, respectively), with optimal chilled-water loop control · Fixed set points, approach, and range Because the fixed values were chosen to be optimal at design con- ditions, differences in performance for all strategies are minimal at high loads. However, at part-load conditions, Figure 23 shows that the savings associated with the use of optimal control can become significant. Optimal control ofthe chilled-water loop results in great- er savings than that for the condenser loop for part-load ratios less than about 50%. The overall savings over a cooling season depend on COP SYSTEM OPTIMAL X-Axis: Relative Chilled-water Load Chart Type: line 0.2 0.4 0.6 0.8 1.0 item_01 6.5 5.8 5.0 4.8 3.5 Fig. 23 Comparisons of Optimal Control with Conventional Control Strategies Inc. ASHRAE, 2019 user. single for Licensed | {}
178d0abf-3e0a-47c2-a96a-81bd2554233c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 43.26 2019 ASHRAE Handbook-HVAC Applications (SI) the time variation ofthe load. Ifthe cooling load is relatively constant and near the design load, fixed values of temperature set points, ap- proach, and range could be chosen to give near-optimal performance. However, for typical building loads with significant daily and sea- sonal variations, the penalty for using a fixed set-point control strategy is typically in the range of5 to 20% ofthe cooling system en- ergy. Even greater energy savings are possible with economizer con- trol and discharge air temperature reset with constant-volume systems. Kao (1985) investigated the effect of different economizer and supply air reset strategies on both heating and cooling energy use for CAV, VAV, and dual-duct air-handling systems for four dif- ferent buildings. The results indicated that substantial improvements in a building' s energy use may be obtained. v ariable- Versus Fixed-Speed Equipment. Using variable- speed motors for chillers, fans, and pumps can significantly reduce energy costs but can also complicate the problem of determining optimal control. The overall savings from using variable-speed equip- ment over a cooling season depend on the time variation of the load. Typically, using variable-speed drives reduces equipment operating costs 20 to 50% compared to equipment with fixed-speed drives. Figure 24 gives the overall optimal system performance for a cooling plant with either variable- or fixed-speed, variable-vane con- trol of a centrifugal chiller. At part-load conditions, the system COP associated with using a variable-speed chiller is improved as much as 25%. However, the power requirements are similar at conditions associated with peak loads, because at full load the vanes are wide open and the speed under variable-speed control and fixed-speed operation is the same. The results in Figure 24 are from a single case study of a large chilled-water facility at the Dallas/Ft. Worth Airport (Braun et al. 1989b), constructed in the mid-1970s, where the exist- ing chiller was retrofitted with a variable-speed drive. Differences in performance between variable- and fixed-speed chillers may be smaller for current equipment. The most common design for cooling towers places multiple tower cells in parallel with a common sump. Each tower cell has a fan with one, two, or possibly three operating speeds. Although multiple cells with multiple fan settings offer wide flexibility in control, using variable-speed tower fans can provide additional im- provements in overall system performance. Figure 25 shows an example comparison of optimal performance for single-speed, two- speed, and variable-speed tower fans as a function of load for a given wet-bulb temperature for a system with four cells (Braun et al. 1989b). The variable-speed option results in higher COP under all conditions. In contrast, for discrete fan control, the tower cells are isolated when their fans are off and the performance is poorer. Be- low about 70% of full-load conditions, there is a 15% difference in total energy consumption between single-speed and variable-speed fans. Between two-speed and variable-speed fans, the differences are much smaller, about 3 to 5% over the entire range. Fixed-speed pumps that are sized to give proper flow to a chiller at design conditions are oversized for part-load conditions. Thus, the system will have higher operating costs than with a variable-speed pump of the same design capacity. Multiple pumps with different capacities have increased flexibility in control, and using a smaller fixed-speed pump for low loads can reduce overall power consump- tion. The optimal performance for variable-speed and fixed-speed pumps applied to both the condenser and chilled-water flow loops is shown in Figure 26 (Braun et al. 1989b). Large fixed-speed pumps were sized for design conditions; the small pumps were sized to have one-half the flow capacity of the large pumps. Below about 60% of full-load conditions, a variable-speed pump showed a significant improvement over the use of a single, large fixed-speed pump. With the addition of a small fixed-speed pump, improvements with the variable-speed pump were significant at about 40% of the maximum load. Fan energy consumed by VA V systems is strongly influenced by the device used to vary the airflow. Centrifugal fans with variable- speed drives typically provide the most energy-efficient performance. Brothers and Warren (1986) compared the fan energy consumption for a typical office building in various U.S. locations. The analysis focused on centrifugal and vaneaxial fans with three typical flow modulation devices: (1) dampers on the outlet side of the fan, (2) inlet vanes on the fan, and (3) variable-speed control of the fan motor. In all locations, the centrifugal fan used less energy than the vaneaxial fan. Vaneaxial fans have higher efficiencies at the full-load design point, but centrifugal fans have better off- design characteristics that lead to lower annual energy consumption. For a centrifugal fan, inlet vane control saved about 20% of the energy compared to damper control. Variable-speed control produced average savings of 57% compared to inlet vane control. Hybrid Cooling Plants. Hybrid cooling plants use a combina- tion of chillers that are powered by electricity and natural gas. Braun (2007a) developed a set of near-optimal operating strategies for hybrid cooling plants to reduce operating costs. Operating cost min- Fig. 24 Example of Optimal Performance for Variable- and Fixed-Speed Chillers X-Axis: Relative Chilled-Water Load Y-Axis: Optimal System Coop Chart Type: line 0.2 0.4 0.6 0.8 1.0 item_01 6.5 5.5 4.5 3.5 3 X-Axis: Relative Chilled-Water Load Y-Axis: Optimal System Cop Chart Type: line variable_speed_fans one_speed_fans two_speed_fans item_01 6 5 4 Fig. 25 Example Comparison of One-, Two-, and Variable- Speed Fans for Four-Cell Cooling Tower Inc. ASHRAE, 2019 user. single for Licensed | {}
38bc0ea4-19f3-4c29-a315-5cb485d7c86c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Supervisory Control Strategies and Optimization 43.27 imization for hybrid plants must account for effects of electrical and gas energy costs, electrical demand costs, and differences in main- tenance costs associated with different chillers. Control strategies for hybrid cooling plants were developed by separating hourly energy cost minimization from the problem of determining trade- offs between monthly energy and demand costs. A demand constraint was set for each month, based on a heuristic strategy, and energy cost optimal strategies that attempted to satisfy the demand constraint were applied for cooling tower and chiller control at each decision interval. Simulated costs associated with the individual control strategies compared well with costs for optimal control. Moreover, Braun (2007b) presented an algorithm for determining cooling tower fan settings in hybrid plants in response to loadings on individual chillers. Parameters of the algorithm were evaluated using design information for the chillers and cooling tower fans. In addition to reducing operating costs, use of the open- loop control strategy simplifies the control and improves the stability of tower control compared with using a constant condenser water supply or approach to wet-bulb. Simulated plant cooling costs associated with the algorithm were compared with costs for opti- mized settings, and were within 1% of the minimum costs. The developed control method is general, in the sense that it also applies to cooling plants that have all-electric or all-natural-gas chillers. 3.6 DYNAMIC OPTIMIZATION FOR COOLING USING DISCRETE STORAGE Thermal storage systems allow part or all of the cooling load to be shifted from on-peak to off-peak hours. Discrete cool storage systems typically use water or ice in unpressurized tanks as the thermal storage medium. Charging and discharging rates can be controlled from zero to a maximum design rate, which in some cases may equal the design load. In building structure (passive) storage, the building thermal mass is the storage medium; charging and discharging are accomplished by adjusting space temperatures over a relatively narrow range. Thermally active building systems (TABS), on the other hand, use structural elements with embedded pipes (e.g., radiant floor slabs) to promote controllable charging from within the mass. Conventional TABS relies on passive (uncontrolled) discharge. An active discharge mode has recently been demonstrated in a 250 m2 occupied building. Phase-change materials may be used to increase the capacity of passive or TAB systems. X-Axis: RELATIVE CHILLED-WATER LOAD Y-Axis: OPTIMAL SYSTEM COP Chart Type: line variable_speed_pump small_fixed_speed_pump item_01 6000 4000 Fig. 26 Example of Optimal Performance for Variable- and Fixed-Speed Chillers Utility incentives encouraging use of thermal storage are gener- ally in the form of time-varying energy and peak demand charges. The commercial consumer is charged more for energy during the daytime, and is also levied an additional charge each month based on the peak power consumption during the on-peak period. These incentives can be significant, depending on location, and are often the most important factor affecting an optimal control strategy for systems with thermal storage. Cooling Systems with Discrete Thermal Storage Chapter 51 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment describes several possible storage media and system configurations for discrete thermal storage. Figure 27 depicts a generic storage system coupled to a cooling system and a building load. The storage medium could be chilled water, ice or some other phase change material. Cooling equipment charges (operates at low temperatures to make ice) during unoccupied periods when the cost of electricity is low. During times of occupancy and higher electric rates, ice is melted (storage discharging) as the storage meets all or part of the building load in combination with the primary cooling equipment. Stratified water storage is charged and discharged from the bottom (cold end) ofthe tank, with water returning from the load to the top of the tank during discharge and returning from the top of the tank to the chiller during charging. The primary control variables for the thermal storage systems depicted in Figure 27 are the rate of (1) energy removal from storage by the cooling system (charging rate) and (2) energy addition because of the load (discharging rate). Determining the optimal charging and discharging rates differs considerably from determining optimal set points for cooling plants that do not have storage. With thermal storage, control decisions (i.e., charging and discharging rates) deter- mined for the current hour affect costs and control decisions for several hours in the future. Optimal control of thermal storage sys- tems involves finding a sequence of charging and discharging rates that minimizes the total cost of providing cooling over an extended period of time, such as a day, and requires forecasting and application of dynamic optimization techniques. Constraints include limits on charging and discharging rates. The optimal control sequence results from trade-offs between the costs of cooling the storage during off- peak hours and the cost of meeting the load during on-peak hours. Without utility incentives to use electricity at night, optimal control generally minimizes use ofice storage because the cooling equipment operates less efficiently while charging at low temperatures. For building thermal mass systems, precooling increases heat gains from ![image](/image/placeholder) HEAT GAINS DISCHARGE STORAGE BUILDING CHARGE DIRECT COOLING PRIMARY COOLING EQUIPMENT HEAT REJECTION TO AMBIENT Fig. 27 Generic Storage System for Cooling (Arrows Show Direction of Heat Flow) Inc. ASHRAE, 2019 user. single for Licensed | {}
ee692db8-6c65-45c9-bc51-a6bec81906a0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 43.28 2019 ASHRAE Handbook-HVAC Applications (SI) ![image](/image/placeholder) / CHILLED-WATER/GYCOL chwr PUMPS COOLING COOLING EVAPORATORS CONDENSERS TOWERS CHILLERS COILS STORAGE CONTROL VALVE (V-1) T coil 7 chws BYPASS CONDENSER LOAD VALVE (V-2) WATER PUMPS STORAGE Fig. 28 Schematic of an Ice Storage System the ambient to the building. Close attention to system design and supervisory control is essential if this penalty is to be offset by poten- tially more efficient operation of the chiller at higher chilled-water and lower average heat rejection (night operation) temperatures. Online optimal control of thermal storage, like other HVAC optimal control schemes, is rarely implemented because of the high initial costs associated with sensors (e.g., power) and software implementation. However, heuristic control strategies have been developed that provide near-optimal performance under most cir- cumstances. The following sections provide background on developing control strategies for ice storage and building thermal mass. Detailed descriptions of some specific control strategies are given in the Supervisory Control Strategies section of this chapter. Ice Storage. This section emphasizes ice storage applications, although much of the information applies to chilled-water storage as well. Figure 28 shows a schematic of a typical ice storage system. The system consists of one or more chillers, cooling tower cells, condenser water pumps, chilled-water/glycol distribution pumps, ice storage tanks, and valves for controlling charging and discharging modes of operation. Ice is made at night and used during the day to provide part of a building's cooling requirements; the storage is not sized to handle the full on-peak load requirement on the design day. Typically, in a load-leveling scheme, the storage and chiller capacity are sized such that chiller operates at full capacity during the on-peak period on the design day. Typical modes of operation for the system in Figure 28 are as follows: · Storage charging mode: Typically, charging (i.e., ice making) only occurs when the building is unoccupied and off-peak electric rates are in effect. In this mode, the load bypass valve V-2 is fully closed to the building cooling coils, the storage control valve V-1 is fully open to the ice storage tank (the total chilled-water/glycol flow is through the tank), and the chiller produces low tempera- tures (e.g., -7°C) sufficient to make ice within the tank. · Storage discharging mode: Discharging of storage (i.e., ice melting) only occurs when the building is occupied. In this mode, valve V-2 is open to the building cooling coils and valve V-1 mod- ulates the mixture of flows from the storage tank and chiller to maintain a constant supply temperature to the building cooling coils (e.g., 3°C). Individual valves at the cooling coils modulate their chilled-water/glycol flow to maintain supply air tempera- tures to the zones. · Direct chiller mode: The chiller may operate to meet the load directly without using storage during the occupied mode (typi- cally when off-peak electric rates are in effect). In this mode, valve V-1 is fully closed with respect to the storage tank. For a typical partial-storage system, the storage meets only a por- tion of the on-peak cooling loads on the design day and the chiller operates at capacity during the on-peak period. Thus, the peak power is limited by the capacity of the chiller. For off-design days, there are many different control strategies that meet the building's cooling requirements. However, each method has a different overall operating cost. The best control strategy for a given day is a function of several factors, including utility rates, load profile, chiller characteristics, storage characteristics, and weather. For a utility rate structure that includes both time-of-use energy and demand charges, the optimal strategy can depend on variables that extend over a monthly time scale. Consider the charges typically associated with electrical use within a building. The first charge is the total cost of energy use for the building over the billing period, which is usually a month. Typi- cally, the energy cost rate varies according to time of use, with high rates during the daytime on weekdays and low costs at night and on weekends. The second charge, the building demand cost, is the prod- uct of the peak power consumption during the billing period and the demand cost rate for that stage. The demand cost rate can also vary with time of day, with higher rates for on-peak periods. To determine a control strategy for charging and discharging storage that mini- mizes utility costs for a given system, it is necessary to perform a minimization of the total cost over the entire billing period because of the demand charge. An even more complicated cost optimization results if the utility rate includes ratchet clauses, whereby the demand charge is the maximum of the monthly peak demand cost and some fraction of the previous monthly peak demand cost within the cooling season. In either case, it is not worthwhile to perform an optimization over time periods longer than those for which reliable forecasts of cooling requirements or ambient conditions could be performed (e.g., 1 day). It is therefore important to have simple con- trol strategies for charging and discharging storage over a daily cycle. The following control strategies for limiting cases provide fur- ther insight: · If the demand cost rate is zero and the energy cost rate does not vary with time, minimizing cost is equivalent to minimizing total electrical energy use. In general, cooling plant efficiency is lower when it is being used to make ice than when it is providing cooling for the building. Thus, in this case, the optimal strategy for mini- mum energy use minimizes the use of storage. This approach is used by chiller-priority control, the most common control strat- egy for partial ice storage systems. · Ifthe demand cost rate is zero but energy costs are higher during on-peak than off-peak periods, minimizing cost then involves trade-offs between energy use and energy cost rates. For relatively small differences between on-peak and off-peak rates of less than about 30%, energy penalties for ice making typically outweigh the effect ofreduced rates, and chiller-priority control is optimal for many cases. However, with higher differentials be- tween on-peak and off-peak energy rates or with chillers having smaller charging-mode energy penalties, the optimal strategy might maximize the use of storage. A control strategy that at- tempts to maximize the load-shifting potential of storage is called storage-priority control; in this scheme, the chiller operates during the off-peak period to fully charge storage. During the on- peak period, storage is used to cool the building in a manner that minimizes use of the chiller(s). Partial-storage systems that use storage-priority control strategies require forecasts for building cooling requirements to avoid prematurely depleting storage. · If only on-peak demand costs are considered, then the optimal control strategy tends to maximize the use of storage and controls the discharge of storage in a manner to always minimize the peak building power. A storage-priority, demand-minimization control strategy for partial-storage systems requires both cooling load and non-cooling electrical use forecasts. Inc. ASHRAE, 2019 user. single for Licensed | {}
f9f37c18-aba9-4157-acde-9185b43f69c7 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Supervisory Control Strategies and Optimization 43.29 Several control strategies based on these three simple limiting cases have been proposed for ice storage systems (Braun 1992; Drees and Braun 1996; Grumman and Butkus 1988; Rawlings 1985; Spethmann 1989; Tamblyn 1985). Braun (1992) appears to have been the first to evaluate the performance of chiller-priority and storage-priority control strategies as compared with optimal control. The storage-priority strategy was termed load-limiting con- trol because it attempts to minimize the peak cooling load during the on-peak period. For the system considered, the load-limiting strat- egy provided near-optimal control in terms of demand costs in all cases and worked well with respect to energy costs when time-of- day energy charges were available. However, the scope of the study was limited in terms of the systems considered. Krarti et al. (1996) evaluated chiller-priority and storage-priority control strategies as compared with optimal control for a wide range of systems, utility rate structures, and operating conditions. Similar to Braun (1992), they concluded that load-limiting, storage-priority control provides near-optimal performance when there are signifi- cant differentials between on-peak and off-peak energy and demand charges. However, optimal control provides superior performance in the absence of time-of-day incentives. In general, the monthly utility costs associated with chiller-priority control were signifi- cantly higher than optimal and storage-priority control. However, without time-of-use energy charges, chiller-priority control did pro- vide good performance for individual days when the daily peak power was less than the monthly peak. General guidance based on the work is presented by Henze et al. (2003). Drees and Braun (1996) developed a simple rule-based control strategy that com- bines elements of storage- and chiller-priority strategies in a way that results in near-optimal performance under all conditions. The strategy was derived from heuristics obtained through both daily and monthly optimization results for several simulated systems. A modified version of this strategy is presented in the Supervisory Control Strategies section of this chapter. Braun (2007c, 2007d) also developed a near-optimal control method for charging and discharging of cool storage systems when real-time pricing (RTP) electric rates are available The algorithm requires relatively low-cost measurements (cooling load and stor- age state of charge) and very little plant specific information, is computationally simple, and ensures that building cooling require- ments are always met (e.g., storage is not prematurely depleted). The control method was evaluated for ice storage systems using a simulation tool for different combinations of cooling plants, storage sizes, buildings, locations, and RTP rates. Control Strategies for Cooling Systems with Discrete Thermal Storage The choice of a control strategy for a cooling system with dis- crete thermal storage system results from a trade-off between performance (i.e., operating costs) and ease ofimplementation (i.e., initial costs). Chiller-priority control has the lowest implementation costs, but generally leads to the highest operating costs. Storage- priority strategies provide superior performance, but require the use of a forecaster and a measurement of state of charge for storage. This section presents details of chiller-priority, load-limiting, and rule-based control applied to ice storage systems. Each of these strategies shares the same procedures for charging storage, but dif- fers in how storage is discharged. In general, the control strategies presented in this section are appropriate for systems with utility rate structures that include time-of-use energy and demand charges, but would not be appropriate in conjunction with real-time pricing. Additional information on control strategies for cool storage sys- tems can be found in Chapter 51 of the 2016 ASHRAE Handbook- HVAC Systems and Equipment. Charging Strategies Ice making should be initiated when both the building is unoccupied and off-peak electrical rates are in effect. During the ice-making period, the chiller should operate at full capacity. Cool- ing plants for ice storage generally operate most efficiently at full load because of the auxiliaries and the characteristics of ice-making chillers. With feedback control of the chilled-water/glycol supply temperature, full capacity control is accomplished by establishing a low enough set point to ensure this condition (e.g., -7°C). Internal Melt Storage Tanks. The chiller should operate until the tank reaches its maximum state of charge or the charging period (i.e., off-peak, unoccupied period) ends. This strategy ensures that suffi- cient ice will be available for the next day without the need for a forecaster. Typically, only a small heat transfer penalty is associated with restoring a partially discharged, internal melt storage tank to a full charge. For this type of storage device, the charging cycle always starts with a high transfer effectiveness because water surrounds the tubes regardless of the amount ofice melted. The heat transfer effec- tiveness drops gradually until the new ice formations intersect with old formations, at which point the tank is fully recharged. External Melt Storage Tanks. These tanks have a more signif- icant heat transfer penalty associated with recharging after a partial discharge, because ice forms on the outside of existing formations during charging. In this case, it is more efficient to fully discharge the tank each day and only recharge as necessary to meet the next day's cooling requirements. To ensure that adequate ice is available, the maximum possible storage capacity needed for the next day must be forecast. The storage requirements for the next day depend on the discharge strategy used and the building load. In general, the state of charge for storage necessary to meet the next day's load can be estimated according to occupied period Qload, k 2ch,k Xchg = C S k=1 is the relative state of charge at the end of the charging where Xchg. period, Cs is the maximum change in internal energy of the storage tank that can occur during a normal discharge cycle, and Qload,k and ⌀ch, k are forecasts of the building load and chiller cooling requirement for the kth stage (e.g., hour) of the occupied period. The relative state of charge is defined in terms of two reference states: the fully discharged and fully charged conditions that corre- spond to values of zero and one. These conditions are defined for a given storage based on its particular operating strategy (ASHRAE Standard 150; Elleson 1996). The fully charged condition exists when the control stops the charge cycle as part of its normal sequence. Similarly, the fully discharged condition is the point where no more usable cooling is recovered from the tank. Typically, zero state of charge corresponds to a tank of water at a uniform temperature of 0°C and a complete charge is associated with a tank having maximum ice build at 0°C. (The fully discharged and fully charged conditions are arbitrarily selected reference states.) In abnormal circumstances, a storage tank can be discharged or charged beyond these conditions, resulting in relative states of charge below zero or above one. Hourly forecasts of the next day's cooling requirement can be determined using the algorithm described in the section on Fore- casting Diurnal Cooling and Whole Building Demand Profile. However, long-term forecasts are highly uncertain and a safety factor based on previous forecast errors is appropriate (e.g., uncer- tainty of two or three times the standard deviation of the errors of previous forecasts). Estimates ofhourly chiller requirements should be determined using the intended discharge strategy (described in the next section) and building load forecasts. (44) Inc. ASHRAE, 2019 user. single for Licensed | {}
ad5b7594-3aa6-41b0-bef2-15de4586a2e6 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 43.30 2019 ASHRAE Handbook- -HVAC Applications (SI) Discharging Strategies Three discharge strategies are presented for use with utility structures having on-peak and off-peak energy and demand charges: (1) chiller-priority control, (2) storage-priority, load-limiting con- trol, and (3) a rule-based strategy that uses both chiller-priority and load-limiting strategies. Chiller-Priority Discharge. During the storage discharge mode, the chiller operates at full cooling capacity (or less if sufficient to meet the load) and storage matches the difference between the building requirement and chiller capacity. For the example system shown in Figure 28, the chiller supply temperature set point tchws is If the set equal to the desired supply temperature for the coils tcoil- capacity of the chiller is sufficient to maintain this set point, then storage is not used and the system operates in the direct chiller mode. Otherwise, the storage control valve modulates the flow through storage to maintain the supply set point, providing a cooling rate that matches the difference between the building load and the maximum cooling capacity of the chillers. This strategy is easy to implement and does not require a load forecast. It works well for design conditions, but can result in rela- tively high demand and energy costs for off-design conditions because the chiller operates at full capacity during the on-peak pe- riod. Storage-Priority, Load-Limiting Control. Several storage- priority control approaches ensure that storage is not depleted prematurely. Braun (1992) presented a storage-priority (load- limiting) control strategy, which tends to minimize the peak cooling plant power demand. The operation of equipment for load-limiting control during different parts of the occupied period can be de- scribed as follows: · Off-Peak, Occupied Period. During this period, the goal is to minimize use of storage, and the chiller-priority described in the previous section should be applied. · On-Peak, Occupied Period. During this period, the goal is to operate the chillers at a constant load while discharging the ice storage such that the ice is completely melted when the off-peak period begins. This requires using a building cooling-load fore- caster. At each decision interval (e.g., 15 min), the following steps are applied: Inc. ASHRAE, 2019 user. single for Licensed (1) Forecast the total integrated building cooling requirement until the end of the discharging period. (2) Estimate the state of charge of the ice storage tank from measurements. (3) At any time, the chiller loading for load-limiting control is determined as 0 - X- X C load,occ �LLC = Max min s ⌀ch, min (45) t on where 0 load,occ is a forecast of the integrated building load for the rest of the on-peak period, ton is the time remaining in the on-peak period, Xis the current state of charge defined is a as the fraction of the maximum storage capacity, Xmin minimum allowable state of charge, Cs is the maximum pos- sible energy that could be added to storage during discharge, and 2ch ,min is the minimum allowable chiller cooling capacity. If the chiller does not need to be operated during the remainder of the occupied, on-peak period, the minimum allowable cooling capacity could be set to zero. Otherwise, the cooling capacity should be set to the mini- mum at which the chiller can safely operate. Determine the chiller set-point temperature necessary to (4) achieve the desired loading as 0 LLC tchws C chw = tchwr (46) where tchwr is the temperature of water/glycol returned to the chiller and Cchw spe- is the capacitance rate (mass flow times cific heat) of the flow stream. Hourly forecasts of cooling loads can be determined using the algorithm described in the section on Forecasting Diurnal Cooling and Whole-Building Demand Profiles. The hourly forecasts are then integrated to give a forecast of the total cooling requirement. To ensure sufficient cooling capacity, a worst-case forecast of cooling requirements could be estimated as the sum of the best forecast and two or three times the standard deviation of the errors of previous forecasts. Rule-Based Controller. Drees and Braun (1996) presented a rule-based controller that combines elements of chiller-priority and storage-priority strategies, along with a demand-limiting algorithm to achieve near-optimal control. The demand-limiting algorithm requires a measurement of the total building electrical use. A sim- pler strategy is described here that does not require this measure- ment and yields equivalent performance whenever the peak demand for the billing period is coincident with the peak cooling load. Figure 29 shows a flowchart for the discharge strategy that is applied during each decision interval (e.g., 15 min) during the occupied period. Block 1 determines whether storage use should be maximized or minimized. Block 2 is used if storage use lowers daily energy costs and storage is sufficient to meet the remainder of the load for the occupied period without operating the chillers. Other- wise, the goal of the strategy in block 3 is to minimize storage use while keeping peak load below a limit. This strategy tends to keep the chiller(s) heavily loaded (and therefore, if part-load efficiency is poor, operating efficiently) until they are no longer needed. The logic in each block is as follows: · Block 1: Discharge Strategy Selection. The discharge of storage will not reduce the energy cost whenever the cost of replenishing the ice is greater than the cost of providing direct cooling by the chiller(s). This situation is always the case during the off-peak, occupied period because the electricity rates are the same as those associated with the charging period and chillers are less efficient in ice-making mode than when providing direct cooling. Further- more, during the on-peak, occupied period, using storage generally reduces energy costs whenever the following criterion holds: ECR > COP d/COPc (47) ![image](/image/placeholder) BLOCK 3 BLOCK 1 MINIMIZE STORAGE DISCHARGE RATE CAN STORAGE MEET THE LOAD AND AND REDUCE DAILY ENERGY COSTS? NO KEEP LOAD BELOW PEAK LOAD LIMIT YES BLOCK 2 MAXIMIZE STORAGE DISCHARGE RATE Fig. 29 Flowchart for Rule-Based Controller Discharge Strategy | {}
156e93ac-3761-48d7-893e-f3478d61576d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Supervisory Control Strategies and Optimization 43.31 where ECR is the ratio of on-peak to off-peak energy charges and COPd and COPc are coefficients of performance for the cooling plant (including chiller, pumps, and cooling tower fans) during discharging and charging of the tank. The COPs should be evalu- ated at the worst-case charging and discharging conditions associated with the design day. Typically, this ratio is between about 1.2 and 1.8 for systems with cooling towers. However, the ratio can be lower because ofthe effect of cool nighttime tempera- tures, especially for systems with air-cooled condensers in dry climates. If the criterion of Equation (47) is satisfied, control switches from chiller-priority to storage-priority strategy whenever storage capacity is greater than the remaining integrated load. Therefore, storage-priority control is enabled whenever (X - Xmin)Cs ⌀load, occ · · (48) Hourly forecasts of cooling loads can be determined using the algorithm described in the section on Forecasting Diurnal Cooling and Whole-Building Demand Profiles and then integrated to give a forecast ofthe total cooling requirement. To ensure that adequate ice is available, worst-case hourly forecasts can be determined by adding the expected value of the hourly forecasts and the forecast errors associated with a specified confidence interval (e.g., two standard deviations for a 95% confidence interval). The worst-case hourly forecasts can then be integrated to give a worst-case inte- grated forecast. Block 2: Maximum Use of Storage. In this mode, the chillers are turned off and storage is used to meet the entire load throughout the remainder of the occupied period. However, a chiller may need to be turned on if the storage discharge rate is not sufficient to meet the building load (i.e., the coil supply temperature set point cannot be maintained). Block 3: Minimize Use of Storage with Peak Load Limiting. At any time, a target chiller load is determined as 0 = Min Max 0 0 , 0 load ch ch,peak LCC where Qch,peak is the peak chiller cooling requirement that has occurred during the on-peak period for the current billing period, QLCC is the chiller load associated with load-limiting control and determined with Equation (45), and Qload is the current building load. The chiller set-point temperature necessary to achieve the desired loading is determined as (49) 0 ch tchws tchwr C = Max , t coil chw (50) On the first day of each billing period, 0 ch,peak is set to zero. For this first day, applying Equation (49) leads to the load-limiting control strategy described in the previous section. On subsequent days, load-limiting control is used only if the current peak limit would lead to premature depletion of storage. Whenever the cur- rent load is less than 2ch,peak and �LCC, Equations (49) and (50) lead to chiller-priority control. 3.7 DYNAMIC OPTIMIZATION FOR COOLING USING THERMAL MASS OR TABS Precooling of Building Thermal Mass For conventional night setup strategies, building mass works to increase operating costs (Bloomfield and Fisk 1977). A massless building would require no time for precooling or preheating and would have lower overall cooling or heating loads than an actual building. However, under proper circumstances, using a building's thermal storage for load shifting can significantly reduce opera- tional costs and energy use, even though the total zone loads may increase. This is especially true for cooling of high-performance buildings, in which internal loads may dominate. At any given time, the cooling requirement for a space is caused by convection from internal gains (lights, equipment, and people) and interior surfaces. Because a significant fraction of the internal gain is radiated to interior surfaces, the state of a building' s thermal storage and the convective coupling dictates the cooling require- ment. Precooling the building during unoccupied times reduces the overall convection from exposed surfaces during the occupied period as compared with night setup control and can reduce daytime cooling requirements. The potential for storing thermal energy in the structure and furnishings of conventional commercial buildings is significant compared to the load requirements. Typically, internal gains are about 20 to 40 W per square metre of floor space. The ther- mal capacity for typical concrete building structures is approxi- mately 40 to 80 (W ·h)/K per square metre of floor area. Thus, for an internal space, the energy storage can handle the load for about 1 h for every 0.6 K of precooling of the thermal mass. Opportunities for reducing operating costs by using building thermal mass for cooling derive from four effects: (1) reduction in demand costs, (2) use of low-cost off-peak electrical energy, (3) re- duced mechanical cooling from the use of cool nighttime air for ventilation precooling, and (4) improved mechanical cooling effi- ciency from increased operation at more favorable part-load and ambient conditions. However, these benefits must be balanced with the increase in total cooling requirement that occurs with precooling the thermal mass. Therefore, the savings associated with load shift- ing and demand reductions depend on both the method of control and the specific application. Several simulation studies have been performed that demonstrate a substantial benefit to precooling buildings in terms of cost savings and peak cooling load reduction (Andresen and Brandemuehl 1992; Braun 1990; Rabl and Norford 1991; Snyder and Newell 1990). Possible energy savings ranged from 0 to 25%; possible reductions in total building peak electrical demand ranged from 15 to 50% compared with conventional control. The results can be sensitive to the convective coupling between the air and the thermal mass, and the mass of the furnishings may be important (Andresen and Bran- demuehl 1992). Determining the optimal set of building temperatures over time that minimizes operating costs is complex. Keeney and Braun (1996) developed a simplified approach for determining optimal control of building thermal mass using two optimization variables for the pre- cool period and a set of rules for the occupied period of each day. This approach significantly reduces the computation required for de- termining the optimal control as compared with considering hourly zone set points as optimization variables. Results of the simplified approach compared well with those of detailed optimizations for a range of systems (over 1000 different combinations of building types, weather conditions, cooling plants, and utility rates). Morris et al. (1994) performed a set of experiments using a test facility at the National Institute of Standards and Technology (NIST) to demonstrate the potential for load shifting and load leveling when control was optimized. Two different control strategies were consid- ered: (1) minimum cooling system energy use and (2) minimum peak cooling system electrical demand. The two strategies were imple- mented in the test facility and compared with night setup control. Figure 30 shows the 24 h time variation in the cooling requirement for the test facility allowed to reach a steady-periodic condition, for both the minimum energy use strategy and conventional night setup control. The results indicate a significant load-shifting potential for the optimal control. Overall, cooling requirements during the occu- Inc. ASHRAE, 2019 user. single for Licensed | {}
b467237c-3fc1-4d66-bb12-e60e97807443 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 43.32 2019 ASHRAE Handbook- -HVAC Applications (SI) pied period were approximately 40% less for optimal than for night setup control. Comfort conditions were also monitored for the tests. Figure 31 gives the time variation of predicted mean vote (PMV) for the two control strategies as determined from measurements at the facility. A PMV of zero is a thermally neutral sensation, positive is too warm, and negative too cool. In the region of ±0.5, comfort is not compromised to any significant extent. Figure 31 shows that com- fort conditions were essentially identical for the two control methods during the occupied period. The space temperature, which has the dominant effect on comfort, was maintained at 24°C during the occupied period for both control methods. During the unoccu- pied period, the cooling system was off for night setup control and the temperature floated to warm comfort conditions. On the other hand, the optimal controller precooled the space, resulting in cool comfort conditions before occupancy. During these tests, the mini- mum space temperature during precooling was 20°C, and the space temperature set point was raised to 24°C just before occupancy. Figure 32 shows the 24 h time variation in the cooling require- ment for the test facility for both the minimum peak demand strategy and conventional night setup. Optimal control involved precooling the structure and adjusting space temperatures within the comfort zone (-0.5 PMV 0.5) during the occupied period to achieve minimum demand. Although the true minimum was not achieved during the tests, the peak cooling rate during the occupied period was approximately 40% less for minimum peak demand con- trol than for night setup control. Morris et al. (1994) demonstrated significant savings potential for control ofbuilding thermal mass; however, they also showed that the cost savings are very sensitive to the application, operating con- ditions, and method of control. For example, an investigation into the effect of precooling on the on-peak cooling requirements for an existing building (which may not have been a good candidate for use of building thermal storage) showed only a 10% reduction in the cooling energy required during the occupied period, with a substan- tial increase in the total cooling required and no reduction in the peak cooling requirement (Ruud et al. 1990). System simulations can be used to identify (1) whether the system is a good candidate for using building thermal mass and (2) an effective method for con- trol, before implementing a strategy in a particular building. Keeney and Braun (1997) used system simulation to develop a control strategy that was then tested in a large commercial building X-Axis: TIME OF DAY, h Y-Axis: COOLING LOAD, W Chart Type: line 0 days 1 day 2 days 3 days 4 days 5 days 6 days 7 days 8 days 9 days 10 days 11 days 12 days 13 days 14 days 15 days 16 days 17 days 18 days 19 days 20 days 21 days 22 days 23 days 24 days item_01 500 500 500 500 500 500 500 500 500 1500 1500 1500 1500 1500 1500 1500 1500 1500 1500 1500 1500 1500 1500 500 500 Fig. 30 Comparison of Cooling Requirements for Minimum Energy and Night Setup Control (Morris et al. 1994) located northwest of Chicago. The goal of the control strategy was to use building thermal mass to limit the peak cooling load for con- tinued building operation in the event of the loss of one of the four central chiller units. The algorithm was tested using two nearly identical buildings separated by a large, separately cooled entrance area. The east building used the existing building control strategy; the west building used the precooling strategy developed for this project. The precooling control strategy successfully limited the peak load to 75% of the cooling capacity for the west building, whereas the east building operated at 100% of capacity. Details of the strategy and case study results are presented in the Supervisory Control Strategies section of this chapter. Braun et al. (2001) used on-site measurements from the same building used by Keeney and Braun (1997) to train site-specific models that were then used to develop site-specific control strate- gies for using building thermal mass and to evaluate the possible PMV X-Axis: Time of Day, h Chart Type: line Upper Comfort Limit Lower Comfort LIMIT Minimum Energy Occupied Period item_01 1Hours (h) 0Hours (h) 0Hours (h) -1Hours (h) Fig. 31 Comparison of Predicted Mean Vote (PMV) for Minimum Energy and Night Setup Control (Morris et al. 1994) W LOAD, COOLING X-Axis: TIME OF DAY, h Y-Axis: COOLING LOAD, w Chart Type: line 0 days 4 days 8 days 12 days 16 days 20 days 24 days item_01 700Watts (W) 1700Watts (W) 1500Watts (W) 1300Watts (W) 1200Watts (W) 1000Watts (W) 0Watts (W) Fig. 32 Comparison of Cooling Requirements for Minimum Demand and Night Setup Control (Morris et al. 1994) Inc. ASHRAE, 2019 user. single for Licensed | {}
1d479d2b-daaa-478c-8b16-7081e656d0c0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Supervisory Control Strategies and Optimization 43.33 cost savings of these strategies. The building was an excellent can- didate for using building thermal mass because it had (1) a large differential between on-peak and off-peak energy rates (about a 2- to-1 ratio), (2) a large demand charge (about $16/kW), (3) a heavy structure with significant exposed mass, and (4) cooling loads that are dominated by internal gains, leading to a high storage efficiency. The model underpredicted the total HVAC bill by about 5%, but worked well enough to be used in comparing the performance of alternative control strategies. Table 6 gives estimates of cooling-related costs and savings over the course of three summer months for different control strategies. The light and moderate precool strategies are simple strategies that precool the building at a fixed set point of 19.5°C before occupancy and then maintain a fixed discharge set point in the middle of the comfort range (23°C) during occupancy. The light precool begins at 3 AM, whereas moderate precool starts at 1 AM. The extended pre- cool strategy attempts to maintain the cooled thermal mass until the onset of the on-peak period. In this case, the set point at occupancy is maintained at the lower limit of comfort (20.5°C) until the on- peak period begins at 10 AM. At this point, the set point is raised to the middle of the comfort range (23°C). The other strategies use the extended precooling, but the entire comfort range is used throughout the on-peak, occupied period. The maximum discharge strategy attempts to discharge the mass as quickly as possible after the on-peak period begins. In this case, the set point is raised to the upper limit of comfort within an hour after the on-peak period begins. The slow linear rise strategy raises the set point linearly over the entire on-peak, occupied period (9 h in this case), whereas the fast linear rise strategy raises the set point over 4 h. The strategies that do not use the entire comfort range during the occupied period (light precool, moderate precool and extended pre- cool) all provided about 20% savings compared to night setup. Each of these strategies reduced both energy and demand costs, but the demand costs and reductions were significantly greater than the energy costs and savings. The decreases in energy costs were caused by favorable on-to-off peak energy rate ratios of about 2 to 1. The high on-peak demand charges provided even greater incentives for pre- cooling. The savings increased with the length of the precooling period, particularly when precooling was performed close to the onset of on-peak rates. The maximum discharge strategy, which maximizes discharge of the thermal storage within the structure, provided the largest savings (41%). Much of the additional savings came from reduced demand costs. The linear rise strategies also provided consid- erable savings with greater savings associated with faster increases in the set point temperature. Morgan and Krarti (2006) performed both simulation analyses and field testing to evaluate various precooling strategies. They found that energy cost savings associated with precooling thermal mass depends on several factors, including thermal mass level, cli- mate, and utility rate. For time-of-use (TOU) utility rates, they found that energy cost savings are primarily affected by the ratio of on-peak to off-peak demand charges as well as the ratio of on-peak to off-peak energy charges (see Chapter 51 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment). ASHRAE research project RP-1313 conducted an extensive study ofbuilding thermal mass control (Henze et al. 2007), in which optimal building thermal mass control strategies were investigated for time-of-use electric utility rates structures, including demand charges, with the help of a newly developed integrated optimization and building simulation tool (Henze et al. 2008). Cheng et al. (2008) identified the primary factors that influence optimal control of passive thermal storage, where optimal control strategies are deter- mined with the objective of minimizing total energy and demand costs. A fractional factorial analysis was used to investigate how cost savings are affected by several building and system character- istics, utility rate structures, and climates. Utility rates, internal Table 6 Cooling Season Energy, Demand, and Total Costs and Savings Potential of Different Building Mass Control Strategies ¦ Strategy ¦ Costs in U.S. Dollars ¦ Costs in U.S. Dollars ¦ Costs in U.S. Dollars ¦ Savings, % ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Strategy ¦ Energy ¦ Demand ¦ Total ¦ Savings, % ¦ ¦ Night setup ¦ $90 802 ¦ $189 034 ¦ $279 836 ¦ 0.0 ¦ ¦ Light precool ¦ $84 346 ¦ $147 581 ¦ $231 928 ¦ 17.1 ¦ ¦ Moderate precool ¦ $83 541 ¦ $143 859 ¦ $227 400 ¦ 18.7 ¦ ¦ Extended precool ¦ $81 715 ¦ $134 551 ¦ $216 266 ¦ 22.7 ¦ ¦ Maximum discharge ¦ $72 638 ¦ $91 282 ¦ $163 920 ¦ 41.4 ¦ ¦ Two-hour linear rise ¦ $72 671 ¦ $91 372 ¦ $164 043 ¦ 41.4 ¦ ¦ Four-hour linear rise ¦ $73 779 ¦ $115 137 ¦ $188 916 ¦ 32.5 ¦ ¦ Nine-hour linear rise ¦ $77 095 ¦ $141 124 ¦ $218 219 ¦ 22.0 ¦ Source: Braun et al. (2001). Note: Building located in Chicago, Illinois. loads, building mass level, and equipment efficiency were found to have the largest impacts on cost savings, whereas building envelope characteristics did not have a significant impact. Although the mag- nitude of savings is affected by climate, the relative influences of each of these factors are largely independent of weather. Using the same simulation and optimization environment, Henze et al. (2009) presented advances toward near-optimal building thermal mass control derived from full factorial analyses of the im- portant parameters influencing passive thermal storage for a range of buildings and climate/utility rate structure combinations. In re- sponse to the actual utility rates imposed in the investigated cities, insights and control simplifications were derived from those build- ings deemed suitable candidates. The near-optimal strategies were derived from the optimal control trajectory, consisting of four vari- ables, and then tested for effectiveness and validated with respect to uncertainty regarding building parameters and climate variations. Although no universally applicable control guideline could be found, a significant number of cases (i.e., combinations of build- ings, weather, and utility rate structure) were investigated and offer both insight into and recommendations for simplified control strat- egies. These recommendations are a good starting point for experimentation with building thermal mass control for a substan- tial range of building types, equipment, climates, and utility rates. The cost savings potential of optimal passive thermal storage controls were examined by Greensfelder et al. (2011) for the case of day-ahead, real-time electricity rate structures. The operational strategies of three office building models were optimized in four U.S. cities (Chicago, New Y ork, Houston, and Los Angeles) using price and weather data for the summer of 2008. Building thermal mass was optimized using a predictive optimal controller to define supervisory control strategies in terms of building global cooling temperature set points. A global minimization algorithm deter- mined optimal set-point trajectories for each day divided into four distinct time periods (called building modes). Cost savings were found to range from 0 to 14%, depending on the building, climate, and characteristics of the rate signal. The best cost savings occurred in the presence of price spikes or cool nighttime temperatures. Moreover, it was found that low internal gains favored a more flex- ible precooling strategy, whereas high internal gains coupled with low thermal mass resulted in poor precooling performance. Thermally Activated Building Systems (TABS) One way to reduce cooling energy further along the path to net- zero-energy buildings is thermally activated building systems (TABS): direct cooling of building mass by chilled water in con- junction with chillers designed for very high part-load efficiency in low-lift operation and enthalpy-recovery dedicated outdoor air sys- tems (DOAS). TABS differs from passive storage by cooling the mass directly from the inside, thus eliminating charging-mode convective or Inc. ASHRAE, 2019 user. single for Licensed | {}
afb01a79-391b-45b9-95eb-51b2def69441 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 43.34 2019 ASHRAE Handbook-HVAC Applications (SI) radiative coupling resistances. By directly precooling the mass, in- stead of the occupied space, substantially better storage efficiency and larger effective diurnal storage capacity are achieved. Precool- ing energy percentage savings may be 5 to 35% higher because the condenser-evaporator temperature difference is lower to begin with and because, with the elimination of supply fans and mechanical cooling, energy use is dominated by compressor operation at very low pressure ratios (Armstrong et al. 2009; Katipamula et al. 2010b). Economizer mode, which involves mainly pumping rather than fan transport energy, is extremely energy efficient as well. Katipamula et al. (2010a, 2010b) simulated idealized thermal energy storage (TES) to approximate TABS, and a variable-speed air-cooled chiller with variable-speed distribution pump. The TES and distribution options are shown schematically in Figure 33. The chiller/distribution system was modeled with compressor, condenser fan, and chilled-water pump capable of wide 10:1 speed ranges and statically optimized control, resulting in evaporator tem- peratures of up to 18°C at 10% of design load. Chiller performance was measured by an independent testing laboratory over a wide range of part-load fraction, outdoor temperatures, and chilled-water temperatures (Katipamula et al. 2010a). Performance curves fit to the data are shown in Figure 34. The performance map on the left is for a standard chilled-water reset schedule recommended for VAV systems (ASHRAE Standard 90.1), and the right-hand map represents performance of the chiller with radiant ceiling panels (RCPs) or chilled-beam distribution system serving a conditioned space at Top = 24°C. Compressor, condenser fan, and chilled-water pump are operated at optimal speed under any given condition and part-load fraction. ![image](/image/placeholder) DIRECT OUTDOOR AIR SYSTEM HEAT CHILLER REJECTION ZONE(S) 0 0 TABS 0 0 Fig. 33 Schematic of Thermally Activated Building System with Three Cooling Options A flat electricity rate was assumed, to achieve minimum annual energy use, and the performance of standard and high-performance versions of 12 building types was simulated in 16 climates. The load shifting achieved by TES is shown in Figure 35. The joint distribu- tion of chiller output is expressed in full-load operating hours for each bin cell of2.8 K in outdoor temperature by 10% in rated capac- ity. Compared to the base-case load distribution, operation hours for the TES system are significantly shifted in two respects. The bin in which the full-load equivalent operating hours (FLEOH) peak occurs is typically 8.3 K lower than in the baseline chiller load distribution. Although the chiller continues to operate at high outdoor tempera- tures, it does so at much lower part-load ratios. Conversely, the FLEOH of operation at low outdoor temperature and low part-load ratio significantly increased. The base case for savings used a two-speed chiller built from the same components as the statically optimized chiller and VAV or CAV air-handling unit, depending on building type, with air-side economizer for distribution and no storage. The controller objective function for the TABS storage case, Equation (4), involves only the chiller power used to meet sensible load, P = u/COP(u,t) with E = 1 and D = 0 to produce the highest energy savings. The need for the upper-bound constraint ofEquation (7) was eliminated by providing sufficient mass to satisfy the peak day sensible cooling load and assuming zero charge carryover from day to day. In the simulations, perfect 24 h forecasts of load and outdoor temperature were used; in practice, a model-based predictive control using the forecast methods from this chapter and publicly or commercially available forecasts of weather would result in some loss of performance (Krarti et al. 2007). The results in Table 7 indicate substantial energy savings potential for most of the building types in all 16 cli- mates. For high-performance buildings, the savings were substantial in most building types and climates where economizer cooling potential is modest and the annual sensible load is domi- nant. Capital costs of the base and low-lift TABS systems were estimated and compared. For large office buildings, the TABS cool- ing system capital cost was estimated to be less than that ofthe VAV system. These results are based on simulations in which the control for charging of the TABS is assumed to be modeled exactly. One problem with TABS is that precooling can no longer be reliably controlled by room temperature set-point adjustments. A further Chart Type: line T(x) C T(x) 43 T(x) 32 T(x) 21 T(x) 10 item_01 43kW/kW 43kW/kW 37.5kW/kW 26.5kW/kW 21kW/kW Fig. 34 Performance of Optimally Controlled Chiller for Two Different Load-Side Boundary Conditions Inc. ASHRAE, 2019 user. single for Licensed | {}
8ffcf6cd-016e-4d92-bb57-4d52233952e8 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Supervisory Control Strategies and Optimization 43.35 problem is that the state of charge cannot be readily measured. For these reasons, supervisory control of a real TABS implementation is considered to require some form of model-based predictive control. A full-scale laboratory test of TABS cooling with model-based predictive control was conducted by Gayeski et al. (2012). The test results showed energy savings of25 to 30% compared to an SEER- 16 all-air system for typical Atlanta and Phoenix summer conditions. In each two-week-long test, the same variable-speed compressor/ condenser unit was connected to a conventional indoor unit for the baseline case and to a hydronic evaporator supplying chilled water to a 150 mm concrete slab for the optimal precooling case. The results were comparable to the simulation results of Katipamula et al. (2010b) for a medium office building in Atlanta and Phoenix. Combined Thermal Energy Storage Systems Combination ofTABS and Direct Sensible Cooling. Using two weeks of data from Gayeski et al. (2011b) and Seem et al. 's (1989a) CRTF model, Zakula et al. (2014) compared seasonal performance of a TABS model using TRNSYS software (University of Wisconsin- Madison 2013). They simulated (1) cooling with TABS only, (2) opti- mal scheduling ofVA V precooling, and (3) both TABS and VAV, for dates between May 1 and September 30. Percentages of energy sav- ings for options 1 and 3 are shown in Figure 36. The exposed floor mass in the model achieved about 70% of the savings with TABS alone, through passive precooling; thus, greater savings can be seen by sharing the cooling load between TABS and sensible-only vari- able-refrigerant flow (VRF) precooling. Niswander (2013) modeled the combination of TABS and sensible-only VRF, with model-predictive control deciding the sequence of capacity delivered to the TABS and directly to the room over each 24 h planning horizon. A third mode was also modeled, in which heat was rejected from the VRF terminal units to the TABS at very high COP to reduce the impact of high RTP rates in mid-late afternoon. The controller objective function (Equation [4]) thus Chart Type: bar DRY-BUB TEMPERATURE GRY-BUB TEMPERATURE PART LOAD RATIO OTHERMAL ENERGY STORAGE TES PROFESSIONAL EQUIVNENT OPERATING HOURS NET OPEN TING HOURS PROFESSIONAL HOURS PRET LOOD RETAIL TRADE TEXAS PROFESSIONAL EMPLOAD EQUIVNNT OPERATING HOURS item_01 10% 37.5% 0.5% 10% 50% 40% 50% 65% 0.5% (A) NO STORAGE (TES) Fig. 35 Chiller Load Distributions for Chicago (B) OPTIMAL Chart Type: bar CHICAGO HOUSTON LAS VEGAS MIAMI PHOENIX item_01 45% 50% 50% 45% 40% Fig. 36 Savings Using TABS Only Compared to (A) Conventional VAV and (B) Sensible-Only MPC-VRF (Zakula et al. 2015) Inc. ASHRAE, 2019 user. single for Licensed | {}
808a2385-08f3-447b-adc6-fe08da98140c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 43.36 2019 ASHRAE Handbook- - HVAC Applications (SI) Chart Type: bar PLR (A) PLR RATE item_01 0.6°C 0.8°C 1°C Fig. 37 Full-Load Equivalent Operating Hours (FLEOH) Distributions with TABS Acting Both as Cool Storage and Demand-Responsive Heat Sink Table 7 Energy Savings Potential for Precooling with High Part-Load Efficiency Chiller ¦ ¦ Standard Building ¦ Standard Building ¦ Standard Building ¦ High-Performance Building ¦ High-Performance Building ¦ High-Performance Building ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Building Type ¦ Min. ¦ Max. ¦ Avg. ¦ Min. ¦ Max. ¦ Avg. ¦ ¦ Office, small ¦ 59% ¦ 77% ¦ 70% ¦ -19% ¦ 43% ¦ 25% ¦ ¦ medium ¦ 13% ¦ 52% ¦ 37% ¦ 7% ¦ 50% ¦ 25% ¦ ¦ large ¦ 21% ¦ 61% ¦ 40% ¦ -4% ¦ 36% ¦ 13% ¦ ¦ Retail, standalone ¦ 56% ¦ 73% ¦ 66% ¦ 31% ¦ 50% ¦ 41% ¦ ¦ strip mall ¦ 45% ¦ 63% ¦ 56% ¦ -7% ¦ 41% ¦ 16% ¦ ¦ Primary school ¦ 46% ¦ 55% ¦ 51% ¦ 22% ¦ 46% ¦ 34% ¦ ¦ Secondary school ¦ 32% ¦ 49% ¦ 43% ¦ 10% ¦ 37% ¦ 26% ¦ ¦ Hotel, large ¦ 16% ¦ 57% ¦ 44% ¦ -11% ¦ 47% ¦ 29% ¦ ¦ Supermarket ¦ 59% ¦ 78% ¦ 68% ¦ 35% ¦ 63% ¦ 51% ¦ ¦ Warehouse ¦ 50% ¦ 81% ¦ 69% ¦ -5% ¦ 69% ¦ 40% ¦ ¦ Outpatient ¦ 65% ¦ 83% ¦ 78% ¦ 34% ¦ 67% ¦ 53% ¦ ¦ Hospital ¦ 48% ¦ 76% ¦ 64% ¦ 10% ¦ 49% ¦ 37% ¦ Source: Katipamula et al. (2010b). includes three modes of heat pump operation: P = up/COP(up,t) + uq/COP(ug,t) + u,/COP(urnt) where subscript p denotes precooling of TABS, 9 denotes direct cooling (possibly to effect passive precooling) and r denotes rejection of heat to TABS. Simulations were carried out with E = 1 and D = 0 to produce the highest energy savings, and with RTP rates to produce the largest shifting of load. The upper-bound constraint of Equation (7) was eliminated, but the states of both passive storage and TABS were carried from day to day. Some typical peak-shifting results are shown in Figure 37 for flat rate (left) and a mode of the utility company's RTP rate (right). Combined Passive and Discrete Thermal Storage. Most inves- tigations into the optimal control of combined discrete and passive building thermal storage inventory rely on a detailed white-box or gray-box model of building thermal response and equipment perfor- mance (see, e.g., Henze et al. [2005]). However, Liu and Henze (2006a, 2006b) describe a novel approach to optimally control com- mercial building passive and discrete thermal storage inventory simultaneously: a hybrid control scheme that combines features of model-based optimal control and model-free reinforcement learning control. Theoretically, the reinforcement learning algorithm, based on Watkins and Dayan (1992), approximates dynamic-programming- based optimal control by sampling the cost space and can reach the true optimum, given properly selected learning parameters and enough learning time. The amount of required training is not yet realistic if the controller is directly implemented in a commercial building application. This constitutes the major drawback of the reinforcement learning control approach; contextual information in some form needs to be introduced to expedite learning the prob- lem's fundamental features, whereas reinforcement learning fine- tunes the controller. This realization inspired the development ofthe hybrid learning control scheme (Liu and Henze 2006a). Liu and Henze (2006b) analyzed the performance of this hybrid controller installed in a full-scale laboratory facility. Using the hybrid control approach saved costs when using either discrete or passive TES, compared with conventional building control; however, the savings were lower than for model-based predictive optimal con- trol. In model-based predictive control, the hybrid controller's performance is largely affected by the quality of the training model, and extensive real-time learning is required for the learning control- ler to eliminate any false cues it receives during the initial training period. Nevertheless, compared with standard reinforcement learn- ing, Liu and Henze's proposed hybrid controller is much more readily implemented in a commercial building. 3.8 FORECASTING DIURNAL COOLING AND WHOLE-BUILDING DEMAND PROFILES As discussed previously, forecasts of cooling requirements and electrical use in buildings are often necessary for the control of thermal storage to shift electrical use from on-peak to off-peak peri- ods. In addition, forecasts can help plant operators anticipate major changes in operating modes, such as bringing additional chillers online. Inc. ASHRAE, 2019 user. single for Licensed | {}
57c90d14-c08c-4268-a623-964bb74d4013 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Supervisory Control Strategies and Optimization 43.37 In most methods, predictions are estimated as a function of time- varying input variables that affect cooling requirements and electrical use. Examples of inputs that affect building energy use include (1) ambient dry-bulb temperature, (2) ambient wet-bulb temperature, (3) solar radiation, (4) building occupancy, and (5) wind speed. Methods that include time-varying measured input variables are often termed deterministic methods. Not all inputs affecting cooling requirements and electric use are easily measured. For instance, building occupancy is difficult to determine and solar radiation measurements are expensive. In addi- tion, the accuracy of forecast models that use deterministic inputs depends on the accuracy of future predictions of the inputs. As a result, most inputs that affect building energy use are typically not used. Much of the time-dependent variation in cooling loads and elec- trical use for a building can be captured with time as a deterministic input. For instance, building occupancy follows a regular schedule that depends on time of day and time of year. In addition, variations in ambient conditions follow a regular daily and seasonal pattern. Many forecasting methods use time in place of unmeasured deter- ministic inputs in a functional form that captures the average time dependence of the variation in energy use. A deterministic model has limited accuracy for forecasts because of both unmeasured and unpredictable (random) input variables. Short-term forecasts can be improved significantly by adding pre- vious values of deterministic inputs and previous output measurements (cooling requirements or electrical use) as inputs to the forecasting model. The time history of these inputs provides valuable information about recent trends in the time variation of the forecasted variable and the unmeasured input variables that affect it. Most forecasting methods use historical variables to predict the future. Any forecasting method requires that a functional form is defined and the parameters of the model are learned based on measured data. Either off-line or online methods can be used to estimate parameters. Off-line methods involve estimating parameters from a batch of col- lected data. Typically, parameters are determined by minimizing the sum of squares of the forecast errors. The parameters of the process are assumed to be constant over time in the off-line methods. Online methods allow the parameters of the forecasting model to vary slowly with time. Again, the sum of squares of the forecast errors is minimized, but sequentially or recursively. Often, a forgetting factor is used to give additional weight to the recent data. The ability to track time-varying systems can be important when forecasting cooling requirements or electricity use in buildings, because of the influence of seasonal variations in weather. Forrester and W epfer (1984) presented a forecasting algorithm that uses current and previous ambient temperatures and previous loads to predict future requirements. Trends on an hourly time scale are accounted for with measured inputs for a few hours preceding the current time. Day-to-day trends are considered by using the value of the load that occurred 24 h earlier as an input. One of the major limitations of this model is its inability to accurately predict loads when an occupied day (e.g., Monday) follows an unoccupied (e.g., Sunday) or when an unoccupied day follows an occupied day (e.g., Saturday). The cooling load for a particular hour of the day on a Mon- day depends very little on the requirement 24 h earlier on Sunday. Forrester and W epfer (1984) described a number ofmethods for elim- inating this 24 h indicator. MacArthur et al. (1989) also presented a load profile prediction algorithm that uses a 24 h regressor. Armstrong et al. (1989) presented a very simple method for forecasting either cooling or electrical requirements that does not use the 24 h regressor; Seem and Braun (1991) further developed and validated this method. The "average" time-of-day and time- of-week trends are modeled using a lookup table with time and type of day (e.g., occupied versus unoccupied) as the deterministic input variables. Entries in the table are updated using an exponen- tially weighted, moving-average model. Short-term trends are modeled using previous hourly measurements of cooling require- ments in an autoregressive (AR) model. Model parameters adapt to slow changes in system characteristics. The combination of updating the table and modifying model parameters works well in adapting the forecasting algorithm to changes in season and occu- pancy schedule. Kreider and W ang (1991) used artificial neural networks (ANNs) to predict energy consumption of various HV AC equipment in a commercial building. Data inputs to the ANN included (1) previous hour's electrical power consumption, (2) building occupancy, (3) wind speed, (4) ambient relative humidity, (5) ambient dry-bulb temperature, ⑥ previous hour's ambient dry-bulb temperature, (7) two hours' previous ambient temperature, and (8) sine and cosine of the hour number to roughly represent the diurnal change oftempera- ture and solar insolation. The primary purpose in developing these models was to detect changes in equipment and system performance for monitoring purposes. However, the authors suggested that an ANN-based predictor might be valuable when used to predict energy consumption with a network based on recent historical data. Forecasts of all deterministic input variables are necessary to apply this method. Gibson and Kraft (1993) used an ANN to predict building elec- trical consumption as part of the operation and control of a thermal energy storage (TES) cooling system. The ANN used the following inputs: (1) electric demand of occupants (lighting and other loads), (2) electric demand of TES cooling tower fans, (3) outdoor ambient temperature, (4) outdoor ambient temperature/inside target tem- perature, (5) outdoor ambient relative humidity, ⑥ on/off status for building cooling, (7) cooling system on/off status, (8) chiller #1 direct-cooling mode on/off status, (9) chiller #2 direct-cooling mode on/off status, (10) ice storage discharging mode on/off status, (11) ice storage charging mode on/off status, (12) chiller #1 charging mode on/off status, and (13) chiller #2 charging mode on/ off status. To use this forecaster, values of each of these inputs must be predicted. Although the authors suggest that average occupancy demand profile be used as an input, they do not state how the other input variables should be forecast. Data-Driven Algorithms The development of machine learning and information science has allowed sophisticated data-driven algorithms to be applied in the field of building energy forecasting. A decision (regression) tree is a flow-chart-like structure, where each internal node denotes a test on an attribute, and each branch rep- resents the outcome of a test. The topmost node in a tree is the root node, and the lowermost node is the leaf node. Yu et al. (2010) pro- posed a decision tree method (C4.5) for building energy demand modeling, and found that the C4.5 algorithm can classify and predict building energy demand levels accurately (93% for training data and 92% for test data), identify and rank significant factors of building EUI levels automatically, and provide the combination of significant factors as well as the threshold values that lead to high building energy performance. Chou and Bui (2014) apply a regression tree algorithm (chi- squared automatic interaction detector [CHAID]) to forecast short-term cooling and heating load. However, they find that an ensemble approach (support vector regression [SVR]+ANN) has better prediction accuracy than CHAID. Capozzoli et al. (2015), Idowu et al. (2016), and Williams and Gomez (2016) also examine decision tree algorithms in the modeling process. Ensemble learning is a powerful machine learning method which integrates several base models to generate the final output. It has gained great popularity because ofits excellent generalization perfor- Inc. ASHRAE, 2019 user. single for Licensed | {}
d83c1a6d-a621-443f-82c5-82651687cd3a | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 43.38 mance. Fan et al. (2014) developed ensemble models that more accurately predict next-day energy consumption and peak power demand, compared to eight base models (multiple linear regression, autoregressive integrated moving average, support vector regression, random forests, multilayer perceptron, boosting tree, multivariate adaptive regression splines, and k-nearest neighbors). Jovanovic et al. (2015) use an ensemble consisting of a feed-forward, back- propagation neural network, a radial basis function network, and an adaptive neuro-fuzzy interference system to predict short-term build- ing heating energy consumption. The ensemble model achieves better prediction results than a single network. Deep learning is a class of machine learning algorithms that use a cascade of multiple layers of nonlinear processing units for feature extraction and transformation (Deng and Yu 2014). As an evolution of artificial neural network (ANN)-based prediction methods, it is expected to increase prediction accuracy through higher levels of abstraction, better scalability, and automatic hierarchical feature learning. Mocanu et al. (2016a) investigated two newly developed stochastic models for time-series short-term prediction of energy consumption: conditional restricted Boltzmann machine (CRBM) and factored conditional restricted Boltzmann machine (FCRBM). FCRBM outperform ANN, SVM, recurrent neural networks (RNN), and CRBM models. Mocanu et al. (2016b) also incorporate a deep belief network as an automated feature extraction into short-term building energy modeling process. Other sophisticated predictive algorithms include multivariate adaptive regression splines (MARS) (Cheng and Cau 2014; Wil- liams and Gomez 2016), Bayesian networks (BNs) (O'Neill and O'Neill 2016), extreme learning machine (ELM) (Sajjadi et al. 2016), case-based reasoning (CBR) (Monfet et al. 2014), self- recurrent wavelet neural network (SRWNN) (Chitsaz et al. 2015), meta learning (Cui et al. 2016; Tian et al. 2015), and random forest (RF) (Fan et al. 2014). A Forecasting Algorithm This section presents an algorithm for forecasting hourly cooling requirements or electrical use in buildings that is based on the method developed by Seem and Braun (1991). At a given hour n, the forecast value is E(n) = X(n) + D(h,d) (51) where E(n) = forecast cooling load or electrical use for hour n x (n) = stochastic or probabilistic part of forecast for hour n D(h,d) = deterministic part of forecast at hour n associated with hth hour of day and current day type d The deterministic part of the forecast is simply a lookup table for the forecasted variable in terms of hour of day h and type of day d. Seem and Braun recommend using three distinct day types: unoc- cupied days, occupied days following unoccupied days, and occupied days following occupied days. The three day types account for differences between the building responses associated with return from night setup and return from weekend setup. The building operator or control engineer must specify the number of day types and a calendar of day types. Given the hour of day and day type, the deterministic part of the forecast is simply the value stored in that location in the table. Table entries are updated when a new measurement becomes available for that hour and day type. Updates are accomplished through the use of an exponentially weighted, moving-average (EWMA) model as 2019 ASHRAE Handbook-HVAC Applications (SI) D(h,d) = D(h,d)old + [E(n) - D(h,d)old] (52) where E(n) = measured value of cooling load or electrical use for current hour n = exponential smoothing constant, 0 1 D(h,d)old = previous table entry for D(h,d) As increases, the more recent observations have more influ- ence on the average. As approaches zero, the table entry approaches the average of all data for that hour and day type. When equals one, the table entry is updated with the most recent measured value. Seem and Braun recommend using a value of 0.30 for in conjunction with three day types and 0.18 with two day types. The stochastic portion of the forecast is estimated with a third- order autoregressive model, AR(3), of forecasting errors associated with the deterministic model. With this model, the following equa- tion estimates the next hour's error in the deterministic model fore- cast: X(n + 1)= 1X(n) + 2X(n - 1) + 3X(n - 2) (53) where X(n) =difference between measurement and deterministic forecast of cooling load or electrical use at any hour n 1, 2, 3=parameters of AR(3) model that must be learned The error in the deterministic forecast at any hour is simply X(n) = E(n) - D(h,d) (54) For forecasting more than one hour ahead, conditional expecta- tion is used to estimate the deterministic model forecast errors using the AR(3) model as follows: x n + 2 = x n + 1 + x n + X n - 1 3 1 2 28 n + 1 + 3X n X n + 3 = X n + 2 + 1 28 + k-2 x n + k = x n + k+ 1 + n 1 + x n+k-3 for k>3 3 (55) Inc. ASHRAE, 2019 user. single for Licensed Online estimation of the AR(3) model parameters is accom- plished by minimizing the following time-dependent cost function: n n-k J = X k - x k 2 k=1 (56) where the constant is called the forgetting factor and has a value between 0 and 1. With this formulation, the residual for the current time step has a weight of one and the residual for k time steps back has a weight of k· By choosing a value of that is positive and less than one, recent data have greater influence on the parameter esti- mates. In this manner, the model can track changes caused by seasonal or other effects. Seem and Braun recommend using a for- getting factor of 0.99. Parameters of the AR(3) model should be updated at each hour when a new measurement becomes available. Ljung and Soderstrom (1983) describe online estimation meth- ods for determining coefficients of an AR model. The parameter estimates should be evaluated for stability. If an AR model is not stable, then the forecasts will grow without bound as the time of forecasts increases. Ljung and Soderstrom discuss methods for checking stability. | {}
19ef3828-2a7e-4211-bcbb-f62155b70e38 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Supervisory Control Strategies and Optimization 43.39 Seem and Braun (1991) compared forecasts of electrical usage with both simulated and measured data. Figure 38 shows the stan- dard deviation of the 1 h to 24 h errors in electrical use forecasts for annual simulation results. Results are given for the deterministic model alone, deterministic plus AR(2), and deterministic plus AR(3). For the combined models, the standard deviation of the residuals increases as the forecast length increases. For short time steps (i.e., less than 6 h), the combined deterministic and stochastic models provide much better forecasts than the purely deterministic model (i.e., lookup table). Seem and Braun also investigated a method for adjusting the deterministic forecast based on using weather service forecasts of maximum daily ambient temperature as an input. For short periods (i.e., less than 4 h), forecasts for the temperature-dependent model were nearly identical to forecasts for the temperature-independent model. For longer periods, the temperature-dependent model pro- vided better forecasts than the temperature-independent model. 3.9 PREDICTIVE HV AC CONTROL STRA TEGIES Model predictive control (MPC) is a multivariable control algo- rithm that uses an internal dynamic model of the system, a history of past control moves, forecasts of future disturbances (i.e., weather forecasts), and an algorithm to solve an optimization problem over the receding prediction horizon (i.e., the period for which future informa- tion is available, ranging from a few hours to a few days). The potential of MPC to improve energy management in buildings has been amply demonstrated over the last decade (Cigler et al. 2013; Kummert 2001; Oldewurtel et al. 2012; Touretzky and Baldea 2014). The basic principle of MPC in buildings is that knowledge of forecast weather, anticipated occupancy schedules, and building envelope and system dynamics enable better control of the building energy systems (e.g., by better managing thermal storage capabili- ties). One of the most attractive features of MPC is its ability to specify multi-objective cost functions (e.g., energy consumption and thermal comfort) while handling constraints for states and control (actuator or control set point) variables in a systematic manner. Because of the number of variables and constraints that must be con- sidered, optimization can be complex. Once the optimization algo- rithm determines the optimal sequence of control moves, these moves are applied to a control horizon, which is often shorter than the pre- diction horizon. Chart Type: line 0 6 12 18 24 item_01 1.5kW 3kW 4.5kW 5kW 4.5kW Fig. 38 Standard Deviation of Annual Errors for 1 to 24 h Forecasts Setting up a suitable control-oriented model for the building is crucial for MPC. The degree of modeling effort is difficult to assess in advance, because each model is typically tailored for one specific building. MPC design requires a degree of knowledge of building modeling, such as good understanding on what details are appropri- ate to include or exclude in the control model. Li and Wen (2014) provide a detailed literature review on reported modeling approach- es for MPC purposes. Considerable research has been performed on methods for ob- taining reliable models for building systems. The primary focus of research has been to select a proper model structure and identifica- tion algorithm. Various model structures, including black-box types (e.g., autoregressive with exogenous inputs [ARX], autoregressive moving-average with exogenous inputs [ARMAX], state-space forms) and gray-box types, have been investigated. Many identifi- cation algorithms developed from other fields, such as signal processing and statistics, have been applied to the field of building science. Popular methods are least squares (Armstrong et al. 2006a), prediction error (Kim et al. 2016), maximum likelihood (Bloem 1994), and subspace identification (Ferkl and Siroky 2011). Other identification methods, such the identification for long-range predictive control (Privara et al. 2013), extended or unscented Kal- man filters, and machine learning methods, also have been applied to building systems. Case study comparisons between several model structures and algorithms can be found in Bacher and Madsen (2011), Jimenez and Madsen (2008), and Privara et al. (2013). One of the most popular modeling approaches is to develop a low-order resistance-capacitance (RC) thermal network to represent the building. The parameters of this gray-box model should be cal- ibrated by using real measurement data from the existing building. Purely data-driven models are reliable and robust, but they cannot be easily applied in other buildings. Simulation studies often use two building models: a simulation model, meant to represent the building as accurately as possible, and a control-oriented model, a simpler representation that facilitates solution of the optimization problem (Hu and Karava 2014; Morosan et al. 2010; Oldewurtel et al. 2012). In field studies or experiments, only the control-oriented model is necessary (De Coninck and Helsen 2016). Li et al. (2015) demonstrate the effectiveness of a linear-zone dynamic state-space model in a field demonstration of MPC in a medium-sized commer- cial building. Nonlinear forecasting models, such as those based on neural net- works (NNs), have also been investigated as alternatives to traditional time-series analysis. Florita and Henze (2009) sought to identify the complexity required for short-term weather forecasting in the context of a MPC environment. Moving average (MA) mod- els with various enhancements and neural network models were used to predict weather variables seasonally in numerous geograph- ic locations. Their performance was statistically assessed using the coefficient of variation (CV) and mean bias error (MBE) values. When a cyclical two-stage MPC process of policy planning fol- lowed by execution was used, Florita and Henze (2009) found that even the most complicated nonlinear autoregressive neural network with exogenous input does not appear to warrant the additional ef- forts in forecasting model development and training, in comparison to the simpler MA models. Predictive control strategies for both passive and discrete thermal storage systems have been studied (Braun 2003; Henze 2003) and field tested (Krarti et al. 2007; Morgan and Krarti 2010). Morgan and Krarti (2010) investigated performance of various control strategies for combined passive and discrete TES systems in a Col- orado elementary school equipped with an ice storage system. The predictive optimal control strategies were developed using an EnergyPlus-based simulation environment (Krarti et al. 2007; Zhou et al. 2005). The simulation environment was found to be effective in defining and implementing predictive optimal controls for both Inc. ASHRAE, 2019 user. single for Licensed | {}
74ee5769-28aa-409e-a84b-2808eb97c9a6 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 43.40 2019 ASHRAE Handbook- -HVAC Applications (SI) BUILDING ELECTRICAL CONSUMPTION PROFILES Chart Type: line 12:00 AM 6:00 AM 12:00 PM 6:00 PM item_01 30kWh 30kWh 90kWh 30kWh Fig. 39 Building Electricity Use Profiles for 6 h Predictive Optimal Control BUILDING ELECTRICAL CONSUMPTION PROFILES Chart Type: line 12:00 AM 6:00 AM 12:00 PM 6:00 PM item_01 40kWh 30kWh 90kWh 30kWh Fig. 40 Building Electricity Use Profiles for 24 h Predictive Optimal Control passive and discrete TES systems for the buildings. Figures 39 and 40 show examples of the field testing results for the building energy use performed by Morgan and Krarti (2010). An alternative to a formal MPC approach for identifying optimal temperature set points consists of implementing simple linear ramp- ing profiles in place of abrupt setup or setback profiles. Gradual ramps over a given period of time can significantly reduce the peak power demand required to change from one set point value to an- other, as demonstrated in Date et al. (2016a, 2016b) and Morris et al. (1994). Ramp set-point profiles with different start times can be used in different zones of a building to stagger when heating the zones begins. By staggering the start times, building heating de- mand is smoothed over a certain period. Preheating by a few degrees can also be used when transitioning from night setback to a comfort temperature. By preheating during an off-peak time and to a temperature that is still satisfactory to occupants, the peak demand during critical times can be further reduced. Predetermined rules of operation based on building dynamics and short-term dynamics allow optimization of building operation. For example, Candanedo et al. (2015) proposed near-optimal profiles for transitioning between night setback and a daytime temperature profile. This op- timal transition curve, which significantly reduces peak load in this period, depends only on the time constant ofthe space and the "tran- sition time" established by the building operator. % EFFICIENCY, % EFFICIENCY, Chart Type: line 100 50 item_01 30kPa 70kPa Fig. 41 Effect of Percent of Excess Air on Combustion Efficiency BEI (1991). Copyright 1991 by the Boiler Efficiency Institute. Reprinted by permission from Boiler Efficiency Improvement. 3.10 CONTROL STRATEGIES FOR HEATING SYSTEMS Boiler efficiency depends on many factors, such as combustion airflow rate, load factor, and water temperature in hot-water boilers (or pressure for steam boilers). Opportunities for energy and cost reduction in boiler plants by supervisory control include sequencing and loading of multiple boilers and resetting the hot-water supply temperature set point (for hot-water boilers) or the steam pressure set point (for steam boilers) (Dyer and Maples 1981). Excess Air in Combustion Process Combustion would occur with greatest efficiency (stoichio- metric combustion) if air and fuel could be mixed in the exact proportions indicated in the chemical reaction equation. The ratio of the volume of air needed to burn completely one unit volume of the fuel is known as the stoichiometric air/fuel ratio. The heat released when the fuel burns completely is called the heat of combustion. In practice, it is impossible to achieve stoichiometric combus- tion because burners cannot mix air and fuel perfectly. In combustion processes, excess air is generally defined as air intro- duced above the stoichiometric or theoretical amount required for complete combustion of the fuel. Only the minimum amount of excess air to ensure complete combustion should be supplied to the burner; more air increases the heat rejected to the stack and reduces efficiency. Combustion efficiency depends on the amount of excess air (or oxygen [O2]) in the flue gas, stack temperature rise above Inc. ASHRAE, 2019 user. single for Licensed | {}
8e48e616-f24c-4a7a-9bfe-66411ca217fb | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Supervisory Control Strategies and Optimization 43.41 X-Axis: OXYGEN IN FLUE GAS, % Y-Axis: CARBON MONOXIDE IN FLUE GAS, mg/kg Chart Type: line Upper CO LIMIT Low Fire High Fire item_01 2mg/kg 3mg/kg 1mg/kg Fig. 42 Hypothetical CO-O2 Characteristic Combustion Curves for a Gas-Fired Industrial Boiler Parker et al. (1997). Copyright 1997 by Fairmont Press, Inc. 700 Indian Trail, Lilburn, GA 30047, www.fairmontpress.com Reprinted by permission from Energy Management Handbook. burner inlet air temperature, and amount of unburned hydrocar- bons. As shown in Figure 41, combustion efficiency drops sharply when deficient air is supplied to the burner: the amount ofunburned hydrocarbons rises sharply, thereby wasting fuel. Operating a boiler with high excess air also heats the air unnecessarily, resulting in lower combustion efficiency. Combustion efficiency is opti- mized when excess air is reduced to the minimum. To determine the minimum excess air for a particular boiler, flue gas combustible content as a function of excess O2 should be charted as shown in Figure 42. For a gas-fueled boiler, carbon monoxide should be monitored; for liquid or solid fuel, monitor the smoke spot number (SSN). Different firing rates should be considered because the excess air minimum varies with the firing rate (percent load). Fig- ure 42 shows curves for high and low firing rates. As shown, low firing rates generally produce a more gradual curve; high-rate curves are steeper. For burners and firing rates with a steep combustible con- tent curve, small changes in the amount of excess O2 may cause unstable operation. The optimal control set point for excess air should generally be 0.5 to 1% above minimum, to allow for slight variations in fuel composition, intake air temperature and humidity, barometric pressure, and control system characteristics. Table 8 lists typical, normally attainable optimum excess air levels, classified by fuel type and firing method. Carbon monoxide upper control limits vary with the boiler fuel used. The CO limit for gas-fired boilers may be set typically at 400, 200, or 100 mg/kg. For No. 2 fuel oil, the maximum SSN is typically 1; for No. 6 fuel oil, SSN = 4. However, for any fuel used, local envi- ronmental regulations may require lower limits. To maintain safe unit output conditions, excess air require- ments may be greater than the levels indicated in this table. This condition may arise when operating loads are substantially less than the design rating. Where possible, the vendor's predicted per- formance curves should be checked. If they are unavailable, excess air should be reduced to minimum levels consistent with satisfactory output. Oxygen Trim Control. An oxygen trim control system adjusts the airflow rate using an electromechanical actuator mounted on the boiler's forced-draft fan damper linkage, and measures excess oxygen using a zirconium oxide sensor mounted in the boiler stack. The oxygen sensor signal is compared with a set point value obtained from the boiler's excess air set point curve for the given firing rate. The oxygen trim controller adjusts ("trims") the damper setting to regulate the oxygen level in the boiler stack at this set Table 8 Typical Optimum Excess Air for Various Boiler Types ¦ Fuel Type ¦ Firing Method ¦ Optimum Excess Air, % ¦ Equivalent O2 (by Volume) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Natural gas ¦ Natural draft ¦ 20-30 ¦ 4-5 ¦ ¦ ¦ Forced draft ¦ 5-10 ¦ 1-2 ¦ ¦ ¦ Low excess air ¦ 0.4-2.0 ¦ 0.1-0.5 ¦ ¦ Propane ¦ ¦ 5-10 ¦ 1-2 ¦ ¦ Coke oven gas ¦ ¦ 5-10 ¦ 1-2 ¦ ¦ No. 2 oil ¦ Rotary cup ¦ 15-20 ¦ 3-4 ¦ ¦ ¦ Air-atomized ¦ 10-15 ¦ 2-3 ¦ ¦ ¦ Steam-atomized ¦ 10-15 ¦ 2-3 ¦ ¦ No. 6 oil ¦ Steam-atomized ¦ 10-15 ¦ 2-3 ¦ ¦ Coal ¦ Pulverized ¦ 15-20 ¦ 3-3.5 ¦ ¦ ¦ Stoker ¦ 20-30 ¦ 3.5-5 ¦ ¦ ¦ Cyclone ¦ 7-15 ¦ 1.5-3 ¦ Source: Reprinted from Energy Management Handbook, 8th ed. (Steve Doty and Wayne C. Turner) by special permission of The Fairmont Press, Inc., 700 Indian Trail, Lilburn, GA 30047 (www. .fairmontpress.com). point. In the event of an electronic failure, the boiler defaults to the air setting determined by the mechanical linkages. Carbon Monoxide Trim Control. Carbon monoxide trim con- trol systems are also used to control excess air, and offer several advantages over oxygen trim systems. In carbon monoxide trim sys- tems, the amount of unburned fuel (in the form of carbon monoxide) in the flue gas is measured directly by a carbon monoxide sensor and the air/fuel ratio control is set to actual combustion conditions rather than preset oxygen levels. Thus, the system continuously controls for minimum excess air. Carbon monoxide trim systems are also inde- pendent of fuel type and are virtually unaffected by combustion air temperature, humidity, and barometric pressure conditions. How- ever, they cost more than oxygen trim systems because of the expense of the carbon monoxide sensor. Also, the carbon monoxide level in the boiler stack is not always a measure of excess air. A dirty burner, poor atomization, flame chilling, flame impingement on the boiler tubes, or poor fuel mixing can also raise the carbon monoxide level in the boiler stack (Taplin 1998). Sequencing and Loading of Multiple Boilers Generally, boilers operate most efficiently at a 65 to 85% full-load rating. Boiler efficiencies fall off at higher and lower load points, with the decrease most pronounced at low loads. Boiler efficiency can be calculated by means of stack temperature and percent O2 (or percent excess air) in the boiler stack for a given fuel type. Part-load curves of boiler efficiency versus hot-water or steam load should be developed for each boiler. These curves could be dynamically updated at discrete load levels based on the hot-water or steam plant characteristics to allow the control strategy to continuously predict the input fuel requirement for any given heat load. When the hot- water temperature or steam pressure drops below set point for the predetermined time interval (e.g., 5 min), the most efficient combi- nation of boilers must be selected and turned on to meet the load. The least efficient boiler should be shut down and banked in hot standby if its capacity drops below the spare capacity of the current number of boilers operating (or, for primary/secondary hot-water systems, if the flow rate of the associated primary hot-water pump is less than the difference between primary and secondary hot-water flow rates) for a predetermined time interval (e.g., 5 min). The spare capacity of the current online boilers is equal to their full-load capacity minus the current hot water load. Load Conditions for Bringing Boilers Online or Off-Line The specifics of the strategy for bringing boilers online depend on the type of boiler. Hot-water boilers have dedicated or nondedi- Inc. ASHRAE, 2019 user. single for Licensed | {}
57f1d208-210b-48f3-856f-2f48c7376194 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 43.42 2019 ASHRAE Handbook - HVAC Applications (SI) cated hot-water pumps; steam boilers do not have hot-water pumps, but rely on differences in steam pressure between the boiler steam header discharge and the point of use to distribute steam throughout the system. Hot- w ater Boilers with Dedicated Pumps. The strategy for hot-water boilers with dedicated hot-water pumps is similar to that for chillers with dedicated chilled-water and condenser water pumps: another boiler should be brought online when operating boil- ers reach capacity, because the efficiency of the boiler should include the power to drive its associated hot-water pump. This can be deter- mined when hot-water temperature drops below its set point for a predetermined time interval (e.g., 5 min). Hot-water boilers with dedicated pumps can be brought online and off-line with the following logic: 1. Continuously calculate the load ratio of each boiler or boiler combination. For the ith boiler, Qload LRi= �blr,des,i where LRi is load ratio of the ith boiler combination, Qload is the total boiler plant load, and �blr,des,i is the design (rated) output of the ith boiler combination. 2. Every sampling interval (e.g., 60 s), calculate the predicted input fuel requirement for each boiler combination as LRi 0 blr,des,i IF/= i (58) Inc. ASHRAE, 2019 user. single for Licensed where IFi is the input fuel requirement and ⌀is the efficiency of the ith boiler combination. 3. Continuously evaluate time-averaged values of the hot-water supply temperature over a fixed time interval (e.g., 5 min). 4. Ifthe hot-water supply temperature drops below its set point for a predetermined time interval (e.g., 5 min), then, from boiler part-load performance curves, select the boiler combination with a load ratio between 0.5 and 1.0 and with the least input fuel re- quirement to meet the load, and turn this combination of boilers on. Note that this strategy greatly reduces the possibility of short-cycling boilers because the new combination of boilers to be started likely includes boilers already operating (i.e., only one additional boiler is likely to be added). 5. Ifthe capacity of the least-efficient online boiler drops below the spare capacity of the current number of boilers operating (or for a primary/secondary hot-water system, if the flow rate of the associated primary hot-water pump is less than the difference between primary and secondary hot-water flow rates) for a pre- determined time interval (e.g., 5 min), then shut down and bank this boiler in hot standby. (57) Hot- Water Boilers with Nondedicated Pumps or Steam Boilers. For hot-water systems without dedicated hot-water pumps or for steam systems, the optimal load conditions for bringing boil- ers online or off-line do not generally occur at the full capacity ofthe online boilers. For these systems, a new boiler combination should be brought online whenever the hot-water supply temperature or steam pressure falls below set point for a predetermined time interval (e.g., 5 min) and the part-load efficiency curves ofthe boiler combination predicts that the new combination of boilers can meet the required load using significantly less (e.g., 5%) input fuel. Optimal Boiler Load Distribution Optimal load distribution strategies for boilers are similar to those for chillers. For boilers with similar performance character- istics, the optimal boiler loading is similar to Equation (27) for chillers: 0 load 0 0 blrj N blr ,des i �blr,des,i i=1 is the optimal load for the ith boiler. where Obilers For with significantly different performance characteris- tics, the criterion for optimal boiler loading is similar to Equations (28) and (29) for chillers, except that boiler cost of operation is used: for all i and i Cblr,i Cblrj = Q 0 blr,i blrj (60) (59) N and subject to the constraint that = �blr,i 0 i=1 l⌀ad (61) where Cblr,i and Cblr.j. are the operating costs of boiler i and j, respectively, �blr,i is heating load for the ith boiler, and Qload is total heating load. In general, the boiler operating-cost curve can be calculated as a quadratic function of heating load only. For the ith boiler, Cblr,i = bo,i⌀blr,i +b1,i�blri + b2,i Applying the criterion of Equation (60) to Equation (62), (62) 2b0,i⌀blr,i + by⌀ = 2boj⌀blrj + byj is the optimal load for the ith boiler. where ⌀blri (63) Maintaining Boilers in Standby Mode Itis generally more economical to run fewer boilers at a high rat- ing. However, the integrity of the steam or hot-water supply must be maintained in the event of a forced outage of one of the operating boilers or if the facility experiences highly diverse load swings throughout the heating season. Both conditions can often be satis- fied by maintaining a boiler in standby or "live bank" mode. For example, in this mode, a steam boiler is isolated from the steam sys- tem at no load but is kept at system operating pressure by periodic firing of either the igniters or a main burner to counteract ambient heat losses. Supply Water and Supply Pressure Reset for Boilers Standby losses are reduced and overall efficiencies enhanced by operating hot-water boilers at the lowest acceptable temperature. Condensing boilers achieve significantly higher combustion efficien- cies at water temperatures below the flue gas dew point when they are operating in condensing mode (see Chapter 32 in the 2016 ASHRAE Handbook-HVAC Systems and Equipment). Hot-water boilers of this type are very efficient at part-load operation when a high water temperature is not required. Energy savings are therefore possible if the supply water temperature is maintained at the minimum level required to satisfy the largest heating load. However, to minimize con- densation of flue gases and consequent boiler damage from acid, water temperature should not be reset below that recommended by the boiler manufacturer (typically 60°C). Similarly, energy can be saved in steam heating systems by maintaining supply pressure at the min- imum level required to satisfy the largest heating load. Simple control strategies can be used to generate a suboptimal hot-water temperature (for hot-water boilers) or steam pressure (for steam boilers). An energy management and control system must be interfaced to the boiler controls and be capable of monitoring the position ofthe valve controlling the flow ofhot water to the heating | {}
4bffe745-8bea-4a2c-abbb-40730cbeebe0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Supervisory Control Strategies and Optimization 43.43 coils or steam pressure at the most critical zone. For a hot-water system, 1. Continuously monitor the hot-water valve position of the various heating zones. 2. Ifnone of the hot-water valves are greater than 95% open, lower boiler hot-water supply temperature by a small increment (e.g., 0.5 K) each reset time interval (a predetermined interval estab- lished by system thermal lag characteristics, e.g., 15 to 20 min). 3. Once one hot-water valve opens beyond 95%, stop downward resets of boiler hot-water temperature set point. 4. If two or more hot-water valves open beyond 95%, raise boiler hot-water temperature set point by a small increment (e.g., 0.5 K) each reset interval. For a steam system, the steam header pressure should be low- ered to a value that just satisfies the highest pressure demand. Caution: for nongravity condensate return systems, steam pres- sure reset could impede condensate return (see Chapter 10 of the 2008 ASHRAE Handbook-HVAC Systems and Equipment). Operating Constraints Note that there are practical limitations on the extent of auto- matic operation if damage to the boiler is to be prevented. Control strategies to reduce boiler energy consumption can also conflict with recommended boiler operating practice. For example, in addi- tion to the flue gas condensation concerns mentioned previously, rapid changes in boiler jacket temperature (thermal shock) brought about by abrupt changes in boiler water temperature or flow, firing rate, or air temperature entering the boiler should be avoided. The repeated occurrence of such transient conditions may weaken the metal and lead to cracking and/or loose tubes. It is therefore important to follow all of the recommendations of the American Boiler Manufacturers Association (ABMA 1998). 3.11 CONTROL STRA TEGIES FOR AIR-HANDLING UNITS Air Handler Sequencing and Economizer Cooling Traditional air-handler sequencing strategies use a single proportional-integral (PI) controller to control heating, cooling with outdoor air, mechanical cooling with 100% outdoor air, and mechanical cooling with minimum outdoor air. Sequencing between these different modes is accomplished by splitting the controller output into different regions of operation, as shown in Figure 43. Figure 43 depicts the relationship between the control signal to the valves and dampers and the feedback controller output. The con- troller adjusts its output to maintain the supply air temperature set point. If output is between 100 and 200%, mechanical cooling is used. When outdoor conditions are suitable, the outdoor air dampers X-Axis: Feedback Controller Output, % Y-Axis: Control Signal Chart Type: line Heating-Coil Valve Outdoor Air Damper Cooling-Coil Valve item_01 100% 0% 200% Fig. 43 AHU Sequencing Strategy with Single Feedback Controller switch from minimum position (minimum ventilation air) to fully open. For a dry-bulb economizer, this switch point occurs when ambient air is less than a specified value. This switch point should be less than the switch point to return to minimum outdoor air, to ensure stable control. The economizer switchover temperature may be significantly lower than the return air temperature (e.g., 5 K lower) in humid climates where latent ventilation loads are signifi- cant. However, in dry climates, the switchover temperature may be close to the return temperature (e.g., 24°C). An enthalpy (or wet- bulb) economizer compares outdoor and return air enthalpies (or wet-bulb temperatures) to initiate or terminate economizer opera- tion. In general, enthalpy economizers yield lower energy costs than dry-bulb economizers, but require measurements of outdoor and return air humidity. Humidity sensors require regular maintenance to ensure accurate readings. When controller output is between 0 and 100% (see Figure 43), the cooling coil valve is fully closed and cooling is provided by ambient air only. In this case, the controller output modulates the position of the outdoor air dampers to main- tain the set point. Ifthe controller output signal is between -100 and 0%, the heating coil is used to maintain set point and the outdoor air dampers are set at their minimum position. A single feedback controller is difficult to tune to perform well for all four modes of operation associated with an AHU. An alternative to the traditional sequencing strategy is to use three separate feed- back controllers, as described by Seem et al. (1999). This approach can improve temperature control, reduce actuator usage, and reduce energy costs. Figure 44 shows a state transition diagram for imple- menting a sequencing strategy that incorporates separate feedback controllers. In state 1, a feedback controller adjusts the heating valve to main- tain the supply air set-point temperature with minimum outdoor air. The transition to state 2 occurs after the control signal has been satu- rated at the no-heating position for a period equal to a specified state transition delay (e.g., 3 min). In state 2, a second feedback controller adjusts the outdoor and return air dampers to achieve set point with heating and cooling valves closed. Transition back to state 1 only occurs after the damper control signal is saturated at its minimum value for the state transition delay, whereas transition to state 3 is associated with saturation at the maximum damper position for the ![image](/image/placeholder) STATE 1 Feedback Control of Heating Coil (minimum outdoor air with no mechanical cooling) Damper Control Signal Heating Control Signal Saturated at Minimum Value Saturated at Maximum Value STATE 2 Feedback Control of Dampers (no heating and mechanical cooling) Cooling-Coil Control Signal Damper Control Signal Saturated at Minimum Value Saturated at Maximum Value STATE 3 Feedback Control of Cooling Coil (maximum outdoor air and no heating) Outdoor Air Condition Outdoor Air Condition (temperature (temperature or enthalpy) is less or enthalpy) is greater than than switchover condition switchover condition plus dead band STATE 4 Feedback Control of Cooling Coil (minimum outdoor air and no heating) Fig. 44 AHU Sequencing Strategy with Multiple Feedback Controllers Inc. ASHRAE, 2019 user. single for Licensed | {}
4b910df7-082b-4fea-93b7-173d961148de | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 43.44 2019 ASHRAE Handbook-HVAC Applications (SI) state transition delay. In state 3, the outdoor air damper remains fully open and a third feedback controller is used to adjust the flow of cool- ing water to maintain the supply air temperature at set point. Transi- tion back to state 2 occurs if the controller output is saturated at its minimum value for the state transition delay. For a dry-bulb econo- mizer, transition to state 4 occurs when the ambient dry-bulb temperature is greater than the switchover temperature by a dead band (e.g., 1 K). The feedback controller continues to modulate the cool- ing-coil valve to achieve set point. Transition back to state 3 occurs when the ambient dry-bulb is less than the switchover temperature (e.g., 18°C). For an enthalpy economizer, the ambient enthalpy is compared with return air enthalpy to initiate transitions between states 3 and 4. Supply Air Temperature Reset for Constant Air Volume (CA V) The benefits ofresetting supply air temperature set points for CAV systems are significant. Increasing the supply air set point for cooling reduces both the cooling and reheat required, but does not change fan energy. In general, the set point for a CAV system could be set at the highest value that will keep all zone temperatures at their set points and all humidities within acceptable limits. A simple reset strategy based on this concept follows. At each the decision interval (e.g., 5 min), the following logic can be applied: 1. Check controller outputs for representative zone reheat units and determine time-averaged values over the last decision interval. 2. If any controller output is less than a threshold value (e.g., 5%), then decrease the supply air set point by a fixed value (e.g., 0.25 K) and go to step 4. Otherwise, go to step 3. 3. If all zone humidities are acceptable and all controller outputs are greater than a threshold value (e.g., 10%), then increase the discharge air set point by a fixed value (e.g., 0.25 K) and go to step 4. Otherwise, do not change the set point. 4. Limit the set point between upper and lower limits based on com- fort considerations. Static Pressure Reset for Variable Air Volume (VAV) Flow may be modulated in a VAV system by using dampers on the outlet side of the fan, inlet vanes on the fan, vane-axial fans with controllable pitch fan blades, or variable-speed control of the fan motor. Typically, inputs to any of these controlled devices are mod- ulated to maintain a duct static pressure set point as described in Chapter 48. In a single-duct VA V system, the duct static pressure set point is typically selected by the designer to be a fixed value. The sensor is located at a point in the ductwork such that the established set point will ensure proper operation of the zone VA v boxes under varying load (supply airflow) conditions. A shortcoming of this approach is that static pressure is controlled based on a single sensor intended to represent the pressure available to all VAV boxes. Poor location or malfunction of this sensor will cause operating prob- lems. Inc. ASHRAE, 2019 user. single for Licensed For a fixed static pressure set point, all of the VA V boxes tend to close as zone loads and flow requirements decrease. Therefore, flow resistance increases with decreasing load. Significant fan energy savings are possible ifthe static pressure set point is reset so that at least one of the VAV boxes remains open. With this approach, flow resistance remains relatively constant. Englander and Norford (1992), Hartman (1993), W arren and Norford (1993), and Wei et al. (2004) proposed several different strategies based on this concept. Englander and Norford used simulations to show that either static pressure or fan speed can be controlled directly using a flow error signal from one or more zones and simple rules. Their technique forms the basis of the following reset strategy. At each decision interval (e.g., 5 min), the following logic can be applied: 1. Check the controller outputs for representative VAV boxes and determine time-averaged values over the last decision interval. 2. If any of the controller outputs are greater than a threshold value (e.g., 98%), then increase the static pressure set point by a fixed value (e.g., 5% ofthe design range) and go to step 4. Otherwise, go to step 3. 3. If all controller outputs are less than a threshold value (e.g., 90%), then decrease the static pressure set point by a fixed value (e.g., 5% of the design range) and go to step 4. Otherwise, do not change the set point. 4. Limit the set point between upper and lower limits based on upper and lower flow limits and duct design. 3.12 CONTROL STRATEGIES FOR BUILDING ZONES Recovery from Night Setback or Setup For buildings that are not continuously occupied, significant savings in operating costs may be realized by raising the building set-point temperature for cooling (setup) and by lowering the set point for heating (setback) during unoccupied times. Bloomfield and Fisk (1977) showed energy savings of 12% for a heavyweight building and 34% for a lightweight building. An optimal controller for return from night setback or setup re- turns zone temperatures to the comfort range precisely when the building becomes occupied. Seem et al. (1989b) compared seven dif- ferent algorithms for minimum return time. Each method requires estimating parameters from measurements of the actual return times from night setback or setup. Seem et al. (1989b) showed that the optimal return time for cooling was not strongly influenced by the outdoor temperature. The following quadratic function ofthe initial zone temperature was found to be adequate for estimating the return time: (64) = ao + a1tz,i + a2tzj where is an estimate of optimal return time, tz.i is initial zone tem- perature at the beginning of the return period, and ao, a1, and a2 are empirical parameters. The parameters of Equation (51) may be esti- mated by applying linear least-squares techniques to the difference between the actual return time and the estimates. These parameters may be continuously corrected using recursive updating schemes as outlined by Ljung and Soderstrom (1983). For heating, Seem et al. (1989b) found that ambient temperature has a significant effect on the return time and that the following rela- tionship works well in correlating return times: = ao + (1 - w)(a1tz,i + a2tz,i ) + wa3ta where ta is the ambient temperature, and w is a weighting function given by (65) 「ェ」 - tunoce loce / unoce w = 1000 (66) where tunocc and tocc are the zone set points for unoccupied and occu- pied periods. In the context of Equation (52), this function weights the outdoor temperature more heavily when the initial zone tem- perature is close to the set-point temperature during the unoccupied time. Again, the parameters of Equation (52) may be estimated by applying linear least-squares techniques to the difference between the actual return time and the estimates. | {}
690dfc79-fd98-44df-898f-17b9da482d9d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Supervisory Control Strategies and Optimization 43.45 ![image](/image/placeholder) tsetpoint PRECOOLING STRATEGY NIGHT SETUP CONTROL t OCC t pre TIME OCCUPIED PERIOD 6:00 A.M. 7:30 P.M. Fig. 45 Zone Air Temperature Set Points Ideally, separate equations should be used for zones that have significantly different return times. Equipment operation is initiated for the zone with the earliest return time. In a building with a central cooling system, the equipment should be operated above some min- imum load limit. With this constraint, some zones need to be returned to their set points earlier than the optimum time. Optimal start algorithms often use a measure of the building mass temperature rather than the space temperature to determine return time. Although use of space temperature results in lower energy costs (i.e., shorter return time), the mass temperature may result in better comfort conditions at the time of occupancy. Emergency Strategy to Limit Peak Cooling Requirements Keeney and Braun (1997) developed a simple control strategy that uses building thermal mass to reduce peak cooling require- ments a chiller is lost. This emergency strategy is used only on days where cooling capacity is not sufficient to keep the building in the comfort range using night setup control. It involves precooling the building during unoccupied times and allowing the temperature to float through the comfort zone during occupancy. The precooling control strategy is depicted in Figure 45 along with conventional night setup control. Precooling is controlled at a constant temperature set point tpre. The warm-up period is used to reset the zone air temperature set point so that the cooling system turns off without calling for heating. During this time, the zone air is warmed by lighting and equipment loads. The occupied set point tocc is set at the low end of the comfort region so that the building mass charge is held as long as cooling capacity is available. This set point is maintained until the limit on cooling capacity is reached. After this point, temperatures in the zones float up and the building thermal mass provides additional cooling. If the precooling and occupied set points have been chosen properly and the cooling capacity is sufficient, zone conditions will remain comfortable throughout the occupied period. The peak cooling requirement can be reduced by as much as 25% using this strategy as compared with night setup control. Thus, the loss of one of four identical chillers could be tolerated. This strategy could also be used for spaces such as auditoriums that have a high occupancy density for a short period. The length of time and temperature for precooling and the occu- pied temperature set point chosen for this strategy strongly influence the capacity reduction and could affect occupant comfort. A reasonable strategy is to precool at 20°C beginning at midnight, allow a 30 min warm-up period before occupancy, and then adjust the occupied set point to 21°C. The zone temperature will then rise above this set point when the chillers are operating at capacity. Case Study. The control strategy was tested in a 130 000 m2 of- fice building located near Chicago, Illinois (Keeney and Braun 1997). The facility has two identical buildings with very similar in- X-Axis: TIME Y-Axis: TOTAL CHILLER LOAD, MW Chart Type: line SUN MON TUE WED THU FRI item_01 0.7MW 4.2MW 2.8MW 3.5MW 1.3MW 2.7MW Fig. 46 Total Coil Load for East and West Chiller Units ternal gains and solar radiation loads, connected by a large, separately cooled entrance area. During tests, the east building used the existing building control strategy and the west building used the precooling strategy. Four 3200 kW vapor compression chillers normally provide chilled water to the air-handling units. Loss of one chiller results in a 25% reduction of the total capacity. This condition was simulated by limiting the vane position of the two chiller units that cool the west building to 75%. The capacity limitation was imposed directly at the chiller control panels. Set points were provided to local zone controllers from a modern energy management and control system. Chiller cooling loads and zone thermal comfort conditions were monitored throughout the tests. Consistent with simulation predictions, the precooling control strategy successfully limited the peak load to 75% of the cooling capacity for the west building, whereas the east building operated at 100% of capacity. Figure 46 shows the total chiller coil load for the east and west buildings for a week of testing in the middle of August 1995. The cooling-coil load profile on Monday is the most dramatic example ofload shifting during this test period. The peak cooling load for this facility often occurs on Monday morning. The cooling limit was achieved on Monday during a period in which a heat emergency had been declared in the city. The severe ambient conditions were compounded by a power outage that caused a loss of the west-side chiller units for approximately 20 min. Under these demanding con- ditions, the precooling strategy maintained occupant comfort while successfully limiting cooling demand of the west side of the building to less than 75% of that for the east side. The east-side cooling requirement was at or below the 75% chiller capacity target for Tuesday through Friday, so the emergency precooling strategy was not necessary. For these off-design days, the emergency strategy was not effective in reducing the on-peak cooling requirements because discharge of the mass was not initiat- ed when capacity was below the target. The thermal mass remained charged so that peak reduction would occur if the target value on the off-design days were reset to a lower value. Precooling the top floor of the facility had already been imple- mented into the conventional control strategy used for the east building. This was necessary to maintain comfort conditions with full cooling capacity on hot days. As a result, even greater peak reduction would have been recorded ifthe precool strategy had been compared with conventional night setup control. The total electrical use was greater for the precooled west building; however, the strat- Inc. ASHRAE, 2019 user. single for Licensed | {}
4f7b0ffd-4ac7-4983-b143-a33cd85c2949 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 43.46 2019 ASHRAE Handbook-HVAC Applications (SI) egy was designed for an emergency and does not attempt to mini- mize costs. This emergency strategy should only be applied on days when the available cooling capacity is not sufficient to maintain comfort conditions when using night setup control. Otherwise, the costs of providing cooling could increase significantly. ASHRAE research project RP-1313 (Cheng et al. 2008; Henze et al. 2007, 2008) devel- oped simplified strategies for optimal control of building zone set points to minimize operating costs. REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. ABMA. 1998. Guideline for the integration of boilers and automated con- trol systems in heating applications. American Boiler Manufacturers Association, Arlington, VA. Andresen, I., and M.J. Brandemuehl. 1992. Heat storage in building thermal mass: A parametric study. ASHRAE Transactions 98(1). Paper AN-92- 08-3. Armstrong, P.R., T.N. Bechtel, C.E. Hancock, S.E. Jarvis, J.E. Seem, and T.E. Vere. 1989. Environment for structured implementation of general and advanced HVAC controls-Phase II. Ch. 7: Small business innova- tive research program. DOE Contract DE-AC02-85ER 80290. Armstrong, P.R., J.A. Dirks, R. W. Reilly, J.W. Currie, R.J. Nesse, B. Nekrasov, and O.V. Komarov. 2000. Russian apartment building ther- mal response models for retrofit selection and verification. 2000 ACEEE Summer Study on Energy Efficiency in Buildings. web.mit.edu/ parmstr/www/pubs/verif6.pdf. Armstrong, P.R., L.K. Norford, and S.B. Leeb. 2006a. Control with building mass-Part I: Thermal response model identification. ASHRAE Transac- tions 112(1). Armstrong, P.R., L.K. Norford, and S.B. Leeb. 2006b. Control with building mass- Part II: Simulation. ASHRAE Transactions 112(1). Armstrong, P.R., S. Katipamula, W. Jiang, D. Winiarski, and L.K. Norford. 2009. Efficient low-lift cooling with radiant distribution, thermal storage and variable-speed chiller controls, Part II: Annual energy use and sav- ings. HVAC&R Research (now Science and Technology for the Built Environment) 15(2):402-432. ASHRAE. 2016. Energy standard for buildings except low-rise residential buildings. ANSI/ASHRAE/IES Standard 90.1-2016. ASHRAE. 2014. Method of testing the performance of cool storage systems. ANSI/ASHRAE Standard 150-2000 (RA 2014). Bacher, P., and H. Madsen. 2011. Identifying suitable models for the heat dynamics of buildings. Energy and Buildings 43(7):1511-1522. BEI. 1991. Boiler efficiency improvement. Boiler Efficiency Institute, Auburn, AL. Bellman, R. 1957. Dynamic programming. Princeton University Press, Princeton, NJ. Bloem, J. 1994. System identification applied to building performance data. Office for Official Publications of the European Communities. Bloomfield, D.P., and D.J. Fisk. 1977. The optimization of intermittent heating. Buildings and Environment 12:43-55. Brandemuehl, M.J., and J. Bradford. 1998. Implementation of online optimal supervisory control of cooling plants without storage (RP- 823). ASHRAE Research Project, Final Report. Braun, J.E. 1988. Methodologies for the design and control of central cooling plants. Ph.D. dissertation, University of Wisconsin-Madison. Braun, J.E. 1990. Reducing energy costs and peak electrical demands through optimal control of building thermal storage. ASHRAE Transac- tions 96(1). Paper SL-90-16-2. Braun, J.E. 1992. A comparison of chiller-priority, storage-priority, and optimal control of an ice-storage system. ASHRAE Transactions 98(1): 893-902. Paper AN-92-08-1. Braun, J.E. 2003. Load control using building thermal mass. Journal of Solar Energy Engineering Transactions of the ASME 125:292- 301. Braun, J.E. 2007a. A near-optimal control strategy for cool storage systems with dynamic electric rates. HVAC&R Research (now Science and Tech- nology for the Built Environment) 13(4):557-580. Braun, J.E. 2007b. Impact of control on operating costs for cool storage sys- tems with dynamic electric rates. ASHRAE Transactions 113. Paper LB- 07-037 (RP-1252). Braun, J.E. 2007c. Near-optimal control strategies for hybrid cooling plants. HVAC&R Research (now Science and Technologyfor the Built Environ- ment) 13(4):599-622. Braun, J.E. 2007d. A general control algorithm for cooling towers in cooling plants with electric and/or gas-driven chillers. HVAC&R Research (now Science and Technologyfor the Built Environment) 13(4):581-598. Braun, J.E., and G.T. Diderrich. 1990. Near-optimal control of cooling tow- ers for chilled-water systems. ASHRAE Transactions 96(2):806-813. Paper SL-90-13-3. Braun, J.E., J.W. Mitchell, S.A. Klein, and W.A. Beckman. 1987. Perfor- mance and control characteristics of a large central cooling system. ASHRAE Transactions 93(1):1830-1852. Braun, J.E., S.A. Klein, J.W. Mitchell, and W.A. Beckman. 1989a. Applica- tions of optimal control to chilled water systems without storage. ASHRAE Transactions 95(1):663-675. Paper CH-89-06-6. Braun, J.E., S.A. Klein, J.W. Mitchell, and W.A. Beckman. 1989b. Method- ologies for optimal control to chilled water systems without storage. ASHRAE Transactions 95(1):652-662. Paper CH-89-06-5. Braun, J.E., K. W. Montgomery, and N. Chaturvedi. 2001. Evaluating the performance of building thermal mass control strategies. International Journal ofHVAC&R Research (now HVAC&R Research) 7(4):403-428. Brent, R.P. 1973. Algorithms for minimization without derivatives, Ch. 5. Prentice Hall. Brothers, P. W., and M.L. Warren. 1986. Fan energy use in variable air vol- ume systems. ASHRAE Transactions 92(2B):19-29. Paper PO-86-01-2. Candanedo, J.A., V.R. Dehkordi, A. Saberi-Derakhtenjani, and A.K. Athie- nitis. 2015. Near-optimal transition between temperature setpoints for peak load reduction in small buildings. Energy and Buildings 87:123- 133. Capozzoli, A., D. Grassi, and F. Causone. 2015. Estimation models of heating energy consumption in schools for local authorities planning. Energy and Buildings 105:302-313. Cheng, M.-Y and M.-T. Cao. 2014. Accurately predicting building energy performance using evolutionary multivariate adaptive regression splines. Applied Soft Computing 22:178-188. Cheng, H., M.J. Brandemuehl, G.P. Henze, A.R. Florita, and C. Felsmann. 2008. Evaluation of the primary factors impacting the optimal control of passive thermal storage (RP-1313). ASHRAE Transactions 114(2):57- 64. Paper SL-08-006. Chitsaz, H., H. Shaker, H. Zareipour, D. Wood, and N. Amjady. 2015. Short- term electricity load forecasting of buildings in microgrids. Energy and Buildings 99:50-60. Chou, J.-S., and D.-K. Bui. 2014. Modeling heating and cooling loads by artificial intelligence for energy-efficient building design. Energy and Buildings 82:437-446. Cigler, J., P. Tomasko, and J. Siroky. 2013. BuildingLAB: A tool to analyze performance of model predictive controllers for buildings. Energy and Buildings 57:34-41. Cui, C., T. Wu, M. Hu, J.D. Weir, and X. Li. 2016. Short-term building energy model recommendation system: A meta-learning approach. Applied Energy 172:251-263. Cumali, Z. 1988. Global optimization of HVAC system operations in real time. ASHRAE Transactions 94(1):1729-1744. Paper DA-88-23-1. Cumali, Z. 1994. Application of real-time optimization to building systems. ASHRAE Transactions 100(1). Date, J., M. Fournier, Y. Chen, and A. K. Athienitis. 2016a. Impact of thermal model resolution on peak heating demand calculation under dif- ferent setpoint profiles. ASHRAE Transactions 122(1):278-288. Date, J., J.A. Candanedo, A.K. Athienitis, and M. Fournier. 2016b. Simpli- fied multi-zone thermal modelling of a house for demand reduction & control applications. CLIMA Conference 2016, pp. 1-10. De Coninck, R., and L. Helsen. 2016. Practical implementation and evalua- tion of model predictive control for an office building in Brussels. Energy and Buildings 111:290-298. Deng, L., and D. Yu. 2014. Deep learning: methods and applications. Foun- dations and TrendsⓇ in Signal Processing 7(3-4):197-387. | {}
e9fb6550-538b-443c-927d-5bb86113719c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Supervisory Control Strategies and Optimization 43.47 Doty, S., and W.C. Turner. 2012. Energy management handbook, 8th ed. The Fairmont Press, Lilburn, GA. Drees, K.H. 1994. Modeling and control ofarea-constrained ice storage sys- tems. M.S. thesis, Purdue University, West Lafayette, IN. Drees, K.H., and J.E. Braun. 1995. Modeling of area-constrained ice storage tanks. International Journal of HVAC&R Research (now Science and Technologyfor the Built Environment) 1(2):143-159. Drees, K.H., and J.E. Braun. 1996. Development and evaluation of a rule- based control strategy for ice storage systems. International Journal of HVAC&R Research (now Science and Technologyfor the Built Environ- ment) 2(4):312-336. Dyer, D.F., and G. Maples. 1981. Boiler efficiency improvement. Boiler Effi- ciency Institute. Auburn, AL. Elleson, J.S. 1996. Successful cool storage projects: From planning to oper- ation. ASHRAE. Englander, S.L., and L.K. Norford. 1992. Saving fan energy in VA v systems, Part 2: Supply fan control for static pressure minimization using DDC zone feedback. ASHRAE Transactions 98(1):19-32. Paper 3544. Fan, C., F. Xiao, and S. Wang. 2014. Development of prediction models for next-day building energy consumption and peak power demand using data mining techniques. Applied Energy 127:1-10. Ferkl, L., and J. Siroky. 2010. Ceiling radiant cooling: Comparison of ARMAX and subspace identification modelling methods. Buildings and Environment 45(1):205-212. Florita, A.R., and G.P. Henze. 2009. Comparison of short-term weather fore- casting models for model predictive control. HVAC&R Research (now Science and Technology for the Built Environment) 15(5):835-853. Forrester, J.R., and W.J. Wepfer. 1984. Formulation of a load prediction algorithm for a large commercial building. ASHRAE Transactions 90 (2B):536-551. Paper KC-84-09-3. Gayeski, N.T., J. Gagne, P.R. Armstrong, S. Katipamula, and M. Alvira. 201 1a. Development of a low-lift chiller controller and simplified pre- cooling control algorithm-Final report. Report PNNL-21155, Pacific Northwest National Laboratory, Richland, WA. Gayeski, N.T., P.R. Armstrong, T. Zakula, and L.K. Norford. 2011b. Empir- ical modeling of a rolling-piston compressor heat pump for predictive control in low-lift cooling. ASHRAE Transactions 117(2). Paper ML-11- 023. Gayeski, N.T., P.R. Armstrong, and L.K. Norford. 2012. Predictive pre- cooling of thermo-active building systems with low-lift chillers. HVAC&R Research (now Science and Technologyfor the Built Environ- ment) 18(5):858-873. Gibson, G.L., and T.T. Kraft. 1993. Electric demand prediction using artifi- cial neural network technology. ASHRAE Journal 35(3):60-68. Greensfelder, E.M., G.P. Henze, and C. Felsmann. 2011. An investigation of optimal control of passive building thermal storage with real time pricing. Journal of Building Performance Simulation 4(2). Grumman, D.L., and A.S. Butkus, Jr. 1988. Ice storage application to an Illi- nois hospital. ASHRAE Transactions 94(1):1879-1893. Paper DA-88- 25-3. Hackner, R.J., J.W. Mitchell, and W.A. Beckman. 1984. HVAC system dynamics and energy use in buildings-Part I. ASHRAE Transactions 90(2B):523-535. Paper KC-84-09-2. Hackner, R.J., J. W. Mitchell, and W.A. Beckman. 1985. HVAC system dynamics and energy use in buildings-Part II. ASHRAE Transactions 91(1B):781. Paper CH-85-16-4. Hartman, T. 1993. Terminal regulated air volume (TRAV) systems. ASHRAE Transactions 99(1):791-800. Paper CH-93-03-3. Henze, G.P. 2003. An overview of optimal control for central cooling plants with ice thermal energy storage. Journal of Solar Energy Engineering, Transactions of the ASME 125:302-309. Henze, G.P., M. Krarti, and M.J. Brandemuehl. 1997a. A simulation envi- ronment for the analysis ofice storage controls. International Journal of HVAC&R Research (now Science and Technologyfor the Built Environ- ment) 3(2):128-148. Henze, G.P., R.H. Dodier, and M. Krarti. 1997b. Development of a predic- tive optimal controller for thermal energy storage systems. International Journal ofHVAC&R Research (now Science and Technologyfor the Built Environment) 3(3):233-264. Henze, G.P., M. Krarti, and M.J. Brandemuehl. 2003a. Guidelines for improved performance of ice storage systems. Energy and Buildings 35(2):111-127. Henze, G.P., D. Kalz, S. Liu, and C. Felsmann. 2005. Experimental analysis ofmodel-based predictive optimal control for active and passive building thermal storage inventory. HVAC&R Research (now Science and Tech- nology for the Built Environment) 11(2):189-214. Henze, G.P., M.J. Brandemuehl, C. Felsmann, A. Florita, and H. Cheng. 2007. Evaluation of building thermal mass savings. ASHRAE Research Project RP-1313, Final Report. Henze, G.P., C. Felsmann, A.R. Florita, M.J. Brandemuehl, H. Cheng, and C.E. Waters. 2008. Optimization of building thermal mass control in the presence of energy and demand charges (RP-1313). ASHRAE Transac- tions 114(2):75-84. Paper SL-08-008. Henze, G.P., A.R. Florita, M.J. Brandemuehl, C. Felsmann and H. Cheng. 2009. Advances in near-optimal control of passive building thermal stor- age. Proceedings of the ASME 3rd International Conference on Energy Sustainability, San Francisco. Hiller, C.C., and L. Glicksman. 1977. Heat pump improvement using com- pressor flow modulation. ASHRAE Transactions 83(2). Paper HA-2461. Hu, J., and P. Karava. 2014. A state-space modeling approach and multi- level optimization algorithm for predictive control of multi-zone build- ings with mixed-mode cooling. Building and Environment 80:259-273. Idowu, S., S. Saguna, C. Ahlund, and 0. Schelen. 2016. Applied machine learning: Forecasting heat load in district heating system. Energy and Buildings. 133:478-488. Jimenez, M.J., and H. Madsen. 2008. Models for describing the thermal characteristics of building components. Buildings and Environment 43(2):152-162. Jovanovic, R.Z., A.A. Sretenovic, and B.D. Zivkovic. 2015. Ensemble of various neural networks for prediction of heating energy consumption. Energy and Buildings 94:189-199. Kao, J.Y. 1985. Control strategies and building energy consumption. ASHRAE Transactions 91(2B):510-817. Paper HI-85-15-3. Katipamula, S., P.R. Armstrong, W. Wang, N. Fernandez, H. Cho, W. Goet- zler, J. Burgos, R. Radhakrishnan, and C. Ahlfeldt. 2010a. Development of high-efficiency low-lift vapor compression system Final report. Report PNNL-19227. Katipamula, S., P.R. Armstrong, W. Wang, N. Fernandez, H. Cho, W. Goet- zler, J. Burgos, R. Radhakrishnan, and C. Ahlfeldt. 2010b. Cost-effective integration of efficient low-lift baseload cooling equipment: FY08 final report. Report PNNL-19114. Keeney, K.R., and J.E. Braun. 1996. A simplified method for determining optimal cooling control strategies for thermal storage in building mass. International Journal of HVAC&R Research (now Science and Technology for the Built Environment) 2(1):1-20. Keeney, K.R., and J.E. Braun. 1997. Application of building precooling to reduce peak cooling requirements. ASHRAE Transactions 103(1):463- 469. Paper PH-97-04-1. Kim, D., J. Cai, K.B. Ariyur, and J.E. Braun. 2016. System identification for building thermal systems under the presence of unmeasured disturbances in closed loop operation: Lumped disturbance modeling approach. Buildings and Environment 107:169-180. Krarti, M., M.J. Brandemuehl, and G.P. Henze. 1996. Evaluation of optimal control for ice systems (RP-809). ASHRAE Research Project RP-809, Report. Krarti, M., G. Henze, G. Zhou, P. Ihm, S. Liu, and S. Morgan. 2007. Real- time predictive optimal control of active and passive thermal energy stor- age systems: Final report. Report, Department of Energy Contract DE- FC-36-03G 13026. Kreider, J.F., and X.A. Wang. 1991. Artificial neural networks demonstrated for automated generation of energy use predictors for commercial build- ings. ASHRAE Transactions 97(2):775-779. Paper IN-91-09-3. Kummert, M. 2001. Contribution to the application of modern control tech- niques to solar buildings: Simulation-based approach and experimental validation. Ph.D. dissertation. Fondation Universitaire (now University of Liege), Arlon, Belgium. Lau, A.S., W.A. Beckman, and J. W. Mitchell. 1985. Development of com- puterized control strategies for a large chilled water plant. ASHRAE Transactions 91(1B):766-780. Paper CH-85-16-3. Li, X., and J. Wen. 2014. Review of building energy modeling for control and operation. Renewable and Sustainable Energy Reviews 37:517-537. Li, P., D. Vrabie, D. Li, S. Bengea, S. Mijanovic, and Z.D. O'Neill. 2015. Simulation and experimental demonstration of model predictive control in a building HVAC system. Science and Technologyfor the Built Envi- ronment 21(6):721-732. do.doi.org/10.1080(23744731.2015.1061888. Inc. ASHRAE, 2019 user. single for Licensed | {}
be360627-6fc3-4d6b-9423-dc78914e89bd | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 43.48 2019 ASHRAE Handbook-HVAC Applications (SI) Liu, S., and G.P. Henze. 2006a. Experimental analysis of simulated rein- forcement learning control for active and passive building thermal stor- age inventory-Part 1: Theoretical foundation. Energy and Buildings 38(2):142-147. Liu, S., and G.P. Henze. 2006b. Experimental analysis of simulated rein- forcement learning control for active and passive building thermal stor- age inventory-Part 2: Results and analysis. Energy and Buildings 38(2):148-161. Ljung, L., and T. Soderstrom. 1983. Theory and practice of recursive iden- tification. MIT Press, Cambridge, MA. MacArthur, J. W., A. Mathur, andJ. Zhao. 1989. On-line recursive estimation for load profile prediction. ASHRAE Transactions 95(1):621-628. Paper CH-89-06-1. Mocanu, E., P.H. Nguyen, M. Gibescu, and W.L. Kling. 2016a. Deep learn- ing for estimating building energy consumption. Sustainable Energy, Grids and Networks 6:91-99. Mocanu, E., P.H. Nguyen, W.L. Kling, and M. Gibescu. 2016b. Unsuper- vised energy prediction in a smart grid context using reinforcement cross-building transfer learning. Energy and Buildings 116:646-655. Monfet, D., M. Corsi, D. Choiniere, and E. Arkhipova. 2014. Development of an energy prediction tool for commercial buildings using case-based reasoning. Energy and Buildings 81:152-160. Morgan, S., and M. Krarti. 2006. Impact of electricity rate structures on energy cost savings of pre-cooling controls for office buildings. Building and Environment 42(8):2810-2818. Morgan S., and M. Krarti. 2010. Field testing of optimal controls of passive and active thermal storage. ASHRAE Transactions 116(1). Paper OR-10- 015. Moro�an, P., R. Bourdais, D. Dumur, and J. Buisson. 2010. Building tem- perature regulation using a distributed model predictive control. Energy and Buildings 42(9): 1445-1452. Morris, F.B., J.E. Braun, and S. Treado. 1994. Experimental and simulated performance of optimal control of building thermal storage. ASHRAE Transactions 100(1):402-414. Paper 3776. Niswander, A., and P.R. Armstrong. 2013. Demand responsive cooling with TABS. Intelligent Building Operation Conference, University of Colo- rado, Boulder. Oldewurtel, F., Gyalistras, M. Gwerder, V. Stauch, A. Parisio, C.N. Jones, D. and M. Morari. 2012. Use of model predictive control and weather fore- casts for energy efficient building climate control. Energy and Buildings 45:15-27. O'Neill, Z., and C. O'Neill. 2016. Development of a probabilistic graphical model for predicting building energy performance. Applied Energy 164:650-658. Privara, S., J. Cigler, Z. Vana, F. Oldewurtel, C. Sagerschnig, and E. Zace- kova. 2013. Building modeling as a crucial part for building predictive control. Energy and Buildings 56:8-22. Rabl, A., and L.K. Norford. 1991. Peak load reduction by preconditioning buildings at night. International Journal ofEnergy Research 15:781-798. Rawlings, L.K. 1985. Strategies to optimize ice storage. ASHRAE Journal 27(5):39-44. Ruud, M.D., J.W. Mitchell, and S.A. Klein. 1990. Use of building thermal mass to offset cooling loads. ASHRAE Transactions 96(2). Paper SL-90- 14-2. Sajjadi, S., S. Shamshirband, M. Alizamir, P.L. Yee, and A. Mostafaeipour. 2016. Extreme learning machine for prediction of heat load in district heating systems. Energy and Buildings 122:222-227. Seem, J.E., and J.E. Braun. 1991. Adaptive methods for real-time forecast- ing of building electrical demand. ASHRAE Transactions 97(1):710- 721. Paper NY-91-10-3. Seem, J.E., S.A. Klein, W.A. Beckman, and J.W. Mitchell. 1989a. Compre- hensive room transfer functions for efficient calculation of the transient heat transfer process in buildings. Journal ofHeat Transfer 111:264-273. Seem, J.E., P.R. Armstrong, and C.E. Hancock. 1989b. Comparison ofseven methods for forecasting the time to return from night setback. ASHRAE Transactions 95(2). Seem, J.E., C. Park, and J.M. House. 1999. A new sequencing control strat- egy for air-handling units. International Journal ofHVAC&R Research (now Science and Technologyfor the Built Environment) 5(1):35-58. Snyder, M.E., and T.A. Newell. 1990. Cooling cost minimization using building mass for thermal storage. ASHRAE Transactions 96(2):830- 838. Paper SL-90-14-3. Spethmann, D.H. 1989. Optimal control for cool storage. ASHRAE Trans- actions 95(1):1189-1193. Paper CH-89-22-1. Stoecker, W.F. 1980. Design of thermal systems. McGraw-Hill, New York. Tamblyn, R.T. 1985. Control concepts for thermal storage. ASHRAE Trans- actions 91(1B):5-11. Paper CH-85-01-1. Taplin, H.R. 1998. Boiler plant and distribution system optimization man- ual. Fairmont Press, Lilburn, GA. Tian, W., R. Choudhary, G. Augenbroe, and S.H. Lee. 2015. Importance analysis and meta-model construction with correlated variables in eval- uation of thermal performance of campus buildings. Building and Envi- ronment 92:61-74. Touretzky, C. R., and M. Baldea. 2014. Integrating scheduling and control for economic MPC of buildings with energy storage. Journal ofProcess Control 24(8):1292-1300. University of Wisconsin-Madison. 2013. A TRaNsient SYstems Simulation program. sel.me.wisc.edu/trnsys/. Warren, M., and L.K. Norford. 1993. Integrating VAV zone requirements with supply fan operation. ASHRAE Journal 35(4):43-46. Watkins, C., and P. Dayan. 1992. Q-learning. Machine Learning 8:279-292. Wei, G., M. Liu, and D.E. Claridge. 2004. Integrated damper and pressure reset for VAV supply air fan control. ASHRAE Transactions 1 10(2):309- 313. Paper 4722. Williams, K.T., and J.D. Gomez. 2016. Predicting future monthly residential energy consumption using building characteristics and climate data: A statistical learning approach. Energy and Buildings 128:1-11. Winkelman, F.C., W.F. Buhl, B. Birdsall, A.E. Erdem, K.L. Ellington, and Hirsch & Associates. 1993. DOE-2 BDL summary, version 21.E. LBNL Report 34946, Lawrence Berkeley National Laboratory, Berkeley, CA. Yu, Z., F. Haghighat, B.C.M. Fung, and H. Yoshino. 2010. A decision tree method for building energy demand modeling. Energy and Buildings 42(10):1637-1646. Zakula, T., N.T. Gayeski, P.R. Armstrong, and L.K. Norford. 2011. Variable- speed heatpump performance model, model validation, and optimal con- trol. HVAC&R Research (now Science and Technologyfor the Built Envi- ronment) 17(5):670-691. Zakula, T., P. Armstrong, and L Norford. 2012. Optimal coordination ofheat pump compressor and fan speeds and subcooling over a wide range of loads and conditions. HVAC&R Research (now Science and Technology for the Built Environment) 18(6):1153-1167 Zakula, T., P.R. Armstrong, and L.K. Norford. 2014. Modeling environment for model predictive control of buildings. Energy and Buildings 85:549- 559. Zakula, T., P.R. Armstrong, and L.K. Norford. 2015. Advanced cooling technology with thermally activated building surfaces and model predic- tive control. Energy and Buildings 86:640-650. Zhou, G., P. Ihm, M. Krarti, S. Liu, and G.P. Henze. 2005. Integration of an internal optimization module within EnergyPlus. IBPSA Proceedings. BIBLIOGRAPHY Niswander, A. 2014. Demand Responsive Cooling with TABS Source/Sink and Model-Predictive Control, M.S.M.E. thesis, Masdar Inst., UAE. Seem, J.E., S.A. Klein, W.A. Beckman, and J. W. Mitchell. 1990. Model reduction of transfer functions using a dominant root method. ASME Journal of Heat Transfer 112:547-554. Zakula, T. 2013. Model-predictive control for energy efficient cooling and dehumidification. Ph.D. dissertation, Massachusetts Institute of Technology. Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
50c66411-0bdb-4e44-9d96-0239130b50de | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 44 HVAC COMMISSIONING ¦ CONSIDERATIONS ¦ 44.1 ¦ Life and Property Safety Check ¦ 44.11 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Commissioning Objective ¦ 44.2 ¦ COMMISSIONING COSTS ¦ 44.12 ¦ ¦ Management and Responsibilities ¦ 44.2 ¦ Design-Phase Costs (Including Predesign and ¦ ¦ ¦ COMMISSIONING PROCESS ¦ 44.4 ¦ Design) ¦ 44.12 ¦ ¦ Predesign-Phase Commissioning ¦ 44.5 ¦ Construction- and Occupancy/Operations-Phase ¦ ¦ ¦ Design-Phase Commissioning ¦ 44.5 ¦ Costs ¦ 44.12 ¦ ¦ Construction-Phase Commissioning ¦ 44.8 ¦ Existing Buildings ¦ 44.13 ¦ ¦ Occupancy- and Operations-Phase Commissioning ¦ 44.11 ¦ Certification ¦ 44.13 ¦ COMMISSIONING implements a quality-oriented process for verifying, and documenting that the performance of facilities, systems, and assemblies meets defined objectives and cri- teria. The defined objectives and criteria are often referred to as the owner's project requirements (OPR). The commissioning pro- cess uses the owner' s project requirements as the reference to deter- mine acceptance of the design and construction. Commissioning includes verifying and documenting that the project operational and maintenance documentation and training of operation and mainte- nance personnel occur. The result should be fully functional sys- tems that can be properly operated and maintained throughout the life of the building. This chapter gives an overview of the general commissioning process as covered in ASHRAE Guideline 0-2013, developed for the National Institute of Building Sciences' total building commission- ing program, as well as the best practices for applying the process from ASHRAE Guideline 1.1-2007. The minimum acceptable pro- cess for commissioning is detailed in ASHRAE Standard 202-2013. This chapter provides more narrative discussion on some issues than these two guidelines and the standard. Recommissioning applies commissioning to a project that has been previously delivered using the commissioning process. This may be a scheduled recommissioning developed as part of ongoing com- missioning, or it may be triggered by use change, operational prob- lems, or other needs. Existing building commissioning (often called retrocommissioning) applies commissioning to an existing facility that may or may not have been previously commissioned. It consists of systematically investigating, analyzing, and adjusting operations of existing building equipment, systems, and assemblies, as well as training and documentation for operators to ensure that required per- formance (including energy, comfort, and IAQ) is achieved. Buildings require maintenance and tuning to prevent performance degradation. Existing building commissioning should be performed as part of ongoing efforts to maintain a comfortable and efficient environment within the building. Ithas broad application to virtually every building type with excellent cost/benefit results and payback ratios. Existing building commissioning starts with development of the owner's cur- rent facility requirements, reviewing the existing design, and testing of the existing systems. Any major retrofits required follow the pro- cess for new building commissioning as defined in this chapter. 1. CONSIDERATIONS Applicability The commissioning process described here applies to new con- struction, major renovations, and all systems and assemblies. The preparation of this chapter is assigned to TC 7.9, Building Commis- sioning. Although this chapter focuses on HVAC systems, commissioning can be applied to the building as a total system, which includes structural elements, building envelope, life safety features, electrical systems, communication systems, plumbing, irrigation, controls, and HVAC systems (ASHRAE Guideline 0). Based on owners' pref- erence and project contract scope, total commissioning can include industrial process and process equipment, systems, piping, instru- mentation, electrical, and related control, or these topics may be treated as an independent phase of project commissioning. Systems to be commissioned vary with the systems and assemblies used, building size, project type, and objectives. Owners and commis- sioning providers often focus on systems and assemblies under the commissioning umbrella that have (1) historically not performed well at turnover (e.g., outside air economizers and variable-speed drives), (2) are mission critical (e.g., air cleanliness in a cleanroom, emer- gency power in a hospital), (3) will be costly to fix during occupancy if they fail (e.g., chilled-water piping, window flashing assemblies), or (4) present a life-safety risk if they fail (e.g., fire alarm, smoke con- trol, moisture penetration). Recommendations in this chapter should be appropriately modified for each project. Although commissioning may begin at any time during the project life cycle, owners obtain the highest benefits when commissioning begins at the conceptual or pre- design phase. Background Equipment, components, systems, and assemblies have become more complex. More specialization has occurred in the disciplines and trades, with increased interactions between all elements. This increased specialization and interaction requires increased integra- tion between disciplines and specialized systems by the delivery team. Owners often use low-bid policies, and scopes of design pro- fessionals are often narrowed. The result has been buildings that do not meet owner expectations and often do not work as intended because of programming, design, and construction deficiencies. Commissioning is a value-added service that helps overcome these infrastructure inadequacies and fundamentally improve the perfor- mance of building systems and living conditions for occupants. Benefits The primary benefits of commissioning include improvements in all of the following areas: · Predesign and design Owners develop better understanding of what they want and need through clear, documented OPR Designers understand better what owner is requesting Designers reduce their risk with better communication and input from owner Owners understand better what designers are proposing through a clear, documented basis of design (BOD) 44.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
365dda07-8397-4d28-aff8-10e7c448e6be | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 44.2 2019 ASHRAE Handbook-HVAC Applications (SI) · · Experts review and improve commissioning documents Resolves many potential issues more cost effectively before construction phase Verifies planned systems can be commissioned and tested, and are within owner's ability to maintain Improves specifications and drawings, resulting in improved coordination between all groups Includes thorough training requirements in the construction documents Construction (including system and assembly performance) Increases accountability in submittal process, leading to higher- quality installation Provides tools to help contractors perform installations that meet the project requirements (e.g., construction checklists) Provides performance accountability through construction ob- servation, issue management, and testing Documents verification of system and assembly performance Verifies training completion Includes formal functional testing at completion Occupancy and operations (including maintenance) Improves performance (IAQ, comfort, energy) from start of oc- cupation Reduces amount of troubleshooting Has fewer contractor call backs Ensures thorough documentation in operation and mainte- nance (O&M) manuals Provides a systems manual Verifies documentation submittals Commissioning also reduces potential change orders, requests for information, contractor callbacks, and time required to fine-tune and debug systems during occupancy, and smooths turnover. Build- ing performance improvements give better building and system con- trol, improve energy efficiency, enhance indoor environmental quality, and contribute to increased occupant productivity. Key Contributors Inc. ASHRAE, 2019 user. single for Licensed · Owner/end user · Architect · Mechanical engineer · Electrical engineer · Commissioning authority (CxA) · Mechanical contractor · Electrical contractor · Controls contractor · Sheet metal contractor · Testing, adjusting, and balancing (TAB) agency · Owner's O&M staff · General contractor/construction manager Definitions Basis of Design (BOD). A document that records the concepts, calculations, decisions, and product selections used to meet the OPR and to satisfy applicable regulatory requirements, standards, and guidelines. The document includes both narrative descriptions and lists of individual items that support the design process. Commissioning Authority (CxA). An entity identified by the owner who leads, plans, schedules, and coordinates the commis- sioning team to implement the commissioning process. Commissioning Plan (Cx Plan). A document that outlines the organization, schedule, allocation of resources, and documentation requirements of the commissioning process. Construction Checklist. A form used by the contractor to verify that appropriate components are on site, ready for installation, cor- rectly installed, and functional. Current Facility Requirements (CFR). A written document in which the owner details a facility's current functional requirements and the expectations of how it should be used and operated. This may include goals, measurable performance criteria, cost consid- erations, benchmarks, success criteria, and supporting information to meet the requirements of occupants, users, and owners of the facility. Existing Building Commissioning (EBCx) Process. A quality- focused process for attaining the CFR of an existing facility and its systems and assemblies being commissioned. The process focuses on planning, investigating, implementing, verifying, and document- ing that the facility and/or its systems and assemblies are operated and maintained to meet the CFR with a program to maintain the enhancements for the remaining life of the facility. Facility Guide (FG). A basic building systems description and operating plan with general procedures and confirmed facility oper- ating conditions, set points, schedules, and operating procedures to properly operate the facility. Owner's Project Requirements (OPR). A document that de- tails the functional requirements of a project and the expectations of how it will be used and operated. These include project goals, mea- surable performance criteria, cost considerations, benchmarks, suc- cess criteria, and supporting information. (The term project intent is used by some owners.) Systems Manual. A system-focused, composite document that includes the operation manual, maintenance manual, and additional information of use to the owner during occupancy and operations. Test Procedures. A written protocol that defines methods, per- sonnel, and expectations for tests conducted on components, equip- ment, assemblies, systems, and interfaces among systems. 1.1 COMMISSIONING OBJECTIVE The commissioning objective focuses on documented confirma- tion that a facility fulfills the specified performance requirements for the building owner, occupants, and operators. To reach this objective, it is necessary to (1) clearly document the owner's project require- ments, including performance and maintainability; and (2) verify and document compliance with these criteria throughout design, construction, acceptance, and initial operation phases. Specific goals for commissioning include · Providing documentation and tools to improve quality of deliver- ables (e.g., forms, tracking software, performance calculation tools) · Verifying and documenting that systems and assemblies perform according to OPR by end of construction with building occu- pancy · Providing a uniform and effective process for delivery of con- struction projects · Using quality-based sampling techniques to detect systemic prob- lems · Verifying proper coordination among all contractors, subcontrac- tors, vendors, and manufacturers of all furnished equipment and assemblies in the completed systems · Verifying that adequate and accurate system and assembly docu- mentation is provided to owner · Verifying that operation and maintenance personnel and occu- pants are properly trained 1.2 MANAGEMENT AND RESPONSIBILITIES Management Strategies In each project, a qualified party should be designated as the commissioning authority (CxA). Predesign and Design. Commissioning during predesign and design is most often managed by an independent CxA who is not part | {}
ee8a9da3-4453-4162-aced-904f37e4eb77 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | HVAC Commissioning 44.3 of the formal designer-of-record team. An independent, objective view is critical. The CxA normally provides input to the owner and designers but does not have ultimate authority over design decisions. The CxA should also coordinate, conduct, or approve activities such as assisting in development of the OPR, conducting statistical sam- pling reviews, and developing commissioning specifications and test procedures. The CxA may also review plan designs. Construction. During construction, because of the variety of players, construction management scenarios, and the owner' s objec- tives, numerous methods are used to manage the commissioning process. To maintain objectivity, the CxA should be independent. If the contractor or designer hires the CxA, the potential conflict of interest must be carefully managed. The two primary methods to manage commissioning during construction are commissioning- authority-managed and contractor-managed. In the commissioning-authority-managed approach, the CxA performs many of the planning and technical tasks, such as developing the commissioning plan and test procedures and directing, witnessing, and documenting execution of tests, per- formed by either the contractor or the CxA. In the contractor-managed approach, the contractor may develop the commissioning plan, write test procedures, and direct and document testing, with the CxA reviewing and approving the plan, witnessing selected tests, and reviewing completed test reports. The CxA should report to the owner on the adequacy of a contractor-managed commissioning plan. The contractor may assign staff, a subcontractor, or a subconsultant to manage and coor- dinate commissioning responsibilities. This approach gives the con- tractor more responsibility. Some view this method as less objective, but others consider it more integrated into the building delivery process than the CxA-managed approach. Some project plans use both management approaches, particu- larly when a substantial amount of electrical equipment is being tested. HVAC and controls follow the commissioning-authority- managed approach, and electrical system commissioning follows the contractor-managed approach, but the entire process is still over- seen by the single CxA. Team Members Effective building commissioning requires a team effort. The size and makeup of the team depends on the size and complexity of the project and the owner' s desire for quality assurance. Team members include the owner, occupants, design professionals, construction manager, general contractor, subcontractors, suppliers, equipment manufacturers, and the CxA. The level of effort of team members changes during the different project phases. For example, during design, the designer is a key player in the commissioning process, whereas the contractor may not have been selected. During construction, the general contrac- tor's and installing subcontractors' roles increase. The scope of work of the CxA, design professionals, and con- tractors should be clearly and completely identified in their con- tracts. Without this, change orders, incomplete or missed tasks, and otherwise dysfunctional commissioning may result. Roles and Responsibilities The commissioning team 's responsibilities are to conduct com- missioning activities in a logical, sequential, and efficient manner using consistent protocols and forms, centralized documentation, clear and regular communications and consultations with all neces- sary parties, frequently updated timelines and schedules, and appro- priate technical expertise. The following sections summarize the responsibilities of each party. Additional detail is found in the Com- missioning Process section. Commissioning Authority. Specific responsibilities vary with the management scenario and the CxA's specific scope of services. Ideally, the same party or firm acts as CxA through all project phases. The CxA organizes and leads the commissioning team throughout the project. Predesign and Design Phase. During predesign, the CxA devel- ops the predesign and design-phase commissioning plan and ensures the OPR is developed. During design, the CxA develops detailed commissioning activ- ities. The core CxA responsibilities are · Reviewing designer's BOD, plans, and specifications, ensuring they meet the OPR · Developing initial construction-phase commissioning plan · Ensuring that the commissioning, training, and documentation requirements for all contractors and suppliers are reflected in con- struction contract documents Construction. During construction, the CxA is in charge of the commissioning process and makes the final recommendations to the owner about functional performance of commissioned building sys- tems and assemblies. The CxA directs commissioning activities, and is an independent and objective advocate for the owner. The core commissioning activities during construction involve · Reviewing selected construction submittals to verify confor- mance with OPR, with updates in commissioning plan as needed · Observing selected installations, start-up, and functional perfor- mance tests, including documenting any conditions that require correction · Co-organizing with the discipline design engineer, and planning, developing, reviewing, and observing testing · Codeveloping or assisting with systems manual · Reviewing O&M manual submissions · Verifying operator and maintenance personnel training and docu- mentation · Submitting documented results to owner on all commissioning performed These tasks may vary (e.g., some commissioning scopes involve preparing the O&M or electronic facility's manuals, preparing detailed maintenance management plans, or conducting operator and maintenance personnel training). Occupancy and Operations. During occupancy and operations, the CxA helps resolve commissioning issues and directs opposite- season testing. Often, the CxA participates in a near-warranty-end review of system and assembly performance. Independence. If the CxA 's firm has other project responsibili- ties, a potential conflict of interest exists. Wherever this occurs, the CxA should disclose in writing the nature of the conflict and the means by which it will be managed. If the CxA is not under direct contract to the owner, the owner's interests need to be protected through appropriate oversight of the CxA 's work. Qualifications. The CxA should fully understand commission- ing, design, and construction processes and have technical design, operations, maintenance, and troubleshooting knowledge of the sys- tems and assemblies being commissioned. Excellent written and verbal communication skills are critical. The CxA may represent an individual or a team of commissioning experts, depending on sys- tem complexity, the number of disciplines involved, and commis- sioning scope. Thus, the ability to manage diverse disciplines over long timelines is also important. Construction Manager. The construction manager' s role varies on each project. When they have significant oversight for the owner (e.g., schedule management, submittal review, change order author- ity), their commissioning role is more like the owner' S: they ensure the contractors execute their commissioning responsibilities ac- cording to the commissioning plan, and help resolve issues. Inc. ASHRAE, 2019 user. single for Licensed | {}
5a9f0f2f-d33f-46c1-a210-94b59ccb90cc | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 44.4 General Contractors. Design. The general contractor (if yet selected) reviews commis- sioning requirements and performance criteria for coordination, schedule, and cost implications. Construction. The contractor's role and responsibilities are · Ensuring subcontractors' commissioning work is completed and cooperating with CxA in executing the commissioning plan · Providing input into commissioning plan for CxA 's review and approval · Integrating commissioning schedule into overall project schedule · Participating in commissioning meetings · Responding to questions and issues raised by CxA · Resolving issues identified during commissioning and coordinat- ing correction of identified deficiencies · Providing equipment, system, and assembly data needed by CxA · Performing specified training · Submitting required portions of systems manuals In the contractor-managed approach, the general contractor is often required to hire a third party with direct commissioning skills to manage and execute the contractor commissioning requirements. Trade Contractors. Design. Trade contractors of specialty or complex systems or designs should review commissioning requirements and perfor- mance criteria of their systems for coordination, schedule, and cost implications. Construction. The responsibilities of the installing trade contrac- tors (and vendors, as appropriate) include · Participating with CxA (and the contractor's commissioning manager, when applicable) in executing commissioning plan · Providing input into commissioning plan for CxA 's review and approval · Coordinating with other trades as necessary to facilitate a smooth and complete commissioning process · Participating in commissioning meetings · Responding to questions and issues concerning their work raised by CxA · Executing and documenting tasks in construction checklist and start-up process · Performing and documenting tests when in their scope · Participating in resolving issues within their scope identified during commissioning · Correcting identified deficiencies within their scope · Providing required documentation for systems manuals and com- missioning reports Inc. ASHRAE, 2019 user. single for Licensed Commissioning-related activities of trade contractors are to prepare O&M manuals and submissions to the systems manual and provide training on commissioned systems and assemblies. To avoid confu- sion, the OPR should specify which commissioning activities are the trade contractor's responsibility, and which are the CxA 's. Architect and Engineers (Designers). Design. The design professionals should develop complete basis-of-design (BOD) documentation, including design narratives, rationale, and criteria, according to their scopes of services, and update this document with each new design submission. They pro- vide input to the commissioning plan, respond to questions and con- cerns by the CxA and others, respond to design review comments, and incorporate commissioning requirements in construction con- tract documents. Construction. During construction, designers · Review the commissioning plan · Attend selected commissioning meetings · Answer questions about system design and intended operation 2019 ASHRAE Handbook-HVAC Applications (SI) · Update design narratives in the BOD to reflect as-built conditions · Respond to or incorporate CxA comments on construction sub- mittals and O&M manuals · Help resolve design-related issues raised during commissioning · Perform specified training · Submit required portions of systems manuals Additional tasks sometimes required are to present system descrip- tion overviews for primary systems during O&M staff training, review and approve testing plans and procedures, review com- pleted test forms, or witness selected tests. Owner's Project Management Staff. The owner's project man- agement staff s ultimate responsibility is to see that the commis- sioning plan is executed. The owner, with guidance from the CxA, should include specific responsibilities in all commissioning team members' scopes of services, make sure there is sufficient time for commissioning in the project schedule, ensure the CxA is receiving cooperation from other team members, and ensure that other owner responsibilities (e.g., developing the OPR, having O&M staff par- ticipate during construction) are fulfilled. The owner ensures that all design review and construction-phase issues identified through commissioning are resolved in a timely manner. Owner's Representatives. The owner's representatives are indi- viduals or firms hired to represent the owner's interest during spec- ified phases of the building process. The owner typically retains the project architect or project engineer responsible for HV AC design and the CxA as a team of owner's representatives. Owner's Operations and Management (O&M) Staff. Predesign. The owner's O&M staff should participate in the development of the OPR during predesign. Design. During design, O&M staff may contribute to reviews of the designer's BOD, plans, and specifications. Construction. During construction, the owner's O&M staff should · Assist in reviewing selected submittals · Assist in construction observation, verifying completion of con- struction checklists and observing start-up · Participate in or witness testing, within pre-established lines of responsibility and authority · Review O&M and systems manual · Participate in training Occupancy. During occupancy, the O&M staff should identify any warranty or operational issues and report back to the commis- sioning team. They should participate in the warranty review and may participate in any seasonal testing. O&M staff might also par- ticipate as needed in additional training, particularly any related to the control system or other complex or unfamiliar technology. Occupants and Users. Predesign. The occupants and users should participate in the development of the OPR during predesign. Design. During design, occupants and users may contribute to reviews of the designer' s BOD, plans, and specifications. Construction. During construction, occupants and users may participate in select training and final inspection and walk-throughs. Occupancy. The occupants and users report back to the owner and/or the commissioning team about warranty items and other issues they observe related to the performance of the building. 2. COMMISSIONING PROCESS Commissioning should begin during predesign, and formally continue through the first year of occupancy and operations. Although circumstances may require owners to begin commis- sioning at the design or construction stage of a project, this later | {}
db0d9682-7aba-4e6e-b850-77f02eb89bda | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | HVAC Commissioning 44.5 implementation should, when possible, capture the same informa- tion and verifications developed when commissioning begins at project inception. 2.1 PREDESIGN-PHASE COMMISSIONING Objectives The primary activities and objectives of commissioning during predesign are to · Develop owner's project requirements (OPR) · Identify scope and budget for commissioning process · Develop initial commissioning plan · Review and accept predesign-phase commissioning-process activities · Review and use lessons learned from previous projects Activities Commissioning Team and Management. During the predesign phase, a team is formed to oversee and accomplish commissioning. Responsibility for leadership of the commissioning team should be defined and assigned to the CxA at the beginning of predesign. Owner's Project Requirements (OPR). The OPR forms the basis from which all design, construction, acceptance, and opera- tional decisions are made. It describes the functional requirements ofthe facility and expectations ofhow it will be used and operated. It includes project and design goals, budgets, limitations, sched- ules, owner directives, and supporting information, as well as nec- essary information for all disciplines to properly plan, design, construct, operate, and maintain systems and assemblies (ASH- RAE Guideline 0). The OPR is generally a set of concise objective qualitative state- ments, each with one or more quantitative performance metrics or criteria. The following information should be included: · Functional requirements, needs and goals for building use, oper- ation, maintenance, renovation, and expansion, including user's requirements and space temperature requirements · Occupancy schedules and space plan requirements, including zone-based control areas · Sustainability, reliability, durability, safety, and aesthetic goals · Quality of materials and construction · Warranty, project documentation, and training requirements · Goals for the process and outcome of design and construction (e.g., budgets, schedules, change orders, safety, aesthetics, effects on adjacent or integral occupied spaces and tenants) · General commissioning scope and objectives · General statements about codes, standards, and regulations to be followed · Limitations likely to affect design decisions · Specific features, systems, assemblies, or brands the owner re- quires (these will be repeated in the design narrative) · Instructions to designers on types of design tools and aids ex- pected to be used The CxA ensures that the OPR is developed and is clear and com- plete. The CxA may develop or help develop the OPR with the owner or provide direction and review ofthe OPR developed by oth- ers. Facilitated workshops, surveys, and questionnaires are useful for developing the OPR. Later during design, additional OPR state- ments with performance criteria may be added to the formal list, as desired by the owner and commissioning team. The OPR should still be developed, even if not originally generated in predesign, and included in the systems manual. Scope and Budget for Commissioning. During predesign, the owner, with assistance from the CxA, develops a scope and a rough budget for commissioning. At minimum, design-phase activities should be initially scoped. Once a design-phase commissioning plan is developed, the scope and budget may need to be adjusted. The scope and budget should reflect the commissioning objectives in the OPR. Selecting areas to commission is typically based on the budget, systems or assemblies with which the owner has experienced prob- lems on previous projects, complexity of systems and assemblies, and criticality of the system or assembly in meeting the OPR. During predesign and design, the list of areas to be commissioned may be general (e.g., electrical lighting controls, emergency power, general electrical equipment, HVAC, domestic water system, and envelope fenestration, etc.). Later in design but before scoping construction-phase commissioning, additional detail should be added to each of these categories, and others added as needed to ensure that the scope of commissioning is clear. Adding this detail increases the cost of commissioning, and needs to be specified early in the design phase. Historically, commissioning focused on HVAC. Owners are now asking for more systems to be commissioned, including lighting controls, fire and life safety systems, vertical and horizontal trans- port systems, envelope, plumbing, landscaping, sustainability fea- tures, structural elements, many electrical equipment components, security, data, and communications. Refer to the section on Com- missioning Costs for budgeting guidelines. Predesign-Phase Commissioning Plan One predesign-phase commissioning task should be drafting the commissioning plan for the design phase. The CxA develops this plan with review and comment by the owner and designer, and the plan is updated as the project progresses. The design-phase com- missioning plan should include the following: · Objectives and scope of commissioning · Overview of the process · Detailed commissioning-process activities for design phase · General commissioning-process activities for construction and operations/occupancy phases · Roles and responsibilities · Deliverables · Communication protocols · Schedule · Checklist of requirements and formats · Verification and acceptance procedures Acceptance of Predesign Commissioning The owner's project requirements and commissioning plan should be formally accepted during predesign, after review and comment by the CxA. 2.2 DESIGN-PHASE COMMISSIONING Objectives Design-phase commissioning objectives include the following: Inc. ASHRAE, 2019 user. single for Licensed · Update the owner's project requirements (OPR) · Verify basis of design (BOD) document against OPR · Update the design-phase commissioning plan developed during predesign · Develop and incorporate commissioning requirements into proj- ect specifications · Develop commissioning plan for construction and occupancy/ operations phases, including draft construction checklist · Verify plans and specifications against BOD and OPR · Begin codeveloping with relevant discipline design engineer for systems manual · Define training requirements for O&M personnel · Perform commissioning-focused design reviews | {}
d29f7f3d-7892-430d-96f2-c7a443493ba1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 44.6 · Accept design-phase commissioning Activities Update Design-Phase Commissioning Plan. The initial design- phase commissioning plan is developed during predesign. As more becomes known about systems and assemblies likely to be a part of the project and as project objectives are clarified, the commissioning plan may need to be updated with additional details. The CxA must participate in value engineering and constructability review sessions to ensure that commissioning can be performed. The owner and designer then review and comment on the updated plan, which then becomes the guide for the rest of the design phase. Update the OPR. As design progresses, additional OPR and performance criteria are likely to be identified. Other criteria may need to be altered as more detailed budget and design data become available. Verify the Basis of Design. All BOD elements can be grouped under one of two terms: design narrative or design criteria. These two terms provide a useful separation when writing the design basis. The design narrative is the written description and discussion of the concepts and features the designers intend (during schematic design phase) to incorporate into the design or what they have incor- porated (during the balance of design) to meet the OPR and associ- ated performance criteria as well as codes, standards, and regulations. This narrative should be understandable by all parties of the building construction and operation process, though it may address fairly technical and specialized issues. It includes a brief section on what systems were considered and why they were accepted or rejected, along with the rationale for the system selected. The design narrative should be updated with each phase of design. The design criteria are the project-specific information, includ- ing underlying assumptions for calculations, calculation methodol- ogy, codes and standards followed, equipment used as the basis of design, and design assumptions needed to make design calculations and other decisions, such as · Diversity and safety factors used in sizing · Classes of systems and components (duct class, cleanroom class, explosive or other hazardous classifications, etc.) · Level of redundancy · Occupant density · Limitations and restrictions of systems and assemblies · Inside and outside conditions (space temperature; relative humid- ity; lighting power density; glazing fraction; U-value and shading coefficient; roof, wall, and ceiling R-values; ventilation and infil- tration rates; etc.) · Fire and life safety issues · Summary of primary HV AC load calculations and the methods used Development and Use. The BOD is written by the designer and increases in details as design progresses. The CxA may need to obtain this explanatory information from the designer. An updated BOD with increased detail should be submitted with each new design submission. Each submission is reviewed by the owner and CxA as part of design reviews. Develop Commissioning Plan for Construction and Occu- pancy/Operations Phases. The commissioning plan (Cx plan) is a document that outlines the organization, schedule, allocation of resources, and documentation requirements of the commissioning process. This is an overall plan, developed during the predesign, design, and construction phases, that provides the structure, schedule, and coordination planning for commissioning. The Cx plan includes specifications detailing the scope, objectives, and process of commis- sioning during the construction and occupancy/operations phases of the project. It must specify the scope of work, roles, responsibilities, 2019 ASHRAE Handbook-HVAC Applications (SI) and requirements of the construction contractor. For the construction and occupancy/operations phases, it describes the following: · Commissioning process · Scope of commissioning effort, including systems, assemblies, and components being commissioned · Rigor of commissioning · Roles and responsibilities of each team member · Team contact information · Communication protocols between team members, including documentation requirements · Commissioning overview and details of submittal activities · Construction observation, following checklists, and performing start-up activities · Preliminary schedule for commissioning activities · Process for dealing with deficiencies · Test procedure development and execution · Prefunctional/functional test procedures · Operation and maintenance (O&M) manual review · Warranty-period activities · Operation training procedures · Systems manual development · Description of summary report, progress and reporting logs, and initial schedule (including phasing, if applicable) · Procedures for documenting commissioning activities and resolv- ing issues The commissioning plan developed during predesign is updated to include construction-phase activities. At the beginning of the design phase, the plan is general and is used primarily to guide development of commissioning specifications. The owner and designer review and comment on the plan. As design progresses, the CxA updates and finalizes the plan when the construction docu- ments are completed. The commissioning plan can be issued with the bid documents for reference. Develop and Incorporate Commissioning Requirements into Project Specifications. The specifications in the Cx plan are needed by contractors so they can include commissioning responsi- bilities in pricing and understand how to execute the work. Because commissioning is still relatively new to the building industry, descriptive process language should be included, rather than just delineating requirements. Frequently, for reference, the responsibil- ities of other team members not bound by the specifications (e.g., owner, CxA, construction manager, architect) are given in the com- missioning specifications to ensure clarity and put the contractor' s responsibilities in context. The specification should include definitions, a list of equipment and systems to be commissioned, submittal, construction checklist, testing and documentation requirements, and sample checklists and test forms. If the project uses contractor-managed commissioning, the specification should identify skills and qualifications required of the contractor's commissioning lead. The OPR, along with as much BOD information as possible, should be included in the construction documents and labeled as informational-purposes-only, to differentiate from the contractor's contractual obligations. Training and O&M manual requirements of the contractor also should be included. It is critical that the project specifications in the Cx plan clearly define how the quality control and testing functions that have traditionally been a part of many construction projects (e.g., fire alarm, elevator, duct pressure, room pressurization, emergency power testing) will be integrated with HVAC commissioning. Responsibility for checkout and test procedures, including test procedure review, direction, execution, witnessing, documentation, and approval, must all be clearly described. The acceptance criteria for the test should be included in the specifications. Acceptance cri- teria should be based on the OPR and the systems selected. For Inc. ASHRAE, 2019 user. single for Licensed | {}
7fb690ea-aba7-4083-a25b-2aef4b3c8cf1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | HVAC Commissioning 44.7 example, a project may require tight temperature or humidity tol- erances to meet certification criteria. Systems designed for these projects should be able to control to those tolerances. A system with staged cooling (direct expansion with compressor staging) may not be able to meet a 0.5 K level of control. This should be taken into consideration when selecting the systems for the project. The CxA ensures that contractor responsibilities for commis- sioning are appropriately incorporated into the project specifica- tions. Placing the general commissioning requirements, process descriptions, and specifications in a single section is one method that makes it easy for all parties to know where to look for their responsibilities and find common terminology. The weakness of this method is that some contractors may not realize that this is part of their responsibilities, because it is not described in their sections; therefore, it might be beneficial to split at least part of the commis- sioning requirements into the applicable sections, with a reference back to the section that describes the common commissioning pro- cesses. Often, the commissioning authority writes the commissioning specifications and then works with the designer to integrate them into the project specifications. Alternatively, the designer can de- velop the commissioning specifications, with the CxA reviewing and recommending revisions. Begin Developing Systems Manual. During design, the sys- tems manual contains the OPR, BOD, and drawings and specifica- tions, updated at each design submission and during and after construction. The CxA is often responsible for assembling and maintaining the systems manual; however, the contract documents for the CxA or design professionals should delineate who is respon- sible for this task. The systems manual differs significantly from traditional O&M manuals. This manual expands the scope to include other project information developed and gathered during commissioning, such as traditional equipment O&M data, design and construction doc- uments (OPR, BOD, plans, specifications, and approved construc- tion submittals), system schematics, final commissioning report, training records, commissioning test procedures (filled-in and blank), and optimization and diagnostic data (which can include operational procedures for specific emergency situations, seasonal changeover procedures, fire and emergency power response matrix, smoke management system operation during and after fire, energy efficiency recommendations, troubleshooting guide, re- commissioning frequency, and diagnostic building automation sys- tem trend logs). Scopes of work should clearly identify whether the systems manual includes all project systems and assemblies or just commissioned ones. For more information, see ASHRAE Guide- line 4-2008. The owner, designer, contractor, and commissioning authority each have development responsibilities for parts of the systems manual. Construction documents should list the contents and re- quirements for the systems manual and the responsible party for generating, compiling, and finishing each part of the required doc- umentation. Systems manuals should be available for and used in operator training. Much of the systems manual can be put into elec- tronic media format. The ability to search and auto-update enhances the usability and accessibility of the data. Define Training Requirements. During the design phase, the training requirements of O&M personnel and occupants are identified relative to the systems and assemblies to be installed in the facility. O&M personnel must have the knowledge and skills required to operate the facility to meet the OPR. Occupants also need to understand their effect on the use of the facility and the ability to meet project requirements. Both groups require training. Training needs can be identified using a group-technique work- shop, interviews, or surveys with the owner and occupant repre- sentatives after the systems and assemblies have been specified, and before issuing the construction documents. The contractor's training responsibilities need to be incorporated into the project specifications and should include requirements for the number of training hours for each item of equipment or assembly and submit- tals of training plans and qualifications of trainers. Training likely requires participation of the designer (for system overviews), the CxA (for system overviews, recommissioning, optimization, diag- nostics, and using and maintaining the systems manual), and pos- sibly the contractor, and should be included in their scopes of work. Because turnover in O&M and occupants will occur, training mate- rials should be reusable (e.g., video, written manuals, computer presentations). Perform Design Reviews. Design review by parties not part of the formal designer-of-record team should be conducted to provide an independent perspective on performance, operations, and main- tenance. These document reviews, conducted by experts in the field, should start as early as possible, when options and issues can be more easily resolved. The reviews may be coordinated by the CxA and should include the owner' s technical staff. The CxA may attend some design team meetings, and formally reviews and comments on the design at various stages of development [ideally, at least once during schematic design (predesign), design development, and con- struction document phases]. The CxA 's design review is not intended to replace peer-to-peer design reviews that check for accu- racy and completeness of the design and calculations. A targeted design review may cover the following: · General quality review of documents, including legibility, consis- tency, and level of completeness · Coordination between disciplines · Specification applicability to project and consistency with draw- ings · Verification that BOD assumptions and rationale are reasonable · Verification that system and assembly narrative descriptions are clear and consistent with OPR and the BOD is updated with resolved issues · Verification that plans and specifications are consistent with BOD and OPR, and plans and specifications are updated with resolved issues Potential system performance problems, issues likely to result in change orders, areas where correct installation is difficult, energy efficiency improvements, environmental sustainability, indoor envi- ronmental quality issues, fire and life safety issues, operation and maintenance issues, and other issues may be addressed in these design reviews, depending on the owner's desires and CxA 's scope. Required reviews ensure that training and systems manual require- ments are adequately reflected in construction documents. Some reviews use sampling, giving 10 to 20% of the drawings and specifications for an in-depth review; if only minimal issues are identified, the owner accepts the submission. If significant issues are identified in the sample, either the submittal is sent back to the designer for revamping and a thorough review, or the CxA may per- form a thorough review, depending upon the scope of work defined in the CxA 's contract. After the design team has addressed the issues, the CxA performs a new review. In this type of review, the design team is still responsible for their traditional peer review of con- struction documents for accuracy. The CxA makes recom- mendations to facilitate commissioning and improve building performance, without approving or disapproving either design or documents. The design team is ultimately responsible for design. The CxA should be able to justify all of the recommendations made. Itis the responsibility ofthe owner or project manager to evaluate all review findings with the design team and see that the responsible team member implements the approved ones. All issues are tracked to resolution and verified in later reviews to have been incorporated as agreed. Inc. ASHRAE, 2019 user. single for Licensed | {}
2724a05f-4c96-4146-ae30-51debcf2c8ab | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 44.8 2019 ASHRAE Handbook-HVAC Applications (SI) If the CxA is contracted through a designer, the designer's S com- missioning manager or subconsultant may manage the contractor's issues log. In that case, to minimize conflicts of interest, the CxA is often required to report all issues simultaneously to the designer and to the owner. Accept Design-Phase Commissioning Activities. Commission- ing should include the owner's formal acceptance of the BOD, up- dated OPR, Cx plan, and the design, after review and comment by the CxA. Additional Commissioning Team Tasks. Additional design- phase responsibilities of the commissioning team (led by the CxA, who is frequently responsible for these requirements) include the following: · Build and maintain cohesiveness and cooperation among the proj- ect team · Assist owner in preparing requests for project services that outline commissioning roles and responsibilities developed in the com- missioning plan · Ensure that commissioning activities are clearly stated in all proj- ect scopes of work · Develop scope and budget for project-specific commissioning- process activities · Identify specialists responsible for commissioning specific sys- tems and assemblies · Conduct and document commissioning team meetings · Inform all commissioning team members of decisions that result in modifications to the OPR · Integrate commissioning into the project schedule · Track and document issues and deviations relating to the OPR and document resolutions · Write and review commissioning reports 2.3 CONSTRUCTION-PHASE COMMISSIONING Objectives Commissioning activities should take place throughout the con- struction phase and include verification and documentation that Inc. ASHRAE, 2019 user. single for Licensed · All acceptance testing requirements are documented · All systems and assemblies are provided and installed as specified · All systems and assemblies are started and function properly · All acceptance testing requirements are documented · All record documents are updated · The systems manual is updated and provided to facility staff · Facility staff and occupants receive specified training and orien- tation · Acceptance testing occurs Activities The following primary commissioning activities (in approxi- mately sequential order) address commissioning objectives. The CxA coordinates and ensures that all activities occur and perform successfully. Bidding and Contract Negotiation. A member of the com- missioning team (usually the CxA) may attend the prebid confer- ence to present an overview of commissioning requirements and answer questions. Changes that occur during bidding and contract negotiations related to commissioned systems and assemblies are also reviewed to ensure they agree with the OPR. Commissioning Planning and Kickoff Meetings. The CxA coordinates construction-phase planning and kickoff meetings. The planning meeting held with the contractor, owner, designer, and CxA focuses on reviewing requirements and establishing specific communication and reporting protocols. The commissioning plan is updated from this meeting. The kickoff meeting is held with addi- tional construction team members, who generally include the mechanical, controls, electrical, and test and balancing contractors. At this meeting, the commissioning provider outlines the roles and responsibilities of each project team member, specifies procedures for documenting activities and resolving issues, and reviews the pre- liminary construction commissioning plan and schedule. Team members provide comments on the plan and schedule, and the CxA uses these suggestions to help finalize the commissioning plan and schedule. Submittal Reviews. Commissioning Plan Update. The planning and kickoff meet- ings usually result in an updated commissioning plan. Later, any project phasing or other schedule and scope-related issues (e.g., testing and training plans and schedules) are clarified in further updates. Construction Submittals. The CxA reviews equipment and mate- rial submittals of commissioned systems and assemblies to obtain information needed to develop construction checklists, make mean- ingful observations of construction progress, and aid in developing comprehensive tests. This process also verifies that contractors are providing high-quality submittals that meet the construction docu- ment requirements, and that architects and engineers provide a qual- ity review so construction-related performance issues are identified before construction progress makes them more difficult and expen- sive to address. Submittals could be reviewed concurrently by the design team to allow any discrepancies to be identified before for- mal approval, but the construction submittal review should also be compared to the architects' and engineers' reviews to verify that the architects and engineers are providing a thorough review of the sub- mittals. Controls Submittal and Integration Meeting. Before the contrac- tor develops the controls submittal, the CxA coordinates a controls integration meeting to discuss and resolve methods for implement- ing performance specifications or strategies, interlocks between systems, priority of control between packaged controls and the cen- tral control system, the control system database, point names, graphic details and layout, access levels, etc. Coordination Drawings. The CxA may help the owner monitor the development and coordination of shop drawings to ensure syn- chronization between trades. Early O&M Data. Information beyond typical construction submittals requested by the CxA includes installation and start-up procedures, operation and maintenance information, equipment performance data, and control drawings before formal O&M man- ual submittals. This information allows the CxA to become famil- iar with systems and assemblies to develop construction checklists, start-up plans, and test procedures. Contract Modifications Review. Construction documentation issued during this phase, including requests for information, con- struction field directives, and change orders, should be reviewed by the CxA to identify issues that may affect commissioning and com- pliance with construction documents, BOD, or OPR. Schedule Commissioning Field Activities. The CxA works with the contractors and construction manager to coordinate the commissioning schedule and ensure that commissioning activities are integrated into the master construction schedule. Construction and Commissioning Meetings. The CxA attends periodic planning and job-site meetings to stay informed on con- struction progress and to update parties involved in commissioning. During initial construction, the CxA may attend regular construc- tion meetings and hold a line item on the agenda. Later, the CxA may convene entire meetings devoted to commissioning issues, with more frequent meetings as construction progresses. Attendees vary with the purpose ofthe meeting. Team members should be rep- resented at meetings by parties with technical expertise who are authorized to make commitments and decisions for their respective | {}
e6a58b03-e068-44a6-a04a-a8c61a174b87 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | HVAC Commissioning 44.9 organizations. The CxA should distribute minutes from these meetings. Progress Reports. The CxA provides periodic progress reports to the owner and contractor with increasing frequency as construc- tion progresses. These reports indicate current progress, next steps, and critical issues affecting progress and construction schedule. Update Owner's Project Requirement and Basis of Design. When contract negotiations and/or changes and clarifications made during construction alter or add to the OPR or BOD, these docu- ments should be updated. Normally, the CxA updates the OPR and the designer updates the BOD. Final construction updates to these documents are made at the end of testing, typically a few months into occupancy. Coordinate Owner's Representatives Participation. The commissioning plan should describe participation of the owner's representatives in work such as submittal review, construction checklist verification, construction observation, test procedure re- view and execution, and O&M manual review. The CxA normally coordinates this participation with the contractors. Construction Observation. The CxA should make planned, systematic visits to the site to observe installation of systems and assemblies. The owner's staff may assist in construction observa- tion. The CxA should verify that the first few of any large-quantity items (e.g., variable-air-volume terminal units) are installed prop- erly and used as a mock-up or standard to judge the rest ofthe instal- lation. Any conditions not in compliance with the construction documents or BOD or that may affect system performance, com- missioning, operation, or other project requirements should be documented. These observations normally focus on areas where observers have found problems before, or spot-check items on con- struction checklists. Less often, practitioners are tasked with valida- tions or detailed inspections verifying that equipment or assemblies have been installed properly in every detail. Some practitioners make formal construction observation reports, whereas others merge find- ings into the regular issue logs and progress reports. Site visits should be used to verify completion of construction checklists. The CxA normally witnesses many of the contractor's start-up activities for major equipment to ensure checklists and start-up are documented properly and to gain additional feature and function information from installing technicians. Record Documents. Contractors should be required to immedi- ately update the record drawings when any deviations from the con- struction document occur. During the construction phase, the CxA should verify that the record documents are kept up to date by com- paring the installation with the construction documents, and verify that any changes have been recorded on the record documents. Construction Checklists and Start-up. At the beginning of construction, construction checklists are developed (usually by the CxA in cooperation with the discipline engineer, but sometimes by the contractor or equipment manufacturer) for most commissioned systems and equipment. They are attached to or integrated with manufacturer's installation and start-up procedures. In most proj- ects, contractors fill out the checklists during installation, during normal checkout of equipment and systems, and before and during system start-up, though some commissioning practitioners fill out the checklists themselves. The contractor fully documents start-up and initial checkout, including the construction checklists to ensure systems are ready for testing, and submits them to the CxA, who reviews the forms and spot-checks selected items in the field later in the project. Some CxAs statistically sample items on checklists to verify proper completion (typically random or targeted sampling of 2 to 20%). If an inordinate fraction of the sampled items are deficient (typically more than 10%), the contractor is required to check and document all remaining items. The contractual documents need to contain details of the sampling and actions based on the results. Commissioning Issues Management. The CxA keeps a record of all commissioning issues that require action by the design team, contractor, or owner. The issues should remain uniquely identified, be tied to equipment and systems, and prioritized relative to perfor- mance, cost, and schedule. Issues are tracked to resolution and com- pletely documented. The CxA distributes the updated log to the owner, contractor, construction manager, and HVAC design engi- neer at construction and commissioning meetings. This log can also be placed on project web sites. If the CxA is hired through a con- tractor, the contractor's commissioning manager or subconsultant may manage the contractor's issues log. In that case, to minimize conflicts of interest, the CxA is often required to report all issues simultaneously to the contractor and to the owner. Developing Test Procedures. Step-by-step test procedures and project-specific documentation formats are used for all commis- sioned equipment and assemblies. Manual tests evaluate systems with immediate results. Monitoring testing uses the building automation system or data loggers to record system parameters over time and analyze the data days or weeks later. Automated testing gathers or analyzes system performance data completely electronically, or with significant help from software. Test procedure writing begins immediately after the submittal, because test procedures need to be reviewed and approved before testing occurs, which is generally scheduled about three to six weeks after the submittal review. Test procedures may be based on specifications, applicable standards and codes, submittal data, O&M data, data shipped with the equipment, approved control drawings, and existing test procedures of similar equipment or com- ponents. Tests should cover all functions and modes. Procedural documents clearly describe the test prerequisites, required test conditions, individual systematic test procedures, expected system response and acceptance criteria for each proce- dure, actual response or findings, and any pertinent discussion. Test procedures differ from testing requirements found in the specifi- cations, which describe what modes and features are to be tested and verified and under what conditions. Test procedures describe the step-by-step method of how to test. Simple checklists may be appro- priate for testing simple components, but dynamic testing of inter- acting components requires more detailed procedures and forms. The responsible HVAC design engineer should organize the preparation ofHV AC system testing, adjusting, and balancing (TAB) procedure together with the test and balancing professional and the commissioning authority, depending on their scopes of work. The CxA is responsible for verifying that the test procedures are written and appropriate for determining that equipment, assemblies, and systems function correctly. All parties should have input into the final test procedures to ensure that equipment, assemblies, systems, or people will not be endangered or warranties voided. Industry standard test procedures [e.g., ASHRAE, Air-Conditioning and Refrigeration Institute (ARI), American Composites Manufactur- ers Association (ACMA)] should be referenced whenever possible. Testing and Verification. Responsibilities and Management. Traditional air and water test- ing, adjusting, and balancing is often performed by the contractor or by an independent contractor employed by the owner. Building envelope, elevators, and electrical system testing are generally excluded from HVAC commissioning, but may be included in whole-building commissioning. The CxA reviews the testing and verification plan and results, and may spot-check the results to ver- ify the testing was completed. There is some movement in the indus- try to centralize coordination for quality assurance/quality control (QA/QC) functions under the commissioning team. Each project is unique, and different approaches can be warranted. Critical issues include ensuring that · Appropriate testing rigor is applied Inc. ASHRAE, 2019 user. single for Licensed | {}
342596f8-e8f6-465b-911b-33d8725525dc | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 44.10 2019 ASHRAE Handbook-HVAC Applications (SI) · Technically qualified parties execute and document the testing · Objectivity is maintained · Testing is well documented For systems not usually thoroughly tested by the contractor [e.g., HV AC systems and controls, lighting controls, specialty plumbing, and envelope and interfaces between systems (security, communica- tions, controls, HVAC, fire protection, emergency power)], the CxA may write test procedures that go beyond HV AC tests. The CxA then directs, witnesses, and documents each test executed by the contrac- tor after the contractors have ensured that the systems will pass these tests. The controls subcontractor usually executes the tests, although the CxA may test some equipment with or without the contractor present. Testing that has traditionally been conducted by the contractor (e.g., fire alarm, fire protection, elevator, duct and pipe tests, emer- gency power, some electrical equipment) ideally should be centrally coordinated. This can be the responsibility ofthe contractor or of the CxA. The specifications should clearly establish testing and docu- mentation requirements and define the responsible party. The level of confidence and objectivity can be increased by requiring experts in specific disciplines to witness tests, particularly in some electrical system and envelope assembly field testing. Increasing the required amount offield witnessing by the CxA also improves the confidence that commissioning was correctly performed. Within a given discipline, there may be differing levels of auton- omy. For example, in tests of electrical equipment (e.g., circuit breakers), the contractor may conduct and document the bolt-torque tests, and also be required to hire an independent certified testing agency to conduct other necessary tests that require more special- ized expertise and test equipment. The owner's technical staff can assist in and benefit from partic- ipation in any of the above scenarios. The designer and owner's project management staff may witness selected tests. Verification Testing Scheduling. Verification testing should be performed after equipment and assemblies are complete and started up, construction checklists checked out and submitted, air and water balancing completed, and the contractors' systems testing finished. The contractor is then ready to turn the system over to the owner. Most projects require a certificate of readiness from the contractor certifying that the system has been thoroughly checked out and ver- ified to be completely functional. Ideally, manual testing occurs before substantial completion, but schedule slippage may require testing to occur after this milestone. Some short-term monitoring may be completed with manual testing, but sometimes is postponed until early occupancy. Opposite-season and other deferred testing should be conducted during seasonal changes or peak seasonal con- ditions. Testing Scope. At a minimum, testing includes observing and documenting system operation and function during normal opera- tion, through each of their sequences of operation, and all other modes of operation and conditions, including manual, bypass, emergency, standby, high and low load, and seasonal extremes, and comparing actual performance to that specified in the construction documents. Testing may also be conducted to verify performance criteria found in the BOD and OPR, including system optimization, though deficiencies in these areas are not normally the contractor's responsibility. Manual Testing Methods. Testing includes observing normal operation; changing set points, schedules, and timers; and exercis- ing power disconnects, speed controls, overwriting sensor values, etc., to cause perturbations in the system. System response and results are recorded on test procedure forms, and any issues are doc- umented. Small corrections are often made during testing. Less pressing corrections or issues with unknown solutions are investi- gated later, corrected, and retested. Building automation systems (BAS), when present, can be the backbone for conducting much of the testing, collecting, and ar- chiving data. Before using the BAS, critical sensors, actuators, and features should be verified as calibrated so the system readouts are reliable (although all sensors and actuators should have been cali- brated by the contractor and documented on construction check- lists). The results are viewed on the building automation system screen or at the equipment. Other tests may require hand-held in- struments or visual verification (e.g., evaluating caulking and flash- ings on window installations). Monitoring. Some testing requires monitoring (trending) system operation over time through the BAS or data loggers (when the BAS does not monitor desired points). Monitoring can be used to docu- ment that systems are performing properly during test conditions over the monitoring period. However, this is not a substitute for manual testing, which can cover a wide range of conditions. Moni- toring provides a view of system interactions over the course of nor- mal, start-up, shutdown, and weekend operation. Normally, the CxA analyzes monitored data and submits a report, with any con- cerns added to the issues log. Automated Testing. Various semiautomated testing is conducted in permanent onboard equipment controllers. Currently, most truly automated testing focuses on identifying electrical faults in control- ler components and is used during vendor start-up and troubleshoot- ing activities. Some use logic to identify parameters outside limits, which indicate component malfunctions such as hunting and cali- bration issues. Different types of automated testing intended to help commissioning are under development. Some are primarily tools to gather and display monitored data; others help the analyzer make diagnoses. Equipment manufacturers often integrate automated commissioning testing capabilities into onboard controllers on their equipment. Training. Training should include, as appropriate, (1) the gen- eral purpose of the system; (2) use and management of the systems manual; (3) review of control drawings and schematics; (4) start- up, shutdown, seasonal changeover, and normal, unoccupied, and manual operation; (5) controls set-up and programming; ⑥ diag- nostics, troubleshooting, and alarms; (7) interactions with other systems; (8) adjustments and optimizing methods for energy con- servation; (9) relevant health and safety issues; (10) special main- tenance and replacement sources; (11) tenant interaction issues; and (12) discussion of why specific features are environmentally sustainable. Occupants may also need orientation on certain sys- tems, assemblies, and features in the building, particularly sustain- able design features that can be easily circumvented. The CxA helps the owner ensure that adequate training plans are used by the contractor and that training is completed according to the construction documents. (See the discussion of defining training requirements in the section on Commissioning During Design.) Some CxAs conduct testing with a sample of trainees to verify the efficacy of the training. Most training should be accomplished during construction, be- fore substantial completion. However, for complex systems (e.g., control systems), multiple training sessions should occur before and after substantial completion. Training for systems that will not come into operation until the next season may be delayed. A mean- ingful training program typically includes using the operation and maintenance components ofthe systems manual, which must be sub- mitted before training begins. Selected training materials can be video-recorded as desired by the owner. Commissioning Record. The CxA compiles all commissioning documentation and project data, which are submitted and become part of the systems manual. The commissioning record contains the salient documentation of commissioning, including the commis- sioning final report, issues log, commissioning plan, progress re- ports, submittal and O&M manual reviews, training record, test Inc. ASHRAE, 2019 user. single for Licensed | {}
b8ea4b19-e433-4251-b03e-cdef61fb67e1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | HVAC Commissioning 44.11 schedules, construction checklists, start-up reports, tests, and trend log analysis, grouped by equipment. Final Commissioning Report. The CxA should write (or review) and submit a final commissioning report detailing, for each piece of commissioned equipment or assembly, the adequacy of equipment or assemblies meeting contract documents. The follow- ing areas should be covered: (1) installation, including procedures used for testing equipment with respect to specifications; (2) func- tional performance and efficiency, including test results; (3) O&M manual documentation; and (4) operator training. Noncompliance items should be specifically listed. A brief description of the verifi- cation method used (manual testing, trend logs, data loggers, etc.) and observations and conclusions from the testing should be included. The CxA updates the final commissioning report after occupancy/operations-phase commissioning. The commissioning documents also should include, among other things, · Certificates and warranties of system completion with a complete set of as-built drawings submitted from mechanical, electrical, piping, plumbing, control, and fire protection contractors · Complete records of all problems and solutions occurred during start-up, testing, and adjustments submitted by every individual contractor or subcontractor · Certified system testing and balancing report from the licensed TAB company, with verified major equipment models, capacities, and all tested performance records conforming to system design criteria · Ifroom pressurization is required, a complete room-to-room pres- surization map in the TAB report · If room cleanliness is required, a certified as-built room cleanli- ness report of testing during completion of construction and installation Systems Manual Submittal. The CxA usually compiles the sys- tems manual and provides it to the owner. At the end of construc- tion, the designer, contractor, owner, and CxA provide elements of the systems manual generated during the construction phase. The systems manual should include commissioning test procedures, results of commissioning tests, issue logs and resolution, system schematics, O&M information, record drawings, construction checklists, start-up reports, and trend log analysis, grouped by equipment. The CxA normally reviews and approves systems man- ual submissions by the contractor and designer, similar to traditional O&M manual reviews. Electronic systems manuals, now developed occasionally, will likely become standard in the future. 2.4 OCCUPANCY- AND OPERA TIONS-PHASE COMMISSIONING Occupancy- and operations-phase commissioning typically begins with resolving the findings from performance monitoring over the first month or two into occupancy, and ends with the completion of the first year of occupancy. Objectives Commissioning during this phase should ensure the following: · Initial maintenance and operator training is complete. · Systems and assemblies received functional opposite-season ver- ification. · Outstanding performance issues are identified and resolved before warranty expiration. · Commissioning process evaluation is conducted and satisfacto- rily resolved. Activities Verifying Initial Training Completion. The CxA ensures that any remaining training is conducted according to the contract documents, either by reviewing documentation of the training or through witnessing portions of the training. This normally applies to control systems and training on major systems for which peak sea- son is not near the end of the construction phase. Seasonal Testing. Seasonal testing verifies proper operation of those systems for which peak-load conditions are not available before substantial completion. Additionally, intermediate-season testing may be required for part load, and changeover testing may be required. For example, when completion occurs in winter, final full- load cooling system testing must wait until the following summer. Intermediate-season testing verifies system changeover controls and ability to maintain space conditions per OPR. Testing should be performed by the appropriate contractor and witnessed by the CxA and building operators. However, the owner's operations staff and the CxA, if sufficiently proficient with the controls system, can exe- cute the tests and recall contractors only if there are problems. Near- Warranty-End Review. The CxA may also be asked to return a few months before the contractor's one-year warranty expires, to interview facility staff and review system operation. By acting as the owner's technical representative, the CxA assists facil- ity staff to address any problems or warranty issues. Documentation Update. Any identified operations-phase con- cerns are added to the issues log and the final commissioning report is amended to include occupancy/operations-phase commissioning activities. Changes to the BOD, OPR, or record documents are documented by updating the systems manual near the end of the warranty. Changes to sequences of operation require particular care in ensuring that these updates occur. Commissioning Process Evaluation. The CxA should meet briefly with the owner; general, controls, mechanical, and electri- cal contractors; and mechanical and electrical designers to dis- cuss the commissioning process for this project. Topics to be addressed include what went well, what could be improved, what would best be done differently next time, etc. This will benefit all parties in commissioning future projects. The CxA will submit a report on this meeting to the owner. The occupancy/operations phase typically begins with resolv- ing the findings from monitoring a month or two into occupancy, and ends when the one-year equipment warranties expire. Additional Activities. The CxA may also be given other respon- sibilities during the warranty period, such as helping develop a maintenance management program, optimizing system perfor- mance, and developing electronic facility manuals. Ongoing or Recommissioning. Ongoing monitoring and peri- odic retesting and calibration of selected systems and assemblies are recommended to ensure they comply with the OPR, operating and functioning optimally throughout their life. This is sometimes called recommissioning. Some recommissioning methods rely more on semicontinuous monitoring of primary system performance param- eters with periodic analysis. Other approaches consist of recalibrat- ing and retesting targeted systems and components on a regular schedule, including both manual testing and monitoring. Calibration and test frequency vary with equipment and its application. 2.5 LIFE AND PROPERTY SAFETY CHECK Human life and property safety should be considered in all types of new or renovation projects, during all phases. The National Fire Protection Association (NFPA), American Conference of Govern- mental Industrial Hygienists (ACGIH), and U.S. Occupational Safety and Health Administration (OSHA) have detailed regula- tions for dealing with hazardous conditions that may be present, especially in industrial settings. The following are some of the essential categories to be checked during the entire project commis- sioning process. Inc. ASHRAE, 2019 user. single for Licensed | {}
6a676809-1ab3-4728-a279-2af3e082acce | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 44.12 2019 ASHRAE Handbook HVAC Applications (SI) Hazards Generated on Site Hazards present on the project property require proper attention to safety issues; otherwise, the consequences could affect not only the occupancy' s personnel and the property, but also the surrounding communities. Therefore, the CxA must understand the hazards gen- erated in the property and how to minimize them. Typical sites with hazards include laboratories, manufacturing facilities, chemical plants, or other industrial facilities. Different project properties include many different areas, each with distinct equipment or operating processes that have unique hazards; examples include fuel handling (gas, fuel oil, or coal), chemical emissions, heated lubrication and seal oil, oil-filled trans- formers, cable vaults, coal handling, and control rooms in industrial properties; and cross contamination in hospitals. Implementing comprehensive human health and life protection requirements, as well as fire protection systems that include hazard detection, alarm, and suppression systems, can be a complex chal- lenge that requires the CxA 's thorough understanding and experi- ence of the intricacies of different type of individual projects. Effective Fire and Hazardous Gas Detection and Alarm Systems The fire and hazardous gas detection system provides early and reliable detection of fire or hazardous gas, where such events are likely to occur, alerts personnel and initiates protective actions auto- matically or manually upon operator intervention. Call points include but are not limited to the following: · Gas detectors for oil and gas skids · Hydrogen (H2) detectors for battery rooms · Spark and flame detectors for coal conveyors and fuel oil tanks · Heat detection for oil-filled transformers · Lubrication oil and seal oil skids · Linear heat detectors for cable galleries and fuel oil tanks · Smoke and heat detection for plant and nonplant buildings · Carbon dioxide (CO2) detectors for school classrooms Active Fire Protection Systems These are automatic or manually activated systems involved in actual firefighting: for example, pumping systems, network with fire and gas detection and alarm systems, deluge spray systems, foam systems, CO2 systems, clean agent systems, portable and mobile extinguishers, and fire station and fire tenders. Careful design, high-quality installation, and continuous mainte- nance of explosion prevention and fire protection systems ensures proper safety to the industrial plants. National Security and Emergency Response Plan National security and emergency response have become increas- ingly prominent, and protecting first responders during extraordi- nary events is highly important. Emergency response plans need to include scheduled routines for training, drills, and fire protection system testing for the fire protection crew and others on staff, as well as instructions for cooperation with national security and civil defense programs. Major concerns include firefighter safety, and making sure that first responders have adequate training and cloth- ing and equipment to deal with any emergency (e.g., hazardous materials, radiological attack, ordinary fires or explosions). NFPA Standard 1600, one of NFPA 's most widely implemented standards, establishes a common set of criteria for disaster manage- ment, emergency management, and business continuity programs. Also, Chapter 59 of this volume discusses security concerns and measures for HVAC systems. 3. COMMISSIONING COSTS Commissioning costs vary considerably with project size and building type, equipment type, scope, and traveling requirements (Mills et al. 2004; Wilkenson 2000). Historically, commissioning focused on HV AC and controls, and started during construction. However, quality assurance/quality control (QA/QC) for increasing numbers of systems is included in commissioning, and the process now frequently begins in the design phase. Currently, the commis- sioning industry is not mature; budget estimates, even for relatively detailed scopes of work, vary widely. Clear definition of tasks, deliverables, systems and components to be commissioned, rigor, and testing methods must be provided for comparative pricing. The costing guidelines that follow must be used with great caution and are provided only for rough planning purposes. Understanding what is and is not included in each cost number is critical. Owners should consult commissioning providers with their planned projects to obtain budget estimates, and practi- tioners should use detailed cost breakdowns for their pricing. 3.1 DESIGN-PHASE COSTS (INCLUDING PREDESIGN AND DESIGN) Predesign-phase costs include the CxA 's efforts in attending pre- design meetings and design reviews with the architect's consulting team and owner's representatives. This portion of work may range from 8 to 12% of the CxA 's contract. Design-phase costs include the CxA 's reviewing design submittals, coordinated with the designer, and developing sections of the systems manual (design intent and basic operations from the control submittal). This portion of the work may range from 15 to 20% of the CxA contract. For a project that includes the discussed tasks for all HV AC and controls components, a moderate level of electrical systems com- missioning, and minor plumbing and envelope commissioning, the total commissioning costs (CxA cost plus the additional work of the designers) may range from 0.2 to 0.6% of the total construction cost for a typical office building. This estimate assumes two mod- erate design reviews. Different types of buildings or more complex buildings with larger scopes of design review may cost consider- ably more. 3.2 CONSTRUCTION- AND OCCUPANCY/ OPERATIONS-PHASE COSTS Table 1 estimates the CxA's costs for the construction and occupancy/operation phases under the CxA-managed approach. It includes construction- and occupancy/operations-phase commis- sioning for the HVAC system (including fire and life safety controls, changeover season, and opposite season) and electrical system (in- cluding lighting controls, emergency power, and limited connection and grounding checks). It does not include specialty testing such as full infrared scanning, power quality, switchgear, transformer, or low-voltage-system testing. Complex systems and critical appli- cations have higher costs. For a given building type and complexity, larger buildings tend to come in at the lower end of the range and smaller buildings at the higher. The listed costs cover only the CxA fees; there are also costs to the contractor, designers, and owner's staff. Costs for the mechanical contractor attending meetings, documenting construction checklists, and assisting with testing approximate 10 to 20% of the CxA 's mechanical commissioning costs. The electrical contractor's costs may equal the CxA 's electrical commissioning costs for electrical commissioning (because contractors are usually responsible for hiring their own electrical testing company to perform electrical tests). International Electrical Testing Association (NETA) tests are often already part of the normal construction program, and the only Inc. ASHRAE, 2019 user. single for Licensed | {}
2ccd09ee-917e-4cc2-98ac-b73ef3232c37 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | HVAC Commissioning 44.13 Table 1 Estimated Commissioning Authority Costs to Owner for Construction and Occupancy/Operations Phases ¦ Commissioned System ¦ Total Commissioning Cost ¦ ¦ --- ¦ --- ¦ ¦ HVAC and controlsa ¦ 2.0 to 3.0% of mechanical ¦ ¦ Electrical systema ¦ 1.0 to 2.0% of electrical ¦ ¦ HVAC, controls, and light electricalb ¦ 0.5 to 1.5% of construction ¦ ¦ Sources: aWilkinson (2000). ¦ ¦ bPECI (2000). additional commissioning costs are for the CxA to coordinate test- ing, spot-witness, and review reports. 3.3 EXISTING BUILDINGS Existing building commissioning (EBCx) is a quality-focused process for attaining the current facility requirements (CFR) of an existing facility and/or its systems and assemblies. The process focuses on planning, investigating, implementing, verifying, and documenting that the facility and/or its systems and assemblies are operated and maintained to meet the CFR, with a program to main- tain the enhancements for the remaining life of the facility. System performance normally degrades with use and time, at a rate depend- ing on the quality of maintenance and operations and the number of hours of operation. Quality of maintenance also affects equipment life expectancy. An EBCx effort should include updating or develop- ing an owner's current facility requirements, documenting existing systems, surveying the facility to identify operational inefficiencies, quantifying and prioritizing the inefficiencies found, determining how best to optimize equipment or operation, implementing changes, training operating personnel, documenting operations, and then reverifying with ongoing measurements that the EBCx process activities produced and continue to produce the desired effect. EBCx is used by owners and facility decision makers to optimize the operations of their existing facilities to meet their current facility requirements. The process has five basic steps, with an additional step for multifacility projects: · Multifacility planning (if multiple buildings are involved) · Assessment · Investigation · Implementation · Hand-off · Ongoing commissioning After assembling the team for commissioning, the goals and objectives of the process are defined and documented. Existing information on the facilities is gathered and analyzed to determine the order in which the facilities should be commissioned. The order is based on the goals and objectives of the process. Facility ranking can be based on a number of factors, including energy usage, occu- pant satisfaction, maintenance issues, or other factors determined during development of the goals and objectives. A plan is developed and documents how the EBCx process will proceed among the buildings in the multifacility EBCx program. The assessment phase includes development of the CFR, an ini- tial assessment of the facility, and development of the EBCx plan. The CFR is developed with the help of users, occupants, and owners to define their specific requirements for the facility based on its cur- rent use. The CFR may be different from the original OPR if the facility's use has changed. The initial assessment of the facility is based on existing documentation, benchmarks, interviews with building personnel, and a tour of the facility. From the assessment report, an EBCx plan is developed that defines the project's scope, schedule, team members, and approach of subsequent project phases. The investigation phase includes more detailed interviews with maintenance personnel, testing and documentation of existing build- ing performance, and identification and analysis of recommended changes. When existing systems may not have the capacity to meet the CFR, system deficiencies need to be documented with a decision on when (or whether) upgrading will be done. For example, indoor air quality objectives may not be met because a system was designed under an older standard or code; temperature objectives may not be met because additional computer equipment loads have been added, and the original system was designed to handle a lower load. In each case, a documented recommendation on the options available should be provided to the owner. After the EBCx team identifies recom- mended changes, the CxA develops an investigation report that doc- uments the recommended changes and their associated costs and benefits. This report can be used by the owner to select recommen- dations for implementation. The implementation phase begins with the owner selecting rec- ommendations for implementation. The selected capital, repair, and upgrade projects are implemented and verified. Informal training on the systems and equipment is provided to the owner's personnel as the projects are implemented. The hand-off phase transitions the improvements to the owner' s O&M personnel. This phase includes developing and reviewing the systems manual, owner training, verification of training, and final- izing the existing building commissioning report. The ongoing commissioning phase includes EBCx activities that will continue throughout the facility's life. This phase includes ver- ifying achievement of the CFR, reviewing measurement and verifi- cation data, investigating unacceptable performance, implementing recommended changes to improve performance, updating facility personnel training, and updating building documentation. EBCx has been shown to be a very cost-effective way to improve occupant comfort and productivity and optimize operational costs. Energy savings of 13 to 16% with a one- to four-year payback have been reported (Mills 2009). Buildings with systems ranging from older pneumatic controls to newer building automation systems (BASs) have been success- fully commissioned. Pneumatic controls limit the number of EBCx options that can be implemented, and may also require separate data logging for monitoring parameters used to calculate energy savings. Modern BASs allow lower-cost EBCx as well as trend logging of various parameters to sustain the savings achieved when the sys- tems are verified to be functioning properly and calibrated. 3.4 CERTIFICATION Several groups offer certification of commissioning authorities and providers, including the following: · ASHRAE's Commissioning Process Management Professional (CPMP) program targets individuals who manage and oversee the commissioning process and commissioning team members. Recipients are usually design/consulting professionals and tech- nologists. · The AABC Commissioning Group (ACG) offers a certification program for TAB engineers. · The American Society of Healthcare Engineering offers a Health Facility CommissioningⓇ (HFCX) certification. · The Association of Energy Engineers (AEE) offers a Certified Building Commissioning Professional (CBCPⓇ) certification. · The Building Commissioning Association (BCA) offers certifica- tion for a Certified Commissioning ProfessionalTM (CCPTM). · The National Environmental Balancing Bureau (NEBB) offers certification for commissioning providers by system type (e.g., HVAC, plumbing, fire protection). · The University of Wisconsin offers three levels of certification: professional, managerial, and technical support. Inc. ASHRAE, 2019 user. single for Licensed | {}
13250523-644c-45dc-9828-2a69708ada76 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 44.14 2019 ASHRAE Handbook-HVAC Applications (SI) REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. ASHRAE. 2013. The commissioning process. ASHRAE Guideline 0-2013. ASHRAE. 2007. HVAC&R technical requirements for the commissioning process. ASHRAE Guideline 1.1-2007. ASHRAE. 2008. Preparation of operating and maintenance documentation for building systems. ASHRAE Guideline 4-2008 (RA 2013). ASHRAE 2013. Commissioning Process for Buildings and Systems. ANSI/ ASHRAE/IES Standard 202-2013. Mills, E. 2009. Building commissioning: A golden opportunity for reduc- ing energy costs and greenhouse-gas emissions. Report DE-AC02- 05CH11231. Lawrence Berkeley Laboratory, Berkeley, CA. Available from cx.lbl.gov/2009-assessment.html. Mills, E., H. Friedman, T. Powell, N. Bourassa, D. Claridge, T. Haasl, and M.A. Piette. 2004. The cost-effectiveness of commercial-buildings com- missioning: A meta-analysis of energy and non-energy impacts in exist- ing buildings and new construction in the United States. Lawrence Berkeley National Laboratory Report LBNL-56637. NFPA. 2012. Standard on disaster/emergency management and business continuity programs. Standard 1600. National Fire Protection Associa- tion, Quincy, MA. PECI. 2000. The National Conference on Building Commissioning Proceed- ings. Portland Energy Conservation, OR. Wilkinson, R. 2000. Establishing commissioning fees. ASHRAE Journal 42(2):41-47. BIBLIOGRAPHY ASHRAE. 2012. The commissioning process for smoke control systems. Guideline 1.5-2012. ASHRAE. 2002. Measurement of energy and demand savings. Guideline 14-2002. ASHRAE. 2002. Laboratory design guide. Claridge, D.E., W.D. Turner, M. Liu, S. Deng, G. Wei, C.H. Culp, H. Chen, and S. Y. Cho. 2004. Is commissioning once enough? Energy Engineer- ing 101(4):7-19. DOE. 2002. Continuous commissioning guidebook. www1.eere.energy .gov /famp/pperations_maintenance/on_coguide.html Idaho Department of Administration. 1999. State ofIdaho retrocommission- ing guidelines. Available at dpw.idaho.gov/pdf/app7rcg.pdf. Idaho Department of Administration. 2000. New-building commissioning guidelines. dpw.idaho.gov/pdf/app7nbcg.pdf. Kats, G.H., A.H. Rosenfeld, T.A. McIntosh, and S.A. McGaraghan. 1996. Energy efficiency as a commodity: The emergence of an efficiency sec- ondary marketfor savings in commercial buildings. U.S. Department of Energy Protocol. Available from www.eceee.org/library/conference _prosestingsikcse,Bammuncn_Bruits/19977Pmanc_26 MDAE. 2000. Best practices in commissioning in the state of Montana. Montana Division of Architecture and Engineering. NEBB. 2009. Procedural standards for retro-commissioning of existing buildings. National Environmental Balancing Bureau, Gaithersburg, MD. NEBB. 2014. Procedural standards for whole building systems technical commissioning. National Environmental Balancing Bureau, Gaithers- burg, MD. NFPA. 2015. Flammable and combustible liquids code. Standard 30. Na- tional Fire Prevention Association, Quincy, MA. NFPA. 2015. National fuel gas code. Standard 54. National Fire Protection Association, Quincy, MA. NFPA. 2012. Standard for fire and explosion prevention during cleaning and purging of flammable gas piping systems. Standard 56. National Fire Protection Association, Quincy, MA. NFPA. 2013. Standard for the production, storage, and handling ofliquefied natural gas (LNG). Standard 59A. National Fire Protection Association, Quincy, MA. NFPA. 2011. Boiler and combustion systems hazards code. Standard 85. National Fire Protection Association, Quincy, MA. NFPA. 2015. Life safety codeⓇ. Standard 101. National Fire Protection Association, Quincy, MA. NFPA. 2012. Standard for the prevention of fires and explosions in wood processing and woodworking facilities. Standard 664. National Fire Pro- tection Association, Quincy, MA. SMACNA. 2013. HVAC systems commissioning manual. Sheet Metal and Air Conditioning Contractors' National Association, Chantilly, VA. U.S. DOC. 1992. HVAC functional inspection and testing guide. NTIS Tech- nical Report PB92-173012. U.S. Department of Commerce, Washing- ton, D.C., and General Services Administration, Washington, D.C. U.S. DOE/PECI. 1997. Model commissioning plan and guide commission- ing specifications. NTIS Technical Report DE97004564. U.S. Depart- ment of Energy, Washington, D.C., and Portland Energy Conservation, OR. Inc. ASHRAE, 2019 user. single for Licensed Related Commercial Resources | {}
42a8b16a-4ce7-4934-aec8-dd59e468557d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 45 BUILDING ENVELOPES ¦ Terminology ¦ 45.1 ¦ Roofs ¦ 45.8 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Governing Principles ¦ 45.2 ¦ Walls ¦ 45.8 ¦ ¦ Design Principles ¦ 45.3 ¦ Fenestration ¦ 45.10 ¦ ¦ Quick Design Guide for High-Performance ¦ ¦ Foundations ¦ 45.11 ¦ ¦ Building Envelopes ¦ 45.8 ¦ Existing and Historic Buildings ¦ 45.11 ¦ P physics building envelope design requires knowledge of the governing building performance as well as of building materials and how they are assembled. This chapter provides practi- cal information for designing new building envelopes and retrofits to existing envelopes, always with the notion that the envelope must work well in concert with the building's surroundings and the HVAC system. The information can also be useful for those involved with building envelope investigation and analysis. This chapter was developed with the integrated design approach in mind and assumes that the architect, HV AC designer, building enve- lope designer, and others involved in envelope design and construc- tion communicate and understand the interrelationships between the building enclosure and mechanical systems. Integrated design re- quires a clear statement of the owner' s project requirements (OPR) and design intent, and is described in greater detail in Chapter 60. That chapter may be used as a basis for finding common agreement among designers and engineers using the integrated design approach. The growing use of integrated design in project delivery highlights the building envelope as the principal site where architectural design and mechanical engineering meet. A successful building envelope design requires that the team be knowledgeable about and responsible for the performance require- ments described in this chapter. This chapter does not distinguish the individual responsibilities of each team member, but rather is in- tended to serve the team as a whole. Buildings are designed and constructed to provide shelter from the weather and house conditioned, habitable spaces for occupants. The building envelope is an assembly of components and materials that separate the conditioned indoor environment from the outdoor environment. The envelope typically includes the foundation, walls, windows, doors, and roof. Partitions between interior build- ing zones that have substantially different environmental conditions (such as a swimming pool compared to an office area) are often required to function similarly to building envelopes. Performance requirements for the building envelope include the following (Handegord and Hutcheon 1989; Hendriks and Hens 2000; Hutcheon 1963): · Control heat flow · Control airflow, including airborne contaminants · Control liquid water penetration (with rain as the most important source) · Control water vapor flow · Control light, solar, and other radiation · Control noise · Control fire · Provide strength and rigidity against outside influences (some- times structural) · Be durable · Be constructable, maintainable, and repairable The preparation of this chapter is assigned to TC 4.4, Building Materials and Building Envelope Performance. · Be aesthetically pleasing · Be economical · Be sustainable These performance requirements and their effects on one another must be understood by the project team. Building envelopes should be designed for good overall performance. The first eight listed items arise from the envelope' s function of separating the conditioned and unconditioned environments. Parties responsible for HV AC and building envelope design must be knowledgeable about how each system affects the performance of the other. Review of the heat, air, and moisture characteristics of the proposed envelope is needed for appropriate design of HVAC systems. The building envelope must also be designed with an understanding ofthe interior and exterior en- vironmental design conditions; consequently, the architect or princi- pal designer needs to provide the specific performance requirements to the HVAC designer, including provisions to achieve minimum air- tightness, interior occupancy criteria, and special-use considerations. With a building envelope design suited to the operating requirements, the space-conditioning (HVAC) system generally is smaller in capac- ity and may have simpler control and distribution systems, normally resulting in a system with greater efficiency. This chapter applies information in Chapters 25 to 27 of the 2017 ASHRAE Handbook-Fundamentals to building envelope design. It also incorporates much of the material from previous versions (until 2005) of that volume's Chapter 24. 1. TERMINOLOGY For definitions related to the physics of heat air and moisture transport, see the Terminology section in Chapter 25 of the 2017 ASHRAE Handbook-Fundamentals. An air barrier component is a premanufactured element with air leakage characteristics that are determined during manufactur- ing. An air barrier material is a material with a low air leakage. An air barrier accessory is an element used to connect air bar- rier materials and components to form an air barrier assembly or an air barrier system, or used to fasten the air barrier material to a sub- strate or to framing members. An air barrier assembly is a combination of air barrier materials and air barrier accessories that forms a continuous barrier that con- trols airflow in its immediate area. An air barrier system is a combination of air barrier assemblies, components, and accessories in a building envelope, forming a con- tinuous barrier that controls airflow across the envelope. A building assembly is any part of the building envelope (e.g., wall, window, roof) that has boundary conditions at the conditioned space and the exterior. A building envelope or building enclosure is the overall physi- cal structure that provides separation between conditioned spaces and the outdoor environment or any indoor environment that is sub- stantially different from the conditioned one. 45.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
8f2b6231-3091-4fe0-b98c-98fc2925b9c2 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 45.2 2019 ASHRAE Handbook-HVAC Applications (SI) A (building) component is any physical element or material within a building assembly. Moisture condensation is the change in phase from vapor to liq- uid water. Condensation occurs typically on materials such as glass or metal that are not porous or hygroscopic and on capillary porous materials that are capillary saturated. Condensation should be dis- tinguished from phase change between vapor and bound water in capillary or open porous materials (see moisture content). Durability is the ability of a building or any ofits components to perform its required functions in its service environment over a period of time without unforeseen cost for maintenance or repair (CSA 2007). Fenestration includes all areas (including the frames) in the building envelope that let in light. Fenestration includes windows, curtain walls (vision areas), clerestories, skylights, and glazed doors. Fenestration excludes insulated spandrels and solid doors. Fenestration area is the total area of fenestration measured using the rough opening, including the rough opening for doors. Hygrothermal design analysis is a set of calculation procedures that uses building design and component physical properties to pre- dict heat, air, and moisture performance of envelopes and assem- blies under design conditions. See Chapters 25 to 27 in the 2017 ASHRAE Handbook- -Fundamentals. Infiltration is uncontrolled inward air leakage through open, porous materials, cracks, and crevices in any building component and around windows and doors caused by pressure differences. Exfiltration is uncontrolled outward air leakage through open, porous materials, cracks, and crevices in any building component and around windows and doors caused by pressure differences. Wind washing is uncontrolled wind-induced flow of outdoor air in and behind insulation layers Air intrusion is uncontrolled pressure-induced flow of indoor air in, through, and in front of air-permeable insulation layers, caused by wind pressures, stack effect, or HV AC systems. Convective loop is uncontrolled stack-induced convective flow of cavity air in and around insulation layers Thermal insulation is any material specifically designed to decrease heat flow by equivalent conduction through a building envelope or envelope assembly. Moisture content is the ratio of mass of water to volume of dry material in porous and hygroscopic materials, in kg/m3. Bound water describes the phase of water bound in hygroscopic materials. Sorption (and desorption) describes the change in phase between vapor and bound water. A plenum is a compartment or chamber to which one or more ducts are connected, that forms part of an air distribution system, and is not used for occupancy or storage. A plenum is often under positive or negative air pressure relative to adjacent spaces. The R-value of a material is the thermal resistance for a given thickness of that material, as provided by the manufacturer or listed in Table 4 of Chapter 26 in the 2017 ASHRAE Handbook-Fun- damentals. The system R-value (Rs) is the sum of the individual R-values for each material, excluding air films. The total R-value (RT) is the sum of the system R-value and the interior and exterior air-film resistances (see Chapter 25 in the 2017 ASHRAE Hand- book-Fundamentals). A thermal break is a thermally resistive element that decreases heat conduction through an assembly. A thermal bridge is a thermally conductive element through an otherwise thermally resistive assembly. U-factor or thermal transmittance is the rate of heat transfer per unit surface of an assembly per unit temperature difference between the environments at both sides of the assembly. The clear value only considers the surface film resistances and R-values ofthe material layers comprising the assembly. The U-factor is 1/RT. A whole-wall or effective U-factor also takes into account thermal bridging, convective loops, wind washing, and indoor air washing effects (see Chapter 25 in the 2017 ASHRAE Handbook-Funda- mentals). A vapor retarder or vapor barrier is any component in a building envelope with a low permeance to moisture flow by dif- fusion. A water-resistive barrier (WRB) is a building envelope com- ponent designed to prevent inward movement of liquid water. 2. GOVERNING PRINCIPLES The building envelope is the key element in managing the envi- ronmental loads on the building. These loads are a function of the climate and the indoor conditions, such as air temperature, relative humidity, and air pressure differential. There is a strong interdepen- dence between a building HV AC system and the envelope that must be considered when designing or modifying a building. This inter- dependence centers on controlling heat flow, airflow (including control of airborne contaminants), and water and water vapor flow. Design parameters involved are as follows. Design Parameters Heat. The type and amount ofinsulation to be provided depends on the climate, governing codes, and building use. The insulation should be continuous, while considering the limitations ofthe mate- rials and systems. Discontinuities (or thermal bridges) are the sites of unwanted heat transfer and reduce energy efficiency, which may result in premature soiling (e.g., ghosting), surface condensation, and/or mold growth. In heating- and cooling-dominated climates, reduced thermal performance can affect indoor conditions and increase HVAC loads. The thermal conductivities and R-values of insulating materials allow them to be compared for their effect on heat transfer, though their properties related to air and moisture transfer vary widely. Air. Some buildings are designed for natural ventilation when building use and climate allow, and for mechanical space condition- ing (with ventilation) at other times. During periods of space condi- tioning, the building envelope should show minimal air leakage. This allows better control of (1) HVAC, (2) inflow of airborne con- taminants, and (3) noise transmission. The HVAC system can gen- erate pressure differentials across the envelope that increase air leakage and may create moisture and thermal problems. Itis import- ant to review the interaction ofthe HV AC system and envelope at the design stage. Moisture. Building envelopes should be designed to shed rainwa- ter, prevent accumulation of moisture in moisture-sensitive materi- als, and allow draining and drying of water that accumulates. Airflow through openings in the envelopes a secondary means of moisture transport through building envelopes. Liquid water and frost can accumulate on cold materials in a wall assembly along air movement paths. Vapor diffusion can play a role in wetting and especially in drying of building materials. Although vapor diffusion control in an envelope assembly is im- portant, field experience shows that most moisture problems are as- sociated with bulk water penetration and moisture accumulation caused by air leakage. Despite the historic and code emphasis on va- por barriers, their effect is often secondary. A beneficial exercise during building envelope design is to trace the continuity ofthe elements providing thermal, air, and water pro- tection to the envelope as assembly details are refined. Continuity of the WRB and the air barrier is essential to their performance. Abso- lute continuity of a vapor barrier is not essential to its performance. Hygrothermal analysis can be used to predict envelope perfor- mance and compare these results with the requirements. ASHRAE Standard 160 provides guidance for performing a hygrothermal design analysis. Inputs for hygrothermal modeling include assembly Inc. ASHRAE, 2019 user. single for Licensed | {}
d1d811e2-0dfa-431d-b72c-b32be4eef122 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Building Envelopes 45.3 configuration, material properties, initial conditions, and indoor and outdoor climate conditions. Analysis tools generate outputs that may include heat and moisture flux and material moisture content. Because of the number of assumptions and the limitations of calcu- lations required to complete an analysis, results should be considered guidance to supplement the designer's understanding of envelope performance. They should not be considered an absolute prediction of actual hygrothermal performance. Other Important Performance Criteria Strength and Rigidity. The air barrier system must be able to withstand air pressures to which the building will be subjected. These pressures can often be large, and strength is critical in severe- weather areas such as hurricane zones. Noise. For most occupancies, building envelopes should be de- signed and constructed to reduce noise transfer between conditioned and unconditioned spaces. Sound insulation can be particularly im- portant near noisy areas such as airports, railways, and highways, es- pecially for occupancies that require indoor quiet (e.g., hospitals, hotels, residences, theaters). Constructability. During design, how a building envelope will be built must be considered. If there are practical limitations to how the envelope elements are physically put together, the design intent will be lost and problems are likely to develop during construction. Simplicity in design is an effective way to improve the chances of construction in accordance with the design intent. Construction of the various components must be sequenced so that all components can be correctly assembled, particularly when coordination between multiple trades is required. Investigation of many building failures demonstrates that poor sequencing between trades is a common contributing factor. Integrating constructability early in project design minimizes the number of failures and helps maximize the potential to achieve the results described in this chapter. During con- struction review, specific attention should be given to areas of the building where multiple systems are connected and multiple trades are involved. Use of mockups, design reviews, modeling, and other methods can enhance constructability. Maintainability and Repairability. Building envelopes com- prise many parts and components, with different anticipated service lives. Exterior cladding materials and fenestration may need replacement during the expected life of a building. Foundations and framing are the core elements of a building and should last for the entire building service life. Care should be taken not to cover shorter-lived building components with components having a lon- ger anticipated lifespan. Maintenance of the envelope and HVAC system is important to ensure a functional building. A poorly maintained HV AC system can result in substantial energy loss and have a detrimental effect on the building envelope by subjecting it to unexpected pressures and/ or moisture loads. Verification of airflows and pressure differentials has been incorporated into many sustainable design tools as a check to ensure the building mechanical system is functioning as intended long after commissioning. Sustainability. ASHRAE (2006) defines sustainability as "pro- viding for the needs of the present without detracting from the abil- ity to fulfill the needs of the future. " In this chapter, sustainability refers primarily to durability and energy performance. Durability is essential for sustainable buildings, and moisture control is essential to durability. Additional information on sustainability can be found in Chapter 35 of the 2017 ASHRAE Handbook-Fundamentals. With regard to durability, thermal insulation keeps interior and exterior materials near their respective ambient temperatures. In a well-insulated building in a cold climate, the exterior materials are subjected to harsher conditions (lower temperatures, wetter condi- tions, slower drying, and longer periods at subfreezing tempera- tures) than in one poorly insulated. Exterior materials for well- insulated buildings should therefore be sufficiently robust to with- stand the conditions to which they will be exposed. From an energy perspective, completeness of the air and thermal barrier is critical to achieve good performance. For details on sus- tainable energy use in buildings, see ASHRAE Standard 90.1. Quality Control. Ensuring good envelope performance de- mands a well-established quality control program: the design must minimize damage risk while maximizing thermal efficiency (quali- ty assurance). For that purpose, redundancies should be incorporat- ed to allow for imperfections in construction (e.g., providing for drainage or drying to remove moisture from wall cavities). The building should be designed to enable effective maintenance and re- pair over its anticipated service life. Quality control methods such as construction review and the use of site mock-ups can be invaluable tools to increase the likelihood of good construction. The building envelope differs greatly from mechanical and lighting systems in terms of inspections and commissioning. The building envelope is normally inspected during key phases of con- struction to check compliance with the construction documents and design intent, before many of the elements are enclosed within a wall system. Once enclosed, it is often very difficult to return to these areas to make repairs. At these key phases of completion, inspection measures are critical to ensure that any changes in design maintain the intent. Mechanical and lighting systems, on the other hand, are normally commissioned at the end of a project, meaning that their full-service testing for compliance does not occur until the building is operational and occupied. 3. DESIGN PRINCIPLES Air conditioning and humidification can substantially change the moisture loads on the building envelope. New building materials may have significantly different thermal and moisture characteris- tics than traditional materials. The interdependency between the building envelope and the HVAC system has greater consequences to building durability and performance under problematic heat, air, and moisture conditions. Heat Flow Control A building envelope must adequately reduce heat flow to main- tain energy efficiency and ensure indoor thermal comfort. Gener- ally, heat flow control is achieved by installing thermal insulation as part of a wall, floor, or roof assembly. The most common insulation materials used in building enve- lopes are glass fiber, mineral wool, cellulose, foam boards, and spray-applied foams. All these materials have exposure and perfor- mance limitations (e.g., fire, noise, moisture, ultraviolet) and should be selected carefully to promote long-term performance (see Table 1 in Chapter 26 ofthe 2017 ASHRAE Handbook-Fundamentals for common insulation materials and their properties). Depending on the type of envelope assembly, the location of insulation in the wall can have a direct effect on thermal perfor- mance. For example, placing continuous insulation, such as rigid foam or mineral fiber board, outboard of the exterior sheathing on stud walls reduces conductive heat transfer through the studs and improves overall thermal performance. As with all building envelope assemblies, correct installation of insulation is important in maintaining good thermal performance. For example, small voids left in insulation can result in an apprecia- ble increase in heat flow, with the voids having a greater significance in more highly insulated assemblies. Verschoor (1977) found that convective air currents around thin wall insulation installed verti- cally with air spaces on both sides increased heat loss by 60%. Lecompte (1990) found losses up to 300% depending on the size and distribution of openings around insulation materials. Other factors, Inc. ASHRAE, 2019 user. single for Licensed | {}
f69329c7-5b46-4396-8bc2-a3623c16bffe | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 45.4 2019 ASHRAE Handbook-HVAC Applications (SI) including vibration, temperature cycling, and other mechanical forces, can affect thermal performance by causing settling or other dimensional changes. The thermal barrier should be continuous around the building envelope. This means aligning insulation planes in walls with ther- mal breaks in windows or providing continuity of the thermal plane around corners or at wall/roof connections. Thermal Performance Table 1 in Chapter 26 of the 2017 ASHRAE Handbook- -Funda- mentals gives thermal resistances ofbuilding materials. The thermal resistance of building assemblies is usually less than the sum of the material resistances (and may be significantly so). Data for clear- wall areas (summarized by James and Goss [1993]) do not include the effects of intersections with floors, roofs, and partitions, and do not account for thermal bridges at framing and partitions, air leak- age, or convective air loops. To test the validity of applying clear-wall data to the wall system, a series of three-dimensional heat conduction simulations was per- formed on a single-family, detached, one-story house, assuming no air leakage (Kosny and Desjarlais 1994). These simulations showed that, for a conventional wood-frame stud wall system with studs installed on 400 mm centers and no continuous outboard insulation, the average area-weighted whole-wall R-value was 91% of the clear-wall R-value. For a similar wall using 90 mm steel studs, the whole-wall R-value was only 83% of the clear-wall R-value. A sim- ilar two-dimensional analysis of an attached, two-story, steel-stud house by Tuluca et al. (1997) showed the R-value for the wall sys- tem to be 40 to 50% of the clear-wall R-value. Thermal bridging occurred through framing, metal ties, and exposed slab edges. Sim- ply using the published insulation R-values alone as the R-value for the whole wall overestimates the real thermal performance. For con- structions containing steel studs, for example, use either the R-value zone method or the modified zone method to determine real thermal performance that considers framing effects (see Chapter 27 of the 2017 ASHRAE Handbook- -Fundamentals). Thermal Mass Inc. ASHRAE, 2019 user. single for Licensed Thermal mass describes the ability of a material layer to store thermal energy and the ability of an opaque envelope component to dampen and delay transfer of heat. That damping, if combined with moderate glazing, effective solar shading, a correct ventilation strat- egy, and indoor partitioning with high thermal storage, can help moderate indoor temperature fluctuation under outdoor temperature swings (Brandemuehl et al. 1990). Increased thermal mass may also positively affect energy efficiency (Kosny et al. 1998; Newell and Snyder 1990; Wilcox et al. 1985). Finally, increased thermal mass can help to shift demand for heating and cooling to off-peak periods. Thermal mass is effective as a design tool where the outdoor diurnal temperature fluctuates around the indoor comfort range. In areas where this does not occur, thermal mass has little effect. Damping and time delay are defined by the order in which opaque envelope components are arranged. Best results are achieved when the thermal insulation faces outside and layers with large heat capac- ity face the interior, as confirmed by an in-depth study of six wall configurations by Kosny et al. (1998). Damping capability of such walls also increases with thermal resistance (Van Geem 1986). Hourly-based computer simulations using transient energy sim- ulation tools may provide a good estimate of thermal mass effects. Thermal Bridges A thermal bridge is an envelope area with significantly higher rate of heat transfer than the contiguous enclosure. Primary causes for thermal bridging are (1) parts with low thermal resistance perforat- ing layers with high thermal resistance, (2) geometries that create zones where large exterior surfaces connect to much smaller interior surfaces, and (3) chilled or warmed edges at the edge ofinsulation as a result of discontinuities. Thermal bridges increase energy use. They may lead to moisture condensation in and on the envelope, result in possible mold growth, accelerate surface fouling (ghosting), increase crack risk, and create surfaces with non-uniform temperatures that can result in indoor comfort problems. Slab edges, perimeter beams, balconies, and decks protruding from the building envelope are common areas for thermal bridging. The effect of thermal bridges in envelopes can be assessed using the zone method, modified zone method, acceptable sources of test data, or computer simulation tools. Refer to Chapter 27 of the 2017 ASHRAE Handbook-Fundamentals for details. A comparison between the uninsulated slab edge detail of Figure 1A and the insulated version in Figure 1B illustrates the importance of designing to reduce thermal bridging. (See Steven Winter Asso- ciates [1988] for numerical examples summarized in this section.)] Thermal bridges created by webs of concrete masonry units (CMUs) dictate the maximum thermal efficiency a CMU can attain. To reduce this effect, blocks containing two webs, instead of the usual three, have been used, and web cross section has been reduced by up to 40%. However, even such changes in block design have not significantly improved wall R-value. Instead, applying low-density concrete with significantly lower thermal conductivity effectively improved thermal performance of these masonry units (Kosny and Christian 1995a, 1995b). The same strategy can be used for CMUs containing core-insulating inserts or insulation fill. Air inside a masonry cavity often is at or near the outdoor air tem- perature. Figure 1A shows that, without cavity insulation, the con- crete slab edge and steel beam are exposed to that outdoor air temperature. Both of these elements are made of relatively thermally conductive materials, steel being considerably more conductive than concrete. The result is significant heat loss and a low floor surface temperature near the slab edge, which can be a source of occupant dis- comfort and possible condensation if indoor humidity is sufficiently high. Adding insulation on the outside of these elements (Figure 1B) keeps them inside the thermal envelope. It keeps the structural steel warm, and prevents cold-weather condensation that could lead to cor- rosion, damage to the masonry below, and moisture damage to the surrounding finishes that could lead to interior mold growth. Insulation is sometimes specified for the interior surface of the perimeter beam to increase the thermal resistance of this wall seg- ment. Site conditions rarely allow thorough installation, so the top and bottom flange edges remain exposed, creating a strong thermal bypass and marginalizing the insulation , s effectiveness. Moreover, use of a vapor-permeable insulation makes vapor condensation more likely because it decreases the temperature of the beam chord but does not stop water vapor migration. Concrete balcony decks are often formed by slab extensions that pass through the building envelope. As the exposed exterior surface exchanges heat with the outdoors, the result is extra heat loss at the interior floor and low floor temperatures during cold weather. These low temperatures may extend to the top and bottom of close-by inte- rior walls, with condensation each time their surface temperature drops below the dew point of the interior air. The same mechanism can increase energy use during hot weather because building mechanical systems compensate for additional heat gain. Thermal break elements between slab and balcony or a careful addition of insulation panels can moderate the thermal bridge effect. One- or two-dimensional heat transfer models can be used to analyze more complicated assemblies. Air Leakage Control Uncontrolled air leakage in the form of infiltration, exfiltration, intrusion, and wind washing increases space conditioning costs and | {}
657b9846-1ffe-446d-af87-996a399d911f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Building Envelopes 45.5 ![image](/image/placeholder) FURRED-IN INSULATION UNINSULATED FURRING 명 1. 4 FIREPROOFING FIREPROOFING Not Preferred EXTERIOR INSULATION (A) (B) Air barriers, barriers, planes, and omitted for clarity. vapor drainage weeps, flashings Fig. 1 Schematic Detail of (A) Uninsulated and (B) Insulated Slab Edge and Metal Shelf Angle. may cause moisture problems (see Chapter 25 of the 2017 ASHRAE Handbook-Fundamentals). Air leakage is much more effective than diffusion for transporting water vapor in the building envelope and causing interstitial condensation. Forensic field observations support these research results. Uncontrolled air leakage also short-circuits the transient response of envelope assemblies. It degrades sound insulation of the envelope and may cause draft and related thermal discomfort. These drawbacks underline the need to plan for airflow control in building envelope design by installing an air barrier. Most published literature on air barrier requirements stipulates that an air barrier's air leakage permeance should not exceed 0.02 L/ (s·m2) at 75 Pa when tested in accordance with ASTM Standard E2178 (NRCC 2005; U.S. ACE 2009). The air barrier must be sufficiently supported on both sides and be strong enough to resist expected loads from stack effect, mechanical-system-induced pressures, and wind. For example, a sheet-membrane air barrier material installed using staples against a sheathing in a cavity wall is well supported by the sheathing in a positive-pressure direction, but may be subject to tearing at the fas- tener points under negative pressures, which tend to pull the mem- brane away from the wall. The air barrier must be continuous across the entire building envelope. To ensure continuity at windows and other penetrations, components creating the barrier must be connected with an airtight, durable joint. It is particularly important to ensure continuity of air barrier systems at junctions that create complicated geometries where two or more elements in different planes intersect (e.g., roof/ wall intersections, wall/floor intersections, corners). Maintaining continuity at these assemblies can be further complicated because they often involve different construction trades, requiring coordina- tion between workers. Penetrations (e.g., electrical outlets, light fixtures, plumbing stacks) should be minimized and, if unavoidable, sealed carefully. Airtight electrical boxes are available. Maintaining air barrier sys- tem integrity throughout the building': s life should also be consid- ered. Cutting holes in gypsum board assemblies during renovations, for example, can result in widespread air barrier failure if the board is intended to be the primary air barrier in the assembly. The best location for the air barrier is generally where it is easiest to assemble into a continuous and durable system. The location of the air barrier in a wall assembly may affect overall hygrothermal performance. Permeance properties of the barrier material may be important; see the section on Water Vapor Control. Although the intent should be to construct an airtight building envelope, not all cracks and openings can be sealed in existing buildings, nor can an absolutely tight construction be achieved in new buildings. The objective is to provide an enclosure thatis as tight as possible. Calling out a vapor barrier (see the section on W ater Vapor Control) as "continuous" is not a sufficient specification for an air barrier. Moisture Control Building envelopes are subject to several moisture loads (mois- ture entry mechanisms), including liquid water and water vapor from air leakage and/or diffusion. Historically, the primary moisture control strategy for walls was to restrict water entry by collecting and redistributing moisture that enters with air, before evaporation. Today, good envelope design still requires minimizing accumula- tion and maximizing removal of moisture. Although weather-resis- tive components may be designed with the goal of eliminating water infiltration, some redundancy is obtained when assemblies are also designed to accommodate drainage and drying of incidental mois- ture intrusion. Hygrothermal modeling tools, as described in Chap- ters 25 and 27 of the 2017 ASHRAE Handbook-Fundamentals, can assist designers in understanding the drying potential of assemblies based on the assumed loads; however, current models cannot effec- tively predict drainage. Liquid Water Control Field observations indicate that moisture problems in buildings are most frequently caused by exterior liquid water penetrating or passing through the building envelope. Rain is the most significant moisture source for buildings. Strat- egies to reduce the rain load on exterior walls include using building overhangs to prevent wetting, flashings, drip edges, and other water- shedding elements. During rain, poor flashing details at the interface Inc. ASHRAE, 2019 user. single for Licensed | {}
f9e7b617-0680-4e62-80df-4dec656997f1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 45.6 Inc. ASHRAE, 2019 user. single for Licensed 2019 ASHRAE Handbook-HVAC Applications (SI) of dissimilar materials, incomplete terminations of cladding sys- tems, and other discontinuities in the moisture barrier may result in water entry, which can cause severe damage and loss of durability. For roofs and walls, cladding and building envelope components must be integrated to prevent water infiltration. At grade, rainwater should be carried away from the foundation through gutters, down- spouts, and positive grading (i.e., sloping the surrounding grade to direct water away from the building). An important consideration when designing an envelope for liq- uid water control is sequencing during construction and coordina- tion between trades. Proper sequencing is essential to ensure that systems are correctly connected. Building envelope failure investi- gations often reveal that water penetration problems result from poorly constructed connections between various elements, often caused by inadequate site coordination. Important connection de- tails should be included in the construction documents with enough clarity to allow suitable construction. Lack of detail on drawings and in specifications can result in too many construction decisions being made on site. One method of minimizing moisture entry through the building envelope is to use face sealing (i.e., sealing the outer face of the wall/window junction, interfaces with dissimilar materials, and at building expansion joints). The sealed exterior surface protects against rain and air infiltration and must remain continuous over time to maintain functionality. One example of this type of system is the use of water-resistive coatings over masonry and concrete walls. Great care must be taken when using these coatings to ensure that, when moisture gets into these materials through cracks in the coatings or by other pathways, there is opportunity for it to dry. By nature, face-sealed systems have little or no redundancy to prevent water ingress and accumulation, and they require rigorous mainte- nance schedules for long-term performance. Rain screen design has greater redundancy than face-sealed systems. Rain screen design minimizes penetration by raindrop momentum, capillarity, gravity, and air pressure differences. A rain screen wall contains several components from inside to outside: an air barrier, a WRB (which may perform as air, moisture, and vapor barrier), the air space, and a rain screen. The air space may be an empty air cavity or a cavity filled with a material that drains freely. The air space must be vented to the outdoors through the rain screen and flashed to drain water that penetrates the rain screen. The rain screen 's airflow resistance must be much lower than that of the air barrier, so that it acts as a deterrent for water penetration but is not a watertight seal. It is prudent to protect the WRB and air barrier from temperature extremes and direct exposure to ultravio- let light. With little pressure difference across the rain screen and with good cavity drainage detailing of the cavity, the potential for rain entry into the wall is significantly reduced. Interfaces of the exterior wall air barrier with fenestration air barriers, floors, and interior partition walls must be carefully considered, and may require site mock-ups to adequately determine the best solution. For greater liquid water control, the air cavity may be designed as a pressure-moderation chamber, which involves making the WRB airtight. The cavity should also be compartmented to avoid lateral airflow, especially around corners of the building. Water v apor Control Water vapor entry into the building envelope can be limited by airflow control and water vapor barriers. As described previously, air barriers are intended to restrict air leakage and control convective water vapor ingress, whereas vapor barriers are designed to restrict vapor flow caused by diffusion. It is important for building design- ers to understand the difference between the two mechanisms and how they are controlled. Moisture deposition caused by air leakage is a point-load prob- lem: a large volume of water can be deposited in a discrete location, often near the air leakage point, and can result in substantial dam- age. For that reason, an air barrier has to be continuous and sealed. This differs from moisture deposition cause by vapor diffusion, which is an area function that is directly related to the vapor drive and the vapor permeability of the materials that separate the two zones. A vapor barrier should therefore be continuous, but does not necessarily have to be sealed. The only time a vapor barrier is required to be sealed is when it also functions as the air barrier. w ater v apor Transport Through Air Movement. Air leakage is more effective than diffusion for transporting water vapor in the building envelope, and therefore it is more important to control. To minimize water vapor ingress, the building envelope should be as airtight as possible using the principles described here. Moisture accumulation in the building envelope can also be minimized by controlling the dominant direction of airflow by operating the build- ing at a small negative or positive pressure, depending on climate. In cooling climates, the pressure should be positive to keep out humid outdoor air. In heating climates, the building pressure should remain neutral, or slightly negative or positive relative to the outdoors. Strong negative pressure could risk drawing soil gas or combustion products indoors. Strong positive pressure could risk driving mois- ture into the envelope. In wall systems where the air barrier system also functions as the vapor barrier, it is important to consider its location relative to the expected vapor drive and temperature gradient across the wall. To avoid condensation on the air and vapor barrier, either its surface temperature must be kept above the dew point of the surrounding air by locating it on the warm side of the insulation, or the permeance of the assembly must allow vapor transmission if located at the cold side of the insulation. In the latter case, the air barrier no longer functions as a vapor barrier. w ater Vapor Transport Through Diffusion. Moisture migra- tion by diffusion through materials is a slow process and, as dis- cussed previously, is less likely to contribute to moisture problems in buildings compared to liquid water intrusion or air leakage. How- ever, diffusion can cause moisture problems in special occupancy types or in buildings that experience high moisture loads. The overall diffusion performance of a building is a product of the diffusion characteristics of the envelope materials. A vapor bar- rier is not necessarily a sheet of plastic; many different materials or combination of materials can be used to control vapor diffusion, depending on design conditions. Many building envelope compo- nents, such as some peel-and-stick membranes, metal panels, and glass, have very low vapor permeance. Design and selection of building materials should be based on analysis to verify the desired performance of the assembly under the applicable loads. Many common building and finish materials with low vapor per- meance can have undesirable effects when placed in high-moisture- risk environments. One example is vinyl wallpaper placed at the interior wall surfaces. Under large inward vapor drives or excessive water penetration, this vapor-impermeable layer can lead to moisture accumulation through condensation, or can prevent drying by limiting vapor flows, both of which can lead to significant moisture damage. Careful attention must be paid to the type of materials selected for a wall construction, and where they are located in the wall assembly. Use of vapor-impermeable layers at both the interior and exterior should generally be avoided so that the assembly can dry. Heat, air, and moisture calculations and modeling can be used to analyze an assembly, its climatic exposure, and desired indoor operating con- ditions to determine what methods of vapor control are appropriate. For details, see Chapters 25 to 27 ofthe 2017 ASHRAE Handbook Fundamentals. Common Envelope Problems w all/Window Interface. Air infiltration at the wall/window interface can reduce window performance and damage surrounding | {}
3c66abf3-1418-4df3-b866-2ed678faef05 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Building Envelopes 45.7 building materials and even remote materials, depending on the leakage path. In cold climates, warm, humid indoor air can increase moisture content in the wall cavity around the window. Excess moisture may damage the interior finish, seals of glazing units, insu- lation, exterior cladding, and possibly structural elements. Uncon- trolled cold-air infiltration through the interface in turn can affect occupants' health and comfort by creating a dry indoor environ- ment, cold drafts, and surface condensation on the window frame and glass edges. In warm, humid climates, leakage at the wall/ window interface can result in interior fungal growth, distortion of interior window trim, and deterioration of the interior gypsum wall- board, particularly in air-conditioned buildings (because their inte- rior surfaces are colder). Control of air and water leakage at the wall/window interface is often difficult because that is where multiple systems intersect. Each system may incorporate a different approach for air and water control and must be integrated to provide continuity. Additionally, the different systems are commonly installed by different trades, which require deliberate sequencing to achieve the intended result. These intersections are often complex, making it difficult to inspect and test for performance compliance. Water penetration can result in moisture damage in any climate, although it is generally most severe in climates that impose a low drying potential on a building. Control of Surface Condensation To reduce the potential for condensation on the interior surface of glazing and the window frame, as well as on the surrounding interior wall finishes, the indoor surface temperature can be controlled in the following ways: · Select windows with appropriate condensation resistance for new construction or retrofit. · Seal the wall/window interface and between the sash and frame of operable windows to minimize air leakage. · Make the area of window frame exposed to the interior larger than the area exposed to the outdoors. Window and curtain wall sys- tems with metal frame extensions on the inside have a higher resistance to condensation but contribute to heat loss. · Reduce excessive interior humidity levels. · Keep thermal breaks in the window system in the same plane as the wall insulation. Continuity of the plane of thermal insulation between wall and window maximizes a window's thermal potential and reduces the potential for condensation on interior surfaces of the window frame, glass, and surrounding finish. Insulation in the joint between wall and window frame also compensates for the expected differential movement between the frame and the wall rough opening. Interzonal Environmental Loads Indoor partition walls separating zones such as indoor swimming pools, ice rinks, and freezers from zones conditioned as normal environments should be treated as envelope assemblies. Apart from weather-related loads, these partition walls must perform as build- ing envelopes and need to control airflow, heat flow, liquid water (e.g., swimming pools, industrial settings), and water vapor flow. Interstitial Spaces Building envelope design must consider that modern buildings comprise a collection of interconnected internal chambers and cavi- ties that provide potential pathways for unplanned airflows through- out the building. Concrete masonry cavity walls, wood- and steel- stud gypsum board partitions, chases, soffits, shafts, utility service penetrations, and many other details contain cavities that connect adjacent elements to varying degrees wherever holes and openings have not been closed and sealed. The amount of air leakage depends on pressure differences, number and size of openings, and length and tortuosity ofpaths. Pressure differences generally derive from HVAC operation, differences in air density, and wind. These unplanned airflows often have no obvious adverse effects on occupants or the building, but in many cases they can significantly negatively affect energy demand, moisture deposition, and indoor air quality. Uncon- trolled air leakage paths also add to the risk of undesirable sound transmission between rooms. A full discussion of all possible sources of unplanned airflows is beyond the scope of this chapter; see the References and Bibliography for additional information sources. A common practice in commercial buildings is to use the space above a dropped ceiling as the HV AC system 's return air plenum (Figure 2). The complex three-dimensional assemblies where the exterior wall adjoins a roof or floor at the building perimeter can be difficult to seal against air leakage and thermal bridging if the unique conditions of each design situation are not deliberately addressed. The interior gypsum board in the occupied space often terminates above the visual sight line of the suspended ceiling without extend- ing to the roof or floor deck above. Unless carefully detailed and con- structed, this can result in a leakage point at the building perimeter where negative pressure in the plenum can draw outdoor air into the return air system. If it is cold outdoors, an accidental sensible load penalty is imposed. For hot and humid climates, accidental latent and sensible loads are added that not only affect the energy required to condition the building, but also may lead to moisture and indoor air quality problems from condensation on interior surfaces that are cooler than the dew-point temperature of the incoming outdoor air. Sustained elevated relative humidity in the ceiling space can perpet- uate mold growth. In general, but especially for demanding applica- tions such as health-care and laboratory buildings, ducted returns should be used rather than depressurizing the entire ceiling plenum. Air pressure between the ceiling plenum and the occupied space can ![image](/image/placeholder) BRICK VENEER BUILDING PAPER TOP CHORD BEARING TRUSS INTERIOR GYPSUM SHOULD EXTEND I TO UNDERSIDE OF FLOOR DECK AND BE SEALED RETURN PLENUM OPERATES UNDER NEGATIVE PRESSURE RELATIVE TO OCCUPIED SPACE AND EXTERIOR EXTERIOR SHEATHING METAL STUD SUSPENDED CEILING WALL CAVITY INTERIOR GYPSUM INSULATION Negative-pressure field in the dropped-ceiling return plenum extends to exterior, accidentally coupling the HVAC system to the building enclosure. Fig. 2 Dropped-Ceiling Return Plenum Lstiburek 2007 Inc. ASHRAE, 2019 user. single for Licensed | {}
8c534317-b322-40d7-a178-3f9ae43a79bc | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 45.8 be equalized by installing ceiling grates in the suspended ceiling. Other configurations that may be more appropriate to the specific building design conditions can also be effective. Similar considerations regarding energy loss and moisture depo- sition also apply to underfloor air supply systems that can force con- ditioned air out through the building envelope. 4. QUICK DESIGN GUIDE FOR HIGH- PERFORMANCE BUILDING ENVELOPES 1. Avoid excessive glazing. Follow energy standard and energy code requirements that set maximum glazed areas. Refer to the current version of ASHRAE Standard 90.1 for maximum roof and wall glazing areas. 2. Provide appropriate amounts of thermal insulation in foundation and above-grade walls and roofs. See current versions of ASH- RAE Standards 90. 1 and 90.2. 3. The completed building envelope should be airtight. Determine the level of airtightness to be achieved. Design airtight connec- tions at all junctures in the air barrier system. Construction sequence should allow visual review and ensure performance with the selected criterion. 4. Resolve vapor barrier and vapor control issues using simplified or full hygrothermal analysis (ASHRAE Standard 160). The necessity and requirements for vapor control are specific to building usage, materials, and climate, and should be included in the design process. 5. Provide for effective shedding of rainwater away from the exte- rior wall. Rain screen principles to drain water away from the building should be used where possible. 6. Provide sound insulation appropriate for the building applica- tion. Some specialized facilities such as hospitals, libraries, and theaters require additional care to control sound transmission. 7. Refer to the ASHRAE Advanced Energy Design Guide series for additional information on building design. 5. ROOFS Low-Slope Roof Assemblies Low-slope roofs are typically compact insulated assemblies of a waterproofing membrane together with structural and insulating board material. Insulation is usually rigid board or foam products. The insulation may be below the roofing product(s), or above for an inverted roof membrane assembly (IRMA). If below, it is usually installed in two or more layers with staggered joints to prevent air- flow at the panel joint. Tobiasson (2010) showed that venting low- slope roof systems between the insulation and the membrane is not effective for moisture control. All roofing systems must be designed and constructed to resist wind uplift. Common methods of securing the roofing system to the decking are mechanically fastened, fully adhered, and bal- lasted. Light-colored roofing products, including ballasted roofs, reduce cooling loads (if kept clean), and help moderate the heat island effects in cities. Proper flashing details are important at drains, scuppers, equipment supports, control joints, and other pen- etrations. For low-slope roofing design and practice, see the National Roofing Contractors Association 's (NRCA) Roofing Manual series. Parapets and overhangs should be detailed for continuity of the thermal insulation and air barrier. Wall insulation should meet the roof insulation, so there is no thermal bridge. Roof and wall air barriers must be continuous. These two continuity requirements may require the parapet or overhang to be specified to be installed after the continuity of the insulation and air barrier is ensured. Some parapet details, such as upper termination of interior drywall, flutes in steel decks, three-dimensional conditions, and 2019 ASHRAE Handbook-HVAC Applications (SI) fireproofing sequence for steel, are often overlooked. The roof/ wall junction requires coordination and proper sequencing be- tween trades to ensure proper continuity of the air and thermal control layers. Steep-Roof Assemblies There are two main insulation locations in steep-roof assemblies: at the roof (cathedral) and in the ceiling. For both types, exterior sheathing and roof materials should be able to accommodate wide temperature swings caused by radiant exchange with the sun and sky. Insulated Sloped-Roof (ISR) Assembly. An insulated sloped roof assembly (e.g., cathedral ceiling) is a compact system with insulation parallel to the roof and no air cavity. Principles used in the design and construction of low-slope roofs may be applied in steep- sloped roof construction. According to Hens and Janssens (1999), moisture control is ensured only if airtightness is effective and can be maintained. Air entry and wind washing in insulated cathedral ceilings lead to degraded thermal and moisture (durability) perfor- mance. Ten Wolde and Carll (1992) showed that ventilation of ISR assemblies may increase air leakage, and that the net moisture effect depends on whether the principal source of makeup air is from indoors or outdoors. Use of vapor-permeable versus low-permeance thermal insulation in ISR assemblies can be an important factor in assembly design and performance. Their selection depends on the expected direction of vapor flow within the roofing system, drying potential, and other design considerations. Attics. Standard North American attic construction provides for insulation at the ceiling plane level, leaving the attic space as uncon- ditioned. The ceiling should be made airtight (Jordan et al. 1948). Air exchange with the outdoors provided by vents typically reduces attic air temperature on sunny afternoons. Other effects of ventila- tion, such as wood moisture content and roof surface temperature attenuation, depend more on factors other than the presence or absence of ventilation. Ten Wolde and Rose (1999) critically review four commonly cited reasons for attic ventilation: (1) preventing moisture damage, (2) enhancing the service life of temperature-sen- sitive roofing materials, (3) preventing ice dams, and (4) reducing cooling load. The following additional design and construction elements should be considered for attics and insulated sloped-roof construc- tion: · Valleys are areas of high water concentration and are common sites of leaks. They should be designed to channel high volumes of water and for ease of repair. · Mechanical equipment and ductwork should be placed in condi- tioned spaces. Their placement in unconditioned spaces leads to excess heat loss, energy consumption, and potential condensation on cold ductwork surfaces. · Ice dams are typically caused by snow melting on the roof. Heat sources in the attic that could cause ice dams (e.g., chimneys, air leakage through the ceiling, attic-mounted equipment) should be identified and addressed. v egetated Roofing There has been significant interest in vegetated roofing in recent years in an attempt to save energy or to control building rainwater outflow. On vegetated roofs, both growth medium and vegetation are installed on top of the roof. These assemblies normally require additional precautions and materials to protect the roof membrane from the plants. Quality control is even more critical during instal- lation of a vegetated roof, because repair and eventual replacement are normally considerably more expensive and resource-intensive because of the presence of growing medium. Inc. ASHRAE, 2019 user. single for Licensed | {}
bbfbdb02-7c70-4ff0-b73b-8b0faee4c5a5 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Building Envelopes 45.9 Storing rainwater on the roof can reduce the load on a munici- pality's storm system. There are many methods and products to achieve this. Storage of water and placement of a growing medium can add a considerable amount of mass to a roofing system. Checks to ensure structural capacity are essential for existing buildings, and new buildings must include structural provisions to support the additional weight. Some structural designers include provisions for the weight of a possible future vegetated roofing system because the incremental costs to do so are very small. Vegetated roofing is often referred to as green roofing. Green roofing also refers to roofing systems that have other sustainability attributes such as high albedo. 6. w ALLS Curtain Walls There has been tremendous growth in the use of curtain-wall sys- tems for new building construction in recent years. A modern curtain- wall system is a highly engineered product based on mass production, standardization, and precise manufacturing (CMHC 2004). The sys- tems generally consist oflightweight metal framing components con- nected to form a matrix to contain transparent and opaque wall areas. The framing is typically anchored to the building structural columns or floor slabs. Window wall systems are types of curtain walls that are typically installed floor to floor. Many older systems left slab edges exposed. New window wall systems often include drop-down panels that cover and provide thermal protection to the slab edge. There are two basic kinds of systems: stick built, which are assembled on site from horizontal (rails) and vertical members (mullions), and unitized systems, which are largely assembled in a shop and delivered in sections that are then connected to form the wall. Both types are generally field glazed. Custom systems are also available for specialized applications. Glazing and opaque elements of the curtain-wall frame are fastened using exterior battens (pres- sure plates), structural sealant, or both. Detailed information on the various types of curtain wall systems and glazing methods can be found in Canada Mortgage and Housing Corporation , s Best Practice Guide-Glass and Metal Curtain Walls (CMHC 2004), or the National Institute of Building Sciences' Whole Building Design Guide (NIBS 2010). Curtain-wall assemblies form the entire exterior wall where in- stalled. They need to perform all the functions of a building enve- lope, though they have some significant differences from other walls. Curtain-wall assemblies are made of materials that have no moisture storage capabilities, whereas most other wall types (ma- sonry, concrete, etc.) can store and release moisture over time. They nevertheless can retain significant volumes of water that may lead to penetration if watertightness and drainage are not provided. There are two common methods for a curtain-wall system to man- age exterior moisture: face-sealed and rain-screen design. Face- sealed systems are more susceptible to water penetration because they have no redundancy. Once water penetrates the exterior mois- ture barrier, there is no way for it to drain back to the exterior. Rain screen designs provide redundancy by draining moisture that bypasses the primary outer seal to the outdoors. This provides more protection from rain penetration than face-sealed systems. Because curtain-wall systems are highly engineered and assem- bled out of precisely manufactured components, it is essential that they are assembled in accordance with manufacturers' specifica- tions, with all recommended accessories installed. Omission of any components, such as corner blocks or other drainage elements, can result in reduced drainage capacity, water storage, and eventual pen- etration to the interior. Curtain-wall systems can be used to cover floor slab edges to re- duce thermal bridging. They bring in lots of natural light and can provide great occupant views. However, heavy use of glass often results in poorer thermal performance than for traditional wall as- semblies, or even spandrel sections in a curtain-wall system. The large glazing areas in curtain walls should be considered in terms of solar gain and sizing of mechanical equipment. In cold climates, the large areas of glass and framing can have a radiative cooling effect on a space, and adversely affect thermal comfort. Conversely, in hot climates, large areas of glass can result in heat gains that can over- whelm cooling equipment, or necessitate cooling equipment in ar- eas where mechanical cooling is not typically required. Often, thermal performance of curtain-wall systems is overstated by re- porting center-of-glass or center-of-spandrel-panel thermal perfor- mance values, rather than the overall thermal performance (U-value) of the assembly. Whereas traditional wall assemblies are often built by a number of trades, curtain-wall systems are often constructed by one installer. Connecting the curtain-wall system to surrounding systems, such as roof assemblies or wall, requires coordination of trades. Common problems found in the field include · Improper or poor connection of curtain wall to roofing system · Missing corner blocks or drainage elements, resulting in reduced moisture performance · Missing or blocked vertical drainage channels, resulting in stored water at the glazing head Sloped glazing is similar to curtain-wall systems, although the importance of using a rain-screen design to prevent water penetra- tion to a building interior is enhanced. Properly flashed head joints and detailed drainage at the base of the sloped glazing are essential for long-term performance. Precast Concrete Panels Insulated precast wall (sandwich) panels are often constructed with solid concrete at the perimeter that encloses the insulation (Fig- ure 3A). This concrete has a much greater thermal conductivity than the insulation, resulting in appreciable heat loss through these areas, particularly when added up across an entire building envelope. By changing how panels are assembled (e.g., connecting inner and outer panel sections with plastic tie-rods), a much greater thermal performance is achieved and the excessive perimeter heat loss is ![image](/image/placeholder) Not Dre · CONTINUOUS ■ TOP CASING 4 . · · + RIGID INSULATION -- 」 L RIGID INSULATION , . · CONTINUOUS BOTTOM CASING · METAL OR 1 PLASTIC TIES (A) (B) Fig. 3 Sandwich Panel with Insulation Encased in Concrete Inc. ASHRAE, 2019 user. single for Licensed | {}
a9e4d9df-1cf4-4a03-9f90-e7959505dbdb | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 45.10 2019 ASHRAE Handbook-HVAC Applications (SI) ![image](/image/placeholder) BRICK VENEER Not CONCRETE MASONRY Prefe rred FURRED-IN INSULATION EXTERIOR UNINSULATED INSULATION FURRING (A) (B) Fig. 4 Details of Insulation Around Column in Masonry Wall eliminated (Figure 3B). These types of panels are more susceptible to water penetration, however, so proper panel joint design and exe- cution are even more critical with these types of panels. Precast concrete wall assemblies should be connected using two- stage jointing system. Two-stage joints consist of an inner and outer sealant joint. The exterior joint forms an outdoor weather barrier that keeps most exterior moisture from entering the joint. The inner joint is normally sloped at the bottom of each panel joint to drain water that bypasses the outer joint back to the outdoors, and forms part of the wall' s air-barrier assembly. For more information on pre- cast panel joinery, see CMHC (2002). Steel-Stud Wall Assemblies Steel-stud wall assemblies are commonly used in multifamily, commercial, and industrial construction. These wall assemblies rep- resent a particular challenge because of the studs' high thermal con- ductivity. Adding thermal breaks can prevent excessive heat loss and problems associated with condensation in the wall assembly and on interior finishes. Adding insulated sheathing or insulation outboard of the steel studs significantly reduces heat loss and helps avoid cold surfaces at the interior and in the wall cavity; however, system limitations and manufacturer's instructions should be considered. Wall Geometry with High Thermal Conductivity Inc. ASHRAE, 2019 user. single for Licensed Concrete columns in masonry walls are often left uninsulated. Figure 4 illustrates a wall system with a column at the junction of two exterior brick walls with CMU back-up. The assembly in Fig- ure 4A represents a significant thermal bridge. In Figure 4B, the walls are insulated with polystyrene on metal furring. The amount ofheat flow is greatly reduced in this assembly, and no condensation or subsequent mold growth would be expected on interior surfaces of the column under normal operating conditions. 7. FENESTRA TION Conduction/Convection and Radiation Effects Heat transfer through a window resulting from a temperature dif- ferential between the indoors and outdoors (i.e., conduction, con- vection, and radiation) is a complex and interactive phenomenon. Although glass itself is a poor insulator, technologies can be com- bined to improve a glazing system 's overall thermal performance. Glass also decreases direct transmission of radiant energy from the room or ambient sources. Chapter 15 of the 2017 ASHRAE Hand- book-Fundamentals discusses fenestration in much greater detail. Examination of the modes of heat transfer in a double-glazed window indicates that approximately 70% of the heat flow is through radiation from one glazing layer to the other (Arasteh et al. 1985; Selkowitz 1979). Although glass is largely opaque to infrared radiation, energy is still absorbed and reemitted. Low-emittance coatings that are transparent to the eye significantly reduce the amount of radiant heat transfer through a glazing cavity. With that mode ofheat transfer minimized, conductive and convective modes dominate. To reduce these effects, inert gases with low conductivity (e.g., argon, krypton) are used in low-emittance-coated, double- glazed windows. Inert-gas-filled triple or quadruple glazing layers with low-emittance coatings can additionally reduce heat transfer, although overall thermal performance normally remains signifi- cantly less than a common insulated wall assembly. See Chapter 15 of the 2017 ASHRAE Handbook-Fundamentals for design infor- mation. Air Infiltration Effects Air infiltration at fenestration is influenced by the pressure dif- ference between the indoor and outdoor environments (a function of wind speed, indoor/outdoor temperature differences, and mechani- cal air balance) as well as window-sealing characteristics (Klems 1983; Weidt and Weidt 1980). The infiltration rate of a fenestration product is a function of its method of operating (if any), weather- stripping material used, and construction quality. See Chapter 16 of the 2017 ASHRAE Handbook-Fundamentals for design informa- tion. Solar Gain Solar gain through windows can play a significant role in a build- ing's energy balance. Glazings transmit, reflect, or absorb a given wavelength of solar radiation, depending on glazing characteristics. Transmitted solar radiation contributes heat to a space. Absorbed so- lar radiation is reemitted and/or conducted either to the indoors or outdoors (depending on the glazing system configuration). Solar ra- diation that is reflected away from a building through the use of re- flective glass does not contribute heat to a space (Arasteh et al. 1989), but the designer should be aware of the potential for secondary solar gains reflected from an adjacent structure. Clear glass, the most com- mon glazing material, transmits fairly evenly across the solar spec- trum. Tinted or heat-absorbing glass absorbs solar radiation and gives the glass a specific color. Some tints exhibit a significant degree of spectral sensitivity (i.e., they do not transmit, absorb, and reflect evenly across the solar spectrum). These types of glazing elements offer great flexibility and can be tailored for specific climates or uses (e.g., provide ample daylighting without overheating an interior space). Interactions Between Thermal Loss and Solar Gain In heating-dominated applications, solar gain provides a signifi- cant amount of heat. In some cases, heat supplied by the window can offset that lost through the window. The amount depends on char- acteristics of the site (e.g., how much solar gain is available, how cold the climate is) and the window (e.g., its U-factor and how much incident solar radiation is transmitted). Typical passive solar applications try to maximize the amount of solar heat gain by installing significant areas of southeast- to south- west-facing glass, which receives the most solar radiation during the winter in the northern hemisphere. However, high-performance windows facing north in a heating-dominated but sunny climate can provide more solar gain to a space than heat loss (Arasteh et al. 1989; Dubrous and Wilson 1992; Sullivan et al. 1992). Control of Rain Entry Applying the rain screen principle at the wall/window interface requires the same features as applying it to the wall, including (1) an airflow retarder at the interior, (2) a rain deflector on the outside of the interface, and (3) a drainage path to the outdoors. The line of airtightness is on the inside of the assembly, so it is protected from water, ultraviolet rays, and extremes of temperature. The rain deflector on the outside acts as a rain deterrent only, not | {}
07ba1f52-f58f-4ed8-a7b1-cc301236f690 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Building Envelopes 45.11 as a watertight/airtight seal. A nonairtight rain deflector does not threaten system weathertightness, because pressure differences across the rain deflector are small. The key is to maintain airtight- ness on the inside of the joint. With little pressure difference across the rain deflector and with good detailing for outward drainage of the cavity, rain entry in the wall should be minimal. The interface between an exterior wall air barrier and an interior fenestration air barrier must be carefully considered during the design phase, and may require site mock-ups to adequately determine the best solu- tion. 8. FOUNDATIONS Three common types of below- and at-grade constructions are basements, crawlspaces, and slabs. Many buildings have combina- tions of these types. Key concerns for these assemblies are heat trans- fer and moisture management. Heat Transfer Heat transfer in below- and at-grade constructions is complex. Factors affecting it include thermal conductivity and wetness of the soil, height and temperature of the water table, amount and profile of insulation, and geometry. For a simplified means of estimating heat transfer in these constructions, see Chapter 18 of the 2017 ASHRAE Handbook-Fundamentals. Measured heat transfer through slabs on grade with 10 different insulation profiles can be found in Bareither et al. 1948. Kusuda and Bean (1987) and Mitalas (1983) provide slab shape factors for steady-state calculations ofheat loss. Transient calculations are pro- vided in Hagentoft (1988) and Shipp (1982). An overview is pro- vided in Labs et al. (1988). The following general principles may be applied: · Heat loss through slabs is concentrated at the slab edge. Insulation is more critical there than in the center of the slab. · For sections of basements or crawlspaces that are above grade or shallow below grade, insulation on the outside is more effective than insulation at the interior. For deeper parts of a basement, inte- rior insulation is more effective because of the thermal bridge effect of the footing, which is typically uninsulated. · In crawlspaces and basements, insulation may be applied in the foundation walls or in the floor system above. If insulation is applied in the floor system, the space below may be cold and wet. Some form of moisture protection on the underside of an insu- lated floor system may be necessary. Moisture Below- and at-grade constructions are affected by rainwater sur- rounding the building and by the below-grade water table. For all construction types, ensure that the soil or other finish outside the building is sloped away from the building. Discharge from scup- pers, gutters, and downspouts should be conducted far enough from the building that discharge water cannot saturate soil that is in con- tact with the below- or at-grade assembly (Rose 2010). Foundation depth should correspond to the hydrologic condi- tions of the building site, so that the underground water table is not allowed to encroach on the below-grade space. If it does, then a sump pump must be used to locally lower the water table. Basements and crawlspaces may encounter some flooding in the course of their service lives. Consequently, basement finishes should be selected so that they can withstand water loading and are readily cleaned afterwards. Crawlspaces have been known to be sources of moisture to the building since their introduction in the mid-1900s. Britton (1947) found that the use of low-vapor-permeance ground covers with ven- tilation resulted in drier conditions. This recommendation for ven- tilation was picked up by many codes and guidelines. Venting crawlspaces, however, creates an unconditioned space beneath the building, which may lead to energy penalties and high relative humid- ity during warm weather. It is therefore recommended that crawl- spaces should be treated like basements with insulated perimeter walls, insulated bottom floors, and protection from moisture ingress. The crawlspace should be accessible, well illuminated, and clean. In cold climates, building foundations should resist frost heave. This is commonly done by ensuring footings are below frost depth. The frost-protected shallow foundation uses below-grade insula- tion outboard of the foundation to ensure nonfreezing conditions at the slab edge. Attachment frost heaving may occur (Labs et al. 1988); it is prevented by avoiding puddles of water in contact with the foundation during freezing weather by draining water away from the building, as described previously. 9. EXISTING AND HISTORIC BUILDINGS In recent years, there has been a noticeable shift in emphasis from new construction to work on existing buildings. There can be tremendous advantages in materials use, embodied energy, carbon dioxide emissions, and other environmental issues to renovating existing buildings rather than replacing them with new structures, or adding new structures. In the United States, work on buildings of historic significance is addressed by the Secretary of the Interior' s Standards for the Treatment of Historic Properties (1977). For more information, see Park (2009). Determining what materials were used in the original construc- tion and their actual properties can be a challenge. Many materials are hidden within the structure and require some disassembly to determine underlying structure and components. Necessary investi- gative work may range from review of accurate as-built drawings, to field testing, disassembly, and historical research. Depending on the age of the building, multiple renovations may have created many different assemblies in the building, so a review of available plans and permits issued for the building helps avoid unknown conditions during construction. Properties of older materials can be markedly different from their modern equivalents, so research may be neces- sary: in some cases, actual testing of the materials may be the only way to discover how the materials will react. Chemical compatibil- ity between reused and newer materials may be a concern. For instance, new materials for roofing, waterproofing, and sealant or barrier systems may not be compatible with materials used in the past. A review of changes such as HVAC upgrades or building enve- lope improvements should be incorporated into the design. Some sustainable practices are rapidly evolving, and applicable codes and guidelines are still developing. As a result, there can be challenges to following the letter of the code on renovation projects without fully understanding the physical phenomena behind envelope perfor- mance and interactions with HVAC system effects. This can result in problems ranging from water leakage to advanced degradation of wall components. Sometimes, novel approaches must be sought that allow compliance with the intent of the code while optimizing the durability and performance of existing materials/assemblies. Existing buildings provide the benefit of having a performance history. This can be helpful in understanding the reality of energy consumption as well as moisture storage, air leakage, and water vapor movement through materials and assemblies. The building his- tory can be used to identify defects or weak points in the assembly or interactions between the HVAC system and envelope. The building operates in an equilibrium that depends on indoor and outdoor con- ditions and building material properties. Changes to operating con- ditions or materials can affect everything and alter this equilibrium. An additional concern for existing buildings involves a common practice of owners: some large-scale renovation projects are phased over a period of time. If an overall plan is not developed that Inc. ASHRAE, 2019 user. single for Licensed | {}
a084d648-0240-4e9f-a457-772424ea8d26 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 45.12 2019 ASHRAE Handbook-HVAC Applications (SI) includes understanding ofthe interdependence between the building envelope and HVAC systems, then problems and/or extra expense are very likely to occur over the multiple years that it takes to com- plete the entire renovation plan. The order in which changes are done (e.g., envelope first versus HVAC system first) could also greatly affect overall costs as well as the end result. For example, in hot, humid climates, if the HVAC system is replaced before an envelope-tightening project, extra capacity may have to be installed to meet the interim needs. This extra capacity could cause problems with overcooling and high relative humidity after the envelope tight- ening occurs. Successful renovation projects begin with documenting existing conditions and careful analysis of the effects of potential changes. New materials and systems are selected based on compatibility with existing materials and systems as well as durability and long-term performance characteristics. Building Materials Specific issues to be considered for material changes and selec- tions include addition of new materials, removal of old materials, and replacement of existing materials with a modern equivalent; a full understanding of the purpose of specific layers and materials in the original design is also required. An example involves the use of stone or brick masonry. In older buildings, solid stone or brick masonry walls were designed to perform as barrier systems by absorbing and gradually releasing moisture. These materials relied on heat flow to keep them dry and prevent freeze/thaw damage in cold climates. Reuse of wall systems during energy retrofits poses particular challenges in cold climates. Adding exterior insulation has the ben- efit of providing continuous insulation and moisture control while insulating structural elements from thermal and moisture extremes, but it may conflict with preservation aesthetics as well as zoning requirements. Adding interior insulation increases thermal stresses while reducing the drying potential of the exterior facade, and may lead to increased freeze/thaw cycling in cold climates. It is also dif- ficult to achieve continuous thermal insulation and air barrier around existing interior wall elements. Unavoidable discontinuities create thermal bridges that could become condensation sites. Floors supported by exterior masonry are one example. See Chapter 27 of the 2017 ASHRAE Handbook-Fundamentals for examples of cal- culating thermal resistance values for complex wall assemblies. Hygrothermal analysis and understanding of the potential conse- quences of measures planned on the durability of facades and struc- tural elements must be part of the renovation design process, because this may impose limits on the insulation strategy. Guidance for performing hygrothermal analysis can be found in ASHRAE Standard 160. Inc. ASHRAE, 2019 user. single for Licensed Changing HVAC Equipment and/or Control Strategy When upgrading or replacing existing mechanical systems, the effect of the new HVAC system on the building envelope must be considered. This is particularly important with the addition of humidification. In cold, and even some mild, climates, humidify- ing a previously nonhumidified space may lead to damaging mois- ture accumulation in walls and roofs unless the building envelope can withstand the loads. For a typical nonhumidified building, the interior relative humidity is normally lowest when the exterior temperature is also at a minimum. This is beneficial to the build- ing, because condensation risk on the interior is moderated during the coldest period of the year. Adding humidification (by mechan- ical means or occupant activities) reduces this benefit, and in cold climates may result in surface condensation and/or mold growth for several months out of the year. Durability often is negatively impacted when humidification is added to an existing building unless changes are also made to the envelope to resist condensa- tion. The building envelope requires more attention than just estimat- ing its properties to calculate heating and cooling loads for new equipment. In older buildings with little to no insulation, successful HVAC system design needs to counteract the large envelope losses and solar gains; otherwise, occupant comfort can suffer. This can be particularly noticeable adjacent to windows with single-pane glazing or thermally inefficient walls where additional heating or cooling maybe required to compensate for excessive heat loss. Localized use of space heaters or fans in an existing building indi- cates deficiencies in the previous HVAC system. HVAC system design may have to include perimeter heaters, specialized VA v dis- tribution, or localized heating to prevent low temperatures or mois- ture accumulation in concealed spaces. Additionally, information on existing drawings used to determine thermal performance prop- erties for equipment sizing calculations may not reflect changes already made to the building envelope. Important changes that can affect performance can include window replacements or reflective coatings, adding insulation during reroofing or interior renovation projects, etc. Changing the pressure distribution in building zones or across the exterior envelope also significantly affects the building envelope's moisture performance. Envelope Modifications Without Mechanical System Upgrades Building envelope systems are often upgraded without corre- sponding upgrades to mechanical systems. Failure to modify the existing mechanical system to account for changes in the dynamic performance ofthe building envelope can result in problems such as excess humidity or lack of interior environmental control. Retrofit- ting a building for improved thermal insulation or solar control at glazing systems can effectively reduce cooling loads. Ifthe mechan- ical systems are not modified accordingly, they become oversized for the renovated conditions. This can result in numerous problems, such as poor interior temperature and relative humidity control, or more subtle issues such as inefficient operation. Retaining an older mechanical system may also prevent the full energy savings of an enclosure upgrade from being realized. Improved airtightness should be a criterion of any building en- velope retrofit project. For buildings in cold climates that previ- ously relied on incidental air leakage to provide ventilation, reducing leakage rates may result in high interior air moisture lev- els. In the previously leaky building, incidental leakage was suffi- cient to dilute interior moisture with dry outdoor air and maintain reasonable humidity levels. These buildings should use a ventila- tion system using appropriate energy recovery techniques to main- tain adequate fresh air. Designers should assess the relationship between the building envelope and mechanical system, and design appropriate modifica- tions. Design considerations for converting existing buildings to high-performance buildings include the following: · Investigate existing building envelope conditions, taking care to note sites of damage and repair that may affect performance. In many cases, it may be beneficial to gather information on the building' s historical performance, including utility bills and past occupancy types. · Provide documentation of existing conditions in the building, building envelope, and mechanical systems. For historic build- ings, complete a historic structures report. · Identify major air and/or water leakage sites, and provide reme- dial measures to correct flow through these sites. If appropriate, adopt a strategy to reach an airtightness performance target. · Consider improving thermal performance. Exterior insulation is often preferred over interior or cavity insulation, because cavity | {}
81568e58-afb1-4c3d-b06d-d271b6eab325 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Building Envelopes 45.13 or interior insulation typically allows structural and other mem- bers to act as thermal bridges. Local preservation requirements may govern the location of insulation. · Review possible changes to envelope operating characteristics that result from adding thermal insulation or changing HV AC operation. A change in the moisture and/or heat flow function of the envelope can have a significant effect on durability. · With improved envelope performance, consider downsized me- chanical equipment. REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. Arasteh, D.K., M.S. Reilly, and M.D. Rubin. 1989. A versatile procedure for calculating heat transfer through windows. ASHRAE Transactions 95(2): 755-765. Arasteh, D.K., S. Selkowitz, and J. Hartmann. 1985. Detailed thermal per- formance data on conventional and highly insulating window systems. Thermal Performance ofthe Exterior Envelopes ofBuildings III, pp. 830- 845. ASHRAE. Advanced energy design guides. ASHRAE. 2006. ASHRAE greenguide: The design, construction, and oper- ation of sustainable buildings, 2nd ed. ASHRAE. 2007. Energy standard for buildings except low-rise residential buildings. ANSI/ASHRAE/IESNA Standard 90.1-2007. ASHRAE. 2007. Energy-efficient design of low-rise residential buildings. ANSI/ASHRAE Standard 90.2-2007. ASHRAE. 2009. Criteria for moisture-control design analysis in buildings. ANSI/ASHRAE Standard 160-2009. ASTM. 2003. Standard test method for air permeance of building materials. Standard E2178. American Society for Testing and Materials, West Con- shohocken, PA. Bareither, H.D., A.N. Fleming, and B.E. Alberty. 1948. Temperature and heat-loss characteristic of concrete floors laid on the ground. University of Illinois Small Home Council-Building Research Council Research Report 48-1. Brandemuehl, M.J., J.L. Lepore, and J.F. Kreider. 1990. Modeling and test- ing the interaction of conditioned air with building thermal mass. ASHRAE Transactions 96(2):871-875. Britton, R. 1947. Crawl spaces: Their effect on dwellings-An analysis of causes and results-Suggested good practice requirements. HHFA Tech- nical Bulletin 2. Housing and Home Finance Agency. Washington, D.C. CMHC. 2002. Best practice guide: Architectural precast concrete- Walls and structure. Canada Mortgage and Housing Corporation, Ottawa, ON. CMHC. 2004. Best practice guide: Glass and metal curtain walls. Canada Mortgage and Housing Corporation, Ottawa, ON. CSA. 2007. Guideline on durability in buildings. Standard S478-95 (R2007). Canadian Standards Association, Mississauga, ON. Dubrous, F., and A.G. Wilson. 1992. A simple method for computing energy performance for different locations and orientations. ASHRAE Transac- tions 98(1):841-849. Hagentoft, C.-E. 1988. Heat loss to the groundfrom a building: Slab on the ground and cellar. Department ofBuilding Technology, Lund Institute of Technology, Sweden. Handegord, G., and N. Hutcheon. 1989. Building sciencefor a cold climate. Construction Technology Centre Atlantic, Inc., Fredericton, NB. Hendriks, L., and H. Hens. 2000. Building envelopes in a holistic perspec- tive. IEA ECBCS Annex 32, Final Report, vol. 1. International Energy Agency, Energy Conservation in Buildings and Community Systems, Leuven, Belgium. Hens, H., and A. Janssens. 1999. Heat and moisture response of vented and compact cathedral ceilings: A test house evaluation. ASHRAE Transac- tions 105(1). Hutcheon, N. 1963. Requirements for exterior walls. Canadian Building Digest 48. James, T.B., and W.P. Goss. 1993. Heat transmission coefficients for walls, roofs, ceilings, and floors. ASHRAE. Jordan, C.A., E.C. Peck, F.A. Strange, and L. V. Teesdale. 1948. Attic con- densation in tightly built houses. Housing and Home Finance Agency Technical Bulletin 6. Klems, J. 1983. Methods of estimating air infiltration through windows. Energy and Buildings 5:243-252. Kosny J., and J.E. Christian. 1995a. Steady-state thermal performance of concrete masonry unit wall systems. Thermal Envelopes VI Conference, Clearwater, FL. Kosny, J., and J. Christian. 1995b. Reducing the uncertainties associated with using the ASHRAE-zone method for R-value calculations of metal frame walls. ASHRAE Transactions 101(2):779-788. Kosny, J., and A.O. Desjarlais. 1994. Influence of architectural details on the overall thermal performance ofresidential wall systems. Journal ofTher- mal Insulation and Building Envelopes 18:53-69. Kosny, J., E. Kossecka, A.O. Desjarlais, and J.E. Christian. 1998. Dynamic thermal performance of concrete and masonry walls. Thermal Envelopes VII Conference, Clearwater, FL. Kusuda, T., and J. W. Bean. 1987. Design heat loss factors for basement and slab floors. Thermal insulation: Materials and systems. ASTM STP 922. F.J. Powell and S.L. Matthews, eds. American Society for Testing and Materials, West Conshohocken, PA. Labs, K., J. Carmody, R. Sterling, L. Shen, Y.J. Huang, and D. Parker. 1988. Building foundation design handbook. ORNL/Sub/86-72143/1. Oak Ridge National Laboratory, Oak Ridge, TN. Lecompte, J. 1990. Influence of natural convection in an insulated cavity on the thermal performance of a wall. Insulation Materials, Testing and Applications, pp. 397-420. ASTM STP 1030. American Society for Test- ing and Materials, West Conshohocken, PA. Lstiburek, J. 2007. Building sciences: The hollow building. ASHRAE Jour- nal 49(6):56-58. Mitalas, G.P. 1983. Calculation of basement heat loss. ASHRAE Transac- tions 89(1B):420-437. DRB Paper No. 1198. Division of Building Research. National Research Council Canada, Ottawa, ON. web.mit.edu /parnstr/Public/NRCam/troc23378.pdf. Newell, T.A., and M.E. Snyder. 1990. Cooling cost minimization using build- ing mass for thermal storage. ASHRAE Transactions 96(2):830-838. NIBS. 2010. Whole building design guide. National Institute of Building Sciences, Washington, D.C. www.wbdg.org. NRCA. Roofing and Waterproofing Manual. National Roofing Contractors Association, Rosemont, IL. NRCC. 2005. National building code ofCanada. National Research Council Canada. Park, S. 2009. Moisture in historic buildings and preservation guidance. ASTM Manual 18: Moisture control in buildings: The keyfactor in mold prevention, H. Trechsel and M. Bomberg, eds. American Society for Testing and Materials, West Conshohocken, PA. Rose, W. 2010. Recommendations for remedial and preventive actions for existing residential buildings. ASTM Manual 18: Moisture control in buildings: The keyfactor in mold prevention, H. Trechsel and M. Bomb- erg, eds. American Society for Testing and Materials, West Consho- hocken, PA. Secretary of the Interior. 1977. Standards for the treatment of historic prop- erties. www.nps.gov/history/hps/tps. Selkowitz, S.E. 1979. Thermal performance of insulating window systems. ASHRAE Transactions 85(2):669-685. Shipp, P. 1982. Basement, crawl space and slab-on-grade performance. Thermal Performance of the Exterior Envelopes of Buildings II. ASHRAE. Steven Winter Associates. 1988. Catalog of thermal bridges in commercial and multi-family residential constructions. Report 88-SA407/1 for Oak Ridge National Laboratory, Oak Ridge, TN. Sullivan, R., B. Chin, D. Arasteh, and S. Selkowitz. 1992. A residential fen- estration performance design tool. ASHRAE Transactions 98(1):832- 840. TenWolde, A., and C. Carll. 1992. Effect of cavity ventilation on moisture in walls and roofs. Thermal Performance of the Exterior Envelopes of Buildings V, pp. 555-562. ASHRAE. TenWolde, A., and W. Rose. 1999. Issues related to venting of attics and cathedral ceilings. ASHRAE Transactions 105(1). Tobiasson, W. 2010. Roofs. ASTM Manual 18: Moisture control in build- ings: The key factor in mold prevention, H. Trechsel and M. Bomberg, eds. American Society for Testing and Materials, West Conshohocken, PA. Inc. ASHRAE, 2019 user. single for Licensed | {}
0320d1a0-4b37-40ef-8a29-5476adcd828c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 45.14 2019 ASHRAE Handbook - HVAC Applications (SI) BIBLIOGRAPHY Tuluca, A., D. Lahiri, andJ. Zaidi. 1997. Calculation methods and insulation techniques for steel stud walls in low-rise multifamily housing. ASHRAE Transactions 103(1):550-562. U.S. ACE. 2009. Engineering and Construction Bulletin 2009-29. U.S. Army Corps of Engineers. Van Geem, M.G. 1986. Summary of calibrated hot box test results for twenty-one wall assemblies. ASHRAE Transactions 92(2B):584-602. Verschoor, J.D. 1977. Effectiveness of building insulation applications. USN/CEL Report CR78.006-NTIS AD-A053 452/9ST. Weidt, J.L., and J. Weidt. 1980. Field air leakage of newly installed residen- tial windows. LBL Report 11111. Lawrence Berkeley Laboratory, CA. Wilcox, B., A. Gumerlock, C. Barnaby, R. Mitchell, and C. Huizenza. 1985. The effects of thermal mass exterior walls on heating and cooling loads in commercial buildings. Thermal Performance of the Exterior Enve- lopes of Buildings III, pp. 1187-1224. IEA. 1991. Condensation and energy: Guidelines and practice. IEA ECBCS Annex 14. International Energy Agency, Energy Conservation in Build- ings and Community Systems, Leuven, Belgium. Korsgaard, V., and C.R. Pedersen. 1992. Laboratory and practical experi- ence with a novel water-permeable vapor retarder. Thermal Performance of the Exterior Envelopes of Buildings V, pp. 480-490. ASHRAE. Sanders, C. 1996. Environmental conditions. IEA ECBCS Annex 24, Final Report, vol. 2. International Energy Agency, Energy Conservation in Buildings and Community Systems, Leuven, Belgium. Trechsel, H.R., ed. 1994. Moisture control in buildings. ASTM Manual 18: Moisture control in buildings: The key factor in mold prevention, H. Trechsel and M. Bomberg, eds. American Society for Testing and Materials, West Conshohocken, PA. Inc. ASHRAE, 2019 user single for Licensed Related Commercial Resources | {}
605f7354-dd66-4ed3-bf5b-55cf8952fd02 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 46 BUILDING AIR INTAKE AND EXHAUST DESIGN Exhaust Stack and Air Intake Design Strategies 46.1 Geometric Method for Estimating Stack Height 46.5 Exhaust-To-Intake Dilution or Concentration Calculations 46.7 Other Considerations 46.10 0 UTDOOR air enters a building through its air intake to provide ventilation air to building occupants. Likewise, building ex- haust systems remove air from a building and expel the contaminants to the atmosphere. If the intake or exhaust system is not well de- signed, contaminants from nearby outdoor sources (e.g., vehicle ex- haust, emergency generators, exhaust stacks on nearby buildings) or from the building itself (e.g., laboratory fume hood exhaust, plumb- ing vents) can enter the building before dilution. Poorly diluted con- taminants may cause odors, health impacts, and reduced indoor air quality. This chapter discusses proper design of exhaust stacks and placement of air intakes to avoid adverse air quality impacts. Chap- ter 24 of the 2017 ASHRAE Handbook-Fundamentals describes wind and airflow patterns around buildings in greater detail. Related information can also be found in Chapters 9, 18, 33, 34, and 35 of this volume, Chapters 1 1 and 12 of the 2017 ASHRAE Handbook- Fundamentals, and Chapters 29, 30, and 35 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment. 1. EXHA UST STACK AND AIR INTAKE DESIGN STRATEGIES Stack Design Strategies The dilution a stack exhaust can provide is limited by the disper- sion capability of the atmosphere. Before discharging out the stack, exhaust contamination can be reduced by filters, collectors, and scrubbers to maintain acceptable air quality. The goal of stack design is to specify the minimum flow ofthe exhaust system, exhaust veloc- ity, and stack height that ensures acceptable air quality at all loca- tions of concern. This also reduces the exhaust system's energy consumption. Central exhaust systems that combine airflows from many ex- haust sources should always be used where safe and practical. By combining several exhaust streams, central systems can dilute con- taminants in the exhaust airstream more efficiently. The combined flow can generate an exhaust plume that rises a greater distance above the emitting building. If necessary for air quality reasons, ad- ditional air volume can be added to the exhaust near the exit with a makeup air unit to increase initial dilution and exhaust plume rise. This added air volume does not need heating or cooling, and the ad- ditional energy cost is lower than increasing stack exit velocity. A small increase in stack height may also achieve the same benefit without an added energy cost. In some cases, separate exhaust systems are mandatory. The nature of the contaminants to be combined, recommended industrial hygiene practice, and applicable safety codes need to be considered. Separate exhaust stacks could be grouped in close proximity to one another to take advantage of the larger plume rise of the resulting combined jet. Also, a single stack location for a central exhaust system or a tight cluster of stacks provides more options for locating building air intakes on the building facade or roof. Petersen and Reifschneider (2008) provide guidelines for optimal arrangements The preparation of this chapter is assigned to TC 4.3, Ventilation Require- ments and Infiltration. ![image](/image/placeholder) hplume = hs + hr-hd 1:5 LINE THAT JUST CLEARS RECIRCULATION ZONES top 0 INTAKE A U H G INTAKE B Fig. 1 Flow Recirculation Regions and Exhaust Parameters (Wilson 1982) of ganged stacks. In general, for a tight cluster to be considered as a single stack (i.e., to add stack momentums together) in dilution cal- culations, the stacks must be uncapped and nearly be touching the middle stack of the group. As shown in Figure 1, stack height hs is measured from the roof level on which the exhaust stack is located to the top ofthe stack. Wil- son and Winkel (1982) demonstrated that stacks terminating below the level of adjacent walls and architectural enclosures frequently do not effectively reduce roof-level exhaust contamination. To take full advantage of their height, stacks should be located on the highest roof of a building. Architectural screens used to mask rooftop equipment adversely affect exhaust dilution, depending on porosity, relative height, and distance from the stack. Petersen et al. (1999) found that exhaust dis- persion improves with increased screen porosity. Large buildings, structures, and terrain close to the emitting build- ing can adversely affect stack exhaust dilution, because the emitting building can be within the recirculation flow zones downwind of these nearby flow obstacles (Wilson et al. 1998a). In addition, venti- lation air entering air intakes located on nearby taller buildings can be contaminated by stack exhaust from shorter buildings. Wherever pos- sible, facilities emitting toxic or highly odorous contaminants should not be located near taller buildings or at the base of steep terrain. As shown in Figure 2, stacks should be vertically directed and uncapped. Stack caps that deflect the exhaust jet have a detrimental effect on exhaust plume rise. Small conical stack caps often do not completely exclude rain, because rain does not always fall straight down; periods of heavy rainfall may be accompanied by high winds that deflect raindrops under the cap and into the stack (Changnon 1966). A stack exhaust velocity Ve of about 13 m/s prevents con- densed moisture from draining down the stack and keeps rain from entering the stack. For intermittently operated systems, protection from rain and snow should be provided by stack drains, as shown in Figure 2F to 2J, rather than stack caps. Recommended Stack Exhaust Velocity High stack exhaust velocity and temperatures increase plume rise, which tends to reduce intake contamination. Exhaust velocity 46.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
293b2449-ad63-4163-81e8-30475523346e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 46.2 2019 ASHRAE Handbook-HVAC Applications (SI) ![image](/image/placeholder) PLAQUE RECOMMENDED DISCHARGE VELOCITY: 15 m/s MINIMUM FAN FAN PITCH A B C D E 0 DRAIN DRAIN BEST: NO CAPS OR HEADS ![image](/image/placeholder) STACK HEADS DRAIN LIP PERIPHERAL DRAIN LIP AND 신호주 DRAIN HOLES FAN DRAIN DRAIN F G H J VERTICAL OFFSET POWERHOUSE GOOD: DRAIN-TYPE STACKS ![image](/image/placeholder) CONE CAP INVERTED CONE HINGED COVER DRAIN TUBE K L M N O P Q POOR: SHOULD NOT BE USED Fig. 2 Stack Designs Providing Vertical Discharge and Rain Protection Ve should be maintained above 10 m/s (even with drains in the stack) to provide adequate plume rise and jet dilution. Velocities above 10 m/s provide greater plume rise and dilution, but above 15 to 20 m/s, noise, vibration, and energy costs can become an important concern. An exit nozzle (Figure 2B) can be used to increase exhaust velocity and plume rise. Many laboratory fume hood systems use variable-volume fans that reduce flow from hoods when they are closed. Stack exhaust velocity calculations must be based on the minimum total flow rate from the system, not the maximum. An exception to these exhaust velocity recommendations include when corrosive condensate droplets are discharged. In this case, a velocity of 5 m/s in the stack and a condensate drain are recom- mended to reduce droplet emission. At this low exhaust velocity, a taller stack may be needed to counteract downwash caused by low exit velocity. Another exception is when a detailed dispersion mod- eling analysis is conducted. Such an analysis can determine the min- imum exit velocity needed to maintain acceptable dilution versus stack height. Generally, the taller the stack, the lower the required exit velocity and fan energy consumption. Stack wake downwash occurs where low-velocity exhausts are pulled downward by negative pressures immediately downwind of the stack, as shown in Figure 3. Ve should be at least 1.5 times the design speed UH at roof height in the approach wind to avoid stack wake downwash. A meteorological station design wind speed Umet that is exceeded less than 1% of the time can be used as UH. This value can be obtained from Chapter 14 of the 2017 ASHRAE Hand- book-Fundamentals, or estimated by applying Table 2 of Chapter 24 ofthat volume to annual average wind speed. Because wind speed increases with height, a correction for roof height should be applied ![image](/image/placeholder) PLUME TRAJECTORY WITH DOWNWASH NET PLUME RISE UH Ah hd h s Fig. 3 Reduction of Effective Stack Height by Stack Wake Downwash for buildings significantly higher than 10 m, using the power law rule described in Equation (4) and Table 1 of Chapter 24 of the 2017 ASHRAE Handbook-Fundamentals. Other Stack Design Standards Minimum heights for chimneys and other flues are discussed in the International Building Code (ICC 2006). For laboratory fume hood exhausts, American Industrial Hygiene Association (AIHA) Standard Z9.5 recommends a minimum stack height of 3 m above the adjacent roof line, an exhaust velocity Ve of 15 m/s, and a stack height extending one stack diameter above any architectural screen; National Fire Protection Association (NFPA) Standard 45 specifies a minimum stack height of 3 m to protect rooftop workers. Toxic chemical emissions may also be regulated by federal, state, and local air quality agencies. Contamination Sources Some contamination sources that need consideration in stack and intake design include the following. Toxic Stack Exhausts. Boilers, emergency generators, and lab- oratory fume hoods are some sources that can seriously affect build- ing indoor air quality because of toxic air pollutants. These sources, especially diesel-fueled emergency generators, can also produce strong odors that may require administrative measures, such as gen- erator testing during low building occupancy or temporarily closing the intakes. Automobile and Truck Traffic. Heavily traveled roads and parking garages emit carbon monoxide, dust, and other pollutants. Diesel trucks and ambulances are common sources of odor com- plaints (Smeaton et al. 1991). Avoid placing intakes near vehicle loading zones. Overhead canopies on vehicle docks do not prevent hot vehicle exhaust from rising to intakes above the canopy. When the loading zone is in the flow recirculation region downwind from the building, vehicle exhaust may spread upwind over large sections of the building surface (Ratcliff et al. 1994). Garbage containers may also be a source of odors, and garbage trucks may emit diesel exhaust with strong odors. Kitchen Cooking Hoods. Kitchen exhaust can be a source of odors and cause plugging and corrosion of heat exchangers. Grease hoods have stronger odors than other general kitchen exhausts. Grease and odor removal equipment beyond that for code require- ments may be needed if air intakes cannot be placed an appropriate distance away. Evaporative Cooling Towers. Outbreaks of Legionnaires' dis- ease have been linked to bacteria in cooling tower drift droplets being drawn into the building through air intakes (Puckorius 1999). ASHRAE Guideline 12 gives advice on cooling tower maintenance for minimizing the risk of Legionnaires' disease, and suggests keeping cooling towers as far away as possible from intakes, oper- Inc. ASHRAE, 2019 user. single for Licensed | {}
78594a49-7136-4ba8-829d-eddf04f92605 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Building Air Intake and Exhaust Design 46.3 able windows, and outdoor public areas. No specific minimum sep- aration distance is provided or available. Prevailing wind directions should also be considered to minimize risk. Evaporative cooling towers can have several other effects: water vapor can increase air- conditioning loads, condensing and freezing water vapor can damage equipment, and ice can block intake grilles and filters. Chemicals added to retard scaling and biological contamination may be emitted from the cooling tower, creating odors or health effects, as discussed by Vanderheyden and Schuyler (1994). Building General Exhaust Air. General indoor air that is ex- hausted normally contains elevated concentrations of carbon dioxide, dust, copier toner, off-gassing from materials, cleaning agents, and body odors. General exhaust air should not be allowed to reenter the building without sufficient dilution. Stagnant Water Bodies, Snow, and Leaves. Stagnant water bodies can be sources of objectionable odors and potentially harm- ful organisms. Avoid poor drainage on the roof or ground near the intake. Restricted airflow from snow drifts, fallen leaves, and other debris can be avoided in the design stage with elevated louvers above ground or roof level. Rain and Fog. Direct intake of rain and fog can increase growth of microorganisms in the building. AMCA (2009) recommends selecting louvers and grilles with low rain penetration and installing drains just inside the louvers and grilles. In locations with chronic fog, some outdoor air treatment is recommended. One approach is to recirculate part of the indoor air to evaporate entrained water droplets, even during full air-side economizer operation (maximum outdoor air use). Environmental Tobacco Smoke. Outdoor air intakes should not be placed close to outdoor smoking areas. Plumbing Vents. Codes frequently require a minimum distance between plumbing vents and intakes to avoid odors. Smoke from Fires. Smoke from fires is a significant safety hazard because ofits direct health effects and from reduced visibil- ity during evacuation. NFPA Standard 92A discusses the need for good air intake placement relative to smoke exhaust points. Construction. Construction dust and equipment exhaust can be a significant nuisance over a long period. Temporary precondition- ing of outdoor air is necessary in such situations, but is rarely pro- vided. A simple solution is to provide room and access to the outdoor air duct for adding temporary air treatment filters or other devices, or a sufficient length of duct so that such equipment could be added when needed. Intake louvers and outdoor air ducts also require more frequent inspections and cleaning when construction occurs nearby. Vandalism and Terrorism. Acts of vandalism and terrorism are of increasing concern. Louvers and grilles are potential points of illegal access to buildings, so their placement and construction are important. Intentional introduction of offensive or potentially harmful gaseous substances is also of concern. Some prudent initial design considerations might be elevating grilles and louvers away from easy pedestrian access and specifying security bars and other devices. Also, unlocked stair tower doors required for roof access during emergency evacuations may limit use of rooftop air intakes in sensitive applications because individuals would have ready access to the louvers. For more information, see ASHRAE's (2003) Risk Management Guidance for Health, Safety, and Environmental Security under Extraordinary Incidents. General Guidance on Intake Placement Carefully placed outdoor air intakes can reduce stack height requirements and help maintain acceptable indoor air quality. Rock and Moylan (1999) reviewed literature on air intake locations and design, and Petersen and LeCompte (2002) showed the benefit of placing air intakes on building sidewalls. ASHRAE Standard 62.1 highlights the need to locate makeup air inlets and exhaust outlets to avoid contamination. Experience provides some general guidelines on air intake place- ment. Unless the appropriate dispersion modeling analysis is con- ducted, intakes should never be located in the same architectural screen enclosure as contaminated exhaust outlets. This is especially the case for low-momentum or capped exhausts (which tend to be trapped in the wind recirculation zone within the screen). For more information, see the section on Influence of Architectural Screens on Exhaust Dilution. If exhaust is discharged from several locations on a roof, intakes should be sited to minimize contamination. Typically, this means maximizing separation distance. Where all exhausts of concern are emitted from a single, relatively tall stack or tight cluster of stacks, a possible intake location might be close to the base of this tall stack, ifthis location is not adversely affected by other exhaust locations or is not influenced by tall adjacent structures creating downwash. However, contaminant leakage from the side of the stack has been observed in positively pressurized areas between the exhaust fans and stack exit (Hitchings 1997; Knutson 1997), so air intakes should not be placed very close to highly toxic or odorous exhaust stacks regardless of stack height. Intakes near vehicle loading zones should be avoided. Overhead canopies on vehicle docks do not effectively protect air intakes, and vehicle exhaust may spread over large sections of the building surface. Loading zones also may have garbage and solid waste re- ceptacles that create odors; trucks that serve the receptacles also produce odors. Air intakes should also not be placed near traffic or truck waiting areas. General building exhausts should also not be placed near outdoor contamination sources because flow reversal and ingestion of air through exhaust outlets can occur under some conditions (Seem et al. 1998). Examining airflow around a building can help determine air in- take placement. When wind is perpendicular to the upwind wall, air flows up and down the wall, dividing at about two-thirds up the wall (Figures 4 and 5). The downward flow creates ground-level swirl (shown in Figure 4) that stirs up dust and debris. To take advantage of the natural separation of wind over the upper and lower halves of a building, toxic or nuisance exhausts should be located on the roof and intakes located on the lower one-third of the building, but high enough to avoid wind-blown dust, debris, and vehicle exhaust. If ground-level sources (e.g., wind-blown dust, vehicle exhaust) are major sources of contamination, rooftop intake is desirable. Code Requirements for Air Intakes Many model building codes exist, and local governments adopt and amend codes as needed. Architects and building systems design- ers need to be familiar with local and national codes applicable to each project. Mechanical and plumbing codes typically give minimum required separation distances for some situations; how- Fig. 4 Flow Patterns Around Rectangular Building ![image](/image/placeholder) WIND UNAFFECTED BY BUILDING STREAMLINES 1 5R H C CONTAMINATED UH ROOF VENT : REGION C> C HEIGHT STAGNATION ZONE AREA OF allow H STRONG SURFACE WIND UPWIND VORTEX ZONE OF RECIRCULATING FLOW, �, Inc. ASHRAE, 2019 user. single for Licensed | {}
c2a877e1-4996-4cb8-9f2c-5cbe20036980 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 46.4 ![image](/image/placeholder) ROOF EDGE FLUCTUATING FLOW VORTEX WIND REATTACHMENT WIND H HEIGHT CROSS- W/2 WIND WIDTH ALONG WIND LENGTH Fig. 5 Surface Flow Patterns and Building Dimensions ever, maintaining these separation distances does not necessarily guarantee that intake contamination will not occur. One example of a model building code is the Uniform Mechanical Code (UMC) (IAPMO 1997a), which has been widely adopted in the United States. The UMC requires that exhausts be at least 0.9 m from property lines and 0.9 m from openings into build- ings. Makeup air intakes should be placed to avoid recirculation. Grease- and explosives-bearing ducts, combustion vents, and refrig- eration equipment have special requirements: intakes should be at least 3 m from combustion or plumbing vents and exhaust air out- lets, and be at least 3 m above a road. Cooling towers should be 1.5 m above or 6 m away from intakes. The Uniform Plumbing Code (UPC) (IAPMO 1997b), requires that exhaust vents from domestic water heaters be 0.9 m or more above air inlets. Sanitary vents must be 3 m or more from or 0.9 m above air intakes. When UPC and UMC requirements conflict, the UPC provisions govern. However, local jurisdictions may modify codes, so the adopted versions may have significantly different requirements than the model codes. Treatment and Control Strategies Inc. ASHRAE, 2019 user. single for Licensed When available intake/exhaust separation does not provide the desired dilution factor, or intakes must be placed in undesirable locations, ventilation air requires some degree of treatment, as dis- cussed in Section 6.2.1 of ASHRAE Standard 62. 1. Fibrous media, inertial collectors, and electrostatic air cleaners, ifproperly selected, installed, and maintained, can effectively treat airborne particles. Reducing gaseous pollutants requires scrubbing, absorptive, ad- sorptive, or incinerating techniques. Biological hazards require spe- cial methods such as using high-efficiency particulate air (HEPA) filters and ultraviolet light. Chapters 17, 29, and 30 of the 2016 ASHRAE Handbook- -HVAC Systems and Equipment describe these treatments in detail. One control approach that should be used with care is selective operation of intakes. If a sensor in the intake air- stream detects an unacceptable level of some substance, the outdoor air dampers are closed until the condition passes. This strategy has been used for helicopter landing pads at hospitals and during emer- gency generator testing. The drawbacks are that pressurization is lost and ventilation air is not provided unless the recirculated air is heavily treated. In areas of chronically poor outdoor air quality, such as large urban areas with stagnant air, extensive and typically costly treatment ofrecirculated air may be the only effective option when outdoor air dampers are closed for extended periods. Intake Locations for Heat-Rejection Devices Cooling towers and similar heat-rejection devices are very sen- sitive to airflow around buildings. This equipment is frequently roof-mounted and has intakes close to the roof, where air can be 2019 ASHRAE Handbook- - HVAC Applications (SI) ![image](/image/placeholder) UNDISTURBED Z1 ROOF RECIRCULATION REGION FLOW Z2 HIGH-TURBULENCE REGION Z3 ROOF WAKE BOUNDARY BUILDING WAKE RECIRCULATION REGION 1.5R 0:1 UH ◀-X C C 0 0 Fig. 6 Design Procedure for Required Stack Height to Avoid Contamination (Wilson 1979) considerably hotter and at a higher wet-bulb temperature than air that is not affected by the roof. This can reduce the capacity of cooling towers and air-cooled condensers. Heat exchangers often take in air on one side and discharge heat- ed, moist air horizontally from the other side. Obstructions immedi- ately adjacent to these horizontal-flow cooling towers can drastically reduce equipment performance by reducing airflow. Furthermore, exhaust-to-intake recirculation can be an even more serious problem for this equipment: recirculation of warm, moist exhaust raises the inlet wet-bulb temperature, which reduces performance. Recirculation can be caused by adverse wind direction or local dis- turbance of airflow by an upwind obstruction, or by a close down- wind obstruction. Vertical exhaust ducts may need to be extended to reduce recirculation and improve equipment effectiveness. Wind Recirculation Zones on Flat-Roofed Buildings Stack height design must begin by considering the wind recircu- lation regions (Figure 6). To avoid exhaust reentry, the stack plume must avoid rooftop air intakes and wind recirculation regions on the roof and in the wake downwind of the building. If stacks or exhaust vents discharge within this region, gases rapidly diffuse to the roof and may enter ventilation intakes or other openings. Figures 4 and 6 show that exhaust gas from an improperly designed stack is en- trained into the recirculating flow zone behind the downwind face and is brought back into contact with the building. Wilson (1979) found that, for a flat-roofed building, the upwind roof edge recirculation region height Hc at location Xc and its recir- culation length Lc (shown in Figures 1 and 6) are proportional to the building size scale R: Hc = 0.22R Xc = 0.5R (1) (2) Lc = 0.9R and the wind recirculation cavity length Lr on the downwind side of the building is approximately (3) L, = R (4) where R is the building scaling length: R = B0.67 B 0.33 where Bs is the smaller of the building upwind face dimensions (height or width) and BL is the larger. These equations are approxi- mate but are recommended for use. The dimensions of flow recircu- lating zones depend on the amount of turbulence in the approaching (5) | {}
4cc242de-a3d4-4ae4-9704-6340b4f80efc | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Building Air Intake and Exhaust Design 46.5 wind. High levels of turbulence from upwind obstacles can decrease the coefficients in Equations (1) to (4) by up to a factor of two. Tur- bulence in the recirculation region and in the approaching wind also causes considerable fluctuation in the position of flow reattachment locations (Figures 5 and 6). Rooftop obstacles such as penthouses, equipment housings, and architectural screens are accounted for in stack design by calculat- ing the scale length R for each of these rooftop obstacles from Equa- tion (5) using the upwind face dimensions of the obstacle. The recirculation regions for each obstacle are then calculated from Equations (1) to (4). When a rooftop obstacle is close to the upwind edge ofa roof or another obstacle, the flow recirculation zones inter- act. Wilson (1979) gives methods for dealing with these situations. Building-generated turbulence is confined to the roof wake re- gion, whose upper boundary Z3 in Figure 6 is Z3/R = 0.28(x/R)0.33 where x is the distance from the upwind roof edge where the recir- culation region forms. Building-generated turbulence decreases with increasing height above rooflevel. At the edge ofrooftop wake boundary Z3, turbulence intensity is close to the background level in the approach wind. The high levels ofturbulence in the air below the boundary Z2 in Figure 6 rapidly diffuse exhaust gases downward to contaminate roof-level intakes. As shown in Figure 6, the boundary Z2 of this high-turbulence region downwind of a wind recirculation region is approximated by a straight line sloping at 10:1 downward from the top of the wind recirculation zone to the roof. The stack in Figure 6 may be inadequate because at point A the plume intersects the high turbulence boundary Z2. The geometric method for stack height is discussed in more detail in the next section. 2. GEOMETRIC METHOD FOR ESTIMATING STACK HEIGHT This section presents a method of specifying stack height hs so that the lower edge of the exhaust plume lies above air intakes and wind recirculation zones on the roof and downwind of the emitting building, based on flow visualization studies (Wilson 1979). This method does not calculate exhaust dilution in the plume; instead, it estimates the size of recirculation and high turbulence zones, and the stack height to avoid contamination is calculated from the shape of the exhaust plume. High vertical exhaust velocity is accounted for with a plume rise calculation that shifts the plume upward. Low vertical exhaust velocity that allows stack wake downwash of the plume (see Figure 3) is accounted for by reducing the effective stack height. This stack height should prevent reentry of exhaust gas into the emitting building most of the time, ifno large buildings, structures, or terrain are nearby to disturb the approaching wind. The geometric method considers only intakes on the emitting building. Additional stack height or an exhaust-to-intake roof-level dilution calculation is often required if the exhaust plume can impinge on a nearby building (Wilson et al. 1998b). Dilution calculations should be used if this method produces an unsatisfactorily high stack, or if exhaust gases are highly toxic releases from fume hood exhaust. Rooftop obstacles can significantly alter dispersion from exhaust stacks immediately downwind of, and of similar height to, the obstacles (Saathoff et al. 2002). The goal of the geometric stack method is to ensure that the exhaust plume is well above the recir- culation zones associated with these obstacles. Step 1. Use Equations (1) to (5) to calculate the height and loca- tion of flow recirculation zones 1 and 2 and the recirculation zone downwind of the building (see Figure 6). All zones associated with rooftop obstacles up- and downwind of the stack location should be included. Note that zone 3 is not used in the geometric design method. Step 2. Draw the recirculation regions on the top and downwind sides of penthouses, equipment housings, architectural screens, and other rooftop obstacles up- and downwind of the stack location. If there are intakes on the downwind wall of the building, include the building recirculation region Lr on this wall. Now, calculate the height hsc of a stack with a rain cap (i.e., no plume rise) and draw a line sloping down at 1:5 (1 1.3°) in the wind direction above the roof. Slide this line down toward the building as shown in Figure 1 until it contacts any one of the recirculation zones on any obstacle up- or downwind of the stack (or until the line contacts any portion of the building if there are no rooftop zones or sidewall intakes). With the line in this position, its height at the stack location is the smallest allowable plume height hsc for that wind direction. Repeat for other wind directions to find the worst-case (highest) required plume height. ⑥ This estimated hsc is based on an assumption that the plume spreads up and down from hsc with a 1:5 slope (11.3°), as shown in Figure 6. (This slope represents a downward spread of approxi- mately two standard deviations ofa bell-curve Gaussian plume con- centration distribution in the vertical direction.) Step 3. Reduce the stack height to give credit for plume rise from uncapped stacks. Only jet momentum rise is used; buoyancy rise is neglected as a safety factor. For an uncapped stack of diameter de, plume rise hr from the vertical jet momentum of the exhaust is esti- mated versus downwind distance from Briggs (1984) as h, = min { hx, hfs (7) where the plume rise versus downwind distance, in m, is 1 3 3F mX hx = 21 U2H momentum flux, in m4/s2, is de F m = V 2 e 4 the diameter of exhaust is de = 4Ae the jet entrainment coefficient is 1 UH = 3 + Ve j the final plume rise, in m, is 1 2 0.9 F U H U* m hf = U H i and the logarithmic wind profile equation is UH/U* = 2.5 ln(H/z。) where = stack capping factor: 1.0 without cap, 0 with cap x = distance downwind of stack, m Ve = stack exit velocity, m/s Ae = area of exhaust UH = wind speed at building top, m/s H = building height above ground level, m U* = friction velocity, m/s z⌀ = surface roughness length, m Inc. ASHRAE, 2019 user. single for Licensed | {}
a0133892-219d-459b-8f5b-112faf949681 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 46.6 2019 ASHRAE Handbook- -HVAC Applications (SI) Table 1 Atmospheric Boundary Layer Parameters ¦ Terrain Category ¦ z⌀, m ¦ a ¦ , m ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Flat, water, desert ¦ 0.01 ¦ 0.10 ¦ 213 ¦ ¦ Flat, airport, grassland ¦ 0.05 ¦ 0.14 ¦ 274 ¦ ¦ Suburban ¦ 0.65 ¦ 0.22 ¦ 365 ¦ ¦ Urban ¦ 2.0 ¦ 0.33 ¦ 457 ¦ Table 1 describes various Zo values for a range of sites. For example if zo equals 0.65 m and H = 15 m, substituting into the log- arithmic wind profile equation gives UH/U* = 7.9. For an uncapped stack, the capping factor is = 1.0. For a capped stack, = 0, so hr = 0, and no credit is given for plume rise. UH is the maximum design wind speed at roofheight for which air intake con- tamination must be avoided. This maximum design speed must be at least as large as the hourly wind speed exceeded 1% of the time. This 1% design speed is listed for many cities in Chapter 14 of the 2017 ASHRAE Handbook-Fundamentals (on the CD-ROM and ASHRAE Handbook Online). For cities not on this list, set UH equal to 2.5 times the annual average hourly wind speed as recommended in Table 2 of Chapter 24 of the 2017 ASHRAE Handbook- -Funda- mentals. The plume rise of Equation (7) plus the physical stack height should not be considered equivalent to an effective stack height. A real stack of that height has better performance for two reasons: the effective height is achieved immediately instead of somewhere downstream, and the plume is higher than the effective height because of exhaust momentum. Stack height plus plume rise are additive in the geometric method as a simplification, but there are other conservatisms built into the geometric method to offset this approach. Step 4. Increase stack height, if necessary, to account for stack wake downwash caused by low exhaust velocity, as described in the section on Recommended Stack Exhaust Velocity. For a vertically directed jet from an uncapped stack ( = 1.0), Wilson et al. (1998b) recommend a stack wake downwash adjustment hd of hd = de(3.0 - Ve/UH) (8) for Ve/UH 3.0. For Ve/UH 3.0, there is no downwash and hd = 0. Rain caps and louvers are frequently used on stacks of gas- and oil-fired furnaces and packaged ventilation units, for which = 0 and hd = 3.0de. Inc. ASHRAE, 2019 user. single for Licensed The final adjusted stack height hs recommended is hs = hsc -hr + hd The advantage of using an uncapped stack instead of a capped stack is considerable. If the minimum recommended exhaust veloc- ity Ve of1.5UH is maintained for an uncapped stack ( = 1.0), plume downwash hd = 1.5de and hr = 4.5de. For a capped stack ( =0), hd = 3.0de and h, = 0. Using these values in Equation (10), an uncapped stack can be made 6.0de shorter than a capped stack. (9) Example 1. The stack height hs of the uncapped vertical exhaust on the building in Figure 1 must be specified to avoid excessive contamination of intakes A and B by stack gases. The stack has a diameter de of 0.5 m and an exhaust velocity Ve of9.0 m/s. It is located 16 m from the upwind edge of the roof. The penthouse's upwind wall (with intake A) is located 30 m from the upwind edge of the roof, 4 m high, and 7 m long in the wind direction. The top of intake A is 2 m below the penthouse roof. The building has a height H of 15 m and a length of 62 m. The top of intake B is 6 m below roof level. The width (measured into the page) of the build- ing is 50 m, and the penthouse is 9 m wide. The annual average hourly wind speed is 12.8 km/h at a nearby airport with an anemometer height Hmet of 10 m. The building is in suburban terrain (see Table 1). Calculate the required stack height hs by the geometrical method using the lowest allowable design wind speed. of a capped stack by pro- Solution: The first step is to set the height hsc jecting lines with 1:5 slopes so that recirculation zones are covered, as shown in Figure 1. The only influence of intake location is that the downwind recirculation zone must be considered if there is an intake on the downwind wall, which is true for intake B in this example. First, check the rooftop recirculation zone associated with the pent- house. To find the height of this recirculation zone, use Equation (5): R = (4)0.67(9.0)0.33 = 5.23 m Then use Equations (1) and (2): Hc = (0.22)(5.23) = 1.15 m Xc = (0.5)(5.23) = 2.62 m With the 1:5 slope of the lower plume boundary shown in Figure 6, the capped stack height in Figure 1 (measured from the main roof) must be hsc = 0.2(30 - 16 + 2.62) + 1.15 + 4.0 = 8.5 m to avoid the recirculation zone above the penthouse. Next, check the building wake recirculation zone downwind of the building. The plume must also avoid this region because intake B is located there. The length of this recirculation region is found using Equation (4): Lr = (15)0.67(50)0.33 = 22.3 m Projecting the downwind corner of this recirculation region upwind with a 1:5 slope to the stack location gives the required height of a no- downwash capped stack above the main roof level as hsc - 16) = 13.7 m = 0.2(62 + 22.3 for the plume to avoid the recirculation zone on the downwind side of the building. The design stack height is set by the condition of avoiding contami- nation of the building wake, because avoiding the penthouse roof recir- culation requires only a 8.5 m capped stack. Credit for plume rise hr from the uncapped stack requires calculation of the building wind speed UH at H = 15 m. The minimum allowable design wind speed is the speed that is exceeded 1% of the time at the meteorological station. In this case, for Hmet m at the airport meteorological station, this = 10 1% wind speed is Umet = 2.5(12.8) = 32 km/h = 9 m/s, using the rela- tionship described in Table 2 of Chapter 24 of the 2017 ASHRAE Hand- book-Fundamentals. With the airport in open terrain (see Table 1), and the building in suburban terrain, the wind speed adjustment param- eters are amet = 0.14 and = 274 m at the airport, and a = 0.22 and met = 365 m at the building. Using Equation (4) in Chapter 24 of the 2017 ASHRAE Handbook-Fundamentals, with building height H = 15 m, 0.14 0.22 274 15 UH= 9 = 7.1 m/s 10 365 Because Ve /UH = 9.0/7.1 = 1.27 is less than 3.0, there is some plume downwash as shown in Figure 3. From Equation (9), hd = 0.5[3 - 1.0(1.27)] = 0.86 m Then, using Equation (7), the plume rise at the design wind speed and the distance to the closest intake A is calculated to be ¦ x = 14.1 m ¦ ¦ --- ¦ ¦ H = 15 m ¦ ¦ d = 0.5 m ¦ ¦ Ve = 9 m/s ¦ ¦ UH = 7 m/s ¦ ¦ zo = 0.65 m ¦ ¦ F = 5.1 m4/s2 m ¦ ¦ Bj = 1.11 ¦ ¦ ms = 1.52 m ¦ ¦ UH/U* = 7.9 ¦ ¦ hf = 0.73 m ¦ ¦ h, = 0.73 m ¦ Using these values in Equation (10), the uncapped height hsc is, with the height reduction credit for the 1.92 m rise and the height addi- tion to account for the 0.86 m downwash, | {}
2c007b9b-692a-403b-86bd-e7b8da27f669 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Building Air Intake and Exhaust Design 46.7 hs = 13.7 - 0.74 + 0.86 = 13.82 m As shown in Figure 1, this stack height is measured above the main roof. If stack height is higher than desirable, an alternative is to use di- lution calculations. The geometric method does not directly account for dilution within the plume. 3. EXHAUST-TO-INTAKE DILUTION OR CONCENTRATION CALCULATIONS Worst-Case Critical Dilution or Maximum Concentration The geometric stack design procedure does not give a quantita- tive estimate of the worst-case critical dilution factor D crit at an air intake. If a required dilution can be specified with known stack emissions and required health limits, odor thresholds, or air quality regulations, computing critical dilutions is the preferred method for specifying stack heights. Petersen et al. (2002, 2004) and Smeaton et al. (1991) discuss use of emission information and formulation of dilution requirements in more detail. Exhaust from a single-source dedicated stack may require more atmospheric dilution than a single stack with the same exhausts combined, because emissions are diluted in the exhaust manifold. This section describes the methods for computing outdoor dilu- tion of exhausts emitted from a rooftop stack because of atmospheric dispersion processes. The resulting dilution can be converted to contaminant concentration for comparison to odor thresholds or health limits. Dispersion of pollutants from building exhaust depends on the combined effect of atmospheric turbulence in the wind approaching the building and turbulence generated by the building itself. This building-generated turbulence is most in- tense in and near the flow recirculation zones that occur on the up- wind edges ofthe building (Figures 1 and 5). Dilution of exhaust gas is estimated using design procedures developed for tall isolated stacks (EPA 1995, 2004), with modifications to include the high tur- bulence levels experienced by a plume diffusing over a building roof in an urban area (Schulman et al. 2000). Halitsky (1982), Hosker (1984), Meroney (1982), and Wilson and Britter (1982) are good references regarding gas diffusion near buildings. Dispersion models (including physical models) ranging from the simple to very complex are intended to help the designer investigate how pollutants will be distributed in the atmosphere, around the building, and around adjacent buildings and areas. These models identify potential problems that could result in too-high pollution concentrations by air intakes, entrances, or other sensitive areas that can fairly easily be corrected during design by changing design parameters such as exhaust exit velocity, stack location or height, etc. Identifying these problems during the design phase allows for a less expensive, more efficient solution than trying to correct a real problem after the building is completed, when, for example, chang- ing the location and/or height of the stack can be very costly. Dilution and Concentration Definitions A building exhaust system releases a mixture of building air and pollutant gas at concentration Ce (mass of pollutant per volume of air) into the atmosphere through a stack or vent on the building. The exhaust mixes with atmospheric air to produce a pollutant concen- tration C, which may contaminate an air intake or receptor if the concentration is larger than some specified allowable value Callow (see Figure 4). The dilution factor D between source and receptor mass concentrations is defined as D = Ce/C where Ce = contaminant mass concentration in exhaust, kg/m3 C = contaminant mass concentration at receptor, kg/m3 The dilution increases with distance from the source, starting from its initial value of unity. If C is replaced by Callow in Equation (11), the atmospheric dilution D req required to meet the allowable concentration at the intake (receptor) is D = Ce/Callow req (11) The exhaust (source) concentration is given by Ce = m /⌀e = m /(AeVe) (12) m = contaminant mass release rate, kg/s Qe = AeVe = total exhaust volumetric flow rate, m3/s Ae = exhaust face area, m2 Ve = exhaust face velocity, m/s where The concentration units of mass per mixture volume are appro- priate for gaseous pollutants, aerosols, dusts, and vapors. The con- centration of gaseous pollutants is usually stated as a volume fraction f (contaminant volume/mixture volume), or as ppm (parts per million) if the volume fraction is multiplied by 106. The pollut- ant volume fraction fe in the exhaust is fe = Q/2e (13) where 0 is the volumetric release rate of the contaminant gas. Both 0 and Qe are calculated at exhaust temperature Te. The volume concentration dilution factor Dv is Dv = fe⌀ f where f is the contaminant volume fraction at the receptor. If the exhaust gas mixture has a relative molecular mass close to that of air, Dv may be calculated from the mass concentration dilution D by (14) Dv = (Te/Ta)D where (15) Te = exhaust air absolute temperature, K Ta = outdoor ambient air absolute temperature, K Many building exhausts are close enough to ambient temperature that volume fraction and mass concentration dilutions Dv and D are equal. Roof-Level Dilution Estimation Method This section presents equations for predicting worst-case roof- level dilution of exhaust from a vertical stack on a roof. The equa- tions assume a bell-shaped Gaussian concentration profile in both the vertical and cross-wind horizontal directions. Gaussian profiles have been used in many atmospheric dispersion models, such as those used by the U.S. Environmental Protection Agency. Consid- ering their simplicity, bell-shaped Gaussian concentration profiles in the cross-wind y and vertical z directions at a given horizontal dis- tance x represent atmospheric dispersion remarkably well (Brown et al. 1993). The dilution equations predict the roof-level dilution Dr, which is the ratio of contaminant concentration Ce at the exit point of the exhaust to the maximum concentration Cr on the plume centerline at rooflevel, giving Dr = Ce/Cr. The centerline of the plume is defined in the X direction, with y the lateral (cross-wind) distance off the plume centerline (axis), and Z the vertical. Dilution is affected by three processes: (10) · Wind carries the plume downwind. The higher the wind speed, the greater the dilution on the plume axis. Wind speed UH carrying the plume is the wind speed in the undisturbed flow approaching the top of the building. · Wind turbulence spreads the plume vertically and laterally (cross-wind). Plume spreads in the cross-windy direction and the Inc. ASHRAE, 2019 user. single for Licensed | {}
64615b27-9b0b-46b0-b606-6f47b3d14db4 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 46.8 2019 ASHRAE Handbook- - HVAC Applications (SI) vertical z direction are and These plume spreads increase y Z" with downwind distance. · The plume is carried vertically by the initial buoyancy and vertical momentum of the exhaust at the stack exit. The higher the plume, the greater the dilution at the roof surface. The stronger the wind, the less the plume rises, which may produce less dilution. Thus, wind speed can have two effects: (1) at very low wind speed, the exhaust jet from an uncapped stack rises high above roof level, producing a large exhaust dilution D, at a given intake loca- tion; and (2) at high wind speed, the plume rise is low but the dilu- tion is large because of longitudinal stretching of the plume by the wind. Between these extremes is the critical wind speed UH,crits at which the smallest amount of dilution occurs for a given exhaust and intake location. Before performing Gaussian dilution calculations on a rooftop, the effect of rooftop obstacles, wind recirculation zones, and intake location(s) must be considered. Dilution depends on the vertical separation between the plume centerline hplume and htop, defined as the highest of the intake, all active obstacles (discussed later), and recirculation zones defined in Equation (1). Vertical separation is defined as = hplume - ht⌀p htop = 0 if hp lume Plume centerline hplume versus downwind distance defined as hplume = hs + hr - ha (17) where hs is the physical stack height above the roof, h, is the plume rise versus downwind distance defined in Equation (7), and h⌀is the stack wake downwash defined in Equation (9) (see Figure 1). (16) To determine which rooftop obstacles are considered active in defining htop, a line in plan view through the stack start by drawing location and the intake of interest. All obstacles along this line or one obstacle width laterally (v-direction) from the line are consid- ered active. Obstacles and recirculation zones upstream of the stack and downstream of the intake should also be considered. The value of htop is the higher of the active obstacles, recirculation zones (including zones on top of active obstacles) defined in Equation (1), and the height of the intakes. All of these heights should be refer- enced to the same roof level used to determine hs. Once htop is defined and is calculated, dilution at the intake is calculated from Inc. ASHRAE, 2019 user. single for Licensed 4UH y z 2 D+(x) = exp 2 Ved2 2 z When plume height is less than the height of intakes, active obstacles, and recirculation zones (i.e., hplume htop), then = 0 and dilution should be calculated using Equation (23). (18) If exhaust gases are hot, buoyancy increases the rise of the exhaust gas mixture and produces lower concentrations (higher dilutions) at roof level. For all exhausts except very hot flue gases from combustion appliances, it is recommended that plume rise from buoyancy be neglected in dilution calculations and stack design on buildings. By neglecting buoyant plume rise, the pre- dicted dilution has an inherent safety factor, particularly at low wind speed, where buoyancy rise is significant. Cross- Wind and Vertical Plume Spreads for Dilution Calculations Close to the stack, dispersion is governed by mechanical mixing, and the following equations for lateral and vertical plume spread can used (Cimorelli et al. 2005): + y 2x 2 2 1 2 0 where iy is lateral turbulence intensity, iz is vertical turbulence inten- sity, x is distance downwind from the stack, and is initial source 0 size, normally set equal to 0.35de. The lateral and vertical turbu- lence intensity can be calculated using the following equations: (19) 1 2 근 x + 2 2 z 0 iy = 0.75ix; iz= 0.5ix (20) (21) where 30 Z ix = nln /In zo zo n = 0.24 + 0.096 log10zo + 0.016(log1ozo)2 where inputs z and Zo are in metres. The averaging time over which exhaust gas concentration expo- sures are predicted is important in determining roof-level dilution. The preceding equations provide dilution estimates for a 10 to 15 min averaging time, which corresponds to the averaging time for ACGIH short-term exposure limits. If odors are a concern, peak minimum dilution may be needed; dilution for shorter averaging times can be estimated as 0.2 t s (Dr)s = (Dr)15 15 where (Dr)s is the estimate for a shorter averaging time ts and (Dr)15 is the estimate for the 15 min averaging time. For example, assume a predicted dilution of (Dr)15 = 100. The dilution for a 1 min aver- aging time would be 100 x (1/15)0.2 = 58. If estimates for longer averaging times are needed, the preceding estimates should be assumed to be hourly averages and the following conservative mul- tiplication factors (EPA 1992) should be used to obtain the esti- mated maximum concentrations for 3 h, 8 h, 24 h, or annual averaging times: ¦ Averaging Time ¦ Scaling or Multiplying Factors ¦ ¦ --- ¦ --- ¦ ¦ 3 h ¦ 1.1 ¦ ¦ 8 h ¦ 1.4 ¦ ¦ 24 h ¦ 2.5 ¦ ¦ Annual ¦ 12.5 ¦ Equations (17), (18), (19), and (20) imply that dilution does not depend on the location of either the exhaust or intake, only on the horizontal distance x between them and the vertical separation + This is reasonable when both exhaust and intake locations are on the same building wall or on the roof. Dilution can increase if the intake is below roof level on the sidewall of a building and the exhaust stack is located on the roof. Petersen et al. (2004) provide methods for estimating the increased dilution on sidewalls. Stack Design Using Dilution Calculations Example 2. In general, a spreadsheet should be designed using the preced- ing equations to calculate dilution from an exhaust at any specified location on the roof. This example shows the results for a calculation at intake A using the information provided in Example 1. The distance from stack to intake is 14.1 m, and highest point on intake A is 2 m above the roof. Assume a 6.1 m stack height above the roof. Figure 7 provides the calculated dilution versus wind speed. The recommended method involves the following steps: (1) specify the site conditions using Table 1; (2) carry out the calculations outlined in Figure 7 using surface roughness in Table 1 for range of wind speeds; (3) repeat the calculations using a surface roughness half this value and 1.5 times this value; (4) find the lowest dilution for the range of wind speeds of inter- est for each surface roughness; and ⑤ determine the overall minimum | {}
60be70c0-7e77-4a26-a85a-d1cb1ab1435c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Building Air Intake and Exhaust Design 46.9 ¦ Zo = ¦ 0.65 ¦ m ¦ ¦ 11 = ¦ 0.22 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 0 H ¦ ⌀s ¦ is ¦ i x ¦ iz x ¦ ⌀, ¦ ⌀; ¦ 雇 d ¦ B, ¦ U H/U. ¦ Is x ¦ by ¦ h ¦ 雇 plume ¦ 5 ¦ D r ¦ ¦ (m/s) ¦ (m) ¦ (-) ¦ (m) ¦ (m) ¦ (m) ¦ (m) ¦ (m) ¦ (-) ¦ () ¦ (m) ¦ (m) ¦ (m) ¦ (m) ¦ (m) ¦ ¦ ¦ 5.00 ¦ 0.18 ¦ 0.27 ¦ 2.87 ¦ 1.92 ¦ 2.88 ¦ 1.92 ¦ 0.60 ¦ 0.89 ¦ 7.85 ¦ 2.21 ¦ 1.28 ¦ 1.28 ¦ 6.77 ¦ 4.78 ¦ 1100 ¦ ¦ 7.00 ¦ 0.18 ¦ 0.27 ¦ 2.87 ¦ 1.92 ¦ 2.88 ¦ 1.92 ¦ 0.86 ¦ 1.11 ¦ 7.85 ¦ 1.52 ¦ 0.73 ¦ 0.73 ¦ 5.97 ¦ 3.98 ¦ 591 ¦ ¦ 9.00 ¦ 0.18 ¦ 0.27 ¦ 2.87 ¦ 1.92 ¦ 2.88 ¦ 1.92 ¦ 1.00 ¦ 1.33 ¦ 7.85 ¦ 1.14 ¦ 0.47 ¦ 0.47 ¦ 5.57 ¦ 3.58 ¦ 504 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Min ¦ 504 ¦ ¦ Zo = ¦ 0.325 ¦ 1n ¦ ¦ 21 = ¦ 0.20 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ U H ¦ ⌀0 ¦ ix ¦ i, x ¦ iz x ¦ ⌀, ¦ Oz ¦ ha ¦ 防 ¦ UH/U. ¦ hx ¦ hf ¦ h ¦ h plume ¦ 5 ¦ D, ¦ ¦ (m/s) ¦ (m) ¦ (-) ¦ (m) ¦ (m) ¦ (m) ¦ (m) ¦ (m) ¦ (-) ¦ (-) ¦ (m) ¦ (m) ¦ (m) ¦ (m) ¦ (m) ¦ ¦ ¦ 5.00 ¦ 0.18 ¦ 0.23 ¦ 2.46 ¦ 1.64 ¦ 2.47 ¦ 1.64 ¦ 0.60 ¦ 0.89 ¦ 9.58 ¦ 2.21 ¦ 1.41 ¦ 1.41 ¦ 6.91 ¦ 4.91 ¦ 3194 ¦ ¦ 7.00 ¦ 0.18 ¦ 0.23 ¦ 2.46 ¦ 1.64 ¦ 2.47 ¦ 1.64 ¦ 0.86 ¦ 1.11 ¦ 9.58 ¦ 1.52 ¦ 0.81 ¦ 0.81 ¦ 6.05 ¦ 4.05 ¦ 1065 ¦ ¦ 9.00 ¦ 0.18 ¦ 0.23 ¦ 2.46 ¦ 1.64 ¦ 2.47 ¦ 1.64 ¦ 1.00 ¦ 1.33 ¦ 9.58 ¦ 1.14 ¦ 0.52 ¦ 0.52 ¦ 5.62 ¦ 3.63 ¦ 745 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Min ¦ 745 ¦ ¦ Zo ■ ¦ 0.975 ¦ ¦ ¦ n ■ ¦ 0.24 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ U H ¦ ⌀9 ¦ m ix ¦ i, x ¦ iz x ¦ ⌀, ¦ ⌀; ¦ h ょ ¦ 防 ¦ U H/U* ¦ hx ¦ he ¦ h ¦ h plume ¦ 5 ¦ D r ¦ ¦ (m/s) ¦ (m) ¦ (-) ¦ (m) ¦ (m) ¦ (m) ¦ (m) ¦ (m) ¦ (-) ¦ () ¦ (m) ¦ (m) ¦ (m) ¦ (m) ¦ (m) ¦ ¦ ¦ 5.00 ¦ 0.18 ¦ 0.30 ¦ 3.17 ¦ 2.11 ¦ 3.17 ¦ 2.11 ¦ 0.60 ¦ 0.89 ¦ 6.83 ¦ 2.21 ¦ 1.19 ¦ 1.19 ¦ 6.69 ¦ 4.69 ¦ 704 ¦ ¦ 7.00 ¦ 0.18 ¦ 0.30 ¦ 3.17 ¦ 2.11 ¦ 3.17 ¦ 2.11 ¦ 0.86 ¦ 1.11 ¦ 6.83 ¦ 1.52 ¦ 0.68 ¦ 0.68 ¦ 5.92 ¦ 3.93 ¦ 470 ¦ ¦ 9.00 ¦ 0.18 ¦ 0.30 ¦ 3.17 ¦ 2.11 ¦ 3.17 ¦ 2.11 ¦ 1.00 ¦ 1.33 ¦ 6.83 ¦ 1.14 ¦ 0.44 ¦ 0.44 ¦ 5.54 ¦ 3.54 ¦ 438 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Min ¦ 438 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Overall Minimum ¦ Overall Minimum ¦ 438 ¦ Fig. 7 Spreadsheet for Example 2 dilution and use this value to determine the acceptability of the exhaust design. Dilution from Flush Exhaust Vents with No Stack For exhaust grilles and louvers on the roof or walls ofa building or penthouse, vertical separation = 0 in Equation (19). Combining Equations (19), (20), and (21) gives 4UH y z Ds(x) = Vede (22) The subscripts in the dilution Ds from a surface exhaust distinguishes it from the roof-level dilution Dr from a stack [Equation (19)]. Minimum critical dilutions for flush exhausts can be calculated using the approximate value UH.crit = 2 m/s based on the observation that, for wind speeds less than 2 m/s) at roof height, the atmosphere tends to develop high levels of turbulence that increase exhaust-to- intake dilution. For flush roof exhausts with no stack, and for wall intakes, the experiments of Petersen et al. (2004) suggest that Ds at the intake is at least a factor of2 larger than the dilution at a roof-level intake at the same stretched-string distance S from the stack. Example 3. The exhaust flow of Qe = 1.76 m3/s in Example 1 comes from a louvered grille at location A. The exhaust grille is 0.7 m high and 0.7 m wide. What is the critical exhaust-to-intake dilution factor at intake B on the downwind wall of the building for an averaging time of 15 min? Solution: Exhaust grille A has a face area of Ae = 0.49 m2 and an exhaust velocity Ve of 707 fpm (3.59 m/s). From Equation (8), the effective exhaust diameter is de = [(4)(0.49)/ ]0.5 = 0.79 m. The stretched-string distance S from exhaust A to intake B is the sum of the 2 m from the top of A to the top of the penthouse, plus the 7 m length of the penthouse, plus the sloped line of horizontal length 24.9 m from the downwind edge of the penthouse roof, and a vertical drop of 4 m to the roof, plus the 6 m to intake B: 2 S = 2 + 7 + 24.92 + 4 + 6 = 35.8 m The critical wind speed is assumed to be UH,crit = 2 m/s for capped stacks and flush vents. The critical dilution of exhaust from A at intake B is calculated from Equation (23). Using a similar method as outlined in Example 2, Figure 8 shows the calculation table results where S and x are assumed equal. These are conservative estimates because they represent the dilution at a low critical wind speed of2 m/s. Dilution at a Building Sidewall (Hidden) Intakes Petersen et al. (2004) provided results of an ASHRAE research study that outlined methods for estimating dilution or concentration for visible versus hidden intakes. A hidden intake is typically on a building side wall or on the side wall of a roof obstruction opposite the exhaust source. A visible intake is at roof level or on top of an obstruction, directly above the exhaust source. The basic approach starts following the method for estimating dilution at a rooftop intake. Dilution is calculated at the rooftop location above the side- wall receptor; dilution at this distance is then increased by the fac- tors given in Petersen et al. (2004). A conservative dilution increase factor for most building configurations is 2.0. EPA Models In late 2005, the EPA recommended that the AERMOD modeling system (Cimorelli et al. 2005) be used instead of the previously pre- ferred industrial source complex (ISC3) model (EPA 1995). The new model includes state-of-the-art boundary layer parameterization techniques, convective dispersion, plume rise formulations, and complex terrain/plume interactions, as well as a building downwash algorithm. AERMOD can be used to calculate short-term (hourly) exposure and long-term (monthly and annual) exposure. Both the short- and long-term models are divided into three source classifica- tions: (1) point source, (2) line source, and (3) area source. For exhaust stack design, the point source is the model of interest. The EPA (2006) guideline also describes a short- and a long-term dry deposition model. AERMOD uses the Gaussian equation to calcu- late the concentration of the contaminant concentration downwind of the source. The models consider the wind speed profile, use plume rise formulas, calculate dispersions factors (which take into consid- eration different landscapes, building wakes and downwash, and buoyancy), calculate the vertical distribution, and consider decay of the contaminant. More information on AERMOD and other EPA models can be found at www.epa.gov/scram. Remember that the EPA models are primarily designed to predict concentration (or dilu- tion) values downwind of the building on which the exhausts are located. For predicting effects at building intakes, operable windows, and entrances, alternative modeling methods are required. Inc. ASHRAE, 2019 user. single for Licensed | {}
e4b68437-7819-4089-98e8-14c3d4df477c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 46.10 2019 ASHRAE Handbook-HVAC Applications (SI) ¦ Zo = ¦ 0.65 ¦ m ¦ ¦ n ¦ 0.22 ¦ ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ U H ¦ 0 8 ¦ I x ¦ , x 1 ¦ , x z ¦ 0 , ¦ 0 z ¦ h d ¦ 5 ¦ D r ¦ ¦ (m/s) ¦ (m) ¦ (-) ¦ (m) ¦ (m) ¦ (m) ¦ (m) ¦ (m) ¦ (m) ¦ ¦ ¦ 2. 00 ¦ 0.28 ¦ 0.27 ¦ 7.30 ¦ 4.86 ¦ 7.30 ¦ 4.87 ¦ 0.96 ¦ - ¦ 126 ¦ ¦ Zo = ¦ 0.325 ¦ m ¦ ¦ n = ¦ 0.20 ¦ ¦ ¦ ¦ ¦ ¦ U H ¦ 0 0 ¦ , X ¦ x 1 ¦ , x Z ¦ 0 1 ¦ 0 z ¦ h d ¦ 5 ¦ D r ¦ ¦ (m/s) ¦ (m) ¦ (-) ¦ (m) ¦ (m) ¦ (m) ¦ (m) ¦ (m) ¦ (m) ¦ ¦ ¦ 2. 00 ¦ 0.28 ¦ 0.23 ¦ 6.24 ¦ 4. 16 ¦ 6.25 ¦ 4. 16 ¦ 0.96 ¦ - ¦ 93 ¦ ¦ Zo = ¦ 0.9 75 ¦ m ¦ ¦ n = ¦ 0.24 ¦ ¦ ¦ ¦ ¦ ¦ U H ¦ 0 0 ¦ x i ¦ , i x ¦ Z , x ¦ , 0 ¦ z o ¦ ょ h ¦ 5 ¦ D r ¦ ¦ (m/s) ¦ (m) ¦ (-) ¦ (m) ¦ (m) ¦ (m) ¦ (m) ¦ (m) ¦ (m) ¦ ¦ ¦ 2.00 ¦ 0.28 ¦ 0.30 ¦ 8.04 ¦ 5.36 ¦ 8.05 ¦ 5.36 ¦ 0. 96 ¦ - ¦ 153 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Overall Minimum ¦ Overall Minimum ¦ 93 ¦ Fig. 8 Spreadsheet for Example 3 Wind Tunnel Modeling Wind tunnel modeling is often the preferred method for predicting maximum concentrations for stack designs and locations of interest when energy and equipment optimization is desired. It is the recommended approach because it gives the most accurate esti- mates of concentration levels in complex building environments. A wind tunnel modeling study is like a full-scale field study, except it is conducted before a project is built. Typically, a scale model ofthe building under evaluation, along with the surrounding buildings and terrain within a 300 m radius, is placed in an atmospheric boundary layer wind tunnel. A tracer gas is released from the exhaust sources ofinterest, and concentration levels of this gas are then measured at receptor locations of interest (e.g., air intakes, operable windows) and converted to full-scale concentration values. Next, these values are compared against the appropriate health or odor design criteria to evaluate the acceptability of the exhaust design. Petersen and Cochran (2008) and Snyder (1981) provide more information on scale-model simulation and testing methods. Scale modeling is also discussed in Chapter 24 of the 2017 ASHRAE Handbook-Funda- mentals. Wind-tunnel studies are highly technical, so care should be taken when selecting a dispersion modeling consultant. Factors such as past experience and staff technical qualifications are extremely important. Computer Simulations Using Computational Fluid Dynamics (CFD) CFD models are used successfully to model internal flow paths in areas such as vivariums and atriums, as well as in external aero- dynamics for the aerospace industry. Aerospace CFD turbulence models, however, are ill suited for modeling atmospheric turbulence in complex full-scale building environments because of the differ- ing geometric scales. More information on CFD modeling is in Chapter 24 of the 2017 ASHRAE Handbook-Fundamentals. Based on the current state ofthe art, CFD models should be used with extreme caution when modeling exhaust plumes from labora- tory pollutant sources. Currently, CFD models can both over- and underpredict concentration levels by orders of magnitude, leading to potentially unsafe designs. If a CFD study is conducted for such an application, supporting full-scale or wind tunnel validation stud- ies should be carried out. Various commercial software packages are available for CFD-driven airflow analysis. Most have advanced user interfaces and resulting visualization capabilities, as well as sophis- ticated physical models and solver options. Usually, commercial software includes advanced technical user support provided by ven- dor specialists. Several open-source research codes are available, as well, but require a much greater user insight into the underlying solution methods and hardware platforms. Normally, no user sup- port or problem-specific validation data are available. Regardless of the software package choice, obtaining an accurate numerical solu- tion requires expertise, training, and understanding of the funda- mental aspects of CFD algorithm construction and implementation. 4. OTHER CONSIDERA TIONS Annual Hours of Occurrence of Highest Intake Contamination To assess the severity of the hazard caused by intake contamina- tion, it is useful to know the number of hours per year that exhaust- to-intake dilution is likely to be lower than some allowable mini- mum dilution. The first step in making a frequency-of-occurrence estimate is to use the method outlined in Examples 2 and 3 to esti- mate the minimum dilution versus wind speed at the intake or receptor location of interest. Next, specify the wind speed range at which the dilution is unacceptable. Weather data are then used to calculate the number of hours per year that wind speeds fall in this range for the 22.5° wind direction sector centered on a line joining the exhaust and intake. Combined Exhausts When exhaust from several collecting stations is combined in a single vent (as recommended in the section on Exhaust Stack and Air Intake Design Strategies), the plume rise increases because of the higher mass flow in the combined jet and results in significantly lower roof-level intake concentration Cr compared to that from sep- arate exhausts. Where possible, exhausts should be combined before release to take advantage of this increase in overall dilution. For example, consider a single fume hood exhaust stack at 0.5 m3/s with a 15.24 m/s exit velocity (Ae = 0.1 m) versus 10 such fume hoods combined into a single stack at 5 m3/s and 15.24 m/s (Ae = 1 m). The Fm term in Equation (7) is proportional to the exhaust velocity times the exhaust area. For this example, F, m by a factor of would increase 10. Based on Equation (7), the plume rise would increase by a factor of (10)0.33, or 2.1. Inc. ASHRAE, 2019 user. single for Licensed | {}
609b7e26-7e46-43f7-84d8-43b8501b872a | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Building Air Intake and Exhaust Design 46.11 Ganged Exhausts Greater plume rise and dilution can be achieved by grouping individual stacks close together. Petersen and Reifschneider (2008) summarized ASHRAE research project RP-1 167 on this topic and provided a method for calculating the plume rise and subsequent dilution for ganged stacks, to optimize stack arrangements. They found that, when stacks are nearly touching, the momentum terms for the individual stacks can add together and Equation (7) can be used to compute plume rise for ganged arrangements. If stacks are situated up- and downwind of each other, the F terms can also be m added for quite large separation distances. If the stacks are not up- or downwind of each other, the paper presents an equation that can used to estimate the fraction of the momentum that can be added. This is a particularly advantageous strategy when a dedicated low- flow exhaust is needed that has toxic chemicals. This stack can be placed next to any high-flow stack and achieve the same plume rise and resulting high dilution. Influence of Architectural Screens on Exhaust Dilution Architectural screens are often placed around rooftop equipment to reduce noise or hide equipment. Unfortunately, these screens interact with windflow patterns on the roof and can adversely affect exhaust dilution and thermal efficiency of equipment inside the screen. This section describes a method to account for these screens by modifying the physical stack height h. Architectural screens gen- erate flow recirculation regions similar to those shown downwind of the building and penthouse in Figure 1. These screens are often made of porous materials with mesh or louvers, which influence the height of the recirculation cavity above the screens. To incorporate the effect of architectural screens into existing dilution prediction equations, use the stack height reduction factor Fh. Stack height hs above the roofmust be multiplied by Fh when the stack is enclosed within a screen (Petersen et al. 1999). Effective stack height hs,eff measured above roof level is hs, eff Fhhs = The stack height reduction factor Fh is directly related to screen porosity Ps For stack heights above the top of the screen that are less than 2.5 times the height of the screen, Fh = 0.81Ps + 0.20 where porosity is (23) (24) Open area Ps Total area (25) Fh is applied directly to hs after the required stack height has been calculated, and should be included where the physical stack height is less than 2.5 times the height of the architectural screen. Example 4. Calculate the required stack height for an uncapped stack with a height of 4.7 m above roof level, surrounded by a 3 m high, 50% porous architectural screen. Solution: To determine the effect of the 50% porous screen, use Equa- tion (25) with Ps = 0.5 Fh = 0.81(0.5) + 0.2 = 0.605 The screen has reduced the effective stack height from its actual height of 4.7 m to hs. eff = 0.605(4.7) = 2.84 m When the effect of the 50% porous screen is added, the 4.7 m stack height is found to behave like a 2.86 m stack. The actual stack height hs must be increased to account for the screen 's effect. This is most easily done by dividing hs by the stack height reduction factor: hs 4.7 hs. corrected Fh 0.605 = = = 7.8 m The corrected 7.8 m high stack effectively behaves like a 4.7 m tall stack, and should produce the same dilution at downwind air intakes. The correct height should be used for input when estimating dilution. Emissions Characterization Typical exhaust sources of concern are fume hoods, emergency generators, kitchens, vivariums, loading docks, traffic, cooling tow- ers, and boilers. Chemical emissions from each source should be characterized to determine a design criterion, or critical concentra- tion. Three types ofinformation are needed to characterize the emis- sions: (1) a list of the toxic or odorous substances that may be emitted, (2) the health limits and odor thresholds for each emitted substance, and (3) the maximum potential emission rate for each sub- stance. Recommended health limits Chealth are based on AIHA Standard Z9.5, which specifies air intake concentrations no higher than 20% of acceptable indoor concentrations for routine emission and 100% of acceptable indoor concentrations for accidental releases. Accept- able indoor concentrations are frequently taken to be the minimum short-term exposure limits (STEL) from the American Conference of Governmental Industrial Hygienists (ACGIH), the Occupational Safety and Health Administration (OSHA), and the National Insti- tute of Occupational Safety and Health (NIOSH), as listed in ACGIH. ACGIH also provides odor thresholds. For laboratories, emission rates are typically based on small- scale accidental releases in fume hoods or in room, either liquid spills or emptying of a lecture bottle of compressed gas. Evapora- tion from liquid spills is computed from equations in EPA (1992) based on a worst-case spill in a fume hood or a room. Compressed gas leaks typically assume a fractured lecture bottle empties in one minute. For other sources, such as emergency generators, boilers, and vehicles, chemical emissions rates are often available from the manufacturer. For general laboratory design purposes, Chapter 17 provides an example emission characterization (i.e., design criterion). A 7.5 L/s chemical emission rate (e.g., from a liquid spill or lecture bottle frac- ture) is assumed, along with a limiting concentration of 3 mg/kg or less at an intake. For dispersion modeling purposes, the emission characterization can be expressed in SI units as 400 g/m3 per g/s, or in dilution units of 1:5000 per 500 L/s of exhaust flow. Chapter 17 includes the following disclaimers regarding this design criterion: (1) laboratories using extremely hazardous substances should conduct a chemical-specific analysis based on published health limits, (2) a more lenient limit may be justified for laboratories with low levels of chemical usage, and (3) project-specific requirements must be devel- oped in consultation with the safety officer. Chapter 17's criterion may be put into perspective by considering the as-manufactured and as-installed chemical hood containment requirements outlined in ANSI/AIHA Standard Z9.5- 2003 (i.e., a concentration at a manikin outside the chemical hood of 0.05 ppm or less for as-manufactured, and 0.10 ppm or less for as-installed, with a 0.07 L/s accidental release in the hood as mea- sured using the ASHRAE Standard 1 10-2016 test method). The as- manufactured requirement is equivalent to a design criterion of750 Inc. ASHRAE, 2019 user. single for Licensed g/m3 per g/s, and the as-installed requirement is equivalent to a design criterion of 1500 g/m3 per g/s. Hence, the ASHRAE crite- rion for a manikin representing a worker outside the chemical hood is 1.9 to 3.8 times less restrictive than that for the air intake or other outdoor locations. It seems reasonable that the air intake has more strict criteria, because the worker at the chemical hood can shut the hood or walk away to avoid adverse exposure. Also, the ASHRAE Standard 110-2016 test is not necessarily a worst-case exposure scenario for the worker. | {}
54ca6391-791a-4450-89e5-01adfe968bdc | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 46.12 2019 ASHRAE Handbook-HVAC Applications (SI) SYMBOLS Ae = stack or exhaust exit face area, m2 BL = larger of two upwind building face dimensions H and W, m Bs = smaller of two upwind building face dimensions H and W, m C = contaminant mass concentration at receptor at ambient air temperature Te, Equation (11), kg/m3 Callow at receptor, Equation = allowable concentration of contaminant (12) Ce = contaminant mass concentration in exhaust at exhaust tempera- ture Te, Equation (11), kg/m3 Cr = maximum mass concentration, kg/m3 D = dilution factor between source and receptor mass concentrations, Equation (11) D = critical dilution factor at roof level for uncapped vertical exhaust crit that produces smallest value of Dr at critical wind speed UH,crit for given exhaust-to-intake distance S and stack height hs D, = roof-level dilution factor D at given wind speed for all exhaust locations at same fixed distance S from intake, Equation (19) D = atmospheric dilution required to meet allowable concentration of req contaminant Callow, Equation (12) Ds = dilution at a wall or roof intake from a flush exhaust grille or louvered exhaust, Equation (23) Dv = dilution factor between source and receptor using volume frac- tion concentrations, Equation (15) de = effective exhaust stack diameter, Equation (8), m Fh = stack height adjustment factor to adjust existing stack height above screen for influence of screen of exhaust gas dilution, Equation (25) F momentum flux, m4/s2 m f = contaminant volume concentration fraction at receptor; ratio of contaminant gas volume to total mixture volume, Equation (15), ppm 10-6 fe = contaminant volume concentration fraction in exhaust gas; ratio of contaminant gas volume to total mixture volume, Equation (14), ppm 10 6 H = building height above ground level, m Hc = maximum height above roof level of upwind roof edge flow recirculation zone, Equation (1), m Hmet = anemometer height, m hd = downwash correction to be subtracted from stack height, Equa- tion (9), m hf = final plume rise, m hplume m = final plume height, Equation (18), hr = plume rise of uncapped vertical exhaust jet, Equation (7), m ns (typically above roof unless = physical exhaust stack height otherwise specified), m hsc = required height of capped exhaust stack to avoid excessive intake contamination, Equation (10), m hs.eff = effective exhaust stack height above roof on which it is located, corrected for an architectural screen surrounding the stack, Equation (24), m htop = height of highest of intake, active obstacle, or recirculation zone on a rooftop between the stack and intake, Equation (17), m hx = plume rise at downwind distance x, m = lateral turbulence intensity = vertical turbulence intensity L = length of building in wind direction, Figure 5, m Lc = length of upwind roof edge recirculation zone, Equation (3), m L, = length of flow recirculation zone behind rooftop obstacle or building, Equation (4), m m = contaminant mass release rate, Equation (13), kg/s Ps porosity of an architectural screen near a stack, Equation (26) = 0 = contaminant volumetric release rate, Equation (14), m3/s Qe = total exhaust volumetric flow rate, Equation (13), m3/s R = scaling length for roof flow patterns, Equation (5), m S = stretched string distance from exhaust to intake, m Ta temperature, Equation (16), K = outdoor ambient air absolute Te temperature, Equation (16), K = exhaust air mixture absolute U* = friction velocity, m/s UH = mean wind speed at height H of upwind wall in undisturbed flow approaching building, Equation (7), m/s UH.crit = critical wind speed that produces smallest roof-level dilution for uncapped vertical exhaust at given X and hs, m/s factor D crit Ve = exhaust gas velocity, Equation (13), m/s W = width of upwind building face, m Xc = distance from upwind roof edge to H⌀ Equation (2), m x = horizontal distance from upwind roof edge where recirculation region forms in direction of wind, m X = downwind horizontal distance from center of stack, Equations (20) and (21), m y = cross-wind distance off the plume centerline, m z = vertical distance, m Z⌀ = surface roughness length, m Z1 = height of flow recirculation zone boundary above roof, Figure 6, m Z2 = height ofhigh-turbulence zone boundary above roof, Figure 6, m Z3 = height of roof edge wake boundary above the roof, Equation ⑥ and Figure 6, m Greek = capping factor; 1.0 for vertical uncapped roof exhaust; 0 for capped, louvered, or downward-facing exhaust / jet entrainment coefficient vertical separation above htop, Equation (17), m 0 standard deviation of initial plume spread at the exhaust used to account for initial dilution, Equation (20), m = standard deviation of cross-wind plume spread, Equation (20), m y = standard deviation of vertical plume spread, Equation (21), m Z REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. AIHA. 2003. Laboratory ventilation. ANSI/AIHA Standard Z9.5-2003. American Industrial Hygiene Association, Fairfax, VA. AMCA. 2009. Application manual for air louvers. AMCA Publication 501-09. Air Movement and Control Association, Arlington Heights, IL. ASHRAE. 2000. Minimizing the risk ofLegionellosis associated with build- ing water systems. ASHRAE Guideline 12-2000. ASHRAE. 2003. Risk management guidancefor health, safety, and environ- mental security under extraordinary incidents. ASHRAE. 2016. Ventilation for acceptable indoor air quality. ANSI/ ASHRAE Standard 62. 1-2016. ASHRAE. 2016. Methods of testing performance of laboratory fume hoods. ANSI/ASHRAE Standard 110-2016. Briggs, G.A. 1984. Plume rise and buoyancy effects. In Atmospheric Science and Power Production, D. Randerson, ed. U.S. Department of Energy DOE/TIC-27601 (DE 84005177), Washington, D.C. Brown, M., S.P. Arya, and W.H. Snyder. 1993. Vertical dispersion from sur- face and elevated releases: An investigation of a non-Gaussian plume model. Journal ofApplied Meteorology 32:490-505. Changnon, S.A. 1966. Selected rain-wind relations applicable to stack design. Heating, Piping, and Air Conditioning 38(3):93. Cimorelli, A.J., S.G. Perry, A. Venkatram, J.C. Weil, R.J. Paine, R.B. Wil- son, R.F. Lee, W.D. Peters, and R. W. Brode. 2005. AERMOD: A dis- persion model for industrial source applications. Part I: General model formulation and boundary layer characterization. Journal of Applied Meteorology 44:682-693. EPA. 1992. Workbook ofscreening techniquesfor assessing impacts oftoxic air pollutants (revised). EPA-454/R-92-024. U.S. Environmental Protec- tion Agency, Office of Air Quality, Planning and Standards, Research Triangle Park, NC. EPA. 1995. User 's guidefor the Industrial source complex (ISC3) disper- sion models, vol. 2: Description of model algorithms. EPA-454/B- 95003B. U.S. Environmental Protection Agency, Research Triangle Park, NC. EPA. 2004. AERMOD: Description of model formulation. EPA-454/R-03- 004, September. U.S. Environmental Protection Agency, Research Tri- angle Park, NC. EPA. 2006. Addendum to user 's guidefor the AMS/EPA Regulatory Model- AERMOD, U.S. Environmental Protection Agency, Washington, D.C. Inc. ASHRAE, 2019 user. single for Licensed | {}
9f910833-2986-4012-bf92-f828af0da07d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Building Air Intake and Exhaust Design 46.13 Halitsky, J. 1982. Atmospheric dilution of fume hood exhaust gases. Amer- ican Industrial Hygiene Association Journal 43(3):185-189. Hitchings, D.T. 1997. Laboratory fume hood and exhaust fan penthouse exposure risk analysis using the ANSI/ASHRAE Standard 110-1995 and other tracer gas methods. ASHRAE Transactions 103(2). Paper BN-97- 14-3. Hosker, R.P. 1984. Flow and diffusion near obstacles. In Atmospheric Sci- ence and Power Production, D. Randerson, ed. U.S. Department of En- ergy DOE/TIC-27601 (DE 84005177). IAPMO. 1997a. Uniform mechanical code. International Association of Plumbing and Mechanical Officials, Ontario, California. IAPMO. 1997b. Uniform plumbing code. International Association of Plumbing and Mechanical Officials, Ontario, California. ICC. 2006. International building code. International Code Council, Falls Church, VA. Knutson, G.W. 1997. Potential exposure to airborne contamination in fan penthouses. ASHRAE Transactions 103(2). Paper BN-97-14-4. Meroney, R.N. 1982. Turbulent diffusion near buildings. Engineering Mete- orology 48:525. NFPA. 2004. Fire protection for laboratories using chemicals. ANSI/NFPA Standard 45-04. National Fire Protection Association, Quincy, MA. NFPA. 2006. Recommended practice for smoke-control systems. Standard 92A-2006. National Fire Protection Association, Quincy, MA. Petersen, R.L., and B.C. Cochran. 2008. Wind tunnel modeling of pollutant dispersion. Ch. 24A in Air quality modeling. EnviroComp Institute and Air and Waste Management Association. Petersen, R.L., and J. W. LeCompte. 2002. Exhaust contamination ofhidden versus visible air intakes. Final Report, ASHRAE RP-1168. Petersen, R.L., and J.D. Reifschneider. 2008. The effect of ganging on pol- lutant dispersion from building exhaust stacks. ASHRAE Transactions 114(1). Petersen, R.L., M.A. Ratcliff, and J.J. Carter. 1999. Influence of architec- tural screens on rooftop concentrations because of o effluent from short stacks. ASHRAE Transactions 105(1). Petersen, R.L., B.C. Cochran, and J.J. Carter. 2002. Specifying exhaust and intake systems. ASHRAE Journal 44(8):30-35. Petersen, R.L., J.J. Carter, and J.W. LeCompte. 2004. Exhaust contamina- tion of hidden vs. visible air intakes. ASHRAE Transactions 110(1). Puckorius, P.R. 1999. Update on Legionnaires' disease and cooling systems: Case history reviews- What happened/what to do and current guide- lines. ASHRAE Transactions 105(2). Paper SE-99-03-2. Ratcliff, M.A., R.L. Petersen, and B.C. Cochran. 1994. Wind tunnel model- ing of diesel motors for fresh air intake design. ASHRAE Transactions 100(2):603-611. Rock, B.A., and K.A. Moylan. 1999. Placement of ventilation air intakes for improved IAQ. ASHRAE Transactions 105(1). Saathoff, P., L. Lazure, T. Stathopoulos, and H. Peperkamp. 2002. The influ- ence of a rooftop structure on the dispersion of exhaust from a rooftop stack. Presented at the 2002 ASHRAE Meeting, Honolulu. Schulman, L., D. Strimaitis, and J. Scire. 2000. Development and evaluation of the PRIME plume rise and building downwash model. Journal ofthe Air and Waste Management Association 50:378-390. Seem, J.E., J.M. House, and C.J. Klaassen. 1998. Volume matching control: Leave the outside air damper wide open. ASHRAE Journal 40(2):58-60. Smeaton, W.H., M.F. Lepage, and G.D. Schuyler. 1991. Using wind tunnel data and other criteria to judge acceptability of exhaust stacks. ASHRAE Transactions 97(2):583-588. Snyder, W.H. 1981. Guideline for fluid modeling of atmospheric diffusion. EPA 600/8-81-009. U.S. Environmental Protection Agency, Environ- mental Sciences Research Laboratory, Office of Research and Develop- ment, Research Triangle Park, NC. Vanderheyden, M.D., and G.D. Schuyler. 1994. Evaluation and quantifica- tion of the impact of cooling tower emissions on indoor air quality. ASHRAE Transactions 100(2):612-620. Wilson, D.J. 1979. Flow patterns over flat roofed buildings and application to exhaust stack design. ASHRAE Transactions 85:284-295. Wilson, D.J. 1982. Critical wind speeds for maximum exhaust gas reentry from flush vents at roof level intakes. ASHRAE Transactions 88(1):503- 513. Wilson, D.J., and R.E. Britter. 1982. Estimates of building surface concen- trations from nearby point sources. Atmospheric Environment 16: 2631- 2646. Wilson, D.J., and G. Winkel. 1982. The effect of varying exhaust stack height on contaminant concentration at rooflevel. ASHRAE Transactions 88(1):513-533. Wilson, D.J., I. Fabris, and M. Y. Ackerman. 1998a. Measuring adjacent building effects on laboratory exhaust stack design. ASHRAE Trans- actions 104(2):1012-1028. Wilson, D.J., I. Fabris, J. Chen, and M. Y. Ackerman. 1998b. Adjacent build- ing effects on laboratory fume hood exhaust stack design. Final Report, ASHRAE RP-897. BIBLIOGRAPHY Chui, E.H., and D.J. Wilson. 1988. Effects of varying wind direction on exhaust gas dilution. Journal of Wind Engineering and Industrial Aero- dynamics 31:87-104. EPA. 2003. AERMOD: Latest feature and evaluation results. EPA-454/ R-03-003. U.S. Environmental Protection Agency, Research Triangle Park, NC. Gregoric, M., L.R. Davis, and D.J. Bushnell. 1982. An experimental inves- tigation of merging buoyantjets in a crossflow. Journal ofHeat Transfer, Transactions of ASME 104:236-240. Li, W. W., and R.N. Meroney. 1983. Gas dispersion near a cubical building. Journal of Wind Engineering and Industrial Aerodynamics 12:15-33. McElroy, J.L., and F. Pooler. 1968. The St. Louis dispersion study. U.S. Pub- lic Health Service, National Air Pollution Control Administration. Petersen, R.L., B.C. Cochran, and J.J. Carter. 2002. Specifying exhaust and intake systems. ASHRAE Journal 44(8):30-35. Petersen, R.L., J.J. Carter, and B.C. Cochran. 2005. Modeling exhaust disper- sion for specifying acceptable exhaust/intake designs. Laboratories for the 21st Century Best Practices Guide, DOE/GO-102005-2104. U.S. Environmental Protection Agency, Washington, D.C. www.nrel.gov/docs /fy05osti/37601.pdf. Snyder, William H., and R.E. Lawson. 1991. Fluid modeling simulation of stack-tip downwash for neutrally buoyant plumes. Atmospheric Environ- ment 25A. Wollenweber, G.C., and H.A. Panofsky. 1989. Dependence of velocity variance on sampling time. Boundary Layer Meteorology 47:205-215. Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
251c50a1-667c-47c1-a379-2e5d3db1ad9c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 47 AIR CLEANERS FOR GASEOUS CONTAMINANTS ¦ Terminology ¦ 47.1 ¦ Air Cleaner System Design ¦ 47.12 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Gaseous Contaminants ¦ 47.3 ¦ Safety ¦ 47.17 ¦ ¦ Problem Assessment ¦ 47.7 ¦ Installation, Start-Up, and Commissioning ¦ 47.18 ¦ ¦ Contaminant Reduction Strategies ¦ 47.8 ¦ Operation and Maintenance ¦ 47.18 ¦ ¦ Contaminant Removal by Ventilation Air Cleaning ¦ 47.8 ¦ Environmental Influences on Air Cleaners ¦ 47.19 ¦ ¦ Equipment ¦ 47.11 ¦ Testing Media, Equipment, and Systems ¦ 47.19 ¦ T HE purpose of gas-phase (molecular) filtration is to remove air contaminants that could adversely affect the occupants, pro- cesses, or contents of a space. The effects are problematic at different concentration levels for different contaminants. There are four cate- gories of harmful effects: toxicity, odor, irritation, and material damage. In most cases, contaminants become annoying through irri- tation or odor before they reach levels toxic to humans, but this is not always true. For example, the potentially deadly contaminant carbon monoxide has no odor. More information on gaseous contaminants and odors can be found in Chapters 11 and 12 of the 2017 ASHRAE Handbook-Fundamentals. Indoor gaseous contaminant levels can sometimes be reduced with ventilation air drawn from outdoors, diluting the contaminants to acceptable levels. However, available outdoor air itself may con- tain undesirable gaseous contaminants at unacceptable concentra- tions. If so, it requires treatment by gaseous contaminant removal equipment before being used for ventilation. In addition, minimizing outdoor airflow, as specified in ASHRAE Standard 62. 1 's IAQ pro- cedure, by using a high recirculation rate and filtration is an attrac- tive means of energy conservation. However, recirculated air cannot be made equivalent to fresh outdoor air by removing only particulate contaminants. Noxious, odorous, and toxic contaminants must also be removed by gaseous contaminant removal equipment, which is frequently different from particulate filtration equipment. This chapter covers design procedures for gaseous contaminant air-cleaning systems for occupied spaces only. Procedures dis- cussed are appropriate to address odors and gaseous irritants. Removal of contaminants for the express purpose of protecting building occupants (whether against deliberate attack or industrial accidents) or to protect artifacts (e.g., in museums) requires appli- cation of the same design principles, but applied more rigorously and with great emphasis on having specific design and performance data, providing redundancy, and added engineering safety factors. Design for protection is not a focus of this chapter, although pub- lished design guidance is included and referenced; for more detail, see Chapter 61. Aspects of air-cleaning design for museums, librar- ies, and archives are included in Chapter 24, and removal of gaseous contaminants from industrial processes and stack gases is covered in Chapter 30 of the 2016 ASHRAE Handbook- -HVAC Systems and Equipment. 1. TERMINOLOGY In particular, gaseous contaminant control technology perfor- mance is a function of (1) the specific contaminant, (2) its concen- tration, (3) airflow rate, and (4) environmental conditions. The terminology related to gaseous contaminant air-cleaning equipment is specific to the field, and some terms that are familiar from particle filtration differ slightly in this context. The preparation of this chapter is assigned to TC 2.3, Gaseous Air Contam- inants and Gas Contaminant Removal Equipment. Absorption. Transport and dissolution of a sorbate into an absor- bent to form a homogeneous mixture having the characteristics of a solution. It is important to distinguish absorption from the surface phenomenon of adsorption, which is one of the most important pro- cesses in operation of air cleaners that remove gaseous contami- nants. Activated Carbon. Carbon, usually in the form of granules, treated to enhance its surface area and consequent ability to adsorb gases through a highly developed pore structure. Activity. Mass of contaminant contained in a physical adsorbent at saturation, expressed as a percentage or fraction of the adsorbent mass (i.e., grams contaminant/grams adsorbent). Activity is an equi- librium property under particular challenge conditions, and is not a function of airflow. (In most cases, commercial bed filters are changed for efficiency reasons well before the adsorbent is saturat- ed.) If a saturated adsorbent bed is then exposed to clean air, some of the adsorbed contaminant will desorb. Activity is generally greater than receptivity. Adsorbent. Any solid having the ability to concentrate signifi- cant quantities of other substances on its surface. Adsorption. Process in which the molecules ofa gas or vapor ad- here by physical or chemical processes to the exposed surface of solid substances (both the outer surface and inner pore surface) with which they come into contact. Adsorption, Chemical (Chemisorption). Binding of a contami- nant to the surface of an adsorbent by forces with energy levels approximately those of a chemical bond. Chemisorption is an irre- versible process. Adsorption, Physical. Attraction of a contaminant to the surface, both outer surface and inner pore surface, of adsorbent media by physical forces (Van der Waals forces). Physical adsorption is a re- versible process. Adsorption Capacity. The amount (mass or moles) of a selected contaminant that can be contained in the media of a gas-phase air- cleaning device under given test conditions and end point. Adsorbent, Regenerated. Adsorbent material which, after satu- ration, may be treated to recover its adsorption properties and thereby enabled for reuse. Adsorption Isotherm. A curve obtained by plotting, at constant temperature, the quantity of adsorbate against the concentration of the substance in the original gas or solution. Breakthrough. Point in the operating cycle of a gas-phase air- cleaning device at which the effluent contaminant concentration be- comes measurable. Thereafter, the effluent concentration may rise rapidly. Breakthrough Curve. Plot of contaminant penetration through the air cleaner versus time for a particular challenge concentration and airflow. Breakthrough Time. Operating time (at constant operating con- ditions) before a certain penetration is achieved. For instance, the 10% breakthrough time is the time between beginning to challenge a physical adsorbent or chemisorbent and the time at which air 47.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
742ed498-98f3-46f6-9ff5-ab2ad86e2c06 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 47.2 2019 ASHRAE Handbook-HVAC Applications (SI) discharged contains 10% of the contaminant feed concentration. Continued operation leads to 50% and eventually to 100% break- through, at which point a physical adsorbent is saturated. For a chemisorbent, the media is exhausted. (Some commercial devices are designed to allow some of the challenge gas to bypass the adsor- bent. These devices break through immediately, and breakthrough time, as defined here, does not apply.) Capacity. See Adsorption Capacity. CAS Number. An identification number unique to each individual chemical, specified by the Chemical Abstracts Service (CAS), a division of the American Chemical Society (ACS). Catalyst. Any substance that, when present in a small quantity, significantly affects the rate of a chemical reaction without itself being consumed or undergoing a chemical change. Most catalysts accelerate reactions, but a few retard them (negative catalysts, or inhibitors). Channeling. The disproportionate or uneven flow offluid (gas or liquid) through passages of lower resistance that can occur in fixed beds or columns of granular media because of nonuniform packing, irregular sizes and shapes of media, gas pockets, wall effects, and other causes. Challenge (Air) Stream. Test contaminant(s) of interest diluted to the specific concentration(s) of the test prior to filtration. Chemisorbent Media. Media formed when an adsorbent such as activated alumina, zeolite, or activated carbon is treated with a chem- ical reagent such as potassium permanganate, potassium hydroxide, or phosphoric acid. Adsorbates are removed by a reaction with the chemical reagent. Concentration. Quantity of one substance dispersed in a defined amount of another. Concentrations of contaminants in air are usu- ally expressed as parts per million by volume (ppmv) or as milli- grams of contaminant per cubic metre of air (mg/m3). Density, Apparent (Bulk Density). Mass under specified con- ditions of a unit volume of a solid physical adsorbent or chemisor- bent, including its pore volume and interparticle voids. Desorption. Process by which adsorbed molecules leave the sur- face of a physical adsorbent and reenter the fluid stream. This pro- cess is the opposite of adsorption. Efficiency. See Removal Efficiency. Inc. ASHRAE, 2019 user. single for Licensed Efficiency Curve. Plot of contaminant removal efficiency against time for a particular challenge concentration and airflow. Equilibrium Capacity. See Adsorption Capacity. HEPA Filter. High-efficiency particle air filter that has perfor- mance compliant with requirements of filter class ISO 35H to ISO 45H (per ISO 29463-1). Mass Transfer Zone. Depth of physical adsorption or chemi- sorption media required to remove essentially all of an incoming contaminant; dependent on type of media, media granule size, con- taminant nature, contaminant inlet concentration, and environmen- tal conditions. Mean Particle Diameter. Weighted average particle size, in millimeters, of a granular adsorbent; computed by multiplying the percent retained in a size fraction by the respective mean sieve openings, summing these values, and dividing by 100. Media. Granular or pelletized physical adsorbent (or chemisor- bent) used in gaseous contaminant air-cleaning equipment. Also used to refer to a material (e.g., a nonwoven) that contains a physical adsorbent or chemisorbent. Penetration. Ratio of contaminant concentration downstream of the media bed to the upstream (challenge) concentration, sometimes expressed as a percentage. Related to fractional efficiency by the expression Efficiency = (1 - Penetration). Unlike particulate filters, physical adsorbents and chemisorbents both decline in efficiency as they load. The decline can be very sudden, and is usually not linear with time. Pressure Drop. Difference in absolute (static) pressure between two points in an airflow system, caused by frictional resistance to airflow in a duct, filter, or other system component such as a media bed or air-cleaning device. Reactivation. Treatment of carbon with elevated temperature and steam to remove the volatiles that have been adsorbed on the carbon, so that the adsorbent can be reused. Regeneration. The process of treating carbon thermally or chemically to extend its life. Removal Efficiency. Fraction or percentage of a challenge con- taminant that is removed by the air-cleaner media bed at a given time. Removal efficiency is also known simply as "efficiency. , , Residence Time. Theoretical time period that a contaminant molecule is within the boundaries of the media bed of a physical adsorbent or chemisorbent. The longer the residence time, the higher the efficiency. For gaseous contaminant removal equipment, residence time is computed as Bed area exposed to airflow x Bed depth Residence time (s) = (1) Airflow rate For commercial gaseous contaminant air cleaners, residence time computation neglects the fact that a significant fraction of the volume of the bed is occupied by the media. For example, a unitary adsorber containing trays totaling 4 m2 media in a 25 mm deep bed, challenged at 1 m3/s, has a residence time of 0.1 s. Given this definition, a deeper media bed, lower airflow rate, or media beds in series increase residence time and thus performance. Because gaseous contaminant air cleaners all tend to have approximately the same granule size, residence time is a generally useful indicator of per- formance. In some engineering disciplines, the media volume is subtracted from the nominal volume of packed beds when calculating residence time. This gives a shorter residence time value and is not normally used for HVAC. A minimum 0.07 s residence time for physical adsorbents, and 0.1 s for chemisorbents, provides for a minimum 95% contact time. Different ways of arranging the media, different media, or different media granule sizes all can change the effective residence time because of their effect on the volume ofthe bed occupied by the media. The geometry and packaging of some technologies makes computation of residence time difficult. For example, the flow pat- tern in pleated fiber-carbon composite media is difficult to specify, making residence time computation uncertain. Therefore, although residence times can be computed for partial-bypass filters, fiber- adsorbent composite filters, or fiber-bonded filters, they cannot be compared directly and may serve more as a rating than as an actual residence time. Manufacturers might publish equivalent residence time values that say that a particular physical adsorbent or chemisor- bent performs the same as a traditional deep-bed air cleaner, but no standard test exists to verify such a rating. Retentivity. Measure of the ability of a physical adsorbent or gas- phase air-cleaning (GPAC) device to resist desorption of an adsor- bate. It is usually stated as a percentage or fraction of the adsorbent mass and calculated as the residual capacity (fraction remaining) after purging the adsorbent with clean, conditioned air, following the challenge breakthrough. Retentivity is generally less than activity. Sorbate. A material that has been or is capable of being taken up by another substance through either absorption or adsorption. Saturation. State of a physical adsorbent when it contains all the contaminant it can hold at the challenge concentration, temperature, and humidity of operation. v apor (V apor-Phase Contaminant). Substance whose vapor pressure is less than the ambient pressure at ambient temperature but is present in the gas phase by evaporation or sublimation. v olatile Organic Compound (VOC). Chemical belonging to the medium-volatility subset of the organic compounds that can be | {}
fcbb87cd-6936-497b-a08d-6ee1b3927e2b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Air Cleaners for Gaseous Contaminants 47.3 Table 1 Emissions of Selected Toxic Compounds from Mainstream and Sidestream Smoke of Cigarettes ¦ Contaminant ¦ Contaminant CAS Number ¦ Mainstream Smoke (MS) Range, �g/cigarette ¦ Sidestream Smoke (SS) Range, ug/cigarette ¦ SS/MS Ratio* ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ "Tar" ¦ ¦ 6100-48 700} ¦ 10 500-34 400} ¦ 0.91 ¦ ¦ Carbon monoxide ¦ 630-08-0 ¦ 11 000-40 700} ¦ 31 500-54 100} ¦ 1.87 ¦ ¦ Nicotine ¦ 54-11-5 ¦ 500-3320 ¦ 1900-5300 ¦ 2.31 ¦ ¦ Acetaldehyde ¦ 75-07-0 ¦ 596.2-2133.4 ¦ 1683.7-2586.8 ¦ 1.31 ¦ ¦ Isoprene ¦ 78-79-5 ¦ 288.1-1192.8 ¦ 743.2-1162.8 ¦ 1.33 ¦ ¦ Acetone ¦ 67-64-1 ¦ 258.5-828.9 ¦ 811.3-1204.8 ¦ 1.52 ¦ ¦ Nitric oxide ¦ 10102-43-9 ¦ 202.8-607.1 ¦ 1000-1600 ¦ 2.79 ¦ ¦ Hydrogen cyanide ¦ 74-90-8 ¦ 98.7-567.5 ¦ 190-350 ¦ 0.77 ¦ ¦ Methyl ethyl ketone ¦ 78-93-3 ¦ 72.5-230.2 ¦ 184.5-332.6 ¦ 1.49 ¦ ¦ Acrolein ¦ 107-02-8 ¦ 51.2-223.4 ¦ 342.1-522.7 ¦ 2.53 ¦ ¦ Toluene ¦ 108-88-3 ¦ 48.3-173.7 ¦ 134.9-238.6 ¦ 1.27 ¦ ¦ Propionaldehyde ¦ 123-38-6 ¦ 46.8-144.7 ¦ 151.8-267.6 ¦ 1.06 ¦ ¦ Hydroquinone ¦ 123-31-9 ¦ 27.7-203.4 ¦ 49.8-134.1 ¦ 0.94 ¦ ¦ Catechol ¦ 120-80-9 ¦ 28.1-222.8 ¦ 64.5-107.0 ¦ 0.85 ¦ ¦ Benzene ¦ 71-43-2 ¦ 28.0-105.9 ¦ 70.7-134.3 ¦ 1.07 ¦ ¦ 1,3-Butadiene ¦ 106-99-0 ¦ 23.6-122.5 ¦ 81.3-134.7 ¦ 1.3 ¦ ¦ Butyraldehyde ¦ 123-72-8 ¦ 28.8-95.6 ¦ 138.0-244.9 ¦ 2.68 ¦ ¦ Formaldehyde ¦ 50-00-0 ¦ 12.2-105.8 ¦ 540.4-967.5 ¦ 14.78 ¦ ¦ Crotonaldehyde ¦ 123-73-9 ¦ 11.6-66.2 ¦ 62.2-121.8 ¦ 1.95 ¦ ¦ Ammonia ¦ 7664-41-7 ¦ 9.8-87.7 ¦ 4000-6600 ¦ 147 ¦ ¦ Phenol ¦ 108-95-2 ¦ 7.0-142.2 ¦ 121.3-323.8 ¦ 9.01 ¦ ¦ Acrylonitrile ¦ 107-13-1 ¦ 7.8-39.1 ¦ 24.1-43.9 ¦ 1.27 ¦ ¦ m-Cresol + p-Cresol ¦ 108-39-4/106-44-5 ¦ 7.3-77.3 ¦ 40.9-113.2 ¦ 4.36 ¦ ¦ Pyridine ¦ 110-86-1 ¦ 2.8-27.7 ¦ 195.7-320.7 ¦ 16.08 ¦ ¦ Styrene ¦ 100-42-5 ¦ 4.5-19.3 ¦ 23.2-46.1 ¦ 2.6 ¦ Source: Modified from IARC (2004). *Median value for sidestream/mainstream smoke ratios for 12 commercial cigarette brands present in indoor air under normal indoor atmospheric conditions of temperature and pressure; specifically, an organic compound with a saturation vapor pressure greater than 10-2 kPa at 25°C. 2. GASEOUS CONTAMINANTS Ambient air contains nearly constant amounts of nitrogen (78% by volume), oxygen (21%), and argon (0.9%), with varying amounts of carbon dioxide (about 0.04%) and water vapor (up to 3.5%). In addi- tion, trace quantities of inert gases (neon, xenon, krypton, helium, etc.) are always present. Gases and vapors other than these natural constituents of air are usually considered to be gaseous contaminants. Their concentrations are almost always small, but they may have serious effects on building occupants, construction materials, or contents. Removing these gas- eous contaminants is often desirable or necessary. Sources ofnonindustrial contaminants are discussed in Chapter 11 in the 2017 ASHRAE Handbook-Fundamentals. However, for con- venience, data on some ofthe contaminants in cigarette smoke (Table 1), and some common contaminants emitted by building materials (Table 2), indoor combustion appliances (Table 3), office equipment (Table 4), and occupants (Table 5) are provided here. Table 6 gives typical outdoor concentrations for gaseous contam- inants at urban sites; however, these values may be exceeded if the building under consideration is located near a fossil fuel power plant, refinery, chemical production facility, sewage treatment plant, munic- ipal refuse dump or incinerator, animal feed lot, or other major source of gaseous contaminants. If such sources have a significant influence on the intake air, a field survey or dispersion model must be run. Many computer programs have been developed to expedite such calcula- tions. Using Source Data to Predict Indoor Concentrations Source data such as those in Tables 1 to 5 provide the type of raw information on which air-cleaning system designs can be based in addition to indicating which parameters to measure. Outdoor air con- taminants enter buildings through the outdoor air intake and through infiltration. The indoor sources enter the occupied space air and are distributed through the ventilation system. If measurements are not available, source data can be used to predict the contaminant challenge to air-cleaning systems using building air quality models. The following relatively simple published model is intended as an introduction to the topic. Meckler and Janssen (1988) described a model for calculating the effect of outdoor pollution on indoor air quality, which is outlined in this section and provided in the appendix of ASHRAE Standard 62.1 and 62.2. A recirculating air-handling schematic is shown in Figure 1 . In this case, mixing is not perfect; the horizontal dashed line represents the boundary of the region close to the ceiling through which air passes directly from the inlet diffuser to the return air intake. Ventilation ef- fectiveness Ev is the fraction of total air supplied to the space that mixes with room air and does not bypass the room along the ceiling. Meckler and Janssen suggest a value of 0.8 for Ev. Any people in the space are additional sources and sinks for gaseous contaminants. In the ventilated space, the steady-state contaminant concentration re- sults from the summation of all processes adding contaminants a to the space divided by the summation of ventilation and other processes removing contaminants b. The steady-state concentration Css for a single component can be expressed as (Meckler and Janssen 1988) Contaminant insertion into space C ss a/b = = Contaminant removal from space where (2) Css = steady-state contaminant concentration, �g/m3 a = contaminants inserted into space, �g/s b For the occupied space, the parameters for insertion of the contam- inant into the occupied space are = contaminants removed from space, ug/s Inc. ASHRAE, 2019 user. single for Licensed | {}
b0d88fb1-0ce3-4244-bd98-334c31e24934 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 47.4 2019 ASHRAE Handbook-HVAC Applications (SI) a = NG⌀ + QiCx + G + (EvPQvCx)/f-knA (3) where N = number of occupants Go = generation rate of contaminant by an occupant, �g/(s·person) Qi = infiltration flow, m3/s Cx = outdoor concentration of contaminant, �g/m3 G = generation rate of contaminant by nonoccupant sources, �g/s Ev = ventilation effectiveness (fraction of supply air passing through bypass boundary zone into occupied space) P = HVAC filter penetration by contaminant, fraction Qv = ventilation airflow, m3/s f = 1 P(1 - Ev) = factor arising from mixing outdoor and recirculated air in the air-handling unit, fraction kn = difference of kd and k、 = net deposition on surfaces for the contaminant, �g/h·m2 A = surface area inside the occupied space on which contaminant can be adsorbed or desorbed, m2 The parameters associated with removal of contaminant from the space are b = QL + Qh + NQo(1 -Po) + (EvQ - Qv)(1 - P)/f+ Qe (4) where QL = leakage (exfiltration) flow, m3/s Inc. ASHRAE, 2019 user. single for Licensed ![image](/image/placeholder) P Q, Cs HVAC Qv M IXED Q RETURN AIR PLENUM Cx BOUNDARY OF ZONE WHERE 1 Ev)Q BYPASS OCCURS (1 Ev)Q QR Go EVQ VOLUME VOF SPACE G KB V,Css WITH Qo TOTAL FUME MIXING HOOD k. 0 Qn g Q OCCUPANT OCCUPANT AS INTERNAL POLLUTION AS FILTER SOURCE AND SINK SOURCES QU A = surface area inside occupied space on which contaminant can be adsorbed or desorbed, m2 V = volume of occupied zone, m3 Css = steady state contaminant concentration in occupied zone, �g/m3 Cs = concentration of contaminant in supply air, �g/m3 Cx = outdoor concentration of contaminant, �g/m3 G = generation rate for contaminant by nonoccupant sources, �g/s Go = generation rate for contaminant by an occupant, �g/(s·person) N = number of occupants Ev = ventilation effectiveness (fraction of supply air passing through bypass boundary zone into occupied space), fraction f = 1 - P (1 - Ev) = factor arising from mixing of outdoor and recirculated air in air- handling unit, fraction ks = contaminant emission rate for occupied zone surfaces, �g/h·m2 kd = contaminant deposition rate for occupied zone surfaces, �g/h·m2 Kn = difference of kd and ks = net deposition on surfaces for contaminant, �g/h·m2 P = HVAC filter penetration by contaminant, fraction Po = fraction of contaminant exhaled from human lung, fraction Q = total supply airflow, m3/s Qe = exhaust airflow, m3/s Qv = ventilation airflow, m3/s Qn = hood airflow, m3/s Qi = infiltration airflow, m3/s QL = leakage (exfiltration) airflow, m3/s Qo = average respiratory airflow for single occupant, m3/s Fig. 1 Recirculatory Air-Handling System with Gaseous Contaminant Modifiers ¦ Qh = hood flow, m3/s ¦ ¦ --- ¦ ¦ N = number of occupants ¦ ¦ Qo = average respiratory flow for single occupant, m3/s ¦ ¦ P 0 = penetration of contaminant through human lung, fraction ¦ ¦ 0 = total flow, m3/s ¦ ¦ Qv = ventilation (makeup) airflow, m3/s ¦ ¦ P = filter penetration for contaminant, fraction ¦ ¦ Qe = exhaust airflow, m3/s ¦ The steady-state contaminant concentration is of interest for both system design and filter sizing. Laying out the equation for the steady- state concentration with all of the parameters, Equation (2), with sub- stitutions of Equations (3) and (4), becomes NGO + QiCx + G + (EvPOvCx)/f-knA (5) C ss QL + Qh + NQo(1 -Po)+ (E,Q-Q,)(1-P)/f+ Qe The following assumptions are made for this model: · No removal of contaminant by HVAC system elements (with the exception of the filter) and ductwork · No contaminant interactions in the air · No removal of contaminants by occupants other than through breathing · Occupied space is perfectly mixed The parameters for this model must be evaluated carefully so that nothing significant is ignored. Leakage flow QL, for example, may include flow up chimneys or toilet vents. It may also help to know how rapidly concentration changes when conditions change suddenly. The dynamic equation for the building in Figure 1 is C⌀ = C ss (Co - Css)e-b0/V + (6) where Ce = concentration in space 0 minutes after a change of conditions V = volume of the ventilated space, m3 Co = concentration in space at time 0 = 0 b = volume per unit time 0 = time with Css given by Equation (2), and b by Equation (4). Reducing air infiltration, leakage, and ventilation air to reduce energy consumption raises concerns about indoor contaminant build- up. A low-leakage scenario may be simulated by letting Qi= QL = Qh = 0. Then the steady-state concentration becomes NG⌀ + G + [(EvPOvCx)/f]+k,A ss NQo(1-Po) + [(EvQ-Qv)(1-P)/f]+le Even if there is no ventilation airflow (Qv = 0), a low-penetration (high-efficiency) gaseous contaminant filter and a high recirculation rate help lower the internal contaminant concentration. In most struc- tures infiltration and exfiltration are never zero. The only inhabited spaces operating on 100% recirculated air are space capsules, undersea structures and vehicles, and structures with life support (to eliminate carbon dioxide and carbon monoxide and supply oxygen). Outdoor air contaminant concentrations and the emission rates of the internal sources are generally unsteady in nature. Buildings may also have multiple rooms within a building zone, with multiple and varying sources of gaseous contaminants and complex room-to-room air changes. In addition, mechanisms other than adsorption may elim- inate gaseous contaminants on building interior surfaces. Nazaroff and Cass (1986) provide estimates for contaminant deposition and emission velocities kd and ks that range from 3 to 600 um/s for surface adsorption only. A worst-case analysis, yielding the highest estimate ofindoor concentration, is obtained by setting the deposition velocity on surfaces to zero. Computer programs (e.g., CONTAM by NIST at www.mist.gov/services.compos/sof/kare/com/ IAQX by US (7) | {}
4f716649-d849-4d45-b782-37adde8f408f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Air Cleaners for Gaseous Contaminants 47.5 Table 2 Example Generation of Gaseous Contaminants by Building Materials ¦ ¦ ¦ Emission Factor Averages (ranges), g/(h·m2) ¦ Emission Factor Averages (ranges), g/(h·m2) ¦ Emission Factor Averages (ranges), g/(h·m2) ¦ Emission Factor Averages (ranges), g/(h·m2) ¦ Emission Factor Averages (ranges), g/(h·m2) ¦ Emission Factor Averages (ranges), g/(h·m2) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Contaminant ¦ CAS Number ¦ Acoustic Ceiling Panels ¦ Carpets ¦ Fiberboards ¦ Gypsum Boards ¦ Paints on Gypsum Board ¦ Particle Boards ¦ ¦ 4-Phenylcyclo-hexene (PCH) ¦ 4994-16-5 ¦ ¦ 8.4 (n.d.-85) ¦ ¦ ¦ ¦ ¦ ¦ Acetaldehyde ¦ 75-07-0 ¦ ¦ 2.8 (n.d.-37) ¦ 9.0 (n.d.-32) ¦ ¦ ¦ 28 (n.d.-55) ¦ ¦ Acetic acid ¦ 64-19-7 ¦ ¦ ¦ 8.4 (n.d.-26) ¦ ¦ ¦ ¦ ¦ Acetone ¦ 67-64-1 ¦ 12 (n.d.-33) ¦ ¦ 35 (n.d.-67) ¦ 37 (n.d.-110) ¦ 35 (n.d.-120) ¦ ¦ ¦ Ethylene glycol ¦ 107-21-1 ¦ ¦ ¦ 140 (n.d.-290) ¦ ¦ 19 (n.d.-190) ¦ 160 (140-200) ¦ ¦ Formaldehyde ¦ 50-00-0 ¦ 5.8 (n.d.-25) ¦ 3.6 (n.d.-41) ¦ 220 (n.d.-570) ¦ 6.8 (n.d.-19) ¦ ¦ 49 (n.d.-97) ¦ ¦ Naphthalene ¦ 91-20-3 ¦ ¦ 11 (n.d.-59) ¦ 3.0 (n.d.-8.2) ¦ ¦ ¦ ¦ ¦ n-Heptane ¦ 142-82-5 ¦ ¦ ¦ 21 (n.d.-53) ¦ ¦ ¦ ¦ ¦ Nonanal ¦ 124-19-6 ¦ 4.9 (1.7-11) ¦ 11 (n.d.-68) ¦ ¦ 10 (n.d.-28) ¦ 3.7 (n.d.-24) ¦ ¦ ¦ Toluene ¦ 108-88-3 ¦ ¦ ¦ 19 (n.d.-46) ¦ ¦ ¦ ¦ ¦ TotalVOC (TVOC)* ¦ N/A ¦ 32 (3.2-150) ¦ 1900 (270-9100) ¦ 400 (52-850) ¦ 15 (n.d.-61) ¦ 2500 (170-6200) ¦ 420 (240-510) ¦ ¦ ¦ ¦ Emission Factor Averages (ranges), g/(h·m2) ¦ Emission Factor Averages (ranges), g/(h·m2) ¦ Emission Factor Averages (ranges), g/(h·m2) ¦ Emission Factor Averages (ranges), g/(h·m2) ¦ Emission Factor Averages (ranges), g/(h·m2) ¦ Emission Factor Averages (ranges), g/(h·m2) ¦ ¦ Contaminant ¦ CAS Number ¦ Plastic Laminates and Assemblies ¦ Non-Rubber- Based Resilient Flooring ¦ Rubber-Based Resilient Flooring ¦ Tackable Wall Panels ¦ Thermal Insulations ¦ Wall Bases (Rubber-Based) ¦ ¦ 1,2,4-Trimethylbenzene ¦ 95-63-6 ¦ ¦ ¦ 210 (n.d.-590) ¦ ¦ ¦ ¦ ¦ 2-Butoxy-ethanol ¦ 111-76-2 ¦ ¦ 2.7 (n.d.-24) ¦ 1.6 (n.d.-24) ¦ ¦ ¦ ¦ ¦ Acetaldehyde ¦ 75-07-0 ¦ ¦ 11 (n.d.-49) ¦ ¦ ¦ ¦ ¦ ¦ Acetone ¦ 67-64-1 ¦ 75 (4.8-150) ¦ 120 (n.d.-830) ¦ ¦ ¦ 12 (1.8-21) ¦ 220 (30-400) ¦ ¦ Butyric acid ¦ 107-92-6 ¦ ¦ 0.51 (n.d.-5.1) ¦ ¦ ¦ ¦ ¦ ¦ Dodecane ¦ 112-40-3 ¦ ¦ ¦ 1.3 (n.d.-20) ¦ ¦ ¦ ¦ ¦ Ethylene glycol ¦ 107-21-1 ¦ ¦ 38 (n.d.-210) ¦ ¦ ¦ ¦ ¦ ¦ Formaldehyde ¦ 50-00-0 ¦ 13 (n.d.-29) ¦ 6.8 (n.d.-79) ¦ ¦ ¦ 5.9 (0.35-14) ¦ 32 (3.6-61) ¦ ¦ Naphthalene ¦ 91-20-3 ¦ ¦ 3.4 (n.d.-14) ¦ 5.6 (n.d.-28) ¦ 6.6 (6.6) ¦ ¦ ¦ ¦ n-Butanol ¦ 71-36-3 ¦ ¦ ¦ ¦ ¦ ¦ 100 (n.d.-200) ¦ ¦ Nonanal ¦ 124-19-6 ¦ ¦ 5.7 (n.d.-19) ¦ 1.4 (n.d.-1 1) ¦ ¦ 1.8 (0.57-4) ¦ ¦ ¦ Octane ¦ 111-65-9 ¦ ¦ ¦ ¦ ¦ ¦ 150 (n.d.-300) ¦ ¦ Phenol ¦ 108-95-2 ¦ 9.4 (4.4-19) ¦ 35 (n.d.-310) ¦ ¦ ¦ ¦ 340 (n.d.-680) ¦ ¦ Toluene ¦ 108-88-3 ¦ ¦ 5.1 (n.d.-12) ¦ ¦ ¦ ¦ ¦ ¦ Undecane ¦ 1120-21-4 ¦ ¦ ¦ ¦ ¦ ¦ 140 (13-270) ¦ ¦ TVOC* ¦ N/A ¦ 160 (6.3-310) ¦ 680 (100-2100) ¦ 15000 (1500-100000) ¦ 270 (100-430) ¦ 7.5 (0.57-26) ¦ 7100 (1200-13000) ¦ Source: CIWMB (2003). n.d. = nondetectable N/A = not applicable *TVOC concentrations calculated from total ion current (TIC) from GC/MS analysis by adding areas of integrated peaks with retention times greater than 5 min, subtracting from sum of area of internal standard chlorobenzene-d5, and using response factor of chlorobenzene-d5 as calibration. Table 3 Example Generation of Gaseous Contaminants by Indoor Combustion Equipment ¦ ¦ Generation Rates, g/kJ ¦ Generation Rates, g/kJ ¦ Generation Rates, g/kJ ¦ Generation Rates, g/kJ ¦ Generation Rates, g/kJ ¦ Typical Heating Rate, kW ¦ Typical Use, h/day ¦ Vented or Unvented ¦ Fuel ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ CO2 124-38-9 ¦ CO 630-08-0 ¦ NO2 10102-44-0 ¦ NO 10102-43-9 ¦ HCHO 50-00-0 ¦ ¦ Typical Heating Rate, kW ¦ Typical Use, h/day ¦ Vented or Unvented ¦ Fuel ¦ ¦ Convective heater ¦ 51 000 ¦ 83 ¦ 12 ¦ 17 ¦ 1.4 ¦ 31 ¦ 4 ¦ U ¦ Natural gas ¦ ¦ Controlled-combustion wood stove ¦ ¦ 13 ¦ 0.04 ¦ 0.07 ¦ ¦ 13 ¦ 10 ¦ V ¦ Oak, pine ¦ ¦ Range oven ¦ ¦ 200 ¦ 10 ¦ 22 ¦ ¦ 32 ¦ 1.0* ¦ U ¦ Natural gas ¦ ¦ Range-top burner ¦ ¦ 65 ¦ 10 ¦ 17 ¦ 1.0 ¦ 9.5/burner ¦ 1.7 ¦ U ¦ Natural gas ¦ *Sterling and Kobayashi (1981) found that gas ranges are used for supplemental heating by about 25% of users in older apartments. This increases the time of use per day to that of unvented convective heaters. Sources: Cole (1983), Leaderer et al. (1987), Moschandreas and Relwani (1989), Sterling and Kobayashi (1981), Traynor et al. (1985), and Wade et al. (1975). EPA at www.cou.gov.air.cea.com/fantation-ood-Ain-ain-air -quality-and-inhalation-exposure-iaqx) are available to handle these calculations. Details on multizone modeling and computational fluid dynamics (CFD) modeling can also be found in Chapter 13 of the 2017 ASHRAE Handbook- -Fundamentals. The assumption of bypass and mixing used in the model pre- sented here can be used to approximate the multiple-room case, because gaseous contaminants are readily dispersed by airflow. Also, a gaseous contaminant diffuses from a location of high con- centration to one of low concentration, even with low rates of tur- bulent mixing. Quantities appropriate for the flows in Equations (2) to (5) are dis- cussed in the Local Source Management and Dilution Through Gen- eral Ventilation sections. Infiltration flow can be approximated by the techniques described in Chapter 16 of the 2017 ASHRAE Hand- book-Fundamentals or, for existing buildings, by tracer or blower- door measurements. ASTM Standard E741 defines procedures for tracer-decay measurements. Tracer and blower-door techniques are given in ASTM (2017); DeFrees and Amberger (1987) describe a variation on the blower-door technique useful for large structures. To assist in understanding how the equations can be applied, an example is included for the steady-state concentration C ss' in this Inc. ASHRAE, 2019 user. single for Licensed | {}
81a5d16c-9609-4af8-ac93-606e044da7a1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 47.6 2019 ASHRAE Handbook-HVAC Applications (SI) Table 4 Gaseous Contaminant Emission Rates, ug/h· unit from Office Equipment ¦ ¦ Desktop Computers ¦ Desktop Computers ¦ Desktop Computers ¦ Desktop Computers ¦ Laptop Computer ¦ Laptop Computer ¦ Laser Printers ¦ Laser Printers ¦ Inkjet Printer ¦ Inkjet Printer ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ Pre-Operational Phase** ¦ Pre-Operational Phase** ¦ Active Operational Phase** ¦ Active Operational Phase** ¦ Pre- Operational Phase ¦ Active Operational Phase ¦ Idle Phase ¦ Active Printing Phase** ¦ Idle Phase ¦ Active Printing Phase ¦ ¦ Ozone ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ (n.d. - 1750)* ¦ ¦ ¦ ¦ Hexamethyl-cyclotrisiloxane ¦ ¦ ¦ ¦ ¦ ¦ ¦ 14.4 ¦ 135.82 ¦ 12.27 ¦ 29.22 ¦ ¦ Octamethyl-cyclotetrasiloxane ¦ 18.48 ¦ (n.d.-35.3) ¦ 8.40 ¦ (n.d.-26.1) ¦ ¦ 1.07 ¦ 5.18 ¦ 116.84 ¦ 2.23 ¦ 4.57 ¦ ¦ Decamethyl-cyclopentasiloxane ¦ 64.16 ¦ (26.8-82.4) ¦ 38.95 ¦ (20.7-84.4) ¦ 14.03 ¦ 24.97 ¦ 2.73 ¦ 113.11 ¦ 0.87 ¦ 1.87 ¦ ¦ Dodecamethyl-cyclobexasiloxane ¦ 171.44 ¦ (66.4-422) ¦ 147.63 ¦ (44.5-240) ¦ 20.19 ¦ 92.93 ¦ ¦ ¦ ¦ ¦ ¦ Tetradecamethyl- cycloheptasiloxane ¦ 26.18 ¦ (9.8-69.1) ¦ 55.94 ¦ (19.7-90.5) ¦ 1.33 ¦ 8.83 ¦ ¦ ¦ ¦ ¦ ¦ Hexadecamethyl- cyclooctasiloxane ¦ 3.09 ¦ (n.d.-8.9) ¦ 25.56 ¦ (7.0-44.7) ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Hexanal ¦ ¦ ¦ ¦ ¦ ¦ ¦ 3.09 ¦ 343.06 ¦ 1.31 ¦ 2.99 ¦ ¦ Octanal ¦ ¦ ¦ ¦ ¦ ¦ ¦ 7.56 ¦ 116.4 ¦ ¦ ¦ ¦ Nonanal ¦ ¦ ¦ ¦ ¦ ¦ ¦ 2.74 ¦ 192.04 ¦ ¦ ¦ ¦ D-Limonene ¦ ¦ ¦ ¦ ¦ ¦ ¦ 0.5 ¦ 69.04 ¦ ¦ ¦ ¦ Toluene ¦ 8.00 ¦ (5.9-10.4) ¦ 46.65 ¦ (22.0-74.0) ¦ ¦ 11.28 ¦ 1.06 ¦ 55.77 ¦ 0.38 ¦ 0.3 ¦ ¦ Ethylbenzene ¦ 5.10 ¦ (0.86-11.4) ¦ 27.21 ¦ (5.7-50.9) ¦ ¦ 0.77 ¦ 0.29 ¦ 70.42 ¦ 0.11 ¦ 0 ¦ ¦ m/p-Xylene ¦ 5.54 ¦ (n.d.-15.1) ¦ 36.97 ¦ (6.2-74.7) ¦ ¦ ¦ 0.45 ¦ 102.19 ¦ ¦ ¦ ¦ o-Xylene ¦ 2.60 ¦ (n.d.-6.4) ¦ 17.61 ¦ (3.5-33.5) ¦ ¦ ¦ 0.22 ¦ 58.51 ¦ ¦ ¦ ¦ Styrene ¦ 7.27 ¦ (2.3-12.5) ¦ 13.21 ¦ (3.4-33.2) ¦ ¦ ¦ 0.68 ¦ 79.97 ¦ 1.36 ¦ 1.24 ¦ ¦ 1,2,3-trimethyl-benzene ¦ 0.42 ¦ (n.d.-1.4) ¦ 3.77 ¦ (1.2-9.1) ¦ ¦ 0.19 ¦ 0.41 ¦ 135.19 ¦ ¦ ¦ ¦ Benzaldehyde ¦ ¦ ¦ 1.88 ¦ (n.d.-7.5) ¦ ¦ ¦ 1.2 ¦ 85.23 ¦ 1.24 ¦ 1.75 ¦ ¦ 1,3-diethyl-benzene, ¦ 0.26 ¦ (0.08-0.53) ¦ 0.66 ¦ (0.46-0.96) ¦ ¦ 0.07 ¦ 0.47 ¦ 104.62 ¦ ¦ ¦ ¦ 2-ethyl-1-Hexanol ¦ 7.04 ¦ (n.d.-12.6) ¦ 13.79 ¦ (5.4-19.8) ¦ 2.22 ¦ 11.65 ¦ 0.98 ¦ 66.66 ¦ 2.26 ¦ 2.11 ¦ ¦ Dodecane ¦ 2.28 ¦ (1.2-3.9) ¦ 3.92 ¦ (1.8-5.3) ¦ 1.87 ¦ 3.53 ¦ 0.24 ¦ 42.68 ¦ ¦ ¦ ¦ Acetophenone ¦ 2.11 ¦ (n.d.-3.7) ¦ 6.51 ¦ (4.9-8.9) ¦ ¦ ¦ 0.9 ¦ 42.02 ¦ 1.93 ¦ 2.18 ¦ ¦ Phenol ¦ 11.83 ¦ (7.0-16.7) ¦ 39.61 ¦ (28.7 -69.1) ¦ 2.25 ¦ 7.6 ¦ 2.03 ¦ 63.85 ¦ 3.12 ¦ 3.19 ¦ ¦ Tridecane ¦ ¦ ¦ ¦ ¦ ¦ ¦ 0.39 ¦ 154.29 ¦ ¦ ¦ ¦ Tetradecane ¦ 6.10 ¦ (2.9-14.2) ¦ 10.85 ¦ (6.0-21.2) ¦ 2.08 ¦ 4.94 ¦ 1.31 ¦ 531.82 ¦ 1.51 ¦ 1.09 ¦ ¦ Pentadecane ¦ ¦ ¦ ¦ ¦ ¦ ¦ 0.52 ¦ 217.51 ¦ 2.41 ¦ 1.73 ¦ ¦ Hexadecane ¦ 3.36 ¦ (1.4-8.0) ¦ 8.35 ¦ (3.9-18.2) ¦ 0.7 ¦ 2.02 ¦ 0.14 ¦ 31.94 ¦ 2.4 ¦ 1.74 ¦ ¦ Source: Modified from Maddalena et *The range of the reported ozone emission rates of laser printers ¦ Source: Modified from Maddalena et *The range of the reported ozone emission rates of laser printers ¦ Source: Modified from Maddalena et *The range of the reported ozone emission rates of laser printers ¦ Source: Modified from Maddalena et *The range of the reported ozone emission rates of laser printers ¦ Source: Modified from Maddalena et *The range of the reported ozone emission rates of laser printers ¦ Source: Modified from Maddalena et *The range of the reported ozone emission rates of laser printers ¦ Source: Modified from Maddalena et *The range of the reported ozone emission rates of laser printers ¦ Source: Modified from Maddalena et *The range of the reported ozone emission rates of laser printers ¦ Source: Modified from Maddalena et *The range of the reported ozone emission rates of laser printers ¦ Source: Modified from Maddalena et *The range of the reported ozone emission rates of laser printers ¦ Source: Modified from Maddalena et *The range of the reported ozone emission rates of laser printers ¦ al. (2011). **The use of "n.d." in place ofa value indicates that no data was available for the minimum of a range Table 5 Emission Rates of Selected Gaseous Compounds from Human Occupants ¦ Contaminant ¦ Contaminant CAS Number ¦ Emission Rate, ug /hr person ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Carbon dioxide ¦ 124-38-9 ¦ 32.8 x 106 ¦ ¦ Carbon monoxide ¦ 630-08-0 ¦ 0.20 x 106 ¦ ¦ Ammonia ¦ 7664-41-7 ¦ 1342 ¦ ¦ Hydrogen sulfide ¦ 7783-06-4 ¦ 119 ¦ ¦ Decamethylcyclopentasiloxane (D5) ¦ 541-02-6 ¦ 3350 ¦ ¦ Acetone ¦ 67-64-1 ¦ 1060 ¦ ¦ Acetic acid ¦ 64-19-7 ¦ 329 ¦ ¦ Isoprene ¦ 78-79-5 ¦ 162 ¦ ¦ Methanol ¦ 67-56-1 ¦ 156 ¦ ¦ Acetaldehyde ¦ 75-07-0 ¦ 114 ¦ ¦ Dodecamethylcyclohexasiloxane (D6) ¦ 540-97-6 ¦ 105 ¦ ¦ 6-Methyl-5-hepten-2-one ¦ 110-93-0 ¦ 99.3 ¦ ¦ Ethanol ¦ 64-17-5 ¦ 94.9 ¦ ¦ Formic acid ¦ 64-18-6 ¦ 48.5 ¦ ¦ Propionic acid/hydroxyacetone ¦ 79-09-4/ ¦ ¦ ¦ 116-09-6 ¦ 40.4 ¦ ¦ ¦ 4-oxopentanal ¦ 626-96-0 ¦ 36.9 ¦ ¦ Octamethylcyclotetrasiloxane (D4) ¦ 556-67-2 ¦ 21 ¦ ¦ Toluene ¦ 108-88-3 ¦ 7.7 ¦ Data compiled from Tang et al. (2016); Tang et al. (2015); and Wang (1975) case, toluene. The example conditions are for an occupied confer- ence room of 6.096 x 12.192 x 3.048 m containing 100 people (the bypass zone above is of undetermined height and does not need to be specified further). The following parameters are used, and the calculation is performed in SI units: A = surface area inside ventilated space on which contaminant can be adsorbed, 260.13 m2 Ev = ventilation effectiveness = 0.8 G = generation rate for contaminant by nonoccupant sources, 0.0 �g/s Go = generation rate for contaminant by an occupant, 0.00639 �g/(s·person) kn = deposition velocity on a for contaminant, 3 ug/h · m2 N = number of occupants, 100 Cx = outdoor concentration of contaminant, 20 �g/m3 P = filter penetration for contaminant, 0.75 P 0 = penetration of contaminant through human lung, 0.5 0 = total flow, 0.8 m3/s Qo = average respiratory flow for a single occupant, 8 L/min = 1.33 x 10-4 m3/s Qv = ventilation (makeup) airflow, 8 L/s · person = 0.008 m3/s; for 100 people, Qv = 0.8 m3/s Using these parameters, the steady-state concentration from Equation (7) becomes Inc. ASHRAE, 2019 user. single for Licensed | {}
4d8ad9d7-e121-481f-a555-3dc23c99fd76 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Air Cleaners for Gaseous Contaminants 47.7 Table 6 Typical U.S. Outdoor Concentration of Selected Gaseous Air Contaminants Inorganic Air Contaminantsa ¦ ¦ ¦ ¦ ¦ Arithmetic Mean Concentration ¦ Arithmetic Mean Concentration ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Inorganic Name ¦ Inorganic Name ¦ CAS Number ¦ Period of Average ¦ �g/m3 ¦ ppb ¦ ¦ Carbon monoxide ¦ Carbon monoxide ¦ 630-08-0 ¦ 1 year (2008) ¦ 2000 ¦ 2 ¦ ¦ Nitrogen dioxide ¦ Nitrogen dioxide ¦ 10102-44-0 ¦ 1 year (2008) ¦ 29 ¦ 15 ¦ ¦ Ozone ¦ Ozone ¦ 10028-15-6 ¦ 3 years (2006-08) ¦ 149 ¦ 76 ¦ ¦ Organic Air Contaminantsb ¦ Organic Air Contaminantsb ¦ Organic Air Contaminantsb ¦ Organic Air Contaminantsb ¦ Organic Air Contaminantsb ¦ Organic Air Contaminantsb ¦ ¦ Name ¦ ¦ Number of ¦ Frequency Detected ¦ Arithmetic Mean Concentration ¦ Arithmetic Mean Concentration ¦ ¦ VOC ¦ CAS number ¦ Sites Tested ¦ (% of Sites) ¦ (ug/m3) ¦ (ppb) ¦ ¦ Chloromethane ¦ 74-87-3 ¦ 87 ¦ 99 ¦ 2.6 ¦ 1.3 ¦ ¦ Benzene ¦ 71-43-2 ¦ 67 ¦ 99 ¦ 3.0 ¦ 0.94 ¦ ¦ Acetone ¦ 67-64-1 ¦ 67 ¦ 98 ¦ 8.6 ¦ 3.6 ¦ ¦ Acetaldehyde ¦ 75-07-0 ¦ 86 ¦ 98 ¦ 3.4 ¦ 1.9 ¦ ¦ Toluene ¦ 108-88-3 ¦ 69 ¦ 96 ¦ 5.1 ¦ 1.4 ¦ ¦ Formaldehyde ¦ 50-00-0 ¦ 99 ¦ 95 ¦ 3.9 ¦ 3.2 ¦ ¦ Phenol ¦ 108-95-2 ¦ 40 ¦ 93 ¦ 1.6 ¦ 0.42 ¦ ¦ m- and p-Xylenes ¦ 1330-20-7 ¦ 69 ¦ 92 ¦ 3.2 ¦ 0.74 ¦ ¦ Ethanol ¦ 64-17-5 ¦ 13 ¦ 92 ¦ 32 ¦ 17 ¦ ¦ Dichlorodifluoromethane ¦ 75-71-8 ¦ 87 ¦ 91 ¦ 7.1 ¦ 1.4 ¦ ¦ o-Xylene ¦ 95-47-6 ¦ 69 ¦ 89 ¦ 1.2 ¦ 0.28 ¦ ¦ Nonanal ¦ 124-19-6 ¦ 40 ¦ 89 ¦ 1.1 ¦ 0.19 ¦ ¦ 2-Butanone ¦ 78-93-3 ¦ 66 ¦ 88 ¦ 1.4 ¦ 0.48 ¦ ¦ 1,2,4-Trimethylbenzene ¦ 95-63-6 ¦ 69 ¦ 87 ¦ 1.2 ¦ 0.24 ¦ ¦ Ethylbenzene ¦ 100-41-4 ¦ 69 ¦ 84 ¦ 0.9 ¦ 0.21 ¦ ¦ n-Decane ¦ 124-18-5 ¦ 69 ¦ 80 ¦ 0.97 ¦ 0.17 ¦ ¦ n-Hexane ¦ 110-54-3 ¦ 38 ¦ 75 ¦ 1.7 ¦ 0.48 ¦ ¦ Tetrachloroethene 4-Ethyltoluene ¦ 127-18-4 622-96-8 ¦ 69 69 ¦ 73 72 ¦ 1.1 0.53 ¦ 0.16 0.11 ¦ ¦ n-Undecane ¦ 1120-21-4 ¦ 69 ¦ 70 ¦ 0.6 ¦ 0.094 ¦ ¦ Nonane ¦ 111-84-2 ¦ 69 ¦ 66 ¦ 0.59 ¦ 0.11 ¦ ¦ 1,1,1-Trichloroethane ¦ 71-55-6 ¦ 66 ¦ 65 ¦ 0.88 ¦ 0.16 ¦ ¦ Styrene ¦ 100-42-5 ¦ 69 ¦ 61 ¦ 0.39 ¦ 0.092 ¦ ¦ Ethyl acetate ¦ ¦ 66 ¦ 58 ¦ 0.43 ¦ 0.12 ¦ ¦ Octane ¦ 141-78-6 111-65-9 ¦ 68 ¦ 56 ¦ 0.44 ¦ 0.094 ¦ ¦ 1,3,5-Trimethylbenzene ¦ 108-67-8 ¦ 69 ¦ 56 ¦ 0.41 ¦ 0.083 ¦ ¦ Hexanal ¦ 66-25-1 ¦ 40 ¦ 53 ¦ 0.65 ¦ 0.16 ¦ aSource: EPA (2009). Note that only statistically viable datasets were used to calculate the national average concentrations, so the numbers may not be fully representative. bSource: EPA (2016b). ss (100) (0.00639) + [(0.8 x 0.75 x 0.8 x 20)/0.85] (100)(0.0001333)(0.5) + [(0.8 x 0.8 - 0.8)(0.25)]/0.85 + 0.8 11.933 3 = 15.7 �g/m 0.759 These calculations can help in determining the space concentra- tion of the contaminant but can also be used in determining changes in filtration to modify that concentration. 3. PROBLEM ASSESSMENT Consensus design criteria (allowable upper limit for any contam- inant) do not exist for most nontoxic chemicals. Chapter 10 of the 2017 ASHRAE Handbook-Fundamentals discusses health effects of gaseous contaminants and explains the various exposure limits used to protect industrial workers indoors. It also provides limited guidance on acceptable indoor air concentrations in commercial buildings and residences. Chapter 1 1 of that volume discusses the nature and non-health-related effects of gaseous contaminants, as well as providing some guidance on measuring their concentrations. Ideally, design for reduction of exposure to gaseous contaminants is based on accurate knowledge of the identity and concentration (as a function of time) of the contaminants and other chemical species that are present, as well as the sources of each contaminant and be- havior of the contaminant in the space. This knowledge may come from estimates of source strength, modeling, direct measurement of the sources, or from direct measurements of the contaminant levels in the indoor air. Unfortunately, definitive assessment is seldom pos- sible, so often careful observation, experience, and judgment must supplement data as the basis for design. For instance, certain molec- ular contaminants may have distinctive odor levels, or have known sources in different geographical regions. Two general design cases exist: (1) ventilation systems in newly constructed buildings for which contaminant loads must be esti- mated or measured, and (2) modification of existing ventilation sys- tems to solve particular problems. For the first case, models, such as described in the section on Gaseous Contaminants, must be used. To estimate the contaminants, identify contaminant-generating activi- ties, estimate and sum the building sources, and identify outdoor air contaminants. Gaps in measured contaminant load data must be filled with estimates or additional measurements. Once contaminant loads are identified, design can begin. To address a particular problem in an existing system, special measurements may also be required to identify the contaminant. Assessing the problem can become an indoor air quality Inc. ASHRAE, 2019 user. single for Licensed | {}
fab67b82-b160-4ce6-95c0-14e910382564 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 47.8 2019 ASHRAE Handbook-HVAC Applications (SI) investigation, which may include building inspection, occupant questionnaires, and local sampling and analysis. The Building Air Quality Guide (EPA 1991) is a useful basic guide for such investiga- tions. Once the contaminant loads are understood, design can begin. Contaminant Load Estimates Valuable guidance on estimating contaminant loads in indus- trial situations is given by Burton (2003). In the 2017 ASHRAE Handbook- -Fundamentals, Chapter 11 discusses sampling and measurement techniques for industrial and nonindustrial environ- ments, and Chapter 12 covers evaluating odor levels. Results of sampling and analysis identify contaminants and their concentrations at particular places and times or over known periods. Several measurements, which may overlap or have gaps in the con- taminants analyzed and times of measurement, are usually used to estimate the overall contaminant load. Measurements are used to develop a time-dependent estimate of contamination in the building, either formally through material balance or informally through experience with similar buildings and contaminates. The de- gree of formality applied depends on the perceived severity of poten- tial effects. 4. CONT AMINANT REDUCTION STRATEGIES Four contaminant reduction strategies may be used to improve the indoor air quality in a building: (1) elimination of sources or reduc- tion of their emissions, (2) local hood usage with exhaust or recircu- lated air cleaning, (3) dilution with increased general ventilation, and (4) general ventilation air cleaning with or without increased venti- lation rates. For indoor contaminant sources, the first three are usu- ally favored because of cost considerations. Reducing concentrations by general air cleaning is more difficult, because it is applied after the contaminants are fully dispersed and at their lowest concentration. the section on Contaminant Removal by Ventilation Air Cleaning discusses the fourth strategy of general ventilation air cleaning in more detail, so it will not be addressed in this section. Elimination or Reduction of Emissions This strategy is the most effective and often the least expensive. For instance, prohibiting smoking in a building or isolating it to lim- ited areas greatly reduces indoor pollution, even when rules are poorly enforced (Elliott and Rowe 1975; Lee et al. 1986). Radon gas levels can be reduced by installing traps in sewage drains, sealing, and subsurface ventilation to prevent entry of the gas (EPA 1987, 1993). Using waterborne materials instead of those requiring organ- ic solvents may reduce VOCs, although Girman et al. (1984) show that the reverse is sometimes true. Substituting carbon dioxide for halocarbons in spray-can propellants is an example of using a rela- tively innocuous contaminant in place of a more troublesome one. Growth of mildew and other organisms that emit odorous contami- nants can be restrained by eliminating or reducing condensation and applying fungicides and bactericides, provided they are registered for the use and carefully chosen to have low offgassing potential. Local Source Management Local source management is more effective than using general ventilation when discrete sources in a building generate substantial amounts of gaseous contaminants. If these contaminants are toxic, irritating, or strongly odorous, local capture and outdoor exhaust is essential. Bathrooms and kitchens are the most common examples. Some office equipment benefits from direct exhaust. Exhaust rates are sometimes set by local codes. The minimum transport velocity required for capturing large particles is larger than that required for gaseous contaminants; otherwise, the problems of capture are the same for both gases and particles. Capture hoods are normally provided with exhaust fans and stacks that vent to the outdoors. Hoods use large quantities of tem- pered makeup air, which requires a great deal of fan energy, so hoods waste heating and cooling energy. Makeup for air exhausted by a hood should be supplied so that the general ventilation balance is not upset when a hood exhaust fan is turned on. Back diffusion from an open hood to the general work space can be eliminated by surrounding the work space near the hood with an isolation enclo- sure, which not only isolates the contaminants, but also keeps unnec- essary personnel out of the area. Glass walls for the enclosure decrease the claustrophobic effect of working in a small space. Increasingly, codes require filtration of hood exhausts to prevent toxic releases to the outdoors. Hoods should be equipped with con- trols that decrease their flow when maximum protection is not needed. Hoods are sometimes arranged to exhaust air back into the occupied space, saving heating and cooling of outdoor air. This prac- tice must be limited to hoods exhausting the most innocuous contam- inants because of the risk of filter failure. Design of effective hoods is described in ACGIH (2013) and in Chapter 33 of this volume. Dilution Through General Ventilation In residential and commercial buildings, the chief use of local source hooding and exhaust occurs in kitchens, bathrooms, and occasionally around specific point sources such as diazo printers. Where there is no local removal of contaminants, the general venti- lation distribution system can sometimes provide contaminant con- centration reduction through dilution. These systems must meet both thermal load requirements and contaminant concentration standards. Complete mixing and a relatively uniform air supply per occupant are desirable for both purposes. The air distribution guide- lines in Chapters 16, 20, and 21 of the 2017 ASHRAE Handbook- - Fundamentals are appropriate for contamination reduction by gen- eral ventilation. Airflow requirements set by ASHRAE Standard 62.1 must be met. When local exhaust is combined with general ventilation, a proper supply of makeup air must balance the exhaust flow for any hoods present to maintain the desired over or underpressure in the building or in specific rooms. Supply fans may be needed to provide enough pressure to maintain flow balance. For instance, clean spaces are designed so that static pressure forces air to flow from cleaner to less clean spaces, and the effects of doors opening and wind pressure, etc., dictate the need for backdraft dampers. Chapter 19 covers clean spaces in detail. 5. CONT AMINANT REMOV AL BY VENTILATION AIR CLEANING If eliminating sources, local hooding, or dilution cannot reduce contaminant concentrations to desired levels, or are only partially effective, the air must be cleaned. Designing an air-cleaning system requires understanding of the capabilities and limitations of the pro- cesses involved. Complete and permanent removal of every contaminant is often not necessary. Intermittent nuisance odors, for instance, can often be managed satisfactorily and economically using a design that shaves the peak to below the odor threshold and then slowly releases the contaminant back into the air, still below the odor threshold. On the other hand, such an approach would be inappropriate for a con- taminant that affected occupants' health. Design goals are discussed at greater length in the section on Air Cleaner System Design. Gaseous Contaminant Removal Processes Many chemical and physical processes remove gases or vapors from air, but those of highest current commercial interest to the HVAC engineer are physical adsorption and chemisorption. The op- erational parameters of greatest interest are removal efficiency, Inc. ASHRAE, 2019 user. single for Licensed | {}
5adfd050-7112-443e-b0dc-a300ca8fef85 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Air Cleaners for Gaseous Contaminants 47.9 ![image](/image/placeholder) , / , / / / , / / , / , MICROPORE MACROPORE Cs SURFACE DIFFUSION IF CB > Cs, NET MASS OF ADSORBATE TRANSFERS FROM GAS STREAM TO SURFACE · DESORPTION OF LOOSELY HELD POLLUTANT MOLECULES OCCURS ADSORBATE SIMULTANEOUSLY WITH / MOLECULES ADSORPTION OR THEREAFTER / CONDENSED IN MICROPORES / / / / / / / / BOUNDARY LAYER CB = CONTAMINANT CONCENTRATION IN AIRSTREAM Cs = CONTAMINANT CONCENTRATION IN DIFFUSION LAYER CLOSE TO MEDIA SURFACE Fig. 2 Steps in Contaminant Adsorption pressure drop, operational lifetime, first cost, and operating and maintenance cost. Other removal processes have been proposed, but currently have limited application in HVAC work, and are only briefly discussed. Physical Adsorption. Physical adsorption is a surface phenom- enon similar in many ways to condensation. Contaminant gas mol- ecules strike a surface and remain bound to it (adsorbed) for an appreciable time by molecular attraction (van der Waals forces). Therefore, high surface area is crucial for effective adsorbents. Sur- faces of gaseous contamination adsorption media are expanded in two ways to enhance adsorption. First, the media are provided in granular, pelletized, or fibrous form to increase the gross surface exposed to an airstream. Second, the media 's surface is treated or activated to develop microscopic pores, greatly increasing the area available for molecular contact. These internal pores account for the majority of available surface area in most commercially available adsorbents. Typical activated alumina has a surface area of 200 to 330 m2 per gram; typical activated carbon has a surface area from 800 to 1600 m2/g. Pores of various microscopic sizes and shapes form minute traps that can fill with condensed contaminant mole- cules. The most common adsorbent granules are millimeter-sized, and the granules are used in the form of packed beds. In general, packed beds composed of larger beaded or pelletized media have slightly lower pressure drops per unit depth of sorbent than those composed of granular or flaked media. On the other hand, the surface area with smaller particles of the adsorbent is more accessible to the contam- inant. Several steps must occur in physical adsorption of a molecule (Figure 2): 1. The molecule is transported from the carrier gas stream across the boundary layer surrounding the adsorbent granule. This occurs randomly, with molecular movement both to and from the sur- face; the net flow of molecules is toward the surface when the concentration of contaminant in the gas flow is greater than at the granule surface. For this reason, adsorption decreases as contam- inant load on the adsorbent surface increases. Very low concen- trations in the gas flow also result in low adsorption rates or even reemission of collected contaminants. 2. The molecules of the contaminant diffuse into the pores to occupy that portion ofthe surface. Diffusion distances are lower and adsorption rates higher for smaller particles of adsorbent. 3. The contaminant molecules are bound to the surface. ![image](/image/placeholder) C C C C SATURATED ADSORPTION ZONE ZONE (MTZ) UNUSED = t3 0 = t. 0 = t, 0 = ち 0 CARBON C。 = UPSTREAM CONCENTRATION C = DOWNSTREAM CONCENTRATION Cb = DOWNSTREAM CONCENTRATION WITH ONLY ADSORPTION ZONE REMAINING Ce = DOWNSTREAM CONCENTRATION WHEN FULLY SATURATED (ESSENTIALLY EQUALS C。) 0 = TIME Fig. 3 Dependence of Contaminant Concentration on Bed Depth and Exposure Time Any of these steps may determine the rate at which adsorption occurs. In general, step 3 is very fast for physical adsorption, but reversible: adsorbed molecules can be desorbed later, either when cleaner air passes through the adsorbent bed or when another con- taminant arrives that either binds more tightly to the adsorbent surface or is present at a much higher concentration. Complete desorption usually requires adding thermal energy to the bed. Providing a sufficient depth of adsorbent and contact time is very important in achieving efficient contaminant removal. When a contaminant is fed at constant concentration and constant gas flow rate through an adsorbent bed of sufficient depth, the gas stream concentration within the bed varies with time 0 and bed depth, as shown in Figure 3. In fixed-bed adsorption, at any given time, the bed can be divided into three zones: (1) the saturated zone containing adsorbent nearly saturated (spent) with the contaminants, (2) the adsorption zone, and (3) a zone with unused adsorbent. Dis- tribution of contaminant in an adsorbent bed is often described in terms of an idealized mass transfer zone (MTZ). Conceptually, all contaminant adsorption takes place in the MTZ. Upstream, the adsorbent is spent and the concentration is equal to the inlet con- centration. Downstream of the MTZ, all contaminant has already been adsorbed. The movement of the MTZ through the media bed is known as the adsorption wave. Though in actuality the front and back of the zone are not sharply defined, for many media/contam- inant combinations the MTZ provides a very useful picture of media performance. The minimum bed depth is based primarily on the length of the mass transfer zone (MTZ), which, at fixed conditions such as tem- perature, partial pressure, and flow rate, is related to the rate of adsorption. The movement of the MTZ through the adsorbent bed can also be graphically represented as a breakthrough curve (Fig- ure 4). When the leading edge of the MTZ reaches the outlet of the bed, the concentration of the contaminant suddenly begins to rise. This is referred to as the breakthrough point. Past the break- through point, the downstream concentration is at less than 0. 1% of the upstream, just as the slope of the curve increases until it reaches an exhaustion point where the bed becomes fully saturated. If the Inc. ASHRAE, 2019 user. single for Licensed | {}
f49ceae7-58df-4072-9452-fdea62980a40 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 47.10 ![image](/image/placeholder) EXHAUSTION (C/Co) POINT DOWNSTREAM POLLUTANT CONCENTRATUNI 11 t2 t3 t4 EXPOSURE TIME BREAKTHROUGH POINT Fig. 4 Breakthrough Characteristics of Fixed-Bed Adsorbents adsorbent bed depth is shorter than the required MTZ, breakthrough will occur almost immediately, rendering the system ineffective. For protection purposes, any contaminant downstream might be too much; for nuisance odors, staying below the odor threshold might be adequate. The interval between these various breakthrough times could be very short, or more significant, depending on contaminant and media. However, not all adsorbent/contaminant combinations show as sharp a breakthrough as in Figure 4. Breakthrough curves can be used to calculate a number of different properties of the adsorbent system such as breakthrough capacity, degree of utiliza- tion, usage rate etc. Multiple contaminants produce more complicated penetration patterns: individually, each contaminant might behave as shown in Figure 4, but each has its own time scale. The better-adsorbing con- taminants are captured in the upstream part of the bed, and the poorer-absorbing are adsorbed further downstream. As the chal- lenge continues, the better-adsorbing compound progressively dis- places the other, meaning the displaced component can leave the adsorbent bed at a higher concentration than it entered. Underhill et al. (1988) and Y oon and Nelson (1988) discuss the effect of relative humidity on physical adsorption. Water vapor acts as a second contaminant, generally present at much higher concentrations than typical indoor contaminants, altering adsorp- tion parameters by reducing the amount of the first contaminant that can be held by the bed and shortening breakthrough times. For solvent-soluble VOCs adsorbed on carbon, relative humidity's effect is modest up to about 50%, and greater at higher percent- ages. On the other hand, chemicals that dissolve in water may experience increased adsorption into the water layer at high rela- tive humidities. Chemisorption. The three steps described for physical adsor- bents also apply to chemisorption. However, the third step in chemisorption involves chemical reactions with electron exchange between the contaminant molecule and the chemisorbent. This ac- tion differs in the following ways from physical adsorption: · Chemisorption is highly specific; only certain contaminant com- pounds will react with a particular chemisorbent. · Chemisorption is not reversible. Once the adsorbed contaminant has reacted, it is not desorbed. However, one or more reaction products, different from the original contaminant, may be formed in the process, and these reaction products may enter the air as new contaminants. · Water vapor often helps chemisorption or is necessary for it, whereas it usually hinders physical adsorption. · Chemisorption per se is a monomolecular layer phenomenon; the pore-filling effect that takes place in physical adsorption does not occur, except where adsorbed water condensed in the pores forms a reactive liquid. Most chemisorbent media are formed by coating or impregnating a highly porous, nonreactive substrate (e.g., activated alumina, zeo- lite, or carbon) with a chemical reactant (e.g., acids, bases, or 2019 ASHRAE Handbook-HVAC Applications (SI) Table 7 Comparison of Physical Adsorption and Chemisorption ¦ Physical Adsorption ¦ Chemisorption ¦ ¦ --- ¦ --- ¦ ¦ Forces operating are weak van der Waal's forces. ¦ Forces operating are similar to those of a chemical bond. ¦ ¦ Heat of adsorption is low (about 20 to 40 kJ mol-1). ¦ Heat of adsorption is high (about 40 to 400 kJ mol-1). ¦ ¦ No compound formation takes place. ¦ Surface compounds are formed. ¦ ¦ Process is reversible; desorption of gas occurs by increasing tempera- ture or decreasing pressure. ¦ Process is irreversible. ¦ ¦ Process does not require any activa- tion energy. ¦ Process requires activation energy. ¦ ¦ Adsorption decreases with increase of temperature. ¦ Adsorption increases with increas- ing temperature. ¦ ¦ Process is not specific in nature: all gases are adsorbed on all solids to some extent, though some com- pounds are adsorbed better than others. ¦ Process is semispecific in nature and occurs only when there is some possibility of compound formation between the gas being adsorbed and the solid adsorbent. ¦ ¦ Process forms a multimolecular layer. ¦ Process forms a unimolecular layer. ¦ ¦ Adapted from www.fachage.com/chelay/prius/comian/Jaingmui/ceon.w ¦ Adapted from www.fachage.com/chelay/prius/comian/Jaingmui/ceon.w ¦ -physical-adsorption-and-chemisorption/ oxidizing chemicals). The reactant will eventually become exhausted, but the substrate may have physical adsorption ability that remains active when chemisorption ceases. General Considerations. Physical adsorption and chemisorp- tion are the removal processes most commonly used in gaseous con- taminant filtration. In most cases, the processes for both involve media supplied as granules, flakes, or pellets, which are held in a retaining structure that allows air being treated to pass through the media with an acceptable pressure drop at the operating airflow. Granular media are traditionally a few millimetres in all dimen- sions, typically on the order of 4 x 6 or 4 x 8 U.S. mesh pellets or flakes. Table 7 summarizes the differences between physical adsorption and chemisorption. Other Processes. Although physical adsorption and chemisorp- tion are the most frequently used, the following processes are used in some applications. Liquid absorption devices (scrubbers) and combustion de- vices are used to clean exhaust stack gases and process gas effluent. They are not commonly applied to indoor air cleanup. Additional in- formation may be found in Chapter 30 of the 2016 ASHRAE Hand- book-HVAC Systems and Equipment. Catalysts can clean air by stimulating a chemical reaction on the surface of the media. Catalytic combustion or catalytic oxidation (CatOx) oxidizes moderate concentrations of unburned hydrocar- bons in air. In general, the goal with catalytic oxidation is to achieve an adequate reaction rate (contaminant destruction rate) at ambient temperature. Reaction products are a concern, because oxidation of VOCs other than hydrocarbons or other reactions can produce unde- sirable by-products such as nitrogen-, sulfur-, and chlorine- containing gases. This technology has been used industrially for years, but its potential use for indoor air cleaning is relatively new. Equipped with custom catalysts and operated at elevated pressures and temperatures, CatOx can be extremely effective at the removal of indoor contaminants, but is not currently cost-competitive in commercial indoor air or HVAC applications, especially if removal of undesirable by-products is required. Availability of waste heat significantly improves CatOx cost competitiveness. CatOx systems have potential application in security and protection applications. Photocatalysis (or photocatalytic oxidation [PCO]) uses light (usually ultraviolet [UV]) and a photocatalyst to perform reduction-oxidation (redox) chemistry on the catalyst's surface as first observed and reported by Fujishima and Honda (1972). The Inc. ASHRAE, 2019 user. single for Licensed | {}
fb07517b-4f73-4a9c-8fe6-a99f4ca4e082 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Air Cleaners for Gaseous Contaminants 47.11 photocatalyst can be granular, bulk, or unsupported, or it can be supported as a thin film on media such as glass, polymer, ceramic, or metal. However, supported photocatalysts are generally used for air treatment. The light sources must emit photons of energy greater than that of the intrinsic band-gap energy E of the photo- catalyst. For example, the photocatalyst titanium dioxide (TiO2) has band-gap energy of 3. 1 eV. For this material, ultraviolet light with wavelengths less than 380 nm has sufficient energy to over- of TiO2. The characteristic chemistry consists of reac- come the Eg tant gases adsorbing onto the photocatalyst, followed by reaction, product formation, and desorption. With appropriate light intensity and sufficiently long residence time, photocatalysis can almost completely oxidize a wide variety of organic compounds such that the exit gas stream contains mostly carbon dioxide and water (Obee and Brown 1995; Obee and Hay 1999; Peral and Ollis 1992; Peral et al. 1997; Tompkins et al. 2005a). In cases of incomplete oxidation, particularly when chlorinated compounds are present as reactants, multiple by-products may be formed (d'Hennezel et al. 1998; Farhanian and Haghighat 2014). ASHRAE research project RP-1134 exhaustively reviewed the literature on UV photocatalysis (Tompkins et al. 2005a, 2005b). Currently, with recent catalyst, lamp, and reactor design devel- opments, UV-PCO can be used as a gas-contaminant removal tech- nology (Chen et al. 2005). A study conducted for an in-duct UV-PCO system utilizing honeycomb monoliths with VOC mix- tures found in indoor air showed single pass VOC removal efficien- cies ranging from 19 to 85%, with the oxidation rates approximately following: alcohols and glycol ethers > aldehydes, ketones, and ter- pene hydrocarbons > aromatic and alkane hydrocarbons > haloge- nated aliphatic hydrocarbons (Hodgson et al. 2005). A time dependent mathematical model has recently been developed to pre- dict the performance of an in-duct PCO air cleaner under realistic indoor conditions (Zhong et al. 2013). In most residential and com- mercial building applications, reduction oflevels is likely to be most effective when the air contaminants can be passed through the UV- PCO filters multiple times. In an HVAC application, the preferred location for a UV-PCO filter is in the return or mixed air, where gas contaminants pass through the filter many times in a given time period. UV-PCO can be an attractive because of its promise of reduced maintenance (no filters and/or adsorption media to main- tain and dispose of periodically) and ability to treat a wide variety of airborne chemicals. Sometimes, the UV-PCO unit is followed by a gas-phase media section that can adsorb any partially oxidized molecules to prevent them from recirculating back into the occupied space (Hodgson et al. 2007). A further extension of UV-PCO being studied is use of UVV (i.e., low-energy UV light with wavelength close to the visible limit of 400 nm) along with UVC (short-wavelength UV light; wavelength of 100 to 280 nm) to generate radicals such as ozone, hydroxyls, and peroxides, which increase contaminant destruction efficiency and hence air-cleaner single-pass efficiency. A down- stream gas-phase media section is necessary in this case to destroy these radicals and prevent them from passing into occupied spaces. Air ionizers (ion generators) may be effective under some cir- cumstances for particulate, VOC, and odor removal. Most ionization technologies are based on the principle of corona discharge (or non- thermal plasma) and can be classified into three categories: needle- point ionization, bipolar ionization, and ozone generators. Air ionization involves the electronically induced formation of positive and/or negative ions, including reactive oxygen species (ROS) that react rapidly with airborne VOCs and particulate species. Manufac- turers of these systems suggest that reactive oxygen species can be present as oxygen radicals, activated oxygen, superoxide or diatomic oxygen, trivalent oxygen, or oxygen cluster ions. Most ionization sys- tems are prone to generate NOx and ozone, which is harmful to humans, and require control systems to maintain ozone levels below safe limits or should be avoided (ASHRAE 2015). There are limited peer-reviewed studies on the effectiveness of ionization systems to remove VOCs and odors in a single pass moving air stream. Ozone is sometimes touted as a panacea for removing gas-phase contaminants from indoor air. However, considerable controversy surrounds its use in indoor air. Ozone is a criteria pollutant and its maximum allowable concentration (8 h time-weighted average [TWA]) is regulated in both indoor (OSHA 1994) and outdoor air (EPA 2016a). Some ozone generators can quickly produce hazardous levels of ozone (Shaughnessy and Oatman 1991). Furthermore, the efficacy of ozone at low concentrations for removing gaseous pollut- ants has not been documented in the literature (Boeniger 1995). Human sensory results obtained in conjunction with a study by Nelson et al. (1993) showed that an ozone/negative ion generator used in a tobacco-smoke environment (1) produced unacceptable ozone levels at the manufacturer's recommended settings, and (2) when adjusted to produce acceptable ozone levels, produced more odor and eye irritation over time than environmental tobacco smoke (ETS). Other work by Nelson (unpublished) has shown the rapid oxidation of NO to NO2 by ozone and only a minor decrease in nicotine concen- trations when ozone is used to "clean" the air. In light of the potential for generating hazardous ozone levels indoors and the lack of scien- tific data supporting its efficacy, using ozone to combat ETS in indoor air is not recommended. In addition, reaction of ozone with both indoor contaminants and building and HVAC surfaces can produce secondary contaminants such as small particles and aldehydes (Mor- rison et al. 1998; Vartiainen et al. 2006; Wang and Morrison 2006). Biofiltration is effective for low concentrations of many VOCs found in buildings (Janni et al. 2001). It is suitable for exhaust air cleaning and is used in a variety of applications including plastics, paper, and agricultural industries and sewage treatment plants. Operating costs are low, and installation is cost-competitive. How- ever, concerns over using uncharacterized mixtures of bacteria in the filter, possible downstream emissions of microbials or chemi- cals, and the risk of unexpected or undetected failure make it unsuit- able for cleaning air circulated to people. Odor counteractants and odor masking products do not remove the contaminant(s) responsible for problem odors from the air; they may apply only to specific odors and have limited effec- tiveness. They also add potential contaminants to the air. 6. EQUIPMENT The purpose of gas-phase filtration equipment is to expose the chosen filtration media or device to the air to be filtered. In most cases, the filtration method uses granular media material, supplied either in bulk, or incorporated into a filter device that can be refill- able or disposable. Typically, the gas filter has a particulate prefilter and afterfilter. The most common retaining structure places the granular media between perforated retaining sheets or screens, as shown in Figures 5A, 5B, 5C, 5D, 5F, and 5H. The perforated retainers or screens must have holes smaller than the smallest particle of the media, and are typically made of aluminum; stainless, painted, plated, or coated steel; plastics; and kraftboard. Figure 51 represents a bonded flat panel filter. Media may also be retained in fibrous filter or other porous sup- port structures, and very fine media can be attached to the surface or within the structure of some particulate filter media, as shown in Figures 5E and 5G. Effect of Media Size. Filtration devices that use small-diameter media generally have higher initial efficiency than the same media in larger particles, because of the larger exposed surface area. Devices that use larger-diameter media generally provide more overall filtration capacity because of the greater mass of media exposed to the air to be filtered. Inc. ASHRAE, 2019 user. single for Licensed | {}
db11556b-60a1-4338-9f8c-7db79d89e2b6 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 47.12 2019 ASHRAE Handbook- -HVAC Applications (SI) ![image](/image/placeholder) 증 WW A. GRANULAR MEDIA TRAY, REFILLABLE OR DISPOSABLE B. GRANULAR MEDIA MODULE, REFILLABLE OR DISPOSABLE ![image](/image/placeholder) ![image](/image/placeholder) F. GRANULAR MEDIA G. E. COMPOSITE MEDIA IN FLANGED UNITARY ADSORBER, DISPOSABLE SERPENTINE CELL, REFILLABLE ![image](/image/placeholder) C. SIDE-ACCESS ADSORBER HOUSING WITH GRANULAR MEDIA TRAYS OR MODULES D. VERTICAL TUBE SYSTEM ADSORBENT-INFUSED PANEL FILTER, H. HONEYCOMB PANEL ABSORBER, 1. BONDED FLAT PANEL DISPOSABLE DISPOSABLE Fig. 5 Sectional and Schematic Views of Typical Physical Adsorbent and Chemisorbent Configurations Equipment Configurations. The typical media-holding devices shown in Figure 5 vary in thickness from 16 mm to as much as 150 mm. Though they can be mounted perpendicular to the airflow (Figure 5A), they more often hold the media at an angle to the air- stream (Figures 5B to 5F) to increase the face area and thereby reduce pressure drop and increase residence time. The honeycomb panels in Figure 5H hold the media in small channels formed by a corrugated spacer material, faced with a plastic mesh material. Though they usually have a low pressure drop, these are often in a holding frame configured at an angle to the airflow, as in Figure 5C. Most of these devices are removed from the airstream, to either be refilled, or replaced. An exception is the vertical tube system, shown in Figure 5D. Itis filled with bulk media, usually from plastic pails or large bags, fed in through top-access hatch(es). Expended media is removed by vacuuming from the same hatches, or from bottom hatches or hoppers. Bypass. Performance of any air cleaner installation is limited by the airflow integrity of the total installation. A 100% efficient filter mounted in a housing that allows unintentional bypass is not truly a 100% efficient filter. Designers should consider the desired overall efficiency and ensure that the housing and filter together meet per- formance goals. One method of detecting significant unintentional bypass is to measure whether the filter achieves its rated pressure drop at full flow; if the pressure drop is low, bypass is likely. 7. AIR CLEANER SYSTEM DESIGN Air cleaner system design consists of determining and sizing the air cleaning technology to be applied, and then choosing equipment with characteristics (size and pressure drop) that can be incorpo- rated into the overall mechanical design. The overall mechanical design may be carried out according to ASHRAE Standard 62.1's IAQ procedure rather than using the ventilation procedure. The gaseous contaminant air-cleaning system designer ideally should have the following information: · A clear goal concerning what level ofair cleaning is needed based on the application · Exact chemical identity of the contaminants present in significant concentrations (not just the ones of concern) · Rates at which contaminants are generated in the space and are transported to air cleaner system. · Rates at which contaminants are brought into the space with out- door air · Time-dependent performance of the proposed air cleaner for the contaminant mixture at concentration and environmental condi- tions to be encountered This information is usually difficult to obtain, though Standard 62.1 's IAQ procedure provides some guidance. The first three items can be obtained by sampling and analysis, but funding is usually not sufficient to carry out adequate sampling except in very simple con- tamination cases. Designers must often make do with a chemical family (e.g., aldehydes). Investigation may allow a rough estimate of contaminant generation rate based on quantity of product used daily or weekly. Experience with the particular application or published guidance (e.g., Rock [2006] for environmental tobacco smoke) can be very helpful. Experimental measurements of air cleaner performance can now be carried out using ASHRAE Standard 145.2 for individual con- taminant gases. Alternatively, performance can be estimated, using Equations (2) to (7), when the exact chemical identity of a contami- nant is known. The chemical and physical properties influencing a contaminant': s removal by air-cleaning devices can usually be ob- tained from handbooks and technical publications. Contaminant properties of special importance are relative molecular mass, normal boiling point at standard temperature and pressure (STP), heat of va- porization, polarity, chemical reactivity, and diffusivity. Air cleaner performance with mixtures of chemically dissimilar compounds is very difficult to predict. Some gaseous contaminants, including ozone, radon, and sulfur trioxide, have unique properties that require design judgment and experience. Inc. ASHRAE, 2019 user. single for Licensed | {}
0eea9f3c-843e-46d7-ae1b-3e92d952b286 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Air Cleaners for Gaseous Contaminants 47.13 ![image](/image/placeholder) CUSTOMER HAS A NEED FOR MOLECULAR FILTRATION SUCH AS FOR: CUSTOMER HAS A NEED FOR MOLECULAR ODOR IAQ - HEALTH FILTRATION SUCH AS FOR: PRODUCT QUALITY ODOR CORROSION IAQ - HEALTH PRODUCT QUALITY CORROSION COMPLETE MOLECULAR CONTAMINATION QUESTIONNAIRE COMPLETE MOLECULAR FEEDBACK/ASSISTANCE CONTAMINATION QUESTIONNAIRE FEEDBACK/ASSISTANCE DO CONTAMINANTS ARE DON'T KNOW HAVE BOILING POINTS NO CONTAMINANTS ABOVE 100°C YES HIGH CONCENTRATION NO (VOCs)? (> 1 PPM)? YES COMMON UNIMPREGNATED DESCRIPTIONS ACTIVATED YES NO CARBON CONTAMINANT CONTAMINANT SOME HIGH FLOW CONTINUOUS? FLOW CONTINUOUS? BOILING AND SOME NO DIESEL OR ENGINE YES (VS SHORT-TERM) (VS INTERMITTENT) EXHAUST LOW BOILING? NO YES "REACTIVE CHEMISTRY" SORBENT-LOADED SORBENT-LOADED BULK MEDIA CLEANING ORDERS, NON-WOVENS NON-WOVENS BLENDED SORBENT FILTERS (AMMONIA) "CARBON SINGLE SORBENT OR MEDIA "CHEMICAL FILTERS" "CHEMICAL FILTERS" IMPREGNATED WITH ACIDS" HIGH FLOW CRITICAL PROBLEM AND VOCs ACIDS (SO2, H2S, HCI, ACIDS HIGH APPLICATION APPLICATION "CARBON HF, ETC.) "CARBON CONCENTRATION "HIGH LOADING/ "HIGH LOADING/ FOOD OR COOKING IMPREGNATED IMPREGNATED HIGH EFFICIENCY ODORS WITH BASES" WITH BASES" DEEP PLEAT" SHALLOW PLEAT" DEEP BED OR "UNIMPREGNATED PANEL + SORBENT DIESEL REACTIVE/ACID DIESEL REACTIVE/ ACTIVATED CARBON" BASES AND VOCs BASES (NH3, AMINES, PLEAT POLISHING GAS, AMMONIA, VOLATILE ACID GAS, VOLATILE "CARBON ETC.) "CARBON ORGANIC COMPOUNDS ORGANIC COMPOUNDS IMPREGNATED IMPREGNATED HIGH FLOW ROOFING TAR WITH ACIDS" WITH ACIDS" PROBLEM NUISANCE "HEGA 653° HIGH CONCENTRATION APPLICATION APPLICATION FORMALDEHYDE AND FORMALDEHYDE "HIGH LOADING/ "LOW LOADING/ VCOs "REACTIVE "REACTIVE DEEP BED FECES OR SULFUR SHALLOW PLEAT" SHALLOW PLEATM CHEMISTRY" CHEMISTRY" OR PANEL ODORS "CARBON DIESEL REACTIVE/ IMPREGNATED LOW FLOW ACID GAS, VOLATILE MISCELLANEOUS WITH BASES" ACIDS, BASES, AND OZONE HIGH ORGANIC COMPOUNDS ODORS PREFILTRATION VOCs "UNIMPREGNATED CONCENTRATION "MULTI-SORBENT" ACTIVATED CARBON" BULK MEDIA OTHER OTHER PANELS CONSULT PRODUCT CONSULT PRODUCT DEVELOPMENT DEVELOPMENT (A) MOLECULAR FILTRATION DECISION TREE Fig. 6 Filtration and Media Selection Methods Finally, design goals must be considered. For a museum or archive, the ideal design goal is total removal of the target contam- inants with no subsequent desorption or release of by-products. For any chemical that may affect health, the design goal is to reduce the concentration to below the level of health concerns. Again, desorp- tion back into the space must be minimized. For odor management, however, 100% removal may be unnecessary, and desorption back into the space at a later time with a lower concentration may be eco- nomical and acceptable. The first step in design is selecting an appropriate physical or chemical adsorption medium. Next, the air cleaner's location in the HVAC system must be decided and any HV AC concerns addressed. Then the air cleaner must be sized so that sufficient media is used to achieve design efficiency and capacity goals and to estimate media replacement requirements. Finally, commercial equipment that most economically meets the needs of the application can be selected. These steps are not completely independent. Media Selection Media selection is clear for many general applications; however, some complex gas mixtures in critical applications may require bench testing to determine if capacity and efficiency values are suit- able for the application. In general, gaseous contaminants that have boiling points greater than 48.9°C and molecular weights over 50 can be removed by physical adsorption using standard activated car- bon. Those with a lower boiling points and molecular weights usu- ally require chemisorption or addition of a catalyst for complete removal. Figure 6 shows the media and filtration selection process. In practice, different uses of the same application may be served well by somewhat different media selections. Any guidance must be (B) MOLECULAR MEDIA DECISION TREE · Competitive adsorption. Multiple contaminants confound per- formance estimates, particularly for physical orbents and perman- ganate media. · Temperature. A temperature increase decreases adsorption in a physical adsorbent, whereas it increases the reaction rates of chemisorbents. · Humidity. For physical adsorbents, the effect of humidity (gen- erally for> 50% rh) depends on the contaminant. Carbon capacity for water-miscible solvents increases; capacity for immiscible or partially miscible solvents decreases. Some humidity is usually required for effective operation of chemisorbents. · Concentration. Increased contaminant concentration improves adsorption for both physical and chemical adsorbents. tempered by consideration of the specifics of a particular location, and guidance given by different manufacturers may differ some- what. Table 8 consolidates general guidance for numerous commer- cial applications from multiple manufacturers. Within each media group, the applications are listed alphabetically; similar applica- tions appear in more than one list, because some applications may be well served with either a single medium or by a blend, with the best choice determined by the specific contaminants present (both chemical identity and concentration). Acceptability may hinge on a specific, hard-to-remove chemical that is present at one site but not at another. Adsorption capacity for a particular chemical or applica- tion may vary from these guidelines with changes in Table 9 provides a general guide to selecting media commonly used to remove particular chemicals or types of chemicals. The media covered are permanganate-impregnated media (PIM), acti- vated carbon (AC), acid-impregnated carbon (AIC), and base- Inc. ASHRAE, 2019 user. single for Licensed | {}
48e92033-9c56-488e-992f-269ad4d3645e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 47.14 2019 ASHRAE Handbook-HVAC Applications (SI) Table 8 Typical Contaminants in Commercial Applications ¦ Commercial Application ¦ Contaminants/Species ¦ ¦ --- ¦ --- ¦ ¦ Activated Carbon or Carbon/Permanganate-Impregnated Media Blend Airport terminals (air side and non-air side), art studios, athletic clubs, auditoriums, banks (customer area), banquet rooms, beauty salons, bus terminals, clinics, darkrooms, decal application, dentists'/doctors' offices, dry cleaners (dust area), factories (office area), florists, grocery stores, kitchen exhausts, locker rooms, office buildings, painted rooms, pharmacies, photo stores, photographic studios, physiotherapy, recreation halls, rendering plants, stores Activated Carbon/Permanganate-Impregnated Media Blend clubs, nurseries, paint shops booths, psychiatric institutions and wards, public toilets, smoking rooms, storage rooms, theaters, waiting rooms Activated Carbon or Permanganate-Impregnated Media Barber shops, dining rooms Carbon/Permanganate Blend or Permanganate-Impregnated Media Embalming rooms, fruit/vegetable storage, greenhouses ¦ Multiple volatile organic gases/solvent vapors and inorganic gases; possibly some gases poorly adsorbed by carbon Multiple organics and inorganics, fumes, food odors, body odors, perfumes, floral scents, odorous fumes, moldy odors, paint fumes, furniture, ETS, NOx, SOx O3, mercaptans, valeric acid, formaldehyde ¦ ¦ Bars, bingo halls, brasseries, cafeterias, casinos, cocktail lounges, conference rooms, correctional facilities, funeral homes, geriatrics, hospitals, hotels (smoking, renovation), ICUs, libraries, lounges, lunch rooms, motels, museums, night (office), penal institutions, projection restaurants, segregated ¦ Mixed gases/ETS; good possibility of volatile organic gases and/ or solvent vapors ETS, body odors, urine, excreta, perfume, multiple odors, food odors, kitchen fumes, food, furniture/furnishings offgassing, multiple organics and inorganics, paint Mixed gases, ETS, food odors Multiple organics; organic gases poorly sorbed by activated carbon Multiple organics, formaldehyde, ethylene ¦ ¦ ¦ ¦ ¦ Fertilizer plants (office) ¦ ¦ ¦ ¦ Largely ammonia ¦ ¦ Activated Carbon Permanganate-Impregnated Media/Acid-Impregnated Carbon Blend ¦ Activated Carbon Permanganate-Impregnated Media/Acid-Impregnated Carbon Blend ¦ ¦ or Garbage disposal areas Permanganate-Impregnated Media Autopsy rooms, banks (vault area), ¦ Mixture of volatile organics and inorganics with ammonia Volatile organic gases poorly adsorbed by activated carbon Formaldehyde, trimethyl amine ¦ ¦ fish markets, hospitals (autopsy), morgues ¦ Mixed organic gases with significant ammonia urine, excreta, animal odors ¦ ¦ Permanganate-Impregnated Media/Acid-Impregnated Carbon Blend Pet shops, animal holding rooms, veterinary hospitals Activated Carbon/Acid-Impregnated Carbon Blend Printing plants Carbon ¦ Mixed hydrocarbons and ammonia ¦ ¦ Acid-Impregnated Notes: Permanganate impregnant is potassium permanganate. Acid impregnants vary. impregnated carbon (BIC). The numeral 1 indicates the best media to use, and 2 the second choice. As was true of Table 6, some difference in opinion exists as to which media is best, and chemicals for which there is disagreement are tagged with an exclamation point. Where information is unavailable, media can be evaluated for their ability to remove specific gases using ASHRAE Standard 145.1. Air Cleaner Location and Other HV AC Concerns Outdoor Air Intakes. Proper location of the outdoor air intake is especially important for applications requiring gaseous contaminant filters because outdoor contaminants can load the filters and reduce their operating lifetime. Outdoor air should not be drawn from areas where point sources of gaseous contaminants are likely: building exhaust discharge points, roads, loading docks, parking decks and ¦ ¦ ¦ ¦ ETS = environmental tobacco smoke · Bypass or partial supply air treatment. Intentional bypass can be achieved with a bypass duct and control damper or by installing an air cleaner in a manner that allows substantial bypass. Partial supply air treatment may be appropriate where a specific threshold contamination level is targeted, when outdoor and indoor contamination rates are known, and the required level of reduction is small to moderate. · Full supply air treatment. Full treatment achieves the best con- taminant concentration reduction, but with the highest cost and largest equipment volume. This approach is most often used in ventilation strategies that reduce outdoor air while maintaining good indoor air quality. When outdoor air quality is adequate, treatment of recircu- ¦ spaces, etc. See Chapter 46 for more information on air inlets. To further help reduce the amount of contaminants from outdoor air, at least on days of high ambient pollution levels, the quantity of outdoor air should be minimized. Air Cleaner Usage. The three principal uses for gaseous con- taminant removal equipment in an HVAC system are as follows: · Outdoor air treatment. Air-cleaning equipment can be located at the outdoor air intake to treat outdoor air only. This treatment is used principally when indoor gaseous contaminant concentra- tions are adequately reduced by outdoor air ventilation, but the outdoor air needs to be cleaned to achieve satisfactory indoor air quality. Note that air-cleaning media performance is a function of the temperature and relative humidity of the incoming air. Prob- lems may arise when outdoor air temperature and relative humidity are either very low or very high. Consult the supplier for advice if the installation is in an extreme climate region. lated ventilation air alone may be adequate to keep indoor con- taminants such as bioeffluents at low levels. Full or bypass treatment of the supply air may be appropriate, depending on the source strength. Sizing Gaseous Contaminant Removal Equipment A number of issues need to be taken into account during equip- ment sizing. These include · Nature of contaminant(s) to be removed · Average and peak concentrations of contaminant(s) · Efficiency of the media used · HVAC considerations, including layout and space available for equipment installation; equipment location; whether air is indoor, outdoor, or supply; and volume airflow and air velocity through the section Inc. ASHRAE, 2019 user. single for Licensed | {}
2272e3dc-09c6-40aa-9aca-a28821d73989 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Air Cleaners for Gaseous Contaminants 47.15 Table 9 Media Selection by Contaminant ¦ Gaseous Contaminant ¦ PIM 1 ¦ AC ¦ AIC BIC ¦ Gaseous Contaminant ¦ PIM ¦ AC AIC ¦ BIC ¦ Gaseous Contaminant ¦ PIM ¦ AC ¦ AIC ¦ BIC ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Acetaldehyde ¦ 1 ¦ 2 1 ¦ ¦ Dichlorofloromethane ¦ ¦ 1 ¦ ¦ Methyl formate ¦ 2 ¦ 1 ¦ ¦ ¦ ¦ Acetic acid (!) ¦ 1 Methylene chloride ¦ 2 ¦ 2,1 ¦ R-114 (see note) ¦ ¦ 1 ¦ ¦ Methyl isobutyl ketone ¦ 2 ¦ 1 ¦ ¦ ¦ ¦ Acetic anhydride (!) ¦ 1,2 ¦ 1 ¦ 2 ¦ Diethylamine ¦ 2 ¦ 1 ¦ ¦ Methyl sulfide ¦ 1 ¦ ¦ ¦ ¦ ¦ Acetone (!) ¦ 1 ¦ 2 ¦ ¦ Dimethylamine ¦ ¦ 1 ¦ 2 ¦ Methyl vinyl ketone ¦ 2 ¦ 1 ¦ ¦ ¦ ¦ Acetylene ¦ 1 ¦ ¦ ¦ Dioctyl phthalate ¦ ¦ 1 ¦ ¦ Naphtha ¦ ¦ 1 ¦ ¦ ¦ ¦ Acrolein ¦ 1 ¦ 2 ¦ ¦ Dioxane ¦ 1 ¦ 2 ¦ ¦ Naphthalene ¦ ¦ 1 ¦ ¦ ¦ ¦ Acrylic acid (!) ¦ 1 ¦ 1 ¦ 2 ¦ Ethanol ¦ 1 ¦ 2 ¦ ¦ Nicotine ¦ 1 ¦ 2 ¦ ¦ ¦ ¦ Allyl sulfide ¦ 1 ¦ 2 ¦ ¦ Ethyl acetate ¦ 2 ¦ 1 ¦ ¦ Nitric acid ¦ ¦ ¦ ¦ 1 ¦ ¦ Ammonia (NH3) ¦ ¦ 1 ¦ ¦ Ethyl chloride (!) ¦ 1,2 ¦ 2,1 ¦ ¦ Nitric oxide (NO) ¦ 1 ¦ ¦ ¦ 2 ¦ ¦ Aniline ¦ 2 ¦ 1 ¦ ¦ Ethylene (C2H4) ¦ 1 ¦ ¦ ¦ Nitrobenzene ¦ ¦ 1 ¦ ¦ ¦ ¦ Arsine ¦ 1 ¦ ¦ ¦ Ethylene oxide ¦ 1 ¦ 2 ¦ ¦ Nitrogen dioxide ¦ 1 ¦ ¦ ¦ 2 ¦ ¦ Benzene ¦ ¦ 1 ¦ ¦ Ethyl ether ¦ 2 ¦ 1 ¦ ¦ Nitromethane ¦ 1 ¦ ¦ ¦ ¦ ¦ Borane (!) ¦ 1 1 ¦ 2,2 ¦ ¦ Ethyl mercaptan (!) ¦ 1,1 ¦ 2 ¦ 2 ¦ Nitrous oxide ¦ ¦ ¦ ¦ 1 ¦ ¦ Bromine ¦ ¦ 1 ¦ ¦ Formaldehyde ¦ 1 ¦ ¦ ¦ Octane (!) ¦ 2 ¦ 1,1 ¦ ¦ ¦ ¦ 1,3 Butadiene ¦ 1 ¦ 2 ¦ ¦ Gasoline ¦ 1 ¦ ¦ ¦ Ozone (03) (!) ¦ 2 2,1 ¦ 1,1 Urea (!) 1 ¦ ¦ ¦ ¦ Butane ¦ ¦ 1 ¦ ¦ General halocarbons ¦ ¦ 1 ¦ ¦ Perchloroethylene ¦ 2 Methyl butyl ketone (!) 1 ¦ 1 1 ¦ ¦ ¦ ¦ 2-Butanone ¦ 1 ¦ 2 ¦ ¦ General hydrocarbons 2,2 ¦ 2 ¦ 1 ¦ ¦ Peroxy acetyl nitrate (PAN) ¦ ¦ 1 Uric ¦ ¦ ¦ ¦ 2-Butoxyethanol ¦ 2 ¦ 1 ¦ ¦ General VOC ¦ 2 ¦ 1 ¦ ¦ Phenol Turpentine ¦ 2 2 1 ¦ 1 ¦ ¦ ¦ ¦ Butyl acetate (!) ¦ 1,2 2 ¦ 2,1 ¦ ¦ Heptane Cyclohexanone ¦ ¦ 1 1,2 ¦ ¦ Phosgene 2 ¦ 2 ¦ 1 ¦ ¦ ¦ ¦ Butyl alcohol ¦ 2 Methylcyclohexane ¦ 1 ¦ ¦ Hydrogen bromide ¦ ¦ 2 Xylene ¦ 1 ¦ Phosphine ¦ 1 ¦ 1,1 ¦ ¦ ¦ ¦ Butyl mercaptan Cyclohexene ¦ 2 ¦ 1 ¦ ¦ Hydrogen chloride Methyl cellosolve acetate ¦ ¦ 2 2 ¦ 1 ¦ Putrescine acid (!) Methylchloroform ¦ 1 ¦ 2 1 ¦ ¦ ¦ ¦ Butylene ¦ 2 ¦ 1 ¦ ¦ Hydrogen cyanide ¦ 1 ¦ ¦ ¦ Pyridine (!) Vinyl chloride ¦ 1 1 ¦ 1 ¦ ¦ ¦ ¦ Butyne ¦ 2 ¦ 1 1 ¦ ¦ Hydrogen fluoride ¦ 1 ¦ ¦ 1 ¦ Skatole ¦ 2 ¦ 1 ¦ ¦ ¦ ¦ Butyraldehyde ¦ 2 ¦ 1 ¦ ¦ Hydrogen iodide ¦ 2 ¦ ¦ ¦ Silane ¦ 1 ¦ ¦ ¦ ¦ ¦ Butyric acid Diborane ¦ ¦ 1 ¦ 2 ¦ Hydrogen selenide ¦ ¦ ¦ ¦ Stoddard solvent ¦ 1 ¦ ¦ ¦ ¦ ¦ Cadaverine ¦ 2 ¦ 1 ¦ ¦ Hydrogen sulfide ¦ 1 ¦ ¦ 1 1 ¦ Stibine ¦ 1 ¦ ¦ ¦ ¦ ¦ Camphor ¦ ¦ 1 ¦ ¦ Iodine ¦ ¦ 1 ¦ ¦ Styrene (!) ¦ 2 ¦ 1,1 ¦ ¦ ¦ ¦ Carbon dioxide (CO2) ¦ Carbon ¦ ¦ w/catalyst ¦ Iodoform ¦ 2 ¦ 1 ¦ ¦ Sulfur dioxide ¦ 1 1 ¦ ¦ ¦ 1 ¦ ¦ Carbon disulfide ¦ 2 ¦ 1 ¦ ¦ Isopropanol ¦ 2 ¦ 1 ¦ ¦ Sulfur trioxide ¦ 1 ¦ ¦ ¦ 1 ¦ ¦ Carbon monoxide (CO) ¦ Carbon ¦ ¦ w/catalyst ¦ Kerosene ¦ ¦ 1 ¦ ¦ Sulfuric acid ¦ ¦ 2 ¦ ¦ 1 ¦ ¦ Carbon tetrachloride ¦ ¦ 1 ¦ ¦ Lactic acid ¦ ¦ 1 ¦ ¦ Toluene ¦ ¦ 1 ¦ ¦ ¦ ¦ Chlorine (Cl2) ¦ ¦ ¦ 1 ¦ Menthol ¦ 2 ¦ 1 ¦ ¦ Triethylamine ¦ ¦ 2 ¦ 1 ¦ ¦ ¦ Chloroform ¦ ¦ 1 ¦ ¦ Mercury vapor ¦ ¦ Impregnated AC ¦ ¦ Trichlorethylene ¦ ¦ 1 ¦ ¦ ¦ ¦ Creosote (!) ¦ 1,2 ¦ 2,1 ¦ ¦ Methanol ¦ 2 ¦ 1 ¦ ¦ 1,1,1, trichloroethane (!) ¦ 1 ¦ 2,1 ¦ ¦ ¦ ¦ Cyclohexane ¦ 2 ¦ 1 ¦ ¦ Methyl acrylate Methyl bromide (!) ¦ 2 2,1 Decane ¦ 1 1 ¦ ¦ R-11 (see below) ¦ ¦ 1 1 ¦ ¦ ¦ ¦ Cyclohexanol Dichlorobenzene ¦ ¦ 1 1 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 1 = primary media selection for contaminant; 2 = secondary media selection. PIM = permanganate-impregnated media; AC = activated carbon; AIC = acid-impregnated carbon; BIC = base-impregnated carbon R-114 is dichlorotetrafluoroethane; R-11 is trichlorofluoromethane. The more undesirable the contaminant of concern, and the greater its concentration, the greater the quantity of media required for removal, and the larger the air cleaner installation. Media effi- ciency depends on the residence time of contaminant(s) in the air cleaner, which in turn depends on media bed depth and HVAC air velocity. There are two common sizing approaches: testing and calculations with Equations (2) to (7), or following manufacturers' guidance. Available Test Methods and Equations. ASHRAE Standard 145.1 provides a method for testing granular media at small scale in a laboratory, and can be used to compare media performances against specific contaminants. ASHRAE Standard 145.2 provides a method of testing a 0.6 x 0.6 m filter under laboratory conditions and can supply more direct evaluation of potential air cleaning installations. Equations (2) to (7) can be used to size equipment, Comments: Some contaminant molecules have isomers that, because they have different physical properties (boiling point, vapor pressures), require different treatment methods. For some contaminants, preferred treatment is ion exchange or another (nonlisted) impregnated carbon. For some contaminants, manufacturer recommendations differ. "!"is used to identify these cases. though the contaminant concentration data required to use the equa- tions effectively may be difficult to obtain. General procedures for developing a specification for an air cleaner installation are as follows: 1. Choose a physical or chemical adsorbent suited to the contami- nant(s) using testing or taking guidance from Tables 6 and 7. 2. Pick an appropriate efficiency for the adsorbent (complete re- moval or partial bypass), depending on the contaminant(s). 3. Choose a desired operating adsorbent end point of 10%, 50%, or other breakthrough, depending on the application and allowable steady-state concentration. A building ventilation performance model, with the adsorber appropriately positioned, allows calcu- lation of the expected indoor concentration at various break- throughs and efficiencies. Inc. ASHRAE, 2019 user. single for Licensed | {}
62c4a8c4-2dc7-4ce8-adff-09b1e3dc63d0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 47.16 4. Obtain a measurement or estimate ofbreakthrough time at adsor- bent use conditions as developed in step 3. 5. Determine the change-out rate for the adsorbent as set by the breakthrough time. 6. Match the computed design requirements to available air cleaning equipment and specify. Manufacturers' Design Guidance. Most manufacturers of air- cleaning system components offer selection guidance. Some of the approaches for traditional granular beds are summarized here. Note that inclusion of this information or exclusion of other approaches does not imply acceptance or endorsement by ASHRAE, but is meant to be an abbreviated overview of present-day practice. The general expectation is of an HVAC application service life of9 to 18 months for a 3120 h air-conditioning year. These values are simply a summary of conventional wisdom directed at meeting that goal, and they can be substantially in error. Manufacturers with laboratory testing facilities may evaluate and specify filters by measuring the initial removal efficiency of the whole filter installed in its frame (similar to the ASHRAE Standard 145.2 test), and measure the amount of contaminant removed as adsorbent capacity is consumed during the test. Curves of efficiency versus capacity are used to guide the customer through the selection process. In situations where multiple contaminants at low concentrations occur, such as in most IAQ investigative work and applications, nei- ther the total load nor specific contaminant can typically be deter- mined. In these cases, a broad-based air-cleaner design approach is usually recommended, consisting of two media banks: activated carbon, followed by permanganate-impregnated media. Sometimes these two media are combined into one bank because of space or pressure drop limitations. · For light-duty applications, the recommendation is to use partic- ulate filter media infused with carbon and/or permanganate media and pleated into a traditional filter design. · For medium-duty applications, granular media are used in 25 to 75 mm deep refillable or disposable bulk-fill modules for increased efficiency and service life. A useful approach for carbon-based air cleaners divides HVAC and IAQ applications into three categories and recommends spe- cific equipment selection based on efficiency and activated carbon mass, as follows: 1. Heavy-duty outdoor air or mixed air IAQ applications with a relatively constant VOC generation rate and relatively constant moderate to severe outdoor air pollution: · For cleaned-air-equivalent air quality (i.e., air cleaned well enough to substitute for outdoor air), use equipment with >90% efficiency and 34 to 45 kg of high-grade carbon per 0.94 m3/s. For a 25 mm bed in common commercial unitary adsorbers, this corresponds to a 0.1 s residence time. · With severe outdoor air pollution from nearby sources, it may be necessary to size equipment at 41 kg of carbon per 0.47 to 0.66 m3/s, which corresponds to 0.14 to 0.2 s residence time. 2. For medium-duty return or mixed-air IAQ applications with con- stant low to moderate VOC generation and cleaned-air- equivalent air quality, use equipment efficiencies of 20 to 90% and 4 to 34 kg of carbon per 0.94 m3/s. This corresponds to par- tial bypass equipment at the low-efficiency end and ranges up to about 0.08 s residence time at the high-efficiency end. 3. For light-duty mixed-air IAQ applications with intermittent low to high VOC generation and an intermittent low to high outdoor air pollution load, use equipment efficiencies of >75% for odor management, which corresponds to a partial bypass design. 2019 ASHRAE Handbook-HVAC Applications (SI) Table 10 Suggested Mesh 4.8 x 3.4 or 4.8 x 2.4 mm Coconut Shell Carbon Residence Time Ranges ¦ Application ¦ Residence Time,a s ¦ ¦ --- ¦ --- ¦ ¦ HVAC odor management applications for indoor air quality ¦ HVAC odor management applications for indoor air quality ¦ ¦ Light duty recirculation ¦ 0.03 to 0.07 ¦ ¦ Light duty - medium duty ¦ 0.07 to 0.10 ¦ ¦ Heavy duty ¦ 0.06 to 0.14 ¦ ¦ Cleanroom corrosion reduction ¦ Cleanroom corrosion reduction ¦ ¦ Recirculation ¦ 0.03 to 0.07 ¦ ¦ Intakes ¦ 0.03 to 0.14 ¦ ¦ Industrial corrosion reduction (refineries, wastewater, pulp, etc.) ¦ 0.12 to 0.28+ ¦ ¦ Corrosive/reactive low-level exhaust applications ¦ 0.12 to 0.28+ ¦ ¦ Toxic gas removal ¦ Not applicable ¦ ¦ Museums ¦ Museums ¦ ¦ Standard applications ¦ 0.07 to 0.12 ¦ ¦ Recirculation applications ¦ 0.06 to 0.10 ¦ ¦ Critical air intake ¦ 0.28+ ¦ ¦ Critical recirculation application ¦ 0.12 to 0.28+ ¦ ¦ Nuclear applicationsb ¦ 0.12 to 0.28+ ¦ Notes: aAll residence times given are rules of thumb using 4.8 x 3.4 or 4.8 x 2.4 mm mesh carbon in granular beds for the application indicated. Other carbon packages, such as pleated filters containing finely divided carbon, may be dramatically different. Particularly at low (�L/m3) contaminant concentrations, well-designed pleated carbon filters can be very efficient and have adequate capacity. bNuclear Grade Carbons are most often an 8 x 16 mesh Source: Data from Ⓒ1992 Extraction Systems, Inc. Another form of manufacturer's guidance of activated carbons is shown in Table 10, which gives suggested packed-bed residence time ranges, developed for the 4.8 x 3.4 or 4.8 x 2.4 mm mesh coco- nut shell carbon typically used in packed beds, for various applica- tions. Mesh size is frequently used to specify granular media. The mesh size is closely related to the U.S. sieve size (the smallest sieve that the granule will pass through), and inversely related to the dimensions of the granule. A table with more information can be found in Chapter 11 of the 2017 ASHRAE Handbook- Fundamentals. Residence times in Table 9 are appropriate for mod- erate to thick beds of large-particle carbons, but do not apply uni- versally to commercial adsorbents. Different ways of arranging the carbon, different adsorbents, or different carbon granule sizes change the residence time required to get a particular result. This is especially true of very finely dispersed activated carbon, which has very fast adsorption kinetics. In addition, the geometry and packaging of some adsorbent technologies make computation of residence time difficult. For instance, cylindrical beds with radial flow have air velocities that decrease from the center to the periphery, so special computational techniques are needed to put residence time on the same basis as for a flat bed. Similarly, the flow pattern in pleated fiber/carbon composite media is difficult to spec- ify, making residence time computation uncertain. Therefore, although residence times can be computed for partial-bypass filters, fiber-adsorbent composite filters, or fiber-bonded filters, they cannot be compared directly with those in Table 9, and serve more as a rating than as an actual residence time. By applying residence time as a rating, manufacturers may publish equivalent residence time values that say, in effect, that this adsorber performs the same as a traditional deep bed adsorber. No standard test exists to verify such a rating. A test can be performed per ASHRAE Standard 145.1 to compare filters (e.g., fiber-bonded filters to a granular adsorber) and determine what is best suited for an application. Inc. ASHRAE, 2019 user. single for Licensed | {}
51c10a7f-7dea-423f-9861-fd9aed8913a4 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Air Cleaners for Gaseous Contaminants 47.17 Special Cases Ozone reaches an equilibrium concentration in a ventilated space without a filtration device. It does so partly because ozone molecules react in air to form oxygen, but also because of reactions with people, plants, ductwork, and materials in the space. This oxi- dation is harmful to all four things, and therefore natural ozone decay is not a satisfactory way to remove ozone, except possibly at low concentrations (<0.2 mg/m3). Fortunately, activated carbon adsorbs ozone readily, both reacting with it and catalyzing its con- version to oxygen. Radon is a radioactive gas that decays by alpha-particle emis- sion, eventually yielding individual atoms of polonium, bismuth, and lead. These atoms form ions, called radon daughters or radon progeny, which are also radioactive; they are especially toxic, lodging deep in the lung when radon is inhaled, where they emit alpha and beta particles that are potentially cancer causing. Radon progeny, both attached to larger aerosol particles and unattached, can be captured by particulate air filters. Radon gas itself may be removed with activated carbon, but in HVAC systems this method costs too much for the benefit derived. Reduction of radon emission at the source by sealing entry points or depressurizing the source location like subslab ventilation are the accepted methods of reducing exposure to radon. Museums, libraries, archives, and similar applications are special cases of air cleaner design for protection, and may require very efficient air cleaning; see Chapter 24 for specifics. Building protection applications, whether to protect occupants against industrial accidents or deliberate acts, cannot reasonably stand alone. It makes little sense to design a complex system that can be easily overcome by physical acts. Air cleaner design alone is not enough. Air cleaning must be part of a complete and in-depth IAQ pro- gram. The designer must have a scenario or series of scenarios against which to design protective systems. Because a given air-cleaning technology may not protect against all challenges, protection against deliberate acts requires a robust design. The air-cleaning technology can be chosen to protect against the most challenging contaminant. Once the challenge contaminants are identified, a more rigorous application of the design method described previously is applied. Military specification hardware is generally suitable, although high-end commercial designs can pro- vide significant protection. Testing of the installed filters is gener- ally required, maintenance costs are significant, and the cost in space allocated to the installation, energy, and capital is high. U.S. government guidance for the designer is available online (FEMA 2003a, 2003b; NIOSH 2002, 2003). The FEMA web site also includes a number of other applicable documents. For addi- tional guidance, see Chapter 60. Energy Concerns Pressure drop across the contaminant filter directly affects energy use. Data on the resistance of the filter as a function of airflow and on the resistance of the heating/cooling coils must be provided by the manufacturer. If no information is available, ASHRAE Standard 145.2 provides a procedure for measuring pressure drop across a full- scale gaseous air cleaner in a laboratory setting. In addition to the gaseous contaminant filter itself, pressure drop through the housing, any added duct elements, and any particulate filters required up- and/ or downstream of the gaseous contaminant filter must be included in the energy analysis. Choosing between using outdoor air only and outdoor air plus filtered recirculated air is complex, but can be based on technical or maintenance factors, convenience, economics, or a combination of these. An energy-consumption calculation is useful. Replacing out- door air with filtered indoor air reduces the amount of air that must be conditioned at an added expense in recirculation pressure drop. Out- door air or filtered recirculated air may be used in any ratio, provided Table 11 Items Included in Economic Comparisons Between Competing Gaseous Contaminant Removal Systems ¦ Capital Costs ¦ Operating Costs ¦ ¦ --- ¦ --- ¦ ¦ Added filtration equipment ¦ Replacement or reactivation of gaseous ¦ ¦ Fan ¦ contaminant filter media ¦ ¦ Motor ¦ Disposal of spent gaseous contaminant ¦ ¦ Sensors and controls ¦ filter media ¦ ¦ Plenum ¦ Added electric power ¦ ¦ Spare media holding units ¦ Maintenance labor ¦ ¦ Floor or duct space ¦ ¦ the air quality level is maintained. Janssen (1989) discusses the logic of these requirements. Where building habitability can be maintained with ventilation alone, an economizer cycle is feasible under appropriate outdoor conditions. However, economizer mode may not be feasible at high humidity, because high humidity degrades the performance of carbon adsorbents. Economic Considerations Capital and operating costs for each competing system should be identified. Chapter 38 provides general information on performing an economic analysis. Table 1 1 is a checklist of filtration items to be considered in such an analysis. It is important that the fan maintain adequate flow and overcome the pressure drop with an in-line air cleaner in place. If a larger blower is required, space must be avail- able. Modifying unitary equipment that was not designed to handle the additional pressure drop through air-cleaning equipment can be expensive. With built-up designs, the added initial cost of providing air cleaners and their pressure drop can be much less because the increases may be only a small fraction of the total. The life of the adsorbent media is very important. The economic benefits of regenerating spent carbon should be evaluated in light of the cost and generally reduced activity levels of regenerated mate- rial. Regeneration of impregnated carbon or any carbon containing hazardous contaminants is never permitted. Spent alumina- or zeolite-based adsorbents also cannot be regenerated. 8. SAFETY Gaseous contaminant removal equipment generally has a low hazard potential. Contaminant concentrations are low, temperature is moderate, and the equipment is normally not closed in. Alumina- or zeolite-based media do not support combustion, but carbon filter banks have been known to catch fire, usually from an external source such as a welder's torch. Check local codes and fire author- ities for regulations on carbon. One authority requires automatic sprinklers in the duct upstream and downstream of carbon filter banks. As a minimum, a smoke detector should be installed down- stream of the filter bank to shut down the fan and sound an alarm in case of fire. Access for safe maintenance and change-out of adsorbent beds must be provided. Physical and chemical adsorbent filters are both much heavier than particulate filters. Suitable lifting equipment must be available during installation and removal to prevent injury. At some point, granular activated carbon (GAC) becomes ex- hausted, and it is necessary to rebed the media. Depending on how the GAC was used, it may be considered nonhazardous and can be removed by the user or a service company. Hazardous media may be toxic, ignitable, corrosive, or reactive; see guidelines in 40 CFR 261 (2012; www.ecfr.gov). It is the responsibility of the generator to determine the nature of the spent carbon waste. A carbon profile should be performed to characterize it as either hazardous or nonhazardous. A spent carbon profile is required to ensure that the spent carbon is safely recycled Inc. ASHRAE, 2019 user. single for Licensed | {}
ed6fb87a-026e-43e2-b6e6-1172479ac7ac | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 47.18 2019 ASHRAE Handbook- -HVAC Applications (SI) or disposed of in compliance with federal, state, and local regula- tions. Disposal of hazardous waste is governed by Resource Con- servation and Recovery Act (RCRA; www .epa.gov/rcra). If adsorbent trays are to be refilled on site, safety equipment must be provided to deal with the dust this generates. Hood usage, dust masks, and gloves are all required to refill adsorbent trays from bulk containers. 9. INSTALLATION, START-UP, AND COMMISSIONING This section provides general guidance on installing gaseous con- taminant removal equipment. Manufacturers can provide complete installation details and drawings. Following the manufacturer's in- structions will ensure that the equipment is installed properly and that it operates as designed. Particulate Filters. Physical adsorbents and chemisorbents cannot function properly if their surfaces are covered and their pores clogged with particulate matter. UV-PCO system perfor- mance is also degraded unless protected by prefilters. A particu- late filter with a minimum efficiency reporting value (MER V) of at least 8 (per ASHRAE Standard 52.2) should be installed ahead of the adsorbent bed to capture dirt and dust and to allow the adsor- bent to capture gas-phase contaminants. W eschler et al. (1994) reported that carbon service life for ozone removal was length- ened by using an improved prefiltration. A secondary, higher- efficiency particulate filter is often desirable in critical and dusty installations. If the air is extremely dirty (e.g., from diesel exhaust or fumes), the filter should have a much higher efficiency rating. A minimum of a MERV 14 particulate filter is recommended for such applications. Final filters downstream of the installation are often used in crit- ical applications where dust from media at start-up is likely, or where vibration of the adsorbent bed may cause granular media to shed particles. These filters should have a minimum MERV 8 rating, but as noted, a secondary and/or higher-efficiency filter may be needed in some applications. Consult the equipment manufac- turer for their recommendation. Equipment Mass. Physical and chemical adsorption equipment is much heavier than particulate filtration equipment, so supporting structures and frames must be designed accordingly. A typical filter with a face area of 610 by 610 mm consisting of a permanent holding frame and sorbent media can have an installed mass of ap- proximately 14 to 182 kg, depending on its depth and configuration. The manufacturer can provide system weights for the selected equipment. Minimize or Eliminate Unintentional Bypass. Unintentional bypass can degrade the installed performance of a gas filter. Adsor- bent beds and ducts must be tightly sealed to prevent bypass of con- taminants. Before installation, and periodically during operation, visually inspect filters and replace any that are damaged. Install the filter according to the airflow direction indicated. Check to be sure that filters are properly seated and to ensure that the bank of filter frames is rigid and reinforced to avoid collapse. It is good practice to caulk all seams between individual holding frames. Granular media settles and compacts over time, and trays or modules must be loaded with media and installed following manufacturers' recom- mendations to eliminate bypass through the media bed. In addition, ensure that all doors, seams, and joints downstream ofthe adsorbent bed are properly sealed to prevent contaminated air from entering the system. When to Install Media. Proper timing for installing adsorbent beds in their holding frames depends on building circumstances. If they are installed at the same time as their holding frames and if the HVAC is turned on during the latter phases of construction, the adsorbents will adsorb paint and solvent vapors and other contaminants before the building is ready for occupancy. In some situations, adsorption of vapors and gases in the ventilation system before official start-up may be desired or needed. However, adsor- bent life will be reduced correspondingly. If sorbent media are not used until the building is ready for occupancy, the unremoved con- taminants may seriously reduce the initial indoor air quality of the building and the usable life of the bed. Thus, shortened life is an acceptable trade-off for the quality of air at the time of occupancy (NAFA 2012). Ifthe media is not in place during fan testing, the test and balance contractor must be instructed to place blank-offs or restrictions in the frames to simulate adsorbent bed pressure drop. Gas-phase adsorbents typically can have significant pressure drop, and failing to account for this detail will negatively affect fan air- flow. The specifications should clearly state when media are to be installed. Pressure Gages. If upstream filtration is adequate, adsorbent pressure drop will not increase during normal operation, unless media settling and compacting occurs. A pressure gage is therefore not normally needed for a particulate filter bank. However, a gage can be useful to detect fouling or unintentional bypass. If the prefil- ters or final filters are installed immediately adjacent to the adsor- bents, it may be more feasible to install the gage across the entire assembly. Provision for Testing. At any time after installation of new media, determining the remaining adsorbent capacity or operating life may be required. (See the section on When to Change Media in under Operation and Maintenance.) The installation should provide access ports to the fully mixed airstream both up- and downstream of the air cleaner. If media samples will be removed to determine remaining life of the gas filter, access must be provided to obtain those samples. Start-Up and Commissioning Special procedures are not required during start-up of an air han- dler with installed gaseous contaminant air cleaners. The testing and balancing contractor normally is required to measure and record resistance of all installed filter banks, including adsorbers, for comparison with design conditions. Refer to manufacturers' instructions. The commissioning authority may require an activity test on a random sample of media to determine if the new media meets spec- ifications or suffered prior exposure that reduced its life. An in situ air sampling test may also be required on the adsorbent; however, no standard method for this test exists. See Chapter 44 for more on commissioning. 10. OPERA TION AND MAINTENANCE Bypass units and filters with adsorbent-infused fibrous media require frequent changing to maintain even low efficiency, but fre- quent maintenance is not required for complete removal units. Com- plete removal media units usually have a replaceable cell that cannot be regenerated or reactivated. This section covers maintenance of complete removal equipment with refillable trays or modules only. When to Change Media The changeout point of physical and chemical adsorbent is diffi- cult to determine. Sometimes media are changed when break- through occurs and occupants complain; but if the application is sensitive, tests for estimated residual activity may be made period- ically. A sample ofthe media in use is pulled from the adsorbent bed or from a pilot cell placed in front of the bed. The sample is sent to the manufacturer or an independent test laboratory for analysis, and the changeout time is estimated knowing the time in service and the life remaining in the sample. Inc. ASHRAE, 2019 user. single for Licensed | {}
4f15437c-3ca8-45cf-ae6d-744ddf641b02 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Air Cleaners for Gaseous Contaminants 47.19 In corrosion control installations, specially prepared copper or silver coupons are placed in the space being protected by the adsor- bent. After some time, usually a month, the coupons are sent to an analytical lab for measurement of corrosion thickness, which indi- cates the effectiveness of the gaseous contaminant removal and pro- vides an indication of system life. A standardized methodology for these tests is described in Instrument Society of America (ISA) Standard 71.04. Replacement and Reactivation Regeneration of granular media is not the same as reactivation (regeneration), which is the process of restoring spent activated car- bon media to its original efficiency (or close to it). In some unit operations, in some industrial applications (e.g., pressure swing adsorption), spent carbon is regenerated in special high-temperature vessels in the absence of oxygen to drive off contaminants. Chemisorber modules can be replaced (or media changed), however chemisorber media cannot be regenerated. Building operating personnel may choose to dump and refill trays and modules at the site after replacing those removed with a spare set already loaded with fresh media. They may also choose to dump the trays locally and send the empty trays to a filter service company for refilling, or they may simply exchange their spent trays for fresh ones. Disposing of spent sorbent by dumping must be lim- ited to building air quality applications where no identifiable haz- ardous chemicals have been collected. 11. ENVIRONMENTAL INFLUENCES ON AIR CLEANERS Environmental conditions, particularly temperature and humid- ity, affect the performance of most gaseous contaminant removal equipment. Physical adsorbents such as activated carbon are partic- ularly susceptible. The user should confirm performance for any air- cleaning device at the expected normal environmental conditions as well as at extremes that might be encountered during equipment outages. The following information is an overview. High relative humidity in the treated airstream lowers efficiency of physical adsorbers, such as carbon, because of competition for adsorption sites from the much more numerous water molecules. Often, performance is relatively stable up to 40 to 50% rh, but some compounds can degrade at higher humidities. Both the chemical nature of the contaminant(s) and the concentration affect perfor- mance degradation as a function of relative humidity. On the other hand, very low relative humidities may make some chemisorption impossible. Therefore, media performance must be evaluated over the expected range of operation, and the relative humidity and tem- perature of the gaseous contaminant removal system should be held within design limits. The effect of relative humidity swings can be better understood by considering a hypothetical physical adsorbent with a saturation capacity for a contaminant of 10% at 50% rh and 5% at 70% rh. Over an extended period at its normal operating condition of 50% rh, the sorbent might reach a loading of2%. At this point a humidity swing to 70% rh would not cause a problem, and the adsorbent could load up to 5% capacity. Should the humidity then swing back to 50%, the adsorbent could continue to adsorb up to 10% by mass of the contaminant. However, ifthe adsorbent were loaded to 8% by mass at 50% rh and the humidity rose to 70% rh, the carbon would be above its equilibrium capacity and desorption would occur until equilibrium was reached. Similarly, swings in temperature and contaminant concentration can affect physical adsorbent performance. Increasing temperature reduces capacity, and increasing concentration increases capacity. Additionally, changes in the identity of the contaminant in the airstream can affect overall performance, as strongly adsorbed con- taminants displace weakly held contaminants. All physical and chemical adsorption media have an ability to capture dust particles and lint, which eventually plug the openings in and between media granules and cause a rapid rise in the pressure drop across the media or a decrease in airflow. All granular gaseous adsorption beds need to be protected against particle buildup by installing particulate filters upstream. A prefilter with a minimum ASHRAE Standard 52.2 MERV of 7 is recommended. Vibration breaks up the granules to some degree, depending on the granule hardness, and causes media settling in some activated carbon filters. ASTM Standard D3802 describes a test for measuring the resistance of activated carbon to his abrasion. Critical systems using activated carbon require hardness above 92%, as described by Standard D3802. Physical adsorption and chemisorption media sometimes accelerate corrosion of metals they come into contact with. Conse- quently, media holding cells, trays, and modules should not be con- structed of uncoated aluminum or steel. Painted steel or acrylonitrile butadiene styrene (ABS) plastic are common and exhibit good ma- terial service lives in many applications. Coated or stainless steel components may be required in more aggressive environments. 12. TESTING MEDIA, EQUIPMENT, AND SYSTEMS Testing may be conducted in the laboratory with small-scale media beds or small pieces of treated fabric or composite material. It may be done on full-scale air cleaners in a laboratory test rig capable of generating the test atmosphere or in the field. Laboratory tests with specific challenge gases are generally intended to evaluate media for developmental, acceptance, or comparative purposes. Full-scale tests using specific challenge contaminants are required to evaluate a complete adsorber as constructed and sold, and are ulti- mately needed to validate performance claims. Field tests under actual conditions are used to ensure that the air cleaners were also properly installed and to evaluate remaining media life. Laboratory Tests of Media and Complete Air Cleaners Small granular media samples have been tested in laboratories for many years, and most manufacturers have developed their own methods. ASTM Standard D5228 describes a test method, but it is not entirely applicable to HVAC work because indoor air tends to have a wide range of contaminants, and the contaminant concentra- tions are several orders of magnitude lower than those used in the testing. Testing for Fundamental Media Properties. The test used to evaluate fundamental properties of physical adsorption media, mea- surement of the adsorption isotherm, is static. In this test, a small sample of the adsorbent media is exposed to the pollutant vapor at successively increasing pressures, and the mass of pollutant adsorbed at each pressure is measured. The low-pressure section of an isotherm can then be used to predict kinetic behavior, although the calculation is not simple. For many years, the test outlined in ASTM Standard D3467, which measured a single point on the iso- therm of an activated carbon using carbon tetrachloride (CCI4) vapor, was widely used for specifying performance of activated carbon. The test has been replaced by one described in ASTM Stan- dard D5228, which uses butane as a test contaminant, because of carbon tetrachloride's toxicity. A correlation has been developed between the results of the two test procedures so that users accustomed to CC14 numbers can rec- ognize the performance levels given by ASTM D5228. It is a qualitative measure of performance at other conditions, and a useful quality control procedure. Inc. ASHRAE, 2019 user. single for Licensed | {}
c91b539c-4f37-4013-a43b-252349f584d4 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 47.20 Another qualitative measure of performance is the Brunauer- Emmett-Teller (BET) method (ASTM Standard D4567), in which the surface area is determined by measuring the mass of an adsorbed monolayer of nitrogen. The results of this test are reported in square metres per gram of sorbent or catalyst. This number is often used as an index of media quality, with high num- bers indicating high sorption. Small-Scale Dynamic Media Testing. ASHRAE Standard 145.1-2015 provides a flow-through test of physical and chemical adsorption media at small scale (about 50 mm diameter test bed) and relatively high concentration (100 ppm). The test is intended to pro- vide data for meaningful comparisons of media, provided that the same contaminant challenge gas is used for each test. Standard 145.1 was developed based on several publications describing similar test procedures. Steady concentrations of a single contaminant are fed to a media bed, and the downstream concentration is determined as a function of the total contaminant captured by the filter (ASTM Stan- dard D3467; Mahajan 1987, 1989; Nelson and Correia 1976). VanOsdell et al. (2006) presented data from ASHRAE research project RP-792 showing that, for a particular VOC adsorbed on acti- vated carbon, tests at high concentration could be extrapolated to indoor levels. In addition, tests of a carbon with one chemical, tol- uene, were used to predict breakthough times for four other chemi- cals with modest success. The breakthrough times correlated well on a log-log plot of breakthrough time versus challenge concentra- tion, and the predictions, based only on chemical properties and tol- uene and carbon performance data, were within approximately 100% of measured values. Because physical adsorbent performance is a function of concen- tration, testing at high concentrations does not directly predict per- formance at low concentrations. The corrections described in the section on Physical Adsorption must be applied. If attempts are made to speed the test by high-concentration loading, pollutant desorption from the filter may confuse the results (Ostojic 1985). An adsorber cannot be tested for every pollutant, and there is no general agreement on which contaminants should be considered typical. Nevertheless, tests run according to the previously men- tioned references do give a useful measure of filter performance on a single contaminant, and they do give a basis for estimates of filter penetrations and filter lives. Filter penetration data thus obtained can be used to estimate steady-state indoor concentrations in the preceding equations. Because physical adsorbers, chemisorbers, and catalysts are affected by the temperature and relative humidity of the carrier gas and the moisture content of the filter bed, they should be tested over the range of conditions expected in the application. Contaminant capture and reaction product generation need to be evaluated by exposing the test filter to unpolluted air and measuring downstream concentrations. Reaction products may be as toxic, odorous, or cor- rosive as captured pollutants. A more recent ASHRAE research project, RP-1557 (Han et al. 2013), tested several physical and chemical adsorbent media against toluene, formaldehyde, ozone, and nitrogen dioxide. It found that relative performance at high-challenge-gas concentration corre- sponded with performance at low concentration. Some progress was also made in developing a mechanistic model for predicting low- concentration behavior for physical adsorbers. Full-Scale Laboratory Tests of Complete Air Cleaners. Full- scale tests of in-duct air cleaners are the system test analogs of the media tests described previously. ASHRAE Standard 145.2-2016 details a full-scale performance test for in-duct air cleaners in a lab- oratory setting. In critical applications, such as chemical warfare protective devices and nuclear safety applications, sorption media are evaluated in a small canister, using the same carrier gas velocity as in the full-scale unit. The full-scale unit is then checked for leakage through gaskets, structural member joints, and thin spots or 2019 ASHRAE Handbook-HVAC Applications (SI) gross open passages in the sorption media by feeding a readily adsorbed contaminant to the filter and probing for its presence downstream (ASME Standard AG-1). Some HVAC filter manufac- turers perform full-scale laboratory testing routinely for develop- ment and testing. Chamber Decay Laboratory Tests of Complete Air Clean- ers. Gaseous contaminant removal devices can be tested in sealed chambers by recirculating contaminated air through them and mea- suring the decay of an initial contaminant concentration over time. Chamber decay tests are generally used for devices that physically cannot be tested in a duct, or that have single-pass efficiencies so low that they cannot be reliably measured using up- and down- stream measurements. The procedures used are gaseous contami- nant analogs to the Association of Home Appliance Manufacturers (AHAM) particulate air cleaner test method, but no consensus test standard exists and test methods vary between laboratories. Decay tests can provide valuable data, but the results are affected by fac- tors extraneous to the air cleaner itself, such as errors introduced by adsorption on the chamber surfaces, leaks in the chamber, and the drawing of test samples. Robust test quality assurance and quality control are required to obtain meaningful data. Daisey and Hodgson (1989) compared the pollutant decay rate with and without the contaminant removal device to examine these uncer- tainties. A useful quantity that can be calculated from data obtained during air-cleaner testing is the clean air delivery rate (CADR). Most air cleaners do not remove 100% of the contaminant(s) that they are intended to mitigate. The CADR expresses this incomplete removal as delivery of a lesser amount of fully cleaned air. For an in- duct test, the CADR is calculated as the product of the single-pass efficiency and the airflow rate through the device. For a chamber test, the CADR is calculated as the product of the decay rate con- stant due to action of the air cleaner and the volume of the chamber. Units are those of airflow rate (i.e., m3/s), allowing direct comparison between the impact of the air cleaner and use of venti- lation air. Note that the CADR may be different for each of the gas- eous contaminants that the air cleaner removes. Field Tests of Installed Air Cleaners Gaseous contaminant air cleaners are expensive enough to place a premium on using their full capacity (service life). For odor man- agement applications, the most reliable measure of the continued usefulness of gaseous contaminant air cleaners may be a lack of com- plaints because of the low concentrations, and complaints often serve as early indicators of exhausted granular beds. This approach is not acceptable for toxic contaminants, for which more formal proce- dures must be used. Unfortunately, and despite significant effort, there is not a simple, accepted standard for field-testing the capacity of gaseous air-cleaning equipment. Two approaches have been used: (1) laboratory testing of samples of media removed from the field and (2) in situ upstream/downstream gas measurements using the ambient contaminant(s) as the challenge. The classic, and still widely used, technique of evaluating the status of a granular air cleaner in the field is to remove a small sam- ple and ship it to a laboratory. Media manufacturers offer this ser- vice. The sample needs to be representative of the air cleaner, so should be obtained from near the center of the air cleaner. Consoli- dated multiple small samples taken over the filter area are more rep- resentative of the air cleaner than one larger sample. The sample needs to be handled and shipped carefully so that it remains repre- sentative of the in-place filter when it reaches the laboratory; labo- ratories can suggest procedures. Given a representative sample and good handling, sampled media test results give a good indication of the state of a media bed. Unfortunately, media sampling as a field-testing procedure has disadvantages. First, it applies only to granular media that can be Inc. ASHRAE, 2019 user. single for Licensed | {}
ff686504-44df-49b8-961c-be333da811c3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Air Cleaners for Gaseous Contaminants 47.21 sampled; cutting a hole in a bonded or pleated media product to obtain a sample destroys the filter. In addition, opening a granular media air cleaner to obtain samples is sufficiently disagreeable to prevent its frequent application. These disadvantages have led to attempts to find more conve- nient ways to evaluate filters in the field. The most widely used alternative approach is to sample the air up- and downstream of the filter and use the ratio to estimate the remaining filter capacity. Field tests of gaseous contaminant air cleaners are conducted using the same general techniques discussed under contaminant measurement and analysis. Depending on the contaminant, type of air cleaner, and application, field testing can be accomplished with active or passive sampling techniques. Liu (1998) discussed the rel- ative merits of the various techniques. Each has the potential to be superior in a given case. For indoor air applications with relatively constant contaminant sources, passive samplers are advantageous because they capture an integrated sample and are more economical. (Real-time samplers are used infrequently in this role.) Up- and downstream measurements are evaluated by converting them to efficiency or fractional penetration and comparing them to measurements made at the time of installation. Because gaseous challenge contaminants cannot be injected into the HV AC system in occupied buildings, the up- and downstream samplers are exposed only to the ambient contaminants, which usually vary in nature and concentration. This complicates interpretation of the data, because air cleaner efficiency varies with concentration and nature of the contaminant. Measurement of efficiency using field samples is most directly interpreted if there is a single contaminant (or relatively consistent group of contaminants [evaluated as TVOC]) with a rel- atively constant challenge concentration. For multiple contaminants at multiple concentrations, judgment and experience are needed to interpret downstream measurements. Bayer and Hendry (2005) attempted to use single-component analyses to evaluate air cleaners in the field. The up- and downstream samples were analyzed not for TVOC, but for particular chemicals (heptane, toluene, ethyl ben- zene, and formaldehyde). Bayer and Hendry found that the time variations of the challenge made the efficiency determinations so variable that the procedure could not be used reliably. REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. ACGIH. 2013. Industrial ventilation: A manual of recommended practice, 28th ed. American Conference of Governmental Industrial Hygienists, Cincinnati, OH. ASHRAE. 2017. Method of testing general ventilation air-cleaning devices for removal efficiency by particle size. ANSI/ASHRAE Standard 52.2- 2017. ASHRAE. 2010. Ventilation for acceptable indoor air quality. ANSI/ ASHRAE Standard 62. 1-2010. ASHRAE. 2016. Ventilation and acceptable indoor air quality in residential buildings. ANSI/ASHRAE Standard 62.2-2016. ASHRAE. 2015. Laboratory test method for assessing the performance of gas-phase air-cleaning media: Loose granular media. ANSI/ASHRAE Standard 145.1-2015. ASHRAE. 2016. Method of testing gaseous contaminant air cleaning devices for removal efficiency. ASHRAE Standard 145.2-2016. ASHRAE. 2015. Position document on filtration and air cleaning. www shina-orgFlenDoMimary/AboutPort Courance hatafch--a and-Air-Cleaning-PD.pdf. ASME. 2015. Code on nuclear air and gas treatment. ANSI/ASME Standard AG-1-2015. American Society of Mechanical Engineers, New York. ASTM. 2009. Standard test method for carbon tetrachloride activity of acti- vated carbon. Standard D3467-04 (R2009). American Society for Testing and Materials, West Conshohocken, PA. ASTM. 2016. Standard test method for ball-pan hardness of activated carbon. Standard D3802-16. American Society for Testing and Materials, West Conshohocken, PA. ASTM. 2013. Standard test method for single-point determination of spe- cific surface area of catalysts and catalyst carriers using nitrogen adsorp- tion by continuous flow method. Standard D4567 -03(2013). American Society for Testing and Materials, West Conshohocken, PA. ASTM. 2010. Standard test method for determination of butane working capacity of activated carbon. Standard D5228-92 (R2010). American Society for Testing and Materials, West Conshohocken, PA. ASTM. 2017. Standard test methods for determining airtightness ofbuildings using an orifice blower door. Standard E1827-11(2017). Society for Test- ing and Materials, West Conshohocken, PA. ASTM. 2011. Standard test method for determining air change in a single zone by means of a tracer gas dilution. Standard E741-11 (R2006). American Society for Testing and Materials, West Conshohocken, PA. Bayer, C. W., and R.J. Hendry. 2005. Field test methods to measure contam- inant removal effectiveness of gas phase air filtration equipment. ASHRAE Transactions 1 1 1(2):285-298. Boeniger, M.F. 1995. Use of ozone generating devices to improve indoor air quality. American Industrial Hygiene Association Journal 56:590-598. Burton, D.J. 2003. Industrial ventilation workbook, 6th ed. American Con- ference of Governmental Industrial Hygienists, Cincinnati, OH. Chen, W., J.S. Zhang, and Z. Zhang. 2005. Performance of air cleaners for removing multiple volatile organic compounds in indoor air. ASHRAE Transactions 111:1 101-1114. CIWMB. 2003. Building material emissions study. California Integrated Waste Management Board, Publication 433-03-015. www.calreccle.ca govPublications/default.asp?pubid=1027. Cole, J.T. 1983. Constituent source emission rate characterization of three gas-fired domestic ranges. APCA Paper 83-64.3. Air and Waste Man- agement Association, Pittsburgh. Daisey, J.M., and A.T. Hodgson. 1989. Initial efficiencies of air cleaners for the removal of nitrogen dioxide and volatile organic compounds. Atmo- spheric Environment 23(9):1885-1892. DeFrees, J.A., and R.F. Amberger. 1987. Natural infiltration analysis of a residential high-rise building. IAQ '87-Practical Control of Indoor Air Problems, pp. 195-210. ASHRAE. d'Hennezel, O., P. Pichat, and D.F. Ollis. 1998. Benzene and toluene gas- phase photocatalytic degradation over H2O and HCI pretreated TiO2: By-products and mechanisms. Journal of Photochemistry and Photobi- ology A: Chemistry 118(3): 197-204. Elliott, L.P., and D.R. Rowe. 1975. Air quality during public gatherings. Journal of the Air Pollution Control Association 25(6):635-636. EPA. 1987. Radon reduction methods: A homeowner s guide, 2nd ed. EPA- 87-010. U.S. Environmental Protection Agency, Center for Environmen- tal Research Information, Cincinnati, OH. EPA. 1993. Radon reduction techniques for detached houses: Technical guid- ance, 3rd ed. EPA/625/5-86/O19. U.S. Environmental Protection Agency, Center for Environmental Research Information, Cincinnati, OH. EPA. 2009. Data from the air quality system measurements. EPA. 2016a. National ambient air quality standards (NAAQS). Environmen- tal Protection Agency, Washington, D.C. www .epa.gov/criteria-air -pollutants/naaqs-table. EPA. 2016b. Summarized data of the Building Assessment Survey and Evaluation Study. www.zpa.gowinkon-ai-ai-gairy-capisonnmarizeda -milicing-assessreem-survey-and-vaination-study EPA. Annual. Identification and listing ofhazardous waste. Code ofFederal Regulations 40 CFR 261. Environmental Protection Agency, Washing- ton, D.C. www.ecfr.gov. EPA/NIOSH. 1991. Building air quality-A guide for building owners and facility managers. U.S. Environmental Protection Agency. Farhanian, D., and F. Haghighat. 2014. Photocatalytic oxidation air cleaner: Identification and quantification of by-products. Building and Environ- ment 72:34-43. FEMA. 2003a. Reference manual to mitigate potential terrorist attacks against buildings. FEMA Publication 426. www.fema.gov/library /viewRecord.do?id=1559. FEMA. 2003b. Primer for design of commercial buildings to mitigate ter- roristattacks. FEMA Publication 427. www.fema.gov/library/viewRecord .do?id=1560. Fujishima, A., and K. Honda. 1972. Electrochemical photolysis of water at a semiconductor electrode. Nature 238:37-38. Inc. ASHRAE, 2019 user. single for Licensed | {}
2d39cee8-5cd4-4832-b15b-dc3380aced6d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 47.22 Girman, J.R., A.P. Hodgson. A.F. Newton, and A.R Winks. 1984. Emissions of volatile organic compounds from adhesives for indoor application. Report LBL 1 7594. Lawrence Berkeley Laboratory, Berkeley, CA. Han, K., C. He, B. Guo, and J. Zhang. 2013. Laboratory comparison of rel- ative performance of gas phase filtration media at high and low challenge concentrations (RP-1557). ASHRAE Research Project, Final Report. Hodgson, A. T., D.P. Sullivan, and W.J. Fisk. 2005. Evaluation ofultra-violet photocatalytic oxidation (UV-PCO) for indoor air applications: Conver- sion of volatile organic compounds at low part-per-billion concentra- tions. Report LBNL-58936. E.O. Lawrence Berkeley National Laboratory, Berkeley, CA. Hodgson, A.T., H. Destaillats, T. Hotchi, and W .J. Fisk. 2007. Evaluation of a combined ultraviolet photocatalytic oxidation (UVPCO)/chemisorbent air cleaner for indoor air applications. Report LBNL-62202. E.O. Law- rence Berkeley National Laboratory, Berkeley, CA. IARC. 2004. Tobacco smoke and involuntary smoking. IARC monographs on the evaluation of carcinogenic risks to humans 83:1-1438. Interna- tional Agency for Research on Cancer. ISA. 1985. Environmental conditions for process measurement and control systems: Airborne contaminants. Standard 71.04-1985. Instrument Society of America, Research Triangle Park, NC. ISO. 2017. High efficiency filters and filter media for removing particles from air -Part 1: Classification, performance, testing and marking. ISO Standard ISO 29463-1:2017. Janssen, J.H. 1989. Ventilation for acceptable indoor air quality. ASHRAE Journal 31(10):40-45. Janni, K.A., W.J. Maier, T.H. Kuehn, C.-H. Yang, B.B. Bridges, D. Vesley, and M.A. Nellis. 2001. Evaluation ofbiofiltration of air-An innovative air pollution control technology (RP-880). ASHRAE Transactions 107(1): 198-214. Leaderer, B.P., R.T. Zagranski, M. Berwick, and J.A.J. Stolwijk. 1987. Pre- dicting NO2 levels in residences based upon sources and source uses: A multi-variate model. Atmospheric Environment 21(2):361-368. Lee, H.K., T.A. McKenna, L.N. Renton, and J. Kirkbride. 1986. Impact of a new smoking policy on office air quality. Proceedings of Indoor Air Quality in Cold Climates, pp. 307-322. Air and Waste Management Association, Pittsburgh. Liu, R.-T. 1998. Measuring the effectiveness of gas-phase air filtration equipment-Field test methods and applications (RP-791). ASHRAE Transactions 104(2):25-35. Maddalena, R.L., T.E. McKone, H. Destaillats, M. Rusell, A.T. Hodgson, and C. Perino. 2011. Quantifying pollutant emissions from office equip- ment: A concern in energy-efficient buildings. Report CEC-500-2011- 046. California Energy Commission. Mahajan, B.M. 1987. A method of measuring the effectiveness of gaseous contaminant removal devices. NBSIR 87-3666. National Institute of Standards and Technology, Gaithersburg, MD. Mahajan, B.M. 1989. A method of measuring the effectiveness of gaseous contaminant removalfilters. NBSIR 89-4119. National Institute of Stan- dards and Technology, Gaithersburg, MD. Meckler, M., and J.E. Janssen. 1988. Use of air cleaners to reduce outdoor air requirements. IAQ '88: Engineering Solutions to Indoor Air Prob- lems, pp. 130-147. ASHRAE. Morrison, G.C., W.W. Nazaroff, J.A. Cano-Ruiz, A.T. Hodgson, and M.P. Modera. 1998. Indoor air quality impacts of ventilation ducts: Ozone removal and emission of volatile organic compounds. Journal of the Air & Waste Management Association 48:941-949. Moschandreas, D.J., and S.M. Relwani. 1989. Field measurement of NO2 gas-top burner emission rates. Environment International 15:499-492. NAFA. 2018. Installation, operation and maintenance of air filtration sys- tems, 4th ed. National Air Filtration Association, Washington, D.C. Nazaroff, W. W., and G.R. Cass. 1986. Mathematical modeling of chemi- cally reactive pollutants in indoor air. Environmental Science & Technology 20:924-934. Nelson, G.O., and A.N. Correia. 1976. Respirator cartridge efficiency studies: VIII. Summary and Conclusions. American Industrial Hygiene Association Journal 37:514-525. Nelson, P.R., Sears, S.B., and D.L. Heavner. 1993. Application of methods for evaluating air cleaner performance. Indoor Environment 2:1 11-117. NIOSH. 2002. Guidance for protecting building environments from airborne chemical, biological, or radiological attacks. DHHS (NIOSH) Publica- tion 2002-139. Department of Health and Human Services, National Institute for Occupational Safety and Health, Cincinnati. 2019 ASHRAE Handbook-HVAC Applications (SI) NIOSH. 2003. Guidance for filtration and air-cleaning systems to protect building environments from airborne chemical, biological, or radiological attacks. DHHS (NIOSH) Publication 2003-136. (www.cdc.gov/niosh/docs/2003-136; www.cdc.gov/niosh/docs/2003-136 /pdfs/2003-136.pdf). Department of Health and Human Services, National Institute for Occupational Safety and Health, Cincinnati. Obee, T.N., and R.T. Brown. 1995. TiO2 photocatalysis for indoor air appli- cations: Effects of humidity and trace contaminant levels on the oxida- tion rates of formaldehyde, toluene and 1,3-butadiene. Environmental Science & Technology 29(5):1223-1231. Obee, T.N., and S.O. Hay. 1999. The estimation of photocatalytic rate con- stants based on molecular structure: Extending to multi-component sys- tems. Journal ofAdvanced Oxidation Technologies 4(2):147-152. OSHA. 1994. Asbestos. Code of Federal Regulations 29 CFR 1910.1000. U.S. Occupational Safety and Health Administration, Washington, D.C. www.ecfr.gov. Ostojic, N. 1985. Test method for gaseous contaminant removal devices. ASHRAE Transactions 91(2):594-614. Peral, J., and D.F. Ollis. 1992. Heterogeneous photocatalytic oxidation of gas-phase organics for air purification: Acetone, 1-butanol, butyralde- hyde, formaldehyde and m-xylene oxidation. Journal ofCatalysis 136(2): 554-565. Peral, J., X. Domenech, and D.F. Ollis. 1997. Heterogeneous photocatalysis for purification, decontamination and deodorization of air. Journal of Chemical Technology and Biotechnology 70(2):117-140. Rock, B.A. 2006. Ventilation for environmental tobacco smoke Controlling ETS irritants where smoking is allowed. Elsevier, New York. Shaughnessy, R.J., and L. Oatman. 1991. The use of ozone generators for the control ofindoor air contaminants in an occupied environment. IAQ '91: Healthy Buildings, pp. 318-324. ASHRAE. Sterling, T.D., and D. Kobayashi. 1981. Use of gas ranges for cooking and heating in urban dwellings. Journal of the Air Pollution Control Associ- ation 31(2):162-165. Tang, X., P.K. Misztal, W. W. Nazaroff, and A.H. Goldstein. 2015. Siloxanes are the most abundant volatile organic compound emitted from engineer- ing students in a classroom. Environmental Science and Technology Let- ters 2(11):303-307. Tang, X., P.K. Misztal, W. W. Nazaroff, and A.H. Goldstein. 2016. Volatile organic compound emissions from humans indoors. Environmental Sci- ence and Technology 50(23):12686-12694. Tompkins, D.T., B.J. Lawnicki, W.A. Zeltner, and M.A. Anderson. 2005a. Evaluation of photocatalysis for gas-phase air cleaning -Part 1: Process, technical, and sizing considerations (RP-1134). ASHRAE Transactions 111(2):60-84. Tompkins, D.T., B.J. Lawnicki, W .A. Zeltner, and M.A. Anderson. 2005b. Evaluation of photocatalysis for gas-phase air cleaning- Part 2: Eco- nomics and utilization (RP-1134). ASHRAE Transactions 111(2):85-95. Traynor, G.W., I.A. Nitschke, W.A. Clarke, G.P. Adams, and J.E. Rizzuto. 1985. A detailed study of thirty houses with indoor combustion sources. Paper 85-30A.3. Air and Waste Management Association, Pittsburgh. Underhill, D.T., G. Mackerel, and M. Javorsky. 1988. Effects of relative humidity on adsorption of contaminants on activated carbon. Proceed- ings of the Symposium on Gaseous and Vaporous Removal Equipment Test Methods (NBSIR 88-3716). National Institute of Standards and Technology, Gaithersburg, MD. VanOsdell, D. W., C.E. Rodes, and M.K. Owen. 2006. Laboratory testing of full-scale in-duct gas air cleaners. ASHRAE Transactions 112(2):418- 429. Vartiainen, E., M. Kulmala, T.M. Ruuskanen, R. Taipale, J. Rinne, and H. Vehkamaki. 2006. Formation and growth of indoor air aerosol particles as a result of D-limonene oxidation. Atmospheric Environment 40:7882- 7892. Wade, W.A., W.A. Cote, andJ.E. Yocum. 1975. A study ofindoor air quality. Journal of the Air Pollution Control Association 25(9):933-939. Wang, T.C. 1975 A study of bioeffluents in a college classroom. ASHRAE Transactions 81(1):32-44. Wang, H., and G.C. Morrison. 2006. Ozone-initiated secondary emission rates of aldehydes from indoor surfaces in four homes. Environmental Science & Technology 40:5263-5268. Weschler, C.J., H.C. Shields, and D. V. Naik. 1994. Ozone-removal efficien- cies of activated carbon filters after more than three years of continuous service. ASHRAE Transactions 100(2):1121-1129. Inc. ASHRAE, 2019 user. single for Licensed | {}
7958d530-ed79-468e-a4f2-53726a161236 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Air Cleaners for Gaseous Contaminants 47.23 Yoon, Y.H., and J.H. Nelson. 1988. A theoretical study of the effect of hu- midity on respirator cartridge service life. American Industrial Hygiene Association Journal 49(7):325-332. Zhong L., F. Haghighat, C.-S. Lee. 2013. Ultraviolet photocatalytic oxida- tion for indoor environment applications: Experiment validation of the model. Building and Environment 62:155-166. BIBLIOGRAPHY Anthony, C.P., and G.A. Thibodeau. 1980. Textbook of anatomy and physi- ology. C. V. Mosby, St. Louis. ASTM. 2013. Standard practice for sampling atmospheres to collect organic compound vapors (activated charcoal tube adsorption method). Standard D3686-13. American Society for Testing and Materials, West Consho- hocken, PA. ASTM. 2016. Standard test method for determination of butane activity of activated carbon. Standard D5742-16. American Society for Testing and Materials, West Conshohocken, PA. ATC. 1990. Technical assistance document for sampling and analysis of toxic organic compounds in ambient air. EPA/600/8-90-005. Environ- mental Protection Agency, Research Triangle Park, NC. Berglund, B., U. Berglund, and T. Lindvall. 1986. Assessment of discomfort and irritation from the indoor air. IAQ '86: Managing Indoor Air for Health and Energy Conservation, pp. 138-149. ASHRAE. Brugnone, R., L. Perbellini, R.B. Faccini, G. Pasini, G. Maranelli, L. Romeo, M. Gobbi, and A. Zedde. 1989. Breath and blood levels of ben- zene, toluene, cumene and styrene in nonoccupational exposure. Inter- national Archives of Environmental Health 61:303-311. CARB. 2015. Ozone and ambient air quality standards. California Air Re- sources Board. www.arf.ca.gov/resenchangs/traps/tsone/ostox.itm. Cain, W.S., C.R. Shoaf, S.F. Velasquez, S. Selevan, and W. Vickery. 1992. Reference guide to odor thresholdsfor hazardous air pollutants listed in the Clean Air Act Amendments of 1990. EPA/600/R-92/047. Environ- mental Protection Agency. Chung, T-W., T.K. Ghosh, A.L. Hines, and D. Novosel. 1993. Removal of selected pollutants from air during dehumidification by lithium chloride and triethylene glycol solutions. ASHRAE Transactions 99(1):834-841. Cohen, S.I., N.M. Perkins, H.K. Ury, and J.R. Goldsmith. 1971. Carbon mon- oxide uptake in cigarette smoking. Archives of Environmental Health 22(1):55-60. Conkle, J.P., B.J. Camp, and B.E. Welch. 1975. Trace composition ofhuman respiratory gas. Archives of Environmental Health 30(6):290-295. EPA. 2018. 2015 National ambient air quality standards (NAAQS) for ozone. United States Environmental Protection Agency. www.epa.gov hotos-politionScortinelemblemei-jiqyanhanbandanapac -ozone. Fanger, P.O. 1989. The new comfort equation for indoor air quality. IAQ '89: The Human Equation: Health and Comfort, pp. 251-254. ASHRAE. Foresti, R., Jr., and 0. Dennison. 1996. Formaldehyde originating from foam insulation. IAQ '86: Managing Indoor Air for Health and Energy Con- servation, pp. 523-537. ASHRAE. Gorban, C.M., I.I. Kondratyeva, and L.Z. Poddubnaya. 1964. Gaseous activity products excreted by man in an airtight chamber. In Problems of Space Biology. JPRS/NASA. National Technical Information Service, Springfield, VA. Hunt, R.D., and D.T. Williams. 1977. Spectrometric measurement of ammonia in normal human breath. American Laboratory (June):10-23. Idem, S. 2002. Leakage of ducted air terminal connections. ASHRAE Re- search Project RP-1132. Kelly, T.J., and D.H. Kinkead. 1993. Testing of chemically treated adsorbent air purifiers. ASHRAE Journal 35(7):14-23. Lodge, J.E., ed. 1988. Methods of air sampling and analysis, 3rd ed. Lewis Publishers, Chelsea, MI. Martin, P., D.L. Heavner, P.R. Nelson, K.C. Maiolo, C.H. Risner, P.S. Sim- mons, W.T. Morgan, and M. W. Ogden. 1997. Environmental tobacco smoke (ETS): A market cigarette study. Environment International 23(1): 75-89. Mehta, M.R, H.E. Ayer, B.E. Saltzman, and R. Romk. 1988. Predicting con- centrations for indoor chemical spills. IAQ '88: Engineering Solutions to Indoor Air Problems, pp. 231-250. ASHRAE. Lee, M-G., S-W. Lee, and S-H. Lee. 2006. Comparison of vapor adsorption characteristics of acetone and toluene based on polarity in activated carbon fixed-bed reactor. Korean Journal of Chemical Engineering (23)5:773-778. Moschandreas, D.J., and S.M. Relwani. 1989. Field measurement of NO2 gas-top burner emission rates. Environment International 15:499-492. NAFA. 1996. Guide to airfiltration, 2nd ed. National Air Filtration Associ- ation, Washington, D.C. Nagda, N.L., and H.E. Rector. 1983. Guidelines for monitoring indoor-air quality. EPA 600/4-83-046. Environmental Protection Agency, Research Triangle Park, NC. Nefedov, I.G., V.P. Savina, and N.L. Sokolov. 1972. Expired air as a source of spacecraft carbon monoxide. Presented at 23rd International Aeronau- tical Congress, International Astronautical Federation, Paris. NIOSH. 1994. NIOSH manual of analytical methods, 4th ed. 2 vols. U.S. Department of Health and Human Services, National Institute for Occu- pational Safety and Health, Cincinnati. NIOSH. Annual. Annual registry of toxic effects of chemical substances. U.S. Department of Health and Human Services, National Institute for Occupational Safety and Health, Washington, D.C. NIOSH. (intermittent). Criteria for recommended standardfor occupational exposure to (compound). U.S. Department of Health and Human Ser- vices, National Institute for Occupational Safety and Health, Washing- ton, D.C. Nirmalakhandan, N.N., and R.E. Speece. 1993. Prediction of activated carbon adsorption capacities for organic vapors using quantitative struc- ture activity relationship methods. Environmental Science and Technol- ogy 27:1512-1516. Perry, Chilton, and Kirkpatrick, 1997. Perry 's chemical engineers' hand- book, 7th ed. McGraw-Hill, New York. Riggen, R.M., W.T. Wimberly, and N.T. Murphy. 1990. Compendium of methods for determination of toxic organic compounds in ambient air. EPA/600/D-89/186. Environmental Protection Agency, Research Triangle Park, NC. Also second supplement, 1990, EPA/600/4-89/017. Rivers, R.D. 1988. Practical test method for gaseous contaminant removal devices. Proceedings of the Symposium on Gaseous and Vaporous Removal Equipment Test Methods (NBSIR 88-3716). National Institute of Standards and Technology, Gaithersburg, MD. Sparks, L.E. 1988. Indoor air quality model, version 1.0. EPA-60018- 88097a. U.S. Environmental Protection Agency, Research Triangle Park, NC. Tham, Y.J., A.L.Puziah, A.M. Abdullah, A. Shamala-Devi, Y.H. Taufiq- Yap. 2011. Performances oftoluene removal by activated carbon derived from durian shell. Bioresource Technology 102:724-728. Weschler, C.J., and H.C. Shields. 1989. The effects of ventilation, filtration, and outdoor air on the composition of indoor air at a telephone office building. Environment International 15:593-604. White, J.B., J.C. Reaves, R.C. Reist, and L.S. Mann. 1988. A data base on the sources of indoor air pollution emissions. IAQ '88: Engineering Solutions to Indoor Air Problems. ASHRAE. WHO. 2018. Air quality guidelines-global update 2005. World Health Orga- nization. www.whoint/pheteafil_typicantocantoranthorair. Winberry, W.T., Jr., L. Forehand, N.T. Murphy, A. Ceroli, B. Phinney, and A. Evans. 1990. EPA compendium of methods for the determination of air pollutants in indoor air. EPA/600/S4-90/010. Environmental Protection Agency. (NTIS-PB 90-200288AS). Woods, J.E., J.E. Janssen, and B.C. Krafthefer. 1996. Rationalization of equivalence between the ventilation rate and air quality procedures in ASHRAE Standard 62. IAQ '86: Managing Indoor Air for Health and Energy Conservation. ASHRAE. Yu, H.H.S., and R.R. Raber. 1992. Air-cleaning strategies for equivalent indoor air quality. ASHRAE Transactions 98(1):173-181. Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
3ff6ed66-c1a6-4c98-951b-36f8f74a1dcf | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 48 DESIGN AND APPLICATION OF CONTROLS ¦ System Types ¦ 48.1 ¦ ¦ --- ¦ --- ¦ ¦ Heating Systems ¦ 48.1 ¦ ¦ Cooling Systems ¦ 48.4 ¦ ¦ Air Systems ¦ 48.8 ¦ ¦ Special Applications ¦ 48.18 ¦ ¦ Design Considerations and Principles ¦ 48.19 ¦ ¦ Control Principles for Energy Conservation ¦ 48.20 ¦ AUTOMATIC control of HV AC systems and equipment usually includes control of temperature, humidity, pressure, and flow rates of air and water. Automatic controls can sequence equipment operation to meet load requirements and to provide safe equipment operation using direct digital control (DDC), electronic, electrical, mechanical, and/or pneumatic devices. Automatic controls are only fully effective when applied to well-designed mechanical systems; they cannot compensate for misapplied systems, excessive under- or oversizing, or highly nonlinear processes. This chapter addresses control of typical HVAC systems, design of controls for system coordination and for energy conservation, and control system commissioning. Chapter 7 of the 2017 ASHRAE Handbook-Fundamentals covers details of component hardware and the basics of control. 1. SYSTEM TYPES A building automation system (BAS) with direct digital, elec- tronic, or pneumatic controls has several physical control loops, with each loop including a controlled variable (e.g., temperature), con- trolled device (e.g., actuator), and the process to be controlled (e.g., heating system). A BAS with DDC controllers can share sensor val- ues with several control loops or have multiple control loops selec- tively activate an actuator. A BAS with DDC controllers allows information such as system status or alarms to be shared through a common communication protocol, between HVAC systems or within building systems and services, thereby enabling advanced, energy-saving, system-level applications. ASHRAE Guideline 13 and Standard 135 have more detailed discussions of networking and interoperability. 2. HEATING SYSTEMS Heating systems include boilers, fired by either fuel combustion or electric resistance, furnaces, electric resistance air heaters, and heat pumps. Systems involving combustion require multiple safe- ties, which should always follow local codes and manufacturers' guidelines. Load affects the required rate of heat input to a heating system. The rate is controlled by cycling a fixed-intensity energy source on and off, or by modulating the intensity of the heating pro- cess. Heating systems may come with factory-mounted controls capable of handling safeties, cycling, and modulation. In addition, a BAS can be used to interface with the heating system or to control it directly. The designer decides under what circumstances to turn equipment on and offin sequence and at what temperature set point to maintain the supply air or water. Hot- w ater and Steam Boilers Hot-water distribution control includes temperature control at hot- water boilers or the converter, reset of heating water temperature, The preparation of this chapter is assigned to TC 1.4, Control Theory and Application. and control of pumps and distribution systems. Other controls to be considered include (1) minimum water flow through boilers, (2) pro- tecting boilers from temperature shock and condensation on the heat exchanger, and (3) coil low-temperature detection. If multiple or alternative heating sources (e.g., condenser heat recovery, solar storage) are used, the control strategy must also include a way to sequence hot-water sources or select the most economical source. Figure 1 shows a system for load control ofa fossil-fuel-fired boil- er. Boiler safety controls, usually factory installed with the boiler, in- clude flame-failure, high-temperature, and other cutouts. ASME Standard CSD-1-2012 requires a manually operated remote shut- down switch located just outside the boiler room door for boilers with fuel input ratings less than 3633 kW. Field-installed operating con- trols must allow safety controls to function in all modes of operation. In most cases, energy savings can be significant if the boiler is con- trolled to reset the water temperature based on heating load or a proxy such as outdoor air temperature. Ifthe boiler is also used for domestic water heating, the reset range will be limited because minimum tem- peratures required to kill bacteria must be maintained. A typical out- door air reset schedule is shown in Figure 1. With DDC devices, reset can be controlled from zone demand, which can improve energy per- formance and ensure all zones are satisfied. To minimize condensa- tion of flue gases and boiler damage in noncondensing boilers, water temperature should not be reset below that recommended by the man- ufacturer, typically 60°C entering water temperature, or condensation may occur and lead to corrosion-related failure. Condensing boilers are specifically designed to allow flue gases to condense and should operate at lower water temperatures to harness latent energy in the flue gas. Aggressive reset ofhot-water temperatures improves the ef- ficiency of condensing boilers, because efficiency is a strong func- tion of boiler entering water temperature. Additional energy savings are achieved using variable-speed pumps controlled to re- duce distribution pump capacity to match the load, as allowed by the boiler's maximum flow. Hot-water heat exchangers or steam-to-water converters are some- times used instead of boilers as hot-water generators. Converters Fig. 1 Boiler Control ![image](/image/placeholder) BOILER SUPPLY OUTDOOR AIR TEMPERATURE [ RESET SCHEDULE OUTDOOR AIR HOT-WATER HEAT TEMPERATURE TEMPERATURE CONTROLS EXCHANGER -18°C 80°C 16°C 60°C BURNER PUMP BOILER □ BOILER RETURN 48.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
8cfc3fbe-8415-40a7-b7f0-dedeb03e5235 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 48.2 2019 ASHRAE Handbook-HVAC Applications (SI) typically do not include a control package; therefore, the engineer must design the control scheme. The schematic in Figure 2 can be used with either low-pressure steam or boiler water from 93 to 180°C. The supply water temperature sensor typically controls two modulating two-way valves in a 1/3 and 2/3 arrangement (because of poor turndown of steam valves) in a steam or high-temperature hot-water supply line. An outdoor temperature sensor (or zone demand, for higher efficiency) can be used to reset the supply water temperature downward as load decreases to improve the controlla- bility of heating valves at low load and to reduce heat losses. A flow or differential pressure switch interlock should close the two- way valve when the hot-water pump is not operating. Ensure that the flow switch operates as expected at minimum flow rate on variable- flow systems. With a BAS, feedback from zone heating valves can be used to control starting and stopping of the hot-water pumps. When shutting down a steam converter or high-temperature hot-water system, close the steam valves and allow the water to circulate long enough to remove residual heat in the converter and prevent the pres- sure relief valve from opening. Hot- Water Distribution Systems Hot water is distributed using variable flow (primarily two-way valves at coils) or constant flow (three-way valves at coils). An example constant flow system is shown in Figure 3. Variable-flow systems are similar to the chilled-water distribution systems shown in Figures 10 and 1 1. Some boilers require constant flow or very high minimum flow rates. They typically are piped using a primary/ secondary system (see Figure 11). These boilers are usually required by their listing to have flow switches to enable the boiler only when flow is proven. Boilers that require small (or zero) minimum flow rates are usually piped in a primary-only configuration with a bypass ![image](/image/placeholder) OUTDOOR AIR TEMPERATURE T CONTROLLER STEAM OR HOT-WATER SUPPLY F HOT-WATER 4 SUPPLY L SHELL-AND-TUBE HEAT EXCHANGER HOT-WATER RETURN Fig. 2 Steam-to- w ater Heat Exchanger Control ![image](/image/placeholder) NO C HEATING COIL NC I EXPANSION TANK NO C PREHEAT S/S う COIL NC → T PUMP BOILER BURNER Fig. 3 Load and Zone Control in Constant Flow System to maintain minimum flow (see Figure 10). A flow meter in the boiler circuit is usually installed to control the bypass valve. The bypass can also be controlled to maintain minimum boiler entering water tem- peratures for noncondensing boilers. Heating Coils Heating coils that are not subject to freezing can be controlled by simple two- or three-way modulating valves (Figure 4). (For infor- mation on the air side of coils, see the section on Air Systems.) The modulating valve is controlled by coil discharge air temperature or by space temperature, depending on the HVAC system. In cold regions, valves are set to normally open to allow heating if control power fails. In many systems, the supply air temperature set point is reset based on the outdoor air temperature, zone damper positions, return air temperature, or some other load proxy. Heating coils in central air-handling units preheat, reheat, or heat, depending on the climate and the amount of minimum outdoor air needed. They can also provide morning warm-up on systems with limited zone heating capacity. The equipment heating coil that first receives the outdoor air intake, even if mixed with indoor air, must have protection against freezing in cold climates, unless (1) the minimum outdoor air quan- tity is small enough to keep the mixed air temperature above freezing in all expected operating conditions and (2) enough mixing occurs to prevent stratification. Even when the average mixed-air temperature is above freezing, inadequate air mixing may allow freezing air to impinge on small areas of the coil, causing localized freezing. This blocks flow and, without a heat source, the rest of the coil and equipment downstream is at risk. Preheating coils that heat 100% outdoor air always need (1) protection against freezing and (2) constant water or steam flow in cold climates. Steam preheat coils should have two-position valves and vacuum breakers to prevent condensate build-up in the coil. The valve should be fully open when outdoor (or mixed) air temperature is below freezing. This causes unacceptably high coil discharge tem- peratures at times, necessitating face-and-bypass dampers for final temperature control (Figure 5). The bypass damper should be sized to provide the same pressure drop at full bypass airflow as the com- bination of face damper and coil does at full airflow. When the out- door air temperature is safely above freezing (roughly 1.7°C), the bypass damper is full open to the coil face and the coil valve can be modulated to improve controllability. Hot-water coils must maintain a minimum water velocity in the tubes (on the order of 0.9 m/s) to avoid stratification and ensure proper heat transfer by maintaining turbulent flow. A two-position valve combined with face-and-bypass dampers (Figure 5) or a coil pump can be used. There are many coil pump piping schemes; the most common are shown in Figures 6 and 7. In each scheme, the con- trol valve modulates to maintain the desired coil air discharge tem- perature and the pump maintains the minimum tube water velocity needed when the outdoor air is below freezing. Pumped coils can still ![image](/image/placeholder) HOT-WATER HOT-WATER HOT-WATER HOT-WATER RETURN SUPPLY RETURN SUPPLY I I C NC NO NO 0 0 HEATING HEATING COIL COIL AIRFLOW AIRFLOW A. TWO-WAY VALVE B. THREE-WAY VALVE Fig. 4 Control of Hot- w ater Coils Inc. ASHRAE, 2019 user. single for Licensed | {}
3eb61979-b2bd-43bc-ade6-6db929ec51cc | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Design and Application of Controls 48.3 freeze in very cold regions, so additional low-temperature protection measures such as freezestats, glycol-based fluids, and default-to- open valves should be used. A low-temperature detector (commonly called a freezestat), is a long, refrigerant-filled capillary tube used as a low-temperature sensing switch. If any short section of the tube is exposed to a low temperature (typically 3.3°C), it can provide an alarm or a hardwired ![image](/image/placeholder) D M LOW-LIMIT THERMOSTAT STEAM OR (FREEZE PROTECTION) HOT WATER T S T DM DM TO OUTDOOR AIR-HANDLING AIR SYSTEM FILTER FACE-AND- HEATING COIL BYPASS DAMPER Fig. 5 Preheat with Face-and-Bypass Dampers ![image](/image/placeholder) HOT-WATER HOT-WATER RETURN SUPPLY CONTROL VALVE TO SUPPLY LOW LIMIT FAN PROTECTION) (FREEZE COIL 6 I PUMP I M S T 0 0 TO AIR-HANDLING OUTDOOR SYSTEM AIR CAPILLARY SENSING FILTER ELEMENT HEATING COIL Fig. 6 Coil Pump Piped Primary/Secondary ![image](/image/placeholder) HOT-WATER HOT-WATER HOT-WATER HOT-WATER RETURN SUPPLY RETURN SUPPLY CONTROL VALVE CONTROL VALVE C ③ COIL ○ PUMP COIL PUMP CHECK VALVE 0 U ① ⑨ (A) (B) Fig. 7 Pumped Hot-W ater Coil Variations: (A) Series and (B) Parallel interlock to shut the outdoor damper and open the return damper, or shut down the fan. Figure 6 shows the conventional primary/secondary (or second- ary/tertiary) arrangement where the coil pump and the pumps feeding the coil are hydraulically independent. It results in con- stant flow through the coil and in either variable flow through the primary loop, if a two-way valve is used, or in constant flow through the primary loop, if a three-way valve is used (shown dashed in the figure). In Figure 7A, the coil pump is in series with the primary pumps; this results in variable primary flow, which can affect flow through parallel coils that do not have pumps when the three-way valve moves, unless the primary system has variable-speed pumps and proper pressure control. The pump is decoupled when the three-way valve is closed to the system. The three-way valve must be oriented with the common port connected to the coil so its flow is not affected by the valve position. Figure 7B shows the coil pump piped in parallel with the primary pumps. This design has the advantage that hot-water flow can be achieved through the coil if the coil pump fails. This design results in coil flow that varies from the pump design flow rate (when the control valve is closed) up through the sum of the pump flow rate plus the primary system flow rate (when the valve is wide open). Unlike the options in the previous two figures, the primary pump must be sized for the pressure drop through the coil at this high flow rate. Similarly, the coil pump must be sized for that pressure drop and not only for the flow it supplies. Flow through the primary cir- cuit may be variable, if a two-way valve is used, or constant, if a three-way valve is used. Some systems may use a glycol solution in combination with any of these methods; however, glycol affects control valve sizing (see Chapter 47 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment) and requires additional maintenance and careful han- dling. Steam Coils. Modulating steam coils are controlled in much the same way as water coils. Control valve size and characteristics are important to achieve proper control (see Chapter 47 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment). Because the entering steam is hotter than the entering temperature of most water coils, a steam coil typically responds more rapidly and is smaller than a comparable water coil. In low-temperature applications, two- position control should be used, as discussed previously. For appli- cations that require precise control at low loads, valves should be in a 1/3 and 2/3 arrangement. Electric heating coils (duct heaters) are controlled in either two- position or modulating mode. Two-position operation uses power relays with contacts sized to handle the amperage of the heating coil. Step controllers can provide sequencing control of multiple stages of electric heat. Each stage may require a contactor, depend- ing on the step controller contact rating. Timed two-position control requires a timer and contactors. The timer can be electromechanical, but it is usually electronic and provides a time base of 1 to 5 min. Thermostat demand determines the percentage of on-time. Because rapid cycling of mechanical or mercury contactors can cause main- tenance problems, solid-state controllers are preferred. These devices may make cycling so rapid that control appears propor- tional; therefore, face-and-bypass dampers are not used. Use of electric heating coils is restricted in some areas by energy standards; check code compliance before using this application. A system with a solid-state controller and safeties is shown in Figure 8. Current in individual elements of electric duct heaters is normally limited to a maximum safe value established by the National Electrical CodeⓇ (NFPA Standard 70) or local codes. An electric heater must have a minimum airflow switch and two high- temperature limit sensors: one with manual reset and one with auto- matic reset (Figure 9). The automatic reset high-limit thermostat Inc. ASHRAE, 2019 user. single for Licensed | {}
cbcbfac9-0142-4345-9c5d-be9cad23bb9e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 48.4 2019 ASHRAE Handbook-HVAC Applications (SI) ![image](/image/placeholder) POWER SUPPLY TIME-PROPORTIONING CONTROLLER C FROM SPACE OR DISCHARGE THERMOSTAT HIGH-LIMIT SENSORS AIRFLOW SENSOR ELECTRIC HEATER Fig. 8 Electric Heat: Solid-State Controller ![image](/image/placeholder) PRESSURE DIFFERENTIAL OR FLOW SWITCH FAN INTERLOCK RELAY POWER AUTOMATIC RESET FUSED HIGH LIMIT DUCT I DISCONNECT ,H SWITCH I HEATER I worko I I I POWER - CONTROL ぬ 7 I 옹 어 ko ownoto I 웅 옹 www. I 0 I SAFETY CONTACTOR I (WHERE NECESSARY) I 。 SUPPLEMENTARY FUSES TEMPERATURE (WHERE NECESSARY SENSOR TO LIMIT CURRENT) INDEPENDENT BACK-UP LIMIT(S) MANUAL RESET Fig. 9 Duct Heater Control normally turns off the control circuit when temperatures exceed safe operating levels. If the control circuit has an inherent time delay or uses solid-state switching devices, a separate safety contactor may be desirable. The manual reset back-up high-limit thermostat is gen- erally set independently to interrupt all current to the heater if other control devices fail. If still energized, electric coils and heaters can be damaged through overheating and potentially start a fire when air stops flowing around them. Control and power circuits must inter- lock with the associated fan to shut off electrical energy when it shuts down. Flow or differential pressure switches may be used for this purpose; however, they should be calibrated to energize only when there is airflow. This precaution shuts off power if a fire damper closes or duct lining blocks the air passage. The switch con- tact should also be calibrated to avoid chattering, which can damage mechanical or mercury contacts. Radiant Heating and Cooling Radiators (more accurately called convectors) can be used either alone or to supplement another heat source. The control strat- egy depends on the function performed. For a radiation-only heating application, rooms are usually controlled individually; each radiator and convector is equipped with an automatic control valve. Depend- ing on room size, one thermostat may control one valve or several valves in unison. Unit-mounted thermostats and packaged controls allow lower component cost, better assembly quality, and avoid the cost and coordination of a second trade for remote sensor installa- tion. Wall-mounted thermostats give the best results when con- trolling the space for the comfort of seated occupants. For supplemental heating applications, where perimeter radia- tion is used to offset perimeter heat losses (the zone or space load is handled separately by a zone air system), sequence the radiation control with the main zone system to ensure there is no simultane- ous heating and cooling. In the past, it was common to control the radiant system based on outdoor air temperature reset of the water temperature perhaps zoned by exposure with a solar compensating outdoor sensor, but this can result in "fighting" between the radiator and the main zone system and is disallowed by energy standards such as ASHRAE Standard 90.1. Radiant panels combine controlled-temperature room surfaces with central air conditioning and ventilation. The radiant panel can be in the floor, walls, or ceiling. Panel temperature is maintained by circulating water or air, or by electric resistance. The central air system can be a basic one-zone, constant-temperature, constant- volume system, with the radiant panel operated by individual room control thermostats, or it can include some or all the features of dual- duct, reheat, multizone, or variable-air-volume (VA V) systems, with the radiant panel operated as a one-zone, constant-temperature sys- tem. Where hydronic tubing or electric heating elements are embed- ded in concrete, the rate of slab temperature change must be limited to prevent thermal expansion from cracking the concrete. Radiant panels for both heating and cooling require controls sim- ilar to those for a four-pipe heating/cooling fan-coil. To prevent con- densation, ventilation air supplied to the space during the cooling cycle should have a dew point below that of the radiant panel sur- face. The dew point should be actively controlled to prevent conden- sation. Outdoor air intake dehumidification and a tight building envelope or positive pressure are required. When internal latent loads increase, the chilled-water temperature for the radiant cooling panels should be reset upward if the dew point becomes too high. 3. COOLING SYSTEMS Chillers Manufacturers almost always supply chillers with an automatic control package installed. Their control functions fall into two cat- egories: capacity and safety. Because of the wide variety of chiller types, sizes, drives, manu- facturers, piping configurations, pumps, cooling towers, distribution systems, and loads, most central chiller plants, including their controls, are custom designed. In the 2016 ASHRAE Handbook- HVAC Systems and Equipment, Chapter 43 describes various chillers (e.g., centrifugal, reciprocating, screw, scroll), and Chapter 13 COV- ers variations in piping configurations and some associated control concepts. Chiller control strategies should always include an under- standing of the chiller limits for minimum flow, minimum tempera- ture, and acceptable rate of change for both. Chiller plants are generally one of two types: variable flow (Fig- ures 10 and 1 1) or constant flow (Figure 12). The figures show a parallel-flow piping configuration. Series-flow chiller configura- tions are often used in variable-primary-flow applications (Figure 10). The higher design water pressure drop of a series configuration is less of a concern in a variable-primary-flow application, because little time is spent at the maximum design flow operating condition. In Figures 10 and 1 1, the bypass line ensures minimum flow through the chiller(s). In Figure 10, flow is measured by the flow meter, and the BAS modulates the bypass valve as needed to maintain the min- imum flow required by the operating chillers. Control of the remote load determines which system type should be used. Throttling two-way coil valves vary flow in response to load, and are used with variable-flow systems. v ariable primary-only systems require greater care in design of the control system and control sequences than primary-secondary systems (Taylor 2002, 2011) but are usually more efficient. Selecting the bypass control valve and tuning the control loop is sometimes difficult because of the widely ranging differential pressure across the valve caused by its location near the pumps. Inc. ASHRAE, 2019 user. single for Licensed | {}
84634a13-86e5-4f21-ad41-b27f4b7106ed | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Design and Application of Controls 48.5 ![image](/image/placeholder) ISOLATION VALVES CLOSED WHEN CHILLER IS STOPPED THROTTLING CONTROL CHILLED-WATER VALVES SUPPLY #1 LOAD CHILLERS #2 LOAD F LOAD CHILLED- WATER PUMPS CHILLED-WATER RETURN Fig. 10 Variable-Flow Chilled- w ater System (Primary Only) ![image](/image/placeholder) CHILLED-WATER ISOLATION VALVES CLOSED WHEN WITH PUMPS CHILLER IS STOPPED ★ VARIABLE-FLOW I CONTROL #1 , LOAD CHILLERS #2 LOAD LOAD THROTTLING CHILLED- CONTROL WATER VALVES PUMPS CHILLED-WATER RETURN Fig. 11 Variable-Flow Chilled- Water System (Primary/Secondary) ![image](/image/placeholder) THREE-WAY ISOLATION VALVES ALTERNATIVE PUMP VALVES (OPTIONAL) CONFIGURATION CHILLED-WATER SUPPLY #1 LOAD EACH PUMP CHILLERS RUNS WITH ITS #2 LOAD RESPECTIVE CHILLER LOAD CHILLED- WATER PUMPS CHILLED-WATER RETURN Fig. 12 Constant-Flow Chilled- Water System (Primary Only) The valve must be large enough to bypass the minimum chiller flow through it with a pressure drop as low as the differential pressure set point used to control chilled-water (CHW) pump variable-fre- quency drives (VFDs). This is necessary because, if only a few valves are open in the system, the pressure at the differential pres- sure sensor location will be nearly equal to the differential pressure at the plant, because there is little pressure drop between these two points due to the low flow rate. This constraint makes the valve oversized for other flow scenarios that can occur, so tuning can be difficult. If the control loop is unstable, cold CHW supply can be fed back into the return intermittently and cause chillers to cycle off because oflow load or cold supply water temperatures. However, if the loop is too slow, it may not respond quickly enough to sudden changes in flow (e.g., when a large number of air-handling units [AHUs] shut off at the same time), resulting in insufficient flow through the chillers and causing them to trip on low flow or low temperature. The decision to reset the chilled-water supply temperature set point should be based on facility requirements. Chilled-water reset may not be appropriate in systems with tight space temperature and humidity requirements (e.g., hospitals, computer data centers, museums, some manufacturing facilities). Resetting the CHW tem- perature set point upward when loads are low is always an effective energy-saving strategy for constant-flow systems. In variable-flow systems, reset may or may not save energy, depending on plant design. High CHW temperature reduces coil performance, so coils in two-way valve systems demand more chilled water for the same load, degrading T and increasing flow and pump energy require- ments. Whether the net energy savings (chiller energy decrease minus pump energy increase) is positive and sufficient to offset the cost of implementing the reset strategy depends on chiller perfor- mance characteristics and the nature of coil loads. Resetting the CHW temperature set point also prevents unstable operation of con- trol valves under very low loads. To ensure that no loads are starved, the chilled-water set point should be reset from the zone or system valve with the greatest load (load reset) (Taylor 2011). The constant-flow system (Figure 12) is only constant flow under each combination of chillers on line; chillers and pumps can be staged if all loads experience similar loads at all times. If that is the case, the plant can supply about 80% of the design flow withjust one of the headered pumps, and the chillers can be sequenced based on return temperature. Both pumps would run simultaneously only under peak demand. Staging may be prevented even at low plant loads if some coils are at high load while others are at low load, causing the chillers to operate at low loads, reducing plant effi- ciency. Use of constant-flow systems may be limited to smaller sys- tems by energy codes. Chiller Plant Operation Optimization Chapter 42 discusses optimized control of chiller plants and details the control strategies that can be applied. This section high- lights the general conclusions that can be drawn from the specific optimization strategy in the section on Sequencing and Loading of Multiple Chillers of that chapter. Multiple chillers of different characteristics should be operated at a point that minimizes overall plant power consumption, consid- ering the power consumption of the auxiliary chilled- and condenser water pumps and cooling tower fans as well as the consumption of the chillers and the load fans (Hartman 2005). For the general case of chillers with different part-load characteristics, operate multiple chillers at identical supply temperatures but different flows to achieve equal partial derivatives of the individual chillers' power consumption with respect to their loads. That is, the ratio of the incremental change in thermal load to the incremental change in input power should be identical for each online chiller. For identical chillers, this is achieved by loading them equally. For constant-speed-drive chillers, sequencing is straightforward. It is best to run one chiller until fully loaded before bringing on a second machine. This dynamic changes for chillers with variable- speed drives, or if the chilled-water pumps are piped in a parallel (headered) arrangement or do not have variable-speed drives; for plants of this configuration, often overall plant power consumption is minimized when more chillers are operating at reduced load com- pared to fewer chillers operating at higher loads. To meet any given plant load, many possible combinations exist for operating points of system equipment (e.g., chillers, pumps, cooling tower fans, air handler fans). When any given piece of equipment's operation point is changed, the operating point of at least one other piece of equipment must be changed to compensate. This results in one component reducing its power use and the other increasing it. Depending on how much each changes, total power Inc. ASHRAE, 2019 user. single for Licensed | {}
a0318200-69f6-4bfc-bbb9-69573d89d31d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 48.6 2019 ASHRAE Handbook-HVAC Applications (SI) use may increase or decrease. The combination of component oper- ating points that results in minimum plant power consumption occurs when all the equipment in each subset that affect a variable (e.g., temperature, load, flow) operate at points where the power consumption partial derivative to the affected variable for each piece of equipment is equal. A practical method to obtain the highest possible plant efficiency for current weather and load conditions uses a mathematical plant energy performance model and minimization to find the most effi- cient set of set points and commands. Alternatively, the most effi- cient configuration is precalculated for all foreseeable conditions and the control commands are then obtained from a lookup table (Nelson 2012). When detailed information about the plant components' part-load energy performance for multiple scenarios is unavailable, or when sophisticated controls are beyond budget, use the following strate- gies. In most cases, they increase energy performance and are rela- tively easy to implement. However, return-on-investment analysis of controls of different sophistication levels is recommended, because the energy savings tend to quickly pay for the additional cost. Cooling Tower Relief. Lowering the condenser water tempera- ture by operating the tower fans at a higher speed reduces the com- pressor lift and the energy consumed by the chillers. Lowering the lift too much, however, may cause the fans to consume more energy than is saved by the chillers. A condenser temperature set point reset (to maintain constant tower approach [when the outdoor wet-bulb temperature is available] or proportional to the heat rejected or based on outdoor air temperature, and limited to the minimum chiller lift as recommended by the chiller's manufacturer), results in chiller en- ergy savings of 1 to 3% for each 1 K reduction in water temperature for constant-speed chillers, and 2 to 5% for each 1 K reduction for variable-speed chillers. Chiller lift is defined as the difference be- tween the chillers' leaving condenser water temperature and leaving evaporator temperature. Supply Chilled- w ater Temperature Reset. Increasing the supply temperature also reduces the chiller lift with similar savings per degree. Consider the effect on the loads and distribution pumps, because variable-speed pumps always (and fans sometimes) need to run harder, offsetting some or all the chiller energy savings. Also, some loads may not get enough cooling and be unable to maintain room temperature. Dehumidification requirements further limit the range of allowed supply temperature increase. As a first approach, the supply temperature set point can be reset between design value and 27 K proportional to the heat load or outdoor air temperature, or to maintain the most open cooling valve in the loads close to full open. Maximize the Number of v ariable-Speed Cooling Towers Used. Depending on the minimum flow needed by the cooling towers, more than one tower per chiller may be used. For example, two variable-speed towers can dissipate the same amount of heat as one tower by running at half the speed, and use about 1/8 of the energy. Optimize the Number of Chillers Running. Ifthe chillers' per- formance improves at part load (e.g., variable-speed centrifugal chillers), adding chillers before they are fully loaded results in more efficient configurations. Use the amount of heat removed or the kilowatts consumed by the chillers and, as a first approach, add a chiller when the operating chiller(s) are at 80% of capacity and shed one when they reach 35%. Maximize (Return Temperature - Supply Temperature). Constant-flow chilled-water systems and constant-speed primary pumps result in more flow than needed for the amount ofheat trans- ported. The excess flow causes unnecessary pump energy use and increased compressor lift, which reduces chiller efficiency. Vari- able primary systems with two-way valves on all loads are the most efficient, but require a system bypass valve and careful control to prevent tripping the chillers (and potentially freezing them) because of low flow, when the load valves close, or when adding chillers. Systems with variable primary and variable secondary pumps and an open decoupler line are the next best in efficiency; they can be controlled to match the primary flow with the secondary, except to maintain the chillers' minimum flow. Next in efficiency are systems with constant primary and variable secondary pumps; these systems are robust and significantly simpler to control, not even requiring flow meters (hence their popularity). Constant-flow systems, which operate at part load most of the time, have the worst energy effi- ciency in most HVAC systems. Performance Monitoring. Research (Deng and Burnett 1997; Erpelding 2007; Hartman 2012) shows that chiller plant perfor- mance begins to degrade soon after chillers are commissioned un- less some form of ongoing commissioning is in place. The cause is usually equipment malfunction, poor maintenance, and/or inappro- priate operation, which is difficult to detect in the complexity of plant operation. A performance-monitoring and -diagnosing system, especially an automated one, identifies deviations from ex- pected operation and provides insights into their causes as well as suggesting improvements, thus prompting action and greatly con- tributing towards plant energy savings throughout its life cycle. Cooling Tower Cooling tower fans are typically controlled to maintain con- denser water supply (CWS) temperature set point, as described pre- viously. The CWS set point may be reset based on chiller load or, in the case ofhydronic free cooling, space conditions. Figure 13 shows a typical cooling tower control schematic. When the system includes large condenser water sumps, the tem- perature sensor' s location must be considered. Large sumps intro- duce significant time delays into the system that must be accounted for in system design and operation. Often, condenser water supply piping does not run full at all times, particularly when draining to a sump. In this case, placing the temperature sensor so that is in contact with the water is important. This may necessitate locating the sensor on the bottom of an elbow or angled into the lower half ofthe pipe (to avoid mounting at the pipe bottom, where it could be susceptible to moisture collection). Two-speed motors or variable-speed drives can reduce fan power consumption at part-load conditions and stabilize condenser water ![image](/image/placeholder) CT-1 START/STOP CT-1 ALARM CT-1 SPEED CT-1 CTS CT-1 STATUS TEMPERATURE · CONDENSER ASD WATER RETURN 人 人 人 VS FLOAT VALVE D81 BASIN ⌀t CONDENSER HEATER WATER CONTACTOR SUPPLY GRADE Fig. 13 Cooling Tower Inc. ASHRAE, 2019 user. single for Licensed | {}
d88c19cf-bc57-4cb7-bb1d-76dadfc83768 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Design and Application of Controls 48.7 temperature. Variable-speed drives (VSDs) improve control be- cause fan speed can be better matched to the cooling load. When there are multiple towers, efficiency is maximized when as many cells as possible are active, which increases mass transfer area and reduces required fan speed. It may be necessary, however, to shut off flow to some cells to maintain minimum tower flow rate, as recom- mended by the tower manufacturer to minimize scaling. Fan speed should be controlled as follows. Two-Speed Motors. The lowest fan speed should be used. For three two-speed towers, staging should be as follows: Tower Stage 1 Stage 2 Stage 3 Stage 4 Stage 5 Stage 6 Stage 7 ¦ 1 ¦ Off ¦ Low ¦ Low ¦ Low ¦ High ¦ High ¦ High ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 2 ¦ Off ¦ Off ¦ Low ¦ Low ¦ Low ¦ High ¦ High ¦ ¦ 3 ¦ Off ¦ Off ¦ Off ¦ Low ¦ Low ¦ Low ¦ High ¦ Provisions should be made to decelerate the fan when switching from high to low speeds. Variable-Speed Drives. All of the operating tower fans should operate at the same speed. Tower fans should also have a vibration switch hard wired to shut down the fan if excessive vibration is sensed. Most tower manufacturers do not recommend bypassing water around the tower as a normal temperature control function, because this causes localized drying of the tower media and spot scaling. Bypass valves may be required for some low-temperature opera- tions or hydronic economizer operations. Check with the tower manufacturer for bypass valve applications. Where year-round tower operation is required in cold regions, cooling towers may require sump heating and/or continuous full flow over the tower to prevent ice formation, and may also require deicing. The cooling tower sump thermostat controls an electric heating element or hot-water or steam valve to keep water in the sump from freezing. Typically, sump heating is locked out during tower operation and when outdoor air temperatures are above freezing. When operating the tower in cold weather, full water flow is needed to prevent localized ice formation. Iftowers build up ice, reversing the fan rotation and sending air backward through the tower can deice them, either manually or automatically. Many operating personnel prefer to do this operation manually so they can observe the towers while deicing is under way. If deicing cycles are needed, the fan starter or VSD must be able to reverse the fan direction. There should be deceleration time interlocks so that the fans spin to a stop before engaging reverse operation. Automatic deicing control strategies are available from tower man- ufacturers. Towers that have internal balancing piping or chambers must be allowed to drain into the basin when the tower is not operating in cold weather. Auxiliary Control Functions. The control system may be re- quired to cycle a fill valve to maintain sump level, or to monitor water consumption or water treatment systems. Ifthe tower does not have sump heaters, the control system may be required to drain the tower and piping when outdoor air approaches freezing, and refill the tower on the next call for cooling. Air-Cooled Chillers Air-cooled chillers are controlled similarly to other chillers. If the chiller is to operate during cold weather, it must be equipped with a low-ambient kit. Typically this is a modulating damper or variable-speed fan that limits airflow across the condenser, usually provided as part of the chiller package. In very cold conditions, additional equipment is required. With variable-flow evaporators, careful attention to the manufacturer's recommended minimum flow must be observed. Chilled-water supply temperature can be reset as described above. The chiller may be equipped with a barrel heater, usually controlled by the chiller's packaged controls, to pre- vent the evaporator from freezing in cold weather. Water-Side Economizers Water-side economizers use cold water from the cooling tower to produce chilled water without (or with reduced) mechanical refrigeration. This is accomplished by running the cooling towers to produce water typically at or below 7°C while ambient wet-bulb temperatures are low. The cold water is pumped through a low approach water-to-water heat exchanger (HX), usually a plate-and- frame type, to produce chilled water at or below 10°C. The heat exchanger prevents contamination of the chilled water by debris and chemicals found in tower water. The heat exchangers can be piped in series or in parallel. With parallel operation, the heat exchanger functions like another chiller. In series arrangement, the heat exchanger precools the chilled-water return to the chillers. When there is enough heat exchanger capacity, the chillers may be turned off and a bypass opened to direct flow around the chillers. The series arrangement allows for integrated (simultaneous) economizer and chiller operation, which is required by some energy standards such as ASHRAE Standard 90. 1 . Chilled-water temperature is controlled by varying the tower fan speed. When changing from water-side economizer mode to chiller mode, the condenser water is cold, which requires that chiller head pressure control be addressed. Con- sult the chiller manufacturer for the requirements of each specific machine. To maintain condenser head pressure, many manufacturers recommend self-contained modulating valves or control valves modulated by the BAS or, preferably, by the chiller controller (many have head pressure control outputs as standard). When modulating the condenser water flow to maintain head pres- sure, the flow switch may need to be bypassed for a short time to keep the machine operating; consult the manufacturer. When the signal used for modulating the valve is controlled by the BAS, it should be directly from a pressure transmitter; relying on pressures obtained from the chiller controller through a network connection can be unstable or unreliable because data refresh rates may be slow or inconsistent. Cooling Coil Chilled-water or brine (glycol) cooling coils are controlled by two- or three-way valves (Figure 14). These valves are similar to those used for heating control, but are usually closed to prevent cooling when the fan is off. The valve typically modulates to main- tain discharge temperature or space temperature set point. Direct-expansion (DX) cooling equipment is usually con- trolled by an air, space, or coil discharge temperature feedback loop in discrete stages, by starting and stopping compressors and by applying mechanical unloaders, liquid-line solenoid valves, or hot-gas bypass valves. Most DX systems for commercial applica- tion have one to SIX stages. ![image](/image/placeholder) CHILLED- CHILLED- CHILLED- CHILLED- WATER WATER WATER WATER RETURN SUPPLY RETURN SUPPLY I C NO NC NC 0 COOLING COOLING COIL COIL AIRFLOW AIRFLOW A. TWO-WAY VALVE B. THREE-WAY VALVE Fig. 14 Control of Chilled- w ater Coils Inc. ASHRAE, 2019 user. single for Licensed | {}
301b8c73-3486-43b2-8ccd-3fa5ec9692dc | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 48.8 2019 ASHRAE Handbook-HVAC Applications (SI) When set up properly, a cycling DX system under a steady load operates like a two-position control loop (see Chapter 7 of the 2017 ASHRAE Handbook-Fundamentals). Some stages run steadily, and one stage cycles on and off. The behavior of the closed loop can be described by the cycling rate and corresponding swing in controlled air temperature. Most algorithms for DX control address both temperature control (e.g., set points, feedback gains, staging dead bands) and equipment cycling restriction (e.g., minimum-on timer, minimum-off timer, interstage delay). These two characteris- tics are inextricably linked by thermal sizing and loading condi- tions. Either characteristic can be affected by adjusting the control algorithm, but it is not possible to affect both characteristics inde- pendently: any reduction in temperature swing is accompanied by an increase in cycling rate. Overtightening temperature control will conflict with cycle controls and be rendered irrelevant. When set up improperly, a DX system may cycle through multiple stages as the temperature oscillates around the set point, rather than having only one stage cycle on and off. Compared to proper operation, both the cycle rate and temperature swing are excessive. This operation can usually be corrected by adjusting parameters in the feedback algorithm. Some staging systems are arranged so that it takes a greater temperature error to activate the higher stages. The result is that, at higher loads, the system operates at higher temperatures, which is usually not desired; it is usually intended that the system operate in the same temperature range, regardless of loading on the stages. This can be accomplished in many ways, including a proportional- plus-integral (PI) controller output driving a staging module. Ifthe DX system serves a single zone, the feedback signal is usu- ally the space temperature, which usually varies by 0.5 to 2.2 K. If the DX equipment serves multiple zones, as in a VAV air handler, the feedback signal is usually the coil discharge temperature. Mea- sured at this point, temperature swings appear much larger, though the effect on zone comfort is the same. When adjusting or specifying a DX system for discharge temperature control, it is important to allow the wider range of temperatures. Also, DX staging capacity on VAV applications should be limited based on air-handling unit (AHU) airflow rate, especially at low-part-load conditions, to pre- vent the coil from freezing. Heat pumps are a variation ofDX systems. (See Chapter 9 ofthe 2016 ASHRAE Handbook-HVAC Systems and Equipment for a detailed description.) Typically, heat pumps are controlled using manufacturer-supplied package controls. A hard-wired space tem- perature sensor or thermostat is connected to the unit. The controls regulate the unit' s staging and cycling of any control valve(s). A BACnet� interface is available on many heat pump units, and can be wired to a BACnet network for monitoring and supervision. Typical BACnet objects include the following: ¦ Analog Inputs ¦ Analog Outputs ¦ Analog Values ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Space temperature ¦ Space temperature set point ¦ Occupied cooling set point ¦ ¦ Supply air temperature ¦ ECM fan override ¦ Occupied heating set point ¦ ¦ Effective cooling set point ¦ Fan variable-frequency- drive (VFD) speed control ¦ Unoccupied cooling set point ¦ ¦ Effective heating set point ¦ Fan variable-frequency- drive (VFD) speed control ¦ Unoccupied heating set point ¦ ¦ Multistate Inputs ¦ Multistate Outputs ¦ Multistate Values ¦ ¦ Effective occupancy state ¦ Occupancy command ¦ Cycle fan ¦ ¦ Effective mode of operation ¦ Fan command ¦ ¦ ¦ Compressor status ¦ Compressor command ¦ ¦ ¦ Fan status ¦ Emergency heat command ¦ ¦ Depending on the BACnet device, many more objects may be available. Some objects may be read-only; these are generally field input sensors (e.g., temperature) or objects that could cause equip- ment damage if commanded inappropriately (e.g., commanding compressor directly). Writable objects are available to the BAS for commanding (e.g., set points). 4. AIR SYSTEMS Variable Air Volume (VAV) Variable-air-volume systems provide thermal control by varying the amount of airflow delivered. A reduction in demand for cool air means the supply fan can operate at a reduced speed, saving energy. Most VA v systems have pressure-independent terminals, which means a separate airflow control loop operates each terminal damper. Supply Fan Control. The VAV supply fan controller · Ensures pressure in the duct is enough to serve the terminals · Prevents excessive pressure from disrupting terminal flow loops · Reduces the risk of excessive pressure from damaging duct sys- tems · Allows for reduced energy consumption at the fan · Keeps the fan in a stable region of the pressure-flow curve Historically, various mechanisms (e.g., bypass damper, variable inlet vanes) have been used to regulate fan output. These methods vary widely in efficiency and energy consumption. Currently, vari- able-speed drives (VSDs) and electrocommutated (EC) motors are the most common because their low energy consumption and low first cost makes them cost effective. They are prescriptively required for most VA v systems by energy standards such as ASHRAE Stan- dard 90.1. The most common variable-airflow method is a closed-loop proportional-with-integral (PI) control, using the pressure measured at a selected point in the duct system. Historically, the set point was a constant, selected by the designer and confirmed by the balancer during system commissioning. However, this control strategy is based on the readings of a single sensor that is assumed to represent the pressure available to all VAV boxes. Choosing duct pressure sensor location can be difficult: if it malfunctions or is placed in a nonrepresentative location, operating problems will result; if it is located too close to the fan, the sensor will not sufficiently indicate service of the terminals. This usually leads to excessive energy con- sumption. Some have reported that placing the sensor at the far end of the duct system couples fan control too closely with the action of a single terminal, making it difficult to stabilize the system. Experi- ence indicates that performance is satisfactory when the sensor is located at 75 to 100% of the distance from the first to the most remote terminal (Figure 15). ASHRAE Standard 90.1 prescriptively requires that the location result in a set point no higher than one- third of the total system static pressure drop. Even with a good sensor location, fixed-pressure set point uses more energy than necessary. There are many operating hours when the fan pushes air through a system full of partly closed dampers. Many energy standards such as ASHRAE Standard 90. 1 prescrip- tively requires automatically adjusting duct pressure based on zone demand as system load varies for systems with DDC at the zone level integrated with the air handler control. Airflow to zones is still regulated by flow loops in the terminal controllers and is unaffected, but all else being equal, the system meets the load more efficiently with the terminal dampers closer to open. This reduces energy con- sumption at the fan. Ideally, pressure is reduced to the point that at least one of the dampers opens all the way. Any further supply fan speed reduction reduces airflow at the terminals. Many methods have been published to automatically reset duct pressure (Ahmed 2001; EDR 2007; Englander and Norford 1992). Inc. ASHRAE, 2019 user. single for Licensed | {}
fe85bec3-9de0-4c96-9b7f-3b15dfa0d1e3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Design and Application of Controls 48.9 Reported energy savings, monitored over weeks or months, have ranged from 30 to 50% of fan energy used by the same system run- ning with a constant-pressure set point. All of these reset designs use data from terminal controllers to alter fan operation. Most reset strategies use zone control data to adjust the set point of the duct pressure control loop. This makes the location of the pressure sensor much less important. Other reset strategies (Hartman 1993) eliminate the pressure control loop, using data from zones to drive the fan directly. Reset strategies may be categorized according to the type of data collected from the terminal controllers. At least three approaches are in commercial use. The terminal controllers may deliver · Damper position (or damper position and flow error) · Flow set point · Saturation signal (terminal indicates that the pressure is insuffi- cient) Data available for coordinating a fan control system vary with the model of terminal controller. Most have both a flow set point and a damper position value, though the suitability of the data for coordination varies. Control system designers should ensure that the data available from terminal controllers, the fan control strat- egy, and network data capacity are compatible. The signal selected for coordination can determine the data com- munication load that the fan control strategy places on the network. Flow set points and saturation signals tend to change less often than damper position or flow measurements, so using them may be more practical with lower available bandwidth, especially in systems with many terminals. Saturation signals are binary, so they do not indi- cate their distance from the critical point. This can affect reset algo- rithm design. One approach (using damper position data) is based on the idea that the desired mechanical operating point occurs when at least one damper is fully (or almost fully) open, and all terminals deliver the required flow. The fan controller processes damper position data from each terminal and adjusts duct pressure (or fan speed) to drive one damper open. To ensure that the open box is not starved, the reference may be set a little lower (95% open, for example), or the controller may check flow (or flow error) data from the terminal controllers. Floating actuator application methods may result in unreliable damper position values for some terminal controllers. It is important to take this into account when selecting a reset method. Rogue zones can provide false feedback and keep the fan at a higher speed than is necessary, and should be identified and cor- rected or removed from the control logic. Rogue zones can be ![image](/image/placeholder) AIR TERMINALS SUPPLY FAN DUCT VSD I DP 75% of L 100% of L Fig. 15 Duct Static-Pressure Control caused by improper box sizing, false thermostat readings, or con- stantly loaded spaces. Another approach (using flow set points) is based on the fact that the required pressure depends on the distribution system (ducts, terminals, diffusers) and required flow. One way is to add the flow set points from each terminal and then use an empirically determined function to set the pressure. A more exact approach puts the individual flow set points into a calibrated model of the duct network, and calculates the pressure needed at fan discharge to drive the required flow to each terminal (Kalore et al. 2003). This online optimization applies the same calculations used to size a fan in real time. The pressure control loop then adjusts the fan speed to maintain the calculated pressure, which results in all terminals being satisfied, with one critical damper fully open (Ahmed 2001, 2002). This method is now in commercial use. In contrast to a reset based on damper position or saturation signals, a reset based on flow set point is open loop; this means that performance depends on careful calibration, but is inherently stable. A third approach (using a saturation signal) distributes more of the logic. Each terminal controller uses flow data, damper position data, timing, or other information to decide whether its local loop is sufficiently supplied by the fan. If not, the saturation signal is acti- vated. If a saturation signal is available, then the fan control algo- rithm depends less on the details of the terminal control than other methods. These signals are typically mated with a fan algorithm that ramps pressure up or down according to the number of unsatisfied terminals or resets static pressure set point using trim-and-respond logic (Taylor 2007). To specify a pressure reset system, a designer can select the fan control algorithm, data that integrate terminal controllers, and char- acteristics ofthe communication network. Alternatively, the designer can specify the logic in performance terms (i.e., that the intended mechanical operating point is the lowest pressure that satisfies the terminals with at least one damper wide open). A performance- based specification allows proposals from vendors with a wider variety of equipment and algorithms. Duct Static Pressure Limit Control. In larger fan systems, or where fire or fire/smoke dampers could close off a significant per- centage of airflow, static pressure limit controls are recommended. When the high limit set point is reached (or low limit on the suction side of the fans for systems with economizer dampers), the fan is deenergized. Limit controls should be manually reset. On large fans, inertia of the fan wheel could damage the ductwork even after the fan is deenergized. Additional protection for the ductwork (e.g., duct pressure relief doors or mechanical relief dampers) is needed in these situations. Space Pressure Control. Differential static-pressure control, differential airflow (CFM offset), and directional bleed airflow are methods used to control pressurization of a space relative to adja- cent spaces or the outdoors. Typical applications include pressure barriers for any occupied space to prevent infiltration of moist unfil- tered and untreated air, or to maintain interior comfort conditions. Applications requiring higher-performance controls include clean- rooms (positive pressure to prevent infiltration; see Chapter 18), laboratories and health care infection control (positive or negative, depending on use; see Chapter 8), and various manufacturing pro- cesses, such as spray-painting rooms (see Chapters 31 and 32 for industrial applications). The pressure controller usually modulates fan speed, dampers or airflow valves to maintain the desired pres- sure relationship or bleed airflow direction as exhaust volumes change. An alternative is to supply sufficient makeup air and to modulate a separate exhaust system to maintain space pressuriza- tion flow as auxiliary exhausts in the space are turned on or off. Health Care Pressurization Codes, Regulations, and Appli- cation Design Guides. The Facility Guidelines Institute (FGI 2014) incorporated ASHRAE/ASHE Standard 170 into their guidelines. Inc. ASHRAE, 2019 user. single for Licensed | {}
26e5785c-9f9b-4589-805e-e937512bd819 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 48.10 These guidelines include requirements for differential pressure or differential flow control for rooms such as positive and negative iso- lation rooms. Refer to the guidelines for details. Building Pressurization. A slight positive building pressure (1 to 20 Pa) is generally desired to reduce infiltration of unconditioned outdoor air. Pressure results from the development of a pressuriza- tion flow between adjacent pressure zones. A zone is positive to an adjacent zone if the pressurization flow across the zone barrier is positive. Generally, outdoor air is required to pressurize the building as a whole. Building static pressure control is one method for control of the relief or exhaust fan; this requires direct measurement of the space and outdoor static pressures. The inside static pressure measuring location must be selected carefully, away from openings to the outdoors, elevator lobbies, and other locations where it can be affected by wind pressure and drafts. Stack effect also affects the reading for tall buildings in hot or cold weather; multiple pressure zones with independent sensors controls may be required to main- tain positive pressure on all floors without overpressurizing some. The outdoor static pressure measuring location must also be selected carefully and oriented to minimize wind effects from all directions. Even with good sensor port locations, pressure read- ings can fluctuate and should be buffered before using for control. If multiple fan systems serve areas that are open to one another, a single pressure control loop should be used to prevent instability. The amount of minimum outdoor air for pressurization varies with building permeability and relief or exhaust fan operation. Con- trol of building pressurization can affect the amount of outdoor air entering the building. Proper return fan control for VAV systems is required for building pressurization. In one approach, outlined in ASHRAE Guideline 16, the return fan is controlled to maintain the return air plenum pressure while exhaust (relief) air dampers are controlled to maintain building static pressure (see Figure 16). For relief fan systems, the relief fan speed is generally directly controlled by building pressure. Direct-measurement pressurization flow compares an interior static pressure location to an outdoor reference to modulate relief fan speed or relief dampers. This control allows for greater opera- tional repeatability, and improved energy savings potential where there are natural relief paths such as operable windows. Indirect building pressure control uses duct or fan airflow mea- surements to control a fixed differential air volume by modulating dampers, fan speed, or discharge rates (Figure 17). Because return air is typically the controlled variable and its rate is set to track the normal changes in VAV supply at a fixed rate, this method is referred to as return fan or airflow tracking. The airflow differential set point is often determined empirically during commissioning as ![image](/image/placeholder) DP BUILDING PRESSURE CONTROL RETURN FAN CONTROL L H LOBBY M VSD MINIMUM OUTDOOR SUPPLY FAN CONTROL AIR CONTROL DP M M VSD LIM AFS + Fig. 16 Supply/Return Fan Control 2019 ASHRAE Handbook-HVAC Applications (SI) that needed to maintain a slight positive pressure with doors and windows closed. Using fixed-differential air volume to maintain pressurization flow, rather than measured space static pressure, results in very stable control. It avoids the instabilities described previously for direct pressure control caused by fluctuating pressures from gusts of wind, opening doors and windows, and multiple air-handling sys- tems serving interconnected areas that interact. However, the con- trol is indirect, so actual space pressure varies (e.g., with stack effect as outdoor air temperature changes). Also, fan tracking is less reli- able than direct-measurement pressurization control because the cumulative error of the two airflow measurements can be large, par- ticularly at low supply/return airflow rates (Advanced VAV Design Guidelines). Airflow quantity is indicated in Figure 18 by Q. QP is leakage in or out of the room, driven by the net pressure differential. Note that each surface may have a different P because this value is relative to the pressure in the space on the other side of the wall. When the control strategy changes from occupied (ventilation air required) to unoccupied warm-up, which does not require ventila- tion but needs thermal control to change the air-balancing require- ments, warm-up is accomplished by setting return airflow equal to or just slightly less than the supply fan airflow, with toilet and other exhaust fans turned off and limiting supply fan volume to return fan capability. If exhaust fans remain running, then the supply fan must deliver sufficient outdoor air to make up the exhaust and still have a slightly pressurized space. During night cooldown, when using large quantities of outdoor air, the return fan operates in the normal mode (Kettler 1995). Unstable fan operation in VAV systems can usually be avoided by proper fan sizing. However, if airflow reduction is large (typi- cally over 60%), fan sequencing is often required to maintain air- flow in the fan's stable range. Zone-based static pressure set point Fig. 18 Building Pressure Model ![image](/image/placeholder) RETURN FAN FLOW RETURN AIR STATION VFD F I F SUPPLY FAN FLOW SUPPLY AIR STATION Fig. 17 Airflow Tracking Control QEX(local) QEX(AHU) QRA Qp QRec QOA Q SA BUILDING BUILDING PRESSURE MODEL: Qp = QOA -QEX MATHEMATICAL EQUIVALENT: QRec + QOA = QSA QRec + QEX = QRA QOA - QEX = QSA - QRA Inc. ASHRAE, 2019 user. single for Licensed | {}
a14a399f-d7a4-4d72-b9a6-e9cd903b304d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Design and Application of Controls 48.11 ![image](/image/placeholder) DP! L H LOBBY VSD SIGNAL SELECTOR M D H VSD + V Fig. 19 Minimum Outdoor Air Control Using Differential Pressure Controls reset, described previously, also allows the fan system with variable- speed drives to almost completely avoid the unstable region of its operating curves until fan speed is so low that instabilities are minor. This logic can allow very large VAV fans to serve very small air- flows, during off-hours for instance. Supply air temperature reset can be used to improve energy performance in most multiple-zone systems, including VAV sys- tems, and is prescriptively required by energy standards such as ASHRAE Standard 90. 1 for systems that have simultaneous heating and cooling at the zone level. In cool weather, supply air tempera- ture can be reset upward based on zone demand, similar to static pressure reset. This reduces reheat energy losses and extends econ- omizer operation, reducing mechanical cooling energy. In warmer weather, when space heat is not needed, supply air temperature should be reduced to reduce fan energy (EDR 2007). Minimum Outdoor Air Control. Fixed minimum outdoor air- flow control provides dilution air for ventilation, pressurization flow (usually exfiltration), and makeup air for exhaust fans. In some circumstances, minimum outdoor air may also provide combustion air for processes converting fuel to heat. Several variations of minimum outdoor airflow control for VAV systems are possible (ASHRAE 2011; Felker and Felker 2010; Ket- tler 2000): · Differential pressure is measured across the outdoor air intake louver or two-position minimum outdoor air damper. The differ- ential pressure set point correlating to the minimum outdoor air- flow is determined by measuring intake airflow directly upstream of the outdoor air damper in the field. This set point is maintained by modulating the return damper when not in economizer opera- tion (Figure 19). · A dedicated outdoor air injection fan with airflow station (Fig- ure 20). · An airflow station installed in the minimum outdoor air section with a minimum flow rate maintained by modulating the intake and return dampers in sequence (Figure 21). In this case, the intake opening should be sized for velocities high enough to facil- itate measurement; some airflow sensors have relatively high minimum velocity requirements. According to the Standard 62.1 User's Manual (ASHRAE 2016), VAV systems require one ofthe preceding methods for min- imum outdoor air control or similar dynamic airflow controls for compliance; a fixed minimum damper position or a fixed-speed outdoor-air fan without control devices will not maintain rates within the required accuracy without overventilating. ASHRAE research project RP-980 (Krarti et al. 2000) and the Standard 62.1 User 's Manual suggest that return fan or airflow tracking are unsatisfactory for minimum outdoor ventilation control because even small errors in measurements of total supply airflow ![image](/image/placeholder) RETURN EXHAUST FAN RETURN AIR AIR D M S/S I S/S DM SUPPLY OUTDOOR SUPPLY NC FAN AIR AIR S/S FLOW OUTDOOR STATION AIR Fig. 20 Minimum Outdoor Air Control with Outdoor Air Injection Fan ![image](/image/placeholder) RETURN AIR M M VSD AFS + M MINIMUM OUTDOOR AIRFLOW MEASUREMENT RETURN AIR M VSD AFS + AFS M T TOTAL OUTDOOR AIRFLOW MEASUREMENT USING STAGED AIRFLOW STATIONS Fig. 21 Outdoor Air Control with Airflow Measuring Stations and total return flow can cause significant errors in the determina- tion and control of minimum outdoor airflow rates. Although air- flow tracking may be an option for building pressurization control, minimum outdoor air must be controlled independently. Measuring the total outdoor airflow range of a VA V design from a minimum of less than 50% to maximum design capacity requires a measurement tool that can provide the needed reliability across the entire anticipated temperature and velocity range. One way to do this with pitot arrays is to subdivide the intake and use dual airflow stations sized for 1/4 and 3/4, or 1/3 and 2/3, of the maximum opening size. This increases the velocity pressure for the pitot array to ensure accurate measurement at minimum pressure drop (Kettler 2000). Thermal velocity sensors, which have a much lower minimum velocity than pitot devices, may be used without creating damper sections. Regardless of the type of system, pressurization flow rate and outdoor airflow rate are controlled separately: the two functions are related but must be independently controlled. The outdoor airflow set point for dilution ventilation should be established using ASHRAE Standard 62.1. In addition, the outdoor air set point for pressurization should be established by adding the pressurization flow requirement to the sum of the local exhausts in the zones served by the air-handling system. The greater of the two dictates the outdoor air set point. Traditional economizer controls call for the outdoor air and recir- culation dampers to be modulated inversely to maintain set point: one opens as the other closes. A more energy-efficient approach for VAV systems is to decouple the outdoor air and recirculation Inc. ASHRAE, 2019 user. single for Licensed | {}
f9f00812-7f68-4ed9-82ad-506fa7bdbd24 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 48.12 Chart Type: line Supply Air Temperature Control Loop Output Signal Minimum Position Outdoor Air Damper item_01 100% 0% 100% Fig. 22 "Integrated" Economizer Cycle Control dampers by individually actuating each. The outdoor airflow rate is then controlled by sequencing the dampers (ASHRAE Guideline 16). This reduces pressure drop and thus reduces fan energy. Dynamic Reset of Minimum Outdoor Air Intake Rates. Demand-controlled ventilation (DCV) is a control scheme de- signed to reduce minimum outdoor air levels when the spaces served have less than design occupancy. The most common scheme is to use CO2 concentration to reset the occupant component of the minimum outdoor air rate required by ASHRAE Standard 62.1. Ventilation reset control (VRC) is a related control scheme for re- setting outdoor air and minimum supply air rates as system venti- lation efficiency changes because of operational changes in the system. Both control schemes are required by ASHRAE Standard 90. 1 for many applications and are described in detail in the user's manual (ASHRAE 2011) for ASHRAE Standard 62.1. When implementing dynamic ventilation reset schemes that re- duce outdoor air intake, ensure that pressurization flow is maintained (i.e., the relationship between outdoor and exhaust air is maintained). When outdoor air dew point approaches or exceeds 16°C, a net pos- itive pressurization flow is required to prevent transport of water and outdoor air contaminants into the building or its envelope (ASHRAE Standard 62. 1). Air-Side Economizer Cycle. Economizer-cycle control reduces cooling costs when outdoor air is cool and dry enough to be used as a cooling medium. The economizer is enabled when outdoor air conditions are below the high-limit device setting. When enabled, the economizer return and outdoor air dampers modulate to main- tain a supply air temperature in sequence with the mechanical cooling. Typically, the economizer is controlled in sequence with the mechanical cooling, using the same supply air temperature con- trol loop. Figure 22 shows integrated control, in which the econo- mizer and mechanical cooling can be active at the same time. This is prescriptively required in most applications by ASHRAE Stan- dard 90. 1. When the outdoor air temperature exceeds the econo- mizer high-limit set point, the economizer is disabled and only minimum outdoor air is supplied. ASHRAE Guideline 16 addresses the sizing and selection of dampers for outdoor air economizer systems. Table 1 summarizes the guideline's recommendations as a function of the relief air system. Refer to the guideline for additional details and rationale. High-limit controls are intended to disable the economizer when supplying outdoor air would use more energy than recirculating air. Common high-limit controls are · Fixed dry-bulb temperature (compares outdoor air dry bulb to a fixed set point) 2019 ASHRAE Handbook-HVAC Applications (SI) Table 1 Economizer Damper Type and Sizing ¦ Relief System ¦ Damper ¦ Blade Type ¦ Face Velocity, m/s ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Return Fan ¦ Relief/exhaust ¦ Opposed ¦ 5.1 to 7.6 ¦ ¦ ¦ Outdoor air ¦ Parallel ¦ 2.0 to 5.1 ¦ ¦ ¦ Return air ¦ Parallel ¦ Per P across damper ~7.6 ¦ ¦ Relief Fan or ¦ Outdoor air ¦ Parallel ¦ 2.0 to 5.1 ¦ ¦ Barometric ¦ Return air ¦ Parallel ¦ 4.1 to 5.1 ¦ · Differential dry-bulb temperature (compares outdoor air dry bulb to return air dry bulb) · Fixed enthalpy (compares outdoor air enthalpy to a fixed set point) · Differential enthalpy (compares outdoor air enthalpy to return air enthalpy) · Electronic enthalpy (compares outdoor air temperature and humidity to a set point that is a curve on the psychrometric chart) · Combinations of these controls ASHRAE Standard 90.1 includes some limitations on which controllers can be used and controller set points based on climate zone. The most energy-efficient high limit theoretically is a combi- nation of differential enthalpy and differential dry-bulb tempera- ture. However, it effectively requires four sensors (one temperature and one humidity in each of the outdoor air and return airstreams), all of which have inaccuracy and can get out of calibration, in par- ticular the humidity sensors. Sensor error may result in increased energy usage relative to other, less expensive high-limit controls. In practice, the simplest, least expensive, and most reliable high-limit control is a fixed outdoor air dry-bulb temperature sensor set to the set point prescriptively required by ASHRAE Standard 90.1. The relief air system should be enabled during economizer oper- ation because the large quantities of outdoor air should leave the building along a planned path of flow and not an unplanned path, such as entry doors that may be pushed open. VAV warm-up control during unoccupied periods requires no outdoor air if exhaust fans are off; typically, outdoor and exhaust dampers remain closed. Where a return fan is installed, the supply fan and return airflows are offset to maintain zero differential airflow. Where outdoor conditions allow, night cooldown control pro- vides 100% outdoor air for cooling during unoccupied periods. The space is cooled to the space set point, typically 5 K above outdoor air temperature. Limit controls prevent operation if outdoor air is above space dry-bulb temperature, if outdoor dew-point tempera- ture is excessive, or if outdoor dry-bulb temperature is too cold (typ- ically 10°C or below). When outdoor air conditions are acceptable and the space requires cooling, the cooldown cycle is the first phase of the optimum start sequence. During unoccupied mode, with air-handling units off or not pro- viding outdoor air, offgassing from building contents and construc- tion materials can accumulate in the space. A preoccupancy purge sequence may be used to dilute the resultant volatile organic com- pounds (VOCs) before initial or daily scheduled occupancy. Purge damper settings are a fixed set point and should be adjusted equiva- lent to the building floor area component of the minimum outdoor air damper settings. Constant- v olume (CV) Systems In a constant-volume system, supply and return fan airflow rates are manually set to meet the airflow requirements for peak thermal load and ventilation for full occupancy. Once set, the airflow does not change; it is constant except when no airflow is needed and the unit is off. The air-handling unit' s economizer outdoor air dampers, heating coil (where applicable), and cooling coil are controlled in sequence to maintain the supply air temperature (SAT) at a set point. For a single-zone constant-volume system, the SAT may also Inc. ASHRAE, 2019 user. single for Licensed | {}
ba79a14e-d56f-4494-9e41-e2fb475aa71b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Design and Application of Controls 48.13 be reset based on outdoor air or return air temperature. For a constant-volume system serving multiple zones, the SAT may be reset to satisfy the zone with the maximum load or the cumulative change represented by the return air temperature. For a SAT reset strategy, the minimum cooling SAT set point should be set no lower than the design cooling coil's leaving air temperature, to prevent excessive chilled-water temperature reset requests that can reduce chiller plant efficiency. The maximum cooling SAT set point is typ- ically 15.6°C in humid climates and 18°C in milder climates. If unoccupied warm-up mode is used, the outdoor damper is closed and the supply air set point is adjusted upward to the desired value. Control strategies for economizers, demand-controlled ventila- tion, morning warm-up, and night cooldown are the same as for VAV systems. Terminal Units A terminal unit (also called a constant-air volume [CA V] or vari- able-air-volume [V AV] box) is the zone-level control device for constant- or variable-volume systems. At a minimum, a terminal unit consists of a calibrated air damper, though different types also include components such a heating coil (in reheat boxes), automatic actuator controlling the calibrated air damper (in VA v boxes), and an integral fan in fan-powered terminal units. A system is considered to be variable volume if primary airflow to the space varies. Total airflow to the space (primary air + plenum air) may be constant for some terminal units, even in a variable- volume system. Space set point is maintained by changing the temperature of the air delivered to the space or, with constant low- temperature supply air, by limiting the amount of the cool air that enters the space, or both. A space temperature of 24°C and 50% rh requires air supplied from the AHU that has typically been cooled to 13°C for moisture removal. Minimum ventilation may require so much cool air that the space is below the desired temperature. Zonal reheat coils at the terminal units heat the supply air at the zone to meet the space temperature set point. VA V systems typically serve fewer than 15 zones per AHU. A terminal unit typically serves 1 to 8 outlets. The system should serve zones with similar thermal loads (e.g., all internal zones or all zones on the same exterior exposure), so that the unit is not contin- ually switching between heating and cooling. To ensure minimum outdoor air ventilation is maintained, outdoor airflow must be con- trolled (see the section on Minimum Outdoor Air Control). A simple fixed damper position typically is not adequate. Individual systems and their respective zones should be grouped together for easy scheduling and system-wide override. The system and zone groups all work in the same operating mode based on their operating schedule, occupancy status, and deviations from set point. See ASHRAE Guideline 13 for best practices in locating zone group operating mode programming logic based on network architecture. Depending on region, climate, and application, terminal unit zone groups should consider the following operating modes: · Occupied · Warmup · Cooldown ![image](/image/placeholder) ZONE R INLET DISCHARGE Fig. 23 Single-Duct Constant- v olume Zone Reheat · Setback · Freeze protection setback · Setup Single-Duct, Constant- v olume. Reheat terminals use a single constant-volume fan system that serves multiple zones (Figure 23). All of the system 's supply air is cooled to satisfy the greatest zone cooling load. Air delivered to other zones is then reheated with heat- ing coils (hot-water, steam, or electric) in individual zone ducts. The reheat coil valve (or electric heating element) modulates as required to maintain the space condition. Because these systems consume more energy than VA v systems, they are generally limited by en- ergy standards to applications with fixed ventilation needs, such as hospitals, special processes, or laboratories. No fan control is required for constant-volume terminal units, because the design, selection, and adjustment of fan components determine the air volume and duct static pressure. The same tem- perature air is supplied to all zones. However, the controller can vary the supply temperature to respond to demand from the zone with the greatest cooling load, thus conserving energy, and demand- controlled ventilation may be implemented where applicable. Single-Duct Variable- Volume. A throttling VAV terminal has an inlet damper that controls the flow of primary supply air (Figure 24). For spaces with exterior exposures or a high airflow requirement of ventilation air requiring heating, a reheat coil can be installed in the discharge. With pressure-independent controls, the space tempera- ture sensor does not control the inlet damper directly. The space tem- perature control loop output is used to reset the primary airflow delivered to the space between a maximum and minimum rate. Direct control of airflow makes the VAV box independent of variations in duct static pressure. The currently recommended control sequence is the dual maximum sequence in Figure 25. As the space goes from design cooling load to design heating load, the airflow set point is first reset from the cooling maximum to the minimum value needed for ven- tilation. Then the supply air temperature is reset from minimum (e.g., 13°C) to maximum (e.g., 32°C), and the reheat coil is modu- lated to maintain the supply air temperature at set point. Lastly, the airflow set point is reset from the minimum up to the heating max- imum. The minimum flow rated for ventilation may be a constant, but is more likely adjusted by occupancy. The minimum flow rate may be further adjusted according to a measured concentration of some air constituent, typically carbon dioxide. Previously, it was common to keep the primary airflow rate always high enough to handle the maximum heating load. ASHRAE Standard 90. 1 and some other energy codes do not allow that prac- tice because it increases simultaneous heating and cooling. An induction VA v terminal controls space temperature by re- ducing supply airflow to the space and by inducing return air from the plenum into the airstream for the space (Figure 26). Both dampers are controlled simultaneously, so as the primary air open- ing decreases, the return air opening increases. When space tem- perature drops below the set point, the supply air damper begins to close and the return air damper begins to open. ![image](/image/placeholder) F DM R INLET C Fig. 24 Throttling VAV Terminal Unit Inc. ASHRAE, 2019 user. single for Licensed | {}
7af61941-05d3-430d-adff-01432101b932 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 48.14 2019 ASHRAE Handbook- -HVAC Applications (SI) Chart Type: line Maximum Cooling Airflow Set Point Maximum Heating Airflow Minimum Airflow Set Point Maximum Cooling Airport item_01 50Feet 25Feet 20Feet 10Feet Fig. 25 Throttling VAV Terminal Unit: Dual Maximum Control Sequence ![image](/image/placeholder) I DM RETURN AIR F DM INLET DISCHARGE RETURN AIR MAXIMUM PRIMARY MAXIMUM COLD AIR PRIMARY INDUCED VOLUME 50% INDUCED RETURN AIR AIR MINIMUM 0 COLD HOT SPACE TEMPERATURE Fig. 26 Induction VAV Terminal Unit ![image](/image/placeholder) F D R INLET FS DISCHARGE RETURN AIR TOTAL DELIVERED AIR MAXIMUM INLET AIR VOLUME REHEAT RETURN AIR AIR 0 COLD HOT SPACE TEMPERATURE Fig. 27 Series Fan-Powered VAV Terminal Unit A series fan-powered terminal unit has an integral fan in series with the primary supply air damper that supplies to the space (Figure 27). These terminals can be either constant or variable volume. In addition to enhancing air distribution in the space, a reheat coil can be added for space heating and to maintain a minimum temperature in the space when the primary system is off, for strategies such as set- back, warm-up, and demand-controlled ventilation. When the space is occupied, the fan runs to provide air to the space. The fan can draw air from the return plenum to compensate for reduced supply air volume. As temperature in the space decreases below the cooling set point, the supply air damper begins to close and the fan draws more air from the return plenum. For zones with a reheat coil, when supply air reaches its minimum volume and the space temperature begins to drop below the heating set point, the valve to the reheat coil begins to open. Depending on the fan and motor, it may be important to start the terminal fan before the central air handler. If primary air is flow- ing when the terminal fan is off, it can spin the fan backwards. This can damage the motor when the terminal fan starts. A parallel fan terminal unit is similar to the series fan terminal, except that the fan is in parallel with the primary supply air VAV damper (Figure 28). These terminals can be either constant or vari- able volume. A reheat coil may be placed in the discharge to the space or in the return plenum opening. The fan is intended to operate primarily in heating mode, but may also operate to maintain a min- imum airflow to the space, allowing reduced primary airflow rates. Total airflow to the space is the sum of the fan output and supply air quantity. When space temperature drops below the cooling set point, the supply air damper begins to reduce the quantity of supply air entering the terminal. Once the supply damper reaches its minimum position and the space temperature begins to drop below the heating set point, the reheat coil valve starts to open. When the space is unoccupied and requires heating for setback or warm-up, the supply air damper is closed, the fan turns on, and the reheat coil valve mod- ulates to maintain the unoccupied set point. Variable-volume, dual-duct terminal units (Figure 29) have inlet dampers (with individual damper actuators and airflow con- trollers) on the cooling and heating supply ducts. The space thermo- stat resets the airflow controller set points in sequence as the space load changes. The airflow controllers maintain adjustable minimum flows for ventilation. Ifthe heating supply has sufficient ventilation air, there need not be any overlap of damper operations (one snaps closed and the other snaps open at the heat/cool changeover point), resulting in no simultaneous heating and cooling in the terminal ![image](/image/placeholder) F D M R INLET FS DISCHARGE AIR AIR ▲ BACKDRAFT DAMPER RETURN PLENUM TOTAL MAXIMUM DELIVERED AIR INLET AIR REHEAT FAN RETURN AIR COLD HOT Fig. 28 Parallel Fan Terminal Unit Inc. ASHRAE, 2019 user. single for Licensed | {}
aeaff6ae-4605-4884-85d4-5d146f7abd5d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Design and Application of Controls 48.15 unit. On systems where the heating supply does not have sufficient ventilation air (e.g., on some dual-fan dual-duct applications), the cooling damper can be controlled to a minimum for ventilation. There are two main control strategies for dual-duct terminal units. Snap acting control is the most efficient control logic and does not require dual-duct boxes with mixing sections that have a high pressure drop. It eliminates the need for mixing plenum be- cause airflows do not mix. However, snap action control logic is not recommended for demand control, because it can cause the zone to oscillate between cooling and heating. It may also cause low supply air temperature on systems with high outdoor airflows and no pre- heat coils because it cannot mix hot and cold air. Mixing control logic is the preferred option for applications with demand-control ventilation or application with high minimum airflow rates. Chilled-beam terminal units are available as active or passive. Active chilled beams are supplied with constant-volume primary air from a dedicated outdoor air system (DOAS) unit or other air system. This air flows through the chilled beam and induces room air. Passive chilled beams do not receive any system air; see Chapter 20 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment. Chilled beams can be two pipe or four pipe, and are controlled similarly to other radiant elements. Compared to some other HVAC systems, chilled beams with DOAS can simplify room control sequences because temperature control and ventilation control are separated. This separation helps HVAC designers when planning to meet the individual loads and makes it easy to design control sequences. Modulating and two-position valves have been applied for tem- perature control with chilled beams. For temperature control, the system needs at least one flow control valve for each temperature control zone. One control valve may serve multiple chilled beams. Mechanical sizing issues or piping arrangements may favor driv- ing several flow control valves in unison from one temperature controller. Preventing condensation on cooling surfaces is important in design and operation of chilled beams and radiant cooling devices. This is mainly accomplished by coordinating the primary systems delivering air and chilled water to the room. The general approach is to dry the supply air sufficiently to keep the space dew point a couple of degrees below the chilled-water supply temperature. Depending on loads and sizing, this may be possible without active control. Often, the solution is to sense relative humidity in some or all of the spaces, calculate the dew point, and deliver that informa- tion to the primary air and water control systems, where reset strat- egies prevent condensation. As a back-up, condensation detectors at the chilled beams are recommended. When the switch closes, indicating condensing con- ditions, the system closes the control valve to the cooling coil. This prevents damage by condensation, but also disables cooling in the space. It is a back-up, safety measure; coordinating air and water distribution temperatures is the primary strategy. Sometimes, the energy advantage that leads to a chilled-beam design depends on optimizing features in the primary systems. In the cooling plant, the water-side economizer and other special strategies that deliver rela- tively warm water to the chilled beams may be critical to efficiency. Overall system efficiency may also depend on reducing use of re- heat in the rooms. The supply air temperature reset strategy that minimizes reheat and controls moisture in the space may be sophis- ticated. Typically, the simple room control strategies must deliver coordinating data into relatively advanced primary plant controls. Humidity Control Humidity control relies on the output ofa humidity sensor located either in the space or in the return air duct. Most comfort cooling involves some natural but uncontrolled dehumidification. The amount of dehumidification is a function of the effective coil surface temperature and is limited by the coolant's freezing point. If water condensing out of the airstream freezes on the coil surface, airflow is restricted and, in severe cases, may be shut off. The practical limit is about 5°C dew point on the coil surface. As indicated in Figure 30, this results in a relative humidity of no less than 30% at a space temperature of 24°C. When lower humidity is needed for a process application (e.g., dryroom), a desiccant dehumidifier is required. Although simple cooling by refrigeration typically provides de- humidification as a by-product of the cooling process, without ad- ditional equipment, it does not directly control space humidity. Dehumidification can be directly controlled in several ways. Ifrel- ative humidity is the critical measure, adding heat to the space de- creases the relative humidity, but usually the object is to remove moisture and lower the dew point. One method is to control the cool- ing coil based on relative humidity, not space temperature. The sup- ply air temperature leaving the coil is lowered until enough moisture is removed from the supply air to maintain the humidity set point. When a relative humidity limit is required, a space or return air hu- midistat is provided in addition to the space thermostat. A control function selects the higher of the output signals from the two de- vices and controls the cooling coil valve to provide either tempera- ture or humidity control. A low-temperature coil used to remove ![image](/image/placeholder) F DM COOLING INLET I DM DISCHARGE HEATING INLET 30% rh F HEATING DAMPER MAXIMUM VOLUME MAXIMUM HEAT AIR MINIMUM COOLING DAMPER 5 24 0 TEMPERATURE, °C COLD HOT SPACE TEMPERATURE Fig. 30 Psychrometric Chart: Cooling and Dehumidifying, Fig. 29 Variable- v olume Dual-Duct Terminal Unit Practical Low Limit Inc. ASHRAE, 2019 user. single for Licensed | {}
ee9e4dc8-8fe0-4509-95ae-a01d5e7b39f1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 48.16 2019 ASHRAE Handbook- -HVAC Applications (SI) moisture from an airstream may lower a space temperature below the desired set point. The process line in Figure 30 shows a signifi- cant loss of sensible temperature before moisture is removed. As space temperature decreases, the relative humidity increases even though the absolute humidity (dew point, grams of moisture, kilo- grams of water to kilograms of air) decreases. A reheat coil is required to maintain the space temperature if moisture removal results in too low a supply air temperature. This coil may be located in the AHU, as shown (Figure 31), or a space- temperature-controlled reheat coil may be provided at the room ter- minal unit. Sprayed-coil dehumidifiers (Figure 32) have been used for dehumidification. Space relative humidity ranging from 35 to 55% at 24°C can be obtained with this equipment; however, the costs of maintenance, reheat, and removal of solid deposits on the coil make the sprayed-coil dehumidifier less desirable than other methods. Air washers with a cold-water spray (down to 5°C) do not re- quire the coil for cooling, though mist eliminators add to the equip- ment in the air handler. The spray cools the air, removes moisture down to the temperature of the spray water, and collects and con- centrates particulates in the spray pan. As with the spray coil, this is messy and slower to respond than other methods. A desiccant-based dehumidifier can lower space humidity below that possible with cooling/dehumidifying coils. This device adsorbs moisture using silica gel or a similar material. For continu- ous operation, heat is added to the adsorbent material out of the dehumidification airstream to evaporate moisture and regenerate the material. This is often in a wheel configuration that rotates the gel from the wet side, where it absorbs moisture, into the heated dryer side, where moisture is driven off and exhausted from the system. The adsorption process adds heat to the dehumidified air. Cooling is required, but at a warmer temperature to limit the need for lower-temperature cooling coils. The psychrometric process is shown in Figure 33, and Figure 34 shows a typical control. There are two control loops to consider: (1) the heating source must be hot enough to regenerate the media for effective moisture removal, and (2) the cooling coil needs only lower the temperature to a point that provides a comfortable space condition. Because the moisture has been removed by adsorption, the conditioned air to the space may be 5 to 7 K warmer than required for an AHU that uses only cooling to control moisture. When the outdoor air is drier, regeneration can use a lower-temperature source, saving heating and subsequent cooling energy. Humidification can be achieved by adding moisture to supply air, using evaporative pans (usually heated), steam injection, or at- omizing spray tubes. A space or return air humidity sensor provides the necessary signal for the controller. A humidity sensor in the duct AIR ENTERING DEHUMIDIFIER DEHUMIDIFYING RECOOLING ![image](/image/placeholder) CH HOT-WATER RETURN RETURN CH HOT-WATER SUPPLY SUPPLY T T NC NO SENSORS IN ZONE 0 AIRFLOW T H COOLING COIL REHEATING COIL Fig. 31 Cooling and Dehumidifying with Reheat Fig. 33 Psychrometric Chart: Desiccant-Based Dehumidification ![image](/image/placeholder) CH RETURN ZONE SENSOR CH SUPPLY H I NC T SPRAY 0 MIXED AND COOLING COIL PREHEATED AIR WITH ELIMINATORS FLOAT VALVE c MAKEUP WATER PUMP ![image](/image/placeholder) NC HEATING SOURCE ⊙ EXHAUST REGENERANT AIR AIR NC COOLING CHEMICAL SOURCE DEHUMIDIFIER ⑨ OUTDOOR OR RETURN AIR CONDITIONED AIR Fig. 34 Desiccant Dehumidifier Fig. 32 Sprayed-Coil Dehumidifier ![image](/image/placeholder) H ZONE SENSOR STEAM DUCT SENSOR H AIRFLOW Fig. 35 Steam Injection Humidifier Inc. ASHRAE, 2019 user. single for Licensed | {}
0d4062be-acdb-40b5-a980-d217ec11f970 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Design and Application of Controls 48.17 should be used to minimize moisture carryover or condensation in the duct (Figure 35). With proper use and control, humidifiers can achieve high space humidity, although they more often are used to maintain design minimum humidity during the heating season. Atomized fine droplets make it easier to mix water in to an airstream, but converting a droplet into water vapor requires heat for the change of state. Because evaporative cooling occurs with an atomized method, additional heat must be provided. Steam is already a vapor, so additional heat is not required for the humidification process. It is important to have not only a space or return sensor to call for adding humidity, but also a duct sensor just downstream of the humidifier to limit the moisture concentration being injected to less than 85%, to avoid condensation on the duct walls. Single-Zone Systems A single-zone system (Figure 36)) is an air handler serving one area of a building that has similar loads and occupancy throughout the zone. Single-zone systems do not require terminal boxes, be- cause zone temperature can be maintained by modulating fan speed and using the heating and cooling control valves (and optional econ- omizer dampers) to control discharge air temperature, as indicated in Figure 37 The fan is typically variable speed, which is now required for many applications by energy standards such as ASHRAE Stan- dard 90.1. A unit ventilator (UV) is designed to heat and ventilate a space by introducing up to 100% outdoor air. Optionally, it can cool and dehumidify with a cooling coil (either chilled-water or direct- expansion). Heating can be by a gas furnace, hot water, steam, or electric resistance. Control of these coils can be by valves or by face-and-bypass dampers. A typical control sequence for a UV is shown schematically in Figure 38 and logically in Figure 39. During the heating stage, this approach (Figure 38) supplies a set minimum quantity of outdoor air. Outdoor air is gradually increased as required for cooling. During warm-up, the heating valve is open, the outdoor air (OA) ![image](/image/placeholder) RETURN AIR T ZONE SENSOR VSC DM OUTDOOR SUPPLY AIR AIR Fig. 36 Single-Zone Fan System Chart Type: line Maximum Set Point Supply Air Temperature Set Point Minimum Speed Minimum Minimum Set Point Cooling Loop Signal item_01 25 20 15 10 25 damper is closed, and the return air (RA) damper is open. As space temperature rises into the operating range of the space thermostat, ventilation dampers move to their set minimum ventilation posi- tions. The heating valve and ventilation dampers are operated in sequence as required to maintain space temperature. The airstream thermostat can override space thermostat action on the heating valve and ventilation dampers to prevent discharge air from drop- ping below a minimum temperature. Figure 39 shows the relative positions of the heating valve and ventilation dampers with respect to space temperature. Makeup air units (Figure 40) are 100% outdoor air units that replace air exfiltrated or exhausted from the building through toilet, laboratory, industrial, and combustion processes. Makeup air is often supplied at or near space conditions, but may also provide space heating and cooling. The makeup air fan is usually turned on, either manually or automatically, whenever exhaust fans are turned on. However, the fan should not start until the outdoor air damper is fully open as proven by an end switch. The two-position outdoor air damper remains closed when the makeup fan is not in operation. The outdoor air limit control opens the preheat coil valve when outdoor air temperature drops to the point where the air requires heating to raise it to the desired supply air temperature. To prevent low- temperature shutdowns on start-up, the heating coil should begin cir- culation and prove heating is available before the outdoor damper ![image](/image/placeholder) ROOM THERMOSTAT AIRSTREAM THERMOSTAT HEATING ELEMENT HEATING VALVE FAN FAN INTERLOCK FILTER FILTER DAMPER \ \ \ / / / ACTUATOR DAMPER DAMPER OUTDOOR RETURN AIR AIR FLOOR Fig. 38 Unit Ventilator Control Arrangements Chart Type: line COOL NORMAL WARM item_01 0.5 0.8 0.4 Fig. 39 Valve and Damper Positions with Respect to Room Temperature Inc. ASHRAE, 2019 user. single for Licensed | {}
dad50610-4b4a-4e0e-98c0-5cb0c3a51bfa | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 48.18 opens and the fan starts. A capillary element freezestat located adja- cent to the coil shuts the fan down for low-temperature detection if air temperature approaches freezing at any spot along the sensing element. Fuel-fired makeup air units have staged or modulating fuel-fired direct or indirect furnaces. Units have manufacturer-supplied con- trols and safeties for flame proving, airflow proving, and discharge air low limit to meet the ANSI Standard Z83.4/CSA Standard 3.7 combined safety standard. The manufacturer's controls either include temperature controls or provide an interface for the control contractor's temperature controls. Multiple-Zone, Dual-Duct Systems A single-fan, dual-duct system uses a single fan to supply sep- arate heating and cooling ducts (Figure 41). Dual-duct terminal mixing boxes are used to control the zone temperature. For VA v ter- minals, static control is similar to that in VA v single-duct systems except that static pressure sensors are needed in each supply duct. A controller allows the sensor detecting the lowest pressure to control the fan output, thus ensuring that there is adequate static pressure to supply the necessary air for all zones. The hot deck has its own heating coil, and the cold deck has its own cooling coil. Each coil is controlled by its own discharge air temperature controller. The hot deck set point may be reset from the zone with the greatest heating demand, and the cold deck ![image](/image/placeholder) ) M OUTDOOR SPACE AIR FS FILTER HEATING COIL FREEZE- STAT SPACE EXHAUST AIR Fig. 40 Makeup Air Unit 2019 ASHRAE Handbook- -HVAC Applications (SI) set point may be reset from the zone with the greatest cooling de- mand. Cooling supply air temperature control is similar to that in single-duct systems, with economizer dampers sequenced with the cooling coil. The economizer causes the supply air temperature entering the hot deck to be as cold as the cold deck, increasing heating energy usage. Because of this inefficiency, single-fan, dual-duct systems with air economizers are not allowed by many energy standards such as ASHRAE Standard 90.1. Dual-fan, dual-duct systems (Figure 41) use separate supply fans for the heating and cooling ducts. This eliminates the econo- mizer inefficiency of single-fan, dual-duct systems. Static-pressure control is similar to that for VAV single-fan, dual-duct, systems, except that each supply fan has its own static pressure sensor and control. 5. SPECIAL APPLICATIONS Mobile Unit Control The operating point of any control that relies on pressure to oper- ate a switch or valve varies with atmospheric pressure. Normal vari- ations in atmospheric pressure do not noticeably change the operating point, but a change in altitude affects the control point to an extent governed by the change in absolute pressure. This pressure change is especially important with controls selected for use in land and aerospace vehicles that are subject to wide variations in altitude. The effect can be substantial; for example, barometric pressure decreases by nearly one-third as altitude increases from sea level to 3000 m. In mobile applications, three detrimental factors are always present in varying degrees: vibration, shock, and acceleration forces. Controls selected for service in mobile units must qualify for the specific conditions expected in the installation. In general, devices containing mercury switches, slow-moving or low-force contacts, or mechanically balanced components are unsuitable for mobile applications; electronic solid-state devices are generally less susceptible to these three factors. Explosive Atmospheres Sealed-in-glass contacts are not considered explosionproof; therefore, other means must be provided to eliminate the possibility of a spark in an explosive atmosphere. ![image](/image/placeholder) _TYPICAL_ZONE BOX RETURN AIR I 2 T - 1 H STATION FLOW T HEATING DM VSC SUPPLY AIR OUTDOOR AIR C SUPPLY FAN FLOW COOLING SUPPLY AIR C STATION I I Fig. 41 Single-Fan, Dual-Duct System Inc. ASHRAE, 2019 user. single for Licensed | {}
dd9742c6-9dcc-49d9-88ec-f815aa5febcb | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Design and Application of Controls 48.19 When using electric control, the control case and contacts can be surrounded with an explosionproof case, allowing only the capsule and the capillary tubing to extend into the conditioned space. It is often possible to use a long capillary tube and mount the instrument case in a nonexplosive atmosphere. This method can be duplicated with an electronic control by placing an electronic sensor in the con- ditioned space and feeding its signal to an electronic transducer located in the nonexplosive atmosphere. Because pneumatic control uses compressed air, it is safe in oth- erwise hazardous locations. However, many pneumatic controls interface with electrical components. All electrical components require appropriate explosionproof protection. Sections 500 to 503 of the National Electrical Code (NFPA Standard 70) include detailed information on electrical installation protection requirements for various types of hazardous atmo- spheres. 6. DESIGN CONSIDERATIONS AND PRINCIPLES In designing and selecting the HVAC system for the entire building, the type, size, use, and operation of the structure must be considered. Subsystems such as fan and water supply are normally controlled by local automatic control or a local loop control, which includes the sensors, controllers, and controlled devices used with a single HVAC system and excludes any supervisory or remote func- tions such as reset and start/stop. However, local control is fre- quently extended to central control to diagnose malfunctions that might result in damage from delay, or that might increase labor and energy costs. Special modes of operation may be required to allow for load shedding, purge, warm-up, cooldown, and lockdown. Initi- ators may be manual or automatic, based on weather, announce- ments of extraordinary events, high concentrations of expected and therefore measured hazardous gases, or daily schedules reset by out- door air temperature. Distributed processing using microprocessors has enabled com- puter use at many locations other than the central control point. It is more common to use DDC instead of pneumatic or electric thermo- stats for local loop controllers. The local loop control is integrated with energy management functions performed by upper-level DDC devices to form a complete BAS. Because HVAC systems are designed to meet maximum design conditions, they nearly always function at partial capacity. The system must be adjusted and operated for many years, so the sim- plest control that produces the necessary results is usually the best. Extraordinary Incidents Building owners and design engineers are sometimes interested in applying the BAS to implement strategies that protect occupants from airborne attack. It is crucial that the engineer does not ap- proach this complex topic as a control system issue. The BAS may include protective features, but only in the context of a comprehen- sively designed ventilation system. A protective ventilation strategy only makes sense in the context of a thorough risk assessment and an overall security plan. If a protective ventilation strategy is at- tempted, it is crucial to consider every air movement device and pathway, not just the main fan(s) and damper(s). It is also necessary to consider possible interaction of a protective operation with other emergency control operations, such as the response to a fire/life safety device (e.g., a smoke detector). ASHRAE (2003), FEMA (2007), and NIOSH (2002), among others, have published references to guide an engineer or building owner in organizing a comprehensive plan. Also see Chapter 59 for more information on this topic. Mechanical and Electrical Coordination Even a pneumatic control system includes wiring, conduit, switchgear, and electrical distribution for many electrical devices. The mechanical designer must inform the electrical designer of the total electrical requirements if controls are to be wired by the elec- trical contractor. Requirements include (1) the devices to be fur- nished and/or connected, (2) electrical load, (3) location of electrical items, (4) a description of each control function, and (5) whether the control system needs to be on emergency power or UPS. Coordination is essential. Proper coordination should produce a control diagram that shows the interface with other control elements to form a complete and usable system. As an option, the control engineer may develop a complete performance specification and require the control contractor to install all wiring related to the spec- ified sequence. The control designer must run the final checks of ![image](/image/placeholder) RETURN AIR I T VSC STATION FLOW HEATING SUPPLY AIR HEATING SUPPLY FAN TYPICAL ZONE BOX T T DM VSC STATION FLOW OUTDOOR AIR COOLING SUPPLY AIR COOLING SUPPLY FAN Fig. 42 Dual-Fan, Dual-Duct Systems Inc. ASHRAE, 2019 user. single for Licensed | {}
012baae7-09a4-48d3-be5f-be64dcfdc0e7 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 48.20 drawings and specifications. Both mechanical and electrical speci- fications must be checked for compatibility and uniformity. Sequences of Operation A BAS requires that the engineer define how the system is to be controlled. These sequences are then programmed into the system by the system installer. Writing clear, unambiguous, concise, yet comprehensive sequences of controls is key to the energy and com- fort performance of the HV AC system, yet it is very difficult to do well. It requires a clear understanding of how controls work, the limitations of the specific DDC hardware specified and the HVAC system design, and a knack for clear thinking and writing. Tech- niques for writing successful control sequences are discussed in ASHRAE Guideline 13. Sequences for typical HVAC systems can be found in the ASHRAE (2005) CD-ROM, Sequences of Opera- tion for Common HVAC Systems. ASHRAE research project RP- 1455 (Hydeman, in progress) investigates sequences of operation for variable-air-volume (VA V) air handlers and terminal units. One goal ofthe project is to specify control sequences that can be readily implemented by design engineers and controls contractors. Other ASHRAE research projects that may be helpful in developing con- trol sequences include RP-1515, on saving energy by reducing minimum airflow from overhead diffusers (Arens et al. 2014) and RP-1547 (Lau et al. 2013), which addresses demand-controlled ventilation based on CO2 in multizone systems. Energy-Efficient Controls The U.S. Green Building Council's (USGBC) Leadership in Energy Efficient Design (LEED) program for new construction and existing buildings provides guidance on designing and building com- mercial, institutional, and government buildings to produce quanti- fiable benefits for occupants, owners, and the environment. During design and construction, LEED provides many opportu- nities for using a BAS. LEED awards points, based on design criteria, to determine at which level a building is certified: platinum, gold, silver, or certified. (For specifics, see http://www.usgbc.org.) Many of these points depend on the sophistication, flexibility, and power of the BAS, not only for comfort and energy efficiency, but also for sustainability verification throughout the facility' s lifetime. Applications. It is recommended that the LEED design team choose the controls consultant/contractor and to have them involved with the team early in design, allowing for controls input on the con- trol schemes. For any facility, the BAS provides thermal comfort and routine programming (e.g., occupied/unoccupied). Under LEED, the con- trols consultant or contractor uses the BAS for benchmarking and alarming when reference points are exceeded (e.g., monitoring facility electrical use). Once a baseline is established, programs with established alarm limits can alert the owner ifthe facility exceeds the baseline by 10% or more, so corrections can be made and continued higher utility expenses avoided. Depending on the facility, this may be monitored for hourly, daily, weekly, or monthly comparison. The BAS can also · Turn solar panels for optimum sun exposure · Adjust blinds and awnings · Keep indoor air quality (IAQ) acceptable by adjusting outdoor air (OA) without overventilating · Open and close windows for natural ventilation · Monitor and adjust indoor and outdoor lighting · Control irrigation based on weather · Collect weather data · Track scheduling hours for occupancy · Monitor equipment run times and set points · Track electricity use profiles 2019 ASHRAE Handbook-HVAC Applications (SI) · Monitor efficiency oflarge equipment performance (e.g., chillers, variable-frequency-drive [VFD] pumping, boilers) All of these factors affect building sustainability. Because the BAS operates in real time, and can compare real- time data to previously defined baselines, it is a valuable tool. Open protocols allow the BAS to monitor, control, and provide critical alarming for non-HVAC equipment (e.g., for power monitoring, chiller performance, VFDs for VAV systems or variable-speed pumping, water efficiency, emergency generators, indoor and out- door lighting, boilers) for a minimal investment. The BAS provides an excellent tool for commissioning both HVAC and other equipment, as required by LEED. Its data acquisi- tion abilities allow comparisons of daily performance as building use changes, thereby allowing the commissioning agent to determine whether equipment is operating properly, and allowing the owner to compare real-time data to previously defined benchmarks in mea- surement and verification (M& V). Typical operation sequences, such as optimizing outdoor air quantities or chiller efficiency, and providing multiple sensing points for thermal comfort, are still used, and are critical for maintaining sustainability. Perhaps the most important aspect of a successful control system is training the owner. Many owners do not fully realize the capabil- ities of BAS, many of which are intangible and somewhat obscure, so it is critical that the owner be given proper training in using the controls system. The order in which training takes place is equally important: mechanical equipment training should come first, then operation and maintenance (O&M) and controls layout configura- tions, use of the controls system to provide thermal comfort and maintain equipment, and, finally, written M& V procedures to main- tain sustainability. If the facility cannot justify a full-time energy manager, then the owner should consider third-party contracting to ensure the facility performs at its designed energy efficiency. 7. CONTROL PRINCIPLES FOR ENERGY CONSERVATION After a building's general needs have been established and the building and system subdivision has been made, the mechanical sys- tem and its control approach can be considered. Designing systems that conserve energy requires knowledge of (1) the building, (2) its operating schedule, (3) the systems to be installed, and (4) ASHRAE Standard 90.1. The principles or approaches that conserve energy are as follows: · Run equipment only when needed. Schedule HVAC unit operation for occupied periods. Run heat at night only to maintain internal temperature at around 13 and 16°C to prevent freezing. Start morning warm-up as late as possible to achieve design internal temperature by occupancy time, considering residual space tem- perature, outdoor temperature, and equipment capacity (optimum start control). Under most conditions, heating and cooling equip- ment can be shut down some time before the end of occupancy, depending on internal and external load and space temperature (optimum stop control). Calculate shutdown time so that space temperature does not drift out of the selected comfort zone before occupancy ends and ensure that ventilation is provided throughout occupancy. · Sequence heating and cooling. Do not supply heating and cooling simultaneously unless it is required for humidity control. Central fan systems should use cool outdoor air, if available, in sequence between heating and cooling. Zoning and system selection should eliminate, or at least minimize, simultaneous heating and cooling. Also, humidification and dehumidification should not take place concurrently. Inc. ASHRAE, 2019 user. single for Licensed | {}
4d2b50b4-348f-409b-a286-5419f4e1f9ba | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Design and Application of Controls 48.21 · Provide only the heating or cooling actually needed. Reset the supply temperature of hot and cold air (or water). In air systems that support variable-speed fans, reset duct static pressure to pro- vide thermal comfort at the lowest possible fan speed and energy consumption. · Supply heating and cooling from the most efficient source. Use free or low-cost energy sources first, then higher-cost sources as necessary. · Apply outdoor air control. When on minimum outdoor air, supply no less than that recommended by ASHRAE Standard 62.1 and, on VAV systems, include controls that ensure that outdoor air rates are maintained under all expected supply air operating con- ditions. System Selection The mechanical system significantly affects the control of zones and subsystems. System type and number and location of zones influence the amount of simultaneous heating and cooling that occurs. For perimeter areas, heating and cooling should be con- trolled in sequence to minimize simultaneous heating and cooling. In general, this sequencing must be accomplished by the control system because only a few mechanical systems (e.g., two-pipe and single-coil) can prevent simultaneous heating and cooling. Systems that require engineered control systems to minimize simultaneous heating and cooling include the following: · VAV cooling with zone reheat. Reduce cooling energy and/or air volume to a minimum before applying reheat. · Four-pipe heating and cooling for unitary equipment. Sequence heating and cooling. · Dual-duct systems. Condition only one duct (either hot or cold) at a time. The other duct should supply a mixture of outdoor and return air. · Single-zone heating/cooling. Sequence heating and cooling. Some exceptions exist, such as dehumidification with reheat. Control zones are determined by the location of the thermostat or temperature sensor that sets the requirements for heating and cooling supplied to the space. Typically, control zones are for a room or an open area of a floor. Energy standards such as ASHRAE Standard 90.1 no longer allow constant-volume systems that reheat cold air or that mix heated and cooled air, except in special applications such as hospi- tals. If used, they should be designed for minimal use of reheat through zoning to match actual dynamic loads and resetting cold and warm air temperatures based on the zone(s) with the greatest demand. Heating and cooling supply zones should be structured to cover areas of similar load. Areas with different exterior exposures should have different supply zones. Systems that provide changeover switching between heating and cooling prevent simultaneous heating and cooling. Some examples are hot or cold secondary water for fan-coils or single-zone fan sys- tems. They usually require small operational zones, which have low load diversity, to allow changeover from warm to cold water without occupant dissatisfaction. Systems for building interiors usually require year-round cooling and are somewhat simpler to control than exterior systems. These interior areas normally use all-air systems with a constant supply air temperature, with or without VA v control. Proper control tech- niques and operational understanding can reduce the energy used to treat these areas. General load characteristics of different parts of a building may lead to selecting different systems for each. Load Matching With individual room control, the environment in a space can be controlled more accurately and energy can be conserved ifthe entire system can be controlled in response to the major factor influencing the load. Thus, water temperature in a water-heating system, steam temperature or pressure in a steam-heating system, or delivered air temperature in a central fan system can be varied as building load varies. Control of the entire system relieves individual space con- trols of part of their burden and provides more accurate space con- trol. Also, modifying the basic rate of heating or cooling input in accordance with the entire system load reduces losses in the distri- bution system. The system must always satisfy the area with the greatest de- mand. Individual controls handle demand variations in the area the system serves. The more accurate the system zoning, the greater the control, the smaller the distribution losses, and the more effectively space conditions are maintained by individual controls. Buildings or zones with a modular arrangement can be designed for subdivision to meet occupant needs. Before subdivision, operat- ing inefficiencies can occur if a zone has more than one thermostat. In an area where one thermostat activates heating while another acti- vates cooling, the terminals should be controlled from a single ther- mostat until the area is properly subdivided. Size of Controlled Area No individually controlled area should exceed about 500 m2 because of the difficulty of obtaining good distribution and offinding a representative location for space control increases with zone area. Each individually controlled area must have similar load character- istics throughout. Equitable distribution, provided through compe- tent engineering design, careful equipment sizing, and proper system balancing, is necessary to maintain uniform conditions throughout a controlled area. The control can measure conditions only at its loca- tion; it cannot compensate for nonuniform conditions caused by improper distribution or inadequate design. Areas or rooms having dissimilar load characteristics or different conditions to be main- tained should be controlled individually. The smaller the controlled area, the better the control and the performance and flexibility. Location of Space Sensors Space sensors and controllers must be located where they accu- rately sense the variables they control and where the condition is representative of the area (zone) they serve. In large open areas having more than one zone, thermostats should be located in the middle of their zones to prevent them from sensing conditions in surrounding zones. Typically, space temperature controllers or sen- sors are placed in the following locations. · Wall-mounted thermostats or sensors are usually placed on in- side walls or columns in the space they serve. Avoid outdoor wall locations. Mount thermostats at generally accessible heights ac- cording to the Americans with Disabilities Act (ADA) (USDOJ 1994) (usually 1220 mm) and in locations where they will not be affected by heat from sources such as direct sun rays, wall pipes or ducts, convectors, or direct air currents from diffusers or equip- ment (e.g., copy machines, coffeemakers, refrigerators). The wall itself should be sealed tightly ifit penetrates a pressurized supply air plenum either under the floor or overhead. Air circulation should be ample and unimpeded by furniture or other obstruc- tions, and the thermostat should be protected against mechanical damage. Thermostats in spaces such as corridors, lobbies, or foy- ers should be used to control those areas only. · Return air thermostats can control floor-mounted unitary con- ditioners such as induction or fan-coil units and unit ventilators. On induction and fan-coil units, the sensing element is behind the return air grille. On classroom unit ventilators that use up to 100% outdoor air for natural cooling, however, provide a forced-flow sampling chamber for the sensing element, which should be located carefully to avoid radiant effect and to ensure adequate air velocity across the element. Inc. ASHRAE, 2019 user. single for Licensed | {}
4d75fb6d-2ec3-4065-bc2a-6210fe732c7d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 48.22 2019 ASHRAE Handbook-HVAC Applications (SI) Ifreturn air sensing is used with a central fan system, locate the sensing element as near as possible to the space being controlled to eliminate any influence from other spaces and the effect of any heat gain or loss in the duct. Where supply/return light fixtures are used to return air to a ceiling plenum, the return air sensing ele- ment can be located in the return air opening. Be sure to offset the set point to compensate for heat from the light fixtures. · Diffuser-mounted thermostats usually have sensing elements mounted on circular or square ceiling supply diffusers and depend on aspiration of room air into the supply airstream. They should be used only on high-aspiration diffusers adjusted for a horizontal air pattern. The diffuser on which the element is mounted should be in the center of the occupied area of the controlled zone. · CO2 sensors for DCV are usually located in spaces with high occupant densities (e.g., conference rooms, auditoriums, court- rooms). Locating the sensor in return air ducts/plenums that serve multiple spaces measures average concentrations and does not provide information on CO2 levels in rooms with the highest con- centrations. CO2 sensors should be located in the breathing zone of the occupied space (see ASHRAE [2011] and USGBC [2009]). Commissioning Commissioning is the process of ensuring that systems are de- signed, installed, functionally tested, and capable of being operated and maintained in conformity with the design intent. Commissioning HVAC systems begins with planning and includes design, construc- tion, start-up, acceptance, and training, and can be applied through- out the life of the building. For HV AC systems, functional performance testing (FPT) is an important part of the commissioning process. FPT is the process of determining the ability of HVAC system to deliver heating, ventilating, and air conditioning in accordance with the final design intent. Commissioning is team-oriented and generally involves co- operation of various parties, including the owner, design engineers, and contractors and subcontractors. A commissioning authority (the designated person, company, or agent who implements the overall commissioning process) generally leads the process. Each commis- sioning process must have a plan that defines the commissioning pro- cess and is developed in increasing detail as the project progresses. The most useful tool used to challenge (simulate changes to) systems operation is the control system itself. A BAS provides the added con- venience of central execution of test steps, and the ability to record responses. The BAS must be commissioned before it can be used to validate the HVAC systems. Commissioning a BAS is discussed in ASHRAE Guideline 11. Commissioning HVAC systems is recom- mended for construction of new buildings, and should be repeated periodically in existing buildings. See Chapter 43 and ASHRAE Guidelines 0 and 1 1 for more information. REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. Ahmed, 0. 2001. A model-based control for VA v distribution systems. Pre- sented at CLIMA Conference, Napoli. Ahmed, 0. 2002. Variable-volume, variable-pressure system. International Facilities Management Association, Research and Development Coun- cil, Orlando, FL. ANSI. 2013. Non-recirculating direct gas-fired industrial air heaters. ANSI Standard Z83.4-2013/CSA Standard 3.7-2013. American National Stan- dards Institute, Washington, D.C., and Canadian Standards Association, Toronto. Arens, E., H. Zhang, T. Hoyt, S. Kaam, J. Goins, F. Bauman, Y. Zhai, T. Webster, and B. West. 2014. Thermal and air quality acceptability in buildings that reduce energy by reducing minimum airflow from over- head diffusers. ASHRAE Research Project RP-1515, Final Report. ASHRAE. 2003. Risk management guidance for health, safety, and environ- mental security under extraordinary incidents. Presidential Ad Hoc Com- mittee for Building Health and Safety Under Extraordinary Incidents. ASHRAE. 2005. Sequences of operation for common HVAC systems. ASHRAE. 2011. Standard 62.1-2010 user 's manual. ASHRAE. 2005. The commissioning process. Guideline 0-2005. ASHRAE. 2007. HVAC&R technical requirements for the commissioning process. Guideline 1.1. ASHRAE. 2009. Field testing ofHVAC controls components. Guideline 11. ASHRAE. 2007. Specifying direct digital control systems. Guideline 13- 2007. ASHRAE. 2010. Selecting outdoor, return, and relief dampers for air-side economizer systems. ASHRAE Guideline 16. ASHRAE. 2013. Ventilation for acceptable indoor air quality. ANSI/ ASHRAE Standard 62.1-2013. ASHRAE. 2013. Energy standard for buildings except low-rise residential buildings. ANSI/ASHRAE/IES Standard 90.1-2013. ASHRAE 2012. BACnet� -A data communication protocol for building automation and control networks. ANSI/ASHRAE Standard 135-2012. ASHRAE. 2013. Ventilation ofhealth care facilities. ANSI/ASHRAE/ASHE Standard 170-2013. ASME. 2012. Controls and safety devices for automatically fired boilers. American Society of Mechanical Engineers, New York. Deng, S.-M., and J. Burnett. 1997. Performance monitoring and measure- ment for central air conditioning chiller plants in buildings in Hong Kong. HKIE Transactions 4(1). EDR. 2009. Advanced variable air volume system design guide. Energy Design Resources, Pacific Gas and Electric Company. Englander, S.L., and L.K. Norford. 1992. Saving fan energy in VAV sys- tems-Part 2: Supply fan control for static pressure minimization. ASHRAE Transactions 98(1):19-32. Erpelding, B. 2007. Real efficiencies of central plants. HPAC Engineering (May). Felker, L.G., and T.L. Felker. 2010. Dampers and airflow control. ASHRAE. FEMA. 2007. Reference manual to mitigate potential terrorist attacks against buildings. Publication 426, Federal Emergency Management Agency, U.S. Department of Homeland Security, Washington, D.C. FGI. 2018. Guidelines for design and construction ofhealth care facilities. Facility Guidelines Institute, Dallas. Hartman, T. 1993. Terminal regulated air volume (TRAV) systems. ASH- RAE Transactions 99(1):791-800, Paper CH-93-03-3. Hartman, T. 2005. Designing efficient systems with the equal marginal per- formance principle. ASHRAE Journal 47(7):64-70. Hartman, T. 2012. New strategies for optimizing building performance. HPAC Engineering. hypac.com/buiking.com/cholo/hew-stes-spingfing/ -building-performance. Hydeman, M. In progress. Advanced control sequences for HVAC sys- tems- Phase 1, air distribution and terminal systems. ASHRAE Re- search Project RP-1455. Kalore, P. - 0. Ahmed, and M. Cascia. 2003. Dynamic control of a building fluid distribution system. Presented at IEEE Conference on Control Applications, Istanbul. Kettler, J. 1995. Minimum ventilation control for VAV systems-Fan tracking vs. workable solutions. ASHRAE Transactions 101(2):625-630. Paper SD-95-02-3. Kettler, J. 2000. Measuring and controlling outdoor airflow. ASHRAE IAQ Applications (Winter). Krarti, M., C.C. Schroeder, E. Jeanette, and M.J. Brandemuehl. 2000. Ex- perimental analysis of measurement and control techniques of outside air intake rates in VAV systems (RP-980). ASHRAE Transactions 106(1): 39-52, Paper 4369. Lau, J., G.K. Yuill, and X. Lin. 2013. CO2-based demand controlled venti- lation for multiple zone HVAC systems. ASHRAE Research Project RP- 1547, Final Report. Nelson, K. 2012. Simulation modeling of central chilled water systems. ASHRAE Transactions 118(1), Paper CH-12-003. NFPA. 2014. National electrical codeⓇ. ANSI/NFPA Standard 70-2014. National Fire Protection Association, Quincy, MA. Inc. ASHRAE, 2019 user. single for Licensed | {}
63a04d3c-e604-450b-894c-f434ce2b0116 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Design and Application of Controls 48.23 NIOSH. 2002. Guidance for protecting building environments from airborne chemical, biological, or radiological attacks. DHHS Publication 2002- 139. National Institute for Occupational Safety and Health, Department of Health and Human Services, Cincinnati. Taylor, S. 2002. Primary-only vs. primary-secondary variable flow systems. ASHRAE Journal 44(2):25-29. Taylor, S. 2007. Increasing efficiency with VAV system static pressure set- point reset. ASHRAE Journal 49(6):24-32. Taylor, S. 2011. Optimizing design and control of chilled water plants, part 1: Chilled water distribution system selection. ASHRAE Journal (July). USDOJ. 1994. ADA standards for accessible design. Title III Regulations, Appendix A. 28CFR36. U.S. Department of Justice, Washington, D.C. USGBC. 2009. LEEDⓇ reference guide for green building design and con- struction. U.S. Green Building Council, Washington, D.C. BIBLIOGRAPHY ASHRAE. 2013. Commissioning process for buildings and systems. ANSI/ ASHRAE/IES Standard 202-2013. Avery, G. 1992. The instability of VAV systems. HPAC Engineering (Feb- ruary):47-50. Federspiel, C.C. 2005. Detecting critical supply duct pressure, ASHRAE Transactions 111(1):957-963, Paper OR-05-13-1. Kettler, J. 2004. Return fans or relief fans: How to choose? ASHRAEJournal 46(4):28-32. Mills, E., H. Friedman, T. Powell, N. Bourassa, D. Claridge, T. Haasl, and M.A. Piette. 2004. The cost-effectiveness of commercial-buildings com- missioning. Report LBNL-56637 (rev.). Lawrence Berkeley National Laboratory. PDF available from sites.google.com/site/evanmillsresearch /home/publications. Salsbury, T. and B. Chen. 2002. A new sequence controller for multistage systems ofknown relative capacities. International Journal ofHVAC&R Research (now Science and Technologyfor the Built Environment) 8(4): 403-428. Seem, J., M. House, G. Kelly, and C. Klaassen. 2000. A damper control sys- tem for preventing reverse airflow through exhaust air dampers. Interna- tional Journal of HVAC&R Research (now Science and Technologyfor the Built Environment) 6(2): 135-148. Shadpour, F. 2001. Fundamentals ofHVAC direct digital control: Practical applications and design. Hacienda Blue, Escondido, CA. U.S. DOE. 2008. Continuous commissioning process. Ch. 8 in Commission- ing for federalfacilities. U.S. Department of Energy, Washington, D.C. energy.gov/node/727996. Inc. ASHRAE, 2019 user single for Licensed | {}
6d51d05a-b0b0-4fbd-a0ab-65c5c97b8b0e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Licensed for single user. Ⓒ 2019 ASHRAE, Inc. Related Commercial Resources | {}
7af14970-0a57-47d4-bdeb-77318d962cd6 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | CHAPTER 49 NOISE AND VIBRATION CONTROL ¦ DATA RELIABILITY ¦ 49.1 ¦ ¦ --- ¦ --- ¦ ¦ ACOUSTICAL DESIGN OF HVAC SYSTEMS ¦ 49.1 ¦ ¦ Receiver Considerations ¦ 49.2 ¦ ¦ Basic Acoustical Design Techniques ¦ 49.8 ¦ ¦ Source Sound Levels ¦ 49.8 ¦ ¦ Path Noise Estimation and Control ¦ 49.18 ¦ ¦ Receiver Room Sound Correction ¦ 49.31 ¦ ¦ Sound Control for Outdoor Equipment ¦ 49.34 ¦ ¦ Fume Hood Duct Design ¦ 49.35 ¦ ¦ Mechanical Equipment Room Sound Isolation ¦ 49.36 ¦ ¦ HVAC Noise-Reduction Design Procedures ¦ 49.39 ¦ ¦ VIBRATION ISOLATION AND CONTROL ¦ 49.43 ¦ ¦ Vibration Measurement ¦ 49.43 ¦ In this chapter, sound and noise are used interchangeably, al- though only unwanted sound is considered to be noise. H interior noise, and its effect on the acoustical environment is AC equipment for a building is one of the major sources of important. Also, noise from equipment located outdoors often prop- agates to the community. Therefore, mechanical equipment must be selected, and equipment spaces designed, with an emphasis on both the intended uses of the equipment and the goal of providing ac- ceptable sound levels in occupied spaces of the building and in the surrounding community. Operation ofHVAC equipment can also in- duce mechanical vibration that propagates into occupied spaces through structureborne paths such as piping, ductwork, and mounts. Vibration can cause direct discomfort and also create secondary ra- diation of noise from vibrating walls, floors, piping, etc. System analysis for noise control uses the source-path-receiver concept. The source of the sound is the noise-generating mechanism. The sound travels from the source via a path, which can be through the air (airborne) or through the structure (structureborne), or a com- bination of both paths, until it reaches the receiver (building occu- pant or outdoor neighbor). Components of the mechanical system (e.g., fans, dampers, dif- fusers, duct junctions) all may produce sound by the nature of the airflow through and around them. As a result, almost all HV AC com- ponents must be considered. Because sound travels effectively in the same or opposite direction of airflow, downstream and upstream paths are often equally important. This chapter provides basic sound and vibration principles and data needed by HVAC system designers. Many of the equations as- sociated with sound and vibration control for HVAC may be found in Chapter 8 of the 2017 ASHRAE Handbook-Fundamentals. Addi- tional technical discussions along with detailed HV AC component and system design examples can be found in the references. 1. DATA RELIABILITY Data in this chapter come from both consulting experience and re- search studies. Use caution when applying the data, especially for sit- uations that extrapolate from the framework of the original research. Test data tolerances and cumulative system effects lead to a typical uncertainty of ±2 dB. However, significantly greater variations may occur, especially in low frequency ranges and particularly in the The preparation of this chapter is assigned to TC 2.6, Sound and Vibration. Related Commercial Resources Equipment Vibration 49.44 Vibration Criteria 49.45 Specification of Vibration Isolators 49.46 Vibration- and Noise-Sensitive Facilities 49.51 Internal Versus External Isolation 49.51 Isolating Vibration and Noise in Piping Systems 49.52 Seismic Protection 49.54 Vibration Investigations 49.54 COMMISSIONING 49.54 TROUBLESHOOTING 49.54 Determining Problem Source 49.55 Determining Problem Type 49.55 63 Hz octave band, where experience suggests that even correctly performed estimates may disagree with actual measured levels by 5 dB, so conservative design practices should be followed. 2. ACOUSTICAL DESIGN OF HVAC SYSTEMS For most HV AC systems, sound sources are associated with the building': s mechanical and electrical equipment. As shown in Figure 1, there are many possible paths for airborne and structureborne sound and vibration transmission between a sound source and re- ceiver. Noise control involves (1) selecting a quiet source, (2) opti- mizing room sound absorption, and (3) designing propagation paths for minimal noise transmission. Different sources produce sounds that have different frequency distributions, called spectral characteristics. For example, as shown in Figure 2, fan noise generally contributes to sound levels in the 16 to 250 Hz octave bands (curve A). (Frequencies that desig- nate the octave bands are often called octave midband [or center] ![image](/image/placeholder) SOUND C SOURCES B E D RECEIVER A Path A: Structureborne path through floor Path B: Airborne path through supply air system Path C: Duct breakout from supply air duct Path D: Airborne path through return air system Path E: Airborne path through mechanical equipment room wall Fig. 1 Typical Paths of Noise and Vibration Propagation in HVAC Systems 49.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
35c7c957-066d-45fd-b9a2-3aa8a2072ef7 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.2 Chart Type: line 16 Hz 31.5 Hz 63 Hz 125 Hz 250 Hz 500 Hz 1000 Hz 2000 Hz 4000 Hz item_01 60dB (fe 20 μPa) 60dB (fe 20 μPa) 55dB (fe 20 μPa) 50dB (fe 20 μPa) 45dB (fe 20 μPa) 40dB (fe 20 μPa) 35dB (fe 20 μPa) 30dB (fe 20 μPa) 25dB (fe 20 μPa) Fig. 2 HVAC Sound Spectrum Components for Occupied Spaces Inc. ASHRAE, 2019 user. single ![image](/image/placeholder) HISS AND WHISTLE Grilles and Water Valves WHINE Pumps and Chillers HUM AND BUZZ Poor Vibration Isolation Fan-Powered VAV Units ROAR Fans and Turbulent Airflow VAV Units RUMBLE Turbulent Airflow and Poor Vibration Isolation THROB Turbulent Airflow and Fan Instability 8 16 31.5 63 125 250 500 1000 2000 4000 8000 for Licensed OCTAVE MIDBAND FREQUENCY, Hz Fig. 3 Frequency Ranges of Likely Sources of Sound-Related Complaints (Schaffer 2005) ![image](/image/placeholder) Diffuser Noise Reciprocating, Centrifugal, and Screw Chillers VAV Unit Noise Fan and Pump Noise Fan Instability, Air Turbulence Rumble, and Structureborne Vibration WHISTLE AND THROB RUMBLE ROAR WHIRR HISS 8 16 31.5 63 125 250 500 1000 2000 4000 8000 OCTAVE MIDBAND FREQUENCY, Hz Fig. 4 Frequencies at Which Different Types of Mechanical Equipment Generally Control Sound Spectra (Schaffer 2005) 2019 ASHRAE Handbook-HVAC Applications (SI) frequencies.) Variable-air-volume (VA V) valve noise usually con- tributes to sound levels in the 63 to 1000 Hz octave bands (curve B). Diffuser noise usually contributes to the overall HVAC noise in the 250 to 8000 Hz octave bands (curve C). The overall sound pressure level associated with all of these sound sources combined is shown as curve D. Figure 3 (Schaffer 2005) shows the frequency ranges and de- scriptive terminology of the most likely sources of HVAC sound- related complaints. Figure 4 (Schaffer 2005) shows the frequencies at which different types of mechanical equipment generally control the sound spectra in a room. Occupant complaints may occur, how- ever, despite a well-designed sound spectrum in the room. Criteria specified in this chapter do not necessarily correspond with all indi- viduals' acceptability criteria. 2.1 RECEIVER CONSIDERA TIONS Indoor Sound Criteria Whether an occupant considers the background noise acceptable generally depends on two factors. First is the perceived loudness of the noise relative to that of normal activities; if it is clearly notice- able, it is likely to be distracting and cause complaint. Second is the sound quality of the background noise; if the noise is perceived as a rumble, throb, roar, hiss, or tone, this may result in complaints of annoyance and stress. The frequency spectrum is then said to be unbalanced. The acoustical design must ensure that HVAC noise is of suffi- ciently low level and unobtrusive quality so as not to interfere with occupancy use requirements. If background noise reduces speech intelligibility, for example, complaints oflost productivity can result. Accordingly, methods of rating HV AC-related noise ideally assess both perceived loudness and sound quality (Wang et al. 2013). Design Guidelines for HV AC-Related Background Sound in Rooms. Table 1 presents recommended goals for indoor back- ground noise levels in various types of unoccupied rooms served by HVAC systems. Perceived loudness and task interference are fac- tored into the numerical part of the rating. The sound quality design target is assumed to be a neutral-sounding spectrum, although some spectral imbalance is probably tolerable within limits for most users. The criteria used are described in the next section. The NC/RC designations relate to reference curves with octave band sound pressure levels that are (1) selected based on appropri- ate loudness in the speech interference range (500 to 2000 Hz) and (2) show contours for high and low frequencies that are balanced at the same loudness level. Acoustical evaluation based on octave bands and target balanced contours is recommended, because over- all dBA ratings do not reflect undesirable contributions of excessive low-frequency noise. The dBA and dBC levels are listed only as ap- proximate references in the case of simplistic measurements, where dBA indicates relative loudness and dBC indicates prevalence of low-frequency noise. Exact specifications should be established by acoustical experts considering occupant sensitivity. An acceptable noise level depends on the specific use of the space, so each number rating typically represents a range of ±5 dB for the design target. For example, private offices and conference rooms are listed as NC/RC 30. This means that unless there are extenuating circumstances, the background noise level should be less than NC/RC 35, but in some locations (e.g., executive offices or specialty conference rooms), a noise criterion of as low as NC/RC 25 might be warranted. On the other hand, there is not necessarily a benefit to achieving the lower number in regular offices, as some background noise maintains a minimum level of acoustic privacy between adjacent offices. Criteria Descriptions. This section presents ways to rate or mea- sure the sound to determine acceptability. The information should help the design engineer select the most appropriate background | {}
53fa7309-b786-4569-9ac6-13bb8bfa6ab5 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.3 Table 1 Design Guidelines for HVAC-Related Background Sound in Rooms ¦ Room Types ¦ Room Types ¦ Octave Band Analysisa ¦ Approximate Overall Sound Pressure Levela ¦ Approximate Overall Sound Pressure Levela ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Room Types ¦ Room Types ¦ NC/RCb ¦ dBAc ¦ dBCc ¦ ¦ Rooms with intrusion from outdoor noise sourcesd ¦ Traffic noise ¦ N/A ¦ 45 ¦ 70 ¦ ¦ Rooms with intrusion from outdoor noise sourcesd ¦ Aircraft flyovers ¦ N/A ¦ 45 ¦ 70 ¦ ¦ Residences, apartments, condominiums ¦ Living areas ¦ 30 ¦ 35 ¦ 60 ¦ ¦ Residences, apartments, condominiums ¦ Bathrooms, kitchens, utility rooms ¦ 35 ¦ 40 ¦ 60 ¦ ¦ Hotels/motels ¦ Individual rooms or suites ¦ 30 ¦ 35 ¦ 60 ¦ ¦ Hotels/motels ¦ Meeting/banquet rooms ¦ 30 ¦ 35 ¦ 60 ¦ ¦ Hotels/motels ¦ Corridors and lobbies ¦ 40 ¦ 45 ¦ 65 ¦ ¦ Hotels/motels ¦ Service/support areas ¦ 40 ¦ 45 ¦ 65 ¦ ¦ Office buildings ¦ Executive and private offices ¦ 30 ¦ 35 ¦ 60 ¦ ¦ Office buildings ¦ Conference rooms ¦ 30 ¦ 35 ¦ 60 ¦ ¦ Office buildings ¦ Teleconference rooms ¦ 25 ¦ 30 ¦ 55 ¦ ¦ Office buildings ¦ Open-plan offices ¦ 40 ¦ 45 ¦ 65 ¦ ¦ Office buildings ¦ Corridors and lobbies ¦ 40 ¦ 45 ¦ 65 ¦ ¦ Courtrooms ¦ Unamplified speech ¦ 30 ¦ 35 ¦ 60 ¦ ¦ Courtrooms ¦ Amplified speech ¦ 35 ¦ 40 ¦ 60 ¦ ¦ Performing arts spaces ¦ Drama theaters, concert and recital halls ¦ 20 ¦ 25 ¦ 50 ¦ ¦ Performing arts spaces ¦ Music teaching studios ¦ 25 ¦ 30 ¦ 55 ¦ ¦ Performing arts spaces ¦ Music practice rooms ¦ 30 ¦ 35 ¦ 60 ¦ ¦ Hospitals and clinics ¦ Patient rooms ¦ 30 ¦ 35 ¦ 60 ¦ ¦ Hospitals and clinics ¦ Wards ¦ 35 ¦ 40 ¦ 60 ¦ ¦ Hospitals and clinics ¦ Operating and procedure rooms ¦ 35 ¦ 40 ¦ 60 ¦ ¦ Hospitals and clinics ¦ Corridors and lobbies ¦ 40 ¦ 45 ¦ 65 ¦ ¦ Laboratories ¦ Testing/research with minimal speech communication ¦ 50 ¦ 55 ¦ 75 ¦ ¦ Laboratories ¦ Extensive phone use and speech communication ¦ 45 ¦ 50 ¦ 70 ¦ ¦ Laboratories ¦ Group teaching ¦ 35 ¦ 40 ¦ 60 ¦ ¦ Churches, mosques, synagogues ¦ General assembly with critical music programse ¦ 25 ¦ 30 ¦ 55 ¦ ¦ Schoolsf ¦ Classrooms ¦ 30 ¦ 35 ¦ 60 ¦ ¦ Schoolsf ¦ Large lecture rooms with speech amplification ¦ 30 ¦ 35 ¦ 60 ¦ ¦ Schoolsf ¦ Large lecture rooms without speech amplification ¦ 25 ¦ 30 ¦ 55 ¦ ¦ Libraries Indoor stadiums, gymnasiums ¦ ¦ 30 ¦ 35 ¦ 60 ¦ ¦ Libraries Indoor stadiums, gymnasiums ¦ Gymnasiums and natatoriumsg ¦ 45 ¦ 50 ¦ 70 ¦ ¦ Libraries Indoor stadiums, gymnasiums ¦ Large-seating-capacity spaces with speech amplificationg ¦ 50 ¦ 55 ¦ 75 ¦ N/A = Not applicable aValues and ranges are based on judgment and experience, and represent general limits of acceptability for typical building occupancies. bNC: this metric plots octave band sound levels against a family ofreference curves, with the number rating equal to the highest tangent line value. RC: when sound quality in the space is important, the RC metric provides a diagnostic tool to quantify both the speech interference level and spectral imbalance. cdBA and dBC: these are overall sound pressure level measurements with A- and C-weight- ing, and serve as good references for a fast, single-number measurement. They are also appropriate for specification in cases where no octave band sound data are available for design. dIntrusive noise is addressed here for use in evaluating possible non-HVAC noise that is likely to contribute to background noise levels. noise rating method for a specific project. Current methods described here and in other references include the traditional A-weighted sound pressure level (dBA) and tangent Noise Criteria (NC), the Room Criterion (RC) and more recent RC Mark II, the Balanced Noise Criterion (NCB), and the Room Noise Criteria (RNC). Each method was developed based on data for specific applications; hence, not all are equally suitable for rating HVAC-related noise in the variety of applications encountered. The preferred sound rating methods generally comprise two distinct parts: a family of criterion curves (specifying sound levels by octave bands), and a procedure for rating the calculated or measured sound data relative to the crite- rion curves with regard to sound quality. cAn experienced acoustical consultant should be retained for guidance on acous- tically critical spaces (below RC 30) and for all performing arts spaces. fSome educators and others believe that HVAC-related sound criteria for schools, as listed in previous editions of this table, are too high and impede learning for affected groups of all ages. See ANSI/ASA Standard S12.60 for classroom acoustics and a justification for lower sound criteria in schools. The HVAC com- ponent of total noise meets the background noise requirement of that standard if HVAC-related background sound is approximately NC/RC 25. Within this cate- gory, designs for K-8 schools should be quieter than those for high schools and colleges. gRC or NC criteria for these spaces need only be selected for the desired speech and hearing conditions. Ideally, HVAC-related background noise should have the follow- ing characteristics: · Balanced contributions from all parts of the sound spectrum with no predominant frequency bands of noise · No audible tones such as hum or whine · No fluctuations in level such as throbbing or pulsing dBA and dBC: A- and C-Weighted Sound Level. The A-weighted sound level (described in Chapter 8 of the 2017 ASHRAE Hand- book-Fundamentals) has been used for more than 60 years as a single-number measure of the relative loudness of noise, especially for outdoor environmental noise standards. The rating is expressed as a number followed by dBA (e.g., 40 dBA). Inc. ASHRAE, 2019 user. single for Licensed | {}
d57bf0b6-15c0-4205-bbab-ef1101bd34b3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.4 A-weighted sound levels can be measured with simple sound level meters. The ratings correlate fairly well with human judg- ments of relative loudness but take no account of spectral balance or sound quality. Thus, two different spectra can result in the same numeric value, but have quite different subjective qualities. Inc. Along with dBA, there is also a C-weighted sound level, de- noted as dBC, which is more sensitive to low-frequency sound contributions to the overall sound level than is dBA. When the quantity dBC - dBA is large (e.g., greater than 25 dB), significant low-frequency sound is present. It is recommended that when specifying background sound levels in dBA, the dBC is also in- cluded in the specification and does not exceed the dBA reading by more than 20 dB. NC: Noise Criteria Method. The NC method for rating noise (de- scribed in Chapter 8 of the 2017 ASHRAE Handbook-Fundamen- tals) has been used for more than 50 years. It is a single-number rating that is somewhat sensitive to the relative loudness and speech interference properties of a given noise spectrum. The method con- sists of a family of criterion curves, shown in Figure 5, extending from 63 to 8000 Hz, and a tangency rating procedure. The criteri- on curves define the limits of octave band spectra that must not be exceeded to meet occupant acceptance in certain spaces. The rating is expressed as NC followed by a number (e.g., NC 40). The octave midband frequency of the point at which the spectrum is tangent to the highest NC curve should also be reported (e.g. NC 40 [125 Hz]). The NC values are formally defined only in 5 dB increments, with intermediate values determined by discretionary interpolation. ASHRAE, 2019 user. Widely used and understood, the NC method is sensitive to level but has the disadvantage that the tangency method used to determine the rating does not require that the noise spectrum precisely follow the balanced shape of the NC curves. Thus, sounds with different frequency content can have the same numeric rating, but rank dif- ferently on the basis of sound quality. With the advent of V AV sys- tems, low-frequency content (i.e., below the 63 Hz octave band) is prevalent, and the NC rating method fails to properly address this issue (Ebbing and Blazier 1992). Consequently, ifthe NC method is single for Licensed Chart Type: line NC NC 60 NC 55 NC 50 NC 45 NC 40 NC 35 NC 30 NC 25 NC 20 NC 15 item_01 65dB 60dB 55dB 50dB 45dB 43dB 40dB 35dB 30dB 25dB 15dB Fig. 5 Noise Criteria Curves 2019 ASHRAE Handbook-HVAC Applications (SI) chosen, sound levels at frequencies below 63 Hz must be evaluated by other means. In HVAC systems that do not produce excessive low-frequency noise and strong discernible pure tones, the NC rating correlates rel- atively well with occupant satisfaction if sound quality is not a sig- nificant concern. NC rating is often used because of its simplicity. RC/RC Mark II: Room Criteria Method. ASHRAE previously recommended the Room Criterion (RC) curves (beginning in Chapter 43 in the 1995 ASHRAE Handbook-HVAC Systems and Equipment, Blazier 1981a, 1981b) as an enhanced method for rating HVAC system related noise. The revised RC Mark II method is now preferred. The RC method is a family of criterion curves and a rating pro- cedure. The shape of these curves represents a well-balanced, bland-sounding spectrum, including two additional octave bands (16 and 31.5 Hz) to deal with excessive low-frequency noise. This rating procedure assesses background noise in spaces on the basis of its effect on speech, and on subjective sound quality. The rating value is expressed as RC followed by a number that represents the level of noise in the speech interference region of the spectrum, and a letter to indicate the quality (e.g., RC 35[N], where N denotes the desirable neutral rating). The RC method includes evaluation of the potential for noise-induced vibration from excessive airborne sound levels at and below 63 Hz. Based on experience and ASHRAE-sponsored research (Broner 1994), the RC method was revised to the RC Mark II method (Bla- zier 1997). Like its predecessor, the RC Mark II method is intended for use as a diagnostic tool for analyzing noise problems in the field. The RC Mark II method is complicated, but computerized spreadsheets and HVAC system analysis programs are available to perform the calculations and graphical analysis. The RC Mark II method has three parts: (1) a family of criterion curves (Figure 6), (2) a procedure for determining the RC numerical rating and the noise spectral balance (quality), and (3) a procedure for estimating occupant satisfaction when the spectrum does not have the shape of an RC curve (quality assessment index) (Blazier 1995). The rating is expressed as RC followed by a number and a let- ter (e.g., RC 35[N]). The number is the arithmetic average rounded to the nearest integer of sound pressure levels in the 500, 1000, and 2000 Hz octave bands (the main speech frequency region) and is known as the preferred speech interference level (PSIL). The let- ter is a qualitative descriptor that identifies the sound' s perceived character: (N) for neutral, (LF) for low-frequency rumble, (MF) for midfrequency roar, and (HF) for high-frequency hiss. There are also two subcategories of the low-frequency descriptor: (LFB), denoting a moderate but perceptible degree of sound-induced ceiling/wall vibration, and (LF A), denoting a noticeable degree of sound-induced vibration. Each reference curve in Figure 6 identifies the shape of a neutral, bland-sounding spectrum, indexed to a curve number corresponding to the sound level in the 1000 Hz octave band. The shape of these curves is based on Blazier (1981a, 1981b), modified at 16 Hz fol- lowing recommendations of the research in Broner (1994). Regions A and B denote levels at which sound can induce vibration in light wall and ceiling construction, which can potentially cause rattles in light fixtures, furniture, etc. Curve T is the octave band threshold of hearing as defined by ANSI Standard S12.2. Procedure for Determining the RC Mark II Rating for a System. Step 1. Obtain the arithmetic average of the sound levels in the principal speech frequency range represented by the levels in the 500, 1000, and 2000 Hz octave bands (PSIL). (This is not to be con- fused with the ANSI-defined "speech-interference level" [SIL], a four-band average obtained by including the 4000 Hz octave band as used with the NCB method.) The RC reference curve is chosen to | {}
83dc13fc-f72f-4c0a-a699-4347c9ec0b26 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.5 X-Axis: Frequency, Hz Y-Axis: Sound Pressure Level, dB (dB) Chart Type: line left right item_01 50dB (dB) 40dB (dB) Note: · Noise levels for lightweight wall and ceiling constructions: - In shaded region B are likely to generate vibration that may be perceptible. There is a slight possibility of rattles in light fixtures, doors, windows, etc. - In shaded region A have a high probability of generating easily perceptible noise- induced vibration. Audible rattling in light fixtures, doors, windows, etc. may be anticipated. · Regions LF, MF, and HF are explained in the text. · Solid dots are sound pressure levels for the example discussed in the text. Fig. 6 Room Criterion Curves, Mark II be that which has the same value at 1000 Hz as the calculated aver- age value. Step 2. Calculate the quality assessment index (QAI) (Blazier 1995), which measures the deviation of the spectrum under evalua- tion from the shape of the RC reference curve. Calculate the energy- averaged spectral deviations from the RC reference curve in each of three frequency groups: low (LF; 16 to 63 Hz), medium (MF; 125 to 500 Hz), and high (HF ; 1000 to 4000 Hz). (A simple arithmetic average of these deviations is often adequate for most engineering purposes.) Equation (1) gives the procedure for the LF region; repeat for the MF and HF regions by substituting the corresponding values at each frequency. LF = 10 log[(100.1△L16 + 100.1△L31.5 + 100.1AL63)/3] The AL terms are the differences between the spectrum being evaluated and the RC reference curve in each frequency band. In this way, three specific spectral deviation factors, expressed in dB with either positive or negative values, are associated with the spectrum being rated. QAI is the range in dB between the highest and lowest values of the spectral deviation factors. If QAI ≤ 5 dB, the spectrum is assigned a neutral (N) rating. If QAI exceeds 5 dB, the sound quality descriptor of the RC rating is the letter designation ofthe frequency region of the deviation factor having the highest positive value. Example 1. The spectrum plotted in Figure 6 indicated by large dots is pro- cessed in Table 2. The arithmetic average of the sound levels in the 500, Table 2 Example 1 Calculation of RC Mark II Rating ¦ ¦ Frequency, Hz ¦ Frequency, Hz ¦ Frequency, Hz ¦ Frequency, Hz ¦ Frequency, Hz ¦ Frequency, Hz ¦ Frequency, Hz ¦ Frequency, Hz ¦ Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ 16 ¦ 31 ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ ¦ Spectrum levels ¦ 64 ¦ 65 ¦ 64 ¦ 57 ¦ 47 ¦ 40 ¦ 35 ¦ 30 ¦ 23 ¦ ¦ Average of 500 to 2000 Hz levels ¦ ¦ ¦ ¦ ¦ ¦ ¦ 35 ¦ ¦ ¦ ¦ RC contour ¦ 60 ¦ 60 ¦ 55 ¦ 50 ¦ 45 ¦ 40 ¦ 35 ¦ 30 ¦ 25 ¦ ¦ Levels: RC contour ¦ 4 ¦ 5 ¦ 9 ¦ 7 ¦ 2 ¦ 0 ¦ 0 ¦ 0 ¦ - 2 ¦ ¦ ¦ ¦ LF ¦ ¦ ¦ MF ¦ ¦ ¦ HF ¦ ¦ ¦ Spectral deviations ¦ ¦ 6.6 ¦ ¦ ¦ 4.0 ¦ ¦ ¦ -0.6 ¦ ¦ ¦ QAI ¦ 7.2 ¦ 7.2 ¦ 7.2 ¦ 7.2 ¦ 7.2 ¦ 7.2 ¦ 7.2 ¦ 7.2 ¦ 7.2 ¦ ¦ RC Mark II rating ¦ RC 35(LF) ¦ RC 35(LF) ¦ RC 35(LF) ¦ RC 35(LF) ¦ RC 35(LF) ¦ RC 35(LF) ¦ RC 35(LF) ¦ RC 35(LF) ¦ RC 35(LF) ¦ 1000, and 2000 Hz octave bands is 35 dB, so the RC 35 curve is selected as the reference for spectrum quality evaluation. The spectral deviation factors in the LF, MF, and HF regions are 6.6, 4.0, and -0.6 respectively, giving a QAI of 7.2. The maximum positive deviation factor occurs in the LF region and QAI exceeds 5; therefore, the rating of the spectrum is RC 35(LF). An average room occupant should perceive this spectrum as rumbly in character. Estimating Occupant Satisfaction Using QAI. The QAI estimates the probable reaction of an occupant when system design does not produce optimum sound quality. The basis for estimating occupant satisfaction is that changes in sound level of less than 5 dB do not cause subjects to change their ranking of sounds of similar spectral content. However, level changes greater than 5 dB do significantly affect subjective judgments. A QAI of 5 dB or less corresponds to a generally acceptable condition, pro- vided that the perceived level of the sound is in a range consistent with the given type of space occupancy as recommended in Table 2. (An exception to this rule is when sound pressure levels in the 16 or 31 Hz octave bands exceed 65 dB. In such cases, there is potential for acoustically induced vibration in typical low-mass office con- struction. Levels above 75 dB in these bands indicate a significant problem with induced vibration.) A QAI that exceeds 5 dB but is less than or equal to 10 dB rep- resents a marginal situation, in which acceptance by an occupant is questionable. However, a QAI greater than 10 dB will likely be objectionable to the average occupant. Table 3 lists sound quality descriptors and QAI values and relates them to probable occupant reaction to the noise. The numerical part of the RC rating may sometimes be less than the specified maximum for the space use, but with a sound quality descriptor other than the desirable (N). For example, a maximum of RC 40(N) is specified, but the actual noise environment turns out to be RC 35(MF). There is insufficient knowledge in this area to de- cide which spectrum is preferable. (1) Even at moderate levels, if the dominant portion of the back- ground noise occurs at a very low frequency, some people can expe- rience a sense of oppressiveness or depression in the environment (Persson- w ayne et al. 1997). Such a complaint may result after exposure to that environment for several hours, and thus may not be noticeable during a short exposure period. NCB: Balanced Noise Criteria Method. The NCB method (ANSI Standard S12.2; Beranek 1989) is used to specify or evaluate room noise, including that from occupant activities. The NCB criterion curves (Figure 7) are intended as an improvement over the NC curves by including the two low-frequency octave bands (16 and 31.5 Hz), and by lowering permissible noise levels at high frequencies (4000 and 8000 Hz). Rating is based on the speech interference level (SIL = the average of the four sound pressure levels at octave midband frequencies of 500, 1000, 2000, and 4000 Hz) with additional tests for rumble and hiss compliance. The rating is expressed as NCB followed by a number (e.g., NCB 40). Inc. ASHRAE, 2019 user. single for Licensed | {}
b05dc423-83e4-4b37-97df-a89706a7b5b6 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.6 2019 ASHRAE Handbook-HVAC Applications (SI) Table 3 Definition of Sound-Quality Descriptor and Quality Assessment Index (QAI), to Aid in Interpreting RC Mark II Ratings of HVAC-Related Sound ¦ Sound-Quality Descriptor ¦ Description of Subjective Perception ¦ Magnitude of QAI ¦ Probable Occupant Evaluation, Assuming Level of Specified Criterion is Not Exceeded ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ (N) Neutral (Bland) ¦ Balanced sound spectrum, no single frequency range dominant ¦ QAI ≤5 dB, L16, L31 ≤ 65 QAI ≤5 dB, L16, L31 > 65 ¦ Acceptable Marginal ¦ ¦ (LF) Rumble ¦ Low-frequency range dominant (16 to 63 Hz) ¦ 5 dB < QAI ≤ 10 dB QAI > 10 dB ¦ Marginal Objectionable ¦ ¦ (LFVB) Rumble, with moderately perceptible room surface vibration ¦ Low-frequency range dominant (16 to 63 Hz) ¦ QAI≤5 dB, 65 10 dB ¦ Marginal Marginal Objectionable ¦ ¦ (LFVA) Rumble, with clearly perceptible room surface vibration ¦ Low-frequency range dominant (16 to 63 Hz) ¦ QAI ≤5 dB, L16, L31 > 75 5 dB < QAI ≤ 10 dB QAI > 10 dB ¦ Marginal Marginal Objectionable ¦ ¦ (MF) Roar ¦ Mid-frequency range dominant (125 to 500 Hz) ¦ 5 dB < QAI ≤ 10 dB QAI > 10 dB ¦ Marginal Objectionable ¦ ¦ (HF) Hiss ¦ High-frequency range dominant (1000 to 4000 Hz) ¦ 5 dB < QAI ≤ 10 dB QAI > 10 dB ¦ Marginal Objectionable ¦ Chart Type: line NCB 65 60 55 50 45 40 35 30 25 20 15 10 item_01 90% 85% 70% 60% 55% 50% 45% 40% 35% 30% 25% 20% 10% Fig. 7 NCB Noise Criterion Curves The NCB method is better than the NC method in determining whether a noise spectrum has an unbalanced shape sufficient to demand corrective action, and it addresses the issue of low- frequency noise. Rating is, however, more complicated than the familiar NC tangency method. The NCB method can still be used as a tangency method; if so used, the point of tangency, which sets the rating, must be cited. RNC: Room Noise Criteria Method. This rating method has been recently introduced and is described in detail in the American National Standards Institute (ANSI) Standard S12.2-2008. It is mentioned here for reference only and, at present, ASHRAE has no formal position on the use of this method. Table 4 summarizes the essential differences, advantages, and disadvantages ofrating methods used to characterize HV AC-related background noise. Unfortunately, at this time there is no acceptable and simple process to characterize the effects of audible tones and level fluctuations, so none of these rating methods address these issues. Noise Criteria for Plumbing Systems. Acceptable noise levels from plumbing fixtures and piping have not been widely identified in the literature, except in ANSI/ASA Standard S12.60. Continuous noise from plumbing fixtures and piping systems with circulating fluids should meet the same noise criteria as HVAC systems. How- ever, many sounds from plumbing fixtures and piping are of short duration or are transient, and typically have a somewhat higher threshold of acceptance. Examples of these sources include water flow noise associated with typical restroom fixtures; noise from waste lines connected to restroom, kitchen, and/or laundry drains; and noise from jetted bathtubs. Table 5 presents suggested maximum A-weighted sound pres- sure levels for various transient plumbing noise sources in buildings with multiple occupancies. These criteria are minimum standards and are intended to apply to plumbing systems serving adjacent and nearby units in multifamily housing projects (apartments and con- dominiums), hospitals, educational facilities, and office buildings. Plumbing noise levels in luxury condominiums or private homes should be 5 to 10 dB lower than levels shown in Table 5. Achieving the recommended plumbing noise criteria in the fin- ished space usually requires special attention to pipe installation details, selection of suitable piping materials, design flow veloci- ties, and selection of appropriate fixtures. Determining Compliance. When taking field measurements to determine whether a space complies with the guidelines presented in Table 1, follow ANSI/ASA Standard S12.72 and note these pre- cautions: · Measure the noise with an integrating sound level meter with a real-time frequency analyzer meeting type 1 or 2 specifications, as defined in ANSI Standards S1.4 and S1.11. The meter should have been calibrated by an accredited calibration laboratory, with some assurance that the calibration accuracy has been main- tained. · Set the meter to display and save the equivalent energy sound pressure level L with the desired frequency filtering (e.g., octave eq bands, A-weighted, etc.). Each measurement should be a mini- mum of 15 s long. Inc. ASHRAE, 2019 user. single for Licensed | {}
c85c58ba-1515-4146-9afe-e9be06cc2cc0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.7 Table 4 Comparison of Sound Rating Methods ¦ Method ¦ Overview ¦ Considers Speech Interference Effects ¦ Evaluates Sound Quality ¦ Components Presently Rated by Each Method ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ dBA ¦ No quality assessment Frequently used for outdoor noise ordinances ¦ Yes ¦ No ¦ Cooling towers Water chillers Condensing units ¦ ¦ NC ¦ Can rate components Limited quality assessment Does not evaluate low-frequency rumble ¦ Yes ¦ Somewhat ¦ Air terminals Diffusers ¦ ¦ RC Mark II ¦ Used to evaluate systems Should not be used to evaluate components Evaluates sound quality Provides improved diagnostics capability ¦ Yes ¦ Yes ¦ Not used for component rating ¦ ¦ NCB ¦ Can rate components Some quality assessment ¦ Yes ¦ Somewhat ¦ See NC ¦ ¦ RNC ¦ Some quality assessment Attempts to quantify fluctuations ¦ Yes ¦ Somewhat ¦ Not used for component rating ¦ Table 5 Plumbing Noise Levels ¦ Receiving (listening) room ¦ Lmax (slow response) ¦ ¦ --- ¦ --- ¦ ¦ Residential bedroom/living room/dining room ¦ 35 ¦ ¦ Hospital patient room/classroom ¦ 40 ¦ ¦ Private office/conference room ¦ 40 ¦ ¦ Residential bathroom/kitchen ¦ 45 ¦ ¦ Open office/lobby/corridor ¦ 50 ¦ · Place the measurement microphone in potential listening loca- tions at least 1 m from room boundaries and noise sources and at least 0.5 m from furniture. More than one location may be mea- sured, and the microphone may be moved during measurement; movement should not exceed 0.15 m/s. · Note the operational conditions ofthe HVAC system at the time of the test. Turn off all non-HVAC system noises during the test. If possible, measure in a normally furnished, unoccupied room. · The test may be repeated with the entire HVAC system turned off, to determine whether the room 's ambient noise level from non- HVAC sources is contributing to the results. · Record the sound level meter make, model, and serial number; measured sound pressure levels for each microphone location; HVAC system 's operating conditions; and microphone location(s). When these levels are used as a basis for compliance verification, the following additional information must be provided: or L lev- · What sound metrics are to be measured (specify Leq max els, etc., in each octave frequency band) · Where and how the sound levels are to be measured (specify the space average over a defined area or specific points for a specified minimum time duration, etc.) · What type(s) of instruments are to be used to make the sound measurements (specify ANSI or IEC Type 1 or Type 2 sound level meters with octave band filters, etc.) · How sound measurements instruments are to be calibrated or checked (specify that instruments are to be checked with an acoustical calibrator both before and after taking sound level mea- surements, etc.) · How sound level measurements are to be adjusted for the presence of other sound sources (specify that background sound level mea- surements be performed without other sound sources under con- sideration operating; if background sound levels are within 10 dB of operational sound levels, then corrections should be per- formed; etc.) · How results of sound measurements are to be interpreted (specify whether octave band sound levels, NC, RC, dBA, dBC or other values are to be reported) Unless these six points are clearly stipulated, the specified sound criteria may be unenforceable. When applying the levels specified in Table 1 as a basis for de- sign, sound from non-HVAC sources, such as traffic and office equipment, may establish the lower limit for sound levels in a space. Outdoor Sound Criteria Acceptable outdoor sound levels are generally specified by local noise ordinances or other government codes, which almost always use the A-weighted noise level (dBA) as their metric. The usual (maximum noise level over a period) or Leq metric is either Lmax (average noise level over a period). The time constant (FAST or SLOW) used for L max Lp depends on the code. or Some communities have no ordinance and depend on state reg- ulations that often use the day/night noise level descriptor LDN, which is a combination of the daytime (7:00 AM to 10:00 PM) and nighttime (10:00 PM to 7:00 AM) average noise levels (Leq) with a 10 dB penalty for nighttime. Other descriptors also exist; specific requirements should be identified at the outset of each project. In some cases, regulatory agencies may also impose project-specific noise conditions on the basis of community reaction and for main- taining an appropriate acoustic environment at the project vicinity. Measurement or estimation of community noise is based on a location, often at the receiver' s property line, from a height of approximately 1.2 m that represents ear height for a typical person seated at ground level to any height to address upper-floor eleva- tions, but can be anywhere within the property line, and often near the facade of the closest dwelling unit. Alternatively, the measure- ment may be made at the property line of the noise source. In the absence of a local noise ordinance, county or state laws or codes or those of a similar community should be used. Even if activ- ity noise levels do not exceed those specified by an ordinance, com- munity acceptance is not ensured. Very low ambient levels or a noise source with an often-repeated, time-varying characteristic or strong tonal content may increase the likelihood of complaints. Without local ordinances, noise levels between 45 and 55 dBA may be considered in residential zones and 55 to 65 dBA in commercial zones. These are for outdoor use areas and, with standard building constructions, they also typically result in acceptable interior noise levels. Often, daytime noise levels (the period of daytime to be defined) are 10 dB higher than nighttime levels. Although most ordinances are given as A-weighted pressure level, attenuation by distance, barriers, buildings, and atmosphere are all frequency dependent. Thus, A-weighted levels do not give an accurate estimation of noise levels at distances from the source. If A-weighted sound levels of sources must be determined by means other than measurement, then octave band or one-third octave band Inc. ASHRAE, 2019 user. single for Licensed | {}
5897bb8c-cbb9-4fd6-90d0-4e63b9d7a008 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.8 2019 ASHRAE Handbook-HVAC Applications (SI) measurements of source sound pressure level at a distance, or (pref- erably) sound power level, must be obtained before calculating the attenuation. 2.2 BASIC ACOUSTICAL DESIGN TECHNIQUES To minimize sound transmitted from system components to occupied spaces, select fans and other related mechanical equip- ment and design air distribution systems considering the following: · Design the air distribution system to minimize flow resistance and turbulence. High flow resistance increases required fan pressure, which results in higher noise being generated by the fan, especially at low frequencies. Turbulence also increases flow noise generated by duct fittings and dampers, especially at low frequencies. · Select a fan to operate as near as possible to its rated peak effi- ciency when handling the required airflow and static pressure. Also, select a fan that generates the lowest possible noise at required design conditions. Using an oversized or undersized fan that does not operate at or near rated peak efficiency can substan- tially increase noise levels. · Design duct connections at both fan inlet and outlet for uniform and straight airflow. Both turbulence (at fan inlet and outlet) and flow separation at the fan blades can significantly increase fan-generated noise. Turning vanes near fan outlets can also increase turbulence and noise, especially if airflow is not sufficiently uniform. · Select duct silencers that do not significantly increase the re- quired fan total static pressure. Silencers with static pressure loss- es of 90 Pa or less can minimize regenerated noise from silencer airflow. · Place fan-powered mixing boxes associated with variable-volume air distribution systems away from noise-sensitive areas. · Minimize flow-generated noise by elbows or duct branch takeoffs whenever possible by locating them at least four to five duct diameters from each other. For high-velocity systems, it may be necessary to increase this distance to up to 10 duct diameters in critical noise areas. Using flow straighteners or honeycomb grids, often called "egg crates, , in the necks of short-length takeoffs that , lead directly to grilles, registers, and diffusers is preferred to using volume extractors that protrude into the main duct airflow. · Keep airflow velocity in ducts serving sound-sensitive spaces as low as possible by increasing the duct size to minimize turbulence and flow-generated noise (see Tables 8 and 9, in the section on Aerodynamically Generated Sound in Ducts). · Duct transitions should not exceed an included expansion angle of 15° , or the resulting flow separation may produce rumble noise. · Use turning vanes in large 90° rectangular elbows and branch takeoffs. This provides a smoother directional transition, thus reducing turbulence. · Place grilles, diffusers, and registers into occupied spaces as far as possible from elbows and branch takeoffs. · Minimize use of volume dampers near grilles, diffusers, and reg- isters in acoustically critical situations. · Vibration-isolate all reciprocating and rotating equipment con- nected to structure. Also, it is usually necessary to vibration- isolate mechanical equipment in the basement of a building as well as piping supported from the ceiling slab of a basement, directly below tenant space. It may be necessary to use flexible piping connectors and flexible electrical conduit between rotating or reciprocating equipment and pipes and ducts that are connected to the equipment. · Vibration-isolate ducts and pipes, using spring and/or neoprene hangers for at least the first 15 m from vibration-isolated equip- ment. · Use barriers near outdoor equipment when noise associated with the equipment will disturb adjacent properties. In normal practice, barriers typically produce no more than 15 dB of sound attenua- tion in the midfrequency range. To be effective, the noise barrier must at least block the direct "line of sight" between the source and receiver. Table 6 lists several common sound sources associated with mechanical equipment noise. Anticipated sound transmission paths and recommended noise reduction methods are also listed. Airborne and/or structureborne sound can follow any or all of the transmis- sion paths associated with a specified sound source. Schaffer (2005) has more detailed information in this area. 2.3 SOURCE SOUND LEVELS Accurate acoustical analysis of HVAC systems depends in part on reliable equipment sound data. These data are often available from equipment manufacturers in the form of sound pressure levels at a specified distance from the equipment or, preferably, equipment sound power levels. Standards used to determine equipment and component sound data are listed at the end of this chapter. When reviewing manufacturers' sound data, obtain certification that the data have been obtained according to one or more of the rel- evant industry standards. If they have not, the equipment should be rejected in favor of equipment for which data have been obtained according to relevant industry standards. See Ebbing and Blazier (1998) for further information. Fans Prediction of Fan Sound Power. The sound power generated by a fan performing at a given duty is best obtained from manu- facturers' test data taken under approved test conditions (AMCA Standard 300 or ASHRAE Standard 68/AMCA Standard 330). Applications of air-handling products range from stand-alone fans to systems with various modules and attachments. These appurte- nances and modules can have a significant effect on air-handler sound power levels. In addition, fans of similar aerodynamic perfor- mance can have significant acoustical differences. Predicting air-handling unit sound power from fan sound levels is difficult. Fan sound determined by tests may be quite different once the fan is installed in an air handler, which in effect creates a new acoustical environment. Proper testing to determine resulting sound power levels once a fan is installed is essential. Fan manufac- turers are in the best position to supply information on their prod- ucts, and should be consulted for data when evaluating the acoustic performance of fans for an air handler application. Similarly, air handler manufacturers are in the best position to supply acoustic information on air handlers. Air handler manufacturers typically provide discharge, inlet, and casing-radiated sound power levels for their units based on one of two methods. A common method is the fan-plus-algorithm method: the fan is tested as a stand-alone item, typically using AMCA Stan- dard 300, and an algorithm is used to predict the effect of the rest of the air-handling unit on the sound as it travels from the fan to the dis- charge and intake openings or is radiated through a casing with known transmission loss values. Another method is described in AHRI Standard 260, in which the entire unit is tested as an assem- bly, including fans, filters, coils, plenums, casing, etc., and the sound power level at the inlet and discharge openings, as well as the radi- ated sound power, is measured in a qualified reverberant room. Whenever possible, data obtained by the AHRI Standard 260 meth- od should be used because it eliminates much ofthe uncertainty pres- ent in the fan-plus-algorithm method. For a detailed description of fan operations, see Chapter 21 in the 2016 ASHRAE Hand- book-HVAC Systems and Equipment. Different fan types have different noise characteristics and within a fan type, several factors influence noise. Inc. ASHRAE, 2019 user. single for Licensed | {}
85e861ae-2f9d-4069-92df-14198c3b21e1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.9 Table 6 Sound Sources, Transmission Paths, and Recommended Noise Reduction Methods ¦ Sound Source ¦ Path No. ¦ ¦ --- ¦ --- ¦ ¦ Circulating fans; grilles; registers; diffusers; unitary equipment in room ¦ 1 ¦ ¦ Induction coil and fan-powered VAV mixing units ¦ 1, 2 ¦ ¦ Unitary equipment located outside of room served; remotely located air-handling equipment, such as fans, blowers, dampers, duct fittings, and air washers ¦ 2, 3 ¦ ¦ Compressors, pumps, and other reciprocating and rotating equipment (excluding air-handling equipment) ¦ 4, 5, 6 ¦ ¦ Cooling towers; air-cooled condensers ¦ 4, 5, 6, 7 ¦ ¦ Exhaust fans; window air conditioners ¦ 7, 8 ¦ ¦ Sound transmission between rooms ¦ 9, 10 ¦ ¦ No. Transmission Paths ¦ Noise Reduction Methods ¦ ¦ 1 Direct sound radiated from sound source to ear Reflected sound from walls, ceiling, and floor 5 Vibration transmitted via building structure to adjacent walls and ceil- 10 Sound transmission ¦ Direct sound can be controlled only by selecting quiet equipment. Reflected sound is controlled by adding sound absorption to room and to equipment location. fittings ¦ ¦ 2 Air- and structureborne sound radiated from casings and through walls of ducts and plenums is transmitted through walls and ceiling into room ¦ Design duct and for low turbulence; locate high-velocity ducts in noncritical areas; isolate ducts and sound plenums from structure with neoprene or spring hangers. ¦ ¦ 3 Airborne sound radiated through supply and return air ducts to diffusers in room and then to listener by Path 1 ¦ Select fans for minimum sound power; use ducts lined with sound- absorbing material; use duct silencers or sound plenums in supply and return air ducts. ¦ ¦ 4 Noise transmitted through equipment room walls and floors to adjacent rooms ¦ Locate equipment rooms away from critical areas; use masonry blocks or for floors in ¦ ¦ ¦ concrete mechanical equipment room walls; use floating mechanical rooms. ¦ ¦ ings, from which it radiates as noise into room by Path 1 transmission and duct ¦ Mount all machines on properly designed vibration isolators; design mechanical equipment room for dynamic loads; balance rotating and reciprocating equipment. Isolate pipe and ducts from structure with neoprene or spring hangers; install flexible connectors between pipes, ducts, and vibrating ¦ ¦ 6 Vibration along pipes walls ¦ machines. ¦ ¦ 7 Noise radiated to outdoors enters room windows 8 Indoor noise follows Path 1 9 Noise transmitted to an air diffuser in a room, into a duct, and out through an air diffuser in another room through, over, and around room partition ¦ Locate equipment away from critical areas; use barriers and covers to interrupt noise paths; select quiet equipment. Select quiet equipment. Design and install duct attenuation to match transmission loss of wall between rooms; use crosstalk silencers in ductwork. Extend partition to ceiling slab and tightly seal all around; seal all pipe, conduit, duct, and other partition penetrations. ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Point of Fan Operation. The point of fan operation has a major effect on acoustical output. Fan selection at the calculated point of maximum efficiency is common practice to ensure mini- mum power consumption. In general, for a given design, fan sound is at a minimum near the point of maximum efficiency. Noise as ¦ ¦ ¦ 1370 increases the operating point shifts to the right, as shown in Fig- ¦ ¦ ¦ 1250 ure 8 (higher airflow and lower static pressure). Low-frequency P ¦ PLENUM FAN, mm DIAMETER 1750 105 1500 102 (M FAN CURVE, Ps 10-12 99 e」 8P ¦ noise can increase substantially at operating points to the left of maximum efficiency (lower airflow and higher static pressure). These operating points should be avoided. Blade-Pass Frequency. The blade-pass frequency is represented by the number of times per second a fans impeller passes a station- ary item: fbp = (rpm x number of impeller blades)/60. All fans gen- erate a tone at this frequency and its multiples (harmonics). Whether this tone is objectionable or barely noticeable depends on the type and design of the fan and the point of operation. Housed Centrifugal Fans. Forward-curved (FC) fans are com- monly used in a wide range of standard air-handler products. The blade-pass of FC fans is typically less prominent and is at a higher frequency than other fans. The most distinguishing acoustical con- cern ofFC fans is the prevalent occurrence oflow-frequency rumble from airflow turbulence generated at blade tips, which can be exac- erbated by nonideal discharge duct conditions (less than five diam- eters of straight duct). FC fans are commonly thought to have 16, 31.5, and 63 Hz (full octave band) rumble, particularly when oper- ating to the left of the maximum efficiency point. Backward-inclined (BI) fans and airfoil (AF) fans are generally louder at the blade-pass frequency than a given FC fan selected for the same duty, but are much more energy efficient at higher pressures and airflow. The blade-pass tone generally increases in prominence with increasing fan speed and is typically in a frequency range that is Chart Title: PLENUM FAN, 1370 mm DIAMETER X-Axis: AIRFLOW, L/s Y-Axis: SCHIND POWER LEVEL (dB) Chart Type: line 15000 17000 19000 21000 23000 25000 27000 29000 31000 item_01 1600dB 1500dB 1250dB 1000dB 900dB 1100dB 1200dB 1300dB 1200dB Fig. 8 Test Data for Plenum Fan, Comparing Operating Point (Static Pressure and Airflow), A-Weighted Sound Power Level difficult to attenuate. Below the blade-pass frequency, these fans generally have lower sound amplitude than FC fans and are often quieter at high frequencies. Care should be taken with all types of housed fans to allow ade- quate clearance around the inlets. Also, note that belt guards and inlet screens may decrease airflow and increase sound generation. Plenum Fans. A plenum fan has no housing around the fan im- peller and discharges directly into the chamber, pressurizing the ple- num, and forcing air through the attached ductwork. Air flows into Inc. ASHRAE, 2019 user. single for Licensed | {}
80cc1fd9-852c-4282-a5d5-dd163b0fc797 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.10 the fan impeller through an inlet bell located in the chamber wall. These fans can substantially lower discharge sound power levels if the fan plenum is appropriately sized and acoustically treated with sound-absorptive material. The plenum discharge should be located away from the fan 's air blast, because blowing directly into the duct can aggravate the blade-pass sound. Avoid obstructing the inlet or crowding the coils or filters. Propeller Fans. Sound from propeller fans generally has a low- frequency-dominated spectrum shape; the blade-pass frequency is typically prominent and occurs in the low-frequency bands because of the small number of blades. Propeller fan blade-pass frequency noise is very sensitive to inlet obstructions. For some propeller fan designs, the shape of the fan venturi (inlet) is also a very important parameter that affects sound levels. In some applications, noise of a propeller fan is described as sounding like a helicopter. Propeller fans are most commonly used on condensers and for power exhausts. Vaneaxial Fans. Generally thought to have the lowest ampli- tudes of low-frequency sound of any of the fan types, axial fans are often used in applications where the higher-frequency noise can be managed with attenuation devices. In the useful operating range, noise from axial fans is a strong function of the inlet airflow sym- metry and blade tip speed. Minimizing Fan Noise. To minimize the required air distribu- tion system sound attenuation, proper fan selection and installation are vital. The following factors should be considered: · Design the air distribution system for minimum airflow resis- tance. High system resistance requires fans to operate at a higher wattage, which generates higher sound power levels. · Carefully analyze system pressure losses. Higher-than-expected system resistance may result in higher sound power levels than originally estimated. · Examine the sound power levels of different fan types and de- signs. Select a fan (or fans) that generates the lowest sound power levels while meeting other fan selection requirements. · Many fans generate tones at the blade-pass frequency and its har- monics that may require additional acoustical treatment of the system. Amplitude of these tones can be affected by resonance in the duct system, fan design, and inlet flow distortions caused by poor inlet duct design, or by operation of an inlet volume control damper. When possible, use variable-speed volume control in- stead of volume control dampers. · Design duct connections at both fan inlet and outlet for uniform and straight airflow. Avoid unstable, turbulent, and swirling inlet airflow. Deviation from acceptable practice can severely degrade both aerodynamic and acoustic performance of any fan and inval- idate manufacturers' ratings or other performance predictions. Variable-Air- V olume (VAV) Systems General Design Considerations. As in other aspects of HVAC system design, ducts for VAV systems should be designed for the lowest practical static pressure loss, especially ductwork closest to the fan or air-handling unit (AHU). High airflow velocities and con- voluted duct routing with closely spaced fittings can cause turbulent airflow that results in excessive pressure drop and fan instabilities that can cause excessive noise, fan stall, or both. Many VA V noise complaints have been traced to control prob- lems. Although most problems are associated with improper instal- lation, many are caused by poor design. The designer should specify high-quality fans or air handlers within their optimum ranges, not at the edge of their operation ranges where low system tolerances can lead to inaccurate fan flow capacity control. Also, in-duct static pressure sensors should be placed in duct sections having the lowest possible air turbulence (i.e., at least three equivalent duct diameters from any elbow, takeoff, transition, offset, or damper). 2019 ASHRAE Handbook-HVAC Applications (SI) Balancing. VAV noise problems have also been traced to improper air balancing. For example, air balance contractors com- monly balance an air distribution system by setting all damper posi- tions without considering the possibility of reducing fan speed. The result is a duct system in which no damper is completely open and the fan delivers air at a higher static pressure than would otherwise be necessary. If the duct system is balanced with at least one balanc- ing damper wide open, fan speed and corresponding fan noise could be reduced. Lower sound levels occur ifmost balancing dampers are wide open or eliminated. The specified goal should be to balance the system at the lowest static pressure required to operate the box located at the farthest point in the system. Fan Selection. For constant-volume systems, fans should be selected to operate at maximum efficiency at design airflow. How- ever, VA V systems must be selected to operate with efficiency and stability throughout the operating range. For example, a fan selected for peak efficiency at full output may aerodynamically stall at an operating point of 50% of full output, resulting in significantly increased low-frequency noise and unstable airflow. A stalling fan can indicate operation in the surge region, an area of operational instability where airflow reverses direction at the fan blade because of insufficient air entering the fan wheel. Similarly, a fan selected to operate most efficiently at the 50% output point may be very ineffi- cient at full output, resulting in substantially increased fan noise at all frequencies. In general, a fan for a VA v system should be selected for peak efficiency at an operating point between 70 and 80% of the maximum required system capacity, which is where the fan will operate most of the time. This usually means selecting a fan that is one size smaller than that required for peak efficiency at 100% of maximum required system capacity (Figure 9). When the smaller fan operates at higher capacities, it produces up to 5 dB more noise. This occasional increase in sound level is usually more tolerable than stall-related sound problems that can occur with a larger fan operat- ing at less than 100% design capacity most of the time. Air Modulation Devices. The control method selected to vary the air capacity ofa VAV system is important. Variable-capacity con- trol methods can be divided into three general categories: (1) variable inlet vanes (sometimes called inlet guide vanes) or discharge damp- ers that yield a new fan system curve at each vane or damper setting, (2) variable-pitch fan blades (usually used on axial fans) that adjust the blade angle for optimum efficiency at varying capacity require- ments, and (3) variable-speed motor drives in which motor speed is varied by modulation of the power line frequency or by mechanical % PRESSURE, STATIC DESIGN X-Axis: Design from (0 to 175) Y-Axis: Distance in % Chart Type: bar Small-FAN SURGE REGION Large-FAN SURGE REGION System CURVE item_01 50% 75% 100% Fig. 9 Basis for Fan Selection in VAV Systems Inc. ASHRAE, 2019 user. single for Licensed | {}
2ea4f9b3-044a-46db-87d2-d3033e084f34 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.11 means such as gears or continuous belt adjustment. Inlet vane and discharge damper volume controls can add noise to a fan system at reduced capacities, whereas variable-speed motor drives and vari- able-pitch fan blade systems are quieter at reduced air output than at full air output. Variable-Inlet Vanes and Discharge Dampers. Variable-inlet vanes vary airflow capacity by changing inlet airflow to a fan wheel. This type of air modulation varies the total air volume and pressure at the fan, but fan speed remains constant. Although fan pressure and air volume reductions at the fan reduce duct system noise by reducing air velocities and pressures in the duct work, there is an associated increase in fan noise caused by airflow turbu- lence and flow distortions at the inlet vanes. Fan manufacturers' test data show that, on airfoil centrifugal fans, as vanes mounted inside the fan inlet (nested inlet vanes) close, the sound level at the blade-pass frequency of the fan increases by 2 to 8 dB, depend- ing on the percent of total air volume restricted. For externally mounted inlet vanes, the increase is on the order of 2 to 3 dB. The increase for forward-curved fan wheels with inlet vanes is about 1 to 2 dB less than that for airfoil fan wheels. In-line axial fans with inlet vanes generate increased noise levels of2 to 8 dB in the low- frequency octave bands for a 25 to 50% closed vane position. Discharge dampers, typically located immediately downstream of the supply air fan, reduce airflow and increase pressure drop across the fan while fan speed remains constant. Because of air tur- bulence and flow distortions created by the high pressure drop across discharge dampers, there is a high probability of duct rumble near the damper location. If the dampers are throttled to a very low flow, a stall condition can occur at the fan, resulting in an increase in low-frequency noise. Variable-Pitch Fans for Capacity Control. Variable-pitch fan blade controls vary the fan blade angle to reduce airflow. This type of system is predominantly used in axial fans. As air volume and pressure are reduced at the fan, there is a corresponding noise reduction. In the 125 to 4000 Hz octave bands, this reduction usu- ally varies between 2 to 5 dB for a 20% reduction in air volume, and between 8 to 12 dB for a 60% reduction in air volume. Variable-Speed-Motor-Controlled Fan. Three types of elec- tronic variable-speed control units are used with fans: (1) current source inverter, (2) voltage source inverter, and (3) pulse-width modulation (PWM). The current source inverter and third-genera- tion PWM control units are usually the quietest of the three con- trols. In all three types, matching motors to control units and the quality of the motor windings determine the motor's noise output. The motor typically emits a pure tone with an amplitude that depends on the smoothness of the waveform from the line current. The frequency of the motor tone depends on the motor type, wind- ings, and speed, but is typically at the drive's switching frequency. Some drives allow adjustment to a higher frequency that does not carry as well, but at a cost of lower drive efficiency. Both inverter control units and motors should be enclosed in areas, such as mechanical rooms or electrical rooms, where the noise effect on surrounding rooms is minimal. The primary acoustic advantage of variable-speed fans is reduction of fan speed, which translates into reduced noise; dB reduction is approximately equal to 50 x log (higher speed/lower speed). Because this speed reduction generally follows the fan system curve, a fan selected at optimum efficiency initially (lowest noise) does not lose efficiency as the speed is reduced. When using variable-speed controllers, · Select fan vibration isolators on the basis of the lowest practical speed of the fan. For example, the lowest rotational speed might be 600 rpm for a 1000 rpm fan in a commercial system. · Select a controller with a feature typically called critical fre- quency jump band. This feature allows a user to program the · controller to avoid certain fan or motor rpm settings that might excite vibration isolation system or building structure resonance frequencies, or correspond to speeds of other fans in the same system. Check the intersection of the fan 's curve at various speeds against the duct system curve. When selecting a fan controlled by a vari- able-speed motor controller, keep in mind that the system curve does not go to zero static pressure at no flow. The system curve is asymptotic at the static pressure control set point, typically 250 to 370 Pa. An improperly selected fan may be forced to operate in its stall range at slower fan speeds. Terminal Units. Fans and pressure-reducing valves in VA v units should have manufacturer-published sound data indicating sound power levels that (1) are discharged from the low-pressure end of the unit and (2) radiate from the exterior shell of the unit. These sound power levels vary as a function of valve position and fan point of operation. Sound data for VA v units should be obtained accord- ing to the procedures specified by the latest AHRI Standard 880. In critical situations, a mock-up test should be conducted of a produc- tion terminal box under project conditions and space finishes. The test is required because minor changes in box motor, fan, or valve components can affect the noise generated by such equipment. Ifthe VA v unit is located in noncritical areas (e.g., above a store- room or corridor), sound radiated from the shell of the unit may be of no concern. If, however, the unit is located above a critical space and separated from the space by a ceiling with little or no sound transmission loss at low frequencies, sound radiated from the shell into the space below may exceed the desired noise criterion. In this case, it may be necessary to relocate the unit to a noncritical area or to enclose it with a high-transmission-loss construction. Room sound levels can be estimated using attenuation factors detailed in AHRI Standard 885. In general, fan-powered VA v units should not be placed above or near any room with a required sound criterion rating of less than RC 40(N) (Schaffer 2005). For further informa- tion, see the section on Indoor Sound Criteria. Full shutoff of VAV units can produce excessive duct system pressure at low flow, sometimes causing a fan to go into stall, result- ing in accompanying roar, rumble, and surge. Systems providing more than 30% of their air to VAV devices should be provided with a means of static pressure control. Variable-frequency drives are preferred, but in the case of constant-volume air handlers, some means of bypass pressure control should be used to relieve system pressure as VA V devices close down (Schaffer 2005). Rooftop-Mounted Air Handlers Rooftop air handlers can have unique noise control requirements because these units are often integrated into a low-mass roof con- struction. Large roof openings are often required for supply and return air duct connections. These ducts run directly from noise- generating rooftop air handlers to the building interior. Generally, there is insufficient space or distance between roof-mounted equip- ment and the closest occupied spaces below the roof to apply stan- dard sound control treatments. Rooftop units should be located above spaces that are not acoustically sensitive and should be placed as far as possible from the nearest occupied space. This measure can reduce the amount of sound control treatment necessary to achieve an acoustically acceptable installation. The common sound transmission paths associated with rooftop air handlers (Figure 10) are · Flanking-path-borne sound from condenser fans, or compressors breaking in through low-mass roofs or through windows · Airborne through bottom of rooftop unit to spaces below · Structureborne from vibrating equipment in rooftop unit to build- ing structure · Ductborne through supply air duct from air handler Inc. ASHRAE, 2019 user. single for Licensed | {}
a9694bf1-a642-48bf-aa26-760a60975b01 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.12 ![image](/image/placeholder) EXHAUST SUPPLY CONDENSER FANS FAN FAN COMPRESSOR CURB ROOF c エ I エ RETURN AIRBORNE AIR NOISE RADIATED PATH FLANKING STRUCTURE- PATH BORNE SUPPLY AIR PATH NOISE PATH FINISHED CEILING Fig. 10 Sound Paths for Typical Rooftop Installations · Ductborne through return air duct to air handler · Duct breakout noise (see the section on Sound Radiation Through Duct Walls) Flanking-path noise can enter through low-mass roof structures, adjacent walls, and windows. Avoid placing rooftop units on light structure over sensitive spaces or close to higher sidewalls with win- dows or other lightly constructed building elements. If it is neces- sary to place the rooftop unit over sensitive spaces or lightly constructed walls, then lagging with additional layers of gypsum board or other similar material may be required in these areas. Using proper vibration isolation can minimize structureborne sound and vibration from vibrating equipment in a rooftop unit. Special curb mounting bases are available to support and provide vibration isolation for rooftop units. For roofs constructed with open web joists, thin long-span slabs, wooden construction, and any unusually light construction, evaluate all equipment with a mass of more than 130 kg to determine the additional deflection of the structure at mounting points caused by the equipment. Isolator deflection should be a minimum of 10 times the additional static deflection. If the required spring isolator deflection exceeds com- mercially available products, stiffen the supporting structure or change the equipment location. Airborne paths are associated with casing-radiated sound that passes through the air handler enclosure and roof structure to the spaces below. Airborne sound can result from air handler noise or from other equipment components in the rooftop unit. Rooftop units should not be placed on open curbs or over a large opening in the roof structure through which both supply and return air ducts pass. Roof penetrations should be limited to two openings sized to accommodate only the supply and return air ducts. These openings should be properly sealed after installation of the ducts. If a large single opening exists under the rooftop unit, it should be structur- ally, acoustically, and flexibly sealed with one or more layers of gypsum board or other similar material around the supply and return air ducts. Airborne sound transmission to spaces below a rooftop unit can be greatly reduced by placing the rooftop unit on a struc- tural support extending above the roof structure, and running supply and return air ducts horizontally along the roof for several duct diameters before the ducts turn to penetrate the roof. The roof deck/ ceiling system below the unit can be constructed to adequately attenuate sound radiated from the bottom of the unit. Ductborne transmission of sound through the supply air duct con- sists of two components: sound transmitted from the air handler through the supply air duct system to occupied areas, and sound transmitted via duct breakout through a section or sections of the supply air duct close to the air handler to occupied areas. Sound transmission below 250 Hz through duct breakout is often a major acoustical limitation for many rooftop installations. Excessive low- frequency noise associated with fan noise and air turbulence in the region of the discharge section ofthe fan (or air handler) and the first 2019 ASHRAE Handbook-HVAC Applications (SI) duct elbow results in duct rumble, which is difficult to attenuate. This problem is often worsened by the presence of a high-aspect-ratio duct at the discharge section of the fan (or air handler). Rectangular ducts with duct lagging are often ineffective in reducing duct break- out noise. Using either a single- or dual-wall round duct with a radi- used elbow coming off the discharge section of the fan can reduce duct breakout. If space does not allow for the use of a single duct, the duct can be split into several parallel round ducts. Another effective method is using an acoustic plenum chamber constructed of a minimum 50 mm thick, dual-wall plenum panel, lined with fiberglass and with a perforated inner liner, at the discharge section of the fan. Either round or rectangular ducts can be taken off the plenum as necessary for the rest of the supply air distribution sys- tem. Table 7 shows 12 possible rooftop discharge duct configura- tions with their associated low-frequency noise reduction potential (Beatty 1987; Harold 1986, 1991). Ductborne transmission of sound through the return air duct of a rooftop unit is often a problem because there is generally only one short return air duct section between the plenum space above a ceil- ing and the return air section of the air handler. This does not allow for adequate sound attenuation between the fan inlet and spaces below the air handler. Sound attenuation through the return air duct system can be improved by adding at least one (more if possible) branch division where the return air duct is split into two sections that extend several duct diameters before they terminate into the ple- num space above the ceiling. The inside surfaces of all return air ducts should be lined with a minimum of 25 mm thick duct liner. If conditions permit, duct silencers in duct branches or an acoustic plenum chamber at the air-handler inlet section give better sound conditions. Aerodynamically Generated Sound in Ducts Aerodynamic sound is generated when airflow turbulence occurs at duct elements such as duct fittings, dampers, air modulation units, sound attenuators, and room air devices. For details on air modula- tion units and sound attenuators, see the sections on Variable-Air- Volume (VA V) Systems and Duct Silencers. Although fans are a major source of sound in HVAC systems, aerodynamically generated sound can often exceed fan sound be- cause of close proximity to the receiver. When making octave-band fan sound calculations using a source-path-receiver analysis, aero- dynamically generated sound must be added in the path sound calculations at the location of the element. Duct Velocities. The extent of aerodynamic sound is related to the airflow turbulence and velocity through the duct element. The sound amplitude of aerodynamically generated sound in ducts is proportional to the fifth, sixth, and seventh power ofthe duct airflow velocity in the vicinity of a duct element (Bullock 1970; Ingard et al. 1968). Therefore, reducing duct airflow velocity significantly re- duces flow-generated noise. Tables 8 (Schaffer 2005) and 9 (Egan 1988) give guidelines for recommended airflow velocities in duct sections and duct outlets to avoid problems associated with aerody- namically generated sound in ducts. Fixed Duct Fittings. Fixed duct fittings include elbows, tees, transitions, fixed dampers, and branch takeoffs. In all cases, less generated air turbulence and lower airflow velocities result in less aerodynamic sound. Figures 1 1 and 12 show typical frequency spectra for specific sizes of elbows and transitions. Data in these fig- ures are based on empirical data obtained from ASHRAE RP-37 (Ingard et al. 1968). Normalized data from ASHRAE RP-37 and others, which can apply to all types of duct fittings and dampers, have been published (Bullock 1970) and presented in ASHRAE RP-265 (Ver 1983a). When multiple duct fittings are installed adja- cent to each other, aerodynamic sound can increase significantly because of the added air turbulence and increased velocity pres- sures. Note that the magnitude of the field-measured static pressure Inc. ASHRAE, 2019 user. single for Licensed | {}
2eb7cc5d-60af-48f0-ae09-1bac700b2e77 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.13 Table 7 Duct Breakout Insertion Loss-Potential Low-Frequency Improvement over Bare Duct and Elbow Duct Breakout Insertion Loss ¦ ¦ at Low Frequencies, dB ¦ at Low Frequencies, dB ¦ at Low Frequencies, dB ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Discharge Duct Configuration, 3660 mm of Horizontal Supply Duct ¦ 63 Hz ¦ 125 Hz ¦ 250 Hz ¦ Side View End View ¦ ¦ Rectangular duct: no turning vanes (reference) ¦ 0 ¦ 0 ¦ 0 ¦ 22 GAGE AIRFLOW ¦ ¦ Rectangular duct: one-dimensional turning vanes ¦ 0 ¦ 1 ¦ 1 ¦ TURNING VANES ¦ ¦ Rectangular duct: two-dimensional turning vanes ¦ 0 ¦ 1 ¦ 1 ¦ TURNING VANES ¦ ¦ Rectangular duct: wrapped with foam insulation and two layers oflead ¦ 4 ¦ 3 ¦ 5 ¦ SEE FOAM INSULATION END WITH TWO VIEW LAYERS LEAD ¦ ¦ Rectangular duct: wrapped with glass fiber and one layer 16 mm gypsum board ¦ 4 ¦ 7 ¦ 6 ¦ GLASS FIBER PRESSED SEE FLAT AGAINST DUCT END VIEW ¦ ¦ Rectangular duct: wrapped with glass fiber and two layers 16 mm gypsum board ¦ 7 ¦ 9 ¦ 9 ¦ SEE GYPSUM BOARD END SCREWED TIGHT VIEW ¦ ¦ Rectangular plenum drop (2.5 mm thick): three parallel rectangular supply ducts (0.7 mm thick) ¦ 1 ¦ 2 ¦ 4 ¦ 12 GAGE 22 GAGE ¦ ¦ Rectangular plenum drop (2.5 mm thick): one round supply duct (1.2 mm thick) ¦ 8 ¦ 10 ¦ 6 ¦ 18 GAGE 12 GAGE ¦ ¦ Rectangular plenum drop (2.5 mm thick): three parallel round supply ducts 11 14 8 (0.6 mm thick) ¦ Rectangular plenum drop (2.5 mm thick): three parallel round supply ducts 11 14 8 (0.6 mm thick) ¦ Rectangular plenum drop (2.5 mm thick): three parallel round supply ducts 11 14 8 (0.6 mm thick) ¦ Rectangular plenum drop (2.5 mm thick): three parallel round supply ducts 11 14 8 (0.6 mm thick) ¦ 12 GAGE 24 GAGE ○ ○ ○ ¦ ¦ Rectangular (2.0 mm thick) to multiple drop: round mitered elbows with turning vanes, three parallel round supply ducts (0.6 mm thick) ¦ 18 ¦ 12 ¦ 13 ¦ 14 GAGE 24 GAGE ¦ ¦ Rectangular (2.0 mm thick) to multiple drop: round mitered elbows with turn- 18 13 16 ing vanes, three parallel round lined double-wall, 560 mm OD supply ducts GAGE (0.6 mm thick) ¦ Rectangular (2.0 mm thick) to multiple drop: round mitered elbows with turn- 18 13 16 ing vanes, three parallel round lined double-wall, 560 mm OD supply ducts GAGE (0.6 mm thick) ¦ Rectangular (2.0 mm thick) to multiple drop: round mitered elbows with turn- 18 13 16 ing vanes, three parallel round lined double-wall, 560 mm OD supply ducts GAGE (0.6 mm thick) ¦ Rectangular (2.0 mm thick) to multiple drop: round mitered elbows with turn- 18 13 16 ing vanes, three parallel round lined double-wall, 560 mm OD supply ducts GAGE (0.6 mm thick) ¦ 14 GAGE 24 ¦ ¦ Round drop: radiused elbow (2.0 mm thick), single 940 mm diameter supply duct ¦ 15 ¦ 17 ¦ 10 ¦ 14 GAGE 18 GAGE ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ drop across fixed duct fittings does not relate to the aerodynamic generated sound. However, total pressure drop across a duct fitting, which includes the velocity pressure change resulting from air tur- bulence, does affect aerodynamically generated sound. Operable Volume Dampers. Operable damper aerodynamic sound is created because the damper is an obstacle in the airstream, and air turbulence increases as the damper closes. Because total pressure drop across the damper also increases with closure, the aerodynamic sound is related to the total pressure drop. Both single- blade and multiblade dampers, used to balance and control the airflow in a duct system and at room air devices, have similar frequency spectra. Figure 13 shows the frequency spectrum for a 45° damper in a 600 by 600 mm duct (Ingard et al. 1968). Depending on its location relative to a room air device, a damper can generate sound that is transmitted down the duct to the room air device, or radiate sound through the ceiling space into the occupied space below. When an operable control damper is installed close to an air device to achieve system balance, the acoustic performance of the air outlet must be based not only on the air volume handled, but also on the magnitude of the air turbulence generated at the damper. The sound level produced by closing the damper is accounted for by adding a correction to the air device sound rating. As the damper is modulated for air balance, this quantity is proportional to the pres- sure ratio (PR), that is, the throttled total pressure drop across the damper divided by the minimum total pressure drop across the damper. Table 10 provides decibel corrections to determine the effect of damper location on linear diffuser sound ratings. Volume dampers in sound-critical spaces should always be a minimum of 5 to 10 duct diameters from the air device, with an acoustically lined duct between the damper and air device. Acous- tically lined plenums may also be used between the damper and room air device to reduce damper sound. Linear air devices with a round duct connected to an insulated plenum have been successfully used for damper sound control. However, acoustical lining in this type of plenum does not minimize the sound generated by air flowing through a short section of the linear air device. If multiple inlets/outlets are used to spread airflow uniformly over the lined ple- num and air device, then the linear slot generates less sound. Inc. ASHRAE, 2019 user. single for Licensed | {}
139a181c-7233-4eca-9ae9-0e7e6889b7f1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.14 2019 ASHRAE Handbook-HVAC Applications (SI) Chart Type: line 1 2 3 4 5 6 7 8 item_01 70dB (fe 10^-12W) 70dB (fe 10^-12W) 60dB (fe 10^-12W) 50dB (fe 10^-12W) 40dB (fe 10^-12W) 30dB (fe 10^-12W) 20dB (fe 10^-12W) 15dB (fe 10^-12W) ![image](/image/placeholder) WALL OF REVERBERANT ROOM 600 mm 300 mm 600 mm 300 mm TOP TOP □ : 900 mm 600 mm 900 mm 600 mm SIDE SIDE ABRUPT TRANSITION GRADUAL TRANSITION AIRFLOW Fig. 11 Velocity-Generated Sound of Duct Transitions W) 10-12 (re dB LEVEL, POWER SOUND BAND OCTAVE Chart Type: line 125 250 500 1000 2000 4000 8000 item_01 85m/s 70m/s 60m/s 50m/s 40m/s 30m/s 25m/s OCTAVE BAND CENTER FREQUENCY, Hz Note: Comparison of octave band sound power levels produced by airflow through 200 X 200 mm rectangular elbow with and without 7 circular arc turning vanes. Fig. 12 Velocity-Generated Sound of Elbows Chart Type: line Duct velocity (Hz) (Hx) (S) item_01 14.5dB (rels) 8.75dB (rels) 5.5dB (rels) 3.5dB (rels) Fig. 13 Velocity-Generated Sound of 600 by 600 mm Volume Damper (Ingard et al. 1968) Table 8 Maximum Recommended Duct Airflow Velocities to Achieve Specified Acoustic Design Criteria ¦ ¦ ¦ Maximum Airflow Velocity, m/s ¦ Maximum Airflow Velocity, m/s ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Main Duct Location ¦ Design RC(N) ¦ Rectangular Duct ¦ Circular Duct ¦ ¦ In shaft or above drywall ceiling ¦ 45 ¦ 17.8 ¦ 25.4 ¦ ¦ ¦ 35 ¦ 12.7 ¦ 17.8 ¦ ¦ ¦ 25 ¦ 8.6 ¦ 12.7 ¦ ¦ Above suspended acoustic ceiling ¦ 45 ¦ 12.7 ¦ 22.9 ¦ ¦ ¦ 35 ¦ 8.9 ¦ 15.2 ¦ ¦ ¦ 25 ¦ 6.1 ¦ 10.2 ¦ ¦ Duct located within occupied space ¦ 45 ¦ 10.2 ¦ 19.8 ¦ ¦ ¦ 35 ¦ 7.4 ¦ 13.2 ¦ ¦ ¦ 25 ¦ 4.8 ¦ 8.6 ¦ Notes: 1. Branch ducts should have airflow velocities of about 80% of values listed. 2. Velocities in final runouts to outlets should be 50% of values or less. 3. Elbows and other fittings can increase airflow noise substantially, depending on type. Thus, duct airflow velocities should be reduced accordingly. Proper air balancing of a fan/duct system directly affects aero- dynamically generated sound even in a correctly designed and installed duct system. Primary volume dampers in the longest duct from a fan should always be nearly wide open. If the primary damper in the longest duct run is more than 20% closed, the duct system has not been properly air balanced, and the fan may operate at a higher speed than required for the duct system. The result is an increase in air velocities and turbulence throughout the entire duct system, with excessive aerodynamic sound generated at all duct ele- ments. Room Air Devices (Grilles, Registers, Diffusers). Manufac- turers' test data should be obtained in accordance with ASHRAE Standard 70 for room air devices such as grilles, registers, diffusers, air-handling light fixtures, and air-handling suspension bars. De- vices should be selected to meet the noise criterion required or spec- ified for the room. However, the manufacturer's sound power rating Inc. ASHRAE, 2019 user. single for Licensed | {}
3d68c1ea-69fa-4f36-92d7-b86c8180aa74 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.15 Table 9 Maximum Recommended Air Velocities at Neck of Supply Diffusers or Return Registers to Achieve Specified Acoustical Design Criteria ¦ Type of Opening ¦ Design RC(N) ¦ "Free" Opening Airflow Velocity, m/s ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Supply air outlet ¦ 45 ¦ 3.2 ¦ ¦ ¦ 40 ¦ 2.8 ¦ ¦ ¦ 35 ¦ 2.5 ¦ ¦ ¦ 30 ¦ 2.2 ¦ ¦ ¦ 25 ¦ 1.8 ¦ ¦ Return air opening ¦ 45 ¦ 3.8 ¦ ¦ ¦ 40 ¦ 3.4 ¦ ¦ ¦ 35 ¦ 3.0 ¦ ¦ ¦ 30 ¦ 2.5 ¦ ¦ ¦ 25 ¦ 2.2 ¦ Note: Table intended for use when no sound data are available for selected grilles or diffusers, or no diffuser or grille is used. The number of diffusers or grilles increases sound levels, depending on proximity to receiver. Allowable outlet or opening airflow velocities should be reduced accordingly in these cases. Table 10 Decibels to Be Added to Diffuser Sound Rating to Allow for Throttling of Volume Damper ¦ ¦ Damper Pressure Ratio ¦ Damper Pressure Ratio ¦ Damper Pressure Ratio ¦ Damper Pressure Ratio ¦ Damper Pressure Ratio ¦ Damper Pressure Ratio ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1.5 ¦ 2 ¦ 2.5 ¦ 3 ¦ 4 ¦ 6 ¦ ¦ ¦ Location of v olume Damper ¦ dB to Be Added to Diffuser Sound Rating ¦ dB to Be Added to Diffuser Sound Rating ¦ dB to Be Added to Diffuser Sound Rating ¦ dB to Be Added to Diffuser Sound Rating ¦ dB to Be Added to Diffuser Sound Rating ¦ dB to Be Added to Diffuser Sound Rating ¦ ¦ In neck of linear diffuser ¦ 5 ¦ 9 ¦ 12 ¦ 15 ¦ 18 ¦ 24 ¦ ¦ In inlet of plenum of linear diffusers ¦ 2 ¦ 3 ¦ 4 ¦ 5 ¦ 6 ¦ 9 ¦ ¦ In supply duct at least 1.5 m from inlet plenum of linear diffuser ¦ 0 ¦ 0 ¦ 0 ¦ 2 ¦ 3 ¦ 5 ¦ is obtained with a uniform velocity distribution throughout the air device neck or grille collar; this is often not met in practice when a duct turn, sharp transition, or balancing damper immediately pre- cedes the entrance to the diffuser. In these cases, airflow is turbulent and noise generated by the device can be substantially higher than the manufacturer's published data (by as much as 12 dB). In some cases, placing an equalizer grid in the neck of the air device can greatly reduce this turbulence by helping to provide a uniform velocity gradient in the neck of the device, so the sound power generated in the field is closer to that listed in the manufacturer's catalog. At present, air devices are rated by manufacturers in terms of noise criterion (NC) levels, which usually includes a receiver room effect sound correction of 10 dB. The NC ratings may be useful for comparison between different air devices, but are not helpful for source-path-receiver calculations in terms of octave bands. For a complete analysis, the designer should request the component sound power level data in octave bands from the manufacturer. Whether using NC levels or sound power levels, the designer should also correct manufacturer's data for actual room effect, location of air devices, and number of air devices used in a specific design. The acoustical room effect is the reduction in sound level caused by dis- tance from the sound source (e.g., air outlet); the room volume and amount of acoustical absorption present also affect the value. For example, in a small room with an actual calculated room effect of 6 dB, and given a manufacturer's room effect correction of 10 dB, the discrepancy (in this case, 4 dB) must be added to the manufac- turer's data. When an air device is located at the intersection of the ceiling and vertical wall, 6 dB should be added, and in the corner of a room, 9 dB should be added to manufacturer's data. When multi- ple room air devices are located in a small room or grouped together in a large room, the sound of air devices is additive by up to 10 x log(number of air devices). For more information, see the sec- tion on Receiver Room Sound Correction. ![image](/image/placeholder) BASIS OF SOUND LEVELS SAME AS SOUND LEVELS UP TO MANUFACTURER'S MANUFACTURER'S RATING 12 dB HIGHER WITH RATING WITH EQUALIZING GRID NO EQUALIZING GRID (A) D 8 D 2 D SOUND LEVELS SAME AS SOUND LEVELS 12 TO 15 dB HIGHER MANUFACTURER'S RATINGS THAN MANUFACTURER'S RATINGS (B) Fig. 14 (A) Proper and Improper Airflow Condition to an Outlet; (B) Effect of Proper and Improper Alignment of Flexible Duct Connector A flexible duct connection between a branch air duct and an air device provides a convenient means to align the air device with the ceiling grid. The resulting misalignment in this connection, as shown in Figure 14, can cause as much as 12 to 15 dB higher sound levels in the air device's aerodynamically generated sound. Avoiding Aerodynamically Generated Noise. Aerodynamic noise in duct systems can be avoided by · Sizing ductwork and duct elements for low air velocities · Avoiding abrupt changes in duct cross-sectional area or direction · Providing smooth airflow at all duct elements, including branches, elbows, tees, transitions, and room air devices · Providing straight ductwork (preferably 5 to 10 duct diameters) between duct elements · Air-balancing duct system for lowest reasonable fan speed with dampers generally open · Locating volume control dampers a minimum of 3 (preferably 5 to 10) duct diameters away from room air devices (Schaffer 2005) Water and Air-Cooled Chillers and Air-Cooled Condensers Chillers and air-cooled condensers have components such as compressors, motors, gears, and fans that can produce significant amounts of both broadband and tonal noise. The broadband noise is typically caused by flows of refrigerant, water, and air, whereas the tonal noise is caused by rotation of compressors, motors, gears, and fans (in fan-cooled equipment). Chiller and condenser noise is sig- nificant in the octave bands from 63 to 4000 Hz and depends pri- marily on the type of compressor used. Noise from Compressors and Chillers. All compressors pro- duce tonal noise to varying degrees. Acoustical differences among compressors relate in large part to their tonal content: · Centrifugal compressor tonal noise comes from rotation of the impeller, refrigerant flow, and gears (if present). Impeller blade- related tonal content is typically not very strong; sound radiates mainly from the compressor and condenser shell. Centrifugal chiller noise can increase at low capacity (10 to 25%) because changing the inlet guide vane to lower the pressure also increases turbulence. The noise gets worse as flow approaches rotating stall. If capacity is reduced using motor speed control, the Inc. ASHRAE, 2019 user. single for Licensed | {}
577d679f-dbe7-47ea-90fe-99085d67464e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.16 2019 ASHRAE Handbook-HVAC Applications (SI) resulting compressor sound levels generally decrease with de- creasing capacity. · Reciprocating compressor noise has a low-frequency drumming quality, caused by the oscillatory motion of pistons. The tonal content is high, and the sound level decreases very little with decreasing capacity. · Scroll compressors tend to produce relatively weak tones. · Screw compressors (sometimes called helical rotor or rotary compressors) generate very strong tones in the 250 to 2000 Hz octave bands. Rotor-induced tones can be amplified by reso- nances in the oil separation component or refrigerant lines, and by sound radiation from the condenser shells. Screw compressors have been a source of chiller noise complaints in many installa- tions where their tonal characteristics have not been properly accounted for in the building design process. · Absorption chillers produce relatively little noise themselves, but the flow of steam in associated pumps and valves causes signi- ficant high-frequency noise. Noise levels may increase with decreasing capacity as valves close, and combustion air blowers on direct gas-fired units can be noisy. The noise levels of indoor chillers are used primarily for deter- mining compliance with occupational noise exposure in the work- place (in accordance with U.S. Occupational Safety and Health Administration [OSHA] regulations), and secondarily for determin- ing equipment room transmission loss requirements to ensure that the desired sound levels in adjacent or remote spaces are achieved. The noise levels of outdoor chillers and condensing units are pri- marily used to determine compliance with local noise ordinances at property lines and to predict sound levels inside adjacent or nearby buildings and residences. Indoor Water-Cooled Chillers. The dominant noise sources in water-cooled chillers are the compressor (most often centrifugal or screw) and condenser. As physical sizes of chillers increase, their radiated sound power levels also increase. Factory-provided sound data for indoor chillers are typically obtained following AHRI Standard 575, which requires measuring the A-weighted and octave band sound pressure level (Lp) values at many locations 1 m from the chiller and 1.5 m above the floor. AHRI Standard 575 sound pressure levels are generally available at operating points of 25, 50, and 100% of a chiller's nominal full capacity. The average A-weighted sound pressure levels can be used directly along with exposure times to determine OSHA com- pliance (OSHA 2011) in the machinery room. An example of the ranges of AHRI Standard 575 values for atypical centrifugal and screw chiller are shown in Figures 15 and 16, respectively. The sound levels depend on manufacturer design, type and size of com- pressor, and operating conditions. AHRI Standard 575 measurements for factory-provided ratings are often made in very large rooms with an anechoic or minimally reverberant environment rather than that typically found in mechan- ical equipment rooms. For that reason, assessment of sound pressure levels in situ should typically be adjusted for each chiller installation to account for the mechanical room s size and surface treatment. For a given chiller at a given operating point, a small equipment room (or one with mostly hard surface finishes) has higher Lp values than one that is large or has sound-absorbing treatments on its ceiling and walls. Figure 17 shows maximum typical adjustment factors that should be added to factory-provided AHRI Standard 575 values to estimate the Lp values in specific installations caused by reverber- ant (reflective) sound effects. The adjustment for each octave band requires knowing the size of an imaginary box that is circumscribed 1 m away from the top and sides of the chiller (the AHRI Standard 575 measurement surface), the dimensions of the equipment room, and the average sound absorption coefficient of the room sur- faces. The adjustment in each octave band depends on the ratio ofthe areas of the equipment room and the imaginary box as well as the average sound absorption of the room finishes. Each curve in Figure 17 is for a different value of the average sound absorption, with the higher curves being for lower values. DB LEVEL, PRESSURE SOUND Chart Type: line 63 Hz 125 Hz 250 Hz 500 Hz 1000 Hz 2000 Hz 4000 Hz 8000 Hz item_01 85% 80% 75% 70% 85% 90% 75% 65% Fig. 15 Typical Minimum and Maximum AHRI Standard 575 Lp Values for Centrifugal Chillers (450 to 4500 kW) 8P LEVEL, PRESSURE SOUND X-Axis: OCTAVE BAND CENTER FREQUEN, Hz Chart Type: line 63 Hz 125 Hz 250 Hz 500 Hz 1000 Hz 2000 Hz 4000 Hz 8000 Hz item_01 80% 75% 60% 90% 90% 85% 70% 60% Fig. 16 Typical Minimum and Maximum AHRI Standard 575 Lp Values for Screw Chillers (450 to 1400 kW) Inc. ASHRAE, 2019 user. single for Licensed | {}
384bed40-1f75-46d5-9d0e-b413bf6f85f9 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.17 X-Axis: Ratio of ARI Measurement and Room Surface Areas Y-Axis: Reverberant Sound Build-JP (dB) Chart Type: line Black Red Blue Green Light Blue Yellow Orange Purple Light Green item_01 13dB 11dB 10dB 9dB 8dB 7dB 6dB 5dB 4dB Fig. 17 Estimated Sound Level Build-Up in Mechanical Room for AHRI Standard 575 Chiller Sound Levels Example 2. Estimate the reverberant Lp values in a 13.7 by 12.2 by 6.1 m tall mechanical equipment room (MER) that houses a 1260 kW centrif- ugal chiller. The room has a concrete floor and gypsum board walls and ceiling; all surfaces have an average absorption coefficient of 0.1. The chiller dimensions are 1500 mm wide, 2000 mm tall, and 3000 mm long. Solution: The AHRI Standard 575 measurement surface area SM is determined by adding 1 m to the chiller height and 2 m to both its length and width. The floor area is not included in this calculation. The result is a box 3500 mm wide, 5000 mm long, and 3000 mm tall. The surface area of this box is approximately 68.5 m2. The surface area of the equipment room (floor included) SR is 650 m2. Therefore, the ratio of the areas SR/SM is 650/68.5 = 9.5. Because the average absorption coefficient value for room is 0.1 for all octave bands, see Figure 17 for the adjust- ment factor and Table 1 1 for calculations. The approximate reverberant Lp values in the last line of Exam- ple 2 can be used with sound transmission loss data of the construc- tion to estimate transmitted Lp values in rooms adjacent to a chiller room. An alternative approach to this method for estimating Lp in adja- cent rooms is to use an estimate of the sound power levels of the chiller from the factory-provided AHRI Standard 575 values (Sta- bley 2006) in conjunction with sound transmission loss data. A con- version factor (CF) is determined and used to convert the AHRI Standard 575 sound pressure values to sound power Lw values. The conversion factor is calculated using CF = 10 log(S/So) where S = area of measurement parallelepiped (excluding the top) used in AHRI Standard 575 2(L x H) + 2(W x H) Table 11 Calculations for Reverberation Build-Up ¦ ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ 8000 ¦ ¦ AHRI Standard 575 Lp values ¦ 73 ¦ 74 ¦ 73 ¦ 72 ¦ 74 ¦ 72 ¦ 69 ¦ 63 ¦ ¦ Adjustment from Figure 17 ¦ 7 ¦ 7 ¦ 7 ¦ 7 ¦ 7 ¦ 7 ¦ 7 ¦ 7 ¦ ¦ Approximate revised Lp in MER ¦ 80 ¦ 81 ¦ 80 ¦ 79 ¦ 81 ¦ 79 ¦ 76 ¦ 70 ¦ L, W, and H = length, width, and height of measurement parallelepiped, m S⌀ = 1 m2 and Lw = Lp + CF (3) where L sound power level (A-weighted or octave band) L = sound pressure levels per AHRI Standard 575 p This approach assumes that the factory-provided data were ob- tained in a free-field environment. Indoor chillers are often offered with various types of factory noise-reduction options. These options can include variable-speed drives, or variable-geometry diffusers on centrifugal compressors, to reduce the strength of the noise sources inside the machine. They may also include various external noise-attenuation devices ranging from compressor, refrigerant line, and heat exchanger blankets (typ- ically providing overall noise reduction of2 to 6 dBA), to complete enclosures with sound-absorbing inner surfaces (which may reduce the overall noise by as much as 18 dBA). The amount of compressor noise reduction achieved by external attenuation approaches is usu- ally limited by structureborne transmission of compressor vibration into the equipment frame and heat exchanger shells, which act as sounding boards. Attenuation options for chiller noise control vary widely, depending on the application and the type of compressor used. Typically, they either reduce the sound radiating from the source (using acoustic enclosures or blankets) or reduce the internal sound-generating mechanisms of the source (using variable-speed drives on compressors and variable-geometry diffusers for centrif- ugal compressors). The effectiveness of each approach is affected by variables such as the type of compressor and its behavior with load, heat exchanger design, and type of prime mover used. Field-installed noise-control options include full-sized sheet metal housings with specially treated openings for piping, electrical conduit, and ventilation. This option may require upgraded building construction. For more information, refer to the section on Mechan- ical Equipment Room Sound Isolation. Outdoor Air-Cooled Chillers and Condensers. Outdoor units often use either reciprocating, scroll, or screw compressors. They are also used as the chiller portion of rooftop packaged units. The dominant noise sources in outdoor air-cooled chillers are the com- pressors and the condenser fans, which are typically low-cost, high- speed propeller fans. For air-cooled condensing units, propeller fans are the only significant noise source. (2) Factory sound data for outdoor equipment are obtained in accor- dance with AHRI Standard 370, which requires determination of the equipment's octave band sound power levels (Lw), A-weighted overall sound power level (Lwa), and tone-adjusted A-weighted overall sound power level (Lwat). Because AHRI Standard 370 is a sound power measurement technique, it provides certifiable sound data that can be compared across chiller manufacturers with greater certainty than is possible using the sound-pressure-based AHRI Standard 575. An example of the range of AHRI Standard 370 Lw values for outdoor chillers in the 70 to 1300 kW range is given in Figure 18. Inc. ASHRAE, 2019 user. single for Licensed | {}
0fb324dc-12d7-43bb-ab5a-dac97ff6c455 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.18 Chart Type: line 63 Hz 125 Hz 250 Hz 500 Hz 1000 Hz 2000 Hz 4000 Hz 8000 Hz item_01 110dB (re 10^-12 W) 105dB (re 10^-12 W) 110dB (re 10^-12 W) 105dB (re 10^-12 W) 100dB (re 10^-12 W) 95dB (re 10^-12 W) 90dB (re 10^-12 W) 75dB (re 10^-12 W) Fig. 18 Typical AHRI 370 Lw Values for Outdoor Chillers (70 to 1300 kW) Emergency Generators Factory-supplied noise reduction options for outdoor equipment include compressor enclosures, component sound blankets, over- sized condenser fans, and variable-speed condenser fans. Because air-cooled equipment needs a free flow of cooling air, full enclo- sures are not feasible. However, strategically placed barriers can help reduce noise propagation on a selective basis. For more infor- mation, see the section on Sound Control for Outdoor Equipment. Emergency or standby generators create very high sound lev- els and require special consideration, especially if used inside an occupied building. The primary noise sources include the engine casing, radiator, and engine exhaust, and must be considered sepa- rately if the generator is installed indoors. Sound power levels for these units depend on the power rating, fuel type, engine speed, exhaust muffler design, and radiator system. Overall sound power levels can be as high as 130 dBA (re 10-12 W) for larger (1.5 to 2.0 MW) diesel-powered units with standard mufflers. Noise levels inside generator rooms almost always exceed 100 dBA if the power rating of the unit is greater than 50 kW. Noise from the generator casing is broadband with a relatively uniform spectrum. Octave band noise data are usually available from the generator manufacturer. Casing noise does not vary much with load. Conversely, exhaust noise typically contains strong tones at the engine shaft's running frequency and at the engine firing rate. Standard engine exhaust mufflers reduce exhaust noise by 20 to 25 dBA (compared to unsilenced exhaust), but even with this noise reduction, strong tones still radiate from the exhaust outlet in most cases. High-performance (critical- and supercritical-grade) mufflers are available but are larger and more expensive than standard units. Exhaust pipes should be routed away from noise-sensitive areas, and the exhaust outlet should be located and oriented to ensure that community noise levels are not excessive. In occupied buildings, the entire exhaust pipe should be suspended from the structure above with spring hangers. 2019 ASHRAE Handbook-HVAC Applications (SI) Engine casing noise is best controlled by enclosing the generator in a sound-rated enclosure. The biggest problem with generator room design is finding adequate space for ventilation air. Generators require a substantial volume of air for engine cooling, and con- trolling engine noise transmission using air intake and exhaust paths can be difficult. In most cases, air intake and exhaust openings require sound attenuators. Because engine radiators usually use pro- peller fans to move air across the radiator core, the ventilation sys- tem cannot always handle the added pressure drop created by sound attenuators. In some cases, auxiliary fans are needed to draw fresh air into the generator room through the intake silencers. Sound attenuators at the discharge opening should be located between the radiator and exhaust louver. A smooth, slowly expanding transition duct is required between the radiator and the discharge louver. Non- symmetrical transitions and transitions with expansion angles greater than 15° usually result in nonuniform airflow through the sound attenuators, causing a higher-than-expected pressure drop and reduced airflow. Unless careful space planning is done early in the design phase, there is often not enough space in the generator room to fit the sound attenuators with a proper transition fitting. Emergency generator radiator fans usually make as much or more noise than the engine casing. In noise-sensitive installations, consider using a remote radiator. Most manufacturers offer remote radiators as an option, available in a wide variety of designs and noise levels. Lower sound levels with remote radiators are usually achieved by using larger fans running at lower speeds. Using a remote radiator can often save substantial expense in noise-sensitive applications because airflow requirements in the generator room are dramatically reduced. 2.4 PATH NOISE ESTIMATION AND CONTROL Duct Element Sound Attenuation A major transmission path of noise from mechanical equipment is through air distribution ductwork. Duct elements and concepts COV- ered in this section include plenums, unlined rectangular ducts, acoustically lined rectangular ducts, unlined round ducts, acousti- cally lined round ducts, elbows, acoustically lined round radiused elbows, duct silencers, duct branch power division, duct end reflec- tion loss, and terminal volume regulation units. Simplified tabular procedures for obtaining the sound attenuation associated with these elements are presented. Plenums. Plenums are often placed between a fan and main air distribution ducts to smooth turbulent airflow. They are typically lined with acoustically absorbent material to reduce fan and other mechanical noise. Plenums are usually large rectangular enclosures with an inlet and one or more outlets. Based on experience, ASHRAE-sponsored research (Mouratidis and Becker 2004), and earlier work (Wells 1958), transmission loss associated with a plenum can be expressed using the following con- siderations: At frequencies above the cutoff frequency, as defined by the ple- num , s inlet duct dimensions, the wavelength of sound is small com- pared to the characteristic dimensions of the plenum. Plane wave propagation in a duct exists at frequencies below the cutoff, creating a need to consider two frequency ranges, where · Frequency range (based on the cutoff frequency described in the following paragraphs), which is defined as the upper limit for plane wave sound propagation · In-line inlet and outlet openings · End-in/end-out versus end-in/side-out orientation (i.e., in-line versus elbow configuration) c 등 fc = or fc = 0.586 2a (4) Inc. ASHRAE, 2019 user. single for Licensed | {}
33dceb04-c8e9-4b49-8f16-7226bc51dc9f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.19 where fc = cutoff frequency, Hz c = speed of sound in air, m/s a = larger cross-sectional dimension of rectangular duct, m d = diameter of round duct, m The cutoff frequency fc is the frequency above which plane waves no longer propagate in a duct. At these higher frequencies, waves that propagate in the duct create cross or spinning modes. The transmission loss (TL) in this higher frequency range may be predicted using the following relationship: S out2 Sout( 1 - �a) " TL = b + + OAE 2 S�a 4�r where (5) TL = transmission loss, dB b = 3.505 n = -0.359 Sout = area of plenum outlet, m2 S = total inside surface area of plenum minus inlet and outlet areas, m2 r = distance between centers of inlet and outlet of plenum, m 0 = directivity factor; taken as 2 for opening near center of wall, or 4 for opening near corner of plenum �a average absorption coefficient of plenum lining (see Equation [8]) OAE = offset angle effect; additional attenuation found in Tables 14 and 15, which tabulate frequency-dependent sound transmission properties that are manifested when inlet and outlet of plenum are not in a direct line; 90° angle is referred to as elbow effect The average absorption coefficient �a of plenum lining is given by S1�1 +S2�2 ⌀a = S1 + S2 where ⑥ �1 = sound absorption coefficient of any bare or unlined inside surfaces of plenum S1 = surface area of any bare or unlined inside surfaces of plenum, m2 �2 = sound absorption coefficient of acoustically lined inside surfaces of plenum S2 = surface area of acoustically lined inside surfaces of plenum, m2 In many situations, inner surfaces of a plenum chamber are lined with a sound-absorbing material. For these situations, �a = �2. Table 12 gives sound absorption coefficients for selected common plenum materials. Note: transmission loss (TL) of a plenum is the difference be- tween the duct sound power level at the outlet and inlet of the ple- num, unlike insertion loss (IL) ratings for silencers, which represent the difference (at a downstream measurement location) between the duct sound pressure levels with the silencer and with no silencer (replaced with an empty duct). For purposes here, both TL and IL are interpreted as attenuation, or the net reduction in propa- gating duct sound power. For frequencies that correspond to plane wave propagation in the duct (below the cutoff frequency), the following relationship applies, with a lower frequency limit of 50 Hz: TL = 10.76AfS + We + OAE where (7) Af = surface area coefficient, dB/m2 (see Table 13 for small and large plenum size ranges) We = wall effect, dB (see Table 13 for common HV AC plenum wall types) OAE = offset angle effect Table 12 Sound Absorption Coefficients a of Selected Plenum Materials Octave Midband Frequency, Hz ¦ ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Non-sound-absorbing material ¦ Non-sound-absorbing material ¦ Non-sound-absorbing material ¦ Non-sound-absorbing material ¦ Non-sound-absorbing material ¦ Non-sound-absorbing material ¦ Non-sound-absorbing material ¦ Non-sound-absorbing material ¦ ¦ Concrete ¦ 0.01 ¦ 0.01 ¦ 0.01 ¦ 0.02 ¦ 0.02 ¦ 0.02 ¦ 0.03 ¦ ¦ Bare sheet metal ¦ 0.04 ¦ 0.04 ¦ 0.04 ¦ 0.05 ¦ 0.05 ¦ 0.05 ¦ 0.07 ¦ ¦ Sound-absorbing material (fiberglass insulation board) ¦ Sound-absorbing material (fiberglass insulation board) ¦ Sound-absorbing material (fiberglass insulation board) ¦ Sound-absorbing material (fiberglass insulation board) ¦ Sound-absorbing material (fiberglass insulation board) ¦ Sound-absorbing material (fiberglass insulation board) ¦ Sound-absorbing material (fiberglass insulation board) ¦ Sound-absorbing material (fiberglass insulation board) ¦ ¦ 25 mm, 48 kg/m3 ¦ 0.05 ¦ 0.11 ¦ 0.28 ¦ 0.68 ¦ 0.90 ¦ 0.93 ¦ 0.96 ¦ ¦ 50 mm, 48 kg/m3 ¦ 0.10 ¦ 0.17 ¦ 0.86 ¦ 1.00 ¦ 1.00 ¦ 1.00 ¦ 1.00 ¦ ¦ 75 mm, 48 kg/m3 ¦ 0.30 ¦ 0.53 ¦ 1.00 ¦ 1.00 ¦ 1.00 ¦ 1.00 ¦ 1.00 ¦ ¦ 100 mm, 48 kg/m3 ¦ 0.50 ¦ 0.84 ¦ 1.00 ¦ 1.00 ¦ 1.00 ¦ 1.00 ¦ 0.97 ¦ Note: 63 Hz values estimated from higher-frequency values. ![image](/image/placeholder) INLET W h OUTLET Fig. 19 Schematic of End-In/End-Out Plenum The maximum TL predicted by Equation (7) should be limited to 20 dB. For an end-in/end-out plenum configuration, where the openings are not in-line, the offset angle 0 must be considered in the TL cal- culation. The value of0 is obtained from the following relationship: I I cos 0 2 2 h (8) where (refer to Figure 19) 0 = offset angle representing r to long axis I of duct I = length of plenum, m rv = vertical offset between axes of plenum inlet and outlet, m rh = horizontal offset between axes of plenum inlet and outlet, m For a given offset angle, apply the applicable effects on TL (deci- bel addition or subtraction) for angles up to 45° (Table 14). For an end-in/side-out plenum configuration, where openings are perpendicular to each other, the elbow effect must be considered in the TL calculation. For any plenum configuration involving an elbow condition, apply the applicable effects on TL (decibel addition or subtraction) for the two frequency ranges, both above and below the cutoff (Table 15). For plenum applications within a practical size envelope of0.5 to 30 m3 volume or 5 to 60 m2 surface area, using duct sizes in the range 300 < d < 1200 mm, this model may be applied with an antic- ipated standard deviation of ±3.5 to 5.0 dB for 50 Hz <f≤fc and ±1.5 to 3.0 for fc <f≤ 5000 Hz. Use caution when applying these prediction methods for plenum configurations where either the width or height dimension is <1.5d. In this case, the plenum may not perform as an expansion chamber, thus changing its broadband TL characteristics significantly. Inc. ASHRAE, 2019 user. single for Licensed | {}
ba1eadeb-22ee-4547-91e1-90de32225d9e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.20 2019 ASHRAE Handbook-HVAC Applications (SI) Table 13 Low-Frequency Characteristics of Plenum TL ¦ Frequency ¦ Area Coefficient Af, dB/m2 ¦ Area Coefficient Af, dB/m2 ¦ Wall Effect W⌀ dB Added ¦ Wall Effect W⌀ dB Added ¦ Wall Effect W⌀ dB Added ¦ Wall Effect W⌀ dB Added ¦ Wall Effect W⌀ dB Added ¦ Wall Effect W⌀ dB Added ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Frequency ¦ For Plenum Volume ¦ For Plenum Volume ¦ 25 mm, 40 kg/m3 (Fabric Facing)(Fabric ¦ 50 mm, 40 kg/m3 Facing) ¦ 100 mm, 40 kg/m3 (Perf. Facing) ¦ 200 mm, 40 kg/m3 (Perf. Facing) ¦ 100 mm (Tuned, No Media) ¦ 100 mm, 40 kg/m3 (Double Solid Metal) ¦ ¦ Frequency ¦ <1.5 m3 ¦ >1.5 m3 ¦ 25 mm, 40 kg/m3 (Fabric Facing)(Fabric ¦ 50 mm, 40 kg/m3 Facing) ¦ 100 mm, 40 kg/m3 (Perf. Facing) ¦ 200 mm, 40 kg/m3 (Perf. Facing) ¦ 100 mm (Tuned, No Media) ¦ 100 mm, 40 kg/m3 (Double Solid Metal) ¦ ¦ 50 ¦ 1.4 ¦ 0.3 ¦ 1 ¦ 1 ¦ 0 ¦ 1 ¦ 0 ¦ 0 ¦ ¦ 63 ¦ 1.0 ¦ 0.3 ¦ 1 ¦ 2 ¦ 3 ¦ 7 ¦ 1 ¦ 3 ¦ ¦ 80 ¦ 1.1 ¦ 0.3 ¦ 2 ¦ 2 ¦ 3 ¦ 9 ¦ 2 ¦ 7 ¦ ¦ 100 ¦ 2.3 ¦ 0.3 ¦ 2 ¦ 2 ¦ 4 ¦ 12 ¦ 1 ¦ 6 ¦ ¦ 125 ¦ 2.4 ¦ 0.4 ¦ 2 ¦ 3 ¦ 6 ¦ 12 ¦ 1 ¦ 4 ¦ ¦ 160 ¦ 2.0 ¦ 0.4 ¦ 3 ¦ 4 ¦ 11 ¦ 11 ¦ 0 ¦ 2 ¦ ¦ 200 ¦ 1.0 ¦ 0.3 ¦ 4 ¦ 10 ¦ 16 ¦ 15 ¦ 4 ¦ 3 ¦ ¦ 250 ¦ 2.2 ¦ 0.4 ¦ 5 ¦ 9 ¦ 13 ¦ 12 ¦ 1 ¦ 1 ¦ ¦ 315 ¦ 0.7 ¦ 0.3 ¦ 6 ¦ 12 ¦ 14 ¦ 14 ¦ 5 ¦ 2 ¦ ¦ 400 ¦ 0.7 ¦ 0.2 ¦ 8 ¦ 13 ¦ 13 ¦ 14 ¦ 7 ¦ 1 ¦ ¦ 500 ¦ 1.1 ¦ 0.2 ¦ 9 ¦ 13 ¦ 12 ¦ 13 ¦ 8 ¦ 0 ¦ Source: Mouratidis and Becker (2004). Table 14 Offset Angle Effects on TL for End-Outlet Plenum ¦ Offset Angle Effects on TL for fs fc ¦ Offset Angle Effects on TL for fs fc ¦ Offset Angle Effects on TL for fs fc ¦ Offset Angle Effects on TL for fs fc ¦ Offset Angle Effects on TL for fs fc ¦ Offset Angle Effects on TL for fs fc ¦ Offset Angle Effects on TL for fs fc ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ Offset Angle 0 ¦ Offset Angle 0 ¦ Offset Angle 0 ¦ Offset Angle 0 ¦ Offset Angle 0 ¦ Offset Angle 0 ¦ ¦ Frequency, Hz ¦ 0 ¦ 15.0 ¦ 22.5 ¦ 30.0 ¦ 37.5 ¦ 45.0 ¦ ¦ 50 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ ¦ 63 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ ¦ 80 ¦ 0 ¦ 0 ¦ -1 ¦ -3 ¦ 4 ¦ -6 ¦ ¦ 100 ¦ 0 ¦ 1 ¦ 0 ¦ -2 ¦ -3 ¦ -6 ¦ ¦ 125 ¦ 0 ¦ 1 ¦ 0 ¦ -2 ¦ 4 ¦ -6 ¦ ¦ 160 ¦ 0 ¦ 0 ¦ -1 ¦ -2 ¦ -3 ¦ 4 ¦ ¦ 200 ¦ 0 ¦ 0 ¦ -1 ¦ -2 ¦ -3 ¦ -5 ¦ ¦ 250 ¦ 0 ¦ 1 ¦ 2 ¦ 3 ¦ 5 ¦ 7 ¦ ¦ 315 ¦ 0 ¦ 4 ¦ 6 ¦ 8 ¦ 10 ¦ 14 ¦ ¦ 400 ¦ 0 ¦ 2 ¦ 4 ¦ 6 ¦ 9 ¦ 13 ¦ ¦ 500 ¦ 0 ¦ 1 ¦ 3 ¦ 6 ¦ 10 ¦ 15 ¦ ¦ ≥630 ¦ N/A ¦ N/A ¦ N/A ¦ N/A ¦ N/A ¦ N/A ¦ ¦ Offset Angle Effects on TL for f >fc ¦ Offset Angle Effects on TL for f >fc ¦ Offset Angle Effects on TL for f >fc ¦ Offset Angle Effects on TL for f >fc ¦ Offset Angle Effects on TL for f >fc ¦ Offset Angle Effects on TL for f >fc ¦ Offset Angle Effects on TL for f >fc ¦ ¦ ¦ Offset Angle 0 ¦ Offset Angle 0 ¦ Offset Angle 0 ¦ Offset Angle 0 ¦ Offset Angle 0 ¦ Offset Angle 0 ¦ ¦ Frequency, Hz ¦ 0 ¦ 15.0 ¦ 22.5 ¦ 30.0 ¦ 37.5 ¦ 45.0 ¦ ¦ ≤160 ¦ N/A ¦ N/A ¦ N/A ¦ N/A ¦ N/A ¦ N/A ¦ ¦ 200 ¦ 0 ¦ 1 ¦ 4 ¦ 9 ¦ 14 ¦ 20 ¦ ¦ 250 ¦ 0 ¦ 2 ¦ 4 ¦ 8 ¦ 13 ¦ 19 ¦ ¦ 315 ¦ 0 ¦ 1 ¦ 2 ¦ 3 ¦ 4 ¦ 5 ¦ ¦ 400 ¦ 0 ¦ 1 ¦ 2 ¦ 3 ¦ 4 ¦ 6 ¦ ¦ 500 ¦ 0 ¦ 0 ¦ 1 ¦ 2 ¦ 4 ¦ 5 ¦ ¦ 630 ¦ 0 ¦ 1 ¦ 2 ¦ 3 ¦ 5 ¦ 7 ¦ ¦ 800 ¦ 0 ¦ 1 ¦ 2 ¦ 2 ¦ 3 ¦ 3 ¦ ¦ 1000 ¦ 0 ¦ 1 ¦ 2 ¦ 4 ¦ 6 ¦ 9 ¦ ¦ 1250 ¦ 0 ¦ 0 ¦ 2 ¦ 4 ¦ 6 ¦ 9 ¦ ¦ 1600 ¦ 0 ¦ 0 ¦ 1 ¦ 1 ¦ 2 ¦ 3 ¦ ¦ 2000 ¦ 0 ¦ 1 ¦ 2 ¦ 4 ¦ 7 ¦ 10 ¦ ¦ 2500 ¦ 0 ¦ 1 ¦ 2 ¦ 3 ¦ 5 ¦ 8 ¦ ¦ 3150 ¦ 0 ¦ 0 ¦ 2 ¦ 4 ¦ 6 ¦ 9 ¦ ¦ 4000 ¦ 0 ¦ 0 ¦ 2 ¦ 5 ¦ 8 ¦ 12 ¦ ¦ 5000 ¦ 0 ¦ 0 ¦ 3 ¦ 6 ¦ 10 ¦ 15 ¦ N/A = not applicable Example 3. A small plenum with acoustically lined surfaces is 1.8 m high, 1.2 m wide, and 1.8 m long. The inlet and outlet are each 0.9 m wide by 0.6 m high. The horizontal offset between centers of the plenum inlet and outlet is 0.3 m. The vertical offset is 1.2 m. The inside of the ple- num is completely lined with 25 mm thick fiberglass insulation board, with sound absorption values as shown in Table 8. Determine the trans- mission loss TL associated with this plenum. Solution: The areas of the inlet section, outlet section, and overall surfaces are Table 15 Elbow Effect, dB ¦ ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Frequency, Hz ¦ >fc ¦ ¦ ¦ 50 ¦ 0 ¦ 2 ¦ ¦ 63 ¦ 0 ¦ 3 ¦ ¦ 80 ¦ 0 ¦ 6 ¦ ¦ 100 ¦ 0 ¦ 5 ¦ ¦ 125 ¦ 0 ¦ 3 ¦ ¦ 160 ¦ 0 ¦ 0 ¦ ¦ 200 ¦ 3 ¦ -2 ¦ ¦ 250 ¦ 6 ¦ -3 ¦ ¦ 315 ¦ 3 ¦ -1 ¦ ¦ 400 ¦ 3 ¦ 0 ¦ ¦ 500 ¦ 2 ¦ 0 ¦ ¦ 630 ¦ 3 ¦ 0 ¦ ¦ 800 ¦ 3 ¦ 0 ¦ ¦ 1000 ¦ 2 ¦ 0 ¦ ¦ 1250 ¦ 2 ¦ 0 ¦ ¦ 1600 ¦ 2 ¦ 0 ¦ ¦ 2000 ¦ 2 ¦ 0 ¦ ¦ 2500 ¦ 2 ¦ 0 ¦ ¦ 3150 ¦ 2 ¦ 0 ¦ ¦ 4000 ¦ 2 ¦ 0 ¦ ¦ 5000 ¦ 1 ¦ 0 ¦ ¦ N/A = not applicable Sin = 0.9 x 0.6 = 0.54 m2 Sout = 0.9 x 0.6 = 0.54 m2 S = Total surface area (all walls with lining) = 2(1.2 x 1.8) + 2(1.2 x 1.8) + 2(1.8 x 1.8) - 0.54 - 0.54 = 14.04 m2 with I = 1.8 m, rv= 1.2 m, and rh = 0.3 m, r = (1.82+ 1.22+0.32)1/2 = 2,184 m 0 = cos-1(1.8/2.184) = 35° The cutoff frequency fc is fc = 343/(2 x 0.9) = 190 Hz where 343 m/s is the approximate speed of sound in standard air. Frequency Range #1 (1/3-octave TL in 50 Hzsfsfc range) TL = 10.76xAfxS+We + OAE (9) ¦ N/A = not applicable Sin = 0.9 x 0.6 = 0.54 m2 Sout = 0.9 x 0.6 = 0.54 m2 S = Total surface area (all walls with lining) = 2(1.2 x 1.8) + 2(1.2 x 1.8) + 2(1.8 x 1.8) - 0.54 - 0.54 = 14.04 m2 with I = 1.8 m, rv= 1.2 m, and rh = 0.3 m, r = (1.82+ 1.22+0.32)1/2 = 2,184 m 0 = cos-1(1.8/2.184) = 35° The cutoff frequency fc is fc = 343/(2 x 0.9) = 190 Hz where 343 m/s is the approximate speed of sound in standard air. Frequency Range #1 (1/3-octave TL in 50 Hzsfsfc range) TL = 10.76xAfxS+We + OAE (9) ¦ N/A = not applicable Sin = 0.9 x 0.6 = 0.54 m2 Sout = 0.9 x 0.6 = 0.54 m2 S = Total surface area (all walls with lining) = 2(1.2 x 1.8) + 2(1.2 x 1.8) + 2(1.8 x 1.8) - 0.54 - 0.54 = 14.04 m2 with I = 1.8 m, rv= 1.2 m, and rh = 0.3 m, r = (1.82+ 1.22+0.32)1/2 = 2,184 m 0 = cos-1(1.8/2.184) = 35° The cutoff frequency fc is fc = 343/(2 x 0.9) = 190 Hz where 343 m/s is the approximate speed of sound in standard air. Frequency Range #1 (1/3-octave TL in 50 Hzsfsfc range) TL = 10.76xAfxS+We + OAE (9) ¦ (Consult Table 13 for Af and We and Table 14 for offset angle effect.) Inc. ASHRAE, 2019 user. single for Licensed | {}
7e51e8e0-8577-4c19-9f9d-07314f55fa8e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.21 Frequency Range #2 (1/3-octave TL infe <f≤ 5000 Hz range) " SoutQ Sout(1 - �a) TL = b + + OAE 2 S�a 4元r where OAE = see Table 14 ¦ b = 3.505 ¦ ¦ --- ¦ ¦ n =-0.359 ¦ ¦ 0 = 4 (directivity factor for inlet opening close to adjacent wall or bihedral corner of plenum) ¦ ¦ �a = 1/3-octave average absorption values for 25 mm fiberglass lin- ing (see Table 12) ¦ Note: for angles between tabulated values in Table 14, use linear inter- polation. The results are tabulated as follows: ¦ OAE = offset angle effect ¦ ¦ ¦ --- ¦ --- ¦ ¦ *Column 1 x S + column 2 + column 3 bIncludes OAE value from column 3 per calculation from Equation (10). ¦ °From column 4 or 5, depending on appropri- ate frequency range. ¦ ¦ ¦ ¦ (1) ¦ (2) ¦ (3) ¦ (4) ¦ (5) ¦ ⑥ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1/3- Octave TL in ¦ Freq., Hz ¦ , dB/m2 ¦ Wer dB ¦ OAE, dB ¦ TL for Frequency Range 1,a dB ¦ TL for Frequency Range 2,b dB ¦ Net TL,c dB ¦ ¦ 50 sfs ¦ 50 ¦ 0.3 ¦ 1 ¦ 0 ¦ 6 ¦ ¦ 6 ¦ ¦ 189 Hz ¦ 63 ¦ 0.3 ¦ 1 ¦ 0 ¦ 6 ¦ ¦ 6 ¦ ¦ ¦ 80 ¦ 0.3 ¦ 2 ¦ -4 ¦ 3 ¦ ¦ 3 ¦ ¦ ¦ 100 ¦ 0.3 ¦ 2 ¦ -3 ¦ 4 ¦ ¦ 4 ¦ ¦ ¦ 125 ¦ 0.4 ¦ 2 ¦ - 4 ¦ 4 ¦ ¦ 4 ¦ ¦ ¦ 160 ¦ 0.4 ¦ 3 ¦ -3 ¦ 6 ¦ ¦ 6 ¦ ¦ fc ¦ 200 ¦ ¦ ¦ 12 ¦ ¦ 20 ¦ 20 ¦ ¦ 5000 Hz ¦ 250 ¦ ¦ ¦ 11 ¦ ¦ 19 ¦ 19 ¦ ¦ ¦ 315 ¦ ¦ ¦ 4 ¦ ¦ 13 ¦ 13 ¦ ¦ ¦ 400 ¦ ¦ ¦ 4 ¦ ¦ 14 ¦ 14 ¦ ¦ ¦ 500 ¦ ¦ ¦ 3 ¦ ¦ 13 ¦ 13 ¦ ¦ ¦ 630 ¦ ¦ ¦ 4 ¦ ¦ 14 ¦ 14 ¦ ¦ ¦ 800 ¦ ¦ ¦ 3 ¦ ¦ 14 ¦ 14 ¦ ¦ ¦ 1000 ¦ ¦ ¦ 5 ¦ ¦ 16 ¦ 16 ¦ ¦ ¦ 1300 ¦ ¦ ¦ 5 ¦ ¦ 16 ¦ 16 ¦ ¦ ¦ 1600 ¦ ¦ ¦ 2 ¦ ¦ 13 ¦ 13 ¦ ¦ ¦ 2000 ¦ ¦ ¦ 6 ¦ ¦ 17 ¦ 17 ¦ ¦ ¦ 2500 ¦ ¦ ¦ 4 ¦ ¦ 15 ¦ 15 ¦ ¦ ¦ 3200 ¦ ¦ ¦ 5 ¦ ¦ 16 ¦ 16 ¦ ¦ ¦ 4000 ¦ ¦ ¦ 7 ¦ ¦ 18 ¦ 18 ¦ ¦ ¦ 5000 ¦ ¦ ¦ 8 ¦ ¦ 19 ¦ 19 ¦ Unlined Rectangular Sheet Metal Ducts. Straight, unlined rectangular sheet metal ducts provide a fairly significant amount of low-frequency sound attenuation. Table 16 shows the results of selected unlined rectangular sheet metal ducts (Cummings 1983; Reynolds and Bledsoe 1989a; Ver 1978; W oods Fan Division 1973). Attenuation values in Table 16 apply only to rectangular sheet metal ducts with the lightest gages allowed by Sheet Metal and Air Conditioning Contractors' National Association, Inc. (SMACNA) HVAC duct construction standards. Attenuation for lengths greater than 3 m is not well documented. Sound energy attenuated at low frequencies in rectangular ducts may manifest itself as breakout noise along the duct. Low-frequency breakout noise should therefore be checked. For additional informa- tion on breakout noise, see the section on Sound Radiation Through Duct Walls. Acoustically Lined Rectangular Sheet Metal Ducts. Internal duct lining for rectangular sheet metal ducts can be used to provide both thermal insulation and sound attenuation. The thickness of (10) Table 16 Sound Attenuation in Unlined Rectangular Sheet Metal Ducts ¦ Duct Size, mm ¦ PIA, 1/mm ¦ Attenuation, dB/m Octave Midband Frequency, Hz ¦ Attenuation, dB/m Octave Midband Frequency, Hz ¦ Attenuation, dB/m Octave Midband Frequency, Hz ¦ Attenuation, dB/m Octave Midband Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Duct Size, mm ¦ PIA, 1/mm ¦ 63 ¦ 125 ¦ 250 ¦ >250 ¦ ¦ 150 x 150 ¦ 0.026 ¦ 0.98 ¦ 0.66 ¦ 0.33 ¦ 0.33 ¦ ¦ 305 x 305 ¦ 0.013 ¦ 1.15 ¦ 0.66 ¦ 0.33 ¦ 0.20 ¦ ¦ 305 x 610 ¦ 0.010 ¦ 1.31 ¦ 0.66 ¦ 0.33 ¦ 0.16 ¦ ¦ 610 x 610 ¦ 0.007 ¦ 0.82 ¦ 0.66 ¦ 0.33 ¦ 0.10 ¦ ¦ 1220 x 1220 ¦ 0.003 ¦ 0.49 ¦ 0.33 ¦ 0.23 ¦ 0.07 ¦ ¦ 1830 x 1830 ¦ 0.002 ¦ 0.33 ¦ 0.33 ¦ 0.16 ¦ 0.07 ¦ duct linings for thermal insulation usually varies from 15 to 50 mm; the density of the internal lining usually varies between 24 and 48 kg/m3, but may be as low as 12 kg/m3. For duct lining to attenu- ate sound effectively, it should have a minimum thickness of25 mm. At low frequencies, thicker lining performs slightly better than thin- ner lining. Tables 17 and 18 give attenuation values of selected rect- angular sheet metal ducts for 25 and 50 mm thick glass fiber duct lining, respectively (Herrin et al. 2017; Kuntz 1986; Kuntz and Hoover 1987; Machen and Haines 1983; Reynolds and Albright 2018; Reynolds and Bledsoe 1989a). Note that attenuation values for ducts with a cross-sectional area less than 0.09 m2 or greater than 1.49 m2 in these tables are taken from previous editions of the ASHRAE Handbook and based on laboratory tests using 3 m lengths of lined duct. Insertion loss values for all other duct sizes in these tables were obtained in ASHRAE research project RP-1408 (Reyn- olds and Albright 2018). This research project included lengths of uninterrupted straight ducts from 0.9 to 12 m with varying sizes and lengths of round and rectangular ducts with fiberglass duct liner. The liner used in this testing was 24 kg/m3 for the rectangular ducts. Though previous editions of this table indicated values of dB/m, research projects have shown that attenuation does not vary exactly linearly with length. Therefore, these updated tables show attenua- tion for lengths as actually tested. For interpolation to various duct lengths and cross sections, using the duct liner attenuation spread- sheet (available as an extra feature for the ASHRAE Handbook Online version of this chapter) is recommended. Note that the total attenuated noise will never be below the flow-generated noise level in the duct, and, because of typical flows and flanking noise in prac- tice, attenuation values are capped at 50 dB. Insertion loss values in Tables 1 7 and 18 represent the difference in the space-average sound pressure level measured in a reverbera- tion room with sound propagating through a straight section of unlined rectangular duct minus the corresponding sound pressure level measured when the unlined section of rectangular duct is replaced with a similar section of acoustically lined rectangular duct. The net result is the attenuation resulting from adding duct liner to a sheet metal duct. Insertion loss values discussed in this section apply only to straight rectangular sheet metal ducts made with the lightest gages allowed by the SMACNA HVAC duct construction standards. Inser- tion loss values for heavier gage ductwork are expected to be slightly less than the tabulated values. Insertion loss values in octave and 1/3-octave bands are available in the online version ofthe Handbook. Also available in the online version is a calculator which provides octave band and 1/3-octave band insertion loss values for any duct cross section larger than 305 x 305 mm and smaller than 1220 x 1220 mm in lengths ranging from 0.9 to 12 m. Insertion loss and attenuation values discussed in this section apply only to rectangular sheet metal ducts made with the lightest gages allowed by SMACNA HVAC duct construction standards. Attenuation for lengths greater than 3 m is not well documented. Unlined Round Sheet Metal Ducts. As with unlined rectangular ducts, unlined round ducts provide some natural sound attenuation Inc. ASHRAE, 2019 user. single for Licensed | {}
a0c7956f-f952-4994-8eb4-b4f08ff016d0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.22 2019 ASHRAE Handbook-HVAC Applications (SI) Table 17 Insertion Loss for Rectangular Sheet Metal Ducts with 25 mm Thick Fiberglass Lining Table 18 Insertion Loss for Rectangular Sheet Metal Ducts with 50 mm Thick Fiberglass Lining ¦ ID Dimensions, Length, mm ¦ ID Dimensions, Length, mm ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ ID Dimensions, Length, ¦ Frequency, Insertion Loss, dB Octave Midband Hz ¦ Frequency, Insertion Loss, dB Octave Midband Hz ¦ Frequency, Insertion Loss, dB Octave Midband Hz ¦ Frequency, Insertion Loss, dB Octave Midband Hz ¦ Frequency, Insertion Loss, dB Octave Midband Hz ¦ Frequency, Insertion Loss, dB Octave Midband Hz ¦ Frequency, Insertion Loss, dB Octave Midband Hz ¦ Frequency, Insertion Loss, dB Octave Midband Hz ¦ Frequency, Insertion Loss, dB Octave Midband Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ID Dimensions, Length, mm ¦ ID Dimensions, Length, mm ¦ m ¦ 63 125 ¦ 250 ¦ 500 ¦ 1000 7 ¦ 2000 ¦ 4000 ¦ 8000 ¦ ID Dimensions, Length, ¦ mm m ¦ 63 0 0 ¦ 125 4 10 ¦ 250 38 6 ¦ 500 ¦ 1000 ¦ 2000 8 12 19 ¦ 4000 ¦ 8000 ¦ ¦ 150 x 150 ¦ 3 ¦ ¦ 6 0 4 0 0 ¦ 15 ¦ 27 ¦ 50 ¦ 50 28 ¦ ¦ 43 ¦ 150 x 150 12 31 ¦ 3 19 21 2 3 ¦ 0 ¦ 8 ¦ 29 ¦ 49 ¦ 50 50 50 50 41 ¦ 50 28 7 24 16 ¦ 43 610 x ¦ ¦ ¦ ¦ 3 6 20 ¦ ¦ 5 50 50 30 ¦ 12 ¦ 24 0 ¦ 50 16 27 ¦ 50 40 16 10 13 20 ¦ 35 14 10 ¦ 37 7 ¦ ¦ 3 12 35 50 32 7 13 ¦ 0 ¦ 7 10 ¦ 24 ¦ 44 ¦ 50 29 50 27 ¦ 50 ¦ 37 36 8 ¦ ¦ ¦ ¦ 3 3 ¦ ¦ 5 12 18 ¦ 12 19 ¦ 23 5 ¦ 50 10 ¦ 50 ¦ 9 ¦ 36 ¦ ¦ 3 2 ¦ ¦ 6 28 ¦ 23 ¦ 42 14 13 ¦ 50 50 32 8 ¦ ¦ 36 ¦ ¦ ¦ ¦ 3 ¦ ¦ 5 1 0 ¦ 10 ¦ 22 ¦ 47 ¦ 50 15 22 12 ¦ 33 ¦ ¦ ¦ 3 ¦ 27 7 ¦ 6 0 2 0 1 4 ¦ 21 5 33 ¦ 40 33 ¦ 50 ¦ 50 ¦ 33 ¦ ¦ ¦ 200 x 200 ¦ 3 4 ¦ ¦ 5 2 22 2 4 ¦ 12 ¦ 23 ¦ 50 ¦ 50 0 ¦ 36 ¦ ¦ 200 x 200 19 7 10 ¦ 3 ¦ ¦ 6 0 6 ¦ 23 ¦ 42 16 50 ¦ 50 ¦ 50 11 ¦ 36 ¦ ¦ ¦ ¦ 3 ¦ ¦ 4 1 ¦ 10 ¦ 21 ¦ 45 ¦ 49 50 0 610 2 ¦ 32 ¦ ¦ ¦ 3 ¦ ¦ 6 ¦ 19 42 ¦ 39 21 ¦ 50 49 ¦ 9 ¦ 32 ¦ ¦ ¦ ¦ 3 41 10 ¦ 13 ¦ 4 0 ¦ 9 ¦ 20 ¦ 43 ¦ 45 ¦ 30 10 ¦ ¦ ¦ 3 ¦ ¦ 5 ¦ 18 ¦ 37 ¦ 50 23 11 ¦ 45 12 ¦ 30 15 ¦ ¦ ¦ ¦ 3 ¦ ¦ 4 ¦ 8 ¦ 19 ¦ 40 x 460 ¦ 41 ¦ 28 ¦ ¦ ¦ 3 ¦ ¦ 5 ¦ 16 ¦ 35 43 3 6 ¦ 50 6 ¦ 41 ¦ 28 ¦ ¦ ¦ 250 x 250 ¦ 3 3 ¦ 22 ¦ 4 4 2 ¦ 10 19 ¦ 21 ¦ 44 ¦ 47 ¦ 31 ¦ ¦ 250 x 250 ¦ 3 ¦ ¦ 6 ¦ 19 ¦ 38 0 ¦ 50 3 ¦ 47 12 2 45 ¦ 31 ¦ ¦ ¦ ¦ ¦ ¦ ¦ 8 ¦ 19 ¦ 40 11 15 ¦ 40 ¦ 27 10 2 ¦ ¦ ¦ 3 ¦ ¦ 5 8 ¦ 16 14 ¦ 34 34 910 910 2 3 ¦ 50 ¦ 40 50 ¦ 27 40 ¦ ¦ ¦ ¦ 3 3 14 ¦ ¦ 3 28 44 ¦ 8 12 ¦ 18 6 6 ¦ 38 22 ¦ 37 17 25 ¦ ¦ 26 ¦ ¦ 3 x ¦ ¦ 4 2 ¦ 15 7 13 ¦ 33 ¦ 48 ¦ 37 ¦ 26 610 2 ¦ ¦ ¦ ¦ 3 ¦ ¦ 3 ¦ 7 20 31 ¦ 17 7 11 ¦ 36 ¦ 33 ¦ ¦ 24 ¦ 18 30 10 15 19 ¦ 3 6 12 460 ¦ ¦ 4 ¦ 13 ¦ 31 ¦ 45 ¦ 33 ¦ 24 3 ¦ ¦ ¦ 300 x 300 460 X 460 610 x 12 ¦ 2 ¦ 0 0 ¦ 1 4 ¦ 4 2 4 24 ¦ 13 8 ¦ 31 39 50 ¦ 28 50 ¦ ¦ 20 15 25 ¦ 300 x 300 16 26 ¦ 2 12 ¦ 0 ¦ 3 3 5 ¦ 11 ¦ 24 9 50 35 ¦ 41 50 31 50 26 34 9 ¦ 23 ¦ 20 ¦ 16 ¦ ¦ ¦ 3 ¦ ¦ 2 0 0 3 12 ¦ 7 14 2 4 5 ¦ 19 16 26 46 9 23 15 44 4 ¦ 40 ¦ 43 0 2 7 ¦ 0 ¦ 18 ¦ ¦ 3 ¦ 0 0 0 ¦ 4 2 ¦ 18 50 17 17 23 ¦ 40 ¦ 48 16 ¦ 35 49 ¦ 24 8 ¦ 19 ¦ ¦ ¦ 6 ¦ ¦ 3 ¦ 13 7 ¦ 32 9 6 ¦ 50 35 19 ¦ 50 ¦ 33 0 0 ¦ 23 ¦ ¦ 6 ¦ 0 ¦ 5 ¦ 31 ¦ 50 20 ¦ 50 11 ¦ 50 3 ¦ 31 ¦ 23 ¦ ¦ ¦ 12 ¦ 0 ¦ 4 7 ¦ 25 ¦ 50 25 6 ¦ 50 50 50 48 ¦ 50 ¦ 46 35 9 12 10 2 ¦ 33 21 ¦ ¦ 12 ¦ 0 ¦ 5 ¦ 50 ¦ 50 ¦ 50 21 0 0 12 ¦ 50 6 ¦ 40 21 ¦ 32 13 ¦ ¦ ¦ 2 6 ¦ 0 0 ¦ 1 ¦ 3 6 ¦ 12 12 ¦ 28 6 50 ¦ 23 0 ¦ 16 0 0 ¦ 13 ¦ ¦ 2 ¦ 0 0 ¦ 3 ¦ 9 ¦ 22 0 x ¦ 41 ¦ 19 ¦ 16 ¦ 13 3 12 ¦ ¦ ¦ 3 ¦ 0 0 0 0 0 ¦ 2 3 ¦ 11 ¦ 18 ¦ 42 50 ¦ 34 8 ¦ 20 12 2 ¦ 16 ¦ ¦ 3 ¦ 0 ¦ 4 ¦ 16 38 ¦ 910 910 2 0 ¦ 50 28 2 0 ¦ 46 ¦ 20 30 ¦ 17 ¦ ¦ ¦ 6 5 3 6 ¦ 0 0 ¦ 3 1 1 1 2 ¦ 22 ¦ 30 49 ¦ ¦ 50 50 ¦ 29 ¦ 22 44 9 10 ¦ ¦ 6 ¦ 0 1 ¦ 4 9 14 15 34 5 9 ¦ 28 19 7 4 8 12 ¦ 50 50 50 18 17 ¦ 50 6 3 0 ¦ 33 6 5 8 ¦ 25 45 ¦ ¦ ¦ ¦ 12 2 9 ¦ 0 0 9 ¦ 4 1 17 1 6 2 ¦ 3 ¦ 9 ¦ 50 24 13 21 28 49 ¦ 18 ¦ 12 ¦ 35 10 12 ¦ ¦ 12 3 6 0 ¦ 0 ¦ 5 19 ¦ 48 30 ¦ 50 1 1 ¦ 50 ¦ 50 12 19 ¦ 39 ¦ ¦ ¦ ¦ 3 8 ¦ 0 ¦ 11 ¦ ¦ 10 12 ¦ 39 23 40 50 15 25 ¦ 25 23 13 34 35 24 ¦ 15 ¦ 13 24 42 ¦ ¦ 2 38 ¦ 0 2 ¦ 3 ¦ 7 20 31 50 ¦ 48 ¦ 31 15 14 ¦ 12 4 43 ¦ 10 ¦ ¦ ¦ ¦ 13 ¦ 0 0 0 50 ¦ 1 2 15 ¦ 5 22 ¦ 16 14 19 ¦ 41 3 50 50 ¦ 38 ¦ 16 24 39 50 50 16 2 ¦ 20 32 ¦ 12 2 ¦ 3 6 0 ¦ 0 4 0 6 8 ¦ 14 25 45 ¦ 35 50 50 ¦ 50 50 50 46 50 32 9 ¦ 22 35 50 20 0 ¦ 16 25 43 0 6 9 23 ¦ 15 23 40 39 ¦ ¦ ¦ ¦ 6 12 2 ¦ 0 0 0 ¦ 4 1 2 24 4 ¦ 9 18 3 9 17 37 11 ¦ 28 47 10 22 46 31 39 ¦ 50 50 50 23 6 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Inc. ASHRAE, Ⓒ 2019 user. single for Licensed | {}
82d5fade-36c0-46d9-adb2-4f1c48ef0558 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.23 Table 19 Sound Attenuation in Unlined Straight Round Ducts Attenuation, dB/m ¦ ¦ Octave Band Center Frequency, Hz ¦ Octave Band Center Frequency, Hz ¦ Octave Band Center Frequency, Hz ¦ Octave Band Center Frequency, Hz ¦ Octave Band Center Frequency, Hz ¦ Octave Band Center Frequency, Hz ¦ Octave Band Center Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Diameter, mm ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ ¦ D ≤ 180 ¦ 0.10 ¦ 0.10 ¦ 0.16 ¦ 0.16 ¦ 0.33 ¦ 0.33 ¦ 0.33 ¦ ¦ 180 < D ≤ 380 ¦ 0.10 ¦ 0.10 ¦ 0.10 ¦ 0.16 ¦ 0.23 ¦ 0.23 ¦ 0.23 ¦ ¦ 380 < D ≤ 760 ¦ 0.07 ¦ 0.07 ¦ 0.07 ¦ 0.10 ¦ 0.16 ¦ 0.16 ¦ 0.16 ¦ ¦ 760 < D ≤ 1520 ¦ 0.03 ¦ 0.03 ¦ 0.03 ¦ 0.07 ¦ 0.07 ¦ 0.07 ¦ 0.07 ¦ ![image](/image/placeholder) W W SQUARE ELBOW RADIUSED ELBOW Fig. 20 Rectangular Duct Elbows that should be taken into account when designing a duct system. Compared to rectangular ducts, round ducts are much more rigid and thus breakout, especially atlow frequencies, is significantly less than that from other shapes. Though this reduces attenuation values for low-frequency sound propagating down the duct, it better protects the surrounding space from breakout noise. Table 19 lists sound attenuation values for unlined round ducts (Kuntz and Hoover 1987; Woods Fan Division 1973). Acoustically Lined Round Sheet Metal Ducts. ASHRAE re- search project RP-1408 (Reynolds and Albright 2018) measured the insertion loss of round sheet metal ducts with 25 and 50 mm thick glass fiber duct liner and diameters of305 to 1220 mm. Tables 20 and 21 present the measured insertion loss of acoustically lined round sheet metal ducts as a function of frequency and length of duct lin- ing for a variety of common duct sizes. Insertion loss values for di- ameters smaller than 305 mm and larger than 1220 mm were taken from previous editions of the ASHRAE Handbook. The liner was 64 kg/m3. Though previous editions of this table indicated values of dB/m, research projects have shown that attenuation does not vary exactly linearly with length. Therefore, these updated tables show attenua- tion for lengths as actually tested. For interpolation to various duct lengths and cross sections, using the duct liner attenuation spread- sheet (available as an extra feature for the ASHRAE Handbook Online version of this chapter) is recommended. Note that the total attenuated noise will never be below the flow-generated noise level in the duct, and, because of typical flows and flanking noise in prac- tice, attenuation values are capped at 50 dB. Rectangular Sheet Metal Duct Elbows. Table 22 displays inser- tion loss values for unlined and lined square elbows without turning vanes (Beranek 1960). For lined square elbows, duct lining must extend at least two duct widths w beyond the elbow. Table 22 applies only where the duct is lined before and after the elbow. Table 23 gives insertion loss values for unlined radiused elbows. Table 24 gives insertion loss values for unlined and lined square elbows with turning vanes. The quantityfw in Tables 22 to 24 is the midfrequency of the octave band times the width of the elbow (Figure 20) (Beranek 1960; Ver 1983b). Nonmetallic Insulated Flexible Ducts. Nonmetallic insulated flexible ducts can significantly reduce airborne noise. Insertion loss values for specified duct diameters and lengths are given in Table 25 and in Appendix D of ARI Standard 885. Recommended duct lengths are normally 0.9 to 1.8 m. Take care to keep flexible ducts straight; bends should have as long a radius as possible. Although an Table 20 Insertion Loss for Round Sheet Metal Ducts with 25 mm Thick Fiberglass Lining ¦ ID ¦ ID ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Dimensions, Length, mm ¦ m ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ 8000 ¦ ¦ 150 ¦ 3 ¦ 4 ¦ 6 ¦ 9 ¦ 12 ¦ 22 ¦ 23 ¦ 20 ¦ 13 ¦ ¦ 200 ¦ 3 ¦ 3 ¦ 5 ¦ 9 ¦ 15 ¦ 22 ¦ 22 ¦ 18 ¦ 12 ¦ ¦ 250 ¦ 3 ¦ 2 ¦ 4 ¦ 8 ¦ 15 ¦ 22 ¦ 20 ¦ 16 ¦ 12 ¦ ¦ 300 ¦ 1.5 ¦ 0 ¦ 1 ¦ 4 ¦ 12 ¦ 28 ¦ 29 ¦ 16 ¦ 14 ¦ ¦ ¦ 3 ¦ 0 ¦ 3 ¦ 7 ¦ 19 ¦ 41 ¦ 35 ¦ 21 ¦ 18 ¦ ¦ ¦ 6 ¦ 0 ¦ 5 ¦ 13 ¦ 33 ¦ 50 ¦ 48 ¦ 30 ¦ 26 ¦ ¦ ¦ 12 ¦ 0 ¦ 9 ¦ 24 ¦ 50 ¦ 50 ¦ 50 ¦ 44 ¦ 39 ¦ ¦ 410 ¦ 1.5 ¦ 0 ¦ 1 ¦ 3 ¦ 11 ¦ 26 ¦ 22 ¦ 16 ¦ 16 ¦ ¦ ¦ 3 ¦ 0 ¦ 2 ¦ 6 ¦ 17 ¦ 38 ¦ 27 ¦ 19 ¦ 18 ¦ ¦ ¦ 6 ¦ 0 ¦ 4 ¦ 11 ¦ 29 ¦ 50 ¦ 37 ¦ 25 ¦ 23 ¦ ¦ ¦ 12 ¦ 0 ¦ 7 ¦ 20 ¦ 49 ¦ 50 ¦ 50 ¦ 36 ¦ 32 ¦ ¦ 510 ¦ 1.5 ¦ 0 ¦ 1 ¦ 3 ¦ 10 ¦ 23 ¦ 17 ¦ 14 ¦ 16 ¦ ¦ ¦ 3 ¦ 0 ¦ 2 ¦ 5 ¦ 15 ¦ 33 ¦ 21 ¦ 17 ¦ 17 ¦ ¦ ¦ 6 ¦ 0 ¦ 3 ¦ 9 ¦ 25 ¦ 48 ¦ 28 ¦ 21 ¦ 20 ¦ ¦ ¦ 12 ¦ 0 ¦ 6 ¦ 16 ¦ 44 ¦ 50 ¦ 42 ¦ 29 ¦ 25 ¦ ¦ 610 ¦ 1.5 ¦ 0 ¦ 1 ¦ 2 ¦ 9 ¦ 20 ¦ 13 ¦ 12 ¦ 14 ¦ ¦ ¦ 3 ¦ 0 ¦ 1 ¦ 4 ¦ 14 ¦ 29 ¦ 16 ¦ 14 ¦ 15 ¦ ¦ ¦ 6 ¦ 0 ¦ 2 ¦ 7 ¦ 22 ¦ 44 ¦ 22 ¦ 17 ¦ 17 ¦ ¦ ¦ 12 ¦ 0 ¦ 4 ¦ 13 ¦ 39 ¦ 50 ¦ 32 ¦ 23 ¦ 21 ¦ ¦ 710 ¦ 1.5 ¦ 0 ¦ 1 ¦ 2 ¦ 8 ¦ 17 ¦ 10 ¦ 11 ¦ 12 ¦ ¦ ¦ 3 ¦ 0 ¦ 1 ¦ 3 ¦ 12 ¦ 24 ¦ 12 ¦ 12 ¦ 13 ¦ ¦ ¦ 6 ¦ 0 ¦ 2 ¦ 6 ¦ 20 ¦ 38 ¦ 17 ¦ 14 ¦ 15 ¦ ¦ ¦ 12 ¦ 0 ¦ 4 ¦ 11 ¦ 34 ¦ 50 ¦ 25 ¦ 19 ¦ 18 ¦ ¦ 810 ¦ 1.5 ¦ 0 ¦ 1 ¦ 2 ¦ 8 ¦ 14 ¦ 8 ¦ 9 ¦ 10 ¦ ¦ ¦ 3 ¦ 0 ¦ 1 ¦ 3 ¦ 11 ¦ 20 ¦ 10 ¦ 10 ¦ 11 ¦ ¦ ¦ 6 ¦ 0 ¦ 2 ¦ 5 ¦ 18 ¦ 31 ¦ 14 ¦ 12 ¦ 13 ¦ ¦ ¦ 12 ¦ 0 ¦ 3 ¦ 10 ¦ 31 ¦ 49 ¦ 21 ¦ 17 ¦ 17 ¦ ¦ 910 ¦ 1.5 ¦ 0 ¦ 1 ¦ 1 ¦ 7 ¦ 13 ¦ 7 ¦ 7 ¦ 8 ¦ ¦ ¦ 3 ¦ 0 ¦ 1 ¦ 3 ¦ 11 ¦ 17 ¦ 9 ¦ 8 ¦ 9 ¦ ¦ ¦ 6 ¦ 0 ¦ 1 ¦ 5 ¦ 17 ¦ 25 ¦ 12 ¦ 11 ¦ 11 ¦ ¦ ¦ 12 ¦ 0 ¦ 3 ¦ 9 ¦ 29 ¦ 41 ¦ 18 ¦ 15 ¦ 16 ¦ ¦ 1020 ¦ 1.5 ¦ 0 ¦ 0 ¦ 1 ¦ 7 ¦ 12 ¦ 7 ¦ 6 ¦ 6 ¦ ¦ ¦ 3 ¦ 0 ¦ 1 ¦ 3 ¦ 10 ¦ 15 ¦ 8 ¦ 7 ¦ 7 ¦ ¦ ¦ 6 ¦ 0 ¦ 1 ¦ 5 ¦ 17 ¦ 20 ¦ 11 ¦ 10 ¦ 10 ¦ ¦ ¦ 12 ¦ 0 ¦ 3 ¦ 9 ¦ 27 ¦ 31 ¦ 16 ¦ 15 ¦ 15 ¦ ¦ 1120 ¦ 1.5 ¦ 0 ¦ 0 ¦ 1 ¦ 7 ¦ 11 ¦ 7 ¦ 6 ¦ 5 ¦ ¦ ¦ 3 ¦ 0 ¦ 1 ¦ 2 ¦ 10 ¦ 13 ¦ 8 ¦ 7 ¦ 6 ¦ ¦ 1220 ¦ 6 ¦ 0 ¦ 1 ¦ 5 ¦ 17 ¦ 17 ¦ 10 ¦ 9 ¦ 9 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 23 ¦ 14 ¦ 13 ¦ 14 ¦ ¦ ¦ 12 ¦ 0 ¦ 3 ¦ 8 ¦ 27 ¦ 12 ¦ ¦ 6 ¦ 5 ¦ ¦ ¦ 1.5 ¦ 0 ¦ 0 1 ¦ 1 2 ¦ 7 10 ¦ 13 ¦ 6 7 ¦ 7 ¦ 6 ¦ ¦ ¦ 3 6 ¦ 0 0 ¦ 1 ¦ 4 ¦ 17 ¦ 16 ¦ 9 ¦ 8 ¦ 8 ¦ ¦ ¦ 12 ¦ 0 ¦ 3 ¦ 8 ¦ 29 ¦ 20 ¦ 13 ¦ 11 ¦ 13 ¦ ¦ 1370 ¦ 3 3 ¦ 0 0 ¦ 0 0 ¦ 1 0 ¦ 4 0 ¦ 1 1 ¦ 2 1 ¦ 3 1 ¦ 3 1 ¦ ¦ 1520 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ abrupt bend may provide some additional insertion loss, the noise associated with airflow in the bend may be unacceptably high. Because of potentially high breakout sound levels associated with flexible ducts, take care when using flexible ducts above sound- sensitive spaces. Duct Branch Sound Power Division. When sound traveling in a duct encounters a junction, the sound power contained in the in- cident sound waves in the main feeder duct is distributed between the branches associated with the junction (Ver 1982, 1983b). This division of sound power is called branch sound power division. The corresponding attenuation of sound power transmitted down each branch of the junction is comprised of two components. The first is Inc. ASHRAE, 2019 user. single for Licensed | {}
19c1a7fa-7c77-44a4-963f-6fe6ee7aa4b7 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.24 2019 ASHRAE Handbook-HVAC Applications (SI) Table 21 Insertion Loss for Round Sheet Metal Ducts with 50 mm Thick Fiberglass Lining Inc. ASHRAE, 2019 user. single for Licensed ¦ ID Dimensions, Length, mm ¦ ID Dimensions, Length, mm ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ID Dimensions, Length, mm ¦ ID Dimensions, Length, mm ¦ m 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ 8000 ¦ ¦ 150 ¦ 3 ¦ 6 ¦ 8 ¦ 14 ¦ 22 ¦ 22 ¦ 23 ¦ 20 ¦ 13 ¦ ¦ 200 ¦ 3 ¦ 5 ¦ 7 ¦ 13 ¦ 22 ¦ 22 ¦ 22 ¦ 18 ¦ 12 ¦ ¦ 250 ¦ 3 ¦ 4 ¦ 7 ¦ 13 ¦ 22 ¦ 22 ¦ 20 ¦ 16 ¦ 11 ¦ ¦ 300 ¦ 1.5 ¦ 2 ¦ 4 ¦ 10 ¦ 25 ¦ 41 ¦ 29 ¦ 18 ¦ 16 ¦ ¦ ¦ 3 ¦ 3 ¦ 7 ¦ 17 ¦ 35 ¦ 46 ¦ 37 ¦ 23 ¦ 18 ¦ ¦ ¦ 6 ¦ 5 ¦ 13 ¦ 31 ¦ 50 ¦ 50 ¦ 49 ¦ 32 ¦ 22 ¦ ¦ ¦ 12 ¦ 7 ¦ 22 ¦ 50 ¦ 50 ¦ 50 ¦ 50 ¦ 47 ¦ 29 ¦ ¦ 410 ¦ 1.5 ¦ 2 ¦ 3 ¦ 8 ¦ 24 ¦ 35 ¦ 21 ¦ 17 ¦ 17 ¦ ¦ ¦ 3 ¦ 3 ¦ 6 ¦ 14 ¦ 34 ¦ 42 ¦ 28 ¦ 21 ¦ 19 ¦ ¦ ¦ 6 ¦ 4 ¦ 10 ¦ 25 ¦ 50 ¦ 50 ¦ 39 ¦ 27 ¦ 21 ¦ ¦ ¦ 12 ¦ 5 ¦ 18 ¦ 46 ¦ 50 ¦ 50 ¦ 50 ¦ 39 ¦ 25 ¦ ¦ 510 ¦ 1.5 ¦ 2 ¦ 3 ¦ 6 ¦ 23 ¦ 27 ¦ 16 ¦ 15 ¦ 17 ¦ ¦ ¦ 3 ¦ 2 ¦ 5 ¦ 12 ¦ 32 ¦ 35 ¦ 21 ¦ 18 ¦ 18 ¦ ¦ ¦ 6 ¦ 3 ¦ 8 ¦ 21 ¦ 48 ¦ 48 ¦ 29 ¦ 23 ¦ 20 ¦ ¦ ¦ 12 ¦ 4 ¦ 15 ¦ 39 ¦ 50 ¦ 50 ¦ 43 ¦ 31 ¦ 22 ¦ ¦ 610 ¦ 1.5 ¦ 1 ¦ 2 ¦ 5 ¦ 22 ¦ 21 ¦ 13 ¦ 14 ¦ 16 ¦ ¦ ¦ 3 ¦ 2 ¦ 4 ¦ 10 ¦ 30 ¦ 29 ¦ 16 ¦ 15 ¦ 16 ¦ ¦ ¦ 6 ¦ 2 ¦ 7 ¦ 18 ¦ 45 ¦ 43 ¦ 21 ¦ 18 ¦ 18 ¦ ¦ ¦ 12 ¦ 3 ¦ 12 ¦ 33 ¦ 50 ¦ 50 ¦ 31 ¦ 24 ¦ 20 ¦ ¦ 710 ¦ 1.5 ¦ 1 ¦ 2 ¦ 5 ¦ 21 ¦ 17 ¦ 10 ¦ 12 ¦ 13 ¦ ¦ ¦ 3 ¦ 1 ¦ 3 ¦ 8 ¦ 29 ¦ 24 ¦ 12 ¦ 13 ¦ 14 ¦ ¦ ¦ 6 ¦ 2 ¦ 6 ¦ 15 ¦ 43 ¦ 37 ¦ 16 ¦ 15 ¦ 15 ¦ ¦ ¦ 12 ¦ 3 ¦ 11 ¦ 28 ¦ 50 ¦ 50 ¦ 23 ¦ 19 ¦ 18 ¦ ¦ 810 ¦ 1.5 ¦ 1 ¦ 1 ¦ 4 ¦ 20 ¦ 15 ¦ 9 ¦ 11 ¦ 11 ¦ ¦ ¦ 3 ¦ 1 ¦ 3 ¦ 8 ¦ 27 ¦ 21 ¦ 11 ¦ 12 ¦ 12 ¦ ¦ ¦ 6 ¦ 2 ¦ 5 ¦ 14 ¦ 42 ¦ 31 ¦ 13 ¦ 13 ¦ 13 ¦ ¦ ¦ 12 ¦ 2 ¦ 10 ¦ 25 ¦ 50 ¦ 49 ¦ 18 ¦ 17 ¦ 17 ¦ ¦ 910 ¦ 2 ¦ 1 ¦ 1 ¦ 4 ¦ 19 ¦ 14 ¦ 8 ¦ 9 ¦ 8 ¦ ¦ ¦ 3 ¦ 1 ¦ 2 ¦ 7 ¦ 26 ¦ 18 ¦ 10 ¦ 10 ¦ 9 ¦ ¦ ¦ 6 ¦ 1 ¦ 5 ¦ 13 ¦ 41 ¦ 25 ¦ 12 ¦ 12 ¦ 11 ¦ ¦ ¦ 12 ¦ 3 ¦ 9 ¦ 23 ¦ 50 ¦ 40 ¦ 17 ¦ 15 ¦ 16 ¦ ¦ 1020 ¦ 1.5 ¦ 1 ¦ 1 ¦ 4 ¦ 19 ¦ 12 ¦ 8 ¦ 8 ¦ 6 ¦ ¦ ¦ 3 ¦ 1 ¦ 2 ¦ 7 ¦ 26 ¦ 15 ¦ 9 ¦ 9 ¦ 7 ¦ ¦ ¦ 6 ¦ 2 ¦ 4 ¦ 12 ¦ 40 ¦ 20 ¦ 12 ¦ 11 ¦ 10 ¦ ¦ ¦ 12 ¦ 3 ¦ 9 ¦ 22 ¦ 50 ¦ 29 ¦ 16 ¦ 15 ¦ 15 ¦ ¦ 1120 ¦ 1.5 ¦ 1 ¦ 1 ¦ 4 ¦ 19 ¦ 11 ¦ 7 ¦ 6 ¦ 4 ¦ ¦ ¦ 3 ¦ 1 ¦ 2 ¦ 7 ¦ 26 ¦ 13 ¦ 8 ¦ 7 ¦ 6 ¦ ¦ ¦ 6 ¦ 2 ¦ 4 ¦ 12 ¦ 39 ¦ 16 ¦ 11 ¦ 10 ¦ 9 ¦ ¦ ¦ 12 ¦ ¦ ¦ ¦ ¦ 22 ¦ 16 ¦ 16 ¦ 16 ¦ ¦ ¦ ¦ 3 ¦ 8 ¦ 21 ¦ 50 ¦ ¦ 5 ¦ 5 ¦ 4 ¦ ¦ ¦ 1220 1.5 ¦ 1 1 ¦ 1 2 ¦ 4 7 ¦ 18 25 ¦ 10 12 ¦ 7 ¦ 6 ¦ 6 ¦ ¦ ¦ 3 6 ¦ 2 ¦ 4 ¦ 12 ¦ 38 ¦ 15 ¦ 9 ¦ 9 ¦ 10 ¦ ¦ ¦ 12 ¦ 3 ¦ 7 ¦ 20 ¦ 50 ¦ 21 ¦ 15 ¦ 16 ¦ 17 ¦ ¦ 1370 ¦ 3 3 ¦ 0 0 ¦ 1 0 ¦ 6 5 ¦ 11 8 ¦ 1 1 ¦ 2 1 ¦ 3 0 ¦ 2 0 ¦ ¦ 1520 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Table 22 Insertion Loss of Unlined and Lined Square Elbows Without Turning Vanes ¦ ¦ Insertion Loss, dB ¦ Insertion Loss, dB ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ Unlined Elbows ¦ Lined Elbows ¦ ¦ fw < 48 ¦ 0 ¦ 0 ¦ ¦ 48 ≤fw < 96 ¦ 1 ¦ 1 ¦ ¦ 96 ¦ 5 ¦ 6 ¦ ¦ 190 ¦ 8 ¦ 11 ¦ ¦ 380 ≤fw < 760 ¦ 4 ¦ 10 ¦ ¦ fw > 760 ¦ 3 ¦ 10 ¦ Note: f = center frequency, kHz, and W = width, mm Table 23 Insertion Loss of Radiused Elbows ¦ ¦ Insertion Loss, dB ¦ ¦ --- ¦ --- ¦ ¦ fw < 48 ¦ 0 ¦ ¦ 48 ¦ 1 ¦ ¦ 96 ¦ 2 ¦ ¦ fw> 190 ¦ 3 ¦ Note: - = center frequency, kHz, and w = width, mm Table 24 Insertion Loss of Unlined and Lined Square Elbows with Turning Vanes Insertion Loss, dB ¦ ¦ Unlined Elbows ¦ Lined Elbows ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ fw < 48 ¦ 0 ¦ 0 ¦ ¦ 48 ¦ 1 ¦ 1 ¦ ¦ 96 ¦ 4 ¦ 4 ¦ ¦ 190 ¦ 6 ¦ 7 ¦ ¦ fw> 380 ¦ 4 ¦ 7 ¦ Note: ⌀= center frequency, kHz, and W = width, mm associated with reflection of the incident sound wave if the sum of the cross-sectional areas of individual branches ESBi differs from the cross-sectional area of the main feeder duct. The second and more dominant component is associated with energy division accord- ing to the ratio of the cross-sectional area of an individual branch S Bi divided by ESBi- Values for the attenuation of sound power AL Bi are given in Table 26. Duct Silencers. Silencers, sometimes called sound attenuators, sound traps, or mufflers, are designed to reduce the noise transmit- ted from a source to a receiver. For HVAC applications, the most common silencers are duct silencers, installed on the intake and/or discharge side of a fan or air handler. Also, they may be used on the receiver side of other noise generators such as terminal boxes, valves, dampers, etc. All silencers can be rated for (1) insertion loss, (2) dynamic insertion loss, (3) pressure drop, and (4) self-generated noise in accordance with ASTM Standard E477 test standards. As such, the performance is under rather ideal conditions as seen in Figure 22. Duct silencers are available in varying shapes and sizes to fit project ductwork. Generally, a duct silencer's outer appearance is similar to a piece of ductwork. It consists of a sheet metal casing with length commonly ranging from 0.9 to 3 m. Common shapes include rectangular, round, elbow, tee, and transitional. Figure 21 shows some duct silencer configurations. Insertion loss is the reduction in the sound power level at the receiver after the silencer is installed ("inserted") in the system. Insertion loss is measured as a function of frequency and com- monly published in full octave bands ranging from 63 to 8000 Hz. Dynamic insertion loss is insertion loss with given airflow direction and velocity. A silencer's insertion loss varies depending on whether sound is traveling in the same or opposite direction as airflow. Silencer performance changes with absolute duct velocity. However, airflow velocity generally does not significantly affect | {}
1f56cc0b-1369-4828-86e1-1def61b3e793 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.25 ![image](/image/placeholder) RECTANGULAR RECTANGULAR ELBOW TRANSITIONAL RECTANGULAR T-ELBOW CIRCULAR Fig. 21 Duct Silencer Configurations ![image](/image/placeholder) 8 1 - Airflow m easurement station 2 - System fan 3 - System silencer 4 - Signal source chamber 5 - Pressure test station 6 - Straight silencer under test 7 - Pressure test station 8 - Reverberation room Fig. 22 Typical Facility for Rating Straight Duct Silencers With or Without Airflow silencers giving a pressure drop of 90 Pa or less, including system effects. Pressure drop is measured across the silencer at a given veloc- ity. Good flow conditions are required for accurate measurements at both the inlet and discharge of the silencer. The measuring points are usually 2.5 to 5 duct diameters upstream and downstream of the silencer to avoid turbulent flow areas near the silencer and to allow for any static pressure regain. For nonideal installations, with duct elbows or transitions closer than 2.5 to 5 duct diameters, the total system effect will be larger than the laboratory test data. Airflow-generated self noise is the sound power generated on the receiving side by the silencer when quiet air flows through it. This represents the noise floor, or the lowest level achievable regardless ofhigh insertion loss values. A silencer's self-generated noise is a function of frequency and internal geometry, and is refer- enced to specific velocities and airflow direction (forward or reverse). The airflow-generated sound power of the silencer is log- arithmically proportional to silencer cross-sectional area. Self noise generally does not vary with silencer length. There are three types of HVAC duct silencers: dissipative (with acoustic media), fiber-free reactive (no media), and active. Dissipative Silencers. Dissipative silencers use sound-absorptive media such as fiberglass as the primary means of attenuating sound; mineral wool can be used in high-temperature applications but may Table 25 Insertion Loss for Lined Flexible Duct ¦ Diameter, mm ¦ Length, m ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Diameter, mm ¦ Length, m ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ ¦ 100 ¦ 3.7 ¦ 6 ¦ 11 ¦ 12 ¦ 31 ¦ 37 ¦ 42 ¦ 27 ¦ ¦ ¦ 2.7 ¦ 5 ¦ 8 ¦ 9 ¦ 23 ¦ 28 ¦ 32 ¦ 20 ¦ ¦ ¦ 1.8 ¦ 3 ¦ 6 ¦ 6 ¦ 16 ¦ 19 ¦ 21 ¦ 14 ¦ ¦ ¦ 0.9 ¦ 2 ¦ 3 ¦ 3 ¦ 8 ¦ 9 ¦ 11 ¦ 7 ¦ ¦ 125 ¦ 3.7 ¦ 7 ¦ 12 ¦ 14 ¦ 32 ¦ 38 ¦ 41 ¦ 26 ¦ ¦ ¦ 2.7 ¦ 5 ¦ 9 ¦ 11 ¦ 24 ¦ 29 ¦ 31 ¦ 20 ¦ ¦ ¦ 1.8 ¦ 4 ¦ 6 ¦ 7 ¦ 16 ¦ 19 ¦ 21 ¦ 13 ¦ ¦ ¦ 0.9 ¦ 2 ¦ 3 ¦ 4 ¦ 8 ¦ 10 ¦ 10 ¦ 7 ¦ ¦ 150 ¦ 3.7 ¦ 8 ¦ 12 ¦ 17 ¦ 33 ¦ 38 ¦ 40 ¦ 26 ¦ ¦ ¦ 2.7 ¦ 6 ¦ 9 ¦ 13 ¦ 25 ¦ 29 ¦ 30 ¦ 20 ¦ ¦ ¦ 1.8 ¦ 4 ¦ 6 ¦ 9 ¦ 17 ¦ 19 ¦ 20 ¦ 13 ¦ ¦ ¦ 0.9 ¦ 2 ¦ 3 ¦ 4 ¦ 8 ¦ 10 ¦ 10 ¦ 7 ¦ ¦ 175 ¦ 3.7 ¦ 9 ¦ 12 ¦ 19 ¦ 33 ¦ 37 ¦ 38 ¦ 25 ¦ ¦ ¦ 2.7 ¦ 6 ¦ 9 ¦ 14 ¦ 25 ¦ 28 ¦ 29 ¦ 19 ¦ ¦ ¦ 1.8 ¦ 4 ¦ 6 ¦ 10 ¦ 17 ¦ 19 ¦ 19 ¦ 13 ¦ ¦ ¦ 0.9 ¦ 2 ¦ 3 ¦ 5 ¦ 8 ¦ 9 ¦ 10 ¦ 6 ¦ ¦ 200 ¦ 3.7 ¦ 8 ¦ 11 ¦ 21 ¦ 33 ¦ 37 ¦ 37 ¦ 24 ¦ ¦ ¦ 2.7 ¦ 6 ¦ 8 ¦ 16 ¦ 25 ¦ 28 ¦ 28 ¦ 18 ¦ ¦ ¦ 1.8 ¦ 4 ¦ 6 ¦ 11 ¦ 17 ¦ 19 ¦ 19 ¦ 12 ¦ ¦ ¦ 0.9 ¦ 2 ¦ 3 ¦ 5 ¦ 8 ¦ 9 ¦ 9 ¦ 6 ¦ ¦ 225 ¦ 3.7 ¦ 8 ¦ 11 ¦ 22 ¦ 33 ¦ 37 ¦ 36 ¦ 22 ¦ ¦ ¦ 2.7 ¦ 6 ¦ 8 ¦ 17 ¦ 25 ¦ 28 ¦ 27 ¦ 17 ¦ ¦ ¦ 1.8 ¦ 4 ¦ 6 ¦ 11 ¦ 17 ¦ 19 ¦ 18 ¦ 11 ¦ ¦ ¦ 0.9 ¦ 2 ¦ 3 ¦ 6 ¦ 8 ¦ 9 ¦ 9 ¦ 6 ¦ ¦ 250 ¦ 3.7 ¦ 8 ¦ 10 ¦ 22 ¦ 32 ¦ 36 ¦ 34 ¦ 21 ¦ ¦ ¦ 2.7 ¦ 6 ¦ 8 ¦ 17 ¦ 24 ¦ 27 ¦ 26 ¦ 16 ¦ ¦ ¦ 1.8 ¦ 4 ¦ 5 ¦ 11 ¦ 16 ¦ 18 ¦ 17 ¦ 11 ¦ ¦ ¦ 0.9 ¦ 2 ¦ 3 ¦ 6 ¦ 8 ¦ 9 ¦ 9 ¦ 5 ¦ ¦ 300 ¦ 3.7 ¦ 7 ¦ 9 ¦ 20 ¦ 30 ¦ 34 ¦ 31 ¦ 18 ¦ ¦ ¦ 2.7 ¦ 5 ¦ 7 ¦ 15 ¦ 23 ¦ 26 ¦ 23 ¦ 14 ¦ ¦ ¦ 1.8 ¦ 3 ¦ 5 ¦ 10 ¦ 15 ¦ 17 ¦ 16 ¦ 9 ¦ ¦ ¦ 0.9 ¦ 2 ¦ 2 ¦ 5 ¦ 8 ¦ 9 ¦ 8 ¦ 5 ¦ ¦ 350 ¦ 3.7 ¦ 5 ¦ 7 ¦ 16 ¦ 27 ¦ 31 ¦ 27 ¦ 14 ¦ ¦ ¦ 2.7 ¦ 4 ¦ 5 ¦ 12 ¦ 20 ¦ 23 ¦ 20 ¦ 11 ¦ ¦ ¦ 1.8 ¦ 3 ¦ 4 ¦ 8 ¦ 14 ¦ 16 ¦ 14 ¦ 7 ¦ ¦ ¦ 0.9 ¦ 1 ¦ 2 ¦ 4 ¦ 7 ¦ 8 ¦ 7 ¦ 4 ¦ ¦ 400 ¦ 3.7 ¦ 2 ¦ 4 ¦ 9 ¦ 23 ¦ 28 ¦ 23 ¦ 9 ¦ ¦ ¦ 2.7 ¦ 2 ¦ 3 ¦ 7 ¦ 17 ¦ 21 ¦ 17 ¦ 7 ¦ ¦ ¦ 1.8 ¦ 1 ¦ 2 ¦ 5 ¦ 12 ¦ 14 ¦ 12 ¦ 5 ¦ ¦ ¦ 0.9 ¦ 1 ¦ 1 ¦ 2 ¦ 6 ¦ 7 ¦ 6 ¦ 2 ¦ Note: 63 Hz insertion loss values estimated from higher-frequency insertion loss values. Table 26 Duct Branch Sound Power Division ¦ SBi/ ESBi ¦ ALBi ¦ SBi /ESBi ¦ ALBi ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1.00 ¦ 0 ¦ 0.10 ¦ 10 ¦ ¦ 0.80 ¦ 1 ¦ 0.08 ¦ 11 ¦ ¦ 0.63 ¦ 2 ¦ 0.063 ¦ 12 ¦ ¦ 0.50 ¦ 3 ¦ 0.050 ¦ 13 ¦ ¦ 0.40 ¦ 4 ¦ 0.040 ¦ 14 ¦ ¦ 0.32 ¦ 5 ¦ 0.032 ¦ 15 ¦ ¦ 0.25 ¦ 6 ¦ 0.025 ¦ 16 ¦ ¦ 0.20 ¦ 7 ¦ 0.020 ¦ 17 ¦ ¦ 0.16 ¦ 8 ¦ 0.016 ¦ 18 ¦ ¦ 0.12 ¦ 9 ¦ 0.012 ¦ 19 ¦ Inc. ASHRAE, 2019 user. single for Licensed | {}
4fa2a481-9748-4379-97fe-17adeb456b32 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.26 2019 ASHRAE Handbook-HVAC Applications (SI) contain too much contamination ("shot") for commercial HVAC applications. Usually, the absorptive medium is covered by perfo- rated metal to protect it from erosion by airflow. Ifinternal silencer velocities are high (faster than 23 m/s), media erosion may be fur- ther reduced by a layer of material such as fiberglass cloth or poly- mer film liner placed between the absorptive media and the perforated metal. Dissipative silencers may be supplied as hospital-grade or as film-lined silencers that include special poly- mer film linings to prevent contamination of the airstream by acoustical media fibers and prevent particles from the airstream from getting into the media. These silencers are commonly used in hospitals, pharmaceutical facilities, cleanrooms, and other places where indoor air quality is of paramount concern. Consult manu- facturers for construction and testing performance details. Dissipative silencer performance is primarily a function of si- lencer length; airflow constriction; number, thickness, and shape of splitters or centerbodies; and type and density of absorptive media. The absorptive media allows dissipative silencers to provide signif- icant insertion loss performance over a wide frequency range. Insertion loss performance does not necessarily increase linearly with silencer length; for a given length, silencer designs can produce varying insertion loss and pressure drop data. Even at the same pres- sure drop and length, silencers can be configured to provide varying insertion loss performance across the frequency spectrum. Reactive Silencers. Reactive silencers are constructed only of metal, both solid and perforated, with chambers of specially de- signed shapes and sizes behind the perforated metal that are tuned as resonators to react with and reduce sound power at certain fre- quencies. The outward appearance of reactive silencers is similar to that of their dissipative counterparts. However, because of tun- ing, insertion loss over a wide frequency range is more difficult to achieve. Longer lengths may be required to achieve similar inser- tion loss performance as dissipative silencers. Airflow generally increases the insertion loss of reactive silencers. Figure 23 compares insertion loss of dissipative silencers, with and without protective film materials, against that of a reactive silencer for the same pressure drop. Active Silencers. Active duct silencers, sometimes called noise canceling systems, produce inverse sound waves that cancel noise Chart Type: line 63 Hz 125 Hz 250 Hz 500 Hz 1000 Hz 2000 Hz 4000 Hz 8000 Hz item_01 10dB 15dB 20dB 30dB 35dB 30dB 25dB 20dB Fig. 23 Comparison of1.5 m Long Dissipative and Fiber-Free Reactive Silencer Performance primarily at low frequencies. An input microphone measures noise in the duct and converts it to electrical signals, which are processed digitally to generate opposite, mirror-image sound signals of equal amplitude. A secondary noise source destructively interferes with the primary noise and cancels a significant portion of it. An error microphone measures residual sound beyond the silencer and provides feedback to adjust the computer model for improved performance. Because components are mounted outside the airflow, there is no pressure loss or airflow-generated noise. Performance is limited, however, if excessive turbulence is detected by the microphones. Manufacturers recommend using active silencers where duct veloc- ities are less than 7.6 m/s and where duct configurations are condu- cive to smooth, evenly distributed airflow. Active silencers have significant low-frequency insertion loss, and are self-regulating because, iffan noise levels increase, an active silencer can increase performance to compensate for the increased source noise. Mid- and high-frequency insertion loss is minimal, however, so if required, combinations of active (for low-frequency components) and passive (for mid- and high-frequency components) can be used to achieve insertion loss over a wide frequency range. Test Standard. Data for dissipative and reactive silencers should be obtained from tests consistent with the procedures outlined in ASTM Standard E477. (This standard has not been verified for determining performance of active silencers.) Because insertion loss measurements use a substitution technique, reasonably precise insertion loss values can be achieved (±3 dB down to 125 Hz, and ±5 dB at lower frequencies). Airflow-generated noise values can be obtained with similar accuracy. Round-robin tests performed at sev- eral manufacturers' and independent testing laboratories showed that airflow-generated sound power data have an expected standard deviation of±3 to 6 dB over the octave band frequency range of 125 to 8000 Hz. (For normal distribution, uncertainty with a 95% confi- dence interval is about two standard deviations.) Silencer Selection Issues. When selecting a duct silencer, con- sider the following: · Insertion loss required to achieve required room sound criteria · Allowable pressure drop (if no specific requirement, then keep under 90 Pa, including system effects; when system effects are unknown, keep under 50 Pa, excluding system effects) at system duct velocity · Silencer location and available space · Amount of airflow-generated noise that can be tolerated · Indoor air quality concerns · Duct configuration Insertion Loss Issues To determine the insertion loss required, analyze the duct system, summing noise-generating mechanisms and subtracting attenuation elements (not including the silencer). The silencer's required inser- tion loss is the amount by which the estimated resultant sound pres- sure level in the space exceeds the room criteria for the space. The user should consider both the sound path through the ductwork and outlets as well as potential locations where sound may break out of the ductwork. Allowable Pressure Drop Issues Care should be taken in applying test data to actual project instal- lations. Adverse aerodynamic system effects can significantly affect silencer performance. That is, if the silencer is located where less- than-ideal conditions exists on the inlet and/or the discharge of the silencer (3 to 5 duct diameters of straight duct), then the silencer's effective pressure drop (PD) is increased (total silencer PD = silencer PD per ASTM Standard E477 + system effect losses). In some situations, the added system effect losses can be greater than the silencer's pressure drop. Some manufacturers give guidelines Inc. ASHRAE, 2019 user. single for Licensed | {}
3dea8b18-e835-4150-a83f-4da6f631fcd6 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.27 Table 27 Approximate Silencer System Effect Factors ¦ Silencer Condition ¦ Pressure ¦ ¦ --- ¦ --- ¦ ¦ ¦ Drop Factor* ¦ ¦ Inlet (within 3 to 4 duct diameters) ¦ ¦ ¦ Straight unobstructed duct ¦ 1.0 ¦ ¦ Free air/plenum with smooth inlet ¦ 1.05 ¦ ¦ Radiused elbow, with turning vanes ¦ 1.05 ¦ ¦ no turning vanes ¦ 1.1 ¦ ¦ Miter elbow ¦ 1.3 ¦ ¦ Free air/plenum with sharp inlet ¦ 1.1 to 1.30 ¦ ¦ Fan ¦ 1.1 to 1.3 ¦ ¦ Outlet (within 3 to 4 duct diameters) ¦ ¦ ¦ Straight unobstructed duct ¦ 1.0 ¦ ¦ Duct doubles area abruptly ¦ 1.4 ¦ ¦ Radiused elbow, with turning vanes ¦ 1.5 ¦ ¦ no turning vanes ¦ 1.9 ¦ ¦ Miter elbow ¦ 2.0 ¦ ¦ Abrupt expansion/plenum ¦ 2.0 ¦ ¦ Fan ¦ 1.2 to 1.4 ¦ *Silencer pressure drop (including system effects) = silencer pressure drop per test code X pressure drop factor (inlet) x pressure drop factor (outlet). for estimated pressure loss increases from varying silencer inlet and discharge configurations (Table 27); these should be considered as general guidelines. Substantial variations can occur depending on the type of silencer, its internal geometry, size of silencer, size of duct, airflow turbulence, etc. For example, an elbow fitting located immediately after a silencer prevents regain of the silencer' s leaving velocity pressure. In addition, local velocities in the elbow fitting are greater than the average duct velocity that produces higher over- all static pressure losses. Silencer Location Issues Silencers should generally be located as close to the noise source as possible but far enough away to allow a uniform flow profile to develop. This helps contain noise at the source and limits potential points where unsilenced noise may break out. However, because turbulent airflow usually exists close to noise sources such as fans, valves, dampers, etc., the user should carefully evaluate aerody- namic system effects. A straight silencer has a lower first cost than a transitional or elbow silencer. If space limitations prohibit effective use of a straight silencer, or if pressure drop (including system effects) is greater than the loss allowed, use of elbow or transitional silencers should be evaluated. Special fan inlet and discharge silencers, including cone and inlet box silencers, minimize aerodynamic sys- tem effects, and contain noise at the source. Airflow-Generated Noise Issues In most installations, airflow-generated noise is much less than, and does not contribute to, the reduced noise level on the receiver side of the silencer. This is especially true if the silencer is properly located close to the source. In general, airflow-generated noise should be evaluated if pressure drops exceed 90 Pa (including sys- tem effects), the noise criterion is below NC/RC 35, orifthe silencer is located very close to or in the occupied space. To evaluate airflow-generated noise, sum the noise-generating mechanisms (from noise source to silencer) and subtract the attenu- ation elements (including silencer) in the order they occur to deter- mine the resultant sound power level on the quiet side of the silencer. This resultant level must be summed logarithmically with the silencer's generated noise (referenced to actual duct velocities, inlet and discharge configurations, and cross-sectional area). Ifthe gener- ated noise is more than 10 dB below the residual sound, then the silencer's generated noise will have no effect on system noise levels. Table 28 Duct End Reflection Loss (ERL): Duct Terminated Flush with Wall ¦ Duct Diameter, mm ¦ End Reflection Loss, dB Octave Midband Frequency, Hz ¦ End Reflection Loss, dB Octave Midband Frequency, Hz ¦ End Reflection Loss, dB Octave Midband Frequency, Hz ¦ End Reflection Loss, dB Octave Midband Frequency, Hz ¦ End Reflection Loss, dB Octave Midband Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Duct Diameter, mm ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ ¦ 150 ¦ 18 ¦ 12 ¦ 7 ¦ 3 ¦ 1 ¦ ¦ 200 ¦ 15 ¦ 10 ¦ 5 ¦ 2 ¦ 1 ¦ ¦ 250 ¦ 14 ¦ 8 ¦ 4 ¦ 1 ¦ 0 ¦ ¦ 300 ¦ 12 ¦ 7 ¦ 3 ¦ 1 ¦ 0 ¦ ¦ 400 ¦ 10 ¦ 5 ¦ 2 ¦ 1 ¦ 0 ¦ ¦ 510 ¦ 8 ¦ 4 ¦ 1 ¦ 0 ¦ 0 ¦ ¦ 610 ¦ 7 ¦ 3 ¦ 1 ¦ 0 ¦ 0 ¦ ¦ 710 ¦ 6 ¦ 2 ¦ 1 ¦ 0 ¦ 0 ¦ ¦ 810 ¦ 5 ¦ 2 ¦ 1 ¦ 0 ¦ 0 ¦ ¦ 910 ¦ 4 ¦ 2 ¦ 0 ¦ 0 ¦ 0 ¦ ¦ 1220 ¦ 3 ¦ 1 ¦ 0 ¦ 0 ¦ 0 ¦ ¦ 1830 ¦ 1 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ Duct End Reflection Loss. When low-frequency sound waves encounter the end of a duct that is terminated into a large room, some of the incident sound energy is reflected back into the duct. Duct end reflection loss (ERL) values for a duct terminated flush with a wall are shown in Table 28. To use Table 28 for a rectangular duct, calculate the effective duct diameter D by D = 4A/ 元 (1 1) where A is the cross-sectional area of the rectangular duct (m2). For the frequency range and duct sizes of interest to HVAC designers, the duct ERL may be accurately computed using a simplified equa- tion (Cunefare and Michaud 2008) of the form a2- alco ERL = 10 log 10 1 + �fD where (12) speed of sound (dimensionally consistent with D), m/s frequency, Hz and a2 dimensionless constants determined as follows: al ¦ Termination ¦ a1 ¦ a2 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Flush ¦ 0.7 ¦ 2 ¦ ¦ Free space ¦ 1 ¦ 2 ¦ ERL varies slightly with the frequency spectrum and measure- ment bandwidth. The constants apply to a pink spectrum in octave bands, which is representative of HVAC noise. ERLs greater than 20 dB are difficult to confirm in practice. Many test standards, such as AHRI Standard 260 for ducted equipment, limit ERL to 14 dB when reporting equipment sound power levels. There are many limitations associated with the use of the ERL equation. Free-space conditions may not exist, except for duct ter- minations of 5D or more from a reflecting plane such as a wall or the floor. Such conditions may exist in test laboratories, but are not typ- ical of HV AC duct applications. Inc. ASHRAE, 2019 user. single for Licensed Research (Cunefare and Michaud 2008) has changed our under- standing of ERL for ducts terminated with commercial devices. Ducts that terminate with blade-type diffusers and grilles should be treated as having ERL for a flush termination. This includes terminal devices mounted in suspended acoustical ceiling systems. Slot dif- fusers characterized by high aspect ratios and mounted in a rigid baf- fle have frequency-independent ERL that may be determined by the analytical expression for the area ratio of the diffuser to duct cross- | {}
b1fe2b40-23b3-45f6-8504-390b4e191b27 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.28 2019 ASHRAE Handbook- - HVAC Applications (SI) sectional area. Finally, using flexible duct upstream of diffusers, grilles and other terminal devices reduces ERL to near zero above 63 Hz for all terminal devices. This research suggests that a signifi- cant amount of the low-frequency sound that would normally be reflected back into the duct from an open termination is either transmitted through the flexible duct or radiated by the termination. There is however a frequency-independent ERL associated with the area change in the transition to the flexible duct. Finally, ERL values are based on analytical assumptions and em- pirical data for long and straight duct sections. Many air distribution systems do not have long straight sections (greater than 3D) before they terminate into a room. Many duct sections between a main feed branch and a diffuser may be curved or short. The effects of these configurations on duct end reflection loss are not known. Table 28 can be used with reasonable accuracy for many diffuser configura- tions. However, use caution when a diffuser configuration differs from the conditions used to derive these ERL values. Sound Radiation Through Duct Walls Duct Rumble. Duct rumble is low-frequency sound generated by vibration of a flat duct surface. The vibration is caused when an HVAC fan and its connected ductwork act as a semiclosed, com- pressible-fluid pumping system; both acoustic and aerodynamic air pressure fluctuations at the fan are transmitted to other locations in the duct system. Rumbling occurs at the duct's resonance frequen- cies (Ebbing et al. 1978), and duct rumble levels of 65 to 95 dB in the 16 to 100 Hz frequency range have been measured in occupied spaces. With belt-driven fans, the rumble sound level fluctuates ![image](/image/placeholder) WALL WALL AIR/SOUND PRESSURE AIR/SOUND PRESSURE FLUCTUATIONS FLUCTUATIONS VIBRATING ENTERING DUCT LEAVING DUCT DUCT WALLS SOUND POWER RADIATED FROM DUCT WALLS Fig. 24 Transmission of Rumble Noise Through Duct Walls above and below the mean dB level by 5 to 25 dB at a rate of2 to 10 "beats" per second (Blazier 1993). The most common beat fre- quency occurs at the difference between the fan rpm and twice the belt frequency (belt rpm = fan sheave diameter x sheave rpm x �/belt length). As shown in Figure 24, duct rumble is dependent on the level of duct vibration. The very low resonant frequencies at which duct rumble occurs means that the sound wavelengths are very long (3 to 20 m), and the rumble can exert sound energy over long distances. Low-mass architectural structures such as metal frame and drywall systems near a source of duct rumble can easily vibrate and rattle in sympathy to the rumble. Case histories indicate that duct vibration is much more preva- lent when there is a dramatic change in airflow direction near the fan, and at large, flat, unreinforced duct surfaces (usually greater than 1200 mm in any dimension) near the fan. Problems can occur with dimensions as small as 460 mm ifhigh noise levels are present. Figure 25 shows duct configurations near a centrifugal fan. Good to optimum designs of fan discharge transitions minimize potential for duct rumble; however, this may not completely eliminate the poten- tial for duct rumble, which also depends heavily on flow turbulence at the fan wheel, duct stiffness, air velocity in the duct, and duct res- onant characteristics. Duct liner, sound attenuators, and duct lagging with mass-loaded vinyl over fiberglass do not reduce duct rumble. One approach to eliminate or reduce rumble is to alter the fan or motor speed, which changes the frequency of air pressure fluctuations so that they differ from duct wall resonance frequencies. Another method is to apply rigid materials, such as duct reinforcements and drywall, directly to the duct wall to change the wall resonance frequencies (Figure 26). Noise reductions of 5 to 1 1 dB in the 31.5 and 63 Hz octave fre- quency bands are possible using this treatment. Mass-loaded materials applied in combination with absorptive materials do not alleviate duct rumble noise unless both materials are completely decoupled from the duct by a large air separation (pref- erably greater than 150 mm). The mass-loaded material should have a surface density greater than 20 kg/m2. An example of this type of construction, using two layers of drywall, is shown in Figure 27. Be- cause the treatment is decoupled from the duct wall, it provides the greatest noise reduction. Mass-loaded/absorptive material directly attached to a round duct can be an effective noise control treatment for high-frequency noise above the duct rumble frequency range of 16 to 100 Hz. In addition, the stiffness of round ductwork prevents flexure of the duct wall. Where space allows, round ductwork is an effective method to prevent duct rumble (Harold 1986). However, unless round ducts are used throughout the primary duct system, duct rumble can be still generated at a remote point where round duct is converted to rectangular or flat oval. ![image](/image/placeholder) NOTE 3 NOTE 1 NOTE 2 B NOTE 4 A A A A FLEX CONNECTOR B B 日 B OPTIMUM VERY GOOD GOOD FAIR BAD BAD Notes: 1. Slopes of 1 in 7 preferred. Slopes of 1 in 4 permitted below 10 m/s. 2. Dimension A should be at least 1.5 times B, where B is largest discharge duct dimension. 3. Rugged turning vanes should extend full radius of elbow. 4. Minimum 150 mm radius required. Fig. 25 Various Outlet Configurations for Centrifugal Fans and Their Possible Rumble Conditions Inc. ASHRAE, 2019 user. single for Licensed | {}
c641bee8-a5ea-47b3-a805-338810a1fdfe | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.29 Round ducts can have a resonant ring resonance frequency, which depends on duct material and diameter. The ring frequency is a res- onance frequency that occurs where the circumference of the duct is equal to the wavelength of the bending waves in the duct wall. On rare occasions, loud in-duct noise, such as blade-pass frequency noise from a centrifugal or axial fan, can excite this resonance. In all cases, this resonance causes an increase in radiated noise in the fre- quency region close to the ring frequency. Sound Breakout and Break-In from Ducts. Breakout is sound associated with fan or airflow noise inside a duct that radiates through duct walls into the surrounding area (Figure 28). Breakout can be a problem if it is not adequately attenuated before the duct runs over an occupied space (Cummings 1983; Lilly 1987). Sound that is transmitted into a duct from the surrounding area is called break-in (Figure 29). The main factors affecting breakout and break-in sound transmission are the transmission loss of the duct, total exposed surface area of the duct, and presence of any acousti- cal duct liner. Transmission loss (TL) is the ratio of sound power incident on a partition to the sound power transmitted through a partition. This ratio varies with acoustic frequency as well as duct shape, size, and wall thickness. Higher values of transmission loss result in less noise passing through the duct wall. Breakout sound transmission from ducts is the sound trans- mitted through a duct wall and then radiated from the exterior sur- face of the duct wall. Its sound power level is given by S Lw(out) = Lw(in) + 10log - TLout A where Lw(out) = sound power level of sound radiated from outer surface of duct walls, dB Lw(in) = sound power level of sound inside duct, dB ![image](/image/placeholder) STANDING DUCT SEAM REINFORCEMENT ANGLE (USUALLY 600 mm O.C.) . . SHEET METAL SCREWS HEAVY-GAGE WITH WASHER IN HEAD DUCT (USUALLY 450 mm O.C.) ADHESIVE 16 mm FIRE-RATED DRYWALL BUTT EDGES UP TO SEAMS AND REINFORCEMENTS Fig. 26 Drywall Lagging for Duct Rumble ![image](/image/placeholder) SEALANT METAL STUDS AND TWO LAYERS INSULATION OF DRYWALL BETWEEN DECOUPLED STUDS FROM DUCT Fig. 27 Decoupled Drywall Enclosure for Duct Rumble S = surface area of outer sound-radiating surface of duct, m2 A = cross-section area of inside of duct, m2 TLout = normalized duct breakout transmission loss (independent of s and A), dB Equation (13) is a simplified expression that assumes that the sound power level inside the duct does not decrease with distance over the length of the duct. In fact, for very long ducts (when S >> could become greater than A), the radiated sound power level Lw(out) the sound power level inside the duct, which would violate the con- servation of energy principle. A more accurate expression for break- out is presented in Equation (20). Values of TLout for rectangular ducts are given in Table 29, for round ducts in Table 30, and for flat oval ducts in Table 31 (Cum- mings 1983, 1985; Lilly 1987). Equations for S and A for rectangular ducts are S= 2L(a + b) A = ab where a = larger duct cross-section dimension, m b = smaller duct cross-section dimension, m L = length of duct sound-radiating surface, m (13) where Equations for S and A for round ducts are S= L d d2 A = 4 d = duct diameter, m (14) (15) (16) ![image](/image/placeholder) L Wt SOUND POWER W, Wi-W, DUCT ENTERING DUCT DUCT OUTER DUCT CROSS- SURFACE AREA SECTIONAL AREA A。 A, (17) Fig. 28 Breakout Noise Fig. ![image](/image/placeholder) Wi Wt DUCT 29 Break-In Noise Inc. ASHRAE, 2019 user. single for Licensed | {}
f53e1eff-1bb9-4576-890f-28281eb93d75 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.30 Table 29 TLout Versus Frequency for Rectangular Ducts ¦ Duct Size, mm ¦ Duct Size, mm ¦ Gage ¦ TLour dB Octave Midband Frequency, Hz ¦ TLour dB Octave Midband Frequency, Hz ¦ TLour dB Octave Midband Frequency, Hz ¦ TLour dB Octave Midband Frequency, Hz ¦ TLour dB Octave Midband Frequency, Hz ¦ TLour dB Octave Midband Frequency, Hz ¦ TLour dB Octave Midband Frequency, Hz ¦ TLour dB Octave Midband Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Duct Size, mm ¦ Duct Size, mm ¦ Gage ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ 8000 ¦ ¦ 305 ¦ 305 ¦ 24 ¦ 21 ¦ 24 ¦ 27 ¦ 30 ¦ 33 ¦ 36 ¦ 41 ¦ 45 ¦ ¦ 305 ¦ 610 ¦ 24 ¦ 19 ¦ 22 ¦ 25 ¦ 28 ¦ 31 ¦ 35 ¦ 41 ¦ 45 ¦ ¦ 305 ¦ 1220 ¦ 22 ¦ 19 ¦ 22 ¦ 25 ¦ 28 ¦ 31 ¦ 37 ¦ 43 ¦ 45 ¦ ¦ 610 ¦ 610 ¦ 22 ¦ 20 ¦ 23 ¦ 26 ¦ 29 ¦ 32 ¦ 37 ¦ 43 ¦ 45 ¦ ¦ 610 ¦ 1220 ¦ 20 ¦ 20 ¦ 23 ¦ 26 ¦ 29 ¦ 31 ¦ 39 ¦ 45 ¦ 45 ¦ ¦ 1220 ¦ 1220 ¦ 18 ¦ 21 ¦ 24 ¦ 27 ¦ 30 ¦ 35 ¦ 41 ¦ 45 ¦ 45 ¦ ¦ 1220 ¦ 2440 ¦ 18 ¦ 19 ¦ 22 ¦ 25 ¦ 29 ¦ 35 ¦ 41 ¦ 45 ¦ 45 ¦ Note: Data are for duct lengths of 6.1 m, but values may be used for cross section shown regardless of length. Table 30 Experimentally Measured TLout v ersus Frequency for Round Ducts ¦ Diameter, mm ¦ Length, m ¦ Gage ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Diameter, mm ¦ Length, m ¦ Gage ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ ¦ Long Seam Ducts ¦ Long Seam Ducts ¦ Long Seam Ducts ¦ Long Seam Ducts ¦ Long Seam Ducts ¦ Long Seam Ducts ¦ Long Seam Ducts ¦ Long Seam Ducts ¦ Long Seam Ducts ¦ Long Seam Ducts ¦ ¦ 200 ¦ 4.6 ¦ 26 ¦ >45 ¦ (53) ¦ 55 ¦ 52 ¦ 44 ¦ 35 ¦ 34 ¦ ¦ 350 ¦ 4.6 ¦ 24 ¦ >50 ¦ 60 ¦ 54 ¦ 36 ¦ 34 ¦ 31 ¦ 25 ¦ ¦ 560 ¦ 4.6 ¦ 22 ¦ >47 ¦ 53 ¦ 37 ¦ 33 ¦ 33 ¦ 27 ¦ 25 ¦ ¦ 810 ¦ 4.6 ¦ 22 ¦ (51) ¦ 46 ¦ 26 ¦ 26 ¦ 24 ¦ 22 ¦ 38 ¦ ¦ Spiral Wound Ducts ¦ Spiral Wound Ducts ¦ Spiral Wound Ducts ¦ Spiral Wound Ducts ¦ Spiral Wound Ducts ¦ Spiral Wound Ducts ¦ Spiral Wound Ducts ¦ Spiral Wound Ducts ¦ Spiral Wound Ducts ¦ Spiral Wound Ducts ¦ ¦ 300 ¦ 3.6 ¦ 26* ¦ 52 ¦ 51 ¦ 53 ¦ 51 ¦ 50 ¦ 46 ¦ 36 ¦ ¦ 610 ¦ 7.3 ¦ 24 ¦ 51 ¦ 53 ¦ 51 ¦ 44 ¦ 36 ¦ 26 ¦ 29 ¦ ¦ ¦ 7.3 ¦ 24* ¦ 51 ¦ 51 ¦ 54 ¦ 44 ¦ 39 ¦ 33 ¦ 47 ¦ ¦ ¦ 3 ¦ 16 ¦ >48 ¦ 53 ¦ 36 ¦ 32 ¦ 32 ¦ 28 ¦ 41 ¦ ¦ 915 ¦ 7.3 ¦ 20 ¦ 51 ¦ 51 ¦ 52 ¦ 46 ¦ 36 ¦ 32 ¦ 55 ¦ *Ducts internally lined with 25 mm thick 24 kg/m3 fiberglass with 0.6 mm perforated sheet metal inner liner. Table 31 TLout Versus Frequency for Flat Oval Ducts ¦ Duct Size, mm ¦ Gage ¦ TLout' dB Octave Midband Frequency, Hz ¦ TLout' dB Octave Midband Frequency, Hz ¦ TLout' dB Octave Midband Frequency, Hz ¦ TLout' dB Octave Midband Frequency, Hz ¦ TLout' dB Octave Midband Frequency, Hz ¦ TLout' dB Octave Midband Frequency, Hz ¦ TLout' dB Octave Midband Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Duct Size, mm ¦ Gage ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ ¦ 305 x 152 ¦ 24 ¦ 31 ¦ 34 ¦ 37 ¦ 40 ¦ 43 ¦ ¦ ¦ ¦ 610 x 152 ¦ 24 ¦ 24 ¦ 27 ¦ 30 ¦ 33 ¦ 36 ¦ ¦ ¦ ¦ 610 x 305 ¦ 24 ¦ 28 ¦ 31 ¦ 34 ¦ 37 ¦ ¦ ¦ ¦ ¦ 1220 X 305 ¦ 22 ¦ 23 ¦ 26 ¦ 29 ¦ 32 ¦ ¦ ¦ ¦ ¦ 1220 x 610 ¦ 22 ¦ 27 ¦ 30 ¦ 33 ¦ ¦ ¦ ¦ ¦ ¦ 2440 X 610 2440 x 1220 ¦ 20 18 ¦ 22 28 ¦ 25 31 ¦ 28 ¦ ¦ ¦ ¦ ¦ Note: Data are for duct lengths of 6.1 m, but values may be used for cross section shown regardless of length. L = length of duct sound-radiating surface, m For flat oval ducts, S= L[2(a -b) + b] b2 A= b(a-b)+ 4 where (18) a = length of major axis, m b = length of minor axis, m L = length of duct sound-radiating surface, m (19) Equation (13) assumes no decrease in the internal sound power level with distance along the length ofthe duct. Thus, itis valid only for relatively short lengths of unlined duct. For long ducts or ducts that have internal acoustic lining, one approach is to divide the duct into sections, each of which is short enough to be modeled as a 2019 ASHRAE Handbook- -HVAC Applications (SI) section of duct with constant internal sound power level over the length of each section. The recommended maximum length of each section is the length that would result in a 1 dB reduction in the in- ternal sound power level at the frequency of interest. Alternatively, the total sound power radiated from any duct of any length (includ- ing an internally lined duct) can be calculated in a single step with a modified version of Equation (13) (Lilly 1987): S* Lw(out) = Lw(in) + 10log - TLout A (20) where S* is the effective surface area of the duct. S* = PL*, where P = duct perimeter, and L* = effective length. The effective length L* is calculated as L 1 L* In where (21) = 10(- /10) where = duct attenuation rate, dB/m (see Tables 16 to 21). For lined rectangular ducts, Tables 17 and 18 do not have data at 63 Hz. For rough approximations, use Table 16 values. (22) In most rooms where the listener is close to the duct, an estimate of the breakout sound pressure level can be obtained from Lp = Lw(out) - 10log( rL) (23) where Lp = sound pressure level at a specified point in the space, dB Lw(out) = sound power level of sound radiated from outer surface of duct walls, given by Equation (13) or Equation (20), dB r = distance between duct and position for which Lp is calculated, m L = length of the duct sound-radiating surface, m Note that Equation (23) gives sound pressure from a duct that is in a wide-open ceiling plenum space. If the duct is in a tight space between floor slab and ceiling, it may be up to 6 dB louder. Example 4. A 610 mm by 610 mm by 7.5 m long rectangular supply duct is constructed of 0.75 mm sheet metal. Given the following sound power levels in the duct, what are the breakout sound pressure levels 1.5 m from the surface of the duct? Solution: Using Equations (13) and (23), ¦ ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ ¦ Lw(in) ¦ 90 ¦ 85 ¦ 80 ¦ 75 ¦ 70 ¦ 65 ¦ 60 ¦ ¦ -TLout (Table 29) ¦ -20 ¦ -23 ¦ -26 ¦ -29 ¦ -32 ¦ -37 ¦ - 43 ¦ ¦ 10 log(S/A) ¦ 17 ¦ 17 ¦ 17 ¦ 17 ¦ 17 ¦ 17 ¦ 17 ¦ ¦ Lw(out) ¦ 89 ¦ 79 ¦ 71 ¦ 63 ¦ 55 ¦ 45 ¦ 34 ¦ ¦ -10 log( rL) ¦ -16 ¦ -16 ¦ -16 ¦ -16 ¦ -16 ¦ -16 ¦ -16 ¦ ¦ Lp, dB ¦ 71 ¦ 62 ¦ 55 ¦ 47 ¦ 39 ¦ 29 ¦ 18 ¦ Using Equations (21) to (23), ¦ ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ ¦ Lw(in) ¦ 90 ¦ 85 ¦ 80 ¦ 75 ¦ 70 ¦ 65 ¦ 60 ¦ ¦ -TLout (Table 29) ¦ -20 ¦ -23 ¦ -26 ¦ -29 ¦ -32 ¦ -37 ¦ -43 ¦ ¦ , dB/m (Table 16) ¦ 0.82 ¦ 0.66 ¦ 0.33 ¦ 0.10 ¦ 0.10 ¦ 0.10 ¦ 0.10 ¦ ¦ ¦ 0.94 ¦ 0.95 ¦ 0.98 ¦ 0.99 ¦ 0.99 ¦ 0.99 ¦ 0.99 ¦ ¦ L*, m ¦ 4.0 ¦ 4.5 ¦ 5.7 ¦ 6.9 ¦ 6.9 ¦ 6.9 ¦ 6.9 ¦ ¦ 10 log(S*/A) ¦ 14 ¦ 15 ¦ 16 ¦ 17 ¦ 17 ¦ 17 ¦ 17 ¦ ¦ Lw(out) ¦ 84 ¦ 77 ¦ 70 ¦ 63 ¦ 55 ¦ 45 ¦ 34 ¦ ¦ -10 log( rL) ¦ -16 ¦ -16 ¦ -16 ¦ -16 ¦ -16 ¦ -16 ¦ -16 ¦ ¦ Lp, dB ¦ 68 ¦ 61 ¦ 54 ¦ 47 ¦ 39 ¦ 29 ¦ 18 ¦ Inc. ASHRAE, 2019 user. single for Licensed | {}
121d6fb0-abb0-4cd7-abaa-c8c789272f84 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.31 Example 5. Repeat Example 4, but with 50 mm thick internal duct liner. Solution: Using Equations (13) and (23), ¦ ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ ¦ ¦ Lw(in) ¦ 90 ¦ 85 ¦ 80 ¦ 75 ¦ 70 ¦ 65 ¦ 60 ¦ ¦ -TLout (Table 29) ¦ -20 ¦ -23 ¦ -26 ¦ -29 ¦ -32 ¦ -37 ¦ - 43 ¦ ¦ 10 log(S/A) ¦ 17 ¦ 17 ¦ 17 ¦ 17 ¦ 17 ¦ 17 ¦ 17 ¦ ¦ Lw(out) ¦ 87 ¦ 79 ¦ 71 ¦ 63 ¦ 55 ¦ 45 ¦ 34 ¦ ¦ -10 log( rL) ¦ -16 ¦ -16 ¦ -16 ¦ -16 ¦ -16 ¦ -16 ¦ -16 ¦ ¦ Lp, dB ¦ 71 ¦ 63 ¦ 55 ¦ 47 ¦ 39 ¦ 29 ¦ 18 ¦ Using Equations (21) to (23), ¦ ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ ¦ Lw(in) ¦ 90 ¦ 85 ¦ 80 ¦ 75 ¦ 70 ¦ 65 ¦ 60 ¦ ¦ -TLout (Table 29) ¦ -20 ¦ -23 ¦ -26 ¦ -29 ¦ -32 ¦ -37 ¦ -43 ¦ ¦ , dB/m (Table 18) ¦ 0.5 ¦ 1.0 ¦ 3.0 ¦ 8.2 ¦ 11.5 ¦ 7.2 ¦ 5.9 ¦ ¦ ¦ 0.94 ¦ 0.93 ¦ 0.81 ¦ 0.56 ¦ 0.45 ¦ 0.60 ¦ 0.66 ¦ ¦ L*, m ¦ 5.0 ¦ 3.6 ¦ 1.4 ¦ 0.5 ¦ 0.4 ¦ 0.6 ¦ 0.7 ¦ ¦ 10 log(S*/A) ¦ 14 ¦ 14 ¦ 10 ¦ 5 ¦ 4 ¦ 6 ¦ 7 ¦ ¦ Lw(out) ¦ 84 ¦ 76 ¦ 64 ¦ 51 ¦ 42 ¦ 34 ¦ 24 ¦ ¦ -10 log( rL) ¦ -16 ¦ -16 ¦ -16 ¦ -16 ¦ -16 ¦ -16 ¦ -16 ¦ ¦ Lp, dB ¦ 68 ¦ 60 ¦ 48 ¦ 35 ¦ 26 ¦ 18 ¦ 8 ¦ Example 6. Repeat Example 5 using 610 mm diameter spiral round duct, 0.6 mm thick, 7.6 m long with 25 mm thick acoustical duct lining. Solution: Using Equations (21) and (23), ¦ ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ ¦ Lw(in) ¦ 90 ¦ 85 ¦ 80 ¦ 75 ¦ 70 ¦ 65 ¦ 60 ¦ ¦ -TLout (Table 30) ¦ -51 ¦ -51 ¦ -54 ¦ 44 ¦ -39 ¦ -33 ¦ - 47 ¦ ¦ 10 log (S/A) ¦ 17 ¦ 17 ¦ 17 ¦ 17 ¦ 17 ¦ 17 ¦ 17 ¦ ¦ Lw(out) ¦ 56 ¦ 51 ¦ 43 ¦ 48 ¦ 48 ¦ 49 ¦ 30 ¦ ¦ -10 log( rL) ¦ -16 ¦ -16 ¦ -16 ¦ -16 ¦ -16 ¦ -16 ¦ -16 ¦ ¦ Lp, dB ¦ 40 ¦ 35 ¦ 27 ¦ 32 ¦ 32 ¦ 33 ¦ 14 ¦ Using Equations (21) to (23) yields Octave Midband Frequency, Hz ¦ ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Lw(in) ¦ 90 ¦ 85 ¦ 80 ¦ 75 ¦ 70 ¦ 65 ¦ 60 ¦ ¦ -TL out (Table 30) ¦ -51 ¦ -51 ¦ -54 ¦ -44 ¦ -39 ¦ -33 ¦ -47 ¦ ¦ , dB/m (Table 20) ¦ 0.23 ¦ 0.82 ¦ 1.87 ¦ 4.2 ¦ 5.61 ¦ 4.07 ¦ 2.79 ¦ ¦ ¦ 0.98 ¦ 0.94 ¦ 0.88 ¦ 0.74 ¦ 0.67 ¦ 0.75 ¦ 0.82 ¦ ¦ L*, m ¦ 6.2 ¦ 4.0 ¦ 2.2 ¦ 1.0 ¦ 0.8 ¦ 1.1 ¦ 1.5 ¦ ¦ 10 log (S*/A) ¦ 16 ¦ 14 ¦ 12 ¦ 8.3 ¦ 7.1 ¦ 8.5 ¦ 10 ¦ ¦ Lw(out) ¦ 55 ¦ 48 ¦ 38 ¦ 39 ¦ 38 ¦ 40 ¦ 23 ¦ ¦ -10 log( rL) ¦ -16 ¦ -16 ¦ -16 ¦ -16 ¦ -16 ¦ -16 ¦ -16 ¦ ¦ Lp, dB ¦ 39 ¦ 32 ¦ 22 ¦ 24 ¦ 22 ¦ 25 ¦ 7 ¦ Using round duct eliminates the low-frequency rumble present with rectangular ducts but introduces some mid- and high- frequency noise that can be reduced by adding duct liner as shown. When sound is not transmitted through the wall of a round duct, it propagates down the duct and may become a problem at another point in the duct system. Round flexible and rigid fiberglass ducts do not have high transmission loss properties because they lack the mass or stiffness associated with round sheet metal ducts. Whenever duct sound breakout is a concern, fiberglass or flexible round duct should not be used; these ducts have little or no trans- mission loss, and are essentially transparent to sound. Table 32 Experimentally Measured TLin Versus Frequency for Circular Ducts ¦ Diameter, mm ¦ Length, m ¦ Gage ¦ TLin, dB Octave Midband Frequency, Hz ¦ TLin, dB Octave Midband Frequency, Hz ¦ TLin, dB Octave Midband Frequency, Hz ¦ TLin, dB Octave Midband Frequency, Hz ¦ TLin, dB Octave Midband Frequency, Hz ¦ TLin, dB Octave Midband Frequency, Hz ¦ TLin, dB Octave Midband Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Diameter, mm ¦ Length, m ¦ Gage ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ ¦ Long Seam Ducts ¦ Long Seam Ducts ¦ Long Seam Ducts ¦ Long Seam Ducts ¦ Long Seam Ducts ¦ Long Seam Ducts ¦ Long Seam Ducts ¦ Long Seam Ducts ¦ Long Seam Ducts ¦ Long Seam Ducts ¦ ¦ 203 ¦ 4.57 ¦ 26 ¦ >17 ¦ (31) ¦ 39 ¦ 42 ¦ 41 ¦ 32 ¦ 31 ¦ ¦ 356 ¦ 4.57 ¦ 24 ¦ >27 ¦ 43 ¦ 43 ¦ 31 ¦ 31 ¦ 28 ¦ 22 ¦ ¦ 559 ¦ 4.57 ¦ 22 ¦ >28 ¦ 40 ¦ 30 ¦ 30 ¦ 30 ¦ 24 ¦ 22 ¦ ¦ 813 ¦ 4.57 ¦ 22 ¦ (35) ¦ 36 ¦ 23 ¦ 23 ¦ 21 ¦ 19 ¦ 35 ¦ ¦ Spiral Wound Ducts ¦ Spiral Wound Ducts ¦ Spiral Wound Ducts ¦ Spiral Wound Ducts ¦ Spiral Wound Ducts ¦ Spiral Wound Ducts ¦ Spiral Wound Ducts ¦ Spiral Wound Ducts ¦ Spiral Wound Ducts ¦ Spiral Wound Ducts ¦ ¦ 203 ¦ 3.05 ¦ 26 ¦ >20 ¦ >42 ¦ >59 ¦ >62 ¦ 53 ¦ 43 ¦ 26 ¦ ¦ 356 ¦ 3.05 ¦ 26 ¦ >20 ¦ >36 ¦ 44 ¦ 28 ¦ 31 ¦ 32 ¦ 22 ¦ ¦ 660 ¦ 3.05 ¦ 24 ¦ >27 ¦ 38 ¦ 20 ¦ 23 ¦ 22 ¦ 19 ¦ 33 ¦ ¦ 660 ¦ 3.05 ¦ 16 ¦ >30 ¦ >41 ¦ 30 ¦ 29 ¦ 29 ¦ 25 ¦ 38 ¦ ¦ 813 ¦ 3.05 ¦ 22 ¦ >27 ¦ 32 ¦ 25 ¦ 22 ¦ 23 ¦ 21 ¦ 37 ¦ Note: In cases where background sound swamped sound radiated from duct walls, a lower limit on TLin is indicated by >. Parentheses indicate measurements in which background sound produced greater uncertainty than usual. Table 33 TLin Versus Frequency for Rectangular Ducts ¦ Duct Size, mm ¦ Duct Size, mm ¦ Gage ¦ TLim dB Octave Midband Frequency, Hz ¦ TLim dB Octave Midband Frequency, Hz ¦ TLim dB Octave Midband Frequency, Hz ¦ TLim dB Octave Midband Frequency, Hz ¦ TLim dB Octave Midband Frequency, Hz ¦ TLim dB Octave Midband Frequency, Hz ¦ TLim dB Octave Midband Frequency, Hz ¦ TLim dB Octave Midband Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Duct Size, mm ¦ Duct Size, mm ¦ Gage ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ 8000 ¦ ¦ 305 ¦ 305 ¦ 24 ¦ 16 ¦ 16 ¦ 16 ¦ 25 ¦ 30 ¦ 33 ¦ 38 ¦ 42 ¦ ¦ 305 ¦ 610 ¦ 24 ¦ 15 ¦ 15 ¦ 17 ¦ 25 ¦ 28 ¦ 32 ¦ 38 ¦ 42 ¦ ¦ 305 ¦ 1220 ¦ 22 ¦ 14 ¦ 14 ¦ 22 ¦ 25 ¦ 28 ¦ 34 ¦ 40 ¦ 42 ¦ ¦ 610 ¦ 610 ¦ 22 ¦ 13 ¦ 13 ¦ 21 ¦ 26 ¦ 29 ¦ 34 ¦ 40 ¦ 42 ¦ ¦ 610 ¦ 1220 ¦ 20 ¦ 12 ¦ 15 ¦ 23 ¦ 26 ¦ 28 ¦ 36 ¦ 42 ¦ 42 ¦ ¦ 1220 ¦ 1220 ¦ 18 ¦ 10 ¦ 19 ¦ 24 ¦ 27 ¦ 32 ¦ 38 ¦ 42 ¦ 42 ¦ ¦ 1220 ¦ 2440 ¦ 18 ¦ 11 ¦ 19 ¦ 22 ¦ 26 ¦ 32 ¦ 38 ¦ 42 ¦ 42 ¦ Note: Data are for duct lengths of 6.1 m. Table 34 TLin Versus Frequency for Flat Oval Ducts ¦ ¦ ¦ TLin' dB Octave Midband Frequency, Hz ¦ TLin' dB Octave Midband Frequency, Hz ¦ TLin' dB Octave Midband Frequency, Hz ¦ TLin' dB Octave Midband Frequency, Hz ¦ TLin' dB Octave Midband Frequency, Hz ¦ TLin' dB Octave Midband Frequency, Hz ¦ TLin' dB Octave Midband Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Duct Size, mm ¦ Gage ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ ¦ 305 x 152 ¦ 24 ¦ 18 ¦ 18 ¦ 22 ¦ 31 ¦ 40 ¦ ¦ ¦ ¦ 610 x 152 ¦ 24 ¦ 17 ¦ 17 ¦ 18 ¦ 30 ¦ 33 ¦ ¦ ¦ ¦ 610 x 305 ¦ 24 ¦ 15 ¦ 16 ¦ 25 ¦ 34 ¦ ¦ ¦ ¦ ¦ 1220 X 305 ¦ 22 ¦ 14 ¦ 14 ¦ 26 ¦ 29 ¦ ¦ ¦ ¦ ¦ 1220 X 610 ¦ 22 ¦ 12 ¦ 21 ¦ 30 ¦ ¦ ¦ ¦ ¦ ¦ 2440 X 610 ¦ 20 ¦ 11 ¦ 22 ¦ 25 ¦ ¦ ¦ ¦ ¦ ¦ 2440 X 1220 ¦ 18 ¦ 19 ¦ 28 ¦ ¦ ¦ ¦ ¦ ¦ Note: Data are for duct lengths of 6.1 m. Break-in sound transmission into ducts is sound transmitted into a duct through the duct walls from the space outside the duct. Its sound power level is given by Lw(in) = Lw(out) - TLin 3 where Lw(in) = sound power level of sound transmitted into duct and then transmitted upstream or downstream of point of entry, dB Lw(out) = sound power level of sound incident on outside of duct walls, dB TLin = duct break-in transmission loss, dB Values for TLin for rectangular ducts are given in Table 32, for round ducts in Table 33, and for flat oval ducts in Table 34 (Cum- mings 1983, 1985). (24) Inc. ASHRAE, 2019 user. single for Licensed | {}
8e711b6f-da25-45ae-9300-25c2e55b541a | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.32 Table 34 TLin Versus Frequency for Flat Oval Ducts ¦ Duct Size, mm ¦ Gage ¦ TLin, dB Octave Midband Frequency, Hz ¦ TLin, dB Octave Midband Frequency, Hz ¦ TLin, dB Octave Midband Frequency, Hz ¦ TLin, dB Octave Midband Frequency, Hz ¦ TLin, dB Octave Midband Frequency, Hz ¦ TLin, dB Octave Midband Frequency, Hz ¦ TLin, dB Octave Midband Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Duct Size, mm ¦ Gage ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ ¦ 305 X 152 ¦ 24 ¦ 18 ¦ 18 ¦ 22 ¦ 31 ¦ 40 ¦ ¦ ¦ ¦ 610 x 152 ¦ 24 ¦ 17 ¦ 17 ¦ 18 ¦ 30 ¦ 33 ¦ ¦ ¦ ¦ 610 X 305 ¦ 24 ¦ 15 ¦ 16 ¦ 25 ¦ 34 ¦ ¦ ¦ ¦ ¦ 1220 x 305 ¦ 22 ¦ 14 ¦ 14 ¦ 26 ¦ 29 ¦ ¦ ¦ ¦ ¦ 1220 x 610 ¦ 22 ¦ 12 ¦ 21 ¦ 30 ¦ ¦ ¦ ¦ ¦ ¦ 2440 x 610 ¦ 20 ¦ 11 ¦ 22 ¦ 25 ¦ ¦ ¦ ¦ ¦ ¦ 2440 x 1220 ¦ 18 ¦ 19 ¦ 28 ¦ ¦ ¦ ¦ ¦ ¦ Note: Data are for duct lengths of6.1 m. 2.5 RECEIVER ROOM SOUND CORRECTION The sound pressure level at a given location in a room caused by a particular sound source is a function of the sound power level and sound radiation characteristics of the sound source, acoustic prop- erties of the room (surface treatments, furnishings, etc.), room volume, and distance between the sound source and point of observation. Two types of sound sources are typically encountered in HVAC system applications: point and line. Typical point sources are grilles, registers, and diffusers; air-valve and fan-powered air terminal units and fan-coil units located in ceiling plenums; and return air openings. Line sources are usually associated with sound breakout from air ducts and long slot diffusers. For a point source in an enclosed space, classical diffuse-field theory predicts that as the distance between the source and point of observation is increased, the sound pressure level initially decreases at the rate of 6 dB per doubling of distance. At some point, the rever- berant sound field begins to dominate and the sound pressure level remains at a constant level. For point sound sources in reflective unfurnished rooms, the classic diffuse equation for converting sound power to pressure could be used: Lp = Lw+ 10 log(Q/4�r2 + 4/R) where (25) Lp = sound pressure level, dB (re 20 �Pa) Lw = sound power level, dB (re 10-12 W) 0 = directivity of sound source, dimensionless; see Figure 30 r = distance from source, m R = room constant = [S�/(1 - �)] - sum of all surface areas and their corresponding absorption coefficients, m2 Inc. ASHRAE, 2019 user. single for Licensed A further discussion of assumptions used in converting power to pressure is available in Chapter 8 ofthe 2017 ASHRAE Handbook Fundamentals. However, investigators have found that diffuse-field theory does not apply in rooms with furniture or other sound-scattering objects (Schultz 1985; Thompson 1981). Instead, sound pressure levels decrease at the rate of around 3 dB per doubling of distance between sound source and point of observation. Generally, a true reverberant sound field does not exist in small rooms (room volumes less than 425 m3). In larger rooms reverberant fields usually exist, but typi- cally at distances from the sound sources that are significantly greater than those predicted by diffuse-field theory. Most normally furnished rooms of regular proportions have acoustic characteristics that range from average to medium dead. These usually include carpeted rooms with sound-absorptive ceil- ings. If such a room has a volume less than 425 m3 and the sound source is a single point source, sound pressure levels associated with the sound source can be obtained from (Schultz 1985). Lp = Lw - 10 log r - 5 log V - 3 log f+ 12 2019 ASHRAE Handbook- - HVAC Applications (SI) (26) or Lp = Lw+ A - B (27) where Lp = sound pressure level at specified distance from sound source, dB (re 20 �Pa) Lw = sound power level of sound source, dB (re 10-12 W) r = distance from source to receiver, m V = volume of room, m3 f = frequency Values for A and B are given in Tables 35 and 36. In an alternative calculation for a normally furnished room with volume greater than 425 m3 and a single-point sound source, sound pressure levels associated with the sound source can be obtained from Lp = Lw - C -5 (28) Values for C are given in Table 37. Equation (28) can be used for room volumes of up to 4250 m3, with accuracy typically within 2 to 5 dB. Distributed Array of Ceiling Sound Sources In many office buildings, air supply outlets are located flush with the ceiling of the conditioned space and constitute an array of distributed ceiling sound sources. The geometric pattern depends on the floor area served by each outlet, ceiling height, and thermal load distribution. In interior zones of a building where thermal load requirements are essentially uniform, air delivery per outlet is usu- ally the same throughout the space; thus, these outlets emit nomi- nally equal sound power levels. One way to calculate sound pressure levels in a room with a distributed array is to use Equation (26), (27), or (28) to calculate the sound pressure levels for each individual air outlet at specified locations in the room and then logarithmically add the sound pressure levels for each diffuser at each observation point. This procedure can be very tedious for a room with a large number of ceiling air outlets. For a distributed array of ceiling sound sources (air outlets) of nominally equal sound power, room sound pressure levels tend to be ![image](/image/placeholder) UNIFORM SPHERICAL UNIFORM HEMISPHERICAL RADIATION, NO RADIATION, SINGLE REFLECTING SURFACES REFLECTING SURFACE Q = 1 Q =2 UNIFORM RADIATION UNIFORM RADIATION OVER 1/4 OF A OVER 1/8 OF A SPHERE, SPHERE, LARGE SOURCE, TWO REFLECTING THREE REFLECTING Q MAY VARY SURFACES SURFACES WITH DIRECTION Q=4 Q =8 Fig. 30 Directivity Factors for v arious Radiation Patterns | {}
63982424-d8ec-40c3-8f1d-c747975bf7d4 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.33 Table 35 Values for A in Equation (26) ¦ Room v olume, m3 ¦ Value for A, dB Octave Midband Frequency, Hz ¦ Value for A, dB Octave Midband Frequency, Hz ¦ Value for A, dB Octave Midband Frequency, Hz ¦ Value for A, dB Octave Midband Frequency, Hz ¦ Value for A, dB Octave Midband Frequency, Hz ¦ Value for A, dB Octave Midband Frequency, Hz ¦ Value for A, dB Octave Midband Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Room v olume, m3 ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ ¦ 42 ¦ 4 ¦ 3 ¦ 2 ¦ 1 ¦ 0 ¦ -1 ¦ -2 ¦ ¦ 71 ¦ 3 ¦ 2 ¦ 1 ¦ 0 ¦ -1 ¦ -2 ¦ -3 ¦ ¦ 113 ¦ 2 ¦ 1 ¦ 0 ¦ -1 ¦ -2 ¦ -3 ¦ -4 ¦ ¦ 170 ¦ 1 ¦ 0 ¦ -1 ¦ -2 ¦ -3 ¦ -4 ¦ -5 ¦ ¦ 283 ¦ 0 ¦ -1 ¦ -2 ¦ -3 ¦ -4 ¦ -5 ¦ -6 ¦ ¦ 425 ¦ -1 ¦ -2 ¦ -3 ¦ 4 ¦ -5 ¦ -6 ¦ - 7 ¦ Table 36 Values for B in Equation (26) ¦ Distance from Sound Source, m ¦ Value for B, dB ¦ ¦ --- ¦ --- ¦ ¦ 0.9 ¦ 5 ¦ ¦ 1.2 ¦ 6 ¦ ¦ 1.5 ¦ 7 ¦ ¦ 1.8 ¦ 8 ¦ ¦ 2.4 ¦ 9 ¦ ¦ 3.0 ¦ 10 ¦ ¦ 4.0 ¦ 11 ¦ ¦ 4.9 ¦ 12 ¦ ¦ 6.1 ¦ 13 ¦ uniform in a plane parallel to the ceiling. Although sound pressure levels decrease with distance from the ceiling along a vertical axis, they are nominally constant along any selected horizontal plane. Equation (29) simplifies calculation for a distributed ceiling array. For this case, use a reference plane 1.5 m above the floor. Thus, Lp(1.5) is obtained from Lp(1.5) = Lw(s) - D where Lp(1.5) = sound pressure level at distance of 1.5 m above floor, dB (re 20 Pa) Lw(s) = sound power level of single diffuser in array, dB (re 10-12 W) Values of D are given in Table 38. Nonstandard Rooms The previous equations assume that the acoustical characteristics of a room range from average to medium dead, which is generally true of most rooms. However, some rooms may be acoustically medium live to live (i.e., they have little sound absorption). These rooms may be sports or athletic areas, concert halls, or other rooms designed to be live, or they may be rooms that are improperly designed from an acoustic standpoint. The previous equations should not be used for acoustically live rooms because they can overestimate the decrease in sound pressure levels associated with room sound correction by as much as 10 to 15 dB. When these or other types of nonstandard rooms are encountered, it is best to use the services of an acoustical engineer. Line Sound Sources Sound from breakout from air ducts or long slot diffusers may be modeled as line sources. To convert sound power levels to the corresponding sound pressure levels in a room for such cases, the following equation may be used: Lp =Lw + 10 log(⌀/ rL + 4/R) where レp sound pressure level, dB (re 20 Pa) sound Lw power level, dB (re 10-12 W) Table 37 Values for C in Equation (28) ¦ Distance from Sound Source, m ¦ Value for C, dB Octave Midband Frequency, Hz ¦ Value for C, dB Octave Midband Frequency, Hz ¦ Value for C, dB Octave Midband Frequency, Hz ¦ Value for C, dB Octave Midband Frequency, Hz ¦ Value for C, dB Octave Midband Frequency, Hz ¦ Value for C, dB Octave Midband Frequency, Hz ¦ Value for C, dB Octave Midband Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Distance from Sound Source, m ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ ¦ 0.9 ¦ 5 ¦ 5 ¦ 6 ¦ 6 ¦ 6 ¦ 7 ¦ 10 ¦ ¦ 1.2 ¦ 6 ¦ 7 ¦ 7 ¦ 7 ¦ 8 ¦ 9 ¦ 12 ¦ ¦ 1.5 ¦ 7 ¦ 8 ¦ 8 ¦ 8 ¦ 9 ¦ 11 ¦ 14 ¦ ¦ 1.8 ¦ 8 ¦ 9 ¦ 9 ¦ 9 ¦ 10 ¦ 12 ¦ 16 ¦ ¦ 2.4 ¦ 9 ¦ 10 ¦ 10 ¦ 11 ¦ 12 ¦ 14 ¦ 18 ¦ ¦ 3.0 ¦ 10 ¦ 11 ¦ 12 ¦ 12 ¦ 13 ¦ 16 ¦ 20 ¦ ¦ 4.0 ¦ 11 ¦ 12 ¦ 13 ¦ 13 ¦ 15 ¦ 18 ¦ 22 ¦ ¦ 4.9 ¦ 12 ¦ 13 ¦ 14 ¦ 15 ¦ 16 ¦ 19 ¦ 24 ¦ ¦ 6.1 ¦ 13 ¦ 15 ¦ 15 ¦ 16 ¦ 17 ¦ 20 ¦ 26 ¦ ¦ 7.6 ¦ 14 ¦ 16 ¦ 16 ¦ 17 ¦ 19 ¦ 22 ¦ 28 ¦ ¦ 9.8 ¦ 15 ¦ 17 ¦ 17 ¦ 18 ¦ 20 ¦ 23 ¦ 30 ¦ (29) Table 38 Values for D in Equation (29) ¦ Floor Area per Diffuser, m2 ¦ Value for D, dB Octave Midband Frequency, Hz ¦ Value for D, dB Octave Midband Frequency, Hz ¦ Value for D, dB Octave Midband Frequency, Hz ¦ Value for D, dB Octave Midband Frequency, Hz ¦ Value for D, dB Octave Midband Frequency, Hz ¦ Value for D, dB Octave Midband Frequency, Hz ¦ Value for D, dB Octave Midband Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Floor Area per Diffuser, m2 ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ ¦ Ceiling height 2.4 to 2.7 m ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 9.3 to 14 ¦ 2 ¦ 3 ¦ 4 ¦ 5 ¦ 6 ¦ 7 ¦ 8 ¦ ¦ 18.5 to 23 ¦ 3 ¦ 4 ¦ 5 ¦ 6 ¦ 7 ¦ 8 ¦ 9 ¦ ¦ Ceiling height 3.0 to 3.7 m ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 14 to 18.5 ¦ 4 ¦ 5 ¦ 6 ¦ 7 ¦ 8 ¦ 9 ¦ 10 ¦ ¦ 23 to 28 ¦ 5 ¦ 6 ¦ 7 ¦ 8 ¦ 9 ¦ 10 ¦ 11 ¦ ¦ Ceiling height 4.3 to 4.9 m ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 23 to 28 ¦ 7 ¦ 8 ¦ 9 ¦ 10 ¦ 11 ¦ 12 ¦ 13 ¦ ¦ 32.5 to 37 ¦ 8 ¦ 9 ¦ 10 ¦ 11 ¦ 12 ¦ 13 ¦ 14 ¦ 0 = 1 ifline source is away from reflecting surfaces; 2 ifline source is near a flat reflective surface. r = distance from source, m L = length of line source, m R = room constant = [S /(1 - )] = sum of all surface areas and their corresponding absorption coefficients, m2 This is the classic diffuse room equation for a line source, and may not produce accurate results for standard nondiffuse rooms. Unfortunately, no information is available at this time on how to cor- rect more accurately for the effect of the receiver room on line sources. Room Noise Measurement Measuring HVAC system noise in a room is complicated by sev- eral factors, including the spatial and temporal variability of the noise, variable HVAC system operating conditions, modal charac- teristics of the room, and intrusion of noise from exterior sources. How noise measurements should be taken depends to some extent on the purpose of the measurement. Is the purpose of the measure- ment to verify that the noise level in the room meets a specific cri- teria, or is it meant to troubleshoot an alleged problem? The specific measurement requirements vary depending on the intent. (30) Inc. ASHRAE, 2019 user. single for Licensed For commissioning purposes, there are two levels of assessment: (1) a survey method may be used to make a quick assessment of a space and (2) an engineering method for a more detailed and accu- rate assessment. The survey approach is typically used to assess whether there may be a noise problem in the room. This method re- quires a Type 1 integrating sound level meter equipped with octave band filters if octave band levels are specified by the applicable noise criterion. Measurements can be taken at a single point or at several points, but all measurement points must be at a likely loca- | {}
4f6a0008-4ce1-4e9a-aa9c-3a88d836079c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.34 2019 ASHRAE Handbook- -HVAC Applications (SI) tion for the listener's ears. No measurement locations may be less than 1 m from a room boundary or less than 0.5 m from any object in the room. The measurement microphone must be fixed (or slowly moving) for each measurement, and the minimum duration of each measurement is 15 s. It is recognized that HVAC noise is a time- varying signal, so the energy average sound pressure level Leq must be compared against the noise criterion, not the maximum sound level recorded during the measurement. Ifthe survey method detects a potential noise problem or ifa com- plaint has been registered by an occupant of the space, the engineer- ing method may be implemented if compliance with a noise level specification is required. This method uses the same instrumentation but requires a minimum of four separate measurement locations, uniformly distributed throughout the room. For larger rooms (greater than 20 m2), additional measurement points must be added, propor- tional to the floor area of the room. Unless specified otherwise, the energy average Leq of all measurement locations in the room is com- pared against the noise criterion. If the purpose of the noise measurement is troubleshooting a known problem, more sophisticated instrumentation (e.g., nar- row band analyzers, vibration sensors, intensity probes) may be required. Troubleshooting work should be provided by a compe- tent acoustical consultant with specific experience in this field of work. Contact the Institute of Noise Control Engineering (www .inceusa.org) or the National Council of Acoustical Consultants (www.ncac.com) for a list of experts. In any case, it is important for the operating conditions of the HVAC system to be known at the time of the measurements. If the system contains compressors that cycle on and off during normal operation, the measurements must be taken while the compressors are running. For variable-volume systems, the measurements should be taken at design (maximum) volume. If the condition rarely operates under design flow conditions, measurements must also be taken at a more typical operating condition. Itis also important to make sure that noise from extraneous (non- HVAC) sources does not contaminate the measurements. Room noise measurements may be corrected for these sounds by taking one set of measurements with the HV AC system operating under test conditions and additional measurements with the HV AC sys- tem shut down entirely. This correction can only be applied if the ambient noise is shown to be relatively constant with time. If the energy average of two independent ambient noise level measure- ments (one obtained before and the other obtained after the HVAC system noise measurement) is more than 6 dB below the HVAC noise level in any octave band, then the ambient adjusted HVAC noise level in that octave band may be computed using the following equation: Lp ambient adjusted = 10 log 10 (Lp HVAC/ 10) (Lp ambient/ 10) - 10 Inc. ASHRAE, 2019 user. single for Licensed where Lp HVAC = sound pressure level with HVAC system operating Lp ambient energy average ambient sound pressure level with HVAC = system off The ambient noise correction cannot be allowed if the difference between the two ambient noise levels in any frequency band is more than 3 dB. If this occurs, the ambient noise is not constant with time and the entire set of measurements should be repeated. Remember that that the ambient noise correction is not required if the ambient is at least 10 dB quieter than with the HVAC on. For more information, see the section on Troubleshooting. Chart Title: Noise Barrier Chart Type: line A B SOURCE A + B-D D INSURANCE R E L item_01 0.3Not explicitly visible 1.6Not explicitly visible 2.8Not explicitly visible 0.4Not explicitly visible 1.6Not explicitly visible 0.9Not explicitly visible 3.2Not explicitly visible 2.7Not explicitly visible 2.0Not explicitly visible 2.6 SOUND CONTROL FOR OUTDOOR EQUIPMENT Outdoor mechanical equipment should be carefully selected, installed, and maintained to minimize sound radiated by the equip- ment, and to comply with local noise codes. Equipment with strong tonal components is more likely to provoke complaints than equip- ment with a broadband noise spectrum. Sound Propagation Outdoors Ifthe equipment sound power level spectrum and ambient sound pressure level spectrum are known, the contribution of the equip- ment to the sound level at any location can be estimated by analyz- ing the sound transmission paths involved. When there are no intervening barriers and no attenuation because of berms, ground absorption, or atmospheric effects, the principal factor in sound pressure level reduction is distance. The following equation may be used to estimate the sound pressure level of equipment at a distance from it and at any frequency when the sound power level is known: Lp = Lw + 10 log 0 - 20 logd - 11 (31) where d = distance from acoustic center of source to distant point, m sound pressure level at distance d from sound source, dB p L sound power level of sound source, dB W 0 directivity factor associated with way sound radiates from sound source (see Figure 30) Equation (31) does not apply where d is less than twice the max- imum dimension of the sound source. Lp may be low by up to 5 dB where d is between two and five times the maximum sound source dimension. Also, if the distance is greater than about 150 m, wind, thermal gradients, and atmospheric sound absorption need to be considered. For complex cases, refer to texts on acoustics (e.g., Beranek 1971) and international standards such as ISO Standard 9613-2. Sound Barriers A sound barrier is a solid structure that intercepts the direct sound path from a sound source to a receiver. It reduces the sound pressure level within its shadow zone. Figure 31 shows the geomet- | {}
1ff33694-f993-4383-95d2-6461eeeca7d8 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.35 Table 39 Insertion Loss Values of Ideal Solid Barrier ¦ Path-Length Difference, m ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ Insertion Loss, dB Octave Midband Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Path-Length Difference, m ¦ 31 ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ ¦ 0.003 ¦ 5 ¦ 5 ¦ 5 ¦ 5 ¦ 5 ¦ 6 ¦ 7 ¦ 8 ¦ ¦ 0.006 ¦ 5 ¦ 5 ¦ 5 ¦ 5 ¦ 5 ¦ 6 ¦ 8 ¦ 9 ¦ ¦ 0.015 ¦ 5 ¦ 5 ¦ 5 ¦ 5 ¦ 6 ¦ 7 ¦ 9 ¦ 10 ¦ ¦ 0.03 ¦ 5 ¦ 5 ¦ 5 ¦ 6 ¦ 7 ¦ 9 ¦ 11 ¦ 13 ¦ ¦ 0.06 ¦ 5 ¦ 5 ¦ 6 ¦ 8 ¦ 9 ¦ 11 ¦ 13 ¦ 16 ¦ ¦ 0.15 ¦ 6 ¦ 7 ¦ 9 ¦ 10 ¦ 12 ¦ 15 ¦ 18 ¦ 20 ¦ ¦ 0.3 ¦ 7 ¦ 8 ¦ 10 ¦ 12 ¦ 14 ¦ 17 ¦ 20 ¦ 22 ¦ ¦ 0.6 ¦ 8 ¦ 10 ¦ 12 ¦ 14 ¦ 17 ¦ 20 ¦ 22 ¦ 23 ¦ ¦ 1.5 ¦ 10 ¦ 12 ¦ 14 ¦ 17 ¦ 20 ¦ 22 ¦ 23 ¦ 24 ¦ ¦ 3.0 ¦ 12 ¦ 15 ¦ 17 ¦ 20 ¦ 22 ¦ 23 ¦ 24 ¦ 24 ¦ ¦ 6.1 ¦ 15 ¦ 18 ¦ 20 ¦ 22 ¦ 23 ¦ 24 ¦ 24 ¦ 24 ¦ ¦ 15.2 ¦ 18 ¦ 20 ¦ 23 ¦ 24 ¦ 24 ¦ 24 ¦ 24 ¦ 24 ¦ rical aspects of an outdoor barrier where no extraneous surfaces reflect sound into the protected area. Here the barrier is treated as an intentionally constructed noise control structure. If a sound barrier is placed between a sound source and receiver location, the sound pressure level Lp in Equation (26) is reduced by the insertion loss (IL) associated with the barrier. Table 39 gives the insertion loss of an outdoor ideal solid barrier when no surfaces reflect sound into the shadow zone, and the sound transmission loss of the barrier wall or structure is at least 10 dB greater at all frequencies than the insertion loss expected of the bar- rier. The path-length difference referred to in Table 39 is given by Path-length difference = A + B - D where A, B, and D are as specified in Figure 31. (32) The limiting value of about 24 dB is caused by sound scattering and refracting into the shadow zone formed by the barrier. Practical factors such as size and space restrictions often limit sound barrier performance to 10 to 15 dBA. For large distances outdoors, this scat- tering and bending of sound waves into the shadow zone reduces bar- rier effectiveness. At large distances, atmospheric conditions can significantly affect sound path losses by amounts even greater than those provided by the barrier, with typical differences of 10 dBA. For a conservative estimate, the height of the sound source location should be taken as the topmost part of the sound source, and the height of the receiver should be taken as the topmost location of a sound receiver, such as the top of the second-floor windows in a two- floor house or at a height of 1.5 m for a standing person. Reflecting Surfaces. No other surfaces should be located where they can reflect sound around the ends or over the top of the barrier into the barrier shadow zone. Figure 32 shows examples of reflect- ing surfaces that can reduce the effectiveness of a barrier wall. Width of Barrier. Each end of the barrier should extend hori- zontally beyond the line of sight from the outer edge of the source to the outer edge of the receiver position by a distance of at least three times the path-length difference. Near the ends of the barrier, the effectiveness of the noise isolation is reduced because some sound is diffracted over the top and around the ends. Also, some sound is reflected or scattered from various nonflat surfaces along the ground near the ends of the barrier. In critical situations, the barrier should completely enclose the sound source to eliminate or reduce the effects of reflecting surfaces. Reflection from a Barrier. A large, flat reflecting surface, such as a barrier wall, may reflect more sound toward the source than there would have been with no wall present. If the wall produces no special focusing effect, reflections from the wall will produce levels on the side of the barrier facing the source that are 2 to 3 dB higher. Using acoustical absorption on the barrier surface (source side) reduces this increase. 2.7 FUME HOOD DUCT DESIGN Fume hood exhaust systems are often the major sound source in a laboratory. The exhaust system may consist of individual exhaust fans ducted to separate fume hoods, or a central exhaust fan connected through a collection duct system (commonly known as a manifold) to a large number of hoods, as shown in Figure 33. In either case, a redundancy system consisting of two fans might be used. In addition to fan noise, other sound sources are the air termi- nal unit serving the hood and aerodynamically generated noise from airflow in the ducts and control valves. Sound pressure levels pro- duced in the laboratory space should be estimated using procedures described in this section and manufacturer-supplied noise emission data. Recommended noise level design criteria for laboratory spaces using fume hoods are given in Table 1. To minimize static pressure loss and fan power consumption in a duct system, fume hood ducts should be sized to allow rated airflow at no greater than 10 m/s or at a velocity consistent with regulatory requirements. Duct velocities over 10 m/s should be avoided for acoustical reasons and to conserve energy. Above this speed, the Fig. 32 Reflecting Surfaces That Can Diminish Barrier Effectiveness ![image](/image/placeholder) BUILDING TO RECEIVER BUILDING SOURCE BARRIER ELEVATION TO REFLECTION FROM WALL BEHIND BARRIER RECEIVER SOURCE BARRIER TO RECEIVER SOURCE BARRIER TREES TREES ELEVATION REFLECTION FROM TREES OVER TOP OF BARRIER REFLECTION FROM TREES OR OTHER STRUCTURES AROUND ENDS OF BARRIERS Inc. ASHRAE, 2019 user. single for Licensed | {}
e37088c1-74f2-47c6-ba58-cec500c0ad96 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.36 2019 ASHRAE Handbook- -HVAC Applications (SI) ![image](/image/placeholder) IRIS DAMPERS INLINE THERMOSTAT REHEAT COIL VALVE Fig. 33 Typical Manifold Lab Exhaust Layout design criteria given in Table 1 are unlikely to be met, even with a silenced fan(s). Noise control measures for fume hood systems include the fol- lowing: Fan(s) · Where conditions allow, use backward-inclined, airfoil, or forward- curved centrifugal fans instead of radial-blade fans, and use cau- tion if applying axial-blade fans. · Select fan(s) to operate at a low tip speed and maximum efficiency. · Try to run redundant fans at reduced capacity instead of operating one fan at full capacity. Inc. ASHRAE, 2019 user. single for Licensed Manifold · Design the manifold upstream of the exhaust fan(s) to double as an acoustic plenum as shown in Figure 34 with sound-absorbent sidewall panels, which can be constructed with nonporous lining or packless cavities with perforated inner wall. Fan low-frequency noise can be reduced when the manifold is paral- lel-piped, with large surface area compared to the cross-sectional area of the fume hood ducts connecting to it. Duct silencers · Use prefabricated duct silencers or sections of lined ducts where conditions allow. In addition to galvanized steel, silencers can be fabricated with stainless steel, aluminum, or plastic. · Silencers should be packless design, or have nonporous fill. Exhaust silencers · Where outdoor noise is an issue, round silencers may be required between the fan and the discharge cone. These should be packless or nonporous-fill design. ![image](/image/placeholder) EXHAUST PLENUM AIR VALVE ROOF EXHAUST ! . DUCT CEILING GENERAL EXHAUST GRILLE Fig. 34 Inlet Plenum for Multiple Exhaust Fans Duct design · Design duct elements such as elbows and junctions with low friction to minimize duct pressure loss and aerodynamically generated noise. Use round ducts, because rectangular ducts can have a noise breakout issue. Laboratory flow control valves and air terminal units · Allow 600 to 900 mm minimum of straight duct upstream and downstream from the terminal unit to reduce aerodynamically generated noise at the unit. · Additional straight length may be required on the room side of valves to accommodate high-performance silencers. · Noise generation in flow control valves increases exponentially with pressure loss, so system supply or exhaust pressure should be set at the level necessary to achieve design flow rate with min- imal safety factor. Fume hood location · Where possible, locate fume hoods in private alcoves to reduce lab occupant's noise exposure. All potential noise control measures should be carefully evalu- ated for compliance with applicable codes, safety requirements, and corrosion resistance requirements of the specific fume hood system. In addition, vibration isolation for fume hood exhaust fans is gener- ally required. For some laboratory facilities, particularly those with highly vibration-sensitive instruments such as electron micro- scopes, vibration control can be critical, and a vibration specialist should be consulted. 2.8 MECHANICAL EQUIPMENT ROOM SOUND ISOLATION Location Locating HVAC equipment in a common room allows the de- signer to control noise affecting nearby spaces. Often, these spaces have background noise level criteria that dictate the type of con- struction and treatment necessary to achieve sufficient reduction in equipment noise transmitted to other spaces. The most effective noise control measure for indoor mechanical equipment rooms is to locate them as far away as possible from noise-sensitive areas. In some cases, this requires a separate struc- ture, such as a central chiller plant, to house equipment. Subterra- | {}
fc83cff6-ab64-4c79-a4de-5d0e280a0f3d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.37 nean basement locations are typically best for noisy equipment because the basement usually affects the fewest adjacent locations. Penthouse equipment rooms are common but can create significant challenges for noise and vibration isolation. Rooms containing air- handling units should provide sufficient room for the equipment and associated ductwork to allow smooth transitions and full-radius curved elbows. A building corner location can work well by reducing the number of adjacent interior spaces and the amount of associated outdoor-air ductwork. Using adjacent spaces such as corridors, closets, and storage rooms as buffer zones can pro- vide effective noise control. A common mistake in locating mechanical equipment rooms is to position the room in the core of the building between a stairway, an elevator shaft, and a tele- communications closet, leaving only one wall where supply and return air ductwork can enter and leave the room. This leads to high-velocity air in the ductwork and high static pressures for fans to overcome, leading to higher noise levels. Once the mechanical equipment room location has been estab- lished, the amount of noise created in the room should be assessed and appropriate constructions selected for walls, ceilings, and floors. Concrete masonry units of various available thickness and densities are often used for their durability and effectiveness in reducing low-frequency noise levels. Typically, heavier and thicker materials contain more sound within the space. Special masonry units that provide a limited amount of acoustical absorption using slotted openings and resonator cavities can also be used. The sound isolation of a masonry wall can be significantly improved by using furred-out gypsum wallboard and insulation in cavities. Chillers and other equipment with very high noise levels are best situated in rooms with concrete masonry unit walls. Wall Design Often, because of structural issues and mass limitations, mechan- ical equipment room walls are built from gypsum wallboard on metal or wood studs. To adequately attenuate low-frequency noise, suffi- cient mass and thickness must be provided in the wall partition construction. This typically entails using multiple layers of gypsum wallboard on both sides of the wall with batt insulation in the cavi- ties. Where greater levels of noise reduction are required, walls are built on double, staggered-stud construction using two separate rows · of studs on separate tracks with multiple layers of gypsum wallboard and batt insulation in the cavities (see Table 40). Doors Doors into mechanical equipment rooms are frequently the weak link in the enclosure. Where noise control is important, the doors should be as heavy as possible, gasketed around the perimeter, have no grilles or other openings, and be self-closing. If they lead to sen- sitive spaces, two doors separated by a 1 to 3 m corridor may be nec- essary. Penetrations For all types of walls, service penetrations should be fully caulked and sealed. Pipes, ducts, and conduits that penetrate walls, ceilings, or floors of mechanical rooms should be acoustically treated. Typi- cally, a 13 mm gap around the penetrating element is filled with an appropriate material such as mineral fiber insulation. The penetra- tion is then sealed airtight with resilient caulk (Figure 35). Ducts passing through the mechanical equipment room en- closure pose an additional problem. Sound can be transmitted to either side of the wall through duct walls. Airborne sound in the mechanical room can be transmitted into the duct (break-in) and enter an adjacent space by reradiating (breakout) from duct walls, even if the duct contains no grilles, registers, diffusers, or other openings. Sound levels in ducts close to fans are usually high. Sound can come not only from the fan but also from pulsating duct walls, excessive air turbulence, and air buffeting caused by tight or restricted fan airflow entrance or exit configurations. Duct layout for good aerodynamics and airflow conditions should minimize low-frequency sound generation, which, once generated, is difficult or impossible to remove, especially near noise-sensitive areas. Avoid elements conducive to increased breakout noise transmission and/or with a tendency to vibrate at low frequencies because of nonlaminar airflow. Round ductwork is most resistant to these prob- lems, followed by square and rectangular ducts with aspect ratios less than 2:1. Heavier-than-normal gage metal ductwork, such as 16 ga (1.6 mm thickness) within the mechanical room and over noise-sensitive spaces, can also be used. : ![image](/image/placeholder) V STRAPS OR ISOLATOR HANGERS AS REQUIRED. CAULK OPENINGS FROM WALL SURFACE TO DUCT, PIPE, OR CONDUIT WITH NONHARDENING ACOUSTICAL SEALANT BOTH SIDES OF WALL. USE FIRE-RATED SEALANT AS REQUIRED. PACK ANNULAR SPACE COMPLETELY WITH MINERAL FIBER OR BULK CERAMIC FIBER AS REQUIRED FOR FIRE RATING. RECESS FIBROUS MATERIAL INTO SLEEVE 13 mm OR AS REQUIRED BY THE SPECIFIC U.L. SYSTEM FOR REQUIRED SEALANT THICKNESS. METAL SLEEVE GROUTED INTO CONCRETE OR CMU WALL, 13 TO 19 mm LARGER THAN OUTSIDE DIAMETER OF DUCT OR PIPE. BLOCK WALL GYPSUM WALL Fig. 35 Duct, Conduit, and Pipe Penetration Details Inc. ASHRAE, 2019 user. single for Licensed | {}
f4ea2948-9947-4a49-b24a-82d9b5a9a102 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.38 2019 ASHRAE Handbook-HVAC Applications (SI) Table 40 Sound Transmission Class (STC) and Transmission Loss Values of Typical Mechanical Equipment Room Wall, Floor, and Ceiling Types, dB ¦ ¦ ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Room Construction Type ¦ STC ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ ¦ 200 mm CMU* ¦ 50 ¦ 35 ¦ 35 ¦ 41 ¦ 44 ¦ 50 ¦ 57 ¦ 64 ¦ ¦ 200 mm CMU with 16 mm GWB* on furring strips ¦ 53 ¦ 33 ¦ 32 ¦ 44 ¦ 50 ¦ 56 ¦ 59 ¦ 65 ¦ ¦ 16 mm GWB on both sides of 92 mm metal studs ¦ 38 ¦ 18 ¦ 16 ¦ 33 ¦ 47 ¦ 55 ¦ 43 ¦ 47 ¦ ¦ 16 mm GWB on both sides of 92 mm metal studs with fiberglass insulation in cavity ¦ 49 ¦ 16 ¦ 23 ¦ 44 ¦ 58 ¦ 64 ¦ 52 ¦ 53 ¦ ¦ 2 layers of 16 mm GWB on both sides of 92 mm metal studs with fiberglass insulation in cavity ¦ 56 ¦ 19 ¦ 32 ¦ 50 ¦ 62 ¦ 67 ¦ 58 ¦ 63 ¦ ¦ Double row of 92 mm metal studs, 25 mm apart, each with 2 layers of 16 mm GWB and fiberglass insulation in cavity ¦ 64 ¦ 23 ¦ 40 ¦ 54 ¦ 62 ¦ 71 ¦ 69 ¦ 74 ¦ ¦ 150 mm solid concrete floor/ceiling ¦ 53 ¦ 40 ¦ 40 ¦ 40 ¦ 49 ¦ 58 ¦ 67 ¦ 76 ¦ ¦ 150 mm solid concrete floor with 100 mm isolated concrete slab and fiberglass insulation in cavity ¦ 72 ¦ 44 ¦ 52 ¦ 58 ¦ 73 ¦ 87 ¦ 97 ¦ 100 ¦ ¦ 150 mm solid concrete floor with two layers of 16 mm GWB hung on spring isolators with fiberglass insulation in cavity ¦ 84 ¦ 53 ¦ 63 ¦ 70 ¦ 84 ¦ 93 ¦ 104 ¦ 105 ¦ Note: Actual material composition (e.g., density, porosity, stiffness) affects transmission loss and STC values. *CMU = concrete masonry unit; GWB = gypsum wallboard. Mechanical Chases Mechanical chases and shafts should be acoustically treated the same way as mechanical equipment rooms, especially if they contain noise-producing ductwork, pipes, and equipment such as fans and pumps. The shaft should be closed at the mechanical equip- ment room, and shaft wall construction must provide sufficient reduction of mechanical noise from the shaft to noise-sensitive areas to obtain acceptable noise levels. Chases should not be allowed to become "speaking tubes" between spaces requiring different acous- tical environments. Crosstalk through the shaft must be prevented. Pipes, ducts, conduits, or equipment should be vibration isolated so that mechanical and structureborne noise is not transmitted to the shaft walls and into the building structure. When mechanical equipment rooms are used as supply or return plenums, all openings into the equipment room plenum space may require noise control treatment, especially if any sound-critical space is immediately adjacent. This is particularly true if the space above an acoustical tile ceiling just outside the equipment room is used as a return air plenum. Most acoustical tile ceilings are almost acoustically transparent at low frequencies. Often, supply ducts are run inside a chase that is also used for re- turn air. Itis best to attenuate supply and return paths at the fan rather than let duct breakout noise require additional noise control at the chase return air inlets. Take care to prevent turbulent noise genera- tion in the supply duct through proper supply duct design. Special Construction Types Sound transmission loss values for some typical constructions are given in Table 40. These data are compiled from controlled lab- oratory tests and represent a condition typically superior to that found in field installations, because the in situ acoustical perfor- mance of any wall, floor, or ceiling is adversely affected by flanking paths, holes, penetrations, and other anomalies. Flanking paths include intersections of the wall, floor, or ceiling surface with another wall, floor, or ceiling that is structurally connected. Higher levels of sound isolation can be achieved by decoupling the surfaces and using double-walled, floating floor, or barrier-ceiling construc- tions. Floating Floors and Barrier Ceilings Correctly installed floating floors and barrier ceilings can pro- vide very high levels of sound isolation, allowing mechanical equip- ment rooms to be placed adjacent to noise-sensitive spaces. Like double-walled construction, these configurations decouple two sur- faces by providing separate supporting structures. However, these types of construction can add significant cost and coordination com- plexity and should be carefully evaluated. In a floating floor, the upper floor slab is typically a 100 mm con- crete slab resting on spring, neoprene, and/or fiberglass vibration isolators supported by the subfloor (typically another concrete slab of appropriate thickness). An air gap is maintained between the two slabs and resilient materials are used around the upper slab ' s perim- eter to decouple it from surrounding walls. Air gap and upper slab thickness both affect noise isolation performance and should be considered. Any heavy equipment should be properly supported to account for additional loading and possible short circuiting. Because natural frequencies for floating floor systems are lim- ited by the dynamic response of the air trapped between the floating and structural slabs, these types of systems are not recommended to control structureborne vibration. It is extremely difficult on a floating floor to achieve a natural frequency of less than 15 Hz. While this is low enough to have a significant impact on audible frequencies, it is not low enough to control the vibrations generated by common equipment types. Mounting equipment directly to a floating floor can reduce flanking paths and result in some acoustic benefits. However, ensure that adequate damping is provided in the floating floor and that there are no common natural frequencies present between the floating floor isolation system and any equipment isolation mounted to it. Improper selection can increase the transmitted vibration rather than reduce it. Similarly, barrier ceilings are typically composed of multiple layers of gypsum wallboard attached to a frame suspended from the structure above with vibration-isolating hangers. A sound barrier ceiling's construction is influenced by its purpose. Ifthe ceiling iso- lates two vertically adjacent spaces, mechanical equipment should be placed below the ceiling to ensure a continuous drywall barrier. Ifnoise levels in the occupied space below the sound barrier ceiling are critical, mechanical equipment should be placed above with minimal ceiling penetrations that are properly sealed. Regardless, ductwork, piping, and other equipment require careful coordination of hangers and supports to ensure no rigid contact with the ceiling. Ceiling penetrations should be minimized, because these reduce barrier ceiling performance. In the case of recessed lighting, it is often necessary to use a gypsum wallboard enclosure around the entire fixture so that it does not serve as a flanking path for noise. Design and selection of the floating floor or ceiling should be carefully considered to properly support the dead and live loads it must carry. The floating system (floor or ceiling) is not meant as a means of equipment vibration isolation and serves primarily to con- Inc. ASHRAE, 2019 user. single for Licensed | {}
270d514c-cc8d-48b0-bfeb-c634ace167c7 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.39 trol airborne sound transmission. Acoustical performance of the floating system depends greatly on construction quality, which re- quires careful coordination between all trades. All penetrations and intersections with other surfaces must allow the floor or ceiling to float without any rigid connections. This typically entails maintain- ing clearances of at least 6 mm and filling all gaps with resilient ma- terials such as nonhardening caulk. Sound Transmission in Return Air Systems The fan return air system provides a sound path (through ducts or a ceiling plenum) between a fan and occupied rooms. Where there is a direct opening to the mechanical equipment room from the ceiling plenum, sound levels in adjacent spaces can be high, origi- nating from the fan and other sources in the mechanical equipment room. Low system attenuation between the mechanical equipment room and adjacent spaces exacerbates the problem. Fan intake sound power levels control sound in ducted return air systems; sound power levels of the fan intake and casing-radiated noise components affect plenum return air systems. In some instal- lations, sound from other equipment located in the mechanical equipment room may also radiate through the wall opening and into adjacent spaces. Good design yields room return air system sound levels that are approximately 5 dB below the corresponding room supply air system sound levels. When sound levels in spaces adjacent to mechanical equipment rooms are too high, noise control measures must be provided. The controlling sound paths between the mechanical equipment room and adjacent spaces must be identified. Ducted return air systems can be modified using methods applicable to ducted supply systems. Ceiling plenum return systems should only be used for spaces that are remote from mechanical equipment rooms. Ceiling plenum systems may require additional modifications. Prefabricated silencers can be effective when installed at the mechanical equipment room wall opening or at the suction side of the fan. Improvements in ceiling transmission loss are often limited by typical ceiling penetrations and lighting fixtures. Modifications to the mechanical equipment room wall can be effective for some constructions. Adding acoustical absorption in the mechanical equipment room reduces build-up of reverberant sound energy in this space; however, this typically reduces high-frequency noise by a maximum of 4 dB and low-frequency noise only slightly in areas near the return opening. Sound Transmission Through Ceilings When terminal units, fan-coil units, air-handling units, ducts, or return air openings to mechanical equipment rooms are located in a ceiling plenum above a room, sound transmission through the ceil- ing system can be high enough to cause excessive noise levels in that room. There is no standard test procedure for measuring direct transmission of sound through ceilings from sources close to the ceiling. As a result, ceiling product manufacturers rarely publish data that can be used in calculations. The problem is complicated by the presence of light fixtures, diffusers, grilles, and speakers that reduce the ceiling's transmission loss. Experiments have shown that, for ceiling panels supported in a T-bar grid system, leakage between the panels and grid is the major transmission path; differ- ences among panel types are small, and light fixtures, diffusers, etc., have only a localized effect. To estimate room sound pressure levels associated with sound transmission through the ceiling, sound power levels in the ceiling plenum must be adjusted to account for the transmission loss of the ceiling system and plenum. Measured data must also be adjusted to account for sound absorption in the room. The procedures given here are based on ASHRAE research (Warnock 1998): 1. Obtain octave band radiated sound power levels of device. Table 41 Environmental Correction to Be Subtracted from Device Sound Power ¦ Octave Band Frequency, Hz ¦ Octave Band Frequency, Hz ¦ Octave Band Frequency, Hz ¦ Octave Band Frequency, Hz ¦ Octave Band Frequency, Hz ¦ Octave Band Frequency, Hz ¦ Octave Band Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ ¦ 4 ¦ 2 ¦ 1 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ Table 42 Compensation Factors for Source Area Effect m2 ¦ Area range, ¦ Area range, ¦ Area range, ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 63 Hz ¦ 125 Hz ¦ 250 Hz ¦ Adjustment, dB ¦ ¦ <0.24 ¦ <0.20 ¦ ¦ -3 ¦ ¦ 0.26 to 0.46 ¦ 0.22 to 0.43 ¦ <0.21 ¦ -2 ¦ ¦ 0.47 to 0.67 ¦ 0.46 to 0.66 ¦ 0.25 to 0.56 ¦ -1 ¦ ¦ 0.69 to 0.87 ¦ 0.68 to 0.88 ¦ 0.62 to 0.96 ¦ 0 ¦ ¦ 0.90 to 1.09 ¦ 0.91 to 1.12 ¦ 0.99 to 1.33 ¦ 1 ¦ ¦ 1.11 to 1.30 ¦ 1.13 to 1.34 ¦ 1.37 to 1.70 ¦ 2 ¦ ¦ 1.32 to 1.52 ¦ 1.36 to 1.56 ¦ 1.74 to 2.07 ¦ 3 ¦ ¦ 1.53 to 1.72 ¦ 1.59 to 1.79 ¦ ¦ 4 ¦ ¦ 1.75 to 1.93 ¦ 1.81 to 2.02 ¦ ¦ 5 ¦ ¦ 1.95 to 2.15 ¦ ¦ ¦ 6 ¦ Note: Find correct area in each frequency column and read adjustment from last col- umn on right. 2. Subtract environmental correction from Table 41. 3. Calculate surface area of bottom panel of source closest to ceil- ing tiles (m2). 4. From Table 42, find adjustment to be subtracted from sound power values at three frequencies given there. 5. Select ceiling/plenum attenuation from Table 43 according to ceiling type in use. Note that these values include a typical room effect, so when using these data in analysis, there is no additional line item from Equation (20) or (30). 6. Subtract the three sets of values, taking account of sign where necessary, from sound power values. The result is the average sound pressure level in the room. 7. The sound field in the room may be assumed as uniform up to distances of 5 m from the source. Example 7. A terminal unit with an area of 1.3 m2 and a known sound power level is to be used above a standard 16 mm thick mineral fiber ceiling system in a T-bar grid. What room sound pressure levels can be expected? Solution: ¦ ¦ ¦ Octave Band Frequency, Hz ¦ Octave Band Frequency, Hz ¦ Octave Band Frequency, Hz ¦ Octave Band Frequency, Hz ¦ Octave Band Frequency, Hz ¦ Octave Band Frequency, Hz ¦ Octave Band Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Step ¦ Step ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ ¦ 1 ¦ Sound power ¦ 71 ¦ 71 ¦ 65 ¦ 55 ¦ 54 ¦ 53 ¦ 45 ¦ ¦ 2 ¦ Environmental (Table 41) ¦ -4 ¦ -2 ¦ -1 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ ¦ 4 ¦ Area adjustment (Table 42) ¦ -2 ¦ -2 ¦ -1 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ ¦ 5 ¦ Ceiling/plenum (Table 43) ¦ -13 ¦ -15 ¦ -17 ¦ -19 ¦ -25 ¦ -30 ¦ -33 ¦ ¦ 6 ¦ Room sound pressure levels, dB ¦ 52 ¦ 52 ¦ 46 ¦ 36 ¦ 29 ¦ 23 ¦ 12 ¦ 2.9 HVAC NOISE-REDUCTION DESIGN PROCEDURES These HVAC system design procedures address the 63 to 4000 Hz octave band midfrequency range. Although it is desirable to extend this frequency range down into the 31.5 Hz octave band, acoustical calculations below the 125 Hz octave band are generally not reli- able. With a few exceptions, if acoustical design criteria are met at 4000 Hz, then the 8000 Hz requirements are also met. Guidelines in this chapter and other guides maximize the probability of meeting acoustical design criteria in the 31.5 to 8000 Hz octave bands. There is reasonable probability that the acoustical design criteria will be met when the following requirements are satisfied: Inc. ASHRAE, 2019 user. single for Licensed | {}
a19b1b10-adf6-47e1-89ce-b7e8b366f90c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.40 2019 ASHRAE Handbook- -HVAC Applications (SI) Table 43 Ceiling/Plenum/Room Attenuations in dB for Generic Ceiling in T-Bar Suspension Systems ¦ Tile Type ¦ Approxi- mate Density, kg/m2 ¦ Tile Thick- ness, mm ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ Octave Midband Frequency, Hz ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Tile Type ¦ Approxi- mate Density, kg/m2 ¦ Tile Thick- ness, mm ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ ¦ Mineral fiber ¦ 4.9 ¦ 16 ¦ 13 ¦ 16 ¦ 18 ¦ 20 ¦ 26 ¦ 31 ¦ 36 ¦ ¦ ¦ 2.4 ¦ 16 ¦ 13 ¦ 15 ¦ 17 ¦ 19 ¦ 25 ¦ 30 ¦ 33 ¦ ¦ Glass fiber ¦ 0.5 ¦ 16 ¦ 13 ¦ 16 ¦ 15 ¦ 17 ¦ 17 ¦ 18 ¦ 19 ¦ ¦ ¦ 2.9 ¦ 50 ¦ 14 ¦ 17 ¦ 18 ¦ 21 ¦ 25 ¦ 29 ¦ 35 ¦ ¦ Glass fiber with TL backing ¦ 2.9 ¦ 50 ¦ 14 ¦ 17 ¦ 18 ¦ 22 ¦ 27 ¦ 32 ¦ 39 ¦ ¦ Gypsum board tiles ¦ 8.8 ¦ 13 ¦ 14 ¦ 16 ¦ 18 ¦ 18 ¦ 21 ¦ 22 ¦ 22 ¦ ¦ Solid gypsum board ceiling ¦ 8.8 ¦ 13 ¦ 18 ¦ 21 ¦ 25 ¦ 25 ¦ 27 ¦ 27 ¦ 28 ¦ ¦ ¦ 11.2 ¦ 16 ¦ 20 ¦ 23 ¦ 27 ¦ 27 ¦ 29 ¦ 29 ¦ 30 ¦ ¦ Double layer of gypsum board ¦ 18.1 ¦ 25 ¦ 24 ¦ 27 ¦ 31 ¦ 31 ¦ 33 ¦ 33 ¦ 34 ¦ ¦ ¦ 22 ¦ 32 ¦ 26 ¦ 29 ¦ 33 ¦ 33 ¦ 35 ¦ 35 ¦ 36 ¦ ¦ Mineral fiber tiles, concealed spline ¦ 2.4 to 4.9 ¦ 16 ¦ 20 ¦ 23 ¦ 21 ¦ 24 ¦ 29 ¦ 33 ¦ 34 ¦ mount. Source: Warnock (1998) · Systems are designed in accordance with the equipment selection, placement, and integration guidelines in this chapter, other ASH- RAE guides, and manufacturers' application notes and bulletins. · Acoustical calculations based on the information included in this chapter and the information provided by the equipment man- ufacturer indicate that the system will not exceed the selected acoustical design criteria values in the 63 to 4000 Hz octave band frequency range. The following suggested design procedure uses the Noise Crite- ria (NC) method, which is the most commonly used. Other criteria, such as NCB or RC, may be used. (See the Criteria Descriptions section of this chapter or Chapter 8 of the 2017 ASHRAE Hand- book-Fundamentals for detailed explanations of these methods.) However, it is often difficult to acquire low-frequency sound data, and low-frequency acoustical calculations for HVAC system com- ponents are not reliable. 1. Determine the design goal for HVAC system noise for each critical area according to its use and construction. Choose the desirable NC criterion from Table 1. 2. Select equipment and fittings (e.g., air inlet and outlet grilles, registers, diffusers, and air terminal and fan-coil units that radi- ate sound directly into a room) that are operating comfortably with their specified duty and are quiet for the class of equip- ment in question. The appropriate selection of equipment and fitting will generally result in an efficient acoustic design to meet design goals. 3. Complete initial design and layout of the HVAC system. Include typical duct lining where appropriate. Provide space for duct sound attenuators. Confirm that the airflow velocities are compliant with the specified rates in Tables 8 and 9 of the Aerodynamically Generated Sound in Ducts section of this chapter. 4. Calculate sound pressure level in the room of interest: (a) Acquire sound power data from manufacturers for equip- ment such as air-handling units, packaged rooftop units, exhaust fans, variable-air-volume terminal units, fan- powered terminal units, etc. If manufacturers' data are not available, estimate sound power level based on methods in this chapter or other authoritative sources. 5. 6. 7. 8. 9. (b) Calculate sound attenuation and regenerated sound power of duct elements in the air distribution system of interest. (c) Tabulate sound power and attenuation for each component in each sound transmission path. Start at the supply air fan or packaged air-conditioning unit and end at the room. Investigate both the supply and return air paths in similar ways. Investigate possible duct sound breakout when fans are adjacent to, or roof-mounted fans are above, the room of interest. Combine sound power levels from all paths. See Example 8 for calculation procedures for supply and return air paths, including duct breakout noise contribu- tions. Include a placeholder for the duct sound attenuator so that it is a simple matter to include in calculations later. (d) Convert sound power levels to corresponding sound pres- sure levels in the room using the ASHRAE room correc- tion procedure. (See the Receiver Room Sound Correction section of this chapter.) If the mechanical equipment room is adjacent to the room of interest, determine sound pressure levels in the room of inter- est that are associated with sound transmitted through the mechanical equipment room wall. Air-handling units, ventila- tion and exhaust fans, chillers, pumps, electrical transformers, and instrument air compressors are typical equipment to con- sider. Make sure that noise transmission from adjacent exter- nal spaces outside the room in question, such as cooling towers or air-cooled chillers, is also considered. Also consider the vibration isolation requirements for equipment, piping, and ductwork. (See Egan [1988] or Reynolds and Bledsoe [1991] for calculation procedure.) Combine on an energy basis the sound pressure levels in the room of interest that are associated with all sound paths be- tween the mechanical equipment room or roof-mounted unit(s) and the room of interest. Establish the controlling noise-transmission paths. Determine the corresponding NC level associated with the calculated total sound pressure levels in the room of interest. Take special note of unbalanced sound spectra and tonal char- acteristics. Ifthe NC level satisfies the criteria established in step 1, anal- ysis is complete. If the NC level exceeds the design goal, determine the octave frequency bands in which the corre- sponding sound pressure levels are exceeded and the sound paths associated with these octave frequency bands as deter- mined in step 6. If the resulting noise levels are high enough to cause perceivable vibration, consider both airborne and structureborne noise. Redesign the system: (a) Reselect the offending noise source. This is typically the least costly, most energy-efficient, and most effective change, but is not always possible. (b) Add sound attenuation to paths that contribute to exces- sive sound pressure levels in the room of interest. This may be achieved by using thicker internal acoustic-grade insulation or proprietary silencers. Note that silencers preferably should be inserted at the penetration of the mechanical equipment room (MER) walls or external building elements to minimize breakout before the silencer. (c) Consider increasing the length of ductwork or introducing bends or a plenum to increase the sound attenuation. Care needs to be taken to ensure that the breakout noise path(s) are still acceptable where additional ductwork is intro- duced. (d) Increase the sound transmission loss properties ofbuilding elements where this is the controlling noise path. This may Inc. ASHRAE, 2019 user. single for Licensed | {}
699d7d7e-878f-44c0-8f0b-edb91f704ed2 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.41 be achieved by installing additional mass (e.g., thicker walls or filled concrete masonry units [CMUs]) or by introducing an air gap with a secondary layer (e.g., double glazing). (e) Consider installing noise barriers around the external plant to minimize the direct line of sight between plant and crit- ical spaces. The manufacturers' requirements for access and airflow around equipment must be carefully considered where noise barriers are used. (f) If resultant noise levels are high enough to cause per- ceivable vibration, then major redesign and possibly use of supplemental vibration isolation for equipment and build- ing systems are often required. (g) Reference should also be made to this chapter's sections on Acoustical Design ofHV AC Systems and Basic Acoustical Design Techniques. 10. Repeat steps 4 to 9 until the desired design goal is achieved. Involve the complete design team where major problems are found. Often, simple design changes to building architectural and equipment selection can eliminate potential problems once the problems are identified. Ensure that all valid noise- transmission paths are assessed. 11. Repeat steps 3 through 10 for every room that is to be analyzed. 12. Make sure that environmental noise radiated by outdoor equip- ment such as air-cooled chillers, exhaust fans, condensers, and cooling towers does not disturb adjacent properties or interfere with criteria established in step 1 or any applicable building or zoning noise ordinances. Example 8. This example shows step 4 in the design process. Previous examples demonstrate how to calculate equipment- and air distribution system airflow-generated sound power levels and attenuation values. Here, the individual elements are combined to determine sound pres- sure levels associated with a specific HVAC system. Only a summary of tabulated results is listed rather than showing complete calculations for each element. Calculations for each element are strictly based on the methods in this chapter or manufacturers' data. Noise transmission via the roof structure has not been considered in this example. Air is supplied to the HVAC system by the rooftop unit shown in Figure 36, with a supply and return layout as in Figure 37. The receiver room is directly below the unit. The room has the following dimen- sions: length = 6.1 m, width = 6.1 m, and height = 2.75 m. Assume that the roof penetrations for supply and return air ducts are well sealed and there are no other roof penetrations. In this example, it is assumed that breakout noise (upstream of the supply air silencer) is negligible. The supply side of the rooftop unit is ducted to a VA V terminal control unit serving the room in question. Although these units can create both ductborne and radiated noise, only the ductborne noise has been con- sidered in this example. A return air grille conducts air to a common ceiling return air plenum. The return air is then directed to the rooftop unit through a short rectangular return air duct. The following three sound paths are to be examined. Note that in this example, neither noise transmission via the roof structure nor any ![image](/image/placeholder) ROOFTOP UNIT SUPPLY AIR FAN DUCT SILENCER VAV UNIT RETURN AIR DUCT DIFFUSER PATH 3 PATH 2 PATH 1 Fig. 36 Sound Paths Layout for Example 8 other breakout noise upstream of the silencer has been considered. Those paths, plus VAV unit-radiated noise and other potential breakout noise paths, have been excluded from the analysis for simplification. In critical applications, each of those separate elements must also be con- sidered. Path 1. Fan airborne supply air sound that enters the room from the supply air system through the ceiling diffuser ![image](/image/placeholder) PATH 1, 2 01 6.1 m 2.44 m 02 04 05 03 1.83 m 06 13, 14, 15 07 PATH 2 0.61 m 08 09 10, 11, 12 PATH 1 (A) SUPPLY AIR ![image](/image/placeholder) 810 mm PATH 3 1730 mm 16 18 19 17 PATH 3 2.44 m 14, 20 (B) RETURN AIR Fig. 37 (A) Supply and (B) Return Air Layout for Example 8 NOISE CRITERIA (NC) CURVES Chart Title: NOISE CRITERIA (NC) CORVES X-Axis: OCTAN FRAN GENTED EDELFNOY JR Y-Axis: SOUND PRESSURE LEVEL, dB Chart Type: line 63 125 250 500 1000 2000 4000 8000 item_01 80dB 70dB 60dB 50dB 40dB 30dB 20dB 10dB OCTAVE BAND CENTER FREQUENCY, Hz Fig. 38 NC Rating Calculated Inc. ASHRAE, 2019 user. single for Licensed | {}
6cd82ceb-9687-4d77-b7b6-148150ed94c0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.42 2019 ASHRAE Handbook-HVAC Applications (SI) Path 1: Ducted Supply Air ¦ Element ¦ Element ¦ Sound Power Attenuation, dB ¦ Sound Power Attenuation, dB ¦ Sound Power Attenuation, dB ¦ Sound Power Attenuation, dB ¦ Sound Power Attenuation, dB ¦ Sound Power Attenuation, dB ¦ Sound Power Attenuation, dB ¦ Sound Power Attenuation, dB ¦ Regenerated Sound Power, dB ¦ Regenerated Sound Power, dB ¦ Regenerated Sound Power, dB ¦ Regenerated Sound Power, dB ¦ Regenerated Sound Power, dB ¦ Regenerated Sound Power, dB ¦ Regenerated Sound Power, dB ¦ Regenerated Sound Power, dB ¦ Path Sound Power, dB ¦ Path Sound Power, dB ¦ Path Sound Power, dB ¦ Path Sound Power, dB ¦ Path Sound Power, dB ¦ Path Sound Power, dB ¦ Path Sound Power, dB ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ID ¦ Description ¦ 63 ¦ 125 250 0 5 ¦ 125 250 0 5 ¦ 125 250 0 5 ¦ 500 1000 ¦ 500 1000 ¦ 2000 4000 1 ¦ 2000 4000 1 ¦ 63 125 250 ¦ 63 125 250 ¦ 63 125 250 ¦ 63 125 250 ¦ 63 125 250 ¦ 63 125 250 ¦ 63 125 250 ¦ 2000 4000 63 125 ¦ 2000 4000 63 125 ¦ 2000 4000 63 125 ¦ 2000 4000 63 125 ¦ 250 500 1000 2000 4000 ¦ 250 500 1000 2000 4000 ¦ 250 500 1000 2000 4000 ¦ 250 500 1000 2000 4000 ¦ ¦ 1 ¦ Supply air fan, 3.3 m3/s, 620 Pa static pressure (SP) 58 ¦ 0 600 x 1200 x 16 mm lay-in ceiling 13 ¦ 0 ¦ 0 ¦ 2 ¦ 0 4 8 ¦ 0 0 3 16 ¦ 0 0 ¦ 0 9 ¦ 92 ¦ 86 63 ¦ 80 ¦ 500 78 57 ¦ 1000 78 500 53 ¦ 1000 ¦ 74 ¦ 71 ¦ 92 81 ¦ 86 73 ¦ 80 ¦ 78 ¦ 78 ¦ 74 ¦ 71 ¦ ¦ 2 ¦ 560 mm dia., 90° rad. unlined elbow ¦ 0 55 10 10 ¦ 1 ¦ 2 ¦ 3 19 ¦ 0 ¦ 3 0 ¦ 3 ¦ 3 ¦ 0 ¦ ¦ 0 0 20 25 ¦ 0 ¦ 0 0 ¦ 0 78 0 0 25 ¦ 0 0 ¦ 0 87 ¦ 92 85 ¦ 78 ¦ 70 70 ¦ 75 65 46 ¦ 75 500 54 54 29 ¦ 71 ¦ 68 29 17 ¦ ¦ 3 ¦ 560 mm x 1. 12 m long sound attenuator ¦ 4 ¦ 7 1 ¦ 19 ¦ 31 ¦ 38 ¦ 38 ¦ ¦ 27 ¦ 68 ¦ 79 ¦ 69 ¦ 60 ¦ 59 ¦ 59 ¦ 55 0 ¦ 88 ¦ 82 ¦ 69 ¦ 60 ¦ 250 ¦ 59 ¦ 59 ¦ 55 ¦ ¦ 4 ¦ 560 mm dia., 2.44 m long unlined duct ¦ 0 1 ¦ 0 ¦ 0 1 ¦ 0 ¦ ¦ 0 0 ¦ ¦ 0 ¦ 0 ¦ 0 ¦ 0 0 0 0 ¦ 0 ¦ 0 13 ¦ 0 ¦ 0 ¦ 88 ¦ 82 ¦ 69 ¦ 60 ¦ 59 65 ¦ 59 59 ¦ ¦ 55 ¦ ¦ 5.2 ¦ 250 mm dia. branch, 560 mm dia. main, branch path mm dia. branch, 560 mm dia. main, main 8 600 x 1200 x 16 mm lay-in ceiling ¦ 8 ¦ 8 1 ¦ 8 0 ¦ 8 ¦ ¦ 8 30 ¦ 8 ¦ 8 13 33 ¦ 0 ¦ 0 0 ¦ 0 ¦ 0 ¦ 0 0 ¦ 0 14 ¦ 0 Path ¦ ¦ 80 ¦ 74 61 ¦ 52 ¦ 10 ¦ 51 ¦ 51 34 ¦ 47 ¦ ¦ 6 5.1 ¦ 250 mm dia., 1.83 m long unlined duct ¦ 0 0 13 ¦ 0 ¦ 0 17 ¦ 0 ¦ 42 ¦ 0 ¦ 0 30 ¦ 0 ¦ 0 ¦ 0 0 ¦ 0 ¦ 0 ¦ 0 ¦ ¦ 0 0 3: Return Air Element ¦ 80 ¦ 74 path ¦ 61 ¦ 13 ¦ 52 38 ¦ 51 560 ¦ 51 ¦ 47 35 ¦ ¦ 7 1 ¦ VAV terminal ¦ 0 15 ¦ 0 ¦ 0 17 ¦ 0 63 ¦ 0 0 ¦ ¦ 0 ¦ 0 ¦ 0 ¦ 74 0 0 ¦ 70 ¦ 65 ¦ 63 ¦ 60 ¦ 55 Sound ¦ 80 ¦ 77 81 ¦ 71 68 ¦ ¦ 65 ¦ 63 ¦ 61 ¦ 56 ¦ ¦ 8 ¦ 250 mm dia., 600 mm long unlined duct ¦ 0 Sound Attenuation, ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ ¦ 0 dB ¦ 0 0 ¦ 0 0 ¦ 0 125 ¦ 0 ¦ 0 ¦ 0 ¦ ¦ 0 0 ¦ 80 ¦ 77 ¦ 71 ¦ 65 ¦ ¦ 63 0 ¦ 61 ¦ 56 ¦ ¦ 9 ID ¦ 250 mm dia., 90° rad. unlined elbow Description ¦ 0 ¦ 0 125 250 ¦ 1 500 ¦ 2 4 ¦ 3 1000 ¦ 2000 ¦ 3 4000 ¦ 3 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ 0 ¦ 2000 4000 ¦ 0 0 ¦ 80 ¦ 77 125 250 ¦ 70 ¦ 63 ¦ 60 ¦ 58 0 ¦ 250 ¦ 53 SP ¦ ¦ 10 ¦ 250 mm dia. diffuser, end reflection 2000 4000 air fan, 3.3 m3/s, 620 Pa ¦ 14 ¦ 8 37 ¦ 4 ¦ 1 0 ¦ 0 ¦ ¦ 0 ¦ 0 ¦ 0 82 ¦ 0 74 ¦ 0 ¦ 0 ¦ 0 ¦ 0 71 ¦ 0 1000 ¦ 66 ¦ 69 16 ¦ 66 ¦ 62 ¦ 60 78 ¦ 58 Power ¦ ¦ 53 ¦ ¦ 11 ¦ 380 x 380 mm rectangular diffuser ¦ 0 ¦ 0 ¦ 0 0 ¦ 0 0 ¦ 0 0 64 0 ¦ 0 58 ¦ ¦ 0 0 ¦ 31 79 ¦ 36 ¦ 39 0 80 15 ¦ 40 ¦ 39 78 ¦ 36 74 ¦ 30 ¦ 66 82 ¦ 69 79 ¦ 66 ¦ 62 0 77 ¦ 0 ¦ 60 Regenerated Sound Power, ¦ 58 ¦ 53 71 ¦ ¦ 12 ¦ ASHRAE room correction: point source* 915 x 1830 mm, 90° mitered unlined elbow ¦ 4 ¦ 5 ¦ 6 ¦ ¦ 7 ¦ 8 64 ¦ 9 3 72 ¦ 10 14 ¦ 0 19 0 0 ¦ 0 0 0 ¦ 0 0 ¦ 0 33 0 ¦ 0 0 0 ¦ 0 0 ¦ 0 0 915 ¦ 62 74 ¦ 64 ¦ 80 72 ¦ 60 0 ¦ 55 74 ¦ 52 3 75 71 ¦ 49 ¦ 43 68 ¦ ¦ Path ¦ Path ¦ 2: Breakout Noise from 560 mm Duct ¦ 2: Breakout Noise from 560 mm Duct ¦ 2: Breakout Noise from 560 mm Duct ¦ 2: Breakout Noise from 560 mm Duct ¦ 2: Breakout Noise from 560 mm Duct ¦ 2: Breakout Noise from 560 mm Duct ¦ 2: Breakout Noise from 560 mm Duct ¦ 2: Breakout Noise from 560 mm Duct ¦ Main ¦ Main ¦ Main ¦ Main ¦ Main ¦ Main ¦ Main ¦ Main ¦ Main ¦ Main ¦ Main ¦ Main ¦ Main ¦ Main ¦ ¦ ¦ Element ¦ Element ¦ Sound Power Attenuation, dB ¦ Sound Power Attenuation, dB ¦ Sound Power Attenuation, dB ¦ Sound Power Attenuation, dB ¦ Sound Power Attenuation, dB ¦ Sound Power Attenuation, dB ¦ Sound Power Attenuation, dB ¦ Regenerated Sound Power, dB Path Sound Power, dB ¦ Regenerated Sound Power, dB Path Sound Power, dB ¦ Regenerated Sound Power, dB Path Sound Power, dB ¦ Regenerated Sound Power, dB Path Sound Power, dB ¦ Regenerated Sound Power, dB Path Sound Power, dB ¦ Regenerated Sound Power, dB Path Sound Power, dB ¦ Regenerated Sound Power, dB Path Sound Power, dB ¦ Regenerated Sound Power, dB Path Sound Power, dB ¦ Regenerated Sound Power, dB Path Sound Power, dB ¦ Regenerated Sound Power, dB Path Sound Power, dB ¦ Regenerated Sound Power, dB Path Sound Power, dB ¦ Regenerated Sound Power, dB Path Sound Power, dB ¦ Regenerated Sound Power, dB Path Sound Power, dB ¦ Regenerated Sound Power, dB Path Sound Power, dB ¦ Regenerated Sound Power, dB Path Sound Power, dB ¦ ¦ ¦ ID 18 ¦ Description 915 x 1830 mm, 2.44 m long lined duct ¦ 63 125 250 500 1000 2000 4000 ¦ 63 125 250 500 1000 2000 4000 ¦ 63 125 250 500 1000 2000 4000 ¦ 63 125 250 500 1000 2000 4000 ¦ 63 125 250 500 1000 2000 4000 ¦ 63 125 250 500 1000 2000 4000 ¦ 63 125 250 500 1000 2000 4000 ¦ 4000 63 125 250 500 1000 2000 63 125 250 500 1000 2000 4000 ¦ 4000 63 125 250 500 1000 2000 63 125 250 500 1000 2000 4000 ¦ 4000 63 125 250 500 1000 2000 63 125 250 500 1000 2000 4000 ¦ 4000 63 125 250 500 1000 2000 63 125 250 500 1000 2000 4000 ¦ 4000 63 125 250 500 1000 2000 63 125 250 500 1000 2000 4000 ¦ 4000 63 125 250 500 1000 2000 63 125 250 500 1000 2000 4000 ¦ 4000 63 125 250 500 1000 2000 63 125 250 500 1000 2000 4000 ¦ 4000 63 125 250 500 1000 2000 63 125 250 500 1000 2000 4000 ¦ 4000 63 125 250 500 1000 2000 63 125 250 500 1000 2000 4000 ¦ 4000 63 125 250 500 1000 2000 63 125 250 500 1000 2000 4000 ¦ 4000 63 125 250 500 1000 2000 63 125 250 500 1000 2000 4000 ¦ 4000 63 125 250 500 1000 2000 63 125 250 500 1000 2000 4000 ¦ 4000 63 125 250 500 1000 2000 63 125 250 500 1000 2000 4000 ¦ 4000 63 125 250 500 1000 2000 63 125 250 500 1000 2000 4000 ¦ ¦ ¦ ¦ 1 0 19 ¦ Supply air fan, 3.3 m3/s, 620 Pa SP ¦ 0 ¦ 0 63 ¦ 0 ¦ 0 0 0 ¦ 0 ¦ ¦ 0 0 39 ¦ 92 0 ¦ ¦ 86 80 ¦ 78 0 ¦ 78 ¦ 74 ¦ 71 ¦ 92 ¦ 86 ¦ 80 ¦ 78 ¦ dB Path dB ¦ 78 74 ¦ 71 63 63 ¦ ¦ ¦ ¦ 2 ¦ 560 mm dia., 90° rad. unlined elbow 1 x 1830 mm end reflection loss ¦ 0 1 0 ¦ 1 1 ¦ 2 Return ¦ 3 ¦ 3 0 ¦ 3 0 54 ¦ 3 0 ¦ 0 ¦ 0 0 ¦ 0 81 ¦ 0 ¦ ¦ 0 ¦ 0 0 0 ¦ 92 mm dia., 6 m long, 0.6 mm duct breakout 0 64 ¦ 85 ¦ 78 ¦ 75 ¦ ¦ 75 71 0 35 ¦ 68 55 1 30 ¦ ¦ ¦ ¦ 3 4 ¦ 560 mm x 1.12 m long sound attenuator 560 mm dia., 2.4 m long unlined duct ¦ 4 0 ¦ 7 0 ¦ 19 0 52 44 ¦ 31 0 28 ¦ 38 0 Power, ¦ 38 0 0 ¦ 27 0 0 78 ¦ 68 0 0 17 ¦ 79 ¦ 69 0 32 ¦ 60 0 34 ¦ 59 0 ¦ 59 0 ¦ 55 0 0 13 ¦ 88 88 48 18 ¦ 82 82 ¦ 69 69 ¦ 60 60 ¦ 59 59 59 59 ¦ ¦ ¦ ¦ ¦ *Based on a location 1.5 m above floor at a receiver 1200 mm from source Path 2. Fan airborne supply air sound that breaks out through the wall of the main supply air duct into the plenum space above the room Path 3. Fan airborne return air sound that enters the room from the inlet of the return air duct. Note that this duct has 25 mm internal liner The tabulated calculations for each path follow, and are graphed in Figure 38: ¦ ¦ Path Sound Pressure Level, dB ¦ Path Sound Pressure Level, dB ¦ Path Sound Pressure Level, dB ¦ Path Sound Pressure Level, dB ¦ Path Sound Pressure Level, dB ¦ Path Sound Pressure Level, dB ¦ Path Sound Pressure Level, dB ¦ Path Sound Pressure Level, dB ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Path Description ¦ 63 ¦ 125 ¦ 250 ¦ 500 ¦ 1000 ¦ 2000 ¦ 4000 ¦ NC ¦ ¦ 1 Ducted supply air path ¦ 62 ¦ 64 ¦ 60 ¦ 55 ¦ 52 ¦ 49 ¦ 43 ¦ 52 ¦ ¦ 2 Breakout noise from 560 mm main duct ¦ 39 ¦ 29 ¦ 17 ¦ 12 ¦ 13 ¦ 18 ¦ 9 ¦ 19 ¦ ¦ 3 Return air path ¦ 64 ¦ 57 ¦ 53 ¦ 46 ¦ 29 ¦ 34 ¦ 30 ¦ 44 ¦ ¦ Total Lp ¦ 66 ¦ 65 ¦ 60 ¦ 56 ¦ 52 ¦ 49 ¦ 43 ¦ 52 ¦ Calculation Procedure Analysis for each path begins at the rooftop unit and proceeds through the different system elements to the receiver room. The element numbers in the tables correspond to those in Figure 37. The source of each element calculation is listed in Table 44. Sound data for the rooftop unit (supply and return openings), VAV terminal, diffuser, and duct sound attenuator are manufac- turers' data. A spreadsheet was used to perform the calculations associated with this example. This type of calculation is often performed iteratively, as described in the preceding design procedure, but using a well-crafted spreadsheet (e.g., the one supplied as an extra feature in the ASHRAE Handbook Online version of this chapter) increases the speed and accuracy of calculations. Calculation tables for paths 1, 2, and 3 are organized with an element in each row. Three spectra (63 Hz to 4000 Hz) are shown for each element. The first and second spectra (sound power atten- uation and regenerated sound power) are either calculated based on the equations and tables in this chapter or acquired from a manufacturer. It is important to note that sound power data and not sound pressure data must be used in these calculations. The spreadsheet subtracts the sound attenuation spectrum, band by band, from the path sound power spectrum in the previ- ous row. Then, the resultant sound power is logarithmically added per band to the element sound power. This calculation is per- formed for each element (row). Lw = 10 log 10Lw1/10 + 10Lw2/10 The last element in each path is either the ASHRAE room sound correction or the ceiling/plenum/room attenuations out- lined in Table 43, which is entered as an attenuation spectrum as it is subtracted directly from the final path sound power spectrum. (33) 3. VIBRATION ISOLATION AND CONTROL Mechanical vibration and vibration-induced noise are common sources of occupant complaints in modern buildings. Low-mass construction in buildings provides conditions that can result in Inc. ASHRAE, 2019 user. single for Licensed | {}
ada83377-abcf-4110-8fd9-488bd79ceca9 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.43 Table 44 Path Element Sound Calculation Reference ¦ ID ¦ Description ¦ Data Source Reference ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ 01 ¦ Supply air fan, 3.3 m3/s, 620 Pa static pressure (SP) ¦ Manufacturer's data ¦ ¦ 02 ¦ 560 mm dia., 90° rad. unlined elbow ¦ Attenuation: Table 23 ¦ ¦ 03 ¦ 560 mm dia. 1.12 m long sound attenuator ¦ Manufacturer's data ¦ ¦ 04 ¦ 560 mm dia., 2.4 m long unlined duct ¦ Attenuation: Table 16 ¦ ¦ 05.2 ¦ 250 mm dia. branch, 560 mm dia. main, branch path ¦ Attenuation: Table 26 ¦ ¦ 05.1 ¦ 250 mm dia. branch, 560 mm dia. main, main path ¦ Attenuation: Table 26 ¦ ¦ 06 ¦ 250 mm dia., 1.83 m long unlined duct ¦ Attenuation: Table 16 ¦ ¦ 07 ¦ VAV terminal ¦ Manufacturer's data ¦ ¦ 08 ¦ 250 mm dia., 600 m long unlined duct ¦ Attenuation: Table 16 ¦ ¦ 09 ¦ 250 mm dia., 90° rad. unlined elbow ¦ Attenuation: Table 23 ¦ ¦ 10 ¦ 250 mm dia. diffuser, end reflection ¦ Attenuation: Table 28 ¦ ¦ 11 ¦ 380 x 380 mm rectangular diffuser ¦ Manufacturer's data ¦ ¦ 12 ¦ ASHRAE room correction: point source ¦ Equation (26) or (27), Tables 35 and 36 ¦ ¦ 13 ¦ 560 mm dia., 6 m long, 0.6 mm duct breakout ¦ Attenuation: Equation (20), Table 30 ¦ ¦ 14 ¦ 600 x 1200 x 16 mm lay-in ceiling ¦ Attenuation: Table 32 ¦ ¦ 15 ¦ ASHRAE room correction: line source ¦ Equation (30) ¦ ¦ 16 ¦ Return air fan, 3.3 m3/s, 620 Pa SP ¦ Manufacturer's data ¦ ¦ 17 ¦ 915 x 1830 mm, 90° mitered unlined elbow ¦ Attenuation: Tables 22 and 24 ¦ ¦ 18 ¦ 915 x 1830 mm, 2.44 m long lined duct, 25 mm thick ¦ Attenuation: Table 17, but use online spreadsheet for interpolation ¦ ¦ 19 ¦ 915 x 1830 mm end reflection loss ¦ Attenuation: Table 27, D = 1.1 m ¦ ¦ 20 ¦ ASHRAE Room Correction ¦ Point source: Equation (26) or (27), Tables 35 and 36 ¦ vibration-related problems. Mandates for energy conservation have resulted in many buildings being designed with variable air volume systems with variable-speed equipment. As rotating equipment spins slower, its forcing frequency approaches the structure , s reso- nant frequency, which can amplify vibration-induced noise and gen- erate vibration at the structure' s resonant frequency. Mechanical equipment is often located in penthouses or on the roof, where struc- tures are typically the most susceptible to inducing vibration-related problems. Mechanical equipment rooms are typically located on intermediate level floors, close to the occupied areas they serve. Occupant complaints associated with building vibration typi- cally take one or more of three forms: · The level of vibration perceived by building occupants is of suf- ficient magnitude to cause annoyance, concern, or alarm · Vibration energy from mechanical equipment, which is transmit- ted to the building structure, is transmitted to various parts of the building and then is radiated as structureborne noise · Vibration in a building may interfere with proper operation of sen- sitive equipment or instrumentation The following sections present basic information to properly select and specify vibration isolators and to analyze and correct field vibration problems. 3.1 VIBRA TION MEASUREMENT Understanding the vibratory characteristics ofHVAC equipment can be of great use in diagnosing the sources of both tonal and broadband sound or vibration. The advent of low-cost vibration measurement systems has made detailed vibration evaluation much more practical and commonplace. At the same time, it is important Chart Type: pie PEAK AVERAGE RMS item_01 20% 5% 35% Fig. 39 Vibration Amplitude Terminology to bear in mind that vibration measurement is a specialty that is best done by, or at least overseen by, a specialist. Components of a vibration measurement system include the fol- lowing: · A transducer, which outputs an electrical signal proportional to its vibration level. The most common transducer, called an accelerometer, measures vibratory acceleration at its point of attachment to the structure. As explained in Chapter 8 of the 2017 ASHRAE Handbook-Fundamentals, accelerometers are the preferred transducers in most situations. They are compact, relatively rugged, capable of a wide measurement range in terms of both vibration level and frequency, and are easy to install (de- pending on the frequency range of interest). · A preamplifier for the transducer, which amplifies the signal to a level suitable to the data acquisition system and for the signal con- ditioner. Depending on the transducer and analyzer type, a pream- plifier may not needed. · An analyzer, or vibration meter, with a display showing the vibration level. The most basic analyzers measure the overall vibration amplitude across a specified frequency range, which does not by itself yield enough analytical detail for troubleshoot- ing. Many are capable of measuring vibration as a function of fre- quency, with constant frequency spacing. These so-called "narrowband, , , fast Fourier transform (FFT), analyzers display or the vibration frequency spectrum with a very high degree of res- olution. Alternative analyzers of the constant-percentage band- width type display the vibration spectrum across a number of frequency bands, the widths of which increase proportionally to the center frequency of each band. These often display vibration at octave, 1/3rd octave, or 1/12th octave frequencies. Any steady-state vibration, such as that generated by a machine operating at a fixed speed, can be expressed as acceleration, veloc- ity, or displacement. By integrating the acceleration signal, it is pos- sible to convert each of these quantities to the others. Integrating the velocity signal yields the displacement. Note that many transducers cannot measure vibration below a minimum frequency associated with the transducer. The practical implication of that limitation is that, in many cases, measured acceleration cannot be fully converted to displacement, and can never be used to quantify static displace- ment. For that reason, where very-low-frequency vibration measure- ments are required, specially designed displacement transducers are needed. Vibration measurements must specify how the amplitudes are expressed. These can be either peak (maximum level), peak-to-peak (the range between minima and maxima), or rms (root mean square). For a sine wave, the peak-to-peak value is twice the peak, and the rms is the peak divided by the square root oftwo (Figure 39). Several factors must be considered when making vibration mea- surements. One of these is transducer attachment to the vibrating object. An extremely rigid attachment method, such as dental Inc. ASHRAE, 2019 user. single for Licensed | {}
6c828a8f-0666-4972-b53e-761ce429dd28 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.44 2019 ASHRAE Handbook- -HVAC Applications (SI) cement, or a screwed connection with oil between the surfaces, is required for accurate measurement at very high frequency (about 5 kHz). Epoxies or other high-quality glues tend to be somewhat more limited but are acceptable in nearly all situations up to 1 kHz. Using magnetic attachments, though convenient and fully accept- able in many cases, limits the upper frequency range of accurate data (typically about 1 kHz). Another common but frequency- limited method of attachment is wax, typically reliable up to 80 Hz. In any case, it is essential to validate that the attachment used in a given application is capable of measuring vibration to the needed degree of accuracy. It is best to contact transducer/analyzer manu- facturers to ensure frequency limits can be accurately measured. Several data processing factors must be considered for narrow- band (FFT) measurement. These significantly affect the quality of spectral data and how they are interpreted. Among them are the win- dow type, number of averages, window overlap, frequency resolu- tion, and sampling frequency. Again, guidance from a specialist should be sought when establishing these factors for a given mea- surement. Typical applications of vibration measurement include · Comparison of overall vibration levels (the total across a defined frequency range) with general guidelines representing typical lev- els to be expected from various classes of machinery. This most basic measurement is often used in connection with routine ma- chinery maintenance or monitoring. · Comparison of vibration spectral values with either equipment specifications, building specifications, or general guidelines. These more complete data, sometimes defined in terms of octave or 1/3 octave frequencies, provide more detailed guidance for machinery health monitoring, equipment qualification, or build- ing certification. · Comparison of vibration spectral values above and below vibra- tion isolators, such as pads or springs, to determine if they are providing the anticipated vibration reduction. Note that, as explained in Chapter 8 of the 2017 ASHRAE Handbook-Fun- damentals, interpretation of the results of these measurements may not be straightforward, especially for multiple-degree-of- freedom systems. · Using a narrowband measurement system, determination of exact frequencies of tonal vibration sources. This information can be critical in identifying the specific machine or vibration component responsible for excessive vibration or noise. In some cases, a high degree of measurement resolution is required to separate closely spaced tones. For example, in 60 Hz applications, twice the motor or compressor running speeds are typically close to 118 Hz, while twice the electrical line frequency is 120 Hz. Clearly, while the dif- ference between these frequencies is inaudible, knowing which source is responsible for a problem is essential to developing a solution. Finally, it is noted that many specialized applications of vibra- tion and dynamic measurement require advanced data acquisition equipment, data analysis software, and associated training. Exam- ples are · Transient vibration measurement · Impact/frequency response measurement · Modal testing · Rotating equipment balancing · Direct displacement measurement (e.g., rotating shaft orbit anal- ysis) 3.2 EQUIPMENT VIBRA TION Any vibrating, reciprocating, or rotating equipment should be mounted such that it does not transmit significant levels of vibration into the surrounding or supporting structure. Vibrations transmitted ![image](/image/placeholder) VIBRATORY FORCE 10 N 100 N 1000 N 90% EFFICIENT ISOLATOR 10% TRANSMISSIBILITY ↓ 1 N 10 N 100 N TRANSMISSION Fig. 40 Transmission to Structure Varies as Function of Magnitude of Vibration Force A B 10 000 N FORCE 1000 N FORCE 99% EFFICIENCY 30% EFFICIENCY 1% TRANSMISSION 70% TRANSMISSION 100 N 700 N Fig. 41 Interrelationship of Equipment Vibration, Isolation Efficiency, and Transmission via machine mounts or attached piping, ductwork, or electrical con- nections can result in vibrating walls, floors, and/or ceilings, which in turn radiate sound and/or vibration. Hence, it is important to pro- vide vibration isolation for all attachments to a vibrating machine, including structural mounts and the connections to piping, ductwork, and the electrical system. It is also important to mitigate residual vibrations in attached piping and ductwork, even when equipment is properly isolated. Vibration can be isolated or reduced to a fraction of the original force with resilient mounts between the equipment and the support- ing structure, provided that the supporting structure has sufficient stiffness and mass. Isolation transmissibility is the percentage ofthe vibratory force transmitted to the support. Isolation efficiency is the percentage of vibratory force not transmitted to the support struc- ture. Figure 40 shows that 90% efficiency results in 10% of the vibration force being transmitted. In this case, the magnitude of transmission to the building is a function of the magnitude of the vibration force. Figure 41 shows the effect of different efficiency levels. See Equation (48) in Chapter 8 of the 2017 ASHRAE Hand- book-Fundamentals, for a more detailed explanation of isolation transmissibility and efficiency. Transmissibility and isolation efficiency are a function ofthe fre- quency of the transmitted (disturbing) force, and the natural fre- quency of the isolation system. The transmissibility is given by (34) 1 T = x 100% 2 1 - n where fa is the frequency of the disturbing force and fn is the natural frequency of the isolator. The efficiency is given by E = 100% - T (35) where Tis the transmissibility given by Equation (34). 3.3 VIBRA TION CRITERIA For the HVAC designer, vibration criteria are specified relative to three areas: (1) human response to vibration, (2) vibration levels associated with potential disruption to the use of sensitive equipment in a building, and (3) vibration severity of an operating machine. Inc. ASHRAE, 2019 user. single for Licensed | {}
23559ae5-bf99-4ebd-88a8-d0cbd361a64d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.45 �m/s VELOCITY, Chart Type: line Curve Designation Velocity Workshop Office Residential Day Residential Night Operating Room VC-A CURVE Research Laboratory VC-B CURVE VC-C CURVE VC-D CURVE VC-E CURVE item_01 8000Hz 0Hz 0Hz 0Hz 0Hz 0Hz 0Hz 0Hz 0Hz 0Hz 0Hz 0Hz 0Hz Fig. 42 Building Vibration Criteria for Vibration Measured on Building Structure Figure 42 and Table 45 present recommended acceptable criteria for vibration in a building structure (IEST 2007; Murray et al. 1997). The vibration values in Figure 42 are measured in one-third octave bands using vibration transducers (usually accelerometers) placed on the building structure near vibrating equipment or in areas containing occupants or sensitive equipment. Occupant vibration criteria are based on guidelines recommended in ANSI Standard S2.71-1983 (R2006) and ISO Standard 2631-2. For sensitive equip- ment, acceptable vibration values specified by equipment manufac- turers should be used. If none are available, then criteria from IEST (2007), as reflected in Figure 42 and Table 45, can be used. If acceptable vibration values are not available from equipment manufacturers, the values specified in Figure 43 can be used. This figure gives recommended equipment vibration severity ratings based on measured rms velocity values (IRD 1988). The vibration values in Figure 43 are measured by vibration transducers (usually accelerometers) mounted directly on equipment, equipment struc- tures, or bearing caps. Vibration levels measured on equipment and components can be affected by equipment unbalance, misalignment of equipment components, and resonance interaction between a vibrating piece of equipment and the floor on which it is placed. If a piece of equipment is aligned and balanced within acceptable tol- erances and excessive vibration levels still exist, the equipment and installation should be checked for possible resonant conditions Table 46 gives maximum allowable rms velocity levels for selected pieces of equipment. Vibration levels measured on equipment structures should be in or below the "good" region in Figure 43. Machine vibration levels in the "fair" or "slightly rough" regions may indicate potential prob- lems requiring maintenance. Machines with vibration levels in these regions should be monitored to ensure problems do not arise. Machine vibration levels in the "rough" and "very rough" regions Table 45 Human Comfort and Equipment Vibration Criteria (in rms velocity) from Continuous Vibration ¦ Human Comforta ¦ Time of Day ¦ 8 to 80 Hz Curve,a,b mm/s ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Human Comforta ¦ Time of Day ¦ rms ¦ ¦ Workshops ¦ All ¦ 0.813 ¦ ¦ Office areas ¦ Allc ¦ 0.406 ¦ ¦ Residential (good environmental standards) ¦ 0700-2200c ¦ 0.203 ¦ ¦ ¦ 2200-0700c ¦ 0.144 ¦ ¦ Hospital operating rooms and critical work areas ¦ All ¦ 0.102 ¦ ¦ Equipment Requirements (For critical, highly sensitive situations, consult manufacturer's requirements) ¦ Equipment Requirements (For critical, highly sensitive situations, consult manufacturer's requirements) ¦ Curvec ¦ ¦ Adequate for computer equipment, probe test equipment, and microscopes less than 40x ¦ Adequate for computer equipment, probe test equipment, and microscopes less than 40x ¦ 0.203 ¦ ¦ Bench microscopes up to 100x magnification; laboratory robots ¦ Bench microscopes up to 100x magnification; laboratory robots ¦ 0.102 ¦ ¦ Bench microscopes up to 400x magnification; optical and other precision balances; coordinate measuring machines; metrol- ogy laboratories; optical comparators; microelectronics manu- facturing equipment; proximity and projection aligners, etc. ¦ Bench microscopes up to 400x magnification; optical and other precision balances; coordinate measuring machines; metrol- ogy laboratories; optical comparators; microelectronics manu- facturing equipment; proximity and projection aligners, etc. ¦ 0.051 ¦ ¦ Microsurgery, eye surgery, neurosurgery; bench microscopes at magnification greater than 400x; optical equipment on isola- tion tables; microelectronic manufacturing equipment, such as inspection and lithography equipment (including steppers) to 3 mm line widthsd ¦ Microsurgery, eye surgery, neurosurgery; bench microscopes at magnification greater than 400x; optical equipment on isola- tion tables; microelectronic manufacturing equipment, such as inspection and lithography equipment (including steppers) to 3 mm line widthsd ¦ 0.025 ¦ ¦ Electron microscopes up to 30 000x magnification; microtomes; magnetic resonance imagers; microelectronics manufacturing equipment, such as lithography and inspection equipment to 1 mm detail sized ¦ Electron microscopes up to 30 000x magnification; microtomes; magnetic resonance imagers; microelectronics manufacturing equipment, such as lithography and inspection equipment to 1 mm detail sized ¦ 0.013 ¦ ¦ Electron microscopes at magnification greater than 30 000x; mass spectrometers; cell implant equipment; microelectronics manufacturing equipment, such as aligners, steppers, and other critical equipment for photolithography with line widths of 1/2 um; includes electron beam systemsd ¦ Electron microscopes at magnification greater than 30 000x; mass spectrometers; cell implant equipment; microelectronics manufacturing equipment, such as aligners, steppers, and other critical equipment for photolithography with line widths of 1/2 um; includes electron beam systemsd ¦ 0.0064 ¦ ¦ Unisolated laser and optical research systems; microelectronics manufacturing equipment, such as aligners, steppers, and other critical equipment for photolithography with line widths of 1/4 um; includes electron beam systemsd ¦ Unisolated laser and optical research systems; microelectronics manufacturing equipment, such as aligners, steppers, and other critical equipment for photolithography with line widths of 1/4 um; includes electron beam systemsd ¦ 0.0032 ¦ ¦ aAny acoustical noise caused by vibrating walls is not considered. bSee Figure 41 for corresponding curves. cIn areas where individuals are sensitive to vibration, use Residential Day curve. ¦ aAny acoustical noise caused by vibrating walls is not considered. bSee Figure 41 for corresponding curves. cIn areas where individuals are sensitive to vibration, use Residential Day curve. ¦ aAny acoustical noise caused by vibrating walls is not considered. bSee Figure 41 for corresponding curves. cIn areas where individuals are sensitive to vibration, use Residential Day curve. ¦ dClasses of microelectronics manufacturing equipment. Table 46 Maximum Allowable rms Velocity Levels ¦ Equipment ¦ Allowable rms Velocity, mm/s ¦ ¦ --- ¦ --- ¦ ¦ Pumps ¦ 3.3 ¦ ¦ Centrifugal compressors ¦ 3.3 ¦ ¦ Fans (vent sets, centrifugal, axial) ¦ 2.3 ¦ indicate a potentially serious problem; immediate action should be taken to identify and correct the problem. 3.4 SPECIFICATION OF VIBRA TION ISOLATORS Vibration isolators must be selected not only to provide required isolation efficiency but also to ensure that the natural frequency of the isolated system is not close to the natural frequency of the floor. If vibration isolators are not correctly selected, the isolator may actually amplify the force transmitted. Floor spans, equipment oper- ating speeds, equipment power, damping, and other factors are con- sidered in Table 47. Note that floor spans in Table 47 are for general reference. In fact, isolators should be selected after establishing the slab's static Inc. ASHRAE, 2019 user. single for Licensed | {}
d3981cc4-d7c0-4aab-9ef9-1552189a4f15 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.46 2019 ASHRAE Handbook-HVAC Applications (SI) Table 47 Selection Guide for Vibration Isolation (see ASHRAE Handbook Online for User-Friendly Selection Graphics) ¦ ¦ ¦ ¦ Equipment Location (Notes for Table 47, Item 1) ¦ Equipment Location (Notes for Table 47, Item 1) ¦ Equipment Location (Notes for Table 47, Item 1) ¦ Equipment Location (Notes for Table 47, Item 1) ¦ Equipment Location (Notes for Table 47, Item 1) ¦ Equipment Location (Notes for Table 47, Item 1) ¦ Equipment Location (Notes for Table 47, Item 1) ¦ Equipment Location (Notes for Table 47, Item 1) ¦ Equipment Location (Notes for Table 47, Item 1) ¦ Equipment Location (Notes for Table 47, Item 1) ¦ Equipment Location (Notes for Table 47, Item 1) ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Floor Span ¦ Floor Span ¦ Floor Span ¦ Floor Span ¦ Floor Span ¦ Floor Span ¦ Floor Span ¦ Floor Span ¦ ¦ ¦ ¦ ¦ ¦ Slab on Grade and up ¦ Slab on Grade and up ¦ Slab on Grade and up ¦ Up to 6 m C ≤ 1kPa SP ¦ Up to 6 m C ≤ 1kPa SP ¦ 6 to 9 m ≤30 ¦ 6 to 9 m ≤30 ¦ 6 to 9 m ≤30 ¦ 9 to 12 m ¦ 9 to 12 m ¦ 9 to 12 m ¦ ¦ ¦ ¦ Shaft Power kW and ¦ ¦ Base Isolator 501 ¦ ¦ Min. Defl., 19 38 ¦ Base Isolator C C A ¦ Min. Defl., ¦ Base C 19 B ¦ Isolator C 3 ¦ Min. Defl., 3 3 19 ¦ Base C C ¦ Isolator ¦ Min. Defl., ¦ Reference ¦ ¦ Equipment Type ¦ Other ¦ RPM ¦ Type ¦ Type 1 3 1 ¦ mm ¦ Type Type B B 89 64 ¦ mm B B ¦ Type 3 ¦ Type B 8,19 ¦ mm ¦ Type ¦ Type 3 ¦ mm ¦ Notes ¦ ¦ Refrigeration Machines and Chillers Packaged Units ¦ Refrigeration Machines and Chillers Packaged Units ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Water-cooled reciprocating ¦ All ¦ All and ¦ A ¦ 2 ¦ 6.4 ¦ A ¦ 4 ¦ 19 19 19 38 ¦ A 4 3 19 ¦ 38 38 ¦ C 3 ¦ A 4 ¦ 64 3 3 ¦ 2,3,12 ¦ ¦ Water-cooled centrifugal, scroll ¦ All ¦ All B C ¦ A ¦ 1 ¦ 6.4 ¦ A 4 ¦ 19 ¦ A ¦ 4 ¦ 38 ¦ A ¦ 4 ¦ 38 19 to 300 ¦ 2,3,4,8,12 3 ¦ ¦ Water-cooled screw ¦ All ¦ All 9,8 ¦ A ¦ 4 ¦ 25 ¦ A 4 ¦ 38 ¦ A ¦ 4 ¦ 64 ¦ A ¦ 4 ¦ 64 ¦ 2,3,4,12 ¦ ¦ Absorption A ¦ All ¦ All ¦ A ¦ 1 ¦ 6.4 ¦ A 4 ¦ 19 ¦ A ¦ 4 ¦ 38 ¦ A 38 ¦ 4 ≤500 Pa SP C ¦ 38 ¦ ¦ ¦ Air-cooled recip., scroll ¦ All A ¦ All ¦ A ¦ 1 C C ¦ 6.4 ¦ A 4 ¦ 38 3 ¦ A A ¦ 4 ¦ 38 ¦ A ¦ 4 ¦ 64 ¦ 2,4,5,12 7.5 ¦ ¦ Air-cooled screw C ¦ All ¦ All ¦ A ¦ 4 Up 610 mm ¦ 25 ¦ A 4 C C ¦ 38 19 3 89 ¦ B ¦ 4 ¦ 64 to 560 mm diameter ¦ B C ¦ 4 ¦ 64 ¦ 2,4,5,8,12 ¦ ¦ Air Compressors and Vacuum Pumps 38 to 500 ¦ Air Compressors and Vacuum Pumps 38 to 500 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Tank-mounted horiz. ¦ ≤7.5 300 to 500 501 and up ¦ All Propeller Fans ¦ A B ¦ 3 B 3,8,9 3,8,9 ¦ 19 ¦ A 3 All 301 A ¦ 19 3 ¦ A ¦ 3 ¦ 38 ¦ A ¦ 3 64 ¦ 38 ¦ 3,15 SP ¦ ¦ ¦ ≥7.5 ¦ All and up C 3 64 ¦ C C B 38 ¦ 3 3 2 ¦ 19 ¦ C ¦ 3 6.4 ¦ 19 ¦ C 3 ¦ 38 3 ¦ C ¦ 3 3 3 ¦ 38 ¦ 3,15 ¦ ¦ Tank-mounted vert. ¦ All ¦ All B C 3 ¦ C 3 3 3 3 89 3 ¦ 3 89 2,3,8,9,19 64 ¦ 19 38 ¦ C 3 C 501 38 C ¦ 3 ¦ 19 ¦ C 3 B ¦ 38 64 ¦ C B 3 B 3 ¦ 3 ¦ 38 300 to 500 ¦ 3,15 ¦ ¦ Base-mounted diameter and up ¦ All ¦ All B ¦ C ¦ 3 64 3 ¦ 19 64 B ¦ C ¦ 3 3 ¦ 19 64 ¦ C 3 ¦ 38 ¦ C 3 ¦ 3 ¦ 38 3 501 ¦ 3,14,15 38 ¦ ¦ Large reciprocating ¦ All A ¦ All Up to 300 B ¦ C ¦ 3 3 ¦ 19 38 ¦ C ¦ 3 38 ¦ 19 C ¦ C 3 A ¦ 38 ¦ C 3 ¦ 3 C 64 ¦ 38 Centrifugal Fans ¦ 3,14,15 ¦ ¦ Pumps ¦ Pumps ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Close-coupled ¦ ≤5.6 All All 9,19 Condensing All 7.5 to 11 Up ¦ All up Up to 300 ¦ B ¦ 2 3 ¦ 6.4 ¦ C 3 19 ¦ 19 ¦ C ¦ 3 89 ¦ 19 3 89 8,19 ¦ C ≥37 3 300 ¦ 3 4 ¦ 19 ¦ 16 ¦ ¦ ¦ ≥5.6 ¦ All Up to 300 All ¦ C C ¦ 3 ¦ 19 300 ¦ C 3 89 3 ¦ 19 300 to 500 ¦ C to 500 ¦ 3 3 ¦ 38 64 ¦ C ¦ 3 ¦ 38 Up to 2,3,8,9,19 C ¦ 16 2,3,8,9,19 ¦ ¦ Large in-line 610 mm diameter and up ¦ 3.7 to 19 All ¦ All ¦ A 64 ¦ 3 6.4 3 ¦ 19 89 64 ¦ A 3 ¦ 38 ¦ A B 3 19 ¦ 3 3 38 ¦ 38 ¦ A ¦ 3 38 A 19 ¦ 38 ¦ ¦ ¦ ¦ ≥19 2,4,8,19 ¦ All ¦ A ¦ 3 19 ¦ 38 Computer Room Units ¦ A 3 3 3 ¦ 38 ¦ A ¦ 3 3 ¦ 38 6.4 19 ¦ A A ¦ 3 3 ¦ 64 ¦ ¦ ¦ End suction and split case ¦ ≤30 ¦ All 3 ¦ C Pa ¦ 3 ¦ 19 25.4 C All ¦ C 3 Units ¦ 19 ¦ C ¦ 3 ¦ 38 ¦ C 3 3 ¦ 3 ¦ 38 ¦ 16 ¦ ¦ ¦ 30 to 93 All All ¦ All A ¦ C ¦ 3 ¦ 19 All ¦ C ¦ 3 1 ¦ 19 6.4 A ¦ C 3 1 6.4 ¦ 38 ¦ C 1 ¦ 3 ¦ 64 6.4 ¦ 10,16 38 19 ¦ ¦ ¦ ≥93 All All ¦ All A 1 19 A ¦ C ¦ 3 ¦ 19 6.4 ¦ C 3 A ¦ 38 1 19 ¦ C ¦ 3 ¦ 64 A D ¦ C Roof-mounted ¦ 3 ¦ 89 ¦ 10,16 ¦ ¦ Packaged pump systems ¦ All All A ¦ All 19 3 19 ¦ A ¦ 3 B ¦ 19 6.4 Heat Pumps, Fan-Coils, ¦ A 3 A A A ¦ 19 ¦ A ¦ 3 ¦ 38 A/D ¦ C 4 ¦ 3 ¦ 64 ¦ ¦ ¦ Cooling Towers ¦ All ¦ Up to 300 to 500 A ¦ A A ¦ 1 1 3 ¦ 6.4 ¦ 4 A 4 ¦ 89 64 38 89 ¦ A 64 ¦ 4 A ¦ 89 ¦ A 3 ¦ 4 3 ¦ 89 64 38 ¦ 5,8,18 5,18 4 ¦ ¦ ¦ ¦ 301 501 and up 89 3 ¦ A 3 ¦ 1 ¦ 6.4 ¦ A 4 A ¦ 19 ¦ A A A ¦ 4 4 4 ¦ 64 19 38 A/D ¦ A A 4 ¦ 4 4 Wall-mounted 38 3 ¦ 38 ¦ 5,18 19 ¦ ¦ Boilers ≥501 ¦ Boilers ≥501 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Fire-tube ¦ All 3 3 38 89 ¦ All 3 89 ¦ A ¦ 1 38 8,19 ¦ 6.4 C 3 9,8 AH, AC, H and v ¦ B 4 B 3,8,9 ¦ 19 3 C ¦ B ¦ 4 ¦ 38 64 ¦ B B 9,8 3 ¦ 4 4 89 C A ¦ 64 6.4 64 ¦ 4 4,9 B 19 ¦ ¦ Water-tube, copper fin Axial Fans, Plenum Fans, Cabinet Fans, Up to 560 mm diameter 3 89 ¦ All ¦ All Fan Sections, All ¦ A A ¦ 1 Centrifugal 2 3 3 ¦ 3 In-line 6.4 B C 6.4 ¦ A 1 Fans A 3 C B B ¦ 3 ¦ A 19 3 64 ¦ 1 A 3 3 ¦ 3 19 38 89 ¦ ¦ ¦ ¦ ¦ Inc. ASHRAE, 2019 user. single for Licensed | {}
a6d1855e-4c70-4b1c-a4fa-73b0cefdbfaa | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.47 Table 47 Selection Guide for Vibration Isolation (Continued) (see ASHRAE Handbook Online for User-Friendly Selection Graphics) ¦ ¦ ¦ ¦ Equipment Location (Notes for Table 47, Item 1) ¦ Equipment Location (Notes for Table 47, Item 1) ¦ Equipment Location (Notes for Table 47, Item 1) ¦ Equipment Location (Notes for Table 47, Item 1) ¦ Equipment Location (Notes for Table 47, Item 1) ¦ Equipment Location (Notes for Table 47, Item 1) ¦ Equipment Location (Notes for Table 47, Item 1) ¦ Equipment Location (Notes for Table 47, Item 1) ¦ Equipment Location (Notes for Table 47, Item 1) ¦ Equipment Location (Notes for Table 47, Item 1) ¦ Equipment Location (Notes for Table 47, Item 1) ¦ Equipment Location (Notes for Table 47, Item 1) ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Floor Span ¦ Floor Span ¦ Floor Span ¦ Floor Span ¦ Floor Span ¦ Floor Span ¦ Floor Span ¦ Floor Span ¦ Floor Span ¦ ¦ ¦ ¦ Power ¦ ¦ Slab on Grade ¦ Slab on Grade ¦ Slab on Grade ¦ Up to 6 m ¦ Up to 6 m ¦ Up to 6 m ¦ 6 to 9 m ¦ 6 to 9 m ¦ 6 to 9 m ¦ 9 to 12 m ¦ 9 to 12 m ¦ 9 to 12 m ¦ ¦ ¦ Equipment Type ¦ Shaft kW and Other ¦ RPM ¦ Base Type ¦ Isolator Type ¦ Min. Defl., mm ¦ Base Type ¦ Isolator Type ¦ Min. Defl., mm ¦ Base Type ¦ Isolator Type ¦ Min. Defl., mm ¦ Base Type ¦ Isolator Type ¦ Min. Defl., mm ¦ Reference Notes ¦ ¦ ¦ >11, ¦ Up to 300 ¦ B ¦ 3 ¦ 19 ¦ C ¦ 3 ¦ 89 ¦ C ¦ 3 ¦ 89 ¦ C ¦ 3 ¦ 89 ¦ 2,3,4,8,9 ¦ ¦ ¦ > 1 kPa SP ¦ 301 to 500 ¦ B ¦ 3 ¦ 19 ¦ C ¦ 3 ¦ 38 ¦ C ¦ 3 ¦ 64 ¦ C ¦ 3 ¦ 64 ¦ 2,3,4,9 ¦ ¦ ¦ ¦ 501 and up ¦ B ¦ 3 ¦ 19 ¦ C ¦ 3 ¦ 38 ¦ C ¦ 3 ¦ 38 ¦ C ¦ 3 ¦ 64 ¦ 2,3,4,9 ¦ ¦ Packaged Rooftop Equipment ¦ All ¦ All ¦ A/D ¦ 1 ¦ 6.4 ¦ D ¦ 3 ¦ 19 ¦ ¦ ¦ See Reference Note 17 ¦ See Reference Note 17 ¦ See Reference Note 17 ¦ See Reference Note 17 ¦ 5,6,8,17 ¦ ¦ Ducted Rotating Equipment ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Small fans, fan-powered boxes ¦ ≤300 L/s ¦ All ¦ A ¦ 3 ¦ 12.7 ¦ A ¦ 3 ¦ 12.7 ¦ A ¦ 3 ¦ 12.7 ¦ A ¦ 3 ¦ 12.7 ¦ 7 ¦ ¦ ¦ ≥301 L/s ¦ All ¦ A ¦ 3 ¦ 19 ¦ A ¦ 3 ¦ 19 ¦ A ¦ 3 ¦ 19 ¦ A ¦ 3 ¦ 19 ¦ 7 ¦ ¦ Engine-Driven Generators ¦ All ¦ All ¦ A ¦ 3 ¦ 19 ¦ C ¦ 3 ¦ 38 ¦ C ¦ 3 ¦ 64 ¦ C ¦ 3 ¦ 89 ¦ 2,3,4 ¦ Piping and Ducts (See sections on Isolating Vibration and Noise in Piping Systems and Isolating Duct Vibration for isolator selection.) Base Types: A. No base, isolators attached directly to equipment (Note 28) B. Structural steel rails or base (Notes 29 and 30) Isolator C. Concrete inertia base (Note 30) D. Curb-mounted base (Note 31) ¦ Types: 1. Pad, rubber, or glass fiber (Notes 20 and 21) 2. Rubber floor isolator or hanger (Notes 20 and 25) ¦ 4. Restrained spring isolator (Notes 22 and 24) ¦ ¦ --- ¦ --- ¦ ¦ 3. Spring floor isolator or hanger (Notes 22, 23, and 26) ¦ 5. Thrust restraint (Note 27) 6. Air spring (Note 25) ¦ Notes for Table 47: Selection Guide for Vibration Isolation These notes are keyed to the column titled Reference Notes in Table 47 and to other reference numbers throughout the table. Although the guide is conservative, cases may arise where vibration transmission to the build- ing is still excessive. If the problem persists after all short circuits have been eliminated, it can almost always be corrected by altering the support path (e.g., from ceiling to floor), increasing isolator deflection, using low- frequency air springs, changing operating speed, improving rotating com- ponent balancing, or, as a last resort, changing floor frequency by stiffen- ing or adding more mass. Assistance from a qualified vibration consultant can be very useful in resolving these problems. Note 1. Isolator deflections shown are based on a reasonably expected floor stiffness according to floor span and class of equipment. Certain spaces may dictate higher levels of isolation. For example, bar joist roofs may require a static deflection of 38 mm over factories, but 64 mm over com- mercial office buildings. Note 2. For large equipment capable of generating substantial vibratory forces and structureborne noise, increase isolator deflection, if necessary, so isolator stiffness is less than one-tenth the stiffness of the supporting structure, as defined by the deflection due to load at the equipment support. Note 3. For noisy equipment adjoining or near noise-sensitive areas, see the Mechanical Sound Isolation. section on Equipment Room Note 4. Certain designs cannot be installed directly on individual isolators (type A), and the equipment manufacturer or a vibration specialist should be consulted on the need for supplemental support (base type). Note 5. Wind load conditions must be considered. Restraint can be achieved with restrained spring isolators (type 4), supplemental bracing, snubbers, or limit stops. Also see Chapter 56. Note 6. Certain types of equipment require a curb-mounted base (type D). Airborne noise must be considered. Note 7. See section on Resilient Pipe Hangers and Supports for hanger locations adjoining equipment and in equipment rooms. Note 8. To avoid isolator resonance select isolator deflection problems, so that resonance frequency is 40% or less of the lowest normal operating speed of equipment (see Chapter 8 in the 2017 ASHRAE Handbook- - Fundamentals). Some equipment, such as variable-frequency drives, and high-speed equipment, such as screw chillers and vaneaxial fans, contain very-high-frequency vibration. This equipment creates new technical challenges in the isolation of high-frequency noise and vibration from a building' s structure. Structural resonances both internal and external to the isolators can significantly degrade their performance at high fre- quencies. Unfortunately, at present no test standard exists for measuring the high-frequency dynamic properties of isolators, and commercially available products are not tested to determine their effectiveness for high frequencies. To reduce the chance ofhigh-frequency vibration transmis- sion, add a minimum 20 mm thick elastomeric pad (type 1, Note 20) to the base plate of spring isolators (type 3, Note 22, 23, 24). For some sen- sitive locations, air springs (Note 25) may be required. If equipment is located near extremely noise-sensitive areas, follow the recommenda- tions of an acoustical consultant. Note 9. To limit undesirable movement, thrust restraints (type 5) are re- quired for all ceiling-suspended and floor-mounted units operating at 500 Pa or more total static pressure. Note 10. Pumps over 55 kW may need extra mass and restraints. Note 11. See text for full discussion. Isolation for Specific Equipment Note 12. Refrigeration Machines: Large centrifugal, screw, and recipro- cating refrigeration machines may generate very high noise levels; spe- cial attention is required when such equipment is installed in upper-story locations or near noise-sensitive areas. If equipment is located near extremely noise-sensitive areas, follow the recommendations of an acoustical consultant. Note 13. Compressors: The two basic reciprocating compressors are (1) single- and double-cylinder vertical, horizontal or L-head, which are usually air compressors; and (2) Y, W, and multihead or multicylinder air and refrigeration compressors. Single- and double-cylinder compressors generate high vibratory forces requiring large inertia bases (type C) and are generally not suitable for upper-story locations. Ifthis equipment must be installed in an upper-story location or at-grade location near noise-sensitive areas, the expected maximum unbalanced force data must be obtained from the equipment manufacturer and a vibration specialist consulted for design of the isolation system. Note 14. Compressors: When using Y, W, and multihead and multicyl- inder compressors, obtain the magnitude of unbalanced forces from the equipment manufacturer so the need for an inertia base can be eval- uated. Note 15. Compressors: Base-mounted compressors through 4 kW and horizontal tank-type air compressors through 8 kW can be installed directly on spring isolators (type 3) with structural bases (type B) if required, and compressors 10 to 75 kW on spring isolators (type 3) with inertia bases (type C) with a mass 1 to 2 times the compressor mass. Note 16. Pumps: Concrete inertia bases (type C) are preferred for all flexible-coupled pumps and are desirable for most close-coupled pumps, although steel bases (type B) can be used. Close-coupled Inc. ASHRAE, 2019 user. single for Licensed | {}
ae65f3d4-a50c-46fe-a72e-035f2846fb5f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.48 2019 ASHRAE Handbook-HVAC Applications (SI) Notes for Table 47: Selection Guide for Vibration Isolation (Continued) pumps should not be installed directly on individual isolators (type A) because the impeller usually overhangs the motor support base, causing the rear mounting to be in tension. The primary requirements for type C bases are strength and shape to accommodate base elbow supports. Mass is not usually a factor, except for pumps over 55 kW, where extra mass helps limit excess movement due to starting torque and forces. Concrete bases (type C) should be designed for a thickness of one-tenth the longest dimension with minimum thickness as follows: (1) for up to 20 kW, 150 mm; (2) for 30 to 55 kW, 200 mm; and (3) for 75 kW and up, 300 mm. Pumps over 55 kW and multistage pumps may exhibit excessive motion at start-up ("heaving"); supplemental restraining devices can be in- stalled if necessary. Pumps over 90 kW may generate high starting forces; consult a vibration specialist. Note 17. Packaged Rooftop Air-Conditioning Equipment: This equip- ment is usually installed on low-mass structures that are susceptible to sound and vibration transmission problems. The noise problems are compounded further by curb-mounted equipment, which requires large roof openings for supply and return air. The table shows type D vibration isolator selections for all spans up to 6 m, but extreme care must be taken for equipment located on spans of over 6 m, especially if construction is open web joists or thin, low-mass slabs. The recommended procedure is to determine the additional deflection caused by equipment in the roof. If additional roof deflec- tion is 6 mm or less, the isolator should be selected for up to 10 times the additional roof deflection. If additional roof deflection is over 6 mm, supplemental roof stiffening should be installed to bring the roof deflec- tion down below 6 mm, or the unit should be relocated to a stiffer roof position. For mechanical units capable of generating high noise levels, mount the unit on a platform above the roof deck to provide an air gap (buffer zone) and locate the unit away from the associated roof penetration to allow acoustical treatment of ducts before they enter the building. Vibration Isolators: Materials, Types, and Configurations Some rooftop equipment has compressors, fans, and other equipment isolated internally. This isolation is not always reliable because ofinternal short-circuiting, inadequate static deflection, or panel resonances. It is recommended that rooftop equipment over 135 kg be isolated externally, as if internal isolation was not used. Note 18. Cooling Towers: These are normally isolated with restrained spring isolators (type 4) directly under the tower or tower dunnage. High- deflection isolators proposed for use directly under the motor-fan assem- bly must be used with extreme caution to ensure stability and safety under all weather conditions. See Note 5. Note 19. Fans and Air-Handling Equipment: Consider the following in selecting isolation systems for fans and air-handling equipment: 1. Fans with wheel diameters of 560 mm and less and all fans operating at speeds up to 300 rpm do not generate large vibratory forces. For fans oper- ating under 300 rpm, select isolator deflection so the isolator natural fre- quency is 40% or less than the fan speed. For example, for a fan operating at 275 rpm, 0.4 x 275 = 110 rpm. Therefore, an isolator natural frequency of 110 rpm or lower is required. This can be accomplished with a 75 mm deflection isolator (type 3). 2. Flexible duct connectors should be installed at the intake and discharge of all fans and air-handling equipment to reduce vibration transmission to air duct structures. 3. Inertia bases (type C) are recommended for all class 2 and 3 fans and air- handling equipment because extra mass allows the use of stiffer springs, which limit heaving movements. 4. Thrust restraints (type 5) that incorporate the same deflection as isolators should be used for all fan heads, all suspended fans, and all base-mounted and suspended air-handling equipment operating at 500 Pa or more total static pressure. Restraint movement adjustment must be made under nor- mal operational static pressures. ¦ Notes 20 through 32 include figures to assist in evaluating commercially available isolators for HVAC equipment. The isolator selected for a partic- ular application depends on the required deflection, life, cost, and compatibility with associated structures. ¦ Notes 20 through 32 include figures to assist in evaluating commercially available isolators for HVAC equipment. The isolator selected for a partic- ular application depends on the required deflection, life, cost, and compatibility with associated structures. ¦ ¦ --- ¦ --- ¦ ¦ RUBBER PADS (Type 1) RUBBER MOUNTS (Type 2) ¦ Note 20. Rubber isolators are available in pad (type 1) and molded (type 2) configurations. Pads are used in single or multiple layers. Molded isolators come in a range of 30 to 70 durometer (a measure of stiffness). Material in excess of 70 durometer is usually ineffective because durometers are not a measure of stiffness of an isolator. Isolators are designed for up to 13 mm deflection, but are used where 8 mm or less deflection is required. Solid rubber and composite fabric and rubber pads are also available. They provide high load capacities with small deflection and are used as noise barriers under columns and for pipe supports. These pad types work well only when they are properly loaded and the mass load is evenly distributed over the entire pad surface. Metal loading plates can be used for this purpose. ¦ ¦ GLASS FIBER PADS (Type 1) ¦ Note 21. Glass fiber with elastic coating (type 1). This type of isolation pad is precompressed molded fiberglass pads individually coated with a flexible, moisture-impervious elastomeric mem- brane. Natural frequency of fiberglass vibration isolators should be essentially constant for the oper- ating load range of the supported equipment. Mass load is evenly distributed over the entire pad surface. Metal loading plates can be used for this purpose. ¦ ¦ SPRING ISOLATOR (Type 3) ¦ Note 22. Steel springs are the most popular and versatile isolators for HVAC applications because they are available for almost any deflection and have a virtually unlimited life. Spring isolators may have a rubber acoustical barrier to reduce transmission of high-frequency vibration and noise that can migrate down the steel spring coil. They should be corrosion protected ifinstalled outdoors or in a corrosive environment. The basic types include the following: Note 23. Open spring isolators (type 3) consist of top and bottom load plates with adjustment bolts for leveling equipment. Springs should be designed with a horizontal stiffness of at least 80% of the vertical stiffness (kx/kv) to ensure stability. Similarly, the springs should have a minimum ratio of 0.8 for the diameter divided by the deflected spring height. ¦ Inc. ASHRAE, 2019 user. single for Licensed | {}
fb86204b-d48f-430c-b8c0-84a3509abf45 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.49 ¦ Notes for Table 47: Vibration Isolators: Materials, Types, and Configurations (Continued) ¦ ¦ --- ¦ ¦ Note 24. Restrained spring isolators (type 4) have hold-down bolts to limit vertical as well as hori- RESTRAINED SPRING zontal movement. They are used with (a) equipment with large variations in mass (e.g., boilers, ISOLATOR chillers, cooling towers) to restrict movement and prevent strain on piping when water is removed, (Type 4) (b) outdoor equipment, such as condensing units and cooling towers, to prevent excessive movement due to wind loads, and (c) with any equipment subject to seismic forces. Spring criteria should be the same as open spring isolators, and snubbers should have adequate clearance so that they are acti- vated only when a temporary restraint is needed. See Chapter 56 for typical snubber types. Closed mounts or housed spring isolators consist of two telescoping housings separated by a resil- ient material. These provide lateral snubbing and some vertical damping of equipment movement, but do not limit the vertical movement. Additional vertical snubbers must be used where vertical travel must be limited (see Chapter 56). Care should be taken in selection and installation to mini- mize binding and short circuiting. ¦ ¦ Note 25. Air springs (type 6) can be designed for any frequency, but are economical only in applica- AIR SPRINGS (Type 6) tions with natural frequencies of 1.33 Hz or less (150 mm or greater deflection). They do not trans- 716 mit high-frequency noise and are often used to replace high-deflection springs on problem jobs (e.g., large transformers on upper-floor installations). A constant air supply (an air compressor with ROLLING LOBE BELLOWS an air dryer) and leveling valves are typically required. ¦ ¦ Note 26. Isolation hangers (types 2 and 3) are used for suspended pipe and equipment and have rub- RUBBER HANGER ber, springs, or a combination of spring and rubber elements. Criteria should be similar to open (Type 2) lateral stability is less important. Where support rod angular misalignment spring isolators, though is a concern, use hangers that have sufficient clearance and/or incorporate rubber bushings to pre- vent the rod from touching the housing. Swivel or traveler arrangements may be necessary for con- SPRING HANGER nections to piping systems subject to large thermal movements. (Type 3) Precompressed spring hangers incorporate some means of precompression or preloading of the 등 30 분 isolator spring to minimize movement of the isolated equipment or system. These are typically used on piping systems that can change mass substantially between installation and operation. ¦ ¦ Note 27. Thrust restraints (type 5) are similar to spring hangers or isolators and are installed in pairs to resist the thrust caused by air pressure. These are typically sized to limit lateral movement to 6.4 mm or less. S THRUST RESTRAINT . (Type 5) ¦ ¦ Note 28. Direct isolation (type A) is used when equipment is unitary and rigid and does not require additional support. Direct isolation can be used with large chillers, some fans, packaged air- DIRECT ISOLATION (Type A) handling units, and air-cooled condensers. If there is any doubt that the equipment can be supported directly on isolators, use structural bases (type B) or inertia bases (type C), or consult the equipment manufacturer. ¦ ¦ STRUCTURAL Note 29. Structural bases (type B) are used where equipment cannot be supported at individual loca- BASES (Type B) tions and/or where some means is necessary to maintain alignment of component parts in equipment. These bases can be used with spring or rubber isolators (types 2 and 3) and should have enough rigid- ity to resist all starting and operating forces without supplemental hold-down devices. Bases are made in rectangular configurations using structural members with a depth equal to one-tenth the lon- gest span between isolators. Typical base depth is between 100 and 300 mm, except where structural or alignment considerations dictate otherwise. ¦ ¦ STRUCTURAL RAILS Note 30. Structural rails (type B) are used to support equipment that does not require a unitary base (Type B) or where the isolators are outside the equipment and the rails act as a cradle. Structural rails can be used with spring or rubber isolators and should be rigid enough to support the equipment without flexing. Usual practice is to use structural members with a depth one-tenth of the longest span between isolators, typically between 100 and 300 mm, except where structural considerations dic- tate otherwise. ¦ ¦ CONCRETE BASES Note 31. Concrete bases (type C) are used where the supported equipment requires a rigid support (Type C) (e.g., flexible-coupled pumps) or excess heaving motion may occur with spring isolators. They con- sist of a steel pouring form usually with welded-in reinforcing bars, provision for equipment hold- down, and isolator brackets. Like structural bases, concrete bases should be sized to support piping elbow supports, rectangular or T-shaped, and for rigidity, have a depth equal to one-tenth the longest span between isolators. Base depth is typically between 150 and 300 mm unless additional depth is specifically required for mass, rigidity, or component alignment. ¦ ¦ Note 32. Curb isolation systems (type D) are specifically designed for curb-supported rooftop CURB ISOLATION (Type D) equipment and have spring isolation with a watertight, and sometimes airtight, assembly. Rooftop rails consist of upper and lower frames separated by nonadjustable springs and rest on top ¦ Inc. ASHRAE, 2019 Ⓒ user. single for Licensed | {}
94ff2a6c-09a4-4512-8fac-eff706e93879 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.50 2019 ASHRAE Handbook- -HVAC Applications (SI) spanned slab 's resonant frequency of the spanned slab, and using an isolator with a deflection 10 times greater than that of the slab. Mechanical equipment should not operate at frequencies near or below resonance. Also note that each item has reference notes to detail isolator selection and installation. The extra spreadsheet in the ASHRAE Handbook Online version of this chapter gathers onto one page all the notes and graphics pertaining to each equipment type. In specifying isolator deflection rather than isolation efficiency or transmissibility, a designer can compensate for floor stiffness and building resonances by selecting isolators that have more deflection than the supporting floor. Isolator deflection is related to the natural frequency of the isolators, and in turn, to the isolator efficiency. Vibration isolators are described in terms of maximum static deflec- tion, which is the amount that a spring compresses under the weight of the equipment. Ifa spring is 50 mm long when unloaded and com- presses to 25 mm when loaded, it has 25 mm of static deflection. Static deflection is directly related to vibration isolation efficiency: 25 mm static deflection equates to about 88% isolation of vibration energy, and 12 mm static deflection isolates roughly 50%. Static deflection is also related to the lowest frequency of vibration. Isolat- ing very low frequencies (less than 20 Hz) requires very large static deflections of 100 mm or more. Beyond a certain point, springs can no longer do the job, in which case two-stage isolators or special air isolators are needed. The relationship between deflection and the natural frequency of the isolated system is given by Equation (36): (36) 15.77 fn = d ~ st where dst is the static deflection in millimetres. To apply the information from Table 47, base type, isolator type, and minimum deflection columns are added to the equipment schedule. These isolator specifications are then incorporated into mechanical specifications for the project. Minimum deflections in the table are based on the experience of acoustical and mechanical consultants and vibration control man- ufacturers. Recommended isolator type, base type, and minimum static deflection are reasonable and safe recommendations for most HVAC equipment installations. The selections are based on concrete equipment room floors 100 to 300 mm thick with typical floor stiffness. The type of equipment, proximity to noise-sensitive areas, and type of building construction may alter these choices, especially in such cases as steel buildings with lightweight floors. The following method develops isolator selection for specific applications: 1. Use Table 47 for floors specifically designed to accommodate mechanical equipment. 2. Use recommendations from the 6 m span column for equipment on ground-supported slabs adjacent to noise-sensitive areas. 3. For roofs and floors constructed with open web joists; thin, long span slabs; wooden construction; and any unusual light construc- tion, evaluate all equipment with a mass of more than 140 kg to determine the additional deflection of the structure caused by the equipment. Isolator deflection should be up to 10 times the addi- tional deflection or the deflection shown in Table 47, whichever is greater. If the required spring isolator deflection exceeds com- mercially available products, consider air springs or two-stage isolation, stiffen the supporting structure, or change the equip- ment location. 4. When mechanical equipment is adjacent to noise-sensitive areas, it is important to not only provide adequate vibration isolation but also to coordinate the construction of the surrounding floors, ceilings, and walls to isolate mechanical equipment room noise. Selecting Vibration Isolators to Meet Isolator Deflection Requirements An overview of the procedure to select vibration isolators is as follows: 1. Establish total mass of equipment to be supported. This includes all equipment and support framework. The mass of piping con- nected to equipment may also need to be considered, because this may be partly supported from the equipment. 2. Establish operating mass (e.g., mass of water in a chiller or cool- ing tower). 3. Determine the location of supporting springs. 4. Calculate the distribution of weight onto each of the supporting springs using static force distribution methods. 5. Consider any dynamic forces that may change the mass distribu- tion over the supporting springs. 6. Select vibration isolators to achieve the minimum deflection based on the vibration-isolator spring constant as advised by the manufacturer. Note that the preceding procedure does not satisfy seismic restraint requirements, which must be considered in vibration isola- tor selection to meet applicable codes and standards. Where requested or for sensitive projects, the following calcula- tions may be presented for review: 1. Dry and operating masses (including any thrust forces) 2. Operating masses at each of the support points, considering the operating condition of the equipment 3. Isolator at each of the support points, given the selected vibration isolator spring constant 4. Wind forces, if installed outdoors. 3.5 VIBRA TION- AND NOISE-SENSITIVE FACILITIES Vibration-sensitive facilities identified in the section on Vibra- tion Criteria are likely to require detailed assessment. Table 47 reflects typical application of vibration isolators in buildings to sat- isfy human comfort requirements. A specialist should be engaged to design vibration isolators for facilities with sensitive noise and vibration requirements, such as concert halls or facilities with elec- tron microscopes or other diagnostic imaging equipment. The spe- cialist will select vibration isolators based on the proximity to sensitive areas, structural design of the facility, and type and oper- ating duty of vibration sources. Vibration propagation through soil may also need to be considered for any facilities close to rail lines or other vibration-generating sources. 3.6 INTERNAL VERSUS EXTERNAL ISOLATION Vibration isolators are most effective if the isolator base is attached directly to the building structure at a support point that is highly stiff compared to the isolator. In many cases, the vibrating equipment (e.g., internal components of air-handling units) can be effectively isolated with internal vibration isolators, where only the moving parts (e.g., fan/motor assembly) are supported by the iso- lators. This approach can reduce the load supported by the isolators and thus can reduce the cost ofisolation. The other primary advan- tage of internal isolation is reduction of vibration and structure- borne noise into the air-handling unit housing. Disadvantages of internal isolation can include the following: · The isolator is often not easily visible in the field to verify that it is functioning properly. · The isolator support point may be near the middle of a beam, which often provides inadequate stiffness for optimum isolator performance. Inc. ASHRAE, 2019 user. single for Licensed | {}
f77878da-ff2c-4c15-af93-81f60e9a90fb | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.51 · Short circuiting ofhoused isolators, caused by horizontal thrust of the fan, can occur. · Commonly provided isolators are not selected based on building support structure or noise criteria, and may not provide sufficient vibration control. · Internal isolation does nothing to reduce vibration in equipment casing and structure caused by air movement. Typically, vibration isolation devices should be applied to either the internal components or the external casing, but not both. It is possible to use both internal and external vibration isolation on the same air-handling unit, but isolator stiffness selection must avoid resonances at or near normal fan and motor rotational speeds. There are multiple resonance frequencies to consider: if the fan or motor operates at or near one of these frequencies, vibration levels could become excessive. The probability of such an interaction increases significantly ifthe fan and motor are driven by a variable- frequency drive. Implementing both internal and external vibration isolation on the same unit should only be attempted with the guid- ance of an experienced vibration consultant. 3.7 ISOLA TING VIBRA TION AND NOISE IN PIPING SYSTEMS All piping systems have mechanical vibration generated by the equipment and impeller-generated and flow-induced vibration and noise, which is transmitted by the pipe wall and the water column. In addition, equipment supported by vibration isolators exhibits some motion from pressure thrusts during operation. Vibration iso- lators have even greater movement during start-up and shutdown as equipment vibration passes through the isolators' resonance fre- quency. The piping system must be flexible enough to (1) reduce vibration transmission along the connected piping, (2) allow equip- ment movement without reducing the performance of vibration isolators, and (3) accommodate equipment movement or thermal movement of the piping at connections without imposing undue strain on the connections and equipment. Flow noise and vibration in piping can be reintroduced by tur- bulence, sharp pressure drops, and entrained air; however, this can be minimized by sizing pipe so that velocities are 1.2 m/s maxi- mum for pipe 50 mm and smaller and using a pressure drop lim- itation of 400 Pa per m of pipe length, with a maximum velocity of 3 m/s for larger pipe sizes. Take care not to exceed these limits. Resilient Pipe Hangers and Supports Resilient pipe hangers and supports may be used to prevent vibration and noise transmission from the piping system to the building structure and to provide flexibility in the piping. Suspended Piping. Isolation hangers described in Note 26 of Table 47 should be used for all piping in equipment rooms and up to 15 m from vibration-isolated equipment and pressure-regulating valve (PRV) stations. To avoid reducing the effectiveness of equip- ment isolators, at least the first three hangers from the equipment should provide the same deflection as the equipment isolators, with a maximum limitation of 50 mm deflection; the remaining hangers should be spring or combination spring and rubber with 20 mm deflection. The first two hangers adjacent to the equipment should be the positioning or precompressed type, to prevent load transfer to equipment flanges when the piping system is filled. The positioning hanger aids in installing large pipe, and many engineers specify this type for all isolated pipe hangers for piping 200 mm and larger. Piping over 50 mm in diameter that is suspended below or within 15 m of noise-sensitive areas should be hung with isolation hangers. Hangers adjacent to noise-sensitive areas should be the spring and rubber combination type 3. Floor-Supported Piping. Floor supports for piping in equipment rooms and adjacent to isolated equipment should use vibration iso- lators as described in Table 47. They should be selected according to the guidelines for hangers. The first two adjacent floor supports should be the restrained spring type, with a blocking feature that pre- vents load transfer to equipment flanges as the piping is filled or drained. Where pipe is subjected to large thermal movement, a slide plate (PTFE, graphite, or steel) should be installed on top of the isolator, and a thermal barrier should be used when rubber products are installed directly beneath steam or hot-water lines. Temperatures above 60°C can affect rubber isolators. Riser Supports, Anchors, and Guides. Many piping systems have anchors and guides, especially in the risers, to permit expansion joints, bends, or pipe loops to function properly. Anchors and guides are designed to eliminate or limit (guide) pipe movement and must be rigidly attached to the structure; this is inconsistent with the resil- iency required for effective isolation. The engineer should try to locate the pipe shafts, anchors, and guides in noncritical areas, such as next to elevator shafts, stairwells, and toilets, rather than adjoin- ing noise-sensitive areas. Where concern about vibration transmis- sion exists, some type of vibration isolation support or acoustical support is required for pipe supports, anchors, and guides. Because anchors or guides must be rigidly attached to the struc- ture, the isolator cannot deflect in the sense previously discussed, and the primary interest is that of an acoustical barrier. Heavy-duty rubber pads that can accommodate large loads with minimal deflec- tion can provide such an acoustical barrier. Figure 44 shows some arrangements for resilient anchors and guides. Similar resilient sup- ports can be used for the pipe. Resilient supports for pipe, anchors, and guides can attenuate noise transmission, but they do not provide the resiliency required to isolate vibration. Vibration must be controlled in an anchor guide system by designing flexible pipe connectors and resilient isolation hangers or supports. Completely spring-isolated riser systems that eliminate the anchors and guides have been used successfully in many instances and give effective vibration and acoustical isolation. In this type of isolation system, the springs are sized to accommodate thermal growth as well as to guide and support the pipe. These systems pro- vide predictable load transfer because of thermal expansion and contraction, but require careful engineering to accommodate move- ments encountered not only in the riser but also in the branch takeoff to avoid overstressing the piping. Flexible Pipe Connectors. Flexible pipe connectors (1) pro- vide piping flexibility to allow isolators to function properly, (2) protect equipment from strain caused by misalignment and expansion or contraction of piping, and (3) attenuate noise and vibration transmission along the piping (Figure 46). Connectors are available in two configurations: (1) hose type, a straight or slightly corrugated wall construction of either rubber or metal; and (2) arched or expansion-joint type, a short-length connector with one or more large-radius arches, of rubber, PTFE, or metal. Metal expansion joints are acoustically ineffective and are seldom successfully used for vibration and sound isolation in HVAC sys- tems; they should not be expected to substitute for conventional pipe vibration isolators. Piping Penetrations. HVAC systems typically have piping that must penetrate floors, walls, and ceilings. If these penetrations are not properly treated, they provide a path for airborne noise, which can destroy the acoustical integrity of the occupied space. Seal open- ings in pipe sleeves between noisy areas, such as equipment rooms, and occupied spaces with an acoustical barrier such as fibrous mate- rial and resilient acoustical caulking, or with engineered pipe pene- tration seals as shown in Figure 45. To accommodate pressure thrust, flexible connectors require an end restraint, which is either (1) added to the connector, (2) incor- Inc. ASHRAE, 2019 user. single for Licensed | {}
3f1b6c5a-b608-4dc8-940a-ddaa53e8a9fd | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.52 2019 ASHRAE Handbook-HVAC Applications (SI) ![image](/image/placeholder) PIPE CLAMP WELDED TO PIPE FOR ANCHOR; OVERSIZED FOR GUIDE ![image](/image/placeholder) RUBBER HOSE METAL HOSE RESILIENTLY ISOLATED PIPE ANCHORS AND GUIDES ![image](/image/placeholder) SPHERICAL RUBBER CONNECTOR ![image](/image/placeholder) 0 WITH CONTROL RODS RUBBER EXPANSION JOINT ![image](/image/placeholder) PIPE CLAMP WELDED TO PIPE SPRING-ISOLATED RISER SYSTEM ![image](/image/placeholder) SPRING MOUNT PAD MOUNT RUBBER MOUNT CONVENTIONAL ISOLATORS AS PIPE SUPPORTS FOR LINES WITH EXPANSION JOINTS Fig. 44 Resilient Anchors and Guides for Pipes ![image](/image/placeholder) FLEXIBLE BELLOWS CLAMPED TO SLEEVE AND PIPE Fig. 45 Acoustical Pipe Penetration Seals porated by its design, (3) added to the piping system (anchoring), or (4) built in by the stiffness of the system. Connector extension caused by pressure thrust on isolated equipment should also be con- sidered when flexible connectors are used. Overextension causes failure. Manufacturers' recommendations on restraint, pressure, and temperature limitations must be strictly observed. Sometimes these restraint systems almost eliminate the effects of the flexible connector. Hose Connectors. Hose connectors accommodate lateral movement perpendicular to length and have very limited or no axial movement capability. Rubber hose connectors can have Table 48 Recommended Live Lengthsa of Flexible Rubber and Metal Hose ¦ Nominal ¦ Nominal ¦ Nominal ¦ Nominal ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Diameter, mm ¦ Length,b mm ¦ Diameter, mm ¦ Length,b mm ¦ ¦ 20 ¦ 300 ¦ 100 ¦ 450 ¦ ¦ 25 ¦ 300 ¦ 125 ¦ 600 ¦ ¦ 40 ¦ 300 ¦ 150 ¦ 600 ¦ ¦ 50 ¦ 300 ¦ 200 ¦ 600 ¦ ¦ 65 ¦ 300 ¦ 250 ¦ 600 ¦ ¦ 80 ¦ 450 ¦ 300 ¦ 900 ¦ Fig. 46 Flexible Pipe Connectors aLive length is end-to-end length for integral flanged rubber hose and is end-to-end less total fitting length for all other types. bPer recommendations of Rubber Expansion Division, Fluid Sealing Association. molded or hand-wrapped construction with wire reinforcing, and are available with metal-threaded end fittings or integral rubber flanges. Application of threaded fittings should be limited to 75 mm and smaller pipe diameter. The fittings should be the mechanically expanded type to minimize the possibility of pressure thrust blowout. Flanged types are available in larger pipe sizes. Table 48 lists recommended lengths. Metal hose is constructed with a corrugated inner core and a braided cover, which helps attain a pressure rating and provides end restraints that eliminate the need for supplemental control assem- blies. Short lengths of metal hose or corrugated metal bellows, or pump connectors, are available without braid and have built-in control assemblies. Metal hose is used to control misalignment and vibration rather than noise and is used primarily where temperature or pressure of flow media precludes the use of other material. Table 48 provides recommended lengths. Rubber expansion or spooljoints are available in two basic types: (1) hand-wrapped with wire and fabric reinforcing, and (2) molded with fabric and wire or with high-strength fabric only (instead of metal) for reinforcing. The handmade type is available in a variety Expansion Joint or Arched Connectors. Expansion joint or arched connectors have one or more convolutions or arches and can accommodate all modes of axial, lateral, and angular movement and misalignment. When made of rubber, they are commonly called expansion joints, spool joints, or spherical connectors; in PTFE, they are known as couplings or expansion joints. Inc. ASHRAE, 2019 user. single for Licensed | {}
0664bf33-3a62-4a5f-a5de-99dd7c582569 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.53 of materials and lengths for special applications. Rubber spherical connectors are molded with high-strength fabric or tire cord rein- forcing instead of metal. Their distinguishing characteristic is a large-radius arch. The shape and construction of some designs allow use without control assemblies in systems operating to 1 MPa, and are the most effective for minimizing vibration transmission. Where thrust restraints are not built in, they must be used as described for rubber hose joints. PTFE expansion joints and couplings are similar in construction to rubber expansion joints with reinforcing metal rings. In evaluating these devices, consider temperature, pressure, and service conditions as well as each device s ability to attenuate vibration and noise. Metal hose connections can accommodate misalignment and attenuate mechanical vibration transmitted through the pipe wall, but do little to attenuate noise. This type of connector has superior resistance to long-term temperature effects. Rubber hose, expansion joints, and spherical connectors attenuate vibration and impeller-generated noise transmitted through the pipe wall. Be-cause rubber expansion joint and spherical connector walls are flexible, they can grow volumetrically and attenuate noise and vibration at blade-pass frequencies. This is a particularly desir- able feature in uninsulated piping systems, such as for condenser or domestic water, which may run adjacent to noise-sensitive areas. However, high pressure has a detrimental effect on the ability ofthe connector to attenuate vibration and noise. Because none of the flexible pipe connectors control flow or velocity noise or completely isolate vibration and noise transmis- sion to the piping system, resilient pipe hangers and supports should be used; these are shown in Note 26 for Table 47 and are described in the Resilient Pipe Hangers and Supports section. Isolating Duct Vibration Flexible canvas and rubber duct connections should be used at fan intake and discharge. However, they are not completely effec- tive because they become rigid under pressure, allowing the vibrat- ing fan to pull on the duct wall. To maintain a slack position of the flexible duct connections, thrust restraints (see Note 27, Table 47) should be used on all equipment as indicated in Table 47. Although vibration transmission from ducts isolated by flexible connectors is not common, flow pulsations within the duct can cause mechanical vibration in the duct walls, which can be transmitted through rigid hangers. Spring or combination spring and rubber hangers are recommended wherever ducts are suspended below or near a noise-sensitive area. 3.8 SEISMIC PROTECTION Seismic restraint requirements are specified by applicable build- ing codes that define design forces to be resisted by the mechanical system, depending on building location and occupancy, location of the system in the building, and whether it is used for life safety. Where required, seismic protection of resiliently mounted equip- ment poses a unique problem, because resiliently mounted systems are much more susceptible to earthquake damage from overturning forces, the impact limits of bare restraints, and resonances inherent in vibration isolators. A deficiency in seismic restraint design or anchorage may not be- come apparent until an earthquake occurs, with possible catastroph- ic consequences. Adequacy of the restraint system and anchorage to resist code design forces must be verified before the event, by either equipment tests, calculations, or dynamic analysis, depending on the item, with calculations or dynamic analysis performed under the direction of a professional engineer. These analysis items may be supplied as a package by the vibration isolation vendor. Restraints for floor-mounted equipment should be designed with adequate clearances so that they are not engaged during normal operation of the equipment. Contact surfaces (snubbers) should be protected with resilient pad material to limit shock during an earth- quake, and restraints should be strong enough to resist the forces in any direction. The integrity of these devices can be verified by a comprehensive analysis, but is more frequently verified by labora- tory tests. Calculations or dynamic analyses should have an engineer's seal to verify that input forces are obtained in accordance with code or specification requirements. Additionally, a professional engineer should make the anchorage calculations in accordance with accepted standards. For more information, see Chapter 56. 3.9 VIBRA TION INVESTIGATIONS Theoretically, a vibration isolation system can be designed to mitigate even the most extreme sources of mechanical vibration. However, isolators should not be used to mask a condition that should be corrected before it damages the equipment and its opera- tion. High vibration levels can indicate a faulty equipment operating condition in need of correction, or they can be a symptom of a res- onance interaction between a vibrating piece of equipment and the structure(s) on which it is supported or to which it is attached. Vibration investigations can include · Measurement of vibration levels on vibrating equipment (see Fig- ure 43 for recommended vibration criteria) · Measurement of vibration levels in building structures to which vibrating equipment is connected, such as a building floor, piping systems, etc. (see Figure 42 and Table 45 for recommended build- ing vibration criteria) · Examination of equipment vibration generated by system compo- nents, such as bearings, drives, pumps, etc. · Measurement of the natural frequencies (resonances) of vibrating equipment or connected structure(s) · Examination of equipment installation factors, such as equipment alignment, vibration isolator placement, etc. (see Table 47) · Measurement of the unbalance of reciprocating or rotating equip- ment components 4. COMMISSIONING In the initial design and final commissioning phases of an HVAC system, sound criteria are needed to determine the degree of noise impact and the amount of noise and vibration reduction required for acceptable background sound and vibration levels based on occu- pancy usage. This chapter is intended primarily to assist with the design phase and provide limited assistance with diagnosing prob- lems. Detailed diagnosis of problems may require the assistance of a vibration consultant or an engineer experienced in HVAC system noise and vibration analysis. Consult the section on Testing for Sound and Vibration in Chapter 39 for the commissioning phase. 5. TROUBLESHOOTING Despite all precautions, situations may arise where there is dis- turbing noise and vibration. Problems can be identified and cor- rected by · Determining which equipment or system is the source of the problem · Determining whether the problem is one of airborne sound, struc- tureborne noise, or vibration · Applying appropriate solutions Troubleshooting can be time consuming, expensive, and diffi- cult, and use of an experienced acoustical consultant is often war- ranted. Proper diagnosis of the problem is most critical to allow for developing the right solution. Once a noise or vibration transmis- sion problem exists, occupants become more sensitive and require Inc. ASHRAE, 2019 user. single for Licensed | {}
5537e95c-6ebc-4812-b003-b25e5712e160 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.54 2019 ASHRAE Handbook-HVAC Applications (SI) greater reduction of the sound and vibration levels than would ini- tially have been satisfactory. The need for troubleshooting should be minimized by properly designing, installing, and testing the system as soon as it is operational and before the building is occupied. 5.1 DETERMINING PROBLEM SOURCE A simple, accurate method of determining the problem source is to turn individual pieces of equipment on and off until the vibration or noise is eliminated. Because the source of the problem is often more than one piece of equipment or the interaction of two or more systems, it is always good practice to double check by shutting off the system and operating the equipment individually. Reynolds and Bevirt (1994) and Schaffer (2005) provide practical information on the measurement and assessment of sound and vibration in buildings. 5.2 DETERMINING PROBLEM TYPE Once the source is identified, the next step is to determine whether the problem is one ofnoise or vibration. Clearly perceptible vibration is often a clue that vibration transmission is the major cause of the problem. The possibility that low-mass wall or ceiling panels are excited by airborne noise should be considered. However, even if the vibration is not readily perceptible, the problem may still be one of vibration transmission causing structureborne noise. This can be checked using the following procedure: · Ifa sound level meter is available, some readings should be taken. If the difference between C-weighted and overall (unweighted or linear) readings is greater than 6 dB, or if the slope of the acoustic spectrum is steeper than 6 dB per octave at low frequencies (below 63 Hz), vibration is likely a contributing factor. · If excessive noise is found close to the equipment and/or main ductwork, airborne noise is probably the main contributor. · If the affected area is remote from source equipment, there is no problem in intermediary spaces, and noise does not appear to be coming from the duct system or diffusers, structureborne noise is probably the cause. One important step in diagnosing many noise or vibration prob- lems, particularly if the affected area is close to the mechanical equipment room, is to check the equipment's vibration isolation system. A simple test is to have one person listen in the affected area while another shouts loudly in the equipment room. If the voice cannot be heard, the problem is likely one of structureborne noise. If the voice can be heard, check for openings in the wall or floor separating the areas. If no such openings exist, the structure sepa- rating the areas does not provide adequate transmission loss. In these situations, see the section on Mechanical Equipment Room Sound Isolation for possible solutions. Inc. ASHRAE, 2019 user. single for Licensed Noise Problems If ductborne sound (i.e., noise from grilles or diffusers or duct breakout noise) appears to be the problem, measure the sound pres- sure levels and compare them with the design criteria (NC, RC, etc.). It is often helpful to obtain sound data with and without termi- nal devices installed. Comparison of the two results shows how much noise a given terminal device contributes. If this reveals the responsible components, the engineer can analyze each sound source using the procedures presented in this chapter to determine whether sufficient attenuation has been provided. If the sound source is a fan, pump, or similar rotating equip- ment, an important question is whether it is operating near the most efficient part ofits operating curve, where most equipment operates best and generates predictable levels of sound and vibration as pub- lished by equipment manufacturers and used in the building design. Excessive vibration and noise can occur if a fan or pump is trying to move too little or too much air or water. Check that vanes, dampers, and valves are in the correct operating position and that the system has been properly balanced. Vibration Problems Vibration and structureborne noise problems can be caused by · Equipment improperly specified or installed, poorly balanced, misaligned, or operating outside of design conditions · Equipment with inadequate or improper vibration isolation · Flanking transmission paths such as rigid pipe or duct connec- tions, obstructions under the base of vibration-isolated equip- ment, improperly installed equipment seismic restraints shorting vibration isolation, or shipping blocks not removed after the equipment has been installed and in operation · Excessive floor flexibility indicative of improper structural sup- port conditions for equipment or inadequate or improper vibra- tion isolation · Resonances in equipment, vibration isolation system, building structure, or connected structures (e.g., piping) Most field-encountered problems result from improperly selected or installed isolators and flanking paths of transmission, which can be simply evaluated and corrected. If the equipment lacks vibration iso- lators, in many cases it is possible to add isolators (see Table 47) with- out altering connected ducts or piping by using structural brackets. Floor flexibility and resonance problems are sometimes encountered and usually require analysis by experts. However, the procedures in the following sections can help identify such problems. Testing Vibration Isolation Systems. Improperly functioning vibration isolation systems are the cause of most field-encountered problems and can be evaluated and corrected by the following pro- cedures: 1. Ensure that the system is free floating by bouncing the base, which should cause the equipment to move up and down freely and easily. Note that this may not be practical on very heavy equipment. On floor-mounted equipment, check that there are no obstructions between the base and the floor that would short cir- cuit the isolation system. This is best accomplished by passing a rod under the equipment. A small obstruction might allow the base to rock, giving the impression that it is free floating when it is not. On suspended equipment, make sure that rods are not touching the hanger box. Rigid connections such as pipes and ducts can prevent equipment from floating freely, prohibit isola- tors from functioning properly, and provide flanking paths for vibration transmission. 2. Determine whether isolator static deflection is as specified or re- quired, changing it if necessary, as recommended in Table 47. A common problem is inadequate deflection caused by underloaded isolators. Overloaded isolators are not generally a problem as long as the system is free-floating and there is space between the spring coils. With most commonly used spring isolators, static deflection can be determined by measuring the operating height and comparing it to free-height information available from the manufacturer. Once the actual isolator deflection is known, determine its adequacy by comparing it with the recommended deflection in Table 47. If a transmission problem exists, it may be caused by (1) exces- sively rough equipment operation, (2) the system not being free floating or flanking path transmission, or (3) a resonance or floor stiffness problem. It is easy to determine the natural frequency of spring isolators from the static deflection determined by spring height measure- ments, but these measurements are difficult with pad and elastomeric isolators and are often not accurate in determining their natural fre- quencies. Although such isolators can theoretically provide natural frequencies as low as 4 Hz, they typically provide higher natural | {}
007ac858-645e-4e67-8b45-8ee51c1e1513 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.55 frequencies and generally do not provide the desired isolation efficiencies for upper floor equipment locations. Therefore, it is recommended to avoid using elastomeric mounts in general for (1) equipment on elevated floors, (2) major equipment, (3) critical applications, and (4) equipment on variable-speed operation; in all such cases, spring isolation should be considered and properly spec- ified. In general, it is very difficult to determine whether vibration iso- lation efficiencies intended in design have been achieved in field installations using field vibration measurements. However, vibra- tion measurements can readily be made on vibrating equipment, equipment supports, floors supporting vibration-isolated equipment, and floors in adjacent areas to determine whether vibration criteria specified in Table 45 or in Figure 42 have been achieved. Floor Flexibility Problems. Floor flexibility problems can occur with heavy equipment installed on long-span floors or thin slabs and with rooftop equipment installed on light structures of open web joist construction. If floor flexibility is suspected, the iso- lators should be one-tenth or less as stiff as the floor to eliminate the problem. Floor stiffness can be determined by calculating the additional floor deflection caused by a specific piece of equip- ment. For example, if a 5000 kg piece of equipment causes floor deflection of an additional 2.5 mm, floor stiffness is 19.6 MN/m, and an isolator combined stiffness of 1.96 MN/m or less must be used. Note that floor stiffness or spring rate, not total floor deflection, is determined. In this example, the total floor deflec- tion might be 25 mm, but if the problem equipment causes 2.5 mm of that deflection, 2.5 mm is the factor that identifies floor stiffness of 19.6 MN/m. As a general guideline, limiting the additional floor deflection (not total deflection) caused by equipment mass to 7.5 mm is advis- able, even when the equipment is provided with proper vibration isolation. This may need to be further reduced for vibration in acoustically critical adjacencies. Resonance Problems. These problems occur when the equip- ment's operating speed is the same as or close to the resonance frequency of(1) an equipment component such as a fan shaft or bear- ing support pedestal, (2) the vibration isolation system, or (3) the resonance frequency of the floor or other building component, such as a wall. Vibration resonances can cause excessive equipment vibra- tion levels, as well as objectionable and possibly destructive vibra- tion transmission in a building. These conditions must always be identified and corrected. Note that, if building structures have reso- nant frequencies, it is important to isolate equipment to avoid ener- gizing those frequencies in the structure. Structural changes can also reduce susceptibility to other excitation sources (e.g., walking, rhythmic activity). When vibrating mechanical equipment is mounted on vibration isolators on a flexible floor, there are two resonance frequencies that must be considered: that of the floor and that of the isolated equip- ment. The lower frequency should be controlled by the stiffness (and consequently the static deflection) of the vibration isolators. This frequency should be significantly less than the normal operat- ing speed (or frequency) of the mechanical equipment and is gener- ally not a problem. The higher resonance frequency is associated with and primarily controlled by the stiffness of the supporting structure. This resonance frequency is usually not affected by in- creasing or decreasing the static deflection of the mechanical equip- ment vibration isolators. Sometimes, when the floor under mechanical equipment is flexible (as occurs with some long-span floor systems and with roof systems supporting rooftop packaged units), the operating speed of the mechanical equipment can coincide with the floor resonance frequency. When this occurs, changing the static deflec- tion of the vibration isolators may not solve the problem. Alterna- tives include changing the rotating speed of the equipment, stiffening the structure, or adjusting a variable-frequency drive to avoid the resonant frequency. Also, adding mass such as a house- keeping pad in concrete under the isolator could be a possible solu- tion. Vibration Isolation System Resonance. Always characterized by excessive equipment vibration, vibration isolation system rigid- body resonance (characterized by the mass of the equipment vibrat- ing on the stiffness of the isolators) usually results in objectionable transmission to the building structure. However, transmission might not occur if the equipment is on grade or on a stiff floor. Vibration isolation system rigid-body resonances can be measured with instrumentation or, more simply, by determining the isolator's nat- ural frequency (as described in the section on Testing Vibration Iso- lation Systems) and comparing this figure to the operating speed of the equipment. When a vibration isolation system resonance problem exists, the system natural frequency must be changed using the following guidelines: · If equipment is installed on excessively stiff pad or rubber elasto- meric mounts, isolators with the deflection recommended in Table 47 should be installed. · If equipment is installed on spring isolators and there is objection- able vibration or noise transmission to the structure, determine whether the isolator is providing the designed static deflection. For example, an improperly selected or installed nominal 50 mm deflection isolator could be experiencing only 3 mm deflection under its static load, which would be in resonance with equipment operating at 500 rpm. If this is the case, the isolators should be replaced with ones having enough capacity to provide the requi- site 50 mm deflection. However, if there is no transmission prob- lem with the isolators, it is not necessary to use greater-deflection isolators than can be conveniently installed. · If equipment is installed on spring isolators and there is objection- able noise or vibration transmission, replace the isolators with springs of the deflection recommended in Table 47. · If equipment is installed on spring isolators of the recommended stiffness and there is objectionable high-frequency (200 Hz or greater) noise or vibration, it is possible that resonances internal to the spring are the culprit. These resonances, sometimes called surge frequencies, can be important in applications where equip- ment (e.g., screw compressors, inverters) generates high-frequency noise. To control their adverse effects, many isolator designs incorporate an elastomeric pad under the spring. It may also be possible to identify an elastomeric mount that can provide the desired static deflection; these typically have better high-frequency characteristics than springs. Building Resonances. These problems occur when some part of the building structure has a resonance frequency coincident with the disturbing frequency (often the operating speed) of some of the equipment. These problems can exist even if the isolator deflections recommended in Table 47 are used. The resulting objectionable noise or vibration should be evaluated and corrected. Often, the res- onance problem is associated with the floor on which the equipment is installed, but it can also occur in a remotely located floor, wall, or other building component. If a noise or vibration problem has a remote source that cannot be associated with piping or ducts, build- ing resonance must be suspected. Building resonance problems can be resolved by the following: · Reduce the vibration force by balancing the equipment. This is not a practical solution for a true resonance problem. However, it is effective when the disturbing frequency is close to the floor's natural frequency, as evidenced by the equal displacement of the Inc. ASHRAE, 2019 user. single for Licensed | {}
405209aa-c0fe-4a2c-b94c-5e60ec335763 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 49.56 2019 ASHRAE Handbook-HVAC Applications (SI) floor and the equipment, especially when the equipment is oper- ating with excessive vibration. · Change the disturbing frequency by changing the equipment operating speed. This is practical only for belt-driven equipment, or equipment driven by variable-frequency drives. · Modify the structure to shift the structural response. Although this requires upsizing the structure and can be costly, if feasible itis often the most effective means of resolving vibration issues. REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. AHRI. 2012. Sound rating of ducted air moving and conditioning equip- ment. ANSI/AHRI Standard 260-2012. Air-Conditioning, Heating, and Refrigeration Institute, Arlington, VA. AHRI. 2011. Sound performance rating of large air-cooled outdoor refriger- ating and air-conditioning equipment. ANSI/AHRI Standard 370-2011. Air-Conditioning, Heating, and Refrigeration Institute, Arlington, VA. AHRI. 2008. Method of measuring machinery sound within an equipment space. ANSI/AHRI Standard 575-2008. Air-Conditioning, Heating, and Refrigeration Institute, Arlington, VA. AHRI. 2008. Performance rating of air terminals. ANSI/AHRI Standard 880-2008. Air-Conditioning, Heating, and Refrigeration Institute, Ar- lington, VA. AHRI. 2008. Procedure for estimating occupied space sound levels in the application of air terminals and air outlets. Standard 885-2008. Air- Conditioning, Heating, and Refrigeration Institute, Arlington, VA. AMCA. 2014. Reverberant room method for sound testing of fans. ANSI/ AMCA Standard 300-2014. Air Movement and Control Association International, Arlington Heights, IL. ANSI. 2014. Sound level meters- Part 1: Specifications. Standard S1.4- 2014. American National Standards Institute, Washington, D.C. ANSI. 2014. Sound level meters- Part 2: Pattern evaluation tests. Standard S1.4-2014. American National Standards Institute, Washington, D.C. ANSI. 2014. Octave-band and fractional-octave-band filters-Part 1: Spec- ifications. Standard S1.11-2014. American National Standards Institute, Washington, D.C. ANSI. 2012. Guide to the evaluation of human exposure to vibration in buildings. Standard S2.71-1983 (R2012). American National Standards Institute, Washington, D.C. ANSI. 2008. Criteria for evaluating room noise. Standard S12.2-2008. American National Standards Institute, Washington, D.C. ASA. 2010. Acoustical performance criteria, design requirements, and guidelines for schools, part 1: Permanent schools, and part 2: Relocatable classroom factors. ANSI/ASA Standard S12.60-2010. Acoustical Soci- ety of America, Melville, NY. ASA. 2015. Procedure for measuring the ambient noise level in a room. ANSI/ASA Standard S12. 72-2015. Acoustical Society of America, Mel- ville, NY. ASHRAE. 1997. Laboratory method of testing to determine the sound power in a duct. ASHRAE Standard 68-1997/AMCA Standard 330-97. ASHRAE. 2011. Method of testing for rating the performance of air outlets and inlets. ANSI/ASHRAE Standard 70-2006 (RA2011). ASTM. 2013. Standard test method for laboratory measurements of acous- tical and airflow performance of duct liner materials and prefabricated silencers. Standard E477-2013. American Society for Testing and Mate- rials, West Conshohocken, PA. Beatty, J. 1987. Discharge duct configurations to control rooftop sound. Heating/Piping/Air Conditioning (July). Beranek, L.L. 1960. Noise reduction. McGraw-Hill, New York. Beranek, L.L. 1971. Noise and vibration control. McGraw-Hill, New York. Beranek, L.L. 1989. Balanced noise criterion (NCB) curves. Journal of the Acoustic Society ofAmerica (86):650-654. Blazier, W.E., Jr. 1981a. Revised noise criteria for design and rating ofHVAC systems. ASHRAE Transactions 87(1):647-657. Paper CH-81-06-2. Blazier, W.E., Jr. 1981b. Revised noise criteria for application in the acous- tical design and rating of HVAC systems. Noise Control Engineering Journal 16(2):64-73. Blazier, W.E., Jr. 1993. Control of low frequency noise in HVAC air- handling equipment and systems. ASHRAE Transactions 99(2):1031- 1036. Paper DE-93-17-2. Blazier, W.E., Jr. 1995. Sound quality considerations in rating noise from heating, ventilating and air-conditioning (HVAC) systems in buildings. Noise Control Engineering Journal 43(3). Blazier, W.E., Jr. 1997. RC Mark II; a refined procedure for rating the noise of heating, ventilating and air-conditioning (HVAC) systems in build- ings. Noise Control Engineering Journal 45(6). Broner, N. 1994. Low-frequency noise assessment metrics- What do we know? (RP-714). ASHRAE Transactions 100(2):380-388. Paper 3821. Bullock, C.E. 1970. Aerodynamic sound generation by duct elements. ASHRAE Transactions 76(2):97-109. Paper KA-2147. Cummings, A. 1983. Acoustic noise transmission through the walls of air- conditioning ducts. Final Report, Department of Mechanical and Aero- space Engineering, University of Missouri, Rolla. Cummings, A. 1985. Acoustic noise transmission through duct walls. ASHRAE Transactions 91(2A):48-61. Paper 2889. Cunefare, K., and A. Michaud. 2008. Reflection of airborne noise at duct ter- minations. ASHRAE Research Project RP-1314, Final Report. Ebbing, C.E., and W.E. Blazier, Jr. 1992. HVAC low frequency noise in buildings. Proceedings INTER-NOISE 92(2):767-770. Ebbing, C.E., and W.E. Blazier, Jr. 1998. Application of manufacturer 's sound data. ASHRAE. Ebbing, C.E., D. Fragnito, and S. Inglis. 1978. Control of low frequency duct-generated noise in building air distribution systems. ASHRAE Transactions 84(2):191-203. Paper AL-2503. Egan, M.D. 1988. Architectural acoustics. McGraw-Hill, New York. Harold, R.G. 1986. Round duct can stop rumble noise in air-handling instal- lations. ASHRAE Transactions 92(2A):189-202. Paper 2988. Harold, R.G. 1991. Sound and vibration considerations in rooftop installa- tions. ASHRAE Transactions 97(1):445-451. Paper NY-91-03-3. Herrin, D.W., K. Ruan, and T-W. Wu. 2016. full-frequency numerical mod- eling of sound transmission in and radiation from lined ducts. ASHRAE Research Project RP-1529, Final Report. IEST. 2007. Considerations in clean room design. IEST Recommended Practice RP-CC012.2. Institute of Environmental Sciences and Technol- ogy, Rolling Meadows, IL. Ingard, U., A. Oppenheim, and M. Hirschorn. 1968. Noise generation in ducts (RP-37). ASHRAE Transactions 74(1):V. 1.1-V.1.10. IRD. 1988. Vibration technology, vol. 1. IRD Mechanalysis, Columbus, OH. ISO. 2003. Mechanical vibration and shock- Evaluation of human expo- sure to whole body vibration, Part 2: Vibration in buildings. Standard 2631-2-2003. International Organization for Standardization, Geneva, Switzerland. ISO. 1996. Acoustics-Attenuation of sound during propagation out- doors-Part 2: General method of calculation. Standard 9613-2-1996. International Organization for Standardization, Geneva, Switzerland. Kuntz, H.L. 1986. The determination of the interrelationship between the physical and acoustical properties of fibrous duct liner materials and lined duct sound attenuation. Report 1068. Hoover Keith and Bruce, Houston, TX. Kuntz, H.L., and R.M Hoover. 1987. The interrelationships between the physical properties of fibrous duct lining materials and lined duct sound attenuation. ASHRAE Transactions 93(2):449-470. Paper 3082. Lilly, J. 1987. Breakout in HVAC duct systems. Sound & Vibration 21(10). Machen, J., and J.C. Haines. 1983. Sound insertion loss properties of lina- coustic and competitive duct liners. Report 436-T-1 778. Johns-Manville Research and Development Center, Denver, CO. Mouratidis, E., and J. Becker. 2004. The acoustic properties of common HVAC plena (RP-1026). ASHRAE Transactions 110(2):597-696. Paper NA-04-3-1. Murray, T.M., D.E. Allen, and E.E. Ungar. 1997. Steel design guide series 11: Floor vibrations due to human activity. American Institute of Steel Construction, Chicago. OSHA. 2011. Occupational noise exposure. 29CFR1910.95. Code of Fed- eral Regulations, Occupational Safety and Health Administration, U.S. Department of Labor, Washington, D.C. Persson-Wayne, K., S. Benton, H.G. Leventhall, and R. Rylander. 1997. Effects on performance and work quality due to low frequency ventila- tion noise. Journal of Sound and Vibration 205(4):467-474. Inc. ASHRAE, 2019 user. single for Licensed | {}
59f16c9c-6ff1-4cb2-aced-76da70badcea | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Noise and Vibration Control 49.57 Reynolds, D.D., and J. Albright. 2018. The effect of lining length on the insertion loss of acoustical duct liner in sheet metal ductwork. ASHRAE Research Project RP-1408, in progress. Reynolds, D.D., and W.D. Bevirt. 1994. Procedural standards for the mea- surement and assessment ofsound and vibration. National Environmen- tal Balancing Bureau, Rockville, MD. Reynolds, D.D., and J.M. Bledsoe. 1989a. Sound attenuation of unlined and acoustically lined rectangular ducts. ASHRAE Transactions 95(1):90-95. Paper 3207. Reynolds, D.D., and J.M. Bledsoe. 1989b. Sound attenuation of acoustically lined circular ducts and radiused elbows. ASHRAE Transactions 95(1): 96-99. Paper 3208. Reynolds, D.D., and J.M. Bledsoe. 1991. Algorithms for HVAC acoustics. ASHRAE. Schaffer, M.E. 2005. A practical guide to noise and vibration control for HVAC systems, 2nd ed. ASHRAE. Schultz, T.J. 1985. Relationship between sound power level and sound pressure level in dwellings and offices. ASHRAE Transactions 91(1A): 124-153. Stabley, R.E. 2006. Sound ratings of water-cooled chillers- Sound pressure or power levels? In Proceedings from Inter-Noise 2006, Honolulu. Insti- tute of Noise Control Engineering of the USA, Indianapolis, IN. Thompson, J.K. 1981. The room acoustics equation: Its limitation and po- tential. ASHRAE Transactions 87(2):1049-1057. Paper CI-81-12-2. Ver, I.L. 1978. A review of the attenuation of sound in straight lined and unlined ductwork of rectangular cross section. ASHRAE Transactions 84(1):122-149. Paper AT-2477-2478. Ver, I.L. 1982. A study to determine the noise generation and noise attenu- ation of lined and unlined duct fittings. Report 5092. Bolt, Beranek and Newman, Boston. Ver, I.L. 1983a. Noise generation and noise attenuation of duct fittings- A review: Part I (RP-265). ASHRAE Transactions 90(2A):354-382. Paper KC-2849. Ver, I.L. 1983b. Noise generation and noise attenuation of duct fittings- -A review: Part II (RP-265). ASHRAE Transactions 90(2A):383-390. Paper KC-2850. Wang, L.M., E.E. Ryherd, and C.C. Novak. 2013. Productivity and percep- tion based evaluation ofindoor noise criteria. ASHRAE Research Project RP-1322, Final Report. Warnock, A.C.C. 1998. Transmission of sound from air terminal devices through ceiling systems. ASHRAE Transactions 104(1A):650-657. Paper 4160. Wells, R.J. 1958. Acoustical plenum chambers. Noise Control (July). Woods Fan Division. 1973. Designfor sound. English Electric Company. BIBLIOGRAPHY AHRI. 2013. Performance and calibration of reference sound sources. ANSI/AHRI Standard 250-2013. Air-Conditioning, Heating, and Re- frigeration Institute, Arlington, VA. AHRI. 2008. Sound rating of outdoor unitary equipment. ANSI/AHRI Stan- dard 270-2008. Air-Conditioning, Heating, and Refrigeration Institute, Arlington, VA. AHRI. 2010. Application of sound rating levels of outdoor unitary equip- ment. ANSI/AHRI Standard 275-2010. Air-Conditioning, Heating, and Refrigeration Institute, Arlington, VA. AHRI. 2011. Requirements for the qualification of reverberant rooms in the 63 Hz octave band. ANSI/AHRI Standard 280-2011. Air-Conditioning, Heating, and Refrigeration Institute, Arlington, VA. AHRI. 2008. Sound rating and sound transmission loss of packaged terminal equipment. ANSI/AHRI Standard 300-2008. Air-Conditioning, Heat- ing, and Refrigeration Institute, Arlington, VA. AHRI. 2008. Sound rating of non-ducted indoor air-conditioning equip- ment. ANSI/AHRI Standard 350-2008. Air-Conditioning, Heating, and Refrigeration Institute, Arlington, VA. AHRI. 2011. Method of measuring sound and vibration of refrigerant com- pressors. ANSI/AHRI Standard 530-2011. Air-Conditioning, Heating, and Refrigeration Institute, Arlington, VA. AIA. 2006. Guidelines for design and construction of health care facilities. American Institute of Architects, Washington, D.C. ANSI. 2012. Mechanical vibration and shock-Evaluations of human expo- sure to whole-body vibration-Part 1: General requirements. ANSI/ ASA Standard S2.72-2010 (R2012). American National Standards Insti- tute, Washington, D.C. ANSI. 2012. Determination of sound power levels and sound energy levels of noise sources using sound pressure- Precision methods for reverber- ation test rooms. ANSI/ASA Standard S12.51-2012/ISO Standard 3741:2010. American National Standards Institute, Washington, D.C. ANSI. 2011. Determination of sound power levels and sound energy levels noise sources using sound pressure Engineering methods for an essen- tially free field over a reflecting plane. ANSI/ASA Standard S12.54- 2011/ISO Standard 3744:2010. American National Standards Institute, Washington, D.C. ASHRAE. 2013. Ventilation for acceptable indoor air quality. ANSI/ ASHRAE Standard 62.1-2013. DHHS. 2014. Thirteenth report on carcinogens. U.S. Department of Health and Human Services, Public Health Service, Washington, D.C. Available from Ver.ntp.niehs.mih.gov/pubhealth/toc/roc1 3/index.html. Environment Canada. 1994. Mineral fibres: Priority substances list assess- ment report. Canadian Environmental Protection Act, Ottawa. Morey, P.R., and C.M. Williams. 1991. Is porous insulation inside an HVAC system compatible with healthy building? ASHRAE IAQ Symposium. Reynolds, D.D., and W.D. Bevirt. 1989. Sound and vibration design and analysis. National Environmental Balancing Bureau, Rockville, MD. Schultz, T.J. 1972. Community noise ratings. Applied Science Publishers, London. SMACNA. 2006. HVAC systems duct design, 4th ed. Sheet Metal and Air Conditioning Contractors' National Association, Vienna, VA. Ver, I.L. 1983. Prediction of sound transmission through duct walls: Breakout and pickup. ASHRAE Transactions 90(2A):391-413. Paper KC-2851. RESOURCES of Acoustical Society of America (ASA) www.acousticalsociety.org Associated Air Balance Council (AABC) www.aabc.com Institute of Noise Control Engineering (INCE) www.inceusa.org National Council of Acoustical Consultants (NCAC) www.ncac.com National Environmental Balancing Bureau (NEBB) www.nebb.org Noise Pollution Clearinghouse www.nonoise.org North American Insulation Manufacturers Association (NAIMA) www.naima.org Sheet Metal and Air Conditioning Contractors' National Association (SMACNA) www.smacna.org Testing, Adjusting and Balancing Bureau (TABB).. www.tabbcertified.org The Air-Conditioning, Heating, and Refrigeration Institute (AHRI) www.ahrinet.org Vibration Institute www.vi-institute.org Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
fbc3bb71-0bf1-44cd-b02c-99293848b405 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 50 WATER TREATMENT: DEPOSITION, CORROSION, AND BIOLOGICAL CONTROL ¦ WATER QUALITY AND ITS SOURCES ¦ 50.1 ¦ Corrosion and Corrosion Control ¦ 50.7 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Water Characteristics ¦ 50.1 ¦ Biological Growth Control ¦ 50.12 ¦ ¦ Water Sources ¦ 50.2 ¦ Nonchemical and Physical Water Treatment Methods ¦ 50.15 ¦ ¦ WATER TREA TMENT ¦ 50.4 ¦ Water Systems ¦ 50.16 ¦ ¦ Control ¦ 50.4 ¦ TERMINOLOGY ¦ 50.23 ¦ T HIS chapter covers the fundamentals of water treatment and conditioning. It provides guidance on the treatment of water and water-based fluids used in heating, air-conditioning, refrigeration, and process systems, with a focus on the control of corrosion, scale, fouling, and biological growth. Proper treatment improves the perfor- mance and energy efficiency of these systems while helping to pro- tect human health and safety. Water treatment extends the life of equipment in both open- and closed-loop systems. Water treatment can help conserve water resources as well as enable the use of alter- native sources of water. All of these benefits help to promote a health- ier, more sustainable environment. 1. WATER QUALITY AND ITS SOURCES 1.1 WATER CHARACTERISTICS Water has unique properties that make it ideal for heating, cool- ing, and steam generating processes. Water is the only common sub- stance that exists in all three states of matter (solid [ice], liquid [water], and gas [steam]) at normal earth temperatures. Water ab- sorbs more heat for a given temperature rise than any other common inorganic substance. Water expands 1600 times as it evaporates to form water vapor and steam at atmospheric pressure. Steam can carry large quantities of heat. Such qualities position water as the ideal material for heating, cooling, and power generating processes. Water supplies contain varying amounts of impurities that can lead to scale formation, corrosion, and other problems in industrial equipment. Starting with rain, water accumulates impurities from its surroundings, dissolving minerals and picking up various substances from the air, soil, vegetation, and other materials. For this reason, water is often referred to as the universal solvent. Falling rain dis- solves carbon dioxide and oxygen from the atmosphere. As carbon dioxide breaks up in water, it forms carbonic acid (H2CO3). When carbonic acid makes contact with soil or rock strata containing lime- stone (CaCO3), it slowly dissolves the calcium to form highly solu- ble calcium bicarbonate. This process occurs in soil or rock strata where temperatures are relatively cool (less than 21°C). Unfortu- nately, bicarbonate does not remain stable as water warms, and the limestone dissolution can be quickly reversed to reform calcium car- bonate when hard water is heated. Calcium carbonate that reforms in water used in heating or air-conditioning applications can eventually become scale, which can increase energy costs, maintenance time, and equipment shutdowns, and can eventually lead to the need for equipment replacement. Water's composition can change as it is transported in pipelines, heated to make steam, or evaporated for cooling or other heat ex- change processes. Impurities in water may reach a solubility limit and be deposited along the way, or the impurities in water may act to The preparation of this chapter is assigned to TC 3.6, Water Treatment. corrode the metal equipment containing it. The actions of water in HVAC systems depend on the types of impurities and the tempera- tures and pressures to which it is subjected, among other factors. The following definitions present the most relevant terms chem- ical and physical terms, properties or characteristics of water rele- vant to water treatment and that affect its use in HVAC and other applications. Parts per million (ppm) is a dimensionless ratio, used in water treatment to express concentration (e.g., one gram in a million grams, one mL per L). Dissolved minerals and impurities commonly found in water are present at very low concentration (e.g., milli- grams in a full glass of water). The most convenient ratio to express concentration is then milligrams per million milligrams, or milli- grams per litre (L), of water (the mass of a litre of water is almost equivalent to 1,000,000 milligrams). In water treatment, ppm con- centration is almost always expressed in mg/L. Hardness refers to the amount of calcium and magnesium (typi- cally expressed in ppm as CaCO3) in the water. It is a historical term referring to the potential for formation of hard calcium and magne- sium carbonate scales, such as those found in improperly treated boilers and cooling-water systems. Harder water contributes to scale formation because heating encourages deposition of calcium car- bonate, or lime scale. Solubility of most calcium and magnesium salts decreases with an increase in temperature, so these salts tend to form scale on heat transfer surfaces where the metal skin tempera- ture is greater than the bulk water temperature. Boiler and cooling- water treatment programs are designed to control deposition of hardness salts through pretreatment removal ofhardness (e.g., water softening by ion exchange) or internal chemical additive condition- ing to solubilize, remove, or otherwise control deposition. Alkalinity is a measure of the capacity of water to neutralize strong acids and bases, defined in a specific water testing procedure. This procedure uses a measurable amount of a dilute acid solution of known concentration to change the color of two specific indicators, phenolphthalein and methyl orange. Alkalinity is the measured car- bonate and bicarbonate minerals (calculated as calcium carbonate [CaCO3]), and refers to the primary alkaline earth minerals. Alka- linity also includes hydroxide ion (OH-), when present. All natural waters contain some alkalinity. The presence of alkalinity contrib- utes to scale formation, because it can contribute carbonate ions, driving formation of calcium carbonate. In natural waters, alkalinity almost always consists of bicarbonate, although some carbonate al- kalinity may also be present. Borate, hydroxide, phosphate, and oth- er constituents, if present, are included in the alkalinity measurement in treated waters. Alkalinity is measured using two different end-point indicators. The phenolphthalein alkalinity (P alkalinity) measures the strong alkali present, including carbonate and hydroxide, and the methyl orange alkalinity (M alkalinity), or total alkalinity, measures the total alkalinity in the water. Note that total alkalinity includes the phenolphthalein alkalinity. For most natural waters, the actual 50.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
634f8ce4-a2d6-4e7c-b72b-dcd397a71b3b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 50.2 Table 1 Alkalinity Relationship Based on P and M Tests ¦ Situation ¦ Hydroxyl ¦ Level of Alkalinity Contributed by Carbonate ¦ Bicarbonate ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ P = M ¦ M ¦ 0 ¦ 0 ¦ ¦ P > 1/2M ¦ 2P - M ¦ 2 (M - P) ¦ 0 ¦ ¦ P = 1/2M ¦ 0 ¦ M ¦ 0 ¦ ¦ P < 1/2M ¦ 0 ¦ 2P ¦ M - 2P ¦ ¦ P = 0 ¦ 0 ¦ 0 ¦ M ¦ P= P alkalinity = phenolphthalein alkalinity M = M alkalinity = methyl orange (total) alkalinity chemical species present can be estimated after performing two spe- cific alkalinity tests. Treated waters may also include the hydroxide alkalinity contributed by OH- (Table 1). pH is a measure of the concentration of hydrogen ions (the acid strength) of a solution. Mathematically, it is defined as the negative logarithm of the hydrogen ion concentration (pH of 1 is very acidic; pH of 14 is very basic; a pH of 7 is neutral at ambient temperature.) The pH concept is fundamental to an understanding of water chem- istry and to control of pretreatment systems, boilers, and cooling towers. All water systems depend on either pH control or maintain- ing pH above a specified minimum level. Unexpected changes in pH (~1.0 to 1.5 pH increase or decrease) are usually a warning of prob- lems that must be corrected. Chlorides are the total of dissolved chloride components of salts such as sodium chloride, potassium chloride, calcium chloride, magnesium chloride, etc. Sodium chloride and calcium chloride (CaCl2) are the most common chloride salts found in water. Chlo- rides do not ordinarily contribute to scale, because they are very sol- uble. However, chlorides are corrosive and can be excessively so when present in high concentration, as in seawater, because of their ability to react with and weaken the natural protective oxide films present on most metals. Determining the concentration of chlorides in water is a useful measuring tool in evaporative systems for deter- mining cycles of concentration. Most water constituents change in concentration when common treatment chemicals are added or due to chemical changes that take place in normal operation. Chlorides are not affected by such changes, so, with few exceptions, only evaporation affects chloride concentration. Therefore, the ratio of chlorides in a water sample from an operating system to those ofthe makeup water provides a measure of how much the water has been concentrated. (Note: Chloride levels will change if the system is treated with chemicals releasing chloride.) Conductivity, or specific conductance, measures the ability of water to conduct electrical current and act as an electrolyte. Con- ductivity increases with an increase in total dissolved solids (ions) present in the water. Specific conductance can be used to estimate total dissolved solids. Dissolved solids consist of salts, including water hardness, and other materials that combine with water as a solution. They can affect the formation of corrosion and scale. Total dissolved solids are referred to as TDS. Dissolved solids content is most commonly determined instrumentally based on the electrical conductivity of water or the weight of residue after water is totally evaporated. Suspended solids include both organic and inorganic solids sus- pended in water (particularly unpurified water from surface sources or those that have been circulating in open equipment). Organic matter in surface supplies may be colloidal (homogeneously sus- pended). Naturally occurring compounds such as lignin and tannins are often colloidal. At high velocities, hard suspended particles can abrade equipment. Settled suspended matter of all types can con- tribute to corrosion, as it fosters corrosive microbiology. Total sus- pended solids are referred to as TSS and should not include TDS. 2019 ASHRAE Handbook-HVAC Applications (SI) Silica is dissolved sand or silica-bearing rock (such as quartz) through which the water flows. Silica is the cause of very hard and tenacious scales that can form in heat transfer systems. These de- posits can be particularly hard to remove if allowed to concentrate. Fortunately, silicate deposition is less common than other deposits. Soluble iron in water can originate from metal corrosion in wa- ter systems or as a contaminant in the makeup water supply. The iron can form heat-insulating deposits by precipitation as iron hy- droxide or iron phosphate in the presence of phosphate-based water treatment or phosphate in the makeup water. Sulfates are the dissolved sulfate salts of sodium, potassium, cal- cium, and magnesium in the water. Their presences is the product of dissolution of sulfate-bearing rock, such as gypsum. Calcium and magnesium sulfate scale is very hard and difficult to remove and greatly interferes with heat transfer. Sulfates also contribute to scale formation in high-calcium waters. Calcium sulfate scale, however, forms at much higher concentrations than the more common calcium carbonate scale. High sulfates also contribute to increased corrosion because of their high conductivity and support of microbiologically influenced corrosion (MIC). Turbidity is the amount of opacity caused by suspended matter and is often described as cloudiness or haziness in water. It should not be confused with color. Water may be dark in color but still clear and not turbid. Turbidity is caused by suspended matter, in a finely divided state, which can scatter and deflect incoming light. Clay, silt, organic matter, microscopic organisms, and similar materials are common causes of turbidity. Although suspended matter and turbidity are closely related, they are not synonymous. Suspended matter is the quantity of insoluble material in water that can be removed by filtration. Levels of suspended matter and turbidity will likely change based on the dynamics of water flow or lack of flow. Turbidity of water used in HVAC systems should be as low as pos- sible, particularly for steam boiler feedwater. Turbidity can concen- trate in the boiler and settle as sludge or mud. It can also cause increased boiler blowdown, plugging, overheating, priming, and foaming. Biological matter such as bacteria, algae, and fungi can be pres- ent in water, and their growth in water systems can cause operating, maintenance, and health problems. Microbial growth should be as- sumed to occur in most water systems below 65°C. Problems caused by biological materials range from green algae growth in cooling towers to bacterial slime formations. This growth can plug equip- ment, drastically reduce heat exchanger (transfer) efficiencies, and cause microbial corrosion. Holding time index (HTI) is defined as the time required to completely exchange the volume of a system via bleed off. It calcu- lated by dividing system volume by the rate of system bleed off, or blowdown. HTI is reflective of the amount of aging within a system. Dispersant is a term used to express an additive's ability to aid in suspending very small particles, so they do not readily agglom- erate, settle, or adhere to surfaces. Dispersants are typically chain- like compounds (polymers) that can attach to and engulf very small particles. Dispersive polymers are designed to include area of elec- trical negative charge to impart repulsive activity between polymer- engulfed particles. 1.2 WATER SOURCES Potable Water Sources Municipal water sources in the United States are generally of high quality and in compliance with federal government (EPA) stan- dards as well as state and local requirements. Depending on the pri- mary source, water properties may be quite constant, as where water is drawn from the Great Lakes or fixed-strata deep wells. In contrast, some properties are quite variable in the more arid parts of the Inc. ASHRAE, 2019 user. single for Licensed | {}
a54fc840-9547-42e8-b744-a2ba80c7a13a | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | W ater Treatment: Deposition, Corrosion, and Biological Control 50.3 United States, where water may be obtained from rivers, lakes, or wells as season and water demand dictate. Highly variable water properties can be particularly challenging in management of boiler and cooling tower treatment programs (e.g., obtaining desired response from treatment control equipment, maintaining proper function of water conditioning equipment such as water softeners, dealing with water that varies between being corrosive and being scale forming). Municipal supplies, though free of contaminants initially, can pick up iron corrosion debris from miles-long delivery mains leading to episodes of iron-rich "red water. Municipal water should also not be presumed microbiologically sterile. Water mains typically possess biofilm of significant thickness. Corporate, public, and private water well sources of potable water are generally have lower quality, consistency of chemical properties, or reliability of supply. In addition, issues of odor, taste, or turbidity may arise, and contaminants typically not found in mu- nicipally processed water may be present. Alternative Water Sources Facilities are under continuous pressure to reduce costs and operate in a more environmentally responsible manner. Historically, energy conservation has overshadowed water conservation in these efforts. However, in many locations, the reduced availability and increased cost of water now make water conservation much more attractive. More facilities are subject to limits on water consumption and the amount of wastewater that can be discharged. Although there are energy source alternatives to oil and gas, there is no sub- stitute for fresh water. The economic and environmental payback on reducing water usage is greater than ever. As a large consumer of potable water, evaporative cooling-water systems, including cooling towers, are an obvious target for water conservation efforts. Because of supply and cost pressures, more facilities are considering alternative makeup water sources, such as air handler condensate, rainwater, and reclaim water. In some cases, alternative water sources are blended with potable water to improve water use efficiency. Using one or more of these alternative water sources for cooling tower makeup conserves fresh water for other uses and can provide significant cost savings. Evaluating an Alternative Water Source. It is important to un- derstand the impurities in an alternative makeup water source and how they affect cooling tower operation before substituting for po- table water. Some water sources can be successfully used without further treatment, whereas others require additional treatment mea- sures to control problems related to corrosion, scale, and microbio- logical growth. Air Handler Condensate. In warm, humid climates, the normal operation of air-conditioning equipment produces large quantities of condensate from the air handler cooling coils. This cold, near- distilled-quality water is typically sent to the drain. In some cases, this water can be readily recovered for other uses, including cooling tower makeup. Because air handler condensate does not contain the dissolved mineral impurities present in potable water, using this cold, nearly pure water for cooling tower makeup also allows oper- ation at lower bleed rates. Because the quantity of condensate generated by a cooling coil is a direct function of the airflow rate and change in the relative humidity, it varies considerably throughout the year. For example, a 3517 kW cooling load in a commercial facility with 25% outdoor air produces 0.30 L/s of condensate when the outdoor air temperature is 29°C with 80% relative humidity (rh) and 0.17 L/s with 60% rh. Case studies have shown that 10 to 40% of cooling tower makeup require- ments can often be met with air handler condensate in facilities that operate in warm, humid climates. Depending on the location of the air-handling units and the cooling towers, the collection system can be as simple as a gravity- fed tank with a level controller and pump. Corrosion-resistant tanks and piping are recommended because of the corrosivity of such pure water. Typically, an oxidizing biocide is added to the condensate storage tank to prevent microbiological problems. Each facility is different, but the water savings and payback on using air handler condensate for cooling tower makeup water can be significant. The need for cooling tower makeup and the availability of it from cooling coils are generally simultaneous, thus minimizing storage costs. Rainwater. Although unpredictable, rainwater is a good alterna- tive source in some areas. Approximately 1 litre of water can be recovered per millimetre of rain per square metre of collection sur- face. For a 200 m2 roof, this translates to about 200 litres of water per millimetre of rain. A typical rainwater recovery system directs rainwater from the roof to a storage tank rather than a storm sewer. This cache can then be used for various purposes throughout a facility, including irriga- tion and cooling tower makeup. Parking decks can also be used to harvest rainwater; however, special media filters are required to remove oil and other contaminants before use. Like air handler condensate, rainwater is relatively pure. Once collected from a roof and filtered, it can be used as cooling tower makeup water with little treatment beyond adding an oxidizing bio- cide to the storage tank to minimize microbiological growth. Reclaimed Water. Reclaimed water, or recycled water, is highly treated wastewater from a wastewater treatment plant. This nonpo- table water source is delivered to a facility through purple or laven- der piping to distinguish it from potable water supplies. Itis suitable for irrigation, deep well injection, and possibly for open recirculating cooling systems. Compared to potable water, reclaimed water contains a higher concentration of hardness and alkalinity, which increases the ten- dency to form scale deposits. It can also contain appreciable levels of phosphate and ammonia, components not normally present in significant amounts in potable water. The increased phosphate content in reclaimed water also makes calcium phosphate scale formation in heat exchange equipment a concern, unless the proper treatment measures are taken, such as operating the cooling tower at a higher bleed rate, using sulfuric acid for pH control, and/or adding a phosphate specific polymeric dis- persant. Although reclaimed water is disinfected to control pathogenic microorganisms, there is an increased potential for microbiological problems when used in cooling tower systems. In part, this is related to the presence of ammonia and other nitrogen compounds, which are nutrients that support bacteria growth. Reclaimed water also has higher background bacteria levels than potable water. Because of the increased potential for corrosion and deposit problems related to bacteria growth, additional biocides are usually required. A combi- nation of oxidizing and nonoxidizing biocides usually works best. Chlorine dioxide is an excellent biocide because of its nonionic nature, and is better at penetrating biofilm than chlorine or bromine. New technologies greatly simplify chlorine dioxide generation and application, making this an attractive alternative biocide. Blended Water. Blending one or more alternative water sources can reduce overall water consumption and costs associated with operating a cooling tower system. In some applications, it may be necessary to blend potable water with reclaim water to provide a makeup water quality suitable for use in cooling towers. Where there is excess water softener or reverse osmosis (RO) capacity, blending with high-alkalinity, high-hardness potable water can allow a cooling tower to operate at greatly reduced bleed rates. Alternative water streams such as RO reject water may also be suit- able for use as tower makeup with blending. Consistent blending is important when considering a blended water supply for cooling tower makeup. It is difficult to control the bleed rate and treatment levels when the makeup quality varies Inc. ASHRAE, 2019 user. single for Licensed | {}
b8f30ef3-9a4c-45fa-a254-fc2d9016e933 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 50.4 widely. Equipment systems can be engineered to correctly blend two or more water supplies. 2. WATER TREATMENT 2.1 CONTROL Deposition Several different types of deposits can form in boiler and cooling-water systems, and terms such as scale, fouling, deposit, film, coating, precipitate, and others are sometimes used inter- changeably in the industry to describe these materials. However, it is important to use the correct term in describing these phenomena, because the operating procedures and chemical treatments used to help prevent these various deposits from forming, and to remove them when necessary, depend on the specific composition of the deposits. Deposit refers to any material formed on either the internal or external surfaces of components in contact with water. Fouling describes the condition of a system in which deposits have formed, including microbiological fouling. Microbiological fouling is slime or biofilm that accumulates by incorporating inor- ganic particulate matter such as calcium carbonate, silica, and cor- rosion products. Scale is formed from minerals, formerly dissolved in water, de- posited from the water onto heat transfer surfaces or pipes. As water is evaporated in a cooling tower, the concentration of dissolved sol- ids becomes greater, and the solubility of particular scale-causing mineral salts can be exceeded. When this situation occurs in an un- treated cooling-water system, scale will form on any surface in con- tact with the water, especially on heat transfer surfaces. The most common scaling minerals are (1) calcium carbonate, (2) calcium phosphate, (3) calcium sulfate, and (4) silica, usually in that order. Formation of magnesium silicate scale is also possible under certain conditions. Most salts, including silica, are more soluble in hot wa- ter than in cold water; however, most calcium and magnesium salts, including calcium phosphate and calcium carbonate, are more sol- uble in cold water. This is called reverse solubility. As recirculating water passes through the cooling system, the water temperature in- creases. As a result, calcium and magnesium scales may form any- where in the system, but most likely on heated surfaces such as heat exchangers or surface condensers. Silica forms in areas having the lowest water temperature, such as in the cooling tower fill. Several key factors influence whether scale forms: Minerals such as calcium and magnesium are relatively insoluble in water and can form scale deposits when exposed to conditions commonly found in cooling-water systems. A layer of scale as thin as 0.40 mm can reduce heat exchanger capacity by 15%. · Temperature · pH · Alkalinity · Hardness (amount of scale-forming salts) · Total dissolved solids (influence of other dissolved materials, which may or may not be scale-forming) As any of these factors changes, so do scaling tendencies. Changes in pH or alkalinity can greatly affect scale formation. For example, as pH or alkalinity increases, calcium carbonate becomes less soluble and deposits on surfaces. Some materials, such as silica (SiO2), are less soluble at lower alkalinities. When the amount of scale-forming material dissolved in water exceeds its saturation point, scale may result. In addition, other dissolved solids may influence scale-forming tendencies. In general, a higher level of scale-forming dissolved solids results in a greater chance for scale formation. 2019 ASHRAE Handbook- -HVAC Applications (SI) Calcium Carbonate Formation (Hard Lime Scale) The progression of calcium carbonate deposition and scale forma- tion is fundamentally a reversal of the process of creating hard water (when carbonic acid in rainwater dissolves limestone). However, this bond is easily undone once water is put to practical use, because the bicarbonate component of hard water is thermally unstable: 2HCO3- + heat CO3 -2 +CO2 Alkalinity breakdown produces carbonate ion and carbon dioxide (easily lost from a system as a gas). The percentage of bicarbonate broken down grows so long as heat continues to be added to water. The solubility of calcium bicarbonate is more than 10 000 mg/L. The solubility of calcium carbonate at 24°C is roughly 10 mg/L: 4 mg/L calcium ions and 6 mg/L carbonate ions. Basic chemistry dictates that, for aqueous salts of limited solubility, any effort to in- crease the concentration of one constituent must cause the concen- tration of the other constituent to fall. Expressed mathematically, when a soluble salt such as calcium carbonate is dissolved in water, multiplying the concentration of each constituent produces a fixed number Ksp (or solubility product or constant). Hard water typically contains roughly two bicarbonate ions for every calcium ion. Cooling tower and boiler makeup water supplies frequently hold up to 300 mg/L hardness or more, which may be fur- ther concentrated several times by evaporation in a cooling tower or boiler. Calcium and bicarbonate concentrations may easily ap- proach several hundred mg/L each. Alkalinity breakdown can then lead to levels of 100 mg/L or greater of carbonate ions combined with a near equal concentration of calcium ions to form a very high- ly supersaturated solution of calcium carbonate, in violation of the solubility product limit. Scale and sludge are not produced instantly when hard water is introduces into a cooling tower or boiler, because calcium carbonate precipitates only very slowly from a supersaturated solution of cal- cium and carbonate ions. Such supersaturated solutions are termed metastable, in that there is great potential for precipitation to occur, but time is required for its initiation. The mechanism of initiation is complex and beyond the scope of this chapter; it is mainly important to note that the process of calcium carbonate formation starts with alkalinity breakdown and CO2 loss from a boiler or cooling tower system. A metastable condition is then created throughout the entire bulk phase of cooling or boiler water, and nucleated crystals of cal- cium carbonate (limestone) eventually form. As surface nucleation occurs, various conditions in a cooling tower or boiler system dic- tate where deposits form within the system, along with the extent and physical character ofthe deposit. For example, hotter heat trans- fer surfaces speed nucleation and promote formation of the densest crystal structure (calcite), biofilm in cooling water systems captures microcrystals to form calcium-carbonate-rich mud and sludge, and carbonate-rich deposits can form on cooling tower fill at wet/dry boundaries due to hypersaturation. Deposition, Scale, and Suspended-Solids Control Whether dealing with a boiler or cooling tower, treatment strategy is dictated by makeup chemical properties and the "stress" and operating constraints placed on water. Treatment of an HV AC type cooling tower fed with makeup water ofrelatively low hardness is usually quite different than that for an industrial process cooling tower fed with high hardness makeup water. In some instances, local water resource conservation or discharge regulations may dramati- cally affect the treatment strategy used. Steam Boilers: · Makeup water conditioning: Inc. ASHRAE, 2019 user. single for Licensed | {}
f5b8d53d-f669-4d66-b5ed-87c56c2469d6 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | w ater Treatment: Deposition, Corrosion, and Biological Control 50.5 - Ion exchange (softening) to remove calcium and magnesium. - Reverse osmosis (RO) to remove almost all dissolved solids including calcium and magnesium. - Deionization (DI) to remove all dissolved solids. - Deaerator to aid control of carbonate species and pH. · Direct chemical treatment of boiler water: - Various chemical additives such as sodium hydroxide, sodium carbonate, phosphates, dispersive agents, etc. may be added to "soften" boiler water, but this practice is considered out of date, and makeup water conditioning is favored. Chemical additives are typically used to address low level hardness not removed by makeup conditioning or due to external contamination. · Maintain good internal boiler and steam condensate protection against corrosion to control iron deposition on internal boiler sur- faces. Cooling Towers: · Makeup water conditioning: - Ion exchange (softening) to remove calcium and magnesium. - Ion exchange to remove alkalinity using weak cation exchange resin followed by degasification. - Reverse osmosis (RO) to remove almost all dissolved solids in- cluding calcium and magnesium. - Deionization (DI) to remove virtually all dissolved solids. · Add acid to cooling tower water to remove alkalinity and control carbonate ion formation · Add scale inhibitors and dispersives to dramatically slow rate of particle nucleation and agglomeration. Scaling Indices To help determine the tendency of water to form or dissolve cal- cium carbonate scale, several scaling indices have been developed. These indices are only for predicting calcium carbonate scale, not scale of other calcium compounds (such as calcium sulfate). The indices are calculated using the pH, alkalinity, calcium hardness, temperature, and total dissolved solids of the water. Langelier Saturation Index (LSI). This index was developed to calculate the calcium carbonate scale-forming and scale-dissolving tendencies of drinking (potable) water at or near ambient tempera- tures (Langelier 1936). Using a water's calcium hardness, total alka- linity, and total dissolved solids measurements, along with the water's pH and temperature values, the pH of saturation pH(s) is calculated. Subtracting the water's pH(s) from its actual pH then results in the LSI. If the water's measured pH (pH [actual]) is greater than its pH(s) (i.e., positive LSI value), the water has a scale- forming tendency. If the water' s pH (actual) is less than its pH(s) (i.e., negative LSI value), the water will have a scale-dissolving ten- dency. The water' s equilibrium or neutral value is at an LSI of zero. Because this index was originally designed to predict calcium car- bonate scale in potable water, there are serious deficiencies in the accuracy of this index when applied to evaporative cooling water, heating water, or potable hot water. The temperature component in the LSI calculation is considered appropriate for water that is carried at ambient soil temperatures through buried distribution piping. However, this was later deemed insufficient for process water used for cooling towers or boilers where values tended almost always to be positive, yet indications of deposition of calcium carbonate were absent. Experience shows that the LSI can be used as a trending value in process water systems to indicate changes in stability, rather than an absolute condition. The LSI is calculated as LSI = pH(actual) - pH(s) where pH(s) = (9.3 + A + B) - (C + D) A = [log(TDS) - 1] / 10 B = -13.12 x log[temp °C + 273] + 34.55 C = log[Ca2+] - 0.4 D = log[alkalinity] Note: All log values are base 10; alkalinity is the total alkalinity measured as mg/L CaCO3; Ca2+ is the calcium measured as mg/L CaCO3; and TDS is total dissolved solids measured in mg/L. Ryznar Stability Index (RSI). This index is a more accurate formula for predicting calcium carbonate scale (Ryznar 1944). Ryznar altered the LSI by measuring scale thickness in distributed water systems and comparing the calculated LSI with field results. With this information, he made revisions to the LSI. With his for- mula, an RSI value of 6.0 is considered neutral water, with values > 6.0 indicating a tendency to dissolve calcium carbonate, and values < 6.0 a tendency to deposit calcium carbonate. RSI gives more accu- rate results than LSI in waters with a pH less than 7.8, but still gives an indication of scale formation at higher pH values. Regardless, the RSI was useful for the era 's acid feed water treatment programs, which operated at pH < 7.8. The RSI is calculated as RSI = 2 pH(s) - pH(actual) where pH(s) is calculated as in the LSI. Practical (Puckorius) Scaling Index (PSI). Puckorius and Brooke (1991) presented a modified version of the RSI that gives a more accurate and consistent indication of the calcium carbonate scaling potential of cooling water. The PSI takes into consideration the effect of the type of total alkalinity of the cooling water on the measured pH(actual). The measured pH does not always relate cor- rectly to bicarbonate alkalinity, because of the buffering effect of other ions. Rather than using the measured pH in calculating the PSI, an adjusted, or equilibrium pH pH(eq) is used. As with the RSI, a PSI value of 6 indicates stable water, and a value lower than 6 indicates a scale-forming tendency. Without scale control treat- ment, a cooling tower with a PSI of 6 to 7 should operate scale free. Use of the PSI is most applicable when cooling-water pH is above 7.5. The PSI is calculated as PSI = 2 x pH(s) - pH(eq) where pH(s) is as calculated in the LSI, and pH(eq) = 1.465 x log[alkalinity as CaCO3] + 4.54. Simple models and calculators and more information on these indices can be found online from various sources. Scale and Deposit Formation Control Methods used to control scale and deposit formation include the following: · Limit the concentration of scale-forming minerals, impurities, and contaminants in a steam boiler or evaporative cooling-water system by intentionally wasting (removing) water from the system via blowdown (bleed-off). This, in effect, lowers concentration that tends to increase during the continuing evaporation of steam or cooling water from these systems. Scale control is thus achieved through operation of the system at subsaturated conditions. · Remove scale-forming minerals, impurities, and contaminants before they enter the boiler or cooling-water system, using exter- nal or pretreatment systems. This can be done using (1) softened water, blending soft or RO water with other makeup water to achieve a desired saturation index, (2) cycles of concentration, or (3) both methods. · Make mechanical changes in the system, such as increasing water flow or surface areas ofheat exchangers, to reduce tendencies and potential for scale/deposit formation. Inc. ASHRAE, 2019 user. single for Licensed | {}
ecdcf46a-76e5-4db2-944e-707c9d778a1b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 50.6 · Feed acid to reduce alkalinity and keep common scale-forming minerals such as calcium carbonate in solution. · Implement a water treatment program designed to control scale and deposit formations in the boiler or cooling-water system. Retention Time. Controlling cycles of concentration also con- trols the time that minerals, as well as treatment chemicals and other water constituents, are held within a system. Evaporative-cooling- water systems have a load and volume dependent water residence or turnover time referred to as the holding time index (HTI), also called the retention time of the system. HTI is the measure of time that it takes for an analyte in the cooling-water system to decrease to 50% of its original value through the process of system losses (blowdown and drift) plus the addition of makeup water to the system. The greater the HTI of the system, the longer water is held in the system and the greater the probability that dissolved, scale- forming minerals will nucleate to produce deposits. At the same time, the greater the HTI of the system, the longer a biocide dosage is held in the system water for a greater contact time to promote microbial kill or control. HTI for a cooling-water system is calculated as follows: HTI = 0.693 x V/BD where V = volume of system BD = blowdown rate for system evaporation rate (ER)/[cycles of concentration (CC) - 1] Mechanisms. Water treatment chemical scale inhibitors work by the following mechanisms: · Threshold inhibition chemicals control scale formation by dra- matically extending the time required for deposit nucleation. If nucleation time is extended beyond a system's HTI, mineral deposits fail to form. The most commonly used threshold scale inhibitors are organophosphorus compounds (phosphonates) and low-molecular-weight acrylate polymers. Both classes of materials function as threshold inhibitors; however, the polymeric materials are more effective as dispersants. · Scale conditioners modify the crystal structure of scale forming minerals as the nucleate, creating a bulky, transportable sludge instead of a hard deposit. Scale conditioners include lignin, tan- nins, and polymeric compounds. Suspended Solids and Deposition Control Strainers, filters, and separators may be used to reduce sus- pended solids to an acceptable level. Generally, if the screen has openings 0.076 mm (200 mesh), it is called a strainer; ifit is finer than 200 mesh, it is called a filter. Strainers. A strainer is a closed vessel with a cleanable screen designed to remove and retain foreign particles down to 0.025 mm diameter from fluids. Strainers extract material to protect equipment downstream from constrictions or damage, and to allow saving the extracted product if it is valuable. Strainers are available as single- basket or duplex units, manual or automatic cleaning units, and may be made of cast iron, bronze, stainless steel, copper-nickel alloys, or plastic. Supplemental magnetic inserts are available where micro- scopic iron or steel particles are present in the fluid. Cartridge Filters. These are typically used as final or tertiary filters to remove nearly all suspended particles from about 0.102 to 0.00102 mm or smaller. Cartridge filters are typically disposable (i.e., once plugged, they must be replaced). The frequency of replacement, and thus the economic feasibility of their use, depends on the concentration of suspended solids in the fluid, the size of the smallest particles to be removed, and the removal efficiency of the cartridge filter selected. 2019 ASHRAE Handbook-HVAC Applications (SI) In general, cartridge filters are ideal for systems where contami- nation levels are less than 0.01% by mass (<100 mg/L). They are available in many different materials and configurations. Filter media materials include yarns, felts, papers, nonwoven materials, resin-bonded fabric, woven wire cloths, sintered metal, and ceramic structures. The standard configuration is a cylinder with an overall length of approximately 254 mm, an outside diameter of approxi- mately 63.5 to 69.85 mm, and an inside diameter of about 25.4 to 38.1 mm, where the filtered fluid collects in the perforated internal core. Overall lengths from 101.6 to 1016 mm are readily available. Cartridges made of yarns, resin-bonded, or melt-blown fibers normally have a structure that increases in density near the center. These depth-type filters capture particles throughout the total media thickness. Thin media, such as pleated paper (membrane types), have a narrow pore size distribution design to capture particles at or near the surface of the filter. Surface-type filters can normally han- dle higher flow rates and provide higher removal efficiency than equivalent depth filters. Cartridge filters are rated according to man- ufacturers' guidelines. Surface-type filters have an absolute rating, whereas depth-type filters have a nominal rating that reflects their general classification function. Higher-efficiency, melt-blown depth filters are available with absolute ratings as needed. Bag-Type Filters. These filters are composed of a bag of mesh or felt supported by a removable perforated metal basket, placed in a closed housing with an inlet and outlet. The housing is a tubular pressure vessel with a hinged or clamped cover on top for access to the bag and basket. The inlet can be in the cover, in the side (above the bag), or in the bottom. The side inlet is the simplest type. In any case, the liquid enters the top of the bag. The outlet is located at the bottom of the side (below the bag). Pipe connections can be thread- ed or flanged. Single-basket housings can handle up to 14 L/s, mul- tibaskets up to 221 L/s. The support basket is usually of 304 stainless steel perforated with 3 mm holes. (Heavy wire mesh baskets also exist.) The baskets can be lined with fine wire mesh and used by themselves as strainers, without adding a filter bag. Some manufacturers offer a second, inner basket (and bag) that fits inside the primary basket. This provides for two-stage filtering: first a coarse filtering stage, then a finer one. The benefits are longer service time and possible elimination of a second housing to accomplish the same function. Filter bags are made of many materials: cotton, nylon, polypro- pylene, and polyester, with a range of size ratings from <0.00102 to 0.838 mm. Felted materials are most common because of their depth-filtering quality, which provides high dirt-loading capability, and their fine pores. Mesh bags are generally coarser, but are reus- able and, therefore, less costly. The bags have a support ring sewn into their opening; this holds the bag open and seats it on top of the basket rim. They can be configured with lift handles, thermal sealed edges instead of sewn stitches, and glazed (thermal pressed) finish to prevent release of fibers. In operation, the liquid enters the bag from above, flows out through the basket, and exits the housing, cleaned of particulate down to the desired size. The contaminant is trapped inside the bag, making it easy to remove without spilling any downstream. Sand Filters. A downflow filter is used to remove suspended solids from a water stream. The degree of suspended solids removal depends on the combinations and grades of the medium being used in the vessel. During the filtration mode, water enters the top of the filter vessel. After passing through a flow impingement plate, it enters the quiescent (calm) freeboard area above the medium. In multimedia downflow vessels, various grain sizes and types of media are used to filter the water. This design increases the suspend- ed solids holding capacity of the system, which in turn increases the backwashing interval, which conserves water. Multimedia vessels might also be used for low-suspended-solids applications, where chemical additives may be required. Inc. ASHRAE, 2019 user. single for Licensed | {}
174e2901-157c-4b55-a65c-2e10f9a44f40 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | w ater Treatment: Deposition, Corrosion, and Biological Control 50.7 Sand filters for cooling-water systems are usually high rate (13.58 L/[s · m2]), with filter media rated from 0.00051 to 0.0102 mm. Some filter vessels are configured to allow water to enter at an angle to create a vortex-shaped filter bed and enhance removal effi- ciency. Total filtration rate is determined by either system volume turnovers or percent of circulation flow rate. Filter vessels are usu- ally installed sidestream with a booster pump. When they are installed next to cooling towers, filter piping is used to sweep clean tower basin floors at a rate of 0.68 to 1.02 L/(s·m2) via sweep noz- zles. This usually calls for a bigger booster pump to create the sweeping action. When the vessel has retained enough suspended solids to develop a substantial pressure drop, the unit must be backwashed (either manually or automatically) by reversing the direction of flow. This operation removes the accumulated solids out through the top of the vessel. The Handbook Online version of this chapter fea- tures separator animations. Centrifugal-Gravity Separators. In this type of separator, liq- uids enter the unit tangentially, which sets up a circular cyclone flow path. The liquids are accelerated into the separation chamber. Cen- trifugal forces toss particles heavier than the liquid to the perimeter of the separation chamber. Solids drop along the perimeter and into the quiescent collection chamber in. A low-solids liquid is then drawn into the separator vessel vortex (low-pressure area) and up through the separator outlet at the top of the vessel. Solids are either purged periodically by a manual or automatic timed purge, or con- tinuously bled from the separator to a solids collection/filter cham- ber. Advantages of separators include a constant pressure drop even as solids are collected, a negligible water loss in the purge cycle, and no backwash or interruption of service. Disadvantages are that they will not remove particles with lower density than the primary liquid (e.g., cottonwood seeds). Notes: In specifying filtration systems, third-party testing by an accredited or independent agency should be specified. The test report documentation should include a description of methods, piping diagrams, performance data, and certification. Filters described in this section may also be used where indus- trial process cooling water is involved. For this type of service, con- sultation with the filtration equipment manufacturer is essential to ensure proper application. 2.2 CORROSION AND CORROSION CONTROL Corrosion is the destruction of a material, usually a metal or alloy, through chemical or electrochemical reaction with its envi- ronment. This is the mechanism by which a metal reverts to an oxide (hydroxide) of sulfide state. Pure metals fall into two practical groups when considering their interaction with pure neutral-pH water: those that can react and those that do not. Common examples of those that can react are magnesium, aluminum, zinc, chromium, iron, tin-nickel, and lead. Examples of pure metals that should not react include copper, silver, platinum, and gold. Exceptions exist depending on the character of metal oxide surface films. Very tena- cious surface oxide film can block corrosion of a metal that is the- oretically very reactive with water (aluminum, chromium, and nickel, or austenitic stainless steels). Corrosion is therefore a two- step process: (1) penetrating any protective oxide surface film (depolarization) and (2) establishing a continuing reaction between water and metal in a depolarized state. Depolarization involves a chemical reaction that fully or partially removes or weakens protective surface oxide film, thereby exposing base metal. Acidic conditions tend to dissolve protective films and produce uniform metal loss. High chloride tends to weaken protec- tive film on steel so that subsequent corrosion is more irregular. In most instances, the second reaction is electrochemical in nature, much like that in an electric battery. For corrosion to occur, a corrosion cell consisting of an anode, a cathode, an electrolyte, and an electrical connection must exist. Metal ions dissolve into the electrolyte (water) at the anode, leaving behind electrons. These electrons flow through the metal (electric connection) to other points (cathodes) where electron-consuming reactions occur. The result of this activity is the loss of metal and often the formation of a deposit. The rapidity of corrosion depends on the rate of flow of the electrons. Mechanisms for various types of corrosion are shown in Figure 1. Types of Corrosion Corrosion is often divided into three broad categories: (1) uniform (general), (2) localized (pitting), and (3) galvanic (dissimilar metal corrosion). Many other types of corrosion associated with these three main categories are of concern in water treatment and commonly encountered in boiler and cooling water systems for both HVAC and processes, including stress, fatigue, crevice, erosion, and microbio- logically influenced corrosion. Corrosion in practical systems is rarely of one type but the result of an aggregate of several forms. Uniform (general) corrosion (Figure 1D) is the most common type and is caused by a chemical or electrochemical reaction that results in the deterioration of the entire exposed surface of a metal. It is essentially due to general attack, removal, or weakening of whatever protective metal oxide surface film may be present on a metal. Wetted metal surfaces below 66°C are typically coated by biofilm. Beneath biofilm, pH is lower than in bulk phase water by virtue of microbio- logical metabolism. This lower relative pH tends to weaken protective oxide surface film and expose subsurface elements to corrosive hydro- gen ions. Biological activity in and beneath biofilm also produces enzymes reactive with protective metal oxide surface film. Low pH and high chloride are primary contributors to the removal ofprotective iron oxide films from steel. Ultimately, metal can deteriorate to the point of failure. Uniform attack corrosion accounts for the greatest amount of metal destruction by corrosion, but is considered a normal condition when metals are exposed to water based fluids, because it is (1) evenly distributed over a given metal surface throughout a system and (2) predictable, manageable, and often preventable. Uniform cor- rosion can be compensated for by using corrosion-resistant construc- tion materials, applying protective coatings, or providing appropriate cathodic corrosion protection. In some (but not all) cases, uniform cor- rosion can be controlled by changing the chemical environment. Rais- ing pH and reducing chloride and total dissolved solids can reestablish protective surface oxide films on steel and ferrous alloys. The effects of uniform corrosion can be anticipated through measurement of material specimens exposed to the anticipated operating environment in a corrosion coupon rack. Coupons are inserted in the rack for a pre- determined exposure before being removed, cleaned, weighed, and examined to determine rates of corrosion. ![image](/image/placeholder) CURRENT FLOW STEEL STEEL COPPER STEEL A. GALVANIC CORROSION B. CREVICE CORROSION DEPOSIT CURRENT CURRENT FLOW FLOW CATHODE ANODE CATHODE CORROSION C. UNDERDEPOSIT CORROSION D. GENERAL CORROSION INHIBITOR FILM CURRENT CURRENT FLOW FLOW CATHODE PIT PIT CATHODE ANODE E. PITTING ATTACK Fig. 1 Corrosion Types and Mechanisms Inc. ASHRAE, 2019 user. single for Licensed | {}
15de96f7-bb25-4c9d-afde-05fdae77fb88 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 50.8 Localized (pitting) corrosion (Figure 1E) results when a small defect or hole forms in protective metal oxide surface film, usually as the result of inconsistent inhibitor film formation at that location. This area becomes electrochemically anodic, while part of the remaining metal becomes cathodic, producing a localized galvanic reaction, often referred to as a concentration cell. The deterioration of this small area penetrates the metal and can quickly lead to fail- ure. This form of corrosion is often difficult to detect because it is usually relatively small and may be covered and hidden by corro- sion-produced compounds (corrosion byproducts). Pitting is the most serious form of corrosion, because the action is concentrated in a small area. Pits often appear with roughly equal depth and diam- eter. Continued corrosion reaction in pits of ferrous metals can cause the appearance of hollow, tube-like growths above the metal surface, called tubercles. These are formed by layering deposits of iron oxide species, a by-product of the pit formation at the base of the tubercle. Like corrosion cells, pits may reach an autocatalytic stage ofrapid corrosion, though not always. Tubercles, however, are always the result of an autocatalytic process. Unlike crevice corro- sion, pitting is thought to be self-initiated in otherwise unmarred surfaces by the presence of deposits and chloride salts. The pit then concentrates chlorides in the hollow. The process is accelerated by the presence of oxygen, which creates a localized adjacent cathode to the anodic surface of the pit, forcing concentrated anodic deteri- oration and enlarging the pit. Galvanic (dissimilar metal) corrosion (Figures 1A and 2) occurs when two different metals are located together in an electro- lyte (solution). A galvanic couple forms between the two metals, where one metal becomes the anode and the other the cathode. The anode, or sacrificial metal, corrodes and deteriorates faster than it would alone, while the cathode deteriorates more slowly than it would otherwise. Galvanic corrosion is limited to the immediate area of the juncture ofthe two dissimilar metals. Deterioration ofthe anodic metal is most severe at the point of contact and diminishes markedly with distance. Galvanic corrosion rarely extends more than a few inches from where dissimilar metals make contact. Three conditions must exist for galvanic corrosion to occur: · Electrochemically dissimilar metals must be present. · The metals must be in intimate electrical contact. · The metals must be exposed to an electrolyte. Common examples of galvanic corrosion in water systems are metal-to-metal contacts between steel and copper alloys (brass); aluminum and steel; zinc and steel; and zinc coated galvanized steel; and carbon steel or stainless steel. If galvanic corrosion ![image](/image/placeholder) ACTIVE END (ANODIC) Magnesium · OCCURS WHEN TWO Galvanized Steel DIFFERENT METALS Mild Steel ARE IN THE SAME Cast Iron SYSTEM 18-8 Stainless Steel Type 304 (Active) 18-12-3 Stainless Steel Type 316 (Active) Lead Tin ● MORE REACTIVE Muntz Steel METAL WILL CORRODE Nickel (Active) IN PRESENCE OF LESS 76-Ni-16 Cr-7 Fe Alloy (Active) REACTIVE METAL Brass Copper 70:30 Cupro Nickel · POTENTIAL FOR 67-Ni-33 Cu Alloy (Monel) GALVANIC CORROSION Titanium INCREASES WITH 18-8 Stainless Steel Type 304 (Passive) INCREASING DISTANCE 18-12-3 Stainless Steel Type 316 (Passive) ON CHART Graphite Gold Platinum PASSIVE END (CATHODIC) Fig. 2 Galvanic Corrosion 2019 ASHRAE Handbook-HVAC Applications (SI) occurs, the metal named first is the anode and experiences the cor- rosion. Stress corrosion cracking (SCC), or environmental cracking, can result from a combination of environmental conditions affecting the metal and in alloys subject to tensile stress. The stress may be applied, residual (from processing), or a combination. The resulting crack formation is generally intergranular. Corrosion fatigue may occur by one of two mechanisms. In the first, cyclic stresses (e.g., from rapid heating and cooling) are con- centrated at points where surface defects are present and corrosion has roughened or pitted the metal surface. In the second type, cracks often initiate because of the action of applied cyclic stresses where a magnetite film fails on metal surfaces. Caustic cracking occurs when metal is stressed in a fluid with a high caustic content, and a mechanism of concentration occurs. Crevice corrosion (Figure 1B) occurs in the void between a metal and another surface. These opposing surfaces can be metal (similar or dissimilar), gaskets, organic residue, or scale deposits. In this void, and usually in the presence of a stagnant solution, a local- ized corrosion environment is created. Also referred to as underde- posit corrosion, it is similar to concentration cell corrosion issues. As in pitting, the crevice allows the concentration of chlorides in the void, and the presence of oxygen enhances the reaction. Erosion corrosion (flow-accelerated corrosion) occurs as a result of flow or impact that can physically remove inhibitor films and the protective metal oxide surface. This type of corrosion usu- ally occurs because of altered flow patterns or a flow rate that is above design. Suspended solids in a solution can greatly contribute to erosion corrosion. Control of suspended solids can reduce ero- sion in systems and enhance material life cycle and durability. Cavitation corrosion, a form of erosion corrosion, is caused by the rapid formation and collapse of vapor bubbles during a change in fluid pressures in a solution and adjacent to a metal surface. Microbiologically influenced corrosion (MIC), also called mi- crobial corrosion, bacterial corrosion, or biocorrosion, involves the reaction of microbiological species with metals. It is caused or promoted by microorganisms, usually chemoautotrophs, which are microbes that can produce corrosive acids and enzymes as a part of their cellular metabolism. Bacteria do not attack metal or protective metal oxide surface films. The acids, enzymes, cause attack and other metabolic byproducts produced by bacteria, especially when bacteria create a biofilm. MIC can be a very serious problem in building HVAC recirculating water systems, involving many forms, mechanisms, and types of microbiological organisms, including the following. · Iron-related bacteria (IRB), such as Gallionellea ferrugine and Ferrobacillus species, cause corrosion of iron and steel in recir- culating water systems by direct metabolism of iron. Some of these organisms consume iron as a part of their metabolic process and then deposit it in the form of hydrated ferric hydroxide along with mucous secretions. Iron bacteria are commonly found in all types of cooling systems, especially in low-flow areas. · Sulfate-reducing bacteria (SRB) are the best known group of organisms involved in MIC. These anaerobic organisms (i.e., they live without metabolizing oxygen) metabolize sulfur in one form or another. The most widely known, Desulfovibrio, is often found in cooling systems, especially where oil or sludge is present. Met- abolic processes involve the transfer of electrons from a "food source" to an electron acceptor (oxidizing agent) for the purpose of obtaining energy and the building blocks for continued cell growth. The principle electron acceptor under aerobic (oxygen rich) conditions is oxygen. When oxygen is depleted or absent, SRBs can use sulfate as an alternative electron acceptor to oxygen. In the process, sulfate is converted to corrosive hydrogen sulfide. Inc. ASHRAE, 2019 user. single for Licensed | {}
15833d03-516e-41d8-ac09-c718fd688f84 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | w ater Treatment: Deposition, Corrosion, and Biological Control 50.9 Table 2 Corrosion Rate Guidelines ¦ Open Recirculating HVAC Cooling-Water Systems ¦ Open Recirculating HVAC Cooling-Water Systems ¦ Open Recirculating HVAC Cooling-Water Systems ¦ Open Recirculating HVAC Cooling-Water Systems ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Description ¦ Carbon Steel ¦ Copper Alloys ¦ Stainless Steel* ¦ ¦ Negligible or excellent Mild or very good Good Moderate to fair Poor Very poor to severe ¦ 0.0254 mm 0.0254 to.0762 mm 0.0762 to 0.127 mm 0.127 to 0.2032 mm 0.2032 to 0.254 mm >0.254 mm ¦ 0.00254 mm 0.00254 to 0.00635 mm 0.00635 to 0.00889 mm 0.00889 to 0.0127 mm ¦ Acceptable <0.00254 mm Unacceptable >0.00254 mm ¦ ¦ ¦ ¦ 0.0127 to 0.0254 mm >0.0254 mm ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 0.00508 to 0.0127 mm 0.0127 to 0.02032 mm ¦ 0.00635 to 0.00889 mm ¦ ¦ ¦ Closed Recirculating HVAC Water Systems (Hot, Chilled, and Tempered Loops) ¦ Closed Recirculating HVAC Water Systems (Hot, Chilled, and Tempered Loops) ¦ Closed Recirculating HVAC Water Systems (Hot, Chilled, and Tempered Loops) ¦ Closed Recirculating HVAC Water Systems (Hot, Chilled, and Tempered Loops) ¦ ¦ Description Excellent ¦ Carbon Steel 0.00508 mm ¦ Copper Alloys 0.00254 mm ¦ Aluminum* <0.00127 mm ¦ ¦ ¦ ¦ ¦ 0.00127 to 0.00254 mm ¦ ¦ Good ¦ ¦ 0.00254 to 0.00889 mm ¦ ¦ ¦ Moderate ¦ ¦ ¦ 0.00254 to 0.00508 mm ¦ ¦ Poor Very poor to severe ¦ 0.02032 to 0.0254 mm 0.0254 mm ¦ 0.00635 to 0.0127 mm 0.0127 mm *Not A WT Guideline. ¦ 0.00508 to 0.00762 mm >0.00762 mm ¦ Source: Boffardi (2000). · Acid-producing bacteria (APB) include the slime-forming bac- teria Pseudomonas, Aerobacter, and Bacillus, which exude com- pounds such as formic, acetic, and oxalic acids in their metabolic processes. These organic acids cause low-pH conditions at local sites, resulting in corrosion. Thiobacillus is a common APB that oxidizes sulfur compounds into sulfuric acid, which is extremely corrosive and leads to localized underdeposit and pitting corro- sion, often resulting in pinholes in system piping. · Biological deposits (BD) such as algae, yeast, molds, fungi, and bacterial slimes can also cause MIC. Even in the absence of spe- cific corrosive organisms, biological deposits establish an envi- ronment for corrosion by establishment of concentration cells and lowering pH, resulting in underdeposit corrosion. Biological deposits also act as traps providing food for other organisms, accelerating metabolism and growth. This complex matrix sets up a corrosion potential between adjacent areas of a metal surface that may have different type of deposits. In general, the longer it is allowed to flourish, the more difficult, time consuming, and expensive it is to bring under control. To control and/or prevent MIC, it is important to understand the processes that cause it. An effective control and prevention program must address all types of biological growths in recirculating water systems. Factors Affecting Corrosion All cooling-water system metals of construction will corrode at some rate. Therefore, the rate of corrosion is of prime importance. This rate is commonly expressed in terms of penetration (thickness of metal lost) as millimetres. Table 2 provides guidelines for cate- gorizing corrosion rates. The following paragraphs describe the effects of various factors on corrosion. Moisture. Corrosion does not occur in dry environments. How- ever, some moisture is present as water vapor in most environments. In pure oxygen, almost no iron corrosion occurs at relative humidity up to 99%. However, when contaminants such as sulfur dioxide or solid particles of charcoal are present, corrosion can proceed at rel- ative humidity of 50% or more. The corrosion reaction proceeds on surfaces of exposed metals such as iron and unalloyed steel as long as the metal remains wet. Many alloys develop protective corrosion- product films or oxide coatings and are thus unaffected by moisture. an Oxygen. Oxygen dissolved in water (DO) does not lead to cor- rosion of active metals such as aluminum, chromium, nickel, or zinc because these metals form protective oxide surface films acting as polarizing barriers that separate potentially oxygen-reactive metal from DO. Basic ferrous metals (steel and iron) unfortunately form only semiprotective oxide films susceptible to depolarization by nu- merous chemical and mechanical influences. While oxygen is fre- quently blamed for corrosion of basic ferrous metals, this is untrue in the strict sense. Once depolarization of surface film on steel oc- curs, DO perpetuates the attack unless the film can be repaired by corrosion inhibitors (which reestablish film integrity). Ironically, molybdate, a commonly used corrosion inhibitor, requires the pres- ence of oxygen to work effectively. pH. The acidic or basic (alkaline) nature of a solution is quanti- fied by pH; a neutral solution has a pH of 7. Acidic solutions are below 7, and basic solutions are above 7. The pH of cooling water influences the potential of most metals to corrode. Corrosion tends to increase as pH levels decrease (become more acidic) because pro- tective surface film tends to weaken or dissolve as pH falls below 7.0. However, different metals show different corrosion curves with respect to pH. Basic solutions are generally less corrosive to ferrous systems because they tend to make surface oxide film less soluble. It is practical in many water systems to minimize corrosion by add- ing caustic or alkaline buffering agents to raise and stabilize the pH at 9 or higher. Aluminum can corrode above a pH of 8.5 because its protective film weakens or dissolves; this reduces the acceptable range of pH in systems that contain both steel and aluminum. Chlorides. Chloride is nonvolatile, commonly found in water, easily concentrated as water evaporates. Chloride ions can combine with the iron of protective surface film, weakening the film and making steel progressively more vulnerable to pitting and general corrosion, as chloride concentration rises and/or pH falls. Once pro- tective film is depolarized, exposed elemental iron is free to react with oxygen. Because depolarization establishes an electrochemical circuit, the rate of reaction depends not only on the amount of oxygen present but also on the electrical conductance of the water; the higher the chloride and all other ionic species such as sulfate, sodium, potassium, etc., the more readily electrochemical activity proceeds. Increasing the amount of dissolved solids increases the conduc- tivity of the electrolyte (water). Because a corrosion cell depends on the ability of the electrolyte to conduct the flow of electrons, the presence of more dissolved solids increases corrosion. For the Inc. ASHRAE, 2019 user. single for Licensed | {}
30bf6283-6c27-4f82-8612-a9cc4ef882b1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 50.10 Inc. corrosion reaction to proceed, a potential difference between anodic and cathodic areas is required. The potential difference between lo- cations on a metal surface is caused by variations in solute concen- tration in the localized environment. The increase in corrosion caused by such conditions is called concentration cell corrosion. Crevices, cracks, pits, and foreign deposits on the metal surface can create conditions that contribute to corrosion. The anodic area, where corrosion proceeds, is in the crevice or pit, or under the de- posit. Whether the process is metal ion or oxygen concentration based, available chlorides accelerate the reactions. The process turns into an autocatalytic reaction, resulting in rapid destruction of the metal alloy. Though slow to start, once chlorides are introduced, this series of events leads to rapid failure of the metal unless the pro- cess is mechanically repaired or properly inhibited. ASHRAE, 2019 Galvanic (Dissimilar Metal) Corrosion. Another factor that accelerates corrosion is the difference in potential of dissimilar metals coupled together and immersed in an electrolyte. The following factors control the severity of corrosion resulting from such dissimilar metal coupling: user. single for · Relative differences in position (potential) in the galvanic se- ries, with reference to a standard electrode (see Figure 2): the greater the difference, the greater the driving force of the reaction. · Relative area or mass relationship between anode and cathode areas: because the amount of current flow (and therefore total metal loss) is determined by the potential difference and resistance of the circuits, a small anodic area corrodes more rapidly in the presence of a large cathodic area or mass. A larger anodic area or mass relative to the cathode reduces the penetration rate. · Intentional polarization of either cathodic or anodic areas: technology is available to create polarization to reduce the poten- tial difference between components of piping systems, large stor- age tanks, and various metal structures and thus reduce the rate of attack at points of naturally occurring anodic activity. · Ionic content of water or electrolyte: as the concentration of the ionic components of the electrolyte increases, the resulting higher electrical conductivity increases the rate of galvanic corrosion be- cause the resistance to electron flow through water is reduced. Licensed Stress. Stresses in metallic structures rarely have significant effects on the uniform corrosion resistance of metals and alloys. Stress may be due to mechanical loading, vibration, large or cyclic temperature swings, repeated impact, or chemical or MIC gouging (acting alone or in combination). Stresses in some metals and alloys can cause corrosion cracking when the metals are exposed to spe- cific corrosive environments. The cracking can have catastrophic effects. Almost all metals and alloys exhibit susceptibility to stress corrosion cracking in at least one environment. Common examples are steels in hot caustic solutions, high-zinc-content brasses in ammonia, and stainless steels in hot chlorides. Metal manufacturers have technical details on specific materials and their resistance to stress corrosion. Temperature. Higher temperatures speed up chemical reactions and weaken protective surface films. Thus, corrosion rates are great- est in areas where temperatures are the hottest. Even temperature variations within a single piece of metal cause the warmer areas to become anodic to the cooler areas and corrode. An increase in temperature may increase the corrosion rate, but only to a point. Oxygen solubility decreases as temperature increas- es and, in an open system, may approach zero as water boils. Be- yond a critical temperature level, the corrosion rate may decrease because of a decrease in oxygen solubility. However, in a closed sys- tem, where oxygen cannot escape, the corrosion rate may continue to increase with an increase in temperature until the oxygen is used up. For those alloys that depend on oxygen in the environment for maintaining a protective oxide film (e.g., stainless steel), the reduc- 2019 ASHRAE Handbook-HVAC Applications (SI) tion in oxygen content caused by an increase in temperature can ac- celerate the corrosion rate by preventing oxide film formation. Temperature can affect corrosion potential by causing a salt dis- solved in the environment to precipitate on the metal surface as a protective layer of scale. One example is calcium carbonate scale in hard waters. Temperature can also affect the nature of the corrosion product, which may be relatively stable and protective in certain temperature ranges and unstable and nonprotective in others. An example of this is zinc in distilled water: the corrosion product is nonprotective from 60 to 88°C but reasonably protective at other temperatures. Pressure. Where dissolved gases such as oxygen and carbon di- oxide affect the corrosion rate, pressure on the system may increase their solubility and thus increase corrosion. Similarly, a vacuum on the system reduces the solubility of the dissolved gas, thus reducing corrosion. In a heated system, pressure may rise with temperature. It is impractical to control system corrosion by pressure control alone. Flow v elocity. The impact of flow velocity on corrosion rate depends on several factors, including · Amount of oxygen in the water · General chemical environment (e.g., low pH, high chlorides, high MIC potential due to sulfates) · Temperature · Suspended solids in the water · Type of metal exposed (copper and iron are both susceptible) · Flow rate In metal systems where corrosion products retard corrosion by acting as a physical barrier, high flow velocities may remove those protective barriers and increase the potential for corrosion. A turbu- lent environment may cause uneven attack, from both erosion and corrosion. This corrosion is called erosion corrosion. Itis common- ly found in piping with sharp bends where the flow velocity is high. Copper and softer metals are more susceptible to this type of attack. When flow velocity is low (less than 1 m/s), suspended solids can drop out and cause deposition as well as underdeposit corrosion, in- cluding concentration cell corrosion and microbial corrosion. Low flow velocity can also affect transport of corrosion inhibitors and po- larization of corrosion cells. Solids Management. The presence of solids, either suspended or deposited, in the waters of HVAC and process systems can cause abrasion, enhance corrosion, and reduce heat transfer. Suspended sol- ids in flowing waters increase erosion corrosion. Underdeposit cor- rosion can form under dust, dirt, rust, silt, and other solids introduced into evaporative cooling-water systems; mud, rust, and silts can deposit in closed-loop piping systems, especially in dead legs, stor- age and heat exchanger tanks, end bells, or cast iron boiler sections. See the section on Deposition, Scale, and Suspended-Solids Control for further discussion of control. Other major factors affecting corrosion include those discussed in the microbiological and fouling control sections. They center on the contaminants and/or conditions that work to · Prevent inhibitors from reaching the metal surface · Remove inhibitors and/or the protective films from the metal sur- face · Promote the formation of biofilm and/or deposits under which corrosion can occur Such conditions are common in systems with high suspended matter and/or poor microbiological control programs, as well as those systems with process contamination and/or poor deposit con- trol programs, including poor corrosion control programs contrib- uting corrosion debris (byproducts) as deposits. | {}
ddc0afaf-a46e-4200-85c3-fd27d48b042b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | w ater Treatment: Deposition, Corrosion, and Biological Control 50.11 Corrosion Preventive and Protective Measures Materials Selection. Any piece of heating or air-conditioning equipment can be made of metals that are virtually corrosionproof under normal and typical operating conditions. However, economics usually dictate common material choices. When selecting construction materials, the following factors should be considered: · Corrosion resistance of the metal in the operating environment. · Corrosion products that may be formed and their effects on equip- ment operation. · Ease of construction using a particular material. · Design and fabrication limitations on corrosion potential. · Economics of construction, operation, and maintenance during the projected life of the equipment. Expenses may be minimized in the long run by paying more for a corrosion-resistant material and avoiding regular maintenance. · Use of dissimilar metals should be avoided. Where dissimilar materials must be used, insulating gaskets and/or applied coatings must be used to prevent galvanic corrosion. · Compatibility of chemical additives with materials in the system. Protective Coatings. The operating environment has a signifi- cant role in the selection of protective coatings. The suitability of a coating for a particular environment also depends on the surface preparation of the metal to be protected, coating thickness, and coating application technique. Coating durability depends on the ad- hesion between the coating and the metal. Adhesion depends greatly on surface preparation, including cleaning, degreasing, and the ap- plication of primers. Defects in a coating are difficult to prevent. These defects can be flaws introduced into the coating during application or mechanical damage sustained after application. To maintain corrosion protec- tion, defects must be repaired both in the fabrication process and in the operational environment. Defects in coatings, called holidays, can lead to significant localized corrosion of the base metal, most commonly in the form of oxide lifting or cathodic disbondment. Oxide lifting occurs when anodic corrosion products accumulate under a coating adjacent to holidays, lifting the coating from the pro- tected surface. Cathodic disbondment is the result of the cathodic reduction of dissolved oxygen, which, along with water, migrates under the coating from holidays. Once under the coating, blistering occurs, separating the coating from the protected surface. Cycles of Concentration. Some corrosion control may be achieved by optimizing the cycles of concentration (the degree to which soluble mineral solids in the makeup water have increased in the circulating water because of evaporation). Generally, adjustment of the blowdown rate and pH to produce a slightly scale-forming condition (see the section on Scale and Deposit Formation Control) results in an optimum condition between excess corrosion and excess scale. Chemical Methods. Historically, several chemicals have been used to inhibit corrosion. It is important that the inhibitor not inter- fere with the heat transfer or other functions of the metal. In general, corrosion inhibitors function in one of three ways: · Passivation: these inhibitors form a thin protective oxide film on the metal surface. Nitrites and molybdates work in this way. · Precipitation: these inhibitors contain materials that are precipi- tated out of solution to form protective films at sites in a corrosion cell. Zinc and phosphates work this way. · Adsorption: these inhibitors are directly adsorbed onto the metal surface, where they form a protective layer. Organics usually function in this manner. Many inhibitors work best when initially applied at two to three times their normal dosage for several weeks. This pretreatment procedure improves corrosion control by rapidly establishing the protective inhibitor films to new metal surfaces. This procedure should also be repeated for start-ups that follow shutdowns and any time pH or other deviations occur. Film-forming chemical inhibitors reduce or stop corrosion by interfering with the corrosion mechanism. Inhibitors usually affect either the anode or the cathode. The most common inhibitors are molybdates, phosphates, zinc, phosphonates, silicates, nitrite- borates, aromatic azoles, and organics. Although very effective, chromate inhibitors are severely restricted because of their environ- mental toxicity and federal laws that have banned their use. The most important factor in an effective corrosion inhibition program is consistent control of both the corrosion inhibition chemicals and the key water characteristics. No program will be effective without con- trolling these factors. Anodic corrosion inhibitors establish a protective film at the anode. They stop the corrosion cell by blocking the electrochemical reaction at the anodic site and reestablishing polarization. Though these inhibitors can be very effective, they can also be very danger- ous ifinsufficient anodic inhibitor is present, because the entire cor- rosion potential can be focused at unprotected anode sites. Severe localized pitting attack can occur at unprotected anodic sites if insufficient inhibitor is present. Cathodic corrosion inhibitors retard oxygen reduction at the cathode and slow overall electrochemical activity. Cathodic inhibi- tors are not as effective as fully deployed anodic inhibitors, but are commonly used in conjunction with anodic inhibitors to reduce anodic inhibitor dosage requirement. General corrosion inhibitors protect by forming a film on all metal surfaces, whether anodic or cathodic. Optimum corrosion in- hibition is typically obtained through use of one or more anodic and/ or cathodic inhibitor(s). Filming inhibitors are chemical additives that form a molecular film on metals to create a barrier to corrosion (analogous to paint but much thinner). A filming inhibitor bonds to metal through direct molecular charge interaction between the inhibitor and the metal's surface due to opposite electrical charge. Such bonding is quite strong. The class of copper corrosion inhibitors termed azoles is a good example. Cathodic Protection. Sacrificial anodes reduce galvanic attack by providing a metal (such as zinc or magnesium) that is more active (anodic) in the galvanic series than two metals in a galvanic couple. A sacrificial anode becomes anodic to the surface metal and sup- plies electrons to relatively cathodic surfaces, thereby limiting the corrosion of the more anodic metal in the galvanic couple. Proper design and placement of anodes is important. When properly used, they can reduce loss of steel from the tube sheet of exchangers using copper tubes. Sacrificial anodes have helped supplement chemical programs in many cooling-water and process water systems. Impressed-current protection is a similar corrosion control tech- nique that reverses the corrosion cell's normal current flow by impressing a stronger current of opposite polarity. Direct current is applied to an anode (inert [platinum, graphite] or expendable [alu- minum, cast iron]), reversing the galvanic flow and converting the steel from a corroding anode to a protective cathode. The method is very effective in protecting essential equipment such as elevated water storage tanks, steel tanks, or buried pipelines and structures. Corrosion Measurement Uniform, or general, corrosion can be quantitatively measured. Localized corrosion, by definition, may only be observed in some cases, and is unobservable in most cases. Although the process of localized corrosion itself is not measurable, damage to metals by localized corrosion attack can be assessed through various means, such as eddy current testing of chiller tubes. Inc. ASHRAE, 2019 user. single for Licensed | {}
50291422-5f1a-4202-8aa8-d542f936ea9f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 50.12 Corrosion Coupons. Using corrosion coupons is an accepted method for evaluating uniform corrosion rates in both closed- and open-loop systems. Coupon specimens can sometimes exhibit re- sults of localized attack, most frequently from underdeposit and/or microbiologically influenced corrosion. Evidence of excessive lo- calized attack on a coupon specimen may invalidate the coupon specimen from further inclusion in a test or series evaluation. Care- ful selection, handling, placement, alignment, and recording of cou- pon specimens is required for accurate test results. Flow rates and velocities of the fluid through the coupon rack are also essential: ve- locity of 1 m/s is normally used, and velocities in excess of 1.5 m/s may influence erosion, particularly of soft metals such as copper. Ideally, constant flow should be maintained throughout the test pe- riod and variable-flow piping systems should use pressure-indepen- dent flow control devices in the coupon rack piping. Coupon specimens should not be disturbed during a test. Mild steel and copper are commonly used as coupons; admiralty grades of brass and various grades of stainless steel are less common. Regardless, coupon selection should reflect system metallurgy. Place- ment of the least noble coupon specimen should precede progres- sively more noble coupons in the rack in the direction of fluid flow. Because of high initial corrosion rates of the specimen coupon metals, long-duration tests of coupons (60 to 90 days) yield more accurate results in operating systems than shorter tests (15 to 30 days). For comparison and trend analysis, a series of tests should be conducted using the same or similar exposure lengths. Electronic corrosion sensors or probes can be used to determine uniform corrosion rates in a system or to augment a corrosion cou- pon program. Many different types of probes and systems are avail- able, including electric resistance and inductive resistance probes. Linear polarization resistance probes give real-time feedback of cor- rosion rates. However, because rates of uniform corrosion are rarely consistent over time, the readings from linear polarization devices should be monitored or logged to assess trends in the corrosion rates and system stability. Electronic sensors do not exhibit the clear dif- ferences between uniform and localized attack that may be observ- able on coupon specimens. Consult a water treatment professional about the proper type of probe for the specific application and water treatment program. 2.3 BIOLOGICAL GROWTH CONTROL Heating equipment operates above normal biological tempera- ture limits and therefore has fewer microbial problems. Hydronic systems operated below about 50°C provide conditions for growth and proliferation of microorganisms: abundant water, aeration, a possible supply of nutrients, and surfaces upon which to attach. Nutrients may include inorganic and organic compounds added di- rectly to fight corrosion/scale/foam (e.g. nitrites) or introduced as a process or operational contaminant. Problems associated with the uncontrolled growth of microorganisms in cooling or low-tem- perature heating water systems can be categorized in the following four areas: · Plugging and fouling by biological slime (biofilm/biomass) · Biodeterioration (e.g., wood rot) · Microbiologically influenced/induced corrosion (MIC) · Potential health/safety issues (e.g., disease-causing bacteria) Generally speaking, microbiological activity depends on, and reacts to, the specific conditions of a given water system. Clean, municipally treated, drinking (potable) water likely has extremely low biological activity. Wastewater and sewage are most likely highly biologically active. There are a vast number of different bio- logical entities that can potentially be found in water, and the topic of microbiology is far too complex for involved discussion in this 2019 ASHRAE Handbook-HVAC Applications (SI) context, but there are a few key microbiological concepts very important to water treatment: · All practical water systems have some degree ofbiological activity. · Carbon is the primary component of biological activity, along with nitrogen and phosphorous. · Biological activity appears in two forms: freely circulating organ- isms (planktonic) and organisms attached to surfaces (sessile); the same organism types may be found circulating or in biofilms. · Sessile organisms form biofilm, which is present in all water con- duits to a degree (even human arteries and in the human digestive tract). · Metabolism is an oxidation/reduction process involving transfer of electrons from an electron source (food/nutrient) to an electron acceptor, most commonly oxygen. Through this process, an organism obtains energy and the building blocks for growth and reproduction. · Metabolism is fostered by biological catalysts (enzymes). · Metabolism produces inorganic and organic waste products, which tend to be acidic/corrosive. · Some organisms (aerobic) require oxygen to maintain metabo- lism and die or go dormant in the absence of oxygen (obligate aerobes). · Some organisms (anaerobic) only use other electron acceptors (oxidizing agents), such as sulfate, and die or go dormant in the presence of oxygen (obligate anaerobes). · Some organisms can metabolize with or without oxygen (facul- tative anaerobes). · Chemical/biochemical conditions (e.g., pH, oxygen level, en- zyme presence) may be considerably different under biofilm than in general water circulation (bulk phase water). · Biofilm mass depends on nutrient availability, temperature, and oxygen. · Small particles of biofilm, containing a large number of cells, freely detach from biofilm to migrate within a system and pro- mote biofilm extension Biological Categories Microorganisms found in cooling-water systems generally fall into one of three categories: (1) bacteria, (2) algae, or (3) fungi. These organisms can enter a cooling system in various ways: through the makeup water supply; from the atmosphere during nor- mal operation; or from accumulations of environmental organic matter such as insects, bird droppings, grass clippings, and con- struction debris. Microbial growth can interfere with a cooling oper- ation by causing fouling or corrosion, and may pose a health hazard. Bacteria. When considering biological growth in a cooling system, it is important to distinguish between planktonic (free- living) and sessile (attached) microorganisms: · Planktonic bacteria are suspended in the water and sometimes referred to as "free floaters" or "swimmers. " These are aerobic bacteria that thrive in an oxygenated environment. They are not harmful to the cooling system, because they do not directly cause deposits or corrosion, but they can provide nutrients for other mi- croorganisms. Generally speaking, the count of planktonic bacte- ria increases with increasing organic carbon nutrient as measured by the water': s chemical oxygen demand (COD) or its total organ- ic carbon (TOC) content. In addition, some planktonic bacteria, such as Legionella pneumophila, are pathogenic and can present a significant human health risk. · Sessile bacteria are nonswimming (attached) bacteria, some- times called "stickers. " Sessile organisms cause the majority of the corrosion problems in cooling-water systems, because they are not detected in total bacteria counts and tend to be overlooked until problems arise. They establish themselves by attaching to contact surfaces to develop microcolonies with dense biomatrix Inc. ASHRAE, 2019 user. single for Licensed | {}
5400c30b-bf5c-4b95-b370-9135a66a0aca | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | w ater Treatment: Deposition, Corrosion, and Biological Control 50.13 structures. Sessile bacteria types include slime formers and anaer- obic (corrosive) bacteria. Slime formers can grow and form gelat- inous deposits on almost any surface in contact with the cooling water. These deposits can grow so large that they restrict water flow and interfere with heat transfer; they also may promote un- derdeposit corrosion. Usually, if slime formers are present in the system, deposits can be felt on the sides of the cooling tower basin just below the water level. Anaerobic bacteria thrive in oxygen- deprived environments and often establish colonies beneath slime deposits or under other types of deposits. Surface microbial mea- surements using special coupons and/or other monitoring devices can be used to monitor sessile bacteria. Biological fouling can be caused by a wide variety of organisms that produce biofilm and slime masses. Slimes can be formed by bacteria, algae, yeasts, or molds and frequently consist of a mixture of these organisms combined with organic and inorganic debris. Among the problematic bacterial species, sulfate-reducing bacteria (SRB) and iron-related bacteria (IRB) are the most concerning spe- cies (after Legionella). Their presence suggests a potential for severe corrosion and fouling. IRB are commonly found in tubercles and account for assimilation of ferrous ions to form mounds offerric hydroxide, whereas SRB are usually found in the bottom of tuber- cles with black iron sulfides and sometimes elemental sulfur. The sulfur products give off a rotten egg smell. They signal the presence of acid-producing bacteria and deep penetrating pits. Because biofilm microorganisms can dramatically enhance, ac- celerate, and, in some cases, initiate localized corrosion (pitting), they are tested and monitored for critical heat transfer operations. Monitoring methods include the following: · Visual and tactile inspection · Water analysis for ammonia, chemical oxygen demand (COD), total organic carbon (TOC), adenosine triphosphate (ATP), bac- teria speciation 's, and planktonic plate counts · Online biofilm monitors, including corrosion-resistant coupons, disks/plugs, electrochemical sensors, thermal gradient sensors, and sidestream devices to track hydrodynamic pressure differen- tial and heat transfer Microorganisms can influence localized corrosion directly by their metabolism or indirectly by the deposits they form. Corrosion may not be mediated by simply killing the planktonic microorgan- isms. Biofilm removal through chemical and/or mechanical clean- ing is usually necessary. Corrosion can be substantially mediated by inhibiting microorganism metabolism with proper choice of a bio- cide program. Algae uses energy from the sun to convert bicarbonate or carbon dioxide into biomass. Algal mass can block piping, distribution holes, and nozzles. Control Measures Eliminating sunlight from wetted surfaces such as distribution troughs, cooling media, and sumps significantly reduces algae growth. A distribution deck cover, which drastically reduces the sunlight reaching the algae, is one of the most cost effective control devices for a cooling tower. Eliminating dead legs and low-flow areas in the piping and the cooling loop reduces biological growth in those areas. Careful selec- tion of materials of construction can remove nutrient sources and environmental niches for growth and also helps mitigate corrosion. Maintaining a high-quality makeup water supply with low bacterial counts reduces biological growth. Equipment should be designed with adequate access for inspection, sampling, and manual cleaning. Mechanical aids include submicron filter media, fine strainers, scrapers/brushes, and flow and temperature control. Nonchemical treatment approaches include biocidal paint, ultraviolet light, soni- cation with ultrasound, and modification of contact surface material. Sometimes, effective control of slime and algae requires a com- bination of mechanical and chemical treatments. For example, when a system already contains a considerable accumulation of slime, a preliminary mechanical cleaning makes the subsequent application of a biocidal chemical more effective in killing the growth and more effective in preventing further growth. A build-up of scale deposits, corrosion products, and sediment in a cooling system also reduces the effectiveness of chemical biocides. Routine disinfection of cool- ing towers, including the use of high-level chlorination and a biodis- persant, helps control Legionella as well as other microorganisms. Sidestream filtration and monitoring devices such as corrosion cou- pons, test spools, and biofilm sensors can enhance control ofbiofilm growth. Alternating two different types of biocide can overcome resistance developed by bacteria against a single biocide. The two different types should include two different kill mechanisms. More cooling-water treatment programs fail because of lack of microbiological control than from any other treatment problem. Scale, corrosion, and fouling are often symptoms of poor microbi- ological control. Corrosion often occurs under bacterial slime lay- ers. Inorganic foulants are trapped in slime layers, compounding problems. The effects of uncontrolled microbiological activity and fouling may negate the effectiveness of even the best programs for scale prevention and corrosion inhibition. Appropriate biocides must be selected to handle the most prevalent problems first, per- haps in conjunction with dispersants to penetrate and remove depos- its. Effective microbiological control is an absolute necessity for a open cooling-water program to be successful. An effective microbicide (biocide) program has four steps: · Identify the types and concentrations of microorganisms present in the system. · Select proper biocides based on system design, discharge restric- tions, and types of microorganisms. · Implement proper application, dosage, contact time, and control of the selected biocides. · Perform seasonal disinfection cleanings. Microbicides. Chemical biocides used to control biological growth in cooling systems fall into two broad categories: oxidizing and nonoxidizing. There are numerous options commercially avail- able. Some address a broad spectrum of organisms, whereas others are used to target specific types of organisms such as algae, SRBs, or fungi. Selection of the biocides should always be left to water treatment professionals. Effective biocide treatment is usually a combination of an oxidiz- ing biocide with a nonoxidizing biocide. The oxidizer may be fed continuously or intermittently. Nonoxidizing biocide may be intro- duced with either oxidizing biocide strategy. Oxidizing biocides pro- vide quick-kill results and are best used to control biofilm; nonoxidizers are relatively slow acting and best used to suppress MIC activity. A biodispersant (surfactant) is often also incorporated to enhance biocide performance. Oxidizing Biocides. These substances (chlorine, bromine, ozone, iodine, chlorine dioxide, and halogen-releasing compounds such as bromochlorodimethylhydantoin [BCDMH or BCD]) are among the most effective biocide chemicals used in water treatment. However, they are not always effective or appropriate for use in cooling-water systems with high organic loading, high tempera- tures, and/or systems with corrosion or contaminant (compatibility) issues. Chlorine dioxide is probably the one oxidizing biocide least affected by high chemical oxygen demand (COD) and total organic carbon (TOC). In air washers, the odor may become offensive to building/facility occupants, or the exit air (to the building/facility) may be too corrosive for the environment. In wooden cooling towers, high levels of oxidizing biocides can cause delignification. Inc. ASHRAE, 2019 user. single for Licensed | {}
35d026ea-7a96-4e73-b5c4-d537f88396f2 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 50.14 Overdosing of oxidizing biocides may cause corrosion issues with metallic components in any system. Accurate feed and control of oxidizing biocides for the most effective, efficient, and safe appli- cation requires using appropriate feed and control equipment. In many systems, the most effective use of oxidizing biocides is to maintain a constant, low-level residual in the system. However, if halogen-based oxidizing biocides are fed intermittently (slug dosed), a pH below 8 is most advantageous, because of the pH- dependent dissociation curve where the halogen (particularly chlo- rine) is more prevalent in the more biocidal active (hypohalous acid) form. The residual oxidizing biocide concentration should be tested on a routine basis. Most halogenation programs can benefit from using dispersants or surfactants to penetrate and break up microbial masses and biofilm. Chlorine has been the oxidizing biocide of choice for many years, either as chlorine gas, or in liquid form as sodium hypochlo- rite. Other forms of chlorine are available, such as powders, pellets, or calcium hypochlorite sticks; chlorine-releasing compounds (e.g., chloramines, chloroisocyanurates). It can also be produced electro- lytically with brine on site. Use of chlorine gas is declining because ofhealth and safety concerns involved in handling it and because of environmental pressures concerning the formation of EPA- regulated halogenated disinfection by-products. In hot-water sys- tems, including potable hot-water systems, chlorine loses efficacy up to 70% at temperatures of 60 to 71°C. Ozone is a gaseous form of oxygen consisting of three oxygen atoms (O3). As a biocide, it has several advantages compared to chlorine: it does not produce halogenated disinfection by-products, it breaks down to nontoxic compounds rapidly in the environment, it is more potent than chlorine in destructing biofilms, and it requires significantly less chemical handling. The disadvantages of ozone are its short half-life, instability for storage, and reaction by- products that are more biodegradable than their precursors. Use of ozone-generating equipment in an enclosed space requires safety protocols to protect operators from the toxic gas. Bromine is usually produced through reactions of an oxidizer such as sodium hypochlorite with sodium bromide on site, or by release from solids of chlorobromohydantoin compounds. Bromine has certain advantages over chlorine: it is less volatile, and broma- mines break down more rapidly than chloramines in the environ- ment. Also, when slug feeding biocide in high-pH systems, hypobromite ions may have an advantage because their biocidal power is better than that of hypochlorite ions. This effect is less important when biocides are fed continuously at low dosage. Like chlorine, bromine can affect the environment with formation of EPA-regulated halogenated disinfection by-products. Water conditions should be reviewed to determine the need for scale and corrosion inhibitors and then, as with all oxidizing bio- cides, inhibitor chemicals should be carefully selected to ensure compatibility. To maximize the biocidal performance of ozone, the injection equipment should be designed to provide adequate contact of the ozone with the circulating water. In larger systems, ensure that the ozone is not depleted before ozonated water has circulated through the entire system. Iodine is provided in pelletized form, often from a rechargeable cartridge. Iodine is a relatively expensive chemical for use on cool- ing towers and is probably only suitable for use on smaller systems. Chlorine dioxide gas is effective in low concentrations (0.2 to 0.5 mg/L residual). It must be generated on site. Unlike ozone, it is not affected by pH, and has a longer half-life and therefore a higher penetrating power because oflower oxidizing potential. It is usually generated with sodium chlorite precursor by either an electrolytic generator or reactions with acids. Its drawbacks are instability in storage, costly generating equipment, and precursors and acid salt in the end-product solution. 2019 ASHRAE Handbook-HVAC Applications (SI) Hydrogen peroxide (H2O2) is a liquid that is usually available in concentrations of 50% or less, by mass, in water. Hydrogen peroxide is considered one of the most environmentally friendly oxidizing biocides, because it degrades to water; however, concentrated hydrogen peroxide reacts in a violent manner when it comes into contact with organic chemicals and materials. Nonoxidizing Biocides. These biocides destroy organisms either by poisoning the organism, blocking its ability to uptake energy, or disrupting its protective coating (cellular membranes) and exposing the organism to a hostile environment. Most nonoxi- dizers are also known as biostats, which means they inhibit growth of microorganisms. When selecting a nonoxidizing biocide, many factors must be considered for its effective and efficient use, including system pH and relevant water chemistry, chemical compatibility with other treatment products and system contaminants, and the system turn- over rate, or holding time index (HTI), for adequate microbial con- tact time. Common nonoxidizing biocides include the following: · Quaternary ammonium compounds · Polyquats · Methylene bis(thiocyanate) (MBT) · Isothiazolones · Tetalhydoxe,3-fimethy-2H-13.54fAirandaxide-24fice (Thione) · Tributyl tetradecyl phosphonium chloride (TTPC) · Bis(tributyltin) oxide (TBTO) · Carbamates/Dithiocarbamates · 2-(Decylthio)ethanamine (DTEA) · Glutaraldehyde · Dodecylguanidine (Guanides) · Tetrakisb(hydnoxymethyl)phosphonium sulfate (THPS, TKHPS) · 2-(tar-hupplaming)+4chlor-6-ethy/bring/s-manne (TBZ, Tertbuthylazine) · 2-2-Dibromo-3-nirilopropionamide (DBNPA) · 2-Bromo-4-hydroxyacetophenone (BHAP) · 2-Bromo-2-nitropropane-1,3-diol (Bronopol) · Bromo-nitrostyrene (BNS) · Proprietary blends · Aldehyde release treatments · Organosulfur compounds How nonoxidizing biocides are fed is important. Sometimes, the continuous feeding of low dosages is neither effective nor economi- cal. Slug feeding large concentrations to achieve a toxic level of the chemical in the water long enough to kill the organisms present can show better results. W ater blowdown rate and biocide hydrolysis (chemical degradation) rate affect the required dosage. The hydrolysis rate of the biocide is affected by the type of biocide, along with the temperature and pH of the system water. Dosage rates are proportional to system volume; dosage concentrations should be suf- ficient to ensure that the contact time of the biocide is long enough to obtain a high kill rate of microorganisms before the minimum inhib- itory concentration of the biocide is reached. The period between nonoxidizing biocide additions should be based on the system half- life, with sequential additions timed to prevent regrowth ofbacteria in the water. When two nonoxidizing biocides are used, it is important to select the two biocides based on two different kill modes to over- come resistance developed by microbes. Other Biocides. Ultraviolet (UV) irradiation deactivates mi- croorganisms as the water passes around a quartz tube containing the UV lamp. The intensity of the light and thorough contact with the water are critical in obtaining a satisfactory kill of microorgan- isms. Suspended solids in the water or deposits on the quartz tube significantly reduce the effectiveness of this treatment method. Therefore, a filter is often installed upstream of the UV lamp to min- imize these problems. Because ultraviolet light leaves no residual biocide in the water, sessile organisms and organisms that do not Inc. ASHRAE, 2019 user. single for Licensed | {}
2849e60a-7a4b-4985-a797-cc08702f5a39 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | w ater Treatment: Deposition, Corrosion, and Biological Control 50.15 pass the light source are not affected by the ultraviolet treatment. Ultraviolet irradiation may be effective on humidifiers and air washers where the application ofbiocidal chemicals is unacceptable and where 100% of the recirculating water passes the lamp. It is less effective where all microorganisms cannot be exposed to the treat- ment, such as in cooling towers. Ultraviolet lamps require replacement after approximately every 9000 h of operation because, although they will light much longer, the quartz glass slowly be- comes opaque to UV light. Copper (Cu) and silver (Ag) ions can effectively control micro- bial populations in water systems when the ionization systems that produce them are properly maintained, operated, and applied. Ions are released into the water via electrochemical means to generate 0.4 to 0.8 mg/L of copper and/or 40 to 80 g/L of silver. The ions assist in the control of bacterial populations. Copper, in particular, effectively controls algae. Handling Biocides. All biocides must be handled with care to ensure personal safety. In the United States, cooling-water biocides are approved and regulated through the EPA and, by law, must be handled in accordance with labeled instructions. Maintenance staff handling the biocides must read the safety data sheets (SDS) and be provided with all appropriate safety equipment to handle the sub- stance. An automatic feed system is preferred, to minimize and eliminate handling of biocides by maintenance personnel. Legionella and Legionnaires' Disease Legionellosis is any disease caused by Legionella bacteria. Legionnaires' disease, a form oflegionellosis, is a potentially fatal, pneumonia-like illness primarily caused by Legionella pneumoph- ila serogroup 2, one of the more than fifty known species of Legio- nella. Legionella are common warm-water microorganisms that are mostly found in surface waters (lakes, ponds, rivers, streams) but can also be found in groundwater sources, including some soils. They tend to grow in biofilm or slime on the surfaces oflakes, rivers, and streams. Legionella adapt to conditions in water distribution systems, thereby sometimes escaping municipal water plant disin- fection (chlorination). They can, therefore, be found in domestic (potable) water plumbing and associated building water systems such as cooling towers, spas, water fountains, and other water-use systems. Within these systems, Legionella can find favorable con- ditions for growth and amplification, and pose a risk for human dis- ease. The mere presence of Legionella does not necessarily result in disease. Several conditions and factors must occur: primarily, there must be a sufficient quantity and/or virulent form of the bacteria made transmittable and then transmitted to a susceptible host. Transmission occurs when a host inhales tiny water droplets (mists or vapor aerosols) containing Legionella from a water-aerosolizing source. Aspiration of water can also occur during normal drinking and swallowing due to choking or gag reflex. Inhalation can bring infectious Legionella to the deep, distal parts (alveoli) of the lungs, where they take over and promote the pneumonia of Legionnaires' disease. The dose of Legionella pneumophila (or other species of Legionella) required to infect humans is not known, and is most probably influenced by host susceptibility. Legionella grow well and amplify in warm water environments and systems that provide favorable conditions for bacterial growth and the formation of biofilm. The optimum temperature range for growth is 32 to 41 °C. The subsequent use of water from such sys- tems harboring Legionella, through faucets, shower sprays, humid- ifying, aerosolizing (misting) devices, or other spray or drift mechanisms of the system may transmit the bacteria to susceptible hosts. Legionella pneumophila was first identified in 1977, following an outbreak of disease associated with a Philadelphia host hotel for an American Legion bicentennial convention in 1976. Since then, surveillance systems and research studies have been established around the world. In recent years, with improved capabilities and changes in clinical methods of diagnosis, there has been an upsurge in reported cases in many countries. Environmental studies continue to provide information and identify novel sources of infection, lead- ing to regular revisions of guidelines and regulations. As of reports in 2014, an estimated 8000 to 18 000 people are hospitalized with Legionnaires' disease each year in the United States, according to the Centers for Disease Control and Prevention (CDC), and the dis- ease has a 5 to 30% mortality rate (www.cdc.gov/legionella/about/). Outbreaks of Legionnaires' disease receive media attention. However, this disease more often occurs as single, isolated cases not associated with any recognized outbreak. When outbreaks occur, they are usually in the summer and early autumn, though cases may occur at any time of year. Water treatment microbial control programs should also include a risk assessment for Legionella control and disease prevention. This includes the effectiveness of treatment products and the pro- gram to control Legionella and the conditions favorable for its growth and amplification, including the accumulation of biofilm (slime/biomass), the presence of amoebae and other protozoans that harbor it, as well as the potential of the water system to produce aerosols and provide routes of aerosol transmission to susceptible human populations. See ASHRAE Standard 188-2015 and ASHRAE Guideline 12- 2000 for further information. 2.4 NONCHEMICAL AND PHYSICAL WATER TREATMENT METHODS Nonchemical water treatment has been used for boiler water, cooling water, potable water, and other process applications for decades. There are multiple classifications of such treatment meth- ods and equipment systems. Adherence to manufacturers' recom- mendations and the proper application of these technologies is critical to achieving successful results. As with traditional methods of water treatment, the ability to achieve successful results should be adequately evaluated for the water treatment system as well as regularly monitored for effective control of scale, corrosion, and biological contamination. Water treatment technologies, published papers, and case histories should be evaluated in light of water sup- ply chemistry, operating environment, duty, and industry standard performance metrics. Several nonchemical and physical water treatment equipment technologies are classified in the following paragraphs, along with brief summaries of their basic claims and theoretical mechanisms of action. Magnetic, or fixed-field magnetic, systems are designed to cause scale-forming minerals to precipitate on suspended solids as opposed to heat exchanger surfaces. This mechanism produces non- adherent particles, often classified as the aragonite form of calcium carbonate versus the hard, adherent calcite. The precipitated parti- cles can then be removed by blowdown, mechanical means, or phys- ical flushing. Electromagnetic systems induce either a constant or variable magnetic flux density (or both), thereby inducing a localized, vari- able electric field in the bulk water. Pulsed-power and electrody- namic field systems generate a combination of variable magnetic flux density with a variable electric field at frequencies greater than the incoming line signal. The induced electric fields alter the surface charge on suspended solids and particulate and force precipitation on these surfaces in the bulk water. Inc. ASHRAE, 2019 user. single for Licensed | {}
1c372344-7cc7-4068-8907-d6686426d782 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 50.16 Cavitation systems can cause formation and sudden collapse of low-pressure bubbles in a water stream by means of a mechanical force. The collapse of the bubbles imparts a shock wave and resul- tant heat locally within the water flow. The energy created during the implosion of bubbles promotes precipitation of minerals in the water stream. Ionization rods create a static electric field that disperses scale- producing foulants, thereby inhibiting precipitation of minerals on equipment surfaces. The dispersion created by the device's electric field also inhibits biological growth. Electrolysis systems pass an electric current between two elec- trodes. Precipitation of minerals occurs at the cathode. Biological growth is inhibited by formation of chlorine gas at the anode; the gas combines with water to form hypochlorite. Ultrasonic systems impart high-frequency acoustic energy in the ultrasonic range to a stream of water. The sound wave produced by ultrasonic devices can cause mechanical damage to bacteria cell walls. Similar to cavitation devices, ultrasonic energy can also pro- duce low-pressure bubbles, which can collapse and damage bacte- rial cell walls. Ultraviolet light systems irradiate a water stream with ultraviolet light. Exposing microorganisms to ultraviolet light inhib- its their biological growth. The ability to effectively and efficiently control microbial populations throughout a cooling-water system with a point-of-use ultraviolet light system must be evaluated for any given system. Ozone systems inject ozone created by coronal plasma, by ultra- violet lamps, or by chemical reaction, into the bulk water. When contact is made with microorganisms, ozone can be a very effective disinfectant for their control. However, it is difficult to maintain an effective residual of ozone throughout a cooling-water system because ofits high reactivity and fast dissipation. Ozone is very vol- atile and can be lost from the system as the water passes through the cooling tower fill. Successful application of ozone for biological control requires that sufficient ozone-generating capacity be pro- vided to sustain a level of ozone residual that will control microbial contamination throughout the cooling-water system. ASHRAE Research Projects ASHRAE research projects RP-765 (Nasrazadani and Chao 1996) and RP-747 (Gan et al. 1996) found ozone only marginally effective in scale and corrosion inhibition, respectively. Ozone has been shown to have a very limited and unpredictable effect on cal- cium carbonate scale, and a limited effect to inhibit corrosion ofmost metals. It provides some reduction of mild steel corrosion, but increases the corrosion rates of copper and copper alloys. It is also known to attack galvanized steel, and increasing the level of ozone in water increases the corrosiveness of the water. ASHRAE research project RP-1 155 (Cho 2002) studied physical water treatment with respect to scale prevention and/or mitigation. For the study, a physical water treatment (PWT) device was defined as a nonchemical method of water treatment for scale prevention or mitigation. Bulk precipitation on colloidal surfaces was proposed as the mechanism of scale prevention. Three different PWT devices (permanent magnets, a solenoid coil device, and a high-voltage electrode) were tested under laboratory conditions. Fouling resis- tance data obtained in a heat transfer test section supported the ben- efit of all three devices when configured in optimum conditions in the laboratory-scale test system. ASHRAE research project RP-1361 (Vidic et al. 2010) studied physical water treatment and microbial control. In this study, a PWT device was defined as a nonchemical method of water treatment for microbial control. Five different PWT devices (magnetic, pulsed electric field, electrostatic, ultrasonic, and hydrodynamic cavitation) were tested in a pilot-scale cooling tower. No statistically significant difference in planktonic and sessile microbial concentrations was 2019 ASHRAE Handbook-HVAC Applications (SI) observed in the (test) pilot-scale cooling tower for any of the devices, as compared to an untreated control tower. Copies of ASHRAE research project final reports can be ob- tained from technologyportal.ashrae.org, and are free to ASHRAE members. 2.5 BOILER w ATER SYSTEMS Steam and hot-water systems can be classified into three broad groups: (1) steam and hot water for space heating and humidity con- trol in commercial and residential HVAC systems and many indus- trial plants; (2) steam for industrial process heating and for use as a process reactant in chemical plants, paper mills, etc.; and (3) steam to drive turbines for electric power generation. The American Society of Mechanical Engineers (ASME) classifies boilers into three basic types: fire-tube, water-tube, and electric (ASME 2015). Boilers are also classified according to pressure, materials of con- struction, size, heat source, or circulation. A general understanding of boiler design and classifications, as well as requirements of the system, is essential to ensure the system receives proper care to maintain reliability. One of the most important classifications of boiler systems is the end use of the steam or hot water. The focus of this section is on steam and hot-water boiler systems for space heat- ing and humidity control in commercial and residential HV AC sys- tems and some industrial plants. Hot-water heating and low-pressure (103 kPa or less) steam sys- tems with >95% condensate return are similar to closed-loop cool- ing systems, except with reversed heat-exchange processes. The hot water or steam adds heat to an HV AC system or to an industrial pro- cess. The hot-water temperature is maintained either by heat exchange with a steam source or electric elements, or by direct firing in a hot-water-heating boiler. Steam generators range from small heating boilers to very large and complex systems generating steam for industrial plants and electric utility stations. All steam boilers operate on certain basic principles. Water is heated to produce steam at a desired pressure. The steam does work by heating a building or a commercial/indus- trial process. To conserve water and energy, waste steam is con- densed after use and a portion of the condensate is returned to the boiler as feedwater, along with required fresh makeup water. All parts of this system, including feedwater preparation, the boiler, and the condensate system, require chemical treatment to protect the equipment, maintain boiler efficiency, and prepare steam with the required quality and purity. · Economics · Chemistry control mechanisms · Dynamics of the operating system · Design of major components · Number of operators available · Training and qualifications of personnel · Preventive maintenance program · Control instrumentation and remote monitoring Selection of w ater Treatment. As discussed in previous sec- tions, many methods are available to prevent or correct water- caused problems. Selection of the proper water treatment method, and the chemicals and equipment necessary to apply that method, depend on many factors. The chemical characteristics of the water, which change with the operation of the equipment, are most im- portant. Other factors contributing to the selection of proper water treatment are The two most significant factors in setting up an economically viable and effective cooling water treatment program are the chem- ical properties of the water supply and cooling capacity (i.e., rated tonnage). Inc. ASHRAE, 2019 user. single for Licensed | {}
68c0bfe4-a5f2-45dc-b0ae-8a7299df0e57 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | w ater Treatment: Deposition, Corrosion, and Biological Control 50.17 Open Systems Systems classified as open are routinely or continuously in con- tact with the atmosphere. Examples include steam systems which breathe in and exhale air, and condenser water systems that spray the water in an airstream. Open systems are constantly exposed to oxygen (a major corrosive element), local trace gases, and debris entrained in the air. These systems require significant effort and cost to establish and maintain desired conditions. Steam Systems Scale in boilers is a direct result of precipitation of the calcium, magnesium, iron, and silica from the boiler feedwater. Scale can be prevented by removing a portion of the scale-forming ingredients prior to the boiler with external equipment, or within the boiler itself with internal boiler water treatment. One of the most troublesome deposits frequently encountered in steam boilers is iron and combinations of iron with calcium and phosphate used in boiler water treatment. These sticky, adherent sludge deposits are caused by excessive amounts ofiron entering the boiler with the feedwater. This iron is in the form of iron oxide or iron carbonate corrosion products. It is a result of corrosion taking place in sections prior to the boiler, such as steam and condensate lines, condensate receivers, deaerators, and boiler feedwater lines. A program for preventing scale deposits must include treatment to prevent this troublesome type of sludge deposit. Many treatment methods are available for steam-producing boil- ers; the method selected depends on · Makeup water quality · Makeup water quantity (or percentage condensate return) · Pretreatment equipment · Boiler operating conditions · Steam purity requirements · Economics When possible, the removal of scale-forming minerals and other objectionable minerals from the water before it enters the boiler sys- tem is preferred to internal boiler treatment. The internal boiler treatment program should be designed as a polishing tool to ensure clean heat transfer surfaces. External Boiler Water Pretreatment (Water Conditioning) The selection of the proper pretreatment system depends on boiler type, size, source water mineral content, and the desired oper- ator involvement in system operation. This section discusses typical pretreatment solutions for steam boilers in HVAC applications. Some of the pretreatment system components will have a positive effect on water and energy usage. Some components will also require chemical additives and conditioners as consumables. Selec- tion criteria should include the effects of all components, as well as local water type and sanitary discharge regulations. The most common sources of corrosion in boiler systems are dis- solved gases: oxygen, carbon dioxide, and ammonia. Of these, oxy- gen is the most aggressive potentially leading to pitting of boiler tubes. Dissolved oxygen is undesirable because it can cause major corrosion damage in the boiler system and greatly increases treat- ment chemical requirements. The importance of eliminating oxygen as a source of pitting and iron deposition cannot be overemphasized. Even small concentrations of this gas can cause serious corrosion problems. Deaerators and feedwater heaters function on the principle that the dissolved gases are decreasingly soluble as the temperature of their solution is raised. However, even the most efficient deaerators cannot remove all of the dissolved oxygen. Although deaerators can reduce dissolved oxygen to about 7 g/L, trace amounts are still present and can cause corrosion. Chemical oxygen scavengers then must be added to the feedwater, preferably in the storage sec- tion of the deaerator or feedwater tank, to remove the final traces of dissolved oxygen. The most commonly used oxygen scavenger is sodium sulfite. Itis very effective and can be easily measured in the water. In smaller steam boilers, mixing of makeup water and conden- sate normally occurs in an unpressurized vessel called a feedwater tank. Although much less sophisticated and efficient than a deaera- tor, a feedwater tank serves much the same purpose, which is to pre- heat the feedwater and promote removal ofharmful dissolved gases. Whether a deaerator or a feedwater tank is used, its proper operation is important to the overall success of the water treatment program. Unless proper treatment measures are taken, dissolved gases can cause major corrosion damage in feedwater lines, economizers, boiler internals, steam-operated equipment, and condensate return piping. Types of pretreatment for boilers include the following: · · · Ion Exchange Resin. Ion exchange resin allows for specific ions or groups ofions to be removed from the water and be exchanged for another ion that will have a less negative effect on the steam system. These resin beads then require regeneration to remove the objectionable ions to drain and replenish the reaction sites with the appropriate ions. Ion exchange resins can be classified in two groups: anion exchanger and cation exchanger. - Zeolite softeners are cation exchangers that remove calcium and magnesium (and some dissolved iron) from the water and replace them with sodium ions, effectively removing the scaling minerals from the makeup water. The resin is regenerated with sodium chloride salt (NaCI) solution. It is also possible to regenerate with potassium chloride salt (KCI) to minimize sodium effluent during regeneration. Water softeners have negligible effect on the total dissolved solids of the water. - Chloride cycle dealkalizers are anion exchangers that remove carbonates from the water and replace them with chloride ions. This minimizes carbonic acid formation in the condensate network, and reduces chemical consumption. Reducing the carbonate alkalinity of the incoming water may also offer opportunities to reduce boiler blowdown rates, resulting in water and energy savings. The resin is regenerated with sodium chloride salt (NaCI) solution and sodium hydroxide (caustic soda, NaOH). A chloride cycle dealkalizer must be installed downstream of a water softener. Deionizers use both anion and cation resin. Ions are removed through a mixed-bed deionizer or individual anion and cation exchanger vessels in series. Deionization removes virtually all anions and cations in the incoming water, replacing them with H+ and OH-, which in turn form water. Deionizers are often regen- erated off site by a third-party service, although large systems (microchip manufacturers) may have automatic regeneration with acid and caustic soda, which requires increased operator involve- ment. The water produced by a deionizer is extremely low in dis- solved solids and offers significant reductions in boiler blowdown requirements, leading to water and energy savings. This water quality also minimizes carbonic acid formation in the condensate network, and reduces chemical consumption. Deionizers are typ- ically seen in clean-steam applications. Membrane separation allows water to pass through a semiper- meable membrane while preventing most dissolved minerals from passing through with the water. This is done by cross-flow filtra- tion. The dissolved mineral ions are flushed to drain via a concen- trate (reject) stream. Membrane separation increases total pretreatment system water input by 20 to 50% because of the Inc. ASHRAE, 2019 user. single for Licensed | {}
34814ef8-2f4d-44f2-a01e-d08c3acbe15c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 50.18 increased water requirement of the concentrate stream, although it may be possible to reuse this stream for other applications on site. · Reverse osmosis (RO) produces the highest quality (lowest dis- solved mineral content) of all membrane separation technologies. Typical removal rates are >95%. The water quality produced by RO systems is very low in dissolved solids and offers significant reductions in boiler blowdown requirements, leading to energy savings. This water quality also minimizes carbonic acid formation in the condensate network, and reduces chemical consumption. · Mechanical deaeration (deaerators) (1) remove oxygen, carbon dioxide, and other noncondensable gases from steam boiler feed- water; and (2) heat the incoming makeup water and return con- densate to an optimum temperature for minimizing solubility of the undesirable gases, providing the highest temperature water for injection to the boiler. A deaerator is a vessel specifically de- signed to preheat the feedwater to remove dissolved gases, pri- marily oxygen. Boiler Feedwater After pretreatment to remove hardness and other problem impu- rities, the makeup water is combined with returned condensate to become boiler feedwater. In larger boilers, the mixing of makeup water and condensate normally takes place in the deaerator. Makeup water introduces appreciable amounts of oxygen into the system. Oxygen can also enter the feedwater system via the con- densate return system. Possible return line sources are direct air leakage on the suction side of pumps, systems under vacuum, the breathing action of closed condensate receiving tanks, open conden- sate receiving tanks, and leakage of non-deaerated water used for condensate pump seal and/or quench water. Boiler Internal Treatments Even after the best external treatment of the water source, boiler feedwater (including return condensate) still contains impurities that could adversely affect boiler operation. Internal boiler water treatment is then applied to minimize potential problems and avoid catastrophic failure, regardless of external treatment malfunction. Prevention of Scale. After the feedwater is pretreated, scale is controlled with phosphates, acrylates, polymers, chelates, and coag- ulation programs. Chelates, polymers, and acrylates work by bind- ing the hardness, thereby preventing precipitation and scale formation. Phosphates and coagulation programs work in combina- tion with sludge conditioners (tannins, lignin, starches, and syn- thetic polymers) to produce a softened precipitate that is removed by blowdown of the steam boiler. Prevention of Corrosion and Oxygen Pitting. Although steam boilers can corrode as the result of low boiler water pH or misuse of certain chemicals, corrosion is primarily caused by oxygen. After mechanical deaeration, boiler feedwater must be treated chemically to remove the final traces of dissolved oxygen in the feedwater. An oxygen scavenger, such as catalyzed sodium sulfite, should then be fed to react with the residual feedwater oxygen. Oxygen scavengers provide added protection not only to the boiler, but also to the steam and condensate systems. Oxygen at levels as low as 0.005 mg/L can cause oxygen pitting in the steam and condensate system if not chemically reduced by oxygen scavengers. Steam Boiler Lay-Up. Most of the corrosion damage to boilers and associated equipment occurs during idle periods. The corrosion is caused by the exposure of wet metal to oxygen in the air or water. For this reason, special precautions must be taken to prevent corro- sion while boilers are out of service. Although sulfite introduction to remove oxygen is the most com- mon form of treatment for steam boilers, it is not always the most ef- fective for various operational reasons that prevent adequate maintenance of the required continuous sulfite residual. Sulfite maintenance can be particularly difficult in low-pressure heating 2019 ASHRAE Handbook-HVAC Applications (SI) boilers, most often operated without feedwater deaeration. To deal with this situation, boiler corrosion-inhibitor treatment strategies have been developed that do not primarily remove dissolved oxygen, but act to restore a stable protective oxide surface film on steel. Var- ious chemicals such as nitrite, chromate, molybdate, hydrazine, ery- thorbate, diethyl-hydroxylamine and others act to prevent oxygen attack by creating a stable oxide film on steel. Wet Boiler Lay-Up (Steam Boiler). This is a method of storing boilers full of water so that they can be returned to service. It involves adding extra chemicals (usually something to increase alkalinity, an oxygen scavenger, and a dispersant) to the boiler water. Along with the boiler water additives, vapor-phase corrosion inhibitors can also be used for wet storage. The water level is raised in the idle boiler to eliminate air spaces, and the boiler is kept completely full of treated water. Superheaters require special protection. Nitrogen gas can also be used on airtight boilers to maintain a positive pressure on the boiler, thereby preventing oxygen in-leakage. Dry Boiler Lay-Up. This method oflay-up is usually for longer boiler outages. It involves draining, cleaning, and drying the boiler. A material that absorbs moisture, such as hydrated lime or silica gel, is placed in trays inside the boiler. Vapor-phase corrosion inhibitors can also be used for dry storage. The boiler is then sealed carefully to keep out air. Periodic inspection and replacement of the drying chemical are required during long storage periods. Boiler Blowdown Control. As a steam boiler produces steam, the dissolved and suspended solids, as well as the nonvolatile treat- ment chemicals, stay in the boiler (bulk water). As more steam is pro- duced and feedwater is introduced, the concentration of these dissolved and suspended solids increases (and with it, sludge forma- tion). The increased alkalinity and dissolved minerals decrease boiler water surface tension. This leads to the formation of water droplets that can carry over with the steam, causing wet steam. Wet steam can cause water hammer, erosion corrosion of the steam net- work, and increased condensate drainage from drip traps. Imple- menting blowdown can decrease the concentration of dissolved and suspended solids. There are two types of boiler blowdown: continu- ous (or surface) blowdown and manual (or bottom) blowdown. Continuous (or surface) blowdown uses a calibrated valve and a blowdown tap near the boiler water surface. As the name implies, it continuously takes water from the top of the boiler (just beneath the surface water level) at a predetermined rate. Continuous blow- down is not included on all boilers. Dissolved solids tend to concen- trate near the water surface in the steam drum. Therefore, surface blowdown is most effective in reducing the concentration of dis- solved solids. By code (ASME 2015), all steam boilers must include a means for manual (bottom) blowdown. Manual blowdown allows removal of solids that settle at the bottom (mud-drum or belly) of the boiler. Bottom blowdown is used to remove precipitated sludge from the boiler mud drum. There is no absolute rule for frequency of bottom blowdown. It can vary between once per shift to once or twice a week. The required frequency depends on the boiler, feedwater qual- ity, and type of chemical treatment program. A precipitating treat- ment program reacts with hardness in the feedwater to form a sludge that must be removed through bottom blowdown. A solubilizing treatment program keeps hardness in solution and creates little in the way of sludge. Boiler Blowdown Guide. Blowdown results in the loss of heated water and treatment chemicals. Economical operation requires careful control of blowdown to maintain safe solids levels, while minimizing both heat and chemical losses. Contact the boiler manufacturer for the recommended blowdown procedures. If none are available, the following can be used as a general guide: Inc. ASHRAE, 2019 user. single for Licensed | {}
95c54af8-69c6-4bd2-aace-913658e502e2 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | w ater Treatment: Deposition, Corrosion, and Biological Control 50.19 1. Open the blowdown valve nearest the boiler (note that this should be a quick-opening valve) 2. Slowly open the downstream valve until the line is hot 3. Continue opening the downstream valve at a steady rate to drop the water level in the sight glass by approximately 13 mm 4. Close the downstream valve quickly, making sure that the hand wheel is backed off slightly from fully closed to relieve any potential strain on the valve packing 5. Close the valve nearest the boiler Manual blowdown should be done with the boiler under a light load when possible. Controlling the continuous blowdown rate is important to pre- vent the problems associated with high levels of dissolved and sus- pended solids, while minimizing the amount of water energy and treatment (waste) being sent to drain. Automated boiler blowdown controllers can measure the conductivity ofthe boiler water (a proxy for total dissolved solids), and control blowdown valves to maintain the correct boiler water cycles of concentration. These systems also have data-logging capability and communication functionality with cloud-based applications and building automation systems. Steam and Condensate Network Other problems associated with steam and condensate systems include general corrosion and pitting corrosion. Naturally occurring bicarbonate alkalinity in the boiler water breaks down to form car- bonate ions and carbon dioxide (CO2). CO2 leaves the boiler with the steam. As the steam condenses and becomes condensate, it dissolves some of the CO2 to form carbonic acid, lowering the condensate pH. To prevent condensate corrosion, these systems must be protected from acidic conditions and oxygen, which lead to general and pitting corrosion respectively. Protection can be mechanical (deaeration/ dealkization), chemical, or include both means. The following meth- ods are commonly used for condensate system protection. Protection from General Corrosion. Mechanical. Reduce alkalinity from boiler feedwater to mini- mize the amount of CO2 in the system. As discussed in the boiler water pretreatment section, alkalinity can be reduced by dealkaliza- tion, demineralization, and reverse osmosis. In many cases, mechanical reduction of alkalinity is not needed because of low- alkalinity makeup water and/or feedwater. Chemical. Feed volatile neutralizing amines to the boiler system. Neutralizing amines are high-pH chemicals that neutralize the car- bonic acid formed in the condensate (acid attack). The three most commonly used neutralizing amines are morpholine, diethylami- noethanol (DEAE), and cyclohexylamine. Neutralizing amines can- not protect against oxygen attack; however, they help keep oxygen less reactive by maintaining an alkaline pH. Neutralizing amines may be fed to the storage section of the deaerating heater, directly to the boiler with the internal treatment chemicals, or into the main steam header. Some steam distribution systems may require more than one feed point to allow proper distribution. Neutralizing amines are usually fed based on maintaining the condensate system pH > 8 and measured corrosion rates. These amines may be fed neat (undiluted), diluted with condensate or demineralized water, or mixed in low concentrations with the internal treatment chemicals. Different amines have different basicity, neutralizing capacity, and distribution ratios. The proper blend is critical to ensure protection of the entire steam and condensate system, especially in larger and more complex buildings and campuses. Protection from Oxygen Corrosion. Mechanical. Reduce oxygen from all steam boiler feedwater to prevent oxygen carryover to the steam and condensate system (via mechanical methods and chemical oxygen scavengers). Chemical. One method includes feeding filming amines to the steam to form a thin, hydrophobic barrier (film) on the condensate system surfaces. Filming amines are various chemicals that form a protective layer on the condensate piping to protect it from both ox- ygen and acid attack. The two most common filming amines are oc- tadecylamine (ODA) and ethoxylated soya amine (ESA). The filming amines should be continuously fed into steam headers at points that allow proper distribution. Combining neutralizing and filming amines is a successful alternative to protect against both acid and oxygen attack. Another practice is to feed a volatile oxygen scavenger to the steam. The need for chemical treatment can be reduced by designing and maintaining tight return systems so that the conden- sate is returned to the boiler and less makeup is required in the boiler feedwater. The greater the amount of makeup, the more the system requires increased chemical treatment. Boiler Water Treatment Chemical Feed Methods A properly designed water treatment program should be auto- mated to feed the appropriate amounts of treatment proportional to the varying loads ofthe steam system. Meter-initiated chemical feed pumps or more complex control packages with chemical level feed- back mechanisms should be considered. Proper injection points for treatment chemicals are important in attaining optimal results from the water treatment program. The chemical handling, delivery, and disposal of containers must be considered. Onsite mixing of chem- icals should be avoided. Chemicals should be fed directly from pre- blended shipping containers or from microbulk double-wall containment tanks that are refilled by the water treatment vendor. Condenser Water Systems Cooling Tower Treatment. The following guidelines are for start-up (or recommissioning) and shutdown of cooling tower sys- tems. Start-Up and Recommissioning for Drained Systems 1. Inspect tower interior for airborne debris and storm or weather related damages, and determine the extent of cleaning and repairs needed. 2. Clean all debris, such as leaves and dirt, from the cooling tower. 3. Close building air intakes in the area of the cooling tower to pre- vent entrainment of biocide and biological aerosols in the build- ing' s air-handling system. 4. Fill the system with water. While operating the condensing water pump(s) and before operating the cooling tower fans, execute one of the following two biocidal pretreatment programs: - Resume treatment with the biocide that had been used before shutdown. Use the services of the water treatment supplier. Maintain the maximum recommended biocide residual for the specific biocide for a period sufficient to bring the system under good biological control (residual and time varies with the biocide). - Treat the system with sodium hypochlorite at a level of 4 to 5 mg/kg free chlorine residual at a pH of 7.0 to 7.6. The residual level of free chlorine should be held at 4 to 5 mg/kg for 6 h. 5. Once the biocide pretreatment program has been successfully completed, turn on the fan and then put the system in service. The standard water treatment program (including biocide treat- ment) should be resumed at this time. Start-Up and Recommissioning for Undrained (Stagnant) Systems When water remains stagnant for more than about 24 h, dis- solved oxygen may disappear and microbiological conditions may change unfavorably. The environment may become increasingly Inc. ASHRAE, 2019 user. single for Licensed | {}
f2e36add-969a-491e-9172-3146de6e51ba | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 50.20 2019 ASHRAE Handbook-HVAC Applications (SI) favorable to MIC activity. Likelihood of this occurring increases if sulfates and COD are high, or if significant amounts of silt or sludge are present. It is always best to clean a cooling tower sys- tem at the end of a cooling season rather than waiting until the start of a new season. 1. Inspect tower interior for airborne debris and storm or weather related damage, and determine the extent of cleaning and repairs needed. 2. Remove accessible solid debris from bulk water storage vessel (cooling tower sump, draindown tank, etc.). 3. Close building air intakes in the area of the cooling tower to pre- vent entrainment of biocide and biological aerosols in the build- ing' s air-handling system. 4. Perform one of the two biocide pretreatment procedures (de- scribed in the section on Start-Up and Recommissioning for Drained Systems) directly to the bulk water storage vessel. 5. Avoid circulating stagnant bulk cooling water over cooling tower fill or operating cooling tower fans during pretreatment. 6. Stagnant cooling water may be circulated with condenser water pumps if tower fill is bypassed. Otherwise, add approved biocide directly to the bulk water and mix with manual or sidestream flow methods to evenly distribute the dosage. Take care to pre- vent creating aerosol spray from the stagnant cooling water from any point in the cooling-water system. 7. When the biocidal pretreatment is successfully completed, the cooling water should be circulated over the tower fill. Once the biocide treatment has been maintained at a satisfactory level for at least 6 h, the cooling tower fans may then be operated safely. Shutdown When the system is to be shutdown for an extended period, the entire system (cooling tower, system piping, heat exchangers, etc.) should be flushed and drained using the following procedure: 1. Add a dispersant and biocide to the system and recirculate for 12 to 24 h. Confer with a water treatment consultant for suitable chemicals and dosage levels. 2. For dry lay-up, shut down pumps and completely drain all water distribution piping and headers, as well as the cooling loop. Remove water and debris from dead legs and low areas in the piping, which may not have completely drained. 3. Rinse silt and debris from the sump. Pay special attention to cor- ners and crevices. Add a mild solution of detergent and disinfec- tant to the sump and rinse. Ifthe sump does not completely drain, pump out the remaining water and residue. 4. Ifthe equipment cannot be completely drained and is exposed to cold temperatures, freeze protection may be required. 5. Significant protection can be afforded to drained piping and sys- tems with nitrogen blanketing or vapor-phase corrosion inhibi- tors. White Rust on Galvanized Steel Cooling Towers White rust is a zinc corrosion product that forms on galvanized surfaces. It appears as a white, waxy, or fluffy deposit composed of loosely adhering crystalline form of zinc carbonate hydroxide. There is some debate in the literature as to the specific chemical composition of white rust and that of the desirable passivated, dura- ble zinc surface, though they are deemed to be very similar in com- position, if not identical. For the purposes of this chapter, and to clearly differentiate the two, white rust is referred to as zinc carbonate hydroxide and the desired passivated surface as zinc car- bonate. The most damaging white rust forms on submerged and consis- tently wetted galvanized surfaces. This loose crystal structure of zinc carbonate hydroxide allows continued access ofthe electrolytic fluid (water) to quickly expose successive layers of the zinc coating over carbon steel sheet or plate, in effect accelerating the zinc anodic reaction locally. This unusually rapid reduction of zinc allows corrosion of the exposed carbon steel, which can affect the life cycle of galvanized steel cooling towers under certain condi- tions. These conditions are generally accepted to be found in waters with pH below 6 or above ~8.5, and with carbonate (P-alkalinity > 0) and hydroxide alkalinity species present in the solution. Further acceleration of white rust formation can be caused by calcium hard- ness below 50 mg/L (3 grains as CaCO3), requiring the evaluation of the use of water softeners on makeup water during passivation. Contemporary cooling tower treatment programs generally in- volve the addition of phosphate-polymer-based scale and corrosion inhibitors and operating cooling-water systems at alkaline pH. Water chemistry at these higher pH levels (>8 to 9+) is naturally less corrosive to steel and copper, but can create an environment where white rust on galvanized steel can occur. Also, some scale preven- tion programs soften the water to reduce hardness, rather than use acid to reduce alkalinity. Resulting soft waters with <50 mg/L hard- ness (as CaCO3) can also be corrosive to galvanized steel. White Rust Prevention. White rust can be prevented in new gal- vanized cooling towers by promoting the formation of a nonporous surface layer of basic zinc carbonate. This barrier layer is formed during a process called passivation and normally protects the gal- vanized steel for many years. Passivation is best accomplished by controlling pH during initial operation of the cooling tower. Con- trolling the cooling-water pH in the range of7 to 8 for 45 to 60 days usually allows passivation of galvanized surfaces to occur. Excur- sions of cooling-water pH (<7 and >8) during passivation is unde- sirable, and consistent monitoring and control are essential to prevent white rust formation. In addition to pH control, initial oper- ation during passivation with moderate hardness levels of 100 to 300 mg/L as CaCO3 and alkalinity levels of 100 to 300 mg/L as CaCO3 promote passivation. Where pH control is not possible or practical (e.g., makeup water is >8 pH), phosphate-based inhibitors may help protect galvanized steel. Using an inhibitor in lieu of ini- tial passivation by pH control may later expose the galvanized sur- faces to white rust formation should the inhibitor fall below recommended residuals and the pH exceed 8. A water treatment company should be consulted for specific formulations. Once-Through Cooling- w ater Systems Economics is an overriding concern in treating water for once- through systems (in which a very large volume of water passes through the system only once). Protection can be obtained with rel- atively little treatment per unit mass of water, because the water does not change significantly in composition while passing through equipment. However, the quantity of water to be treated is usually so large that any treatment other than simple filtration or the addition of a few milligrams per litre of a polyphosphate, silicate, or other inex- pensive chemical may not be practical or affordable. Intermittent treatment with polyelectrolytes can help maintain clean conditions when the cooling water is sediment laden. In such systems, it is gen- erally less expensive to invest more in corrosion-resistant construc- tion materials than to attempt to treat the water. Open Recirculating Cooling- w ater Systems In an open recirculating system with chemical treatment, more chemical must be present, because the water composition changes significantly by evaporation. Corrosive and scaling constituents are concentrated. However, most chemicals are also concentrated by evaporation; therefore, after the initial dosage, only moderate dosages maintain the higher level of treatment needed. The selection of a water treatment program for an open recirculating system depends on the following major factors: · Economics Inc. ASHRAE, 2019 user. single for Licensed | {}
840642a7-b3c2-4dde-b73a-92785b46ef78 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | w ater Treatment: Deposition, Corrosion, and Biological Control 50.21 · Water quality · Performance criteria (e.g., corrosion rate, bacteria count, etc. ) · System metallurgy · Available staffing · Automation capabilities · Environmental requirements · Water treatment supplier An open recirculating system is typically treated with a scale inhibitor, corrosion inhibitor, oxidizing biocide, nonoxidizing bio- cide, and possibly a dispersant. The exact treatment program de- pends on the previously mentioned conditions. A water treatment control scheme for a cooling tower might include · Chemistry and cycles of concentration control using a conductivity controller · Alkalinity control using automatic injection of sulfuric acid based on pH · Scale control using contacting water meters, proportional feed, or traced control technology · Oxidizing biocide control using an ORP (oxidation-reduction potential) controller · Nonoxidizing biocide control using timers and pump systems Air Washers and Sprayed-Coil Units A water treatment program for an air washer or a sprayed-coil unit is usually complex and depends on the purpose and function of the system. Some systems, such as sprayed coils in office buildings, are used primarily to control temperature and humidity. Other sys- tems are intended to remove dust, oil vapor, and other airborne con- taminants from an airstream. Unless the water is properly treated, the fouling characteristics of the contaminants removed from the air can cause operating problems. Scale control is important in air washers or sprayed coils providing humidification. The minerals in the water may become concentrated enough (by evaporation) to cause problems. Inhibitor/ dispersant treatments commonly used in cooling towers are often used in air washers to control scale formation and corrosion. Suit- able dispersants and surfactants are often needed to control oil and dust removed from the airstream. The type of dispersant depends on the nature of the contaminant and the degree of contamination. For maximum operating efficiency, dispersants should produce minimal amounts of foam. Control of slime and bacterial growth is also necessary in the treatment of air washers and sprayed coils. The potential for bio- logical growth is enhanced, especially if the water contains con- taminants that are nutrients for the microorganisms. Because of variations in conditions and applications of air-washing installations and the possibility of toxicity problems, individual treatment options should be discussed with water treatment experts before a program is chosen. Closed Systems Common Elements. All closed loops need a mechanism to introduce chemicals into the system. Pot feeders are the most common tool used for small to medium sized systems, but chemical pumps can also be used to introduce the chemicals. · Filter feeders: Newer systems or pot feeder replacements should use filter feeders. These units have a stainless steel sleeve strainer that is inserted into the specially designed pot feeder and allows the unit to become a filter once a filter bag or cartridge is added. Filtration can occur down to submicron (<0.5 �m) levels. · Corrosion coupon racks: Closed loops should be outfitted with a two- to four-position corrosion coupon rack with a flow meter to verify that the flow rate through the rack is appropriate and rep- resentative of the system (generally 0.9 to 1.5 m/s). · Water meters: Each closed-loop system should be outfitted with a water meter to measure the amount of water fed into the system. A log of the readings should be kept; this helps in detecting leaks. · Filtration: New pipe has varying degrees of moderately loose iron oxide based mill scale. Over time, and with repeated expan- sion and contraction due to temperature change, mill scale is eroded and adds small particles of highly abrasive debris to flowing water. This material can cause roughening of valve seats, scoring of valve stems, and abrasive damage to packings and mechanical seals. Sidestream filtration is recommended to reduce possible abrasive to working surfaces within closed loop systems. When filtration is needed, the easiest solution for smaller systems is replacing the pot feeder with a filter feeder. Filtration down to 5 �m size is desirable; however, dirty systems should start with >25 �m size filtration to allow cheaper coarse filters to do their work first. The optimum size can be determined by a particle size distribution analysis. Pressure gages and a flow meter at the filter outlet should be placed on the filter unit to help identify when the bags, cartridges, or media need to be changed or cleaned, based on the inlet and outlet pressure differentials. Aluminum condensing boilers need filtration because of (1) their high ratios ofmetal surface to water volume and (2) their ribbed and textured aluminum alloy surfaces required for efficient heat transfer. Closed Recirculating Systems (Closed Hydronic Loops). These systems use a water-based solution to transfer heat. The most common distinction defining a closed system is the fact that the method of cooling is not evaporative. Minimal water loss/makeup and minimal air contact are two additional conditions typically associated with closed loops. In a closed recirculating system, water composition remains fair- ly constant, with very little loss of either water or treatment chemi- cal. Closed systems are often defined as those requiring less than 5% makeup per year. The need for water treatment in such systems (e.g. heating water, chilled water, combined cooling and heating, closed-loop condenser water systems) is often ignored based on the rationalization that the total amount of scale from the water initially filling the system would be insufficient to interfere significantly with heat transfer, and that corrosion would not be serious. However, leakage losses are common, and corrosion products can accumulate sufficiently to foul heat transfer surfaces. Therefore, all systems should be adequately treated to control corrosion. Systems with high makeup rates should be treated to control scale as well. One of the most problematic challenges for closed-loop systems is contamination from glycol-based antifreeze used to "winterize" air handler coils. Although the amount of antifreeze contamination amounts to just a a few hundred milligrams per 1000 litres of system volume, fermentation-like breakdown of glycols can produce enough acidic byproducts to lower pH throughout the recirculating water and establish system-wide corrosive conditions. The selection of a treatment program for closed systems should consider the following factors: · Economics · System metallurgy · Operating conditions · Makeup rate · System size Before new systems are treated, they must be cleaned and flushed. Grease, oil, construction dust, dirt, and mill scale are always present in varying degrees and must be removed from the metallic surfaces to ensure adequate heat transfer and to reduce the opportunity for localized corrosion. Detergent cleaners with organic dispersants are available for proper cleaning and preparation ofnew closed systems. Some of the most serious corrosion damage is done to new sys- tems because of improper start-up procedures. In almost all cases, filling a system with untreated water for the purpose of performing Inc. ASHRAE, 2019 user. single for Licensed | {}
70fdfc2b-fe63-449c-83fd-509e80314098 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 50.22 pressure tests causes this problem. Typically, the system is then left stagnant, sometimes for many months, until it is ready to be com- missioned. During that time, anoxic conditions persist, promoting MIC and underdeposit corrosion. MIC will waste system metals, sometimes considerably. New systems should never be filled with untreated water and should not be left stagnant for long periods of time, even when treated. New systems should be thoroughly cleaned and flushed with an appropriate pretreatment chemistry as early as possible, preferably with the initial filling. After a system has been cleaned and thoroughly flushed of pre- treatment chemicals, it should be immediately refilled with water and treated with the recommended corrosion inhibitor and microbi- ological control products. The system should not be allowed to sit empty for any length of time, unless extraordinary effort is made to ensure that it is completely dry. Corrosion inhibiting treatments for closed water systems are usu- ally composed of several constituents and typically contain molyb- date, nitrite, or other inhibitor compounds as a control parameter, reviewed at least annually. The chemical manufacturer's recom- mendations should be followed as to the amount of inhibitor main- tained in the system. HVAC Closed Loops Containing Aluminum. These loops must be treated primarily to control corrosion and sometimes bio- logical fouling, but may also need cleanup programs to remove new or old corrosion products. There are several important water treatment issues that must be addressed in a mixed-metallurgical system: · The pH must be considered for amphoteric metals, such as aluminum and zinc, that can corrode in both acid and alkaline pH environments. Manufacturer specifications should be followed (generally not to exceed 8.5 pH). · Free copper should generally be maintained <0.1 mg/L with a copper inhibitor. · Total aerobic bacteria counts should be controlled to less than 1000 colony-forming units per millilitre (cfu/mL). Mixed-metallurgy corrosion inhibitors should contain appropri- ately dedicated corrosion inhibitors for the metal composition of the system. w ater-Heating Systems Secondary and Low Temperature. Closed, chilled-water sys- tems that are converted to secondary water heating during winter and primary low-temperature water heating, both of which usually operate in the range of 38 to 93°C, require sufficient inhibitors to control corrosion. For more information on treatment selection for these systems, see the section on Corrosion and Corrosion Control. Environment and High Temperature. Water-heating systems (121 to 177°C) and high-temperature, high-pressure hot-water sys- tems (above 177°C) require careful consideration of treatment for corrosion and deposit control. Makeup water for such systems should be demineralized or softened to minimize scale deposits. For corrosion control, oxygen scavengers such as sodium sulfite can be added to remove dissolved oxygen. Electrode boilers are sometimes used to supply low- or high- temperature hot water. Such systems use heat generated from the electrical resistance of the water between electrodes. The conduc- tivity of the recirculating water must be in a specific range depending on the voltage used. Treatment of this type of system for corrosion and deposit control varies. In some cases, oil-based cor- rosion inhibitors that do not contribute to the conductivity of the recirculating water are used. 2019 ASHRAE Handbook- -HVAC Applications (SI) Table 3 Freeze and Burst Protection by Volume ¦ Temperature, °C ¦ Ethylene Glycol, % by Volume ¦ Ethylene Glycol, % by Volume ¦ Propylene Glycol, % by Volume ¦ Propylene Glycol, % by Volume ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Temperature, °C ¦ Freeze ¦ Burst ¦ Freeze ¦ Burst ¦ ¦ -6.7 ¦ 17.3 ¦ 11.9 ¦ 18.0 ¦ 12.0 ¦ ¦ -12.2 ¦ 27.1 ¦ 18.4 ¦ 29.0 ¦ 20.0 ¦ ¦ -18.0 ¦ 25.7 ¦ 23.8 ¦ 36.0 ¦ 24.0 ¦ ¦ -23.3 ¦ 42.2 ¦ 28. 1 ¦ 42.0 ¦ 28.0 ¦ ¦ -28.9 ¦ 47.6 ¦ 32.5 ¦ 46.0 ¦ 30.0 ¦ ¦ -34.4 ¦ 51.9 ¦ 32.5 ¦ 50.0 ¦ 33.0 ¦ ¦ 40.0 ¦ 56.3 ¦ 32.5 ¦ 54.0 ¦ 35.0 ¦ ¦ 45.6 ¦ 60.6 ¦ 32.5 ¦ 57.0 ¦ 35.0 ¦ Glycol Systems Glycol systems are closed-loop water systems that usually con- tain over 20% (by mass) of either propylene glycol or ethylene glycol (aka antifreeze). For most HV AC applications, inhibited non- toxic propylene glycol replaces inhibited toxic ethylene glycol as antifreeze and for burst protection. It is commonly used as an all year coolant in closed evaporative cooler circuits, and in chilled- and hot-water circuits that are exposed to freezing temperatures. In geothermal cooling and heating systems, if not using food- grade propylene glycol, sometimes a mixture of water and alcohol is used, typically ethanol rather than methanol or propanol (because ethanol is safer than methanol and has lower freeze point and vis- cosity than propanol). To protect against freezing during seasonal lay-ups, glycol may be added at the end of a cooling season into parts of closed water systems that are vulnerable to burst failures from freezing. These vulnerable system parts are isolated and filled with 25 to 50% glycol in fall (before seasonal shutdown) to prevent freezing. They are then drained and flushed before summer start-up to resume normal oper- ation. Inhibited glycol, when diluted to below 20%, loses its anti- septic and pH stabilizing (buffering) abilities, turns acidic after decomposition by oxygen and heat, becomes corrosive to metals, and can be a food source for microbes. Most glycol manufacturers recommend keeping inhibited glycol above 25% concentration, and using glycol tank makeup systems to prevent dilution of the bulk water. Flushing without testing for trace glycol can lead to trace gly- col contamination, which can cause high turbidity, corrosiveness, and repulsive odor. See Table 3 for data on glycol and freeze pro- tection. Treating antifreeze systems is similar to treating closed-loop water systems. It requires pretreatment (start-up) cleaning with alka- line low-foaming detergent. When aluminum and/or galvanized steel are present, chemically neutral low-foaming detergent is used to pro- tect those metals. Phosphate-based detergent is also preferred over silicate base, because residual silicate can become a source of fou- lants to the piping when pH turns from neutral to acidic. In addition to controlling freezing points with different concentrations of anti- freeze, corrosion is controlled with either demineralized makeup water or preblended inhibited glycol. Makeup should only be fed by an automatic antifreeze (glycol) feeder. If a standard hydronic water makeup connection is used, the glycol concentration may be diluted below 20% and it may ferment (like wine). A domestic water feed will also dilute inhibitor levels. Use only industrial glycol. Automo- tive glycol contains much less corrosion inhibitor. Do not change glycol products without verifying the corrosion inhibitors they use. Most glycols use a phosphate inhibitor, but at least one vendor uses nitrite. Makeup water quality with total hardness <50 mg/L. as Ca- CO3, chloride as CF <25 mg/L., and sulfate as SO4 <25 mg/L. is preferred for control of corrosion. When inhibitor levels are out of balance, inhibitors may be fed with a bypass filter feeder to control pH, alkalinity, turbidity, and copper and ferrous inhibitors levels. An inhibitor program protects multimetal materials, steel, cast iron, cop- per, brass, and solder with buffered pH between 8 and 10.5; Inc. ASHRAE, 2019 user. single for Licensed | {}
df5bd06f-c90a-4cfc-83d9-b09329ac62a2 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | w ater Treatment: Deposition, Corrosion, and Biological Control 50.23 phosphates are common buffering agents with concentrations be- tween 2000 and 4000 mg/L. Nitrite borate and silicate are less pre- ferred because of potential for unfavorable reactions with glycol. New glycol shall comply with ASTM Standard D1384 (less than 0.5 mL annual penetration of all system metals). Thermal Storage Systems Thermal storage systems require the same attention as other sys- tems for corrosion, scale, and biological control. As with other sys- tems, itis important to begin with a clean system. The system should be properly cleaned and passivated after construction and before operation, and then treated with appropriate corrosion inhibitors and biocides. The large volume typical of thermal storage systems can result in periodically stagnant conditions and solids accumulation. The system should be equipped with a filter to facilitate solids removal. Either a physical or instrumental method of corrosion monitoring should also be used to ensure that acceptable corrosion rates are maintained. Perhaps most important regarding large chilled-water thermal storage (CWTS) systems is having a clear understanding of the treatments recommended. Because water and water treatment addi- tives remain in a CWTS system for many years, the eventual fate of all additive components should be clearly detailed and understood prior to addition. Proposed organic compounds should receive spe- cial consideration by virtue of their potential biological nutrient value (i.e., biochemical oxygen demand [BOD]). Brine Systems Systems containing brine, a strong solution of sodium chloride or calcium chloride, must be treated to control corrosion and deposits. Sodium nitrite, at a minimum 3000 mg/L in calcium brines or 4000 mg/L in sodium brines, and a pH between 7.0 and 8.5, should provide adequate protection. Organic inhibitors are available that may provide adequate protection where nitrites cannot be used. Molybdates should not be used with calcium brines because insol- uble calcium molybdate will precipitate. 3. TERMINOLOGY The following terms are commonly used in the water treatment industry as they pertain to corrosion, scale, deposit, fouling, and microbiological control. Additional terms are defined in the section on Water Characteristics. Alkalinity. The sum of bicarbonate, carbonate, and hydroxide ions in water. Other ions, such as borate, phosphate, or silicate, also contribute to alkalinity. Anion. A negatively charged ion of an electrolyte that migrates toward the anode influenced by an electric potential gradient. Common examples are chloride (CI-1), sulfate (SO4-2), bicarbonate (HCO3-1), carbonate (CO3 -2), and phosphate (PO4-3). Anode. The positive electrode of an electrolytic cell at which oxidation occurs. Biological deposits. Water-formed deposits ofbiological organ- isms or the products of their life processes. Examples include bar- nacles, algae, or bacterial slime (biofilm). Biofilm formation can be found in the arterial and digestive systems of animals and people. Bleed off/blowdown. Water intentionally discharged from a system to limit buildup of dissolved solids. Cathode. The negative electrode of an electrolytic cell at which reduction occurs. Cation. A positively charged ion of an electrolyte that migrates toward the cathode influenced by an electric potential gradient. Common examples are calcium ion (Ca+2), magnesium ion (Mg+2), sodium ion (Na+1), potassium ion (K+1), and ferric iron (Fe+3). Corrosion. The deterioration of a material, usually a metal, by reaction with its environment. Cycles of concentration. Water vapor lost from a cooling tower or steam or condensate lost from a boiler system is pure water free of dissolved solids and must quickly be replaced by makeup water to sustain system operation. The incoming water has dissolved solids; the lost water was free of dissolved solids; therefore, dis- solved solids accumulate in retained system water. Cycles of con- centration can be defined as the ratio of dissolved solids in cooling tower or boiler water to dissolved solids in makeup water. More pre- cisely stated, it is the ratio of the volume of makeup to the volume of bleed off/blowdown. Electrolyte. A solution through which an electric current can flow. Water without ions present in it will not conduct electricity. Ions dissolved in water create an electrolyte and allow current to flow. The more concentrated the ions, the easier it is for current to flow. Filtration. Process of passing a liquid through a porous material in such a manner as to remove suspended matter from the liquid. Galvanic corrosion. Corrosion resulting from the contact of two dissimilar metals in an electrolyte or from the contact of two similar metals in an electrolyte of nonuniform concentration. Hardness. The sum ofthe calcium and magnesium ions in water; usually expressed in mg/kg or mg/L as CaCO3. Inhibitor. A chemical substance that reduces the rate of corro- sion, scale formation, fouling, or slime production. Ion. A positive (cation) or negative (anion) electrically charged atom or group of atoms. Makeup. Water added to a cooling tower or boiler system to replace evaporation or steam loss. Passivity. The tendency of a metal to become inactive in a given environment. Noble metals such as gold, silver, and platinum are inherently passive or unreactive with respect to water. Water reac- tive (active) metals such as iron, aluminum, nickel, and zinc acquire varying degrees of passivity because of natural and inhibitor- enhanced formation of an extremely thin, protective oxide surface film. pH. The logarithm of the reciprocal of the hydrogen ion concen- tration of a solution [-log 10 = log(1/H+)]. pH values below 7 are increasingly acidic; those above 7 are increasingly alkaline. Each whole unit change in pH represents a 10-fold change in hydrogen ion concentration. Polarization. The deviation from the open circuit potential of an electrode resulting from the passage of current. Also used to describe the absence of electron flow where corrosion of an active metal is possible. Depolarization implies passage of electron flow and likely corrosion activity. Potable. Safe to drink. In the U.S., this normally means water that complies with the National Primary Drinking Water Regula- tions (NPDWR; EPA 2009). The NPDWR document is also an excellent source of information about the adverse effects and sources of each regulated contaminant. Some states may also adopt the National Secondary Drinking Water Regulations, which are shown at the end of the NPDWR document and affect cosmetic issues and taste, but not health. ppm. Parts per million by mass. In water, ppm are essentially the same as milligrams per liter (mg/L); 10 000 mg/L = 1%. Scale. (1) The formation at high temperature of thick corrosion product layers on a metal surface. (2) The precipitation of water- insoluble constituents on a surface. Sludge. A sedimentary water-formed deposit, originating from (1) biological sources, (2) capture of suspended particles from the air, and/or (3) in-system formation hardness or corrosion debris. Note, sludge deposits can harden over time, or upon drying, and take on the appearance of scale. Inc. ASHRAE, 2019 user. single for Licensed | {}
7e4c2f46-b828-435d-843c-db3b0d2a1552 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 50.24 2019 ASHRAE Handbook-HVAC Applications (SI) Tuberculation. The formation over a surface of scattered, knob- like mounds of localized corrosion products. w ater-formed deposit. Any accumulation ofinsoluble material derived from water or formed by the reaction with water on surfaces in contact with it. REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. ASHRAE. 2015. Risk management for building water systems. ANSI/ ASHRAE Standard 188-2015. ASHRAE. 2000. Minimizing the risk of legionellosis associated with building water systems. Guideline 12-2000. ASME. 2015. Boiler and pressure vessel code. BPVC-2015. American Society of Mechanical Engineers, New York. ASTM. 2012. Standard test method for corrosion test for engine coolants in glassware. D1384 -05(2012). ASTM International, West Conshohocken, PA. AWT. 2009. Informative and factual case histories for cooling water treat- ment programs-Suggested guidelines and performance levels. AWT Cooling Water Committee. Association of Water Technologies, Rock- ville, MD. Boffardi, B.P. 2000. Standards for corrosion rates. The Analyst (Spring). Association of Water Technologies, Rockville, MD. Cho, Y.I. 2002. Efficiency of physical water treatments in controlling cal- cium scale accumulation in recirculating open cooling water system. ASHRAE Research Project RP-1155, Final Report. EPA. 2009. National primary drinking waterregulations. U.S. Environmen- tal Protection Agency, Washington, D.C. www.epa.gov/ground-water -ink-hilling-atrantical-phimaryding-water---ntion Gan, F., D.-T. Chin, and A. Meitz. 1996. Laboratory evaluation of ozone as a corrosion inhibitor for carbon steel, copper, and galvanized steel in cooling water. ASHRAE Transactions 102(1). Langelier, W.F. 1936. The analytical control of anticorrosion water treat- ment. Journal of the American Water Works Association 28:1500. Nasrazadani, S., and T.J. Chao. 1996. Laboratory evaluations of ozone as a scale inhibitor for use in open recirculating cooling systems. ASHRAE Transactions 102(2). Puckorius, P.R., and J.M. Brooke. 1991. A new practical index for calcium carbonate scale prediction in cooling tower systems. Corrosion 47(4): 280-284. dx.doi.org/10.5006/1 .3585256. Ryznar, J.W. 1944. A new index for determining amount of calcium carbonate scale formed by a water. Journal ofthe American Water Works Association 36:472. Vidic, R.D., S.M. Duda, and J.E. Stout. 2010. Biological control in cooling water systems using non-chemical treatment devices. ASHRAE Re- search Project RP-1361, Final Report. BIBLIOGRAPHY ABMA. 2005. Boiler water quality requirements and associated steam quality for industrial/commercial and institutional boilers. Publication 402. American Boiler Manufacturers Association, Arlington, VA. ASME. 1994. Consensus on operating practicesfor the control offeedwater and boiler water chemistry in modern industrial boilers. Research Com- mittee on Water in Thermal Power Systems, Industrial Boiler Subcom- mittee. American Society of Mechanical Engineers, New York. AWT. 2006. Legionella 2003: An update and statement by the Association of Water Technologies (AWT). Association of Water Technologies, Rock- ville, MD. AWT. 2009. Technical reference and training manual, 2nd ed. Water Treat- ment Publication. Association of Water Technologies, Rockville, MD. AWT. 2012. White rust prevention-An industry update and guide paper. Association of Water Technologies, Rockville, MD. Browning, A., and D. Weimar. 2011. Alternative Sources for Cooling tower Systems. Process Cooling Magazine. DOD. 2005. Industrial water treatment- Operation and maintenance. Uni- fied Facilities Criteria UFC 3-240-13FN25, May 2005.U.S. Department of Defense, Washington, D.C. DOE. 1998. Non-chemical technologies for scale and hardness control. Fed- eral TechnologyAlert DOE/EE-0162. U.S. Department ofEnergy, Wash- ington, D.C. Frayne, C., and R.T. Blake. The METRO handbook of water treatment for HVAC systems. The Metro Group, Long Island City, NY. Lin, Y.E., J.E. Stout, and V.L. Yu. 2011. Controlling Legionella in hospital drinking water: An evidence-based review of disinfection methods. Infection Control and Hospital Epidemiology 32(2). Liu, Z., J.E. Stout, L. Tedesco, M. Boldin, C. Hwang, W.F. Diven, and V.L Yu. 1994. Controlled evaluation of copper-silver ionization in eradicating Legionella pneumophila from a hospital water distribution system. The Journal of Infectious Diseases 169:919-922. Pearson, W. 2011. NCDs and biological control in cooling water systems. CTI Journal 33(1). Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
53048dbb-caa8-4804-9d4d-d9741e1cd40f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 51 SERVICE WATER HEATING ¦ System Elements ¦ 51.1 ¦ Building Applications ¦ 51.11 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Water-Heating Terminology ¦ 51.1 ¦ Hot-Water Load and Equipment ¦ ¦ ¦ System Planning ¦ 51.2 ¦ Sizing ¦ ··· 51.12 ¦ ¦ Design Considerations ¦ 51.2 ¦ Water-Heating Energy Use ¦ 51.30 ¦ ¦ End-Use Fixtures ¦ 51.3 ¦ Health and Safety - ¦ 51.32 ¦ ¦ Distribution ¦ 51.3 ¦ Water Quality, Scale, and Corrosion ¦ 51.33 ¦ ¦ Water-Heating Equipment ¦ 51.9 ¦ Special Concerns ¦ 51.34 ¦ WA TER HEA TING energy use is second only to space condi- tioning in most residential buildings, and is also significant in many commercial and industrial settings. In some climates and applications, water heating is the largest energy use in a building. Moreover, quick availability of adequate amounts of hot water is an important factor in user satisfaction. Both water and energy waste can be significant in poorly designed service water-heating systems: from over- or undersizing pipes and equipment, from poor building layout, and from poor system design and operating strategies. Good service water-heating system design and operating practices will reduce operating costs and can often reduce first costs. The informa- tion in this chapter is thus critical for the sustainable design and operation of many buildings. Research documenting hot-water use in modern systems is lim- ited to certain segments. Some of the data in this chapter on hot- water demands for some types of buildings, applications, and fix- tures may be outdated. Nevertheless, these data are provided for guidance, because they are often still the best available; however, these demand values are not intended for use as designers' sole ref- erences for hot-water system sizing purposes. 1. SYSTEM ELEMENTS A service water-heating system has (1) one or more heat energy sources, (2) heat transfer equipment, (3) a distribution system, and (4) end-use fixtures. Heat energy sources may be (1) fuel combustion; (2) electrical conversion; (3) solar energy; (4) geothermal, air, or other environ- mental energy; and/or (5) recovered waste heat from sources such as flue gases, ventilation and air-conditioning systems, refrigeration cycles, and process waste discharge. Heat transfer equipment is direct, indirect, or a combination of the two. For direct equipment, heat is derived from combustion of fuel or direct conversion of electrical energy into heat and is applied within the water-heating equipment. For indirect heat transfer equip- ment, heat energy is developed from remote heat sources (e.g., boilers; solar energy collection; air, geothermal, or other environ- mental source; cogeneration; refrigeration; waste heat) and is then transferred to the water in a separate piece of equipment. Storage tanks may be part of or associated with either type of heat transfer equipment. Distribution systems transport hot water produced by water- heating equipment to end-use fixtures. For locations where constant supply temperatures are desired, circulation piping or a means of heat maintenance must be provided. End-use fixtures are plumbing faucets, accessories, and equip- ment requiring hot water that may have periods of irregular flow, constant flow, and no flow. These patterns and their related water The preparation of this chapter is assigned to TC 6.6, Service Water Heating Systems. usage vary with different buildings, process applications, and per- sonal preference. Examples of end-use accessories are prerinse spray valves, faucet aerators, showerheads, washdown sprayers, and hose bibbs. Examples of end-use equipment are dishwashers, clothes washers, and pressure washers. 2. WATER-HEA TING TERMINOLOGY Distribution system efficiency. Heat contained in the water at points of use divided by heat delivered at the heater outlet during flow periods. Energy factor. The delivered efficiency of a residential water heater when operated as specified in U.S. Department of Energy (DOE) test procedures (DOE 2001). See also ASHRAE Standard 118.2. First-hour rating. An indicator of the maximum amount of hot water a residential water heater can supply in 1 h when starting with a tank that is up to temperature. This rating is used by the U.S. Fed- eral Trade Commission (FTC) for comparative purposes and by the U.S. Department of Energy (DOE) for selecting the appropriate draw profile when testing for the uniform energy factor. Because peak draws taken over periods less than 1 h frequently drive residen- tial equipment sizing, first-hour rating alone should not be used for equipment sizing. As for larger systems, storage tank volume and heating rate also play important roles. Fixture unit. A number, on an arbitrarily chosen scale, that ex- presses the load-producing effects on the system of different kinds of fixtures. Heat trap. A device to counteract the natural convection of heated water in a vertical pipe. Commercially available heat traps for large equipment are generally 360° loops of tubing; heat traps can also be constructed of pipes connected to the water heater (inlet or outlet) that direct flow downward before connecting to the vertical supply or hot-water distribution system. Tubing or piping heat traps should have a loop diameter or length of downward piping of at least 300 mm. Various prefabricated check-valve-like heat traps are avail- able for residential-sized equipment, using balls, flexible flaps, or moving disks. Input efficiency. Heat entering water in the heating device divided by energy input to the heating unit over a specific period of steady-state conditions, or while heating from cold to hot, depending on how stated (steady-state versus average input efficiency); it does not include heat losses from the water heater jacket and/or tank. When used with fossil-fuel-fired equipment, this is commonly called combustion efficiency. Operating efficiency. Heat delivered at the heater outlet (Qout = mcp[Thot out Tcold in]) divided by heat input to the heating unit - (includes heat losses from water heater jacket and/or tank) for any selected period for systems without recirculation pumps. For dis- tribution systems with recirculation pumps, heat losses include recirculation line losses, because hot water at a reduced 51.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
f5fc8f35-a3c9-4473-8090-a04282b63538 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 51.2 2019 ASHRAE Handbook-HVAC Applications (SI) temperature is returned back to the heater. Thus, operating effi- ciency equals the heat delivered to the middle ofthe distribution line (Qout = mcp [(Thot out Thotreturn)/2 - Tcoldin]) divided by heat input + to heating unit. The operating efficiency of water heaters in systems with continuous recirculation can be further reduced by loss of strat- ification in storage heaters. Elevated return temperatures associated with continuous recirculation systems further reduce the operating efficiency of condensing water heaters (see Figures 1 and 2). This is also referred to the heater's real-world efficiency, which can be easily measured and used to estimate the energy use or operating cost. A system with higher operating efficiency may not always equate to a higher-performing system, because operating efficiency considers water temperature leaving the tank, not water temperature reaching the fixtures. A system with extremely long hot-water dis- tribution piping and no recirculation may show a high operating efficiency, but hot water may never reach the farthest fixtures. Overall system efficiency. Heat energy in the water delivered at points of use divided by the total energy supplied to the heater for any selected period. Recovery efficiency. Heat absorbed by the water divided by heat input to the heating unit during the period that water temperature is raised from inlet temperature to final temperature (includes heat losses from water heater jacket and/or tank). Inc. ASHRAE, Recovery rate. The amount of hot water that a water heater can continually produce, usually reported as flow rate in litres per hour that can be maintained for a specified temperature rise through the water heater. 2019 user. Standby loss. As applied to a tank water heater (under test con- ditions with no water flow), the average hourly energy consumption divided by the average hourly heat energy contained in stored water, expressed as a percent per hour. This can be converted to the average watts energy consumption required to maintain any water/air tem- perature difference by taking the percent times the temperature dif- ference, times 1.15 kWh/(m3 · K) (a nominal specific heat for water), times the tank capacity, and then dividing by 100. single for Licensed Standby loss coefficient. The heat input (in W/K) into a storage water heater when operated as specified in U.S. Department of En- ergy (DOE) test procedures (DOE 2001). This value is essentially the standby loss divided by the difference in temperature between the average stored water temperature and the surrounding air tem- perature. Care should be taken to understand whether a quoted standby loss coefficient includes the heat input efficiency of the heating device. It is possible to directly measure the heat lost from a storage water heater independently of how that water is heated. Sometimes, the reported standby loss coefficient represents only the heat lost; at other times, it represents the amount of energy to make up that heat loss, and considers the heat input efficiency of the heating device. System standby loss. The amount of heat lost from the water heating system and the auxiliary power consumed during periods of nonuse of service hot water. Thermal efficiency. Heat in water flowing from the heater outlet divided by the energy input to the heating unit over a specific period of steady-state conditions (includes heat losses from the water heater jacket and/or tank). Uniform energy factor. The delivered efficiency ofa residential water heater when operated as specified in U.S. Department of Energy (DOE) test procedures (DOE 2014). 3. SYSTEM PLANNING The goals of system planning are to (1) size the system properly; (2) optimize system efficiency; and (3) minimize first, operating, and overall life-cycle costs. It is important to design systems so that they perform well from both functional (hot-water delivery) and energy-use perspectives. Flow rate, temperature, and total flow over specific time periods are the primary factors to be determined in the design of a water-heating and piping system for delivering adequate amounts of hot water. Operating pressures, time of delivery, and water quality are also factors to consider. Presently, separate proce- dures are used to select water-heating equipment and to design the piping system. However, water-heating equipment sizing and piping system design should be considered together for best system design. Oversized or excessively long piping exacerbates delivery delay and/or energy waste. Water-heating equipment, storage facilities, and piping should (1) have enough capacity to provide the required hot water while minimizing waste of energy or water and (2) allow economical system installation, maintenance, and operation. W ater-heating equipment types and designs are based on the (1) energy source, (2) heat exchange method, and (3) control method used to deliver the necessary hot water at the required tem- perature under varying water demand conditions. Application of water-heating equipment within the overall design of the hot-water system is based on (1) location of the equipment within the system, (2) related temperature requirements, (3) volume of water to be used, and (4) flow rate. Consideration of electricity demand charges on the utility bill is also of growing importance. Additional planning is required when the system providing the potable hot water is also used for space heating or other purposes. Some special water heater designs, made for this purpose, are known as combi- nation space- and water-heating systems. Energy Sources Choice of energy source(s) is influenced by local availability of the various energy sources, equipment type, space considerations, locations of water heaters in structures, initial cost, operating cost, maintenance requirements, and other factors. A life-cycle cost anal- ysis is highly recommended. In making energy conservation choices, consult ASHRAE Stan- dards 90.1 and 90.2, or the sections on Service Water Heating Sys- tems of ASHRAE Standard 100, as well as the section on Design Considerations in this chapter. 4. DESIGN CONSIDERA TIONS Hot-water system design should consider the following: · Water heaters of different sizes and insulation may have different standby losses, thermal efficiency, or energy factors. · A distribution system should be properly laid out, sized, and insu- lated to deliver adequate water quantities at temperatures satisfac- tory for the uses served. This reduces standby loss and improves distribution system efficiency. Locating fixtures or usage devices close to each other and to the water-heating equipment is partic- ularly important for minimizing piping lengths and diameters, and thus reducing wait times as well as water and energy waste. · Heat traps between recirculation mains and infrequently used branch lines reduce convection losses to these lines and improve distribution system efficiency. In small residential systems, heat traps can be applied directly to the water heater for the same pur- pose. · Controlling circulating pumps to operate only as needed to main- tain proper temperature at the end of the main reduces losses on return lines. · Provision for shutdown of circulators during building vacancy reduces standby losses. For most large water heating systems, providing some amount of redundant water heating capacity is a good idea, such that water heating loads can still be met when other water heaters in the system are not operational or require regular maintenance. When water heaters are installed in flow parallel, they should be the same size | {}
1c266c9d-04e0-428c-9a73-e37a0ca8abae | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Service Water Heating 51.3 heating rate and other design characteristics to help simplify flow and energy (run time) balancing. Moreover, when heaters are sepa- rate from storage tanks, multiple heaters can be installed in flow par- allel with each other, but serving a single storage tank. Alternatively, they can each serve a separate (equal-sized) storage tank, with each of the storage tanks in flow parallel. To provide back-up heating, a water heater having a heating capacity equal to the other water heaters in the system should be provided, allowing peak loads to be met when any one water heater and/or storage tank is out of com- mission. If design-day peak needed heating rate is 2, then for N equal-sized water heaters, each water heater needs to have a design day heating rate of Q/(N - 1), resulting in having an additional back- up heating capacity amounting to 1/(N - 1) of the total design day load. For example, for N = 5, each water heater needs to have a design-day heating capacity of 1/4 of the design-day total needed heating rate. Four water heaters are needed to serve the design-day load, and the fifth provides a back-up capacity of another 1/4 of the design-day total needed heating rate. W orkable combinations of total design-day needed heating rate and storage volume are deter- mined the same way as for all systems. Design Path for Savings Reducing hot-water consumption not only results in lower water and sewer costs, it is the most effective way to reduce water-heating energy use. Designing in a reverse direction, starting with the hot- water-using equipment and moving back to the water heater, is an effective thought process to achieve higher system efficiency and performance. Step 1: Specify high-performance equipment and accessories that use less hot water, or alternative processes that eliminate the need for hot water for that particular task. Step 2: Locate sinks and equipment in proximity to each other and to the water heater, and optimize the plumbing layout; these are key factors to the efficiency and performance of the overall system. Delivering hot water more efficiently yields permanent energy sav- ings and improved hot-water delivery performance. Consider dis- tributed generation or point-of-use heating for distant sinks where it does not make sense to extend the primary system's distribution system. Step 3: Specify high-efficiency water heaters that are compatible with the distribution system and end-use fixtures. This is impera- tive. Step 4: Before the hot-water system design is finalized, consider integrating preheating technologies such as heat recovery or solar heating. Step 5: Verify proper installation ofthe system, including simple monitoring equipment, which can play an important role in com- missioning and maintaining the system. 5. END-USE FIXTURES Advanced end-use fixtures play an important role in reducing the size of the primary water heater(s) and simplifying the distribution system design. Use of high-efficiency, low-water-use equipment and fixtures, such as faucet aerators, reduced-flow (but still ade- quate) showerheads, and advanced clothes washers and dishwash- ers, achieves multiple benefits, including the ability to use lower water temperatures and lowered total hot water consumption. Thus, in many instances, it is practical to provide localized heating devices, either near or built into the fixture or device, thereby addi- tionally reducing distribution system heat losses and piping first costs. Providing localized heating devices also reduces demands on piping diameter and length for the remaining hot-water distribution system, and may reduce or eliminate the need for hot-water recircu- lation loops in some applications. The U.S. Energy Policy Act of 1992 established a maximum flow rate requirement for hand sink faucets and showerheads. These maximum flow rates were later revised and lowered to 30 mL/s for public hand sinks and 140 mL/s for private hand sinks. Manufactur- ers are now making public sink faucet aerators that flow as low as 20 mL/s and private sink faucet aerators that use 95 mL/s. Similarly, manufacturers are now producing showerheads that use 125 mL/s, reduced from the federally mandated 160 mL/s flow rate. Similar improvements have been made in fixtures and equipment for food-service industry hot-water systems. The U.S. Energy Pol- icy Act of 2005 set a maximum flow rate of a prerinse spray valve at 100 mL/s (DOE 2011), reduced from conventional models rated at 160 to 285 mL/s. Spray valves flowing at 40 to 80 mL/s are now available. Dishwashers are now available with built-in heat recovery capability, which reduces dishwasher total energy and hot-water requirements and, when combined with localized or built-in heating ability, can significantly reduce hot-water demands on a building's central hot-water system. Use of localized booster water heaters to produce the high water temperatures required for sanitization of wares in commercial dishwashers is commonplace and reduces temperatures required from a central hot-water system. 6. DISTRIBUTION Piping Material Traditional piping materials include galvanized steel used with galvanized malleable iron screwed fittings. Copper piping and copper water tube types K, L, or M have been used with brass, bronze, or wrought copper water solder fittings. PEX and CPVC piping materials are now used as an alternative in residential appli- cations. Another alternative piping material is stainless steel tube. Particular care must be taken to ensure that the application meets the design limitations set by the manufacturer, particularly regarding temperature and pressure limits, and that the correct materials and methods of joining are used. These precautions are easily taken with new projects, but become more difficult during repairs of existing work. Using incompatible piping, fittings, and joining methods or materials must be avoided, because they can cause severe problems, such as corrosion or leakage caused by dif- ferential thermal expansion. Today, most potable water supplies require treatment before dis- tribution; this may cause the water to become more corrosive. Therefore, depending on the water supply, traditional galvanized steel piping or copper tube may no longer be satisfactory, because of accelerated corrosion. Galvanized steel piping is particularly sus- ceptible to corrosion (1) when hot water is between 60 and 80°C and (2) where repairs have been made using copper tube without a non- metallic coupling. Note that plumbing can be either piping (rela- tively thick wall) or tubing (relatively thin wall), although piping is used in this chapter for both. Before selecting any water piping material or system, consult the local code authority. The local water supply authority should also be consulted about any history of water aggressiveness causing failures of any particular material. Pipe Sizing The Reduction ofLead in Drinking Water Act (effective January 4, 2014) prohibits the use of any pipe, pipe or plumbing fitting or fixture, and associated solder and flux used in all facilities for potable water piping that is not "lead free" as defined in section 1417(d) of the Safe Drinking Water Act, because of possible lead contamination of the water supply (EPA 2013). Sizing hot-water supply pipes from a hydraulic (pressure drop) perspective involves the same principles as sizing cold-water supply pipes (see Chapter 22 ofthe 2017 ASHRAE Handbook-Fundamen- tals). The water distribution system must be correctly sized for the total hot-water system to function properly. Hot-water demand Inc. ASHRAE, 2019 user. single for Licensed | {}
b84db0f0-e560-4c99-975b-c77f6d4e9e35 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 51.4 2019 ASHRAE Handbook- -HVAC Applications (SI) ![image](/image/placeholder) 92 92 90 90 88 88 % % EFFICIENCY, 86 86 84 EFFICIENCY, 84 THERMAL THERMAL 82 82 Hybrid Boiler 80 80 Storage 78 78 Tankless 76 76 15 20 25 30 35 40 45 50 55 15 20 25 30 35 40 45 50 55 INLET WATER TEMPERATURE, °C INLET WATER TEMPERATURE, °C Fig. 1 Effect of Inlet Water Temperature on Thermal Efficiency of Condensing Tankless Heater varies with the type of establishment, usage, occupancy, and time of day. The piping system should be able to meet peak demand at an acceptable pressure loss. It is important not to oversize hot-water supply pipes, because this adversely affects system heat loss and overall energy use. Supply Piping Table 16, Figures 27 and 28, and manufacturers , specifications for fixtures and appliances can be used to determine hot-water demands. These demands, together with procedures given in Chapter 22 of the 2017 ASHRAE Handbook-Fundamentals, are used to size the mains, branches, and risers. Allowance for pressure drop through the heater should not be overlooked when sizing hot-water distribution systems, particularly where instantaneous water heaters are used and where the available pressure is low. Pressure Differential Sizing both cold- and hot-water piping requires that the pressure differential at the point of use of blended hot and cold water be kept to a minimum. This is particularly important for tubs and showers, because sudden changes in flow at fixtures cause discomfort and a possible scalding hazard. Pressure-compensating devices are avail- able. Effect of Distribution Design on Efficiency of Condensing Heaters The distribution system design and operation can have a signifi- cant impact on the efficiency of gas-fired condensing heaters. Lab- oratory tests have shown a significant reduction in the ability of high-efficiency gas water heaters to maintain full condensing func- tion because of elevated inlet-water temperatures. Figure 1 shows the reduction in thermal efficiency of a condensing tankless heater when inlet water temperatures are increased to simulate preheating equipment such as solar water heating systems and heat recovery devices (Huestis 2013; Johnson et al. 2013). The unit loses all con- densing function at inlet temperatures of 54°C, where the thermal efficiency reaches 82%, typical of a standard-efficiency unit. Fig. 2 Effect of Return Water Temperature on Operating Efficiency of Condensing Heaters A second study looked at the effect of continuous recirculation at a narrower band of return water temperatures on the operating effi- ciency of various heaters (Figure 2) with an outlet temperature of 54°C at 190 mL/s water flow rate (Schoenbauer 2012, 2013). This study shows consistent loss of thermal efficiency with higher return water temperatures observed at varying levels across product cate- gories, though the specific loss of efficiency depends on unit design, specifically heat exchanger surface area and storage volume. The storage heater with a storage volume of 208 L and boiler with a flooded volume of less than 14 L demonstrated a steady decline in efficiency from approximately 90% thermal efficiency at 32°C to 84% efficiency at 49°C (partially condensing). For the hybrid heater with a storage volume of 7.6 L, the unit maintained condensing function with an average efficiency of 90% with a return water tem- perature from 32 to 43°C, but then the efficiency rapidly dropped to 78% at 49°C return water temperature. The tankless heater per- formed the worst, with a large drop in operating efficiency from 90% at 31°C to 76% efficiency at 49°C. Both the hybrid and tank- less units lost the ability to capture latent heat from the exhaust gases at 49°C. Finding alternatives to the use of continuous recircu- lation systems, or maintaining a return temperature at 38°C or lower, would significantly improve the efficiency of condensing water heaters. Piping Heat Loss and Hot- W ater Delivery Delays Good hot-water distribution system layout is very important, for both user satisfaction and energy use. This has become increasingly important with the mandated use of low-flow fixtures, which can cause lengthy delays and increased water waste while waiting for hot water to arrive at fixtures compared to higher-flow designs. In general, it is desirable to put fixtures close to each other and close to the water heater(s) that serve them. This minimizes both the diam- eter and length of the hot-water piping required. Recent work has shown that energy loss from hot-water piping due to both heat loss and water waste waiting for hot water to arrive at fixtures can be a significant percentage of total water-heating system energy use (Hiller 2005a; Klein 2004a, 2004b, 2004c; Lutz 2005). Energy losses from hot-water distribution systems usually amount to at Inc. ASHRAE, 2019 user. single for Licensed | {}
658f6272-9b47-44fc-9002-7fa3ed7854b3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Service Water Heating 51.5 Table 1 Piping Heat Loss Factors for Foam In Piping Heat Loss Factors for Foam Insulation with Thermal Conductivity of 0.114 W/(m2.K) ¦ Nominal Pipe Size ¦ Foam Insulation Thickness, mm ¦ UAzero flow, W/(m · K) ¦ High-Value UA flowing' W/(m ·K) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 13 mm rigid copper ¦ 0 ¦ 0.391 ¦ 0.623 ¦ ¦ ¦ 13 ¦ 0.222 ¦ 0.346 ¦ ¦ ¦ 19 ¦ 0.201 ¦ 0.329 ¦ ¦ 19 mm rigid copper ¦ 0 ¦ 0.672 ¦ 0.762 ¦ ¦ ¦ 13 ¦ 0.260 ¦ 0.433 ¦ ¦ ¦ 19 ¦ 0.246 ¦ 0.415 ¦ ¦ 19 mm rolled copper ¦ 0 ¦ 0.579 ¦ 0.579 ¦ ¦ ¦ 19 ¦ 0.239 ¦ 0.277 ¦ ¦ 19 mm roll CU-sand ¦ 0 ¦ 2.08 ¦ 4.89 ¦ ¦ ¦ 19 ¦ 0.269 ¦ 0.307 ¦ ¦ 19 mm PEX-AL-PEXa ¦ 0 ¦ 0.952 ¦ 0.945 ¦ ¦ ¦ 13 ¦ 0.344 ¦ 0.344 ¦ ¦ ¦ 19 ¦ 0.273 ¦ 0.312 ¦ ¦ 19 mm PEXb ¦ 0 ¦ 0.927 ¦ 1.01 ¦ ¦ ¦ 19 ¦ 0.276 ¦ 0329 ¦ ¦ 13 mm PEX ¦ 0 ¦ 0.759 ¦ 0.759 ¦ ¦ ¦ 19 ¦ 0.225 ¦ 0.225 ¦ ¦ 10 mm PEX ¦ 0 ¦ ¦ ¦ ¦ 19 mm CPVC ¦ 0 ¦ 0.762 ¦ 0.901 ¦ ¦ ¦ 19 ¦ 0.257 ¦ 0.295 ¦ Note: Results are for horizontal in-air tests unless otherwise noted. Sources: Hiller (2005a, 2005b, 2006b, 2008, 2009). aHigh-density cross-linked polyethylene, aluminum, high-density cross-linked poly- ethylene multilayer pipe. bHigh-density cross-linked polyethylene. least 10 to 20% of total hot-water system energy use in most potable water-heating systems (Hiller 2005a), and are often as high as 50%; losses of over 90% have been found in some installations (Hiller and Miller 2002; Hiller et al. 2002). Hiller (2005a, 2005b, 2006a, 2006b) measured both piping heat loss and time, water, and energy waste while waiting for hot water to arrive at fixtures. This research measured piping heat loss UA fac- tors for several commonly used piping sizes, types, and insulation levels. See ASHRAE Standard 90 series for pipe insulation require- values are a slight function of water flow rate and ments. UAflowing temperature difference between the hot water and the surroundings. However, for many practical calculation purposes, UA can be con- sidered constant at the values shown in Table 1. Hiller (2008) found that bare copper piping buried in damp sand (typical of under-slab piping) exhibited heat loss rates over eight times higher than the same pipe in air. This much higher heat loss rate is believed to be caused by moisture in the sand near the pipe behaving like a heat pipe by evaporating, recondensing (thus trans- ferring heat to sand particles a short distance away much faster than conduction would), and then wicking back to the pipe. Adding insu- lation to buried piping dramatically reduced the heat-pipe effect by lowering the surface temperature seen by the moisture. Hence, as can be seen in Table 1, adding 19 mm foam pipe insulation to copper piping reduces the heat loss rate in air to around one-half of the uninsulated value, but adding the same insulation to pipe buried in damp sand reduces the heat loss rate to only around 6% ofits unin- sulated value, a reduction by a factor of around 16. Thus adding pipe insulation is highly beneficial for buried piping, and is recom- mended. Table 1 also shows that all ofthe plastic pipes tested to date exhibit moderately to significantly higher heat loss rates than comparably sized copper pipes when tested uninsulated in air. However, when insulated, they exhibit moderately to significantly lower heat loss rates than comparably sized copper pipes with the same insulation. Adding 19 mm foam reduces plastic pipe heat loss rates to around 30% of their uninsulated values when tested in air. This is a reduction in heat loss rate by a factor of three, compared to a factor of two for insulation on copper piping. This result suggests that plastic pipes have higher emissivity for radiation heat loss from the piping than does copper. Theoretical analysis suggests that, for the pipe sizes tested, radiation heat loss from the pipes represents between 30% and 70% oftotal heat loss rate from the pipes, depending on pipe type and size. It has been suggested that the emissivity of copper pipe may increase with age as the outer surface oxidizes to its normal dull- brown appearance from its original bright, shiny surface. Repeat tests on aged copper pipe have not yet been performed. The UA factors of Table 1 are used in Equations (1) to (8) to determine heat loss rates from piping during both flowing and zero- flow (cooldown) conditions, and to find temperature drop while water is flowing through pipe, and pipe temperature at any time during cooldown. Note that piping heat loss and pipe temperature drop are not constant with length under flowing conditions, because the temperature of each successive length of pipe is less than the one before it. The same is true for zero-flow pipe cooldown with respect to time, because the pipe is at a progressively lower temperature at each successive time interval. The result is that pipe temperatures decay inverse-exponentially with length under flowing conditions and with time under cooldown conditions. This is why log-mean temperature difference must be used in heat loss calculations instead of a simple linear temperature difference (Rohsenow and Choi 1961). Under flowing conditions, 0 = mcp (Thot in - Thot out) and (1) 0 = UAflowing Lpipe△Tlm (2) For water flowing in pipes in a constant-air-temperature environ- ment, [(Thot in Tair)-(Thot out Tair)] - △TIm In[(Thot in Tair)/(T hot out air)] T (3) When UAflowing, rate, air temperature, and entering water flow water temperature are known, Equations (1) to (3) can be combined and rearranged to determine pipe-exiting water temperature as fol- lows: (UAflowing)(Lpipe) (mc Pwater Thot out (Thot in - Tair)e + = Tair (4) where △TIm = log mean temperature difference, K 0 = heat loss rate, W m = water flow rate, kg/s Cp = specific heat of water, 4186.8 J/(kg·K) Thot in temperature entering pipe, °C = water Thot out temperature leaving pipe, °C 수 water UAflowing = flowing heat loss factor per metre of pipe, W/(m · K) Lpipe = length of hot-water pipe, m Note that the quantity (UAflowing)(Lpipe)/(mcp) water must be non- dimensional, so appropriate units must be used. Under zero-flow cooldown conditions, (Thot /1 5) /(t2-t1) 0 = (Mcp)w,p,i - Thot (5) Inc. ASHRAE, 2019 user. single for Licensed 0 = UAzero-flow(△TIm) ⑥ | {}
245be1a1-64f3-49b4-9186-ebb043820c90 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 51.6 Table 2 Approximate Heat Loss from Piping at 60°C Inlet, 21°C Ambient ¦ Nominal Size, mm ¦ Bare Copper Tubing, W/m ¦ Bare Copper UA, W/(m·K) ¦ 13 mm Glass Fiber Insulated Copper Tubing, W/m ¦ 13 mm Glass Fiber Insulated Copper UA, W/(m·K) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 19 ¦ 29 ¦ 0.74 ¦ 17.0 ¦ 0.43 ¦ ¦ 25 ¦ 37 ¦ 0.93 ¦ 19.5 ¦ 0.50 ¦ ¦ 32 ¦ 43 ¦ 1.11 ¦ 22.5 ¦ 0.57 ¦ ¦ 38 ¦ 51 ¦ 1.32 ¦ 24.4 ¦ 0.62 ¦ ¦ 50 ¦ 63 ¦ 1.63 ¦ 28.5 ¦ 0.73 ¦ ¦ 64 ¦ 77 ¦ 1.97 ¦ 32.5 ¦ 0.83 ¦ ¦ 75 ¦ 90 ¦ 2.32 ¦ 38.0 ¦ 0.96 ¦ ¦ 100 ¦ 115 ¦ 2.96 ¦ 46.5 ¦ 1.19 ¦ And for pipe in a constant-air-temperature environment: [(Thot 4 Tair) - (Thot 12 Tair)] - - ATIm ln[(T hot / Tair)/(T hot 12 air )] - - T (7) (UA zero-flow)(12 -4) (Mcp)w.p.i Thot 12 4 air)e + (Thot = Tair - T (8) where /1 = initial time 12 = final time 0 = average heat loss rate from time 4 to time 12, W/m (Mcp)w.p.i=sum of mass times specific heat for water, pipe, and insulation, J/ (m· K) Thot / = pipe temperature at the °C Thot 「2 = pipe temperature at t2, °C UAzero-flow-zero-flow heat loss factor per metre of pipe, W/(m · K) Note that the quantity (UA zero-flow)(12-11)/(MCp)w.p.i must be non- dimensional, so appropriate units must be used. Inc. ASHRAE, 2019 user. single for Licensed Pipe temperature at any time during the cooldown process is determined by Equation (8). Total energy lost from piping during zero-flow cooldown is determined by calculating the pipe tempera- ture at time 12 and multiplying the average heat loss rate between t1 and t2 determined by Equation (5) times the duration of the cooldown period (t2-t1). An alternative is to calculate heat loss over short time periods using Equation (6) and sum the results. Table 2 contains earlier piping heat loss data, and shows com- puted piping UA values based on those data. Hiller (2005a, 2005b, 2006b) also produced tables of water/ energy wasted while waiting for hot water to arrive at fixtures. Waste is a strong function ofpipe material, interior finish, diameter, fittings present, flow rate, initial pipe temperature, and entering hot- water temperature. The amount of water wasted to drain is generally an amount greater than pipe volume because temperature of some of the first hot water traveling through the pipe is degraded to below a usable temperature. Initial flow ofhot water into a pipe full of cooler water often does not behave as predicted by steady-state flow theory, because both hot and cold water are flowing simultaneously in the same pipe (a non-steady-state condition). At least three different flow regimes were identified: (1) stratified flow (at low flow rates in horizontal pipes, hot water flows farther along the top side of the pipe than on the bottom side; this can happen even in small-diameter pipes), (2) normal turbulent flow, and (3) shear flow (a relatively sharp hot/ cold interface with little turbulence-induced mixing of hot and cold water because the normal boundary layer is slow to develop under some conditions). These flow regimes are important because each causes different amounts of temperature degradation as hot water flows through the pipe. 2019 ASHRAE Handbook-HVAC Applications (SI) For detailed information on time, water, and energy waste while waiting for hot water to arrive at fixtures, see Hiller (2005b). Simply summarized here, the amount of water waste can be expressed as the ratio of the actual amount of water (actual flow or AF) wasted while waiting for hot-enough-to-use water to arrive at fixtures (defined as 40.5°C by Hiller) divided by pipe volume (PV). When the pipe cools below a usable temperature, AF/PV ratios are usually in the range of 1.0 to 2.0, but can go to infinity at low flow rates in long, uninsulated pipe in cold or otherwise adverse (e.g., damp) heat transfer environments. The critical length of pipe at which AF/PV goes to infinity can be calculated for any flow rate and temperature conditions, using the piping UAflowing factors and Equations (1) to (4). For preliminary engineering design and energy use calculations, Hiller recommends assuming AF/PV values of1.25 to 1.75. For more refined analyses, accounting better for temperature effects on AF/ PV ratio, the data tables in the original reference should be con- sulted. More such data on a larger variety of pipe sizes, types, and environments would be beneficial, but are not currently available. Examples 1 1 to 14 demonstrate how to use piping heat loss and delivery water waste information to calculate hot-water system energy use. Hot- w ater Recirculation Loops and Return Piping Hot-water recirculation loops are commonly used where piping lengths are long and hot water is desired immediately at fixtures. In recirculation-loop systems, return piping and a circulation device are provided. Some recirculation-loop systems use buoyancy-driven natural convection forces to circulate flow, but most are equipped with circulating pumps to force water through the piping and back to the water heater, thus keeping water in the piping hot. The water circulation pump may be controlled by a thermostat (in the return line) set to start and stop the pump over an acceptable temperature range. This thermostat can significantly reduce both heat loss and pumping energy in some applications. An automatic time switch or other control should turn water circulation off when hot water is not required. Other, more advanced circulating pump control schemes, such as on-demand types using manual initiation, flow switches, or occupancy sensors, are also available. Because hot water is corrosive, circulating pumps should be made of corrosion- resistant material. For small installations, a simplified pump sizing method is to allow 3 mL/s for every fixture unit in the system, or to allow 30 mL/ s for each 20 or 25 mm riser; 60 mL/s for each 32 or 40 mm riser; and 130 mL/s for each riser 50 mm or larger. Dunn et al. (1959) and Werden and Spielvogel (1969a, 1969b) discuss heat loss calculations for large systems. For larger installa- tions, piping heat losses become significant. A quick method to size the pump and return for larger systems is as follows: 1. Determine total length of all hot-water supply and return piping. 2. Choose an appropriate value for piping heat loss from Tables 1 or 2 or other engineering data (usually supplied by insulation com- panies, etc.). Multiply this value by the total length of piping involved. A rough estimation can be made by multiplying the total length of covered pipe by 30 W/m or uninsulated pipe by 60 W/ m. Table 2 gives actual heat losses in pipes at a service water temperature of 60°C and ambient temperature of 21°C. The values of 30 or 60 W/m are only recommended for ease in cal- culation. 3. Determine pump capacity as follows: q 0 = Pcp △t where (9) | {}
3a22790b-220f-4853-9473-6dc9e7854b66 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Service Water Heating 51.7 ![image](/image/placeholder) VENT SUPPLY RETURN SUPPLY SUPPLY SUPPLY SUPPLY 0. JPP ら � P 0 MAIN S S S RN ▲ RET RETURN RETURN RETURN RETURN → ⑥ + ⑥ N N B Fig. 3 Arrangements of Hot- Water Circulation Lines Qp = pump capacity, L/s 9 = heat loss, W P = density of water = 0.99 kg/L (50°C) Cp = specific heat of water = 4186.8 J/(kg· K) At = allowable temperature drop, K For a 10 K allowable temperature drop, 9 q Qp(L/s) = 0.99 x 4186.8 x 10 41 450 (10) Caution: This calculation assumes that a 10 K temperature drop is acceptable at the last fixture. 4. Select a pump to provide the required flow rate, and obtain from the pump curves the pressure created at this flow. 5. Check that the pressure does not exceed the allowable friction loss per metre of pipe. 6. Determine the required flow in each circulating loop, and size the hot water return pipe based on this flow and the allowable friction loss from Step 5. Where multiple risers or horizontal loops are used, balancing valves with means of testing are recommended in the return lines. A swing-type check valve should be placed in each return to prevent entry of cold water or reversal of flow, particularly during periods of high hot-water demand. Three common methods of arranging circulation lines are shown in Figure 3. Although the diagrams apply to multistory buildings, arrangements (A) and (B) are also used in residential designs. In circulation systems, air venting, pressure drops through the heaters and storage tanks, balancing, and line losses should be considered. In Figures 3A and 3B, air is vented by connecting the circulating line below the top fixture supply. With this arrangement, air is eliminated from the system each time the top fixture is opened. Generally, for small installations, a nominal pipe size (NPS) 15 or 20 mm hot-water return is ample. All storage tanks and piping on recirculating systems should be insulated as recommended by the ASHRAE Standard 90 series and Standard 100. Heat-Traced, Nonreturn Piping In this system, the fixtures can be as remote as in the hot-water recirculation loops and return piping section. The hot-water supply piping is heat traced with electric resistance heating cable prein- stalled under the pipe insulation. Electrical energy input is self- regulated by the cable's construction to maintain the required water temperature at the fixtures. No return piping system or circulation pump is required. Multiple Water Heaters Depending on fixture spacing, required pipe lengths, and draw spacing, it may be more energy-efficient (and sometimes provide lower first cost) to use more than one water heater rather than using extensive piping runs. Energy losses from high-efficiency water heaters can be lower than recirculation-loop piping heat losses ifthe distance from water heaters to fixtures exceeds 10 to 20 m (Hiller 2005a). Although there are considerations beyond energy use, such as installation, maintenance, and space requirements, using more than one water heater should always be evaluated when designing water heating systems, even in residences, because ofthe potentially large energy savings. Commercial Dishwasher Piping and Pressure Considerations Adequate flow rate and rinse pressure must be maintained for automatic dishwashers to achieve efficient dishwashing in com- mercial kitchens. National Sanitation Foundation (NSF) standards for dishwasher water flow pressure are 100 kPa (gage) minimum, 170 kPa (gage) maximum, and 140 kPa (gage) ideal. Flow pressure is the line pressure measured when water is flowing through the rinse arms of the dishwasher. Low flow pressure can be caused by undersized water piping, stoppage in piping, or excess pressure drop through heaters. Low water pressure causes an inadequate rinse, resulting in poor drying and sanitizing of the dishes. If flow pressure in the supply line to the dishwasher is below 100 kPa (gage), a booster pump or other means should be installed to provide supply water at 140 kPa (gage). Flow pressure over 170 kPa (gage) causes atomization of the 82°C rinse water, resulting in excessive temperature drop (which can be as much as 8 K between rinse nozzle and dishes). A pressure regulator should be installed in the supply water line adjacent to the dishwasher and external to the return circulating loop (if used). To reduce operating difficulties, piping for automatic dishwashers should be installed according to the following recom- mendations: · The cold-water feed line to the water heater should be no smaller than NPS 25 mm. · The supply line that carries 82°C water from the water heater to the dishwasher should not be smaller than NPS 19 mm. · No auxiliary feed lines should connect to the 82°C supply line. · A return line should be installed if the source of 82°C water is more than 1.5 m from the dishwasher. · Forced circulation by a pump should be used if the water heater is installed on the same level as the dishwasher, if the length of return piping is more than 18 m, or if the water lines are trapped. · If a circulating pump is used, it is generally installed in the return line. It may be controlled by (1) the dishwasher wash switch, (2) a manual switch located near the dishwasher, or (3) an immersion or strap-on thermostat located in the return line. · A pressure-reducing valve should be installed in the low- temperature supply line to a booster water heater, but external to a recirculating loop. It should be adjusted, with the water flowing, to the value stated by the washer manufacturer. · A check valve should be installed in the return circulating line. · If a check-valve water meter or a backflow prevention device is installed in the cold-water line ahead of the heater, it is necessary to install a properly sized diaphragm-type expansion tank be- tween the water meter or prevention device and the heater. · NSF standards require an NPS 6 mm IPS connection for a pres- sure gage mounted adjacent to the supply side of the control valve. They also require a water-line strainer ahead of any elec- trically operated control valve (Figure 4). Inc. ASHRAE, 2019 user. single for Licensed | {}
3c7bb00b-d03f-4ac7-a54f-c7f99e67c27b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 51.8 2019 ASHRAE Handbook- HVAC Applications (SI) ![image](/image/placeholder) VACUUM BREAKER FINAL RINSE CONTROL VALVE 8 mm IPS TOP OF DISHWASHER VALVE LINE STRAINER 82°C FINAL RINSE WATER Fig. 4 National Sanitation Foundation (NSF) Plumbing Requirements for Commercial Dishwasher ![image](/image/placeholder) HOT WATER OUT (HIGH TEMPERATURE) WATER HEATER (HIGH TEMPERATURE) T COLD HOT WATER OUT WATER IN (LOW TEMPERATURE) Fig. 5 Two-Temperature Service with Mixing Valve · NSF standards do not allow copper water lines that are not under constant pressure, except for the line downstream of the solenoid valve on the rinse line to the cabinet. Two-Temperature Service Where multiple temperature requirements are met by a single system, the system temperature is determined by the maximum temperature needed. Where the bulk ofthe hot water is needed at the higher temperature, lower temperatures can be obtained by mixing hot and cold water. Automatic mixing valves reduce the temperature of the hot water available at certain outlets to prevent injury or damage (Figure 5). Applicable codes should be consulted for mixing valve requirements. Where predominant use is at a lower temperature, the common design heats all water to the lower temperature and then uses a separate booster heater to further heat the water for the higher- temperature service (Figure 6). This method offers better protection against scalding. A third method uses separate heaters for the higher-temperature service (Figure 7). It is common practice to cross-connect the two heaters, so that one heater can serve the complete installation tem- porarily while the other is valved off for maintenance. Each heater should be sized for the total load unless hot-water consumption can be reduced during maintenance periods. Manifolding Where one heater does not have sufficient capacity, two or more water heaters may be installed in parallel. If blending is needed, a single mixing valve of adequate capacity should be used. It is diffi- cult to obtain even flow through parallel mixing valves. ![image](/image/placeholder) HOT WATER OUT (HIGH TEMPERATURE) HOT WATER OUT (LOW TEMPERATURE) PRIMARY BOOSTER WATER WATER COLD HEATER HEATER WATER IN Fig. 6 Two-Temperature Service with Primary Heater and Booster Heater in Series ![image](/image/placeholder) HOT WATER OUT HOT WATER OUT (LOW TEMPERATURE) (HIGH TEMPERATURE) WATER HEATER WATER HEATER (LOW TEMPERATURE) (HIGH TEMPERATURE) COLD WATER IN Fig. 7 Two-Temperature Service with Separate Heater for Each Service ![image](/image/placeholder) GATE VALVE HOT (TYPICAL) OUTLE EXPANSION TANK COLD INLET UNION (TYPICAL) CHECK VALVE Fig. 8 Reverse/Return Manifold System Heaters installed in parallel should have similar specifications: the same input and storage capacity, with inlet and outlet piping arranged so that an equal flow is received from each heater under all demand conditions. An easy way to get balanced, parallel flow is to use reverse/ return piping (Figure 8). The unit having its inlet closest to the cold- water supply is piped so that its outlet is farthest from the hot-water supply line. Quite often this results in a hot-water supply line that reverses direction (see dashed line, Figure 8) to bring it back to the first unit in line; hence the name reverse/return. Care must be used in commissioning heaters in parallel flow. Field testing (Hiller and Johnson 2015) showed that having water heaters in parallel flow can result in each heater having dramatically different numbers of on/off firing cycles: an important consideration in equipment life and maintenance. Having heaters set to even slightly different on/off temperatures can cause the heater set to the highest temperatures to come on first and end up being the only heater to fire to make up most of the heat loss from the storage and distribution system. Inc. ASHRAE, 2019 user. single for Licensed | {}
ce931611-bf47-4f1a-be2c-3c6bb64d7d00 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Service Water Heating 51.9 7. WATER-HEA TING EQUIPMENT Gas-Fired Systems Storage water heaters incorporate the burner(s), storage tank, outer jacket, and controls such as a thermostat in a single unit and typically have an input-to-storage capacity ratio of less than 300 W/L. Instantaneous water heaters are produced in two distinctly different types. Tank-type instantaneous heaters have an input-to- storage capacity ratio of 300 W/L or more and a thermostat to con- trol energy input to the heater. Water-tube instantaneous heaters have minimal water storage capacity. They usually have a flow switch that controls the burner, and may have a modulating fuel valve that varies fuel flow as water flow changes. Tankless water heaters have almost no storage capacity, and heat water as it flows once through the water heater. Heating rate required varies with water flow rate and needed temperature rise. They are best suited for steady-state operation. Most modern gas-fired tankless water heaters have a flow switch or equivalent to confirm flow before the burner activates. Some have advanced multistage or modulating burners to better control outlet temperature. Some also incorporate fixed or modulating water flow rate controls to ensure that water tem- perature reaches at least a minimum outlet temperature (i.e., it restricts flow rate, possibly below that which the user requested, to avoid undesirably cool outlet water temperature ifburners are already operating at maximum heating rate). Most advanced designs also incorporate electronic ignition controls, thus minimizing standby energy losses compared to having a tank and continuously burning pilot light. Properly applied tankless water heaters thus have lower overall energy use and higher efficiency compared to minimum- efficiency tank types serving the same loads. Note, however, that tankless gas water heaters have on/off cycling-rate-related energy losses that, under water draw events of a small volume, short dura- tion, or intermittent nature may reduce their system efficiency and hot water delivery performance (Glanville et al. 2013). They may also have minimum flow rate requirements before they activate, which may require users to modify their behavior (e.g., use a higher flow rate than they normally would and/or leave water running when they would normally turn it off) to obtain hot water. Sometimes, it may be beneficial to reduce the hot-water delivery temperature to reduce point-of-use mixing with cold water, thereby increasing hot-water flow rate. Circulating tank water heaters are classified in two types: (1) automatic, in which the thermostat is located in the water heater, and (2) nonautomatic, in which the thermostat is located within an asso- ciated storage tank. Hot-water supply boilers are capable of providing service hot water. They are typically installed with separate storage tanks and applied as an alternative to circulating tank water heaters. Outdoor models are wind- and rain-tested. They are available in most of the classifications previously listed. Direct-vent models are installed indoors, but are not vented through a conventional chimney or gas vent and do not use ambient air for combustion. They must be installed with the means specified by the equipment manufacturer for venting (typically horizontal) and for supplying combustion air from outside the building. Power vent equipment uses a powered fan or blower to move combustion products, allowing horizontal as well as vertical venting. Direct-fired equipment passes cold water through a stainless steel or other heat exchange medium, which breaks up the water into very small droplets. These droplets then come into direct contact with heat rising from a flame, which heats the water directly. Residential water-heating equipment is usually the automatic storage type, although increasing numbers of tankless water heaters are being installed. For industrial and commercial applications, commonly used types of heaters are (1) automatic storage, (2) cir- culating tank, (3) instantaneous/tankless and (4) hot-water supply boilers. Installation guidelines for gas-fired water heaters can be found in the National Fuel Gas Code, NFPA Standard 54/ANSI Standard Z223.1. This code also covers sizing and installation of venting equipment and controls. Oil-Fired Systems Oil-fired water heaters are generally the storage tank type. Mod- els with a storage tank of200 L or less with an input rating of30 kW or less are usually considered residential models. Commercial mod- els are offered in a wide range of input ratings and tank sizes. There are models available with combination gas/oil burners, which can be switched to burn either fuel, depending on local availability. Installation guidelines for oil-fired water heaters can be found in NFPA Standard 31/ANSI Standard Z95.1. Electric Electric water heaters are generally the storage type, consisting of a tank with one or more immersion heating elements. The heating elements consist of resistance wire embedded in refractories having good heat conduction properties and electrical insulating values. Heating elements are fitted into a threaded or flanged mounting for insertion into a tank. Thermostats controlling heating elements may be of the immersion or surface-mounted type. Residential storage tank water heaters range up to 450 L with input up to 12 kW. They have a primary resistance heating element near the bottom and often a secondary element located in the upper portion of the tank. Each element is controlled by its own thermo- stat. In dual-element heaters, the thermostats are usually interlocked so that the lower heating element cannot operate if the top element is operating. Thus, only one heating element operates at a time to limit the current draw. Commercial storage tank water heaters are available in many combinations of element quantity, wattage, voltage, and storage capacity. Storage tanks may be horizontal or vertical. Compact, low-volume models are used in point-of-use applications to reduce hot-water piping length. Locating the water heater near the point of use makes recirculation loops unnecessary. Instantaneous or tankless electric water heaters have almost no storage capacity and heat water as it flows once through the water heater. Heating rate required varies with water flow rate and needed temperature rise. Tankless electric water heaters for resi- dential applications are available in heating capacities from a low of about 1.5 kW to a high of about 60 kW. Smaller-capacity units (typically 12 kW or less, but this varies with geographic location and entering cold-water temperature) are sometimes used in lava- tory (sink) and other point-of-use applications such as remote low- use showers, small hot tubs, whirlpool baths, and other low-flow-rate applications. Larger sizes (above 18 kW) can sometimes be used in whole-house applications, depending on geographic location (and hence entering cold water temperature) and site hot-water use pro- files (see Table 15). Tankless water heaters can, if equipped with appropriate controls, be used in booster and/or recirculating water- heating systems. Note that not all models can be used to heat already partially warmed water: this capability varies among models. Heat pump water heaters (HPWHs) use a vapor-compression or sorption refrigeration cycle to extract energy from an air, ground, or water source to heat water. HPWHs may be designed as a single package with the refrigeration system and storage water tank as an integral system; or as the refrigeration system alone, sometimes referred to as an "add-on" water heater, which is connected to a sep- arately specified storage water tank, the size of which is generally dependent upon the application requirements. HPWHs can generate Inc. ASHRAE, 2019 user. single for Licensed | {}
63e5c29d-af62-4dfe-8178-998edba5e1cd | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 51.10 hot-water temperatures up to 60°C, with some models capable of outlet temperatures in the 82°C range. Where a higher delivery tem- perature is required than the HPWH can produce, a supplemental or booster water heater downstream of the storage tank should be used. HPWHs function most efficiently where inlet water temperature is low and the heat source temperature is warm. HPWHs frequently benefit from greater storage tank capacity than standard water heaters for the application because that enables the use of smaller HPWHs with lower first cost. The use of greater storage can also reduce conventional back-up energy use, though it may also increase space requirements. One of the most significant benefits of HPWHs is their ability to produce two to three times more heat output energy per unit of input energy than standard resistance and fossil-fueled water heaters. An air-source HPWH also provides potentially useful supplemental air cooling and dehumidification for occupants, and should be taken into account when defining the energy balance for the application. Cooling output should be directed to provide occupant comfort and avoid interfering with temperature-sensitive equipment (EPRI 1990). Demand-controlled water heating can significantly reduce the cost ofheating water electrically. Demand controllers operate on the principle that a building's peak electrical demand exists for a short period, during which heated water can be supplied from storage rather than through additional energy applications. Shifting the use of electricity for service water heating from peak demand periods allows water heating at the lowest electric energy cost in many elec- tric rate schedules. The building electrical load must be detected and compared with peak demand data. When the load is below peak, the control device allows the water heater to operate. Some controllers can program deferred loads in steps as capacity is available. The priority sequence may involve each of several banks of elements in (1) a water heater, (2) multiple water heaters, or (3) water-heating and other equipment having a deferrable load, such as pool heating and snow melting. When load controllers are used, hot-water stor- age must be sized appropriately. Electric off-peak storage water heating is a water-heating equipment load management strategy whereby electrical demand to a water-heating system is time-controlled, primarily in relation to the building or utility electrical load profile. This approach may require increased tank storage capacity and/or stored-water tem- perature to accommodate water use during peak periods. Inc. ASHRAE, 2019 user. single for Licensed Sizing recommendations in this chapter apply only to water heat- ing without demand or off-peak control. When demand control devices are used, the storage and recovery rate may need to be increased to supply all the hot water needed during the peak period and during the ensuing recovery period. Manian and Chackeris (1974) include a detailed discussion on load-limited storage heating system design. Indirect Water Heating In indirect water heating, the heating medium is steam, hot water, or another fluid that has been heated in a separate generator or boiler. The water heater extracts heat through an external or internal heat exchanger. When the heating medium is at a higher pressure than the service water, the service water may be contaminated by leakage of the heating medium through a damaged heat transfer surface. In the United States, some national, state, and local codes require double- wall, vented tubing in indirect water heaters to reduce the possibility of cross-contamination. When the heating medium is at a lower pressure than the service water, other jurisdictions allow single-wall tubing heaters because any leak would be into the heating medium. Ifthe heating medium is steam, high rates of condensation occur, particularly when a sudden demand causes an inflow of cold water. The steam pipe and condensate return pipes should be of ample size. 2019 ASHRAE Handbook-HVAC Applications (SI) Condensate may be cooled by preheating the cold-water supply to the heater. Corrosion is minimized on the heating medium side of the heat exchanger because no makeup water, and hence no oxygen, is brought into that system. The metal temperature of the service water side of the heat exchanger is usually less than that in direct-fired water heaters. This minimizes scale formation from hard water. Storage water heaters are designed for service conditions where hot-water requirements are not constant (i.e., where a large volume ofheated water is held in storage for periods of peak load). The amount of storage required depends on the load's nature and water heater's recovery capacity. An individual tank or several tanks joined by a manifold may be used to provide the required storage. External storage water heaters are designed for connection to a separate tank (Figure 9). Boiler water circulates through the heater shell, while service water from the storage tank circulates through the tubes and back to the tank. Circulating pumps are usually installed in both the boiler water piping circuit and the circuits between the heat exchanger and the storage tank. Steam can also be used as the heating medium in a similar scheme. Instantaneous indirect water heaters (tankless coils) are best used for a steady, continuous supply ofhot water. In these units, the water is heated as it flows through the tubes. Because the heating medium flows through a shell, the ratio of hot-water volume to heating medium volume is small. As a result, variable flow of the service water causes uncertain temperature control unless a thermo- static mixing valve is used to maintain the hot-water supply to the plumbing fixtures at a more uniform temperature. Some indirect instantaneous water heaters are located inside a boiler. The boiler is provided with a special opening through which the coil can be inserted. Although the coil can be placed in the steam space above the water line of a steam boiler, it is usually placed below the water line. The water heater transfers heat from the boiler water to the service water. The gross output of the boiler must be sufficient to serve all loads. Semi-Instantaneous These water heaters have limited storage to meet the average momentary surges of hot-water demand. They usually consist of a heating element and control assembly devised for close control of the temperature of the leaving hot water. Circulating Tank These water heaters are instantaneous or semi-instantaneous types used with a separate storage tank and a circulating pump. The ![image](/image/placeholder) TANK TEMPERATURE CONTROL ACCESS HOLE HOT-WATER OUTLET RELIEF VALVE AIR VENT THERMOMETER GATE VALVES HOT-WATER STORAGE EXTERNAL TANK STORAGE HEATER ※ 50 mm MIN. COLD- BLOWOFF WATER DRAIN INLET #### CIRCULATOR BOTH CIRCULATORS STEAM CONTROLLED BY BOILER DRAIN SAME TEMPERATURE PLUG CONTROL CIRCULATOR Fig. 9 Indirect, External Storage Water Heater | {}
9b2f7010-7a80-4c17-9e2d-cc3742805712 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Service Water Heating 51.11 storage acts as a flywheel to accommodate variations in the demand for hot water. Blending Injection These water heaters inject steam or hot water directly into the process or volume of water to be heated. They are often associated with point-of-use applications (e.g., certain types of commercial laundry, food, and process equipment). Caution: Cross contamina- tion of potable water is possible. Solar Availability of solar energy at the building site, efficiency and cost of solar collectors, system installation costs, and availability and cost of other fuels determine whether solar energy collection units should be used as a primary heat energy source. Solar energy equipment can also be included to supplement other energy sources and conserve fuel or electrical energy. The basic elements of a solar water heater include solar collec- tors, a storage tank, piping, controls, and a transfer medium. The system may use natural or forced circulation. Auxiliary heat energy sources may be added, if needed. Collector design must allow operation in below-freezing condi- tions, where applicable. Antifreeze solutions in a separate collector piping circuit arrangement are often used, as are systems that allow water to drain back to heated areas when low temperatures occur. Uniform flow distribution in the collector or bank of collectors and stratification in the storage tank are important for good system per- formance. Application of solar water heaters depends on (1) auxiliary energy requirements; (2) collector orientation; (3) temperature of the cold water; (4) general site, climatic, and solar conditions; (5) installation requirements; (6) area of collectors; and (7) amount of storage. Chapter 36 has more detailed design information. Wood Fired Water heaters are available that use wood, usually in chip or pellet form, as the fuel source. Waste Heat Use Waste heat recovery can reduce energy cost and the energy requirement of the building heating and service water-heating equipment. Waste heat can be recovered from equipment or pro- cesses by using appropriate heat exchangers in the hot gaseous or liquid streams. Heat recovered is frequently used to preheat water entering the service water heater. A conventional water heater is typically required to augment the output of a waste heat recovery device and to provide hot water during periods when the host system is not in operation. Refrigeration Heat Reclaim These systems heat water with heat that would otherwise be rejected through a refrigeration, air-conditioning, or heat pump con- denser. Refrigeration heat reclaim uses refrigerant-to-water heat exchangers connected to the refrigeration circuit between the com- pressor and condenser of a host refrigeration or air-conditioning system to extract heat. Water is heated only when the host is oper- ating. Because many simple systems reclaim only superheat energy from the refrigerant, they are often called desuperheaters. However, some units are also designed to provide partial or full condensing. The refrigeration heat reclaim heat exchanger is gen- erally of vented, double-wall construction to isolate potable water from refrigerant. Some heat reclaim devices are designed for use with multiple refrigerant circuits. Controls are required to limit high water temperature, prevent low condenser pressure, and pro- vide for freeze protection. Refrigeration systems with higher run time and lower efficiency provide more heat reclaim potential. Most systems are designed with a preheat water storage tank con- nected in series with a conventional water heater (EPRI 1992). In all installations, care must be taken to prevent inappropriately venting refrigerants. Combination Heating A combination system (combo or combi system) provides hot water for both space heating and domestic use. Most combi systems are one of two types. The first type consists of a water-heating source and a hydronic air handler with a space-heating coil. A space-cooling coil is often included with the air handler to provide year-round comfort. The second type consists of a hydronic space heater with a domestic hot-water loop. The domestic hot-water loop uses an integrated heat exchanger with or without an indirect storage tank. Combi systems can also be subdivided into segregated and nonsegregated systems. A segregated system keeps the potable hot water separate from the fluid used in the heat exchange circuit for space heating, through the installation of additional heat exchangers and pumps if required. A nonsegregated system uses potable hot water to serve both the space-heating circuit and domes- tic hot-water system. In nonsegregated systems, a means to prevent water stagnation is required; this often involves pumping the water around the circuit or flushing the circuit at regular intervals. The benefits of combi systems include (1) cost reductions through the use of one heat generator and one vent system, (2) space savings in most applications through having a packaged system delivering more than one function, and (3) efficiency benefits through the use of advanced controls in select systems that can opti- mize the combi system operation. A method of testing combi systems is given in ASHRAE Stan- dard 124. The test procedures allow the calculation of combined annual efficiency (CAE), as well as space- and water-heating effi- ciency factors. Kweller (1992), Pietsch and Talbert (1989), Pietsch et al. (1994), Subherwal (1986), and Talbert et al. (1992) provide additional design information on noncondensing combi systems. Butcher (2011), Schoenbauer et al. (2012), and Thomas (2011) pro- vide guidance for condensing combi systems. 8. BUILDING APPLICATIONS Service hot water may be used in various ways in residential, com- mercial, institutional, and industrial buildings. In some buildings, such as retail stores and office buildings, hot water is predominately used at lavatory sinks for hand washing and, to a lesser amount, at service sinks for floor-cleaning purposes. In other commercial and institutional buildings, hot-water use is process dominated for oper- ations such as commercial kitchens, laundry, and manufacturing, while hot-water use is minimal for hand washing. Residential facil- ities use hot water in their kitchen, bathroom, and laundry, and the usage is more balanced. The following section identifies some of the common types of facilities that use service hot water. Each facility type is characterized in terms of type of hot-water use, and metrics are provided for average and peak hot-water use. Dormitories. Hot-water requirements for college dormitories generally include showers, lavatories, service sinks, and clothes washers. Peak demand usually results from the use of showers. Load profiles and hourly consumption data indicate that peaks may last 1 or 2 h and then taper off substantially. Peaks occur predomi- nantly in the evening, mainly around midnight. The figures do not include hot water used for food service. Inc. ASHRAE, 2019 user. single for Licensed Military Barracks. Design criteria for military barracks are available from the engineering departments of the U.S. Department of Defense. Some measured data exist for hot-water use in these facilities. For published data, contact the U.S. Army Corps of Engi- neers or Naval Facilities Engineering Command. | {}
b59d70cc-c03d-403b-8218-0ee6d2e9af8c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 51.12 2019 ASHRAE Handbook-HVAC Applications (SI) Motels. Domestic hot-water requirements are for tubs and show- ers, lavatories, and general cleaning purposes. Recommendations are based on tests at low- and high-rise motels located in urban, sub- urban, rural, highway, and resort areas. Peak demand, usually from shower use, may last 1 or 2 h and then drop off sharply. Food ser- vice, laundry, and swimming pool requirements are not included. Nursing Homes. Hot water is required for tubs and showers, wash basins, service sinks, kitchen equipment, and general cleaning. These figures include hot water for kitchen use. When other equipment, such as that for heavy laundry and hydrotherapy purposes, is to be used, its hot-water requirement should be added. Office Buildings. Hot-water requirements are primarily for cleaning and lavatory use by occupants and visitors. Older office buildings often use hot-water recirculation-loop systems and are thus good candidates for water-heating distribution system effi- ciency upgrades through more modern controls and/or addition of point-of-use water heaters. Hot-water use for food service in office buildings is not included. Food Service Facility. Commercial kitchens can be separated into five major stand-alone food service facility types: coffee/ specialty, bar/tavern, deli/sandwich, quick-service restaurant, and full-service restaurant. Commercial kitchens are found in eight major facility types, including nursing/residential care, K-12 schools, supermarkets, office buildings, hotels/casinos with kitchens, hospitals, colleges/universities, and correctional facilities. The three largest segments are coffee/specialty shops, quick-service restaurants and full-service restaurants, together roughly account- ing for 75% of all commercial kitchens. Hot-water use intensity in facilities can be distinguished by types of wares used in the dining room. Many smaller facilities, such as coffee shops, sandwich shops, and quick-service restaurants, use disposable wares (e.g., plates, cups), and therefore have much lower use intensity, whereas larger facilities, such as full-service restaurants and cafeterias, use reusable wares and utensils. Hot water is used primarily for ware washing (e.g., dishes, cups, cutting boards). Other uses include food preparation, floor and equipment cleaning, and hand washing. Apartments. Hot-water requirements for both garden-type and high-rise apartments are for one- and two-bath apartments, for showers, lavatories, kitchen sinks, dishwashers, clothes washers, and general cleaning purposes. Clothes washers can be either in individual apartments or centrally located. These data apply to cen- tral water-heating systems only. Elementary Schools. Hot-water requirements are for lavatories, cafeteria and kitchen use, and general cleaning purposes. When showers are used, their additional hot-water requirements should be added. Recommendations include hot water for dishwashers but not for extended school operation such as evening classes. High Schools. Senior high schools, grades 9 or 10 to 12, require hot water for showers, lavatories, dishwashers, kitchens, and gen- eral cleaning. Junior high schools, grades 7 to 8 or 9, have require- ments similar to those of senior high schools. Junior high schools without showers follow the recommendations for elementary schools. Requirements for high schools are based on daytime use. Rec- ommendations do not take into account hot-water use for additional activities, such as night school. In such cases, the maximum hourly demand remains the same, but the maximum and average daily use increase, usually by the number of additional people using showers and, to a lesser extent, eating and washing facilities. An important consideration in design of water heating and hot water distribution systems in K-12 schools is that schools have low average occupancy levels. Because of holidays, weekends, and other non-use periods (e.g. night), most K-12 schools are unoccu- pied approximately 75% of all hours of the entire year. This makes use of recirculation loops (RL) range from less desirable to highly undesirable from both energy use and first-cost perspectives in such applications. K-12 schools often both use less energy and have lower first cost if loads are served by multiple smaller water heaters located near end uses, eliminating the need for recirculation loops (Hiller 2002, 2005c; Hiller et al. 2002, 2004). 9. HOT-W ATER LOAD AND EQUIPMENT SIZING Methods for sizing storage water heaters vary. Those using recovery versus storage curves are based on extensive research. All methods provide adequate hot water ifthe designer allows for unusual conditions. To serve a hot-water load adequately, the needs ofboth the peak energy withdrawal rate and total integrated energy delivery for end uses must be met. Meeting these needs can be done either by pro- viding a heating rate large enough to meet the peak energy withdrawal rate of the system (and modulating that heating input for smaller loads), or by providing a lower heating rate combined with storage (from which the peak rates can be satisfied). Lower costs are usually achieved by using at least some storage. A variety of different heating rate/storage volume combinations can be used to meet the needs of a given water-heating load profile (Hiller 1998). Load Diversity The greatest difficulty in designing water-heating systems comes from uncertainty about design hot-water loads, especially for buildings not yet built. Although it is fairly simple to test max- imum flow rates of various hot-water fixtures and appliances, actual flow rates and durations are user-dependent. Moreover, the timing of different hot-water use events varies from day to day, with some overlap, but almost never will all fixtures be used simultaneously. As the number of hot-water-using fixtures and appliances grows, the percent of those fixtures used simultane- ously decreases. Some of the hot-water load information in this chapter is based on limited-scale field testing combined with statistical analysis to estimate load demand or diversity factors (percent of total possible load that is ever actually used at one time) versus number of end use points, number of people, etc. Much of the work to provide these diversity factors dates from the 1930s to the 1960s and is therefore outdated; it remains, however, the best information currently avail- able (with a few exceptions, as noted). Of greatest concern is the fact that most of the data from those early studies were for fixtures that used water at much higher flow rates than modern energy-efficient fixtures (e.g., low-flow shower heads and sink aerators, energy- efficient washing machines and dishwashers). Some research has provided limited information on hot-water use by more modern fix- tures, and on their use diversity (Becker et al. 1991; Goldner 1994a, 1994b; Goldner and Price 1999; Hiller 1998; Hiller and Johnson 2015; Hiller and Lowenstein 1996, 1998; Thrasher and De W erth 1994), but much more information in a variety of applications is needed before the design procedures can be updated. Using the older load diversity information usually results in a water-heating system that adequately serves the loads, but often results in substan- tial oversizing. Oversizing can be a deterrent to using modern high- efficiency water-heating equipment, which may have higher first cost per unit of capacity than less efficient equipment. Sustainable design must consider these effects. Residential Table 3 shows typical hot-water usage in a residence, including usage rates of modern ultralow-use appliances and fixtures. It is more difficult to show typical values for newer devices, because some auto- matically adjust the amount of hot water they use based on sensed load or cycle setting. In its Minimum Property Standardsfor Housing, the U.S. Department of Housing and Urban Development (HUD 1994) established minimum permissible water heater sizes (Table 4). Storage water heaters may vary from the sizes shown if combinations ofrecovery and storage are used that produce the required 1 h draw. Inc. ASHRAE, 2019 user. single for Licensed | {}
13739aad-6145-4b08-81f5-baaa4eefacd4 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Service Water Heating 51.13 X-Axis: TANK SIZE, L Y-Axis: FIRST-HOUR RATING, L Chart Type: line 75 95 115 135 155 175 195 215 235 255 275 item_01 123.5L 133.5L 143.5L 151.5L 188.5L 222.5L 224.5L 325L 355L 365L 425L Fig. 10 First-Hour Rating (FHR) Relationships for Residential w ater Heaters Table 3 Typical Residential Use of Hot Water ¦ Use ¦ High Flow, Litres/Task ¦ Low Flow (Water Savers Used), Litres/Task ¦ Ultralow Flow, Litres/ Task ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Food preparation ¦ 19 ¦ 11 ¦ 11 ¦ ¦ Hand dish washing ¦ 15 ¦ 15 ¦ 11 ¦ ¦ Automatic dishwasher ¦ 57 ¦ 57 ¦ 11 to 38 ¦ ¦ Clothes washer ¦ 121 ¦ 80 ¦ 19 to 57 ¦ ¦ Shower or bath ¦ 76 ¦ 57 ¦ 38 to 57 ¦ ¦ Face and hand washing ¦ 15 ¦ 8 ¦ 4 to 8 ¦ The first-hour rating (FHR) is a measure of the maximum amount of hot water that a water heater can supply in 1 h of opera- tion when started from operational temperature under specific test conditions (DOE 2014). The linear regression lines shown in Figure 10 represent the FHR for 45 electric heaters (both resistance and heat pump) and 150 gas heaters (DOE 2017). Regression lines are not included for oil-fired heaters because of limited data. The FHR represents water-heater performance characteristics that are similar to those represented by the 1 h draw values listed in Table 4. Resi- dential water-heating equipment sizing is frequently driven by amounts of water used over periods of considerably less than 1 h, often as short as 15 minutes (Hiller 1998). Over these short periods, storage tank volume is a better indicator ofhot-water delivery capa- bility than FHR for residential applications. Water heater FHRs changed (generally become lower) because of changes in the DOE test and rating conditions that went into effect in 2015. Another factor to consider when sizing water heaters is the set- point temperature. At lower storage tank water temperatures, the tank volume and/or energy input rate may need to be increased to meet a given hot-water demand. Currently, manufacturers ship res- idential water heaters with a recommendation that the initial set point be approximately 50°C to minimize the potential for scalding. Reduced set points generally lower standby losses and increase the water heater' s efficiency and recovery capacity, but may also reduce the amount of hot water available. The structure and lifestyle of a typical family (variations in family size, age of family members, presence and age of children, hot-water use volume and temperature, and other factors) cause Chart Type: bar HOUR 1 HOUR 2 HOUR 3 HOUR 4 HOUR 5 HOUR 6 HOUR 7 HOUR 8 HOUR 9 HOUR 10 HOUR 11 HOUR 12 HOUR 13 HOUR 14 HOUR 15 HOUR 16 HOUR 17 HOUR 18 HOUR 19 HOUR 20 HOUR 21 HOUR 22 HOUR 23 HOUR 24 item_01 2Hours 1Hours 1Hours 1Hours 1Hours 1Hours 1Hours 2Hours 3Hours 7Hours 10Hours 12Hours 13Hours 14Hours 15Hours 16Hours 17Hours 18Hours 19Hours 20Hours 21Hours 22Hours 23Hours 24Hours Fig. 11 Residential Average Hourly Hot- w ater Use V USE, HOURLY Chart Type: bar HOUR 1 HOUR 2 HOUR 3 HOUR 4 HOUR 5 HOUR 6 HOUR 7 HOUR 8 HOUR 9 HOUR 10 HOUR 11 HOUR 12 HOUR 13 HOUR 14 HOUR 15 HOUR 16 HOUR 17 HOUR 18 HOUR 19 HOUR 20 HOUR 21 HOUR 22 HOUR 23 HOUR 24 item_01 10 15 5 5 5 10 15 35 30 25 20 15 10 15 20 25 20 25 30 35 30 25 20 25 Fig. 12 Residential Hourly Hot-Water Use, 95% Confidence Level hot-water consumption demand patterns to fluctuate widely in both magnitude and time distribution. Perlman and Mills (1985) developed the overall and peak average hot-water use volumes shown in Table 5. Average hourly patterns and 95% confidence level profiles are shown in Figures 11 and 12. Samples of results from the analysis of similarities in hot- water use are given in Figures 13 and 14. Commercial and Institutional Most commercial and institutional establishments use hot or warm water. The specific requirements vary in total volume, flow rate, duration of peak load period, and temperature. Water heaters and systems should be selected based on these requirements. This section covers sizing recommendations for central storage water-heating systems. Hot-water usage data and sizing curves for dormitories, motels, nursing homes, office buildings, food service establishments, apartments, and schools are based on EEI-sponsored research (Werden and Spielvogel 1969a, 1969b). Caution must be taken in applying these data to small buildings. Also, within any given category there may be significant variation. For example, the motel category encompasses standard, luxury, resort, and conven- tion motels. Inc. ASHRAE, 2019 user. single for Licensed | {}
c8d9d7db-7dfd-42c9-8aef-a48a5b152f53 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 51.14 2019 ASHRAE Handbook-HVAC Applications (SI) Table 4 HUD-FHA Minimum Water Heater Capacities for One- and Two-Family Living Units ¦ Number of Baths ¦ 1 to 1.5 ¦ 1 to 1.5 ¦ 1 to 1.5 ¦ 2 to 2.5 ¦ 2 to 2.5 ¦ 2 to 2.5 ¦ 2 to 2.5 ¦ 3 to 3.5 ¦ 3 to 3.5 ¦ 3 to 3.5 ¦ 3 to 3.5 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Number of Bedrooms ¦ 1 ¦ 2 ¦ 3 ¦ 2 ¦ 3 ¦ 4 ¦ 5 ¦ 3 ¦ 4 ¦ 5 ¦ 6 ¦ ¦ Gasa ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Storage, L ¦ 76 ¦ 114 ¦ 114 ¦ 114 ¦ 150 ¦ 150 ¦ 190 ¦ 150 ¦ 190 ¦ 190 ¦ 190 ¦ ¦ kW input ¦ 7.9 ¦ 10.5 ¦ 10.5 ¦ 10.5 ¦ 10.5 ¦ 11.1 ¦ 13.8 ¦ 11.1 ¦ 11.1 ¦ 13.8 ¦ 14.6 ¦ ¦ 1 h draw, L ¦ 163 ¦ 227 ¦ 227 ¦ 227 ¦ 265 ¦ 273 ¦ 341 ¦ 273 ¦ 311 ¦ 341 ¦ 350 ¦ ¦ Recovery, mL/s ¦ 24 ¦ 32 ¦ 32 ¦ 32 ¦ 32 ¦ 36 ¦ 42 ¦ 34 ¦ 34 ¦ 42 ¦ 44 ¦ ¦ Electrica ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Storage, L ¦ 76 ¦ 114 ¦ 150 ¦ 150 ¦ 190 ¦ 190 ¦ 250 ¦ 190 ¦ 250 ¦ 250 ¦ 300 ¦ ¦ kW input ¦ 2.5 ¦ 3.5 ¦ 4.5 ¦ 4.5 ¦ 5.5 ¦ 5.5 ¦ 5.5 ¦ 5.5 ¦ 5.5 ¦ 5.5 ¦ 5.5 ¦ ¦ 1 h draw, L ¦ 114 ¦ 167 ¦ 220 ¦ 220 ¦ 273 ¦ 273 ¦ 334 ¦ 273 ¦ 334 ¦ 334 ¦ 387 ¦ ¦ Recovery, mL/s ¦ 10 ¦ 15 ¦ 19 ¦ 19 ¦ 23 ¦ 23 ¦ 23 ¦ 23 ¦ 23 ¦ 23 ¦ 23 ¦ ¦ Oila ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Storage, L ¦ 114 ¦ 114 ¦ 114 ¦ 114 ¦ 114 ¦ 114 ¦ 114 ¦ 114 ¦ 114 ¦ 114 ¦ 114 ¦ ¦ kW input ¦ 20.5 ¦ 20.5 ¦ 20.5 ¦ 20.5 ¦ 20.5 ¦ 20.5 ¦ 20.5 ¦ 20.5 ¦ 20.5 ¦ 20.5 ¦ 20.5 ¦ ¦ 1 h draw, L ¦ 337 ¦ 337 ¦ 337 ¦ 337 ¦ 337 ¦ 337 ¦ 337 ¦ 337 ¦ 337 ¦ 337 ¦ 337 ¦ ¦ Recovery, mL/s ¦ 62 ¦ 62 ¦ 62 ¦ 62 ¦ 62 ¦ 62 ¦ 62 ¦ 62 ¦ 62 ¦ 62 ¦ 62 ¦ ¦ Tank-type indirect b,c ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ I-W-H-rated draw, L in 3 h, 55 K rise ¦ ¦ 150 ¦ 150 ¦ ¦ 250 ¦ 250e ¦ 250 ¦ 250 ¦ 250 ¦ 250 ¦ 250 ¦ ¦ Manufacturer-rated draw, L in 3 h, 55 K rise ¦ ¦ 186 ¦ 186 ¦ ¦ 284 ¦ 284e ¦ 284 ¦ 284 ¦ 284 ¦ 284 ¦ 284 ¦ ¦ Tank capacity, L ¦ ¦ 250 ¦ 250 ¦ ¦ 250 ¦ 250e ¦ 310 ¦ 250 ¦ 310 ¦ 310 ¦ 310 ¦ ¦ Tankless-type indirect C,d ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ I-W-H-rated draw, mL/s, 55 K rise ¦ ¦ 170 ¦ 170 ¦ ¦ 200 ¦ 200e ¦ 240 ¦ 200 ¦ 240 ¦ 240 ¦ 240 ¦ ¦ Manufacturer-rated draw, L in 5 min, 55 K rise ¦ ¦ 57 ¦ 57 ¦ ¦ 95 ¦ 95e ¦ 133 ¦ 95 ¦ 133 ¦ 133 ¦ 133 ¦ ¦ Note: Applies to tank-type water heaters only CHeater capacities and inputs are minimum allowable. Variations in tank size are per- aStorage capacity, input, and recovery requirements indicated are typical and may mitted when recovery is based on 4.2 mL/(s·kW) at 55 K rise for electrical, AGA vary with manufacturer. Any combination of requirements to produce stated 1 h recovery ratings for gas, and IBR ratings for steam and hot-water heaters. draw is satisfactory. dBoiler-connected heater capacities (93 °C boiler water, internal or external connec- ¦ Note: Applies to tank-type water heaters only CHeater capacities and inputs are minimum allowable. Variations in tank size are per- aStorage capacity, input, and recovery requirements indicated are typical and may mitted when recovery is based on 4.2 mL/(s·kW) at 55 K rise for electrical, AGA vary with manufacturer. Any combination of requirements to produce stated 1 h recovery ratings for gas, and IBR ratings for steam and hot-water heaters. draw is satisfactory. dBoiler-connected heater capacities (93 °C boiler water, internal or external connec- ¦ Note: Applies to tank-type water heaters only CHeater capacities and inputs are minimum allowable. Variations in tank size are per- aStorage capacity, input, and recovery requirements indicated are typical and may mitted when recovery is based on 4.2 mL/(s·kW) at 55 K rise for electrical, AGA vary with manufacturer. Any combination of requirements to produce stated 1 h recovery ratings for gas, and IBR ratings for steam and hot-water heaters. draw is satisfactory. dBoiler-connected heater capacities (93 °C boiler water, internal or external connec- ¦ Note: Applies to tank-type water heaters only CHeater capacities and inputs are minimum allowable. Variations in tank size are per- aStorage capacity, input, and recovery requirements indicated are typical and may mitted when recovery is based on 4.2 mL/(s·kW) at 55 K rise for electrical, AGA vary with manufacturer. Any combination of requirements to produce stated 1 h recovery ratings for gas, and IBR ratings for steam and hot-water heaters. draw is satisfactory. dBoiler-connected heater capacities (93 °C boiler water, internal or external connec- ¦ Note: Applies to tank-type water heaters only CHeater capacities and inputs are minimum allowable. Variations in tank size are per- aStorage capacity, input, and recovery requirements indicated are typical and may mitted when recovery is based on 4.2 mL/(s·kW) at 55 K rise for electrical, AGA vary with manufacturer. Any combination of requirements to produce stated 1 h recovery ratings for gas, and IBR ratings for steam and hot-water heaters. draw is satisfactory. dBoiler-connected heater capacities (93 °C boiler water, internal or external connec- ¦ Note: Applies to tank-type water heaters only CHeater capacities and inputs are minimum allowable. Variations in tank size are per- aStorage capacity, input, and recovery requirements indicated are typical and may mitted when recovery is based on 4.2 mL/(s·kW) at 55 K rise for electrical, AGA vary with manufacturer. Any combination of requirements to produce stated 1 h recovery ratings for gas, and IBR ratings for steam and hot-water heaters. draw is satisfactory. dBoiler-connected heater capacities (93 °C boiler water, internal or external connec- ¦ Note: Applies to tank-type water heaters only CHeater capacities and inputs are minimum allowable. Variations in tank size are per- aStorage capacity, input, and recovery requirements indicated are typical and may mitted when recovery is based on 4.2 mL/(s·kW) at 55 K rise for electrical, AGA vary with manufacturer. Any combination of requirements to produce stated 1 h recovery ratings for gas, and IBR ratings for steam and hot-water heaters. draw is satisfactory. dBoiler-connected heater capacities (93 °C boiler water, internal or external connec- ¦ Note: Applies to tank-type water heaters only CHeater capacities and inputs are minimum allowable. Variations in tank size are per- aStorage capacity, input, and recovery requirements indicated are typical and may mitted when recovery is based on 4.2 mL/(s·kW) at 55 K rise for electrical, AGA vary with manufacturer. Any combination of requirements to produce stated 1 h recovery ratings for gas, and IBR ratings for steam and hot-water heaters. draw is satisfactory. dBoiler-connected heater capacities (93 °C boiler water, internal or external connec- ¦ Note: Applies to tank-type water heaters only CHeater capacities and inputs are minimum allowable. Variations in tank size are per- aStorage capacity, input, and recovery requirements indicated are typical and may mitted when recovery is based on 4.2 mL/(s·kW) at 55 K rise for electrical, AGA vary with manufacturer. Any combination of requirements to produce stated 1 h recovery ratings for gas, and IBR ratings for steam and hot-water heaters. draw is satisfactory. dBoiler-connected heater capacities (93 °C boiler water, internal or external connec- ¦ Note: Applies to tank-type water heaters only CHeater capacities and inputs are minimum allowable. Variations in tank size are per- aStorage capacity, input, and recovery requirements indicated are typical and may mitted when recovery is based on 4.2 mL/(s·kW) at 55 K rise for electrical, AGA vary with manufacturer. Any combination of requirements to produce stated 1 h recovery ratings for gas, and IBR ratings for steam and hot-water heaters. draw is satisfactory. dBoiler-connected heater capacities (93 °C boiler water, internal or external connec- ¦ Note: Applies to tank-type water heaters only CHeater capacities and inputs are minimum allowable. Variations in tank size are per- aStorage capacity, input, and recovery requirements indicated are typical and may mitted when recovery is based on 4.2 mL/(s·kW) at 55 K rise for electrical, AGA vary with manufacturer. Any combination of requirements to produce stated 1 h recovery ratings for gas, and IBR ratings for steam and hot-water heaters. draw is satisfactory. dBoiler-connected heater capacities (93 °C boiler water, internal or external connec- ¦ Note: Applies to tank-type water heaters only CHeater capacities and inputs are minimum allowable. Variations in tank size are per- aStorage capacity, input, and recovery requirements indicated are typical and may mitted when recovery is based on 4.2 mL/(s·kW) at 55 K rise for electrical, AGA vary with manufacturer. Any combination of requirements to produce stated 1 h recovery ratings for gas, and IBR ratings for steam and hot-water heaters. draw is satisfactory. dBoiler-connected heater capacities (93 °C boiler water, internal or external connec- ¦ bBoiler-connected water heater capacities (82°C boiler water, internal or external tion). connection). cAlso for 1 to 1.5 baths and 4 bedrooms for indirect water heaters. Table 5 Overall (OVL) and Peak Average Hot-Water Use Average Hot-Water Use, L ¦ ¦ Hourly ¦ Hourly ¦ Daily ¦ Daily ¦ Weekly ¦ Weekly ¦ Monthly ¦ Monthly ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Group ¦ OVL ¦ Peak ¦ OVL ¦ Peak ¦ OVL ¦ Peak ¦ OVL ¦ Peak ¦ ¦ All families ¦ 9.8 ¦ 17.3 ¦ 236 ¦ 254 ¦ 1652 ¦ 1873 ¦ 7178 ¦ 7700 ¦ ¦ "Typical" families ¦ 9.9 ¦ 21.9 ¦ 239 ¦ 252 ¦ 1673 ¦ 1981 ¦ 7270 ¦ 7866 ¦ Chart Type: bar 1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 21 22 23 24 item_01 1% 0% 0% 0% 0% 0% 0% 1% 2% 4% 6% 12% 14% 12% 8% 6% 4% 2% 2% 8% 4% 2% 2% 4% Fig. 13 Residential Hourly Hot-Water Use Pattern for Selected High Morning and High Evening Users When additional hot-water requirements exist, increase the recovery and/or storage capacity accordingly. For example, if there is food service in an office building, the recovery and storage capac- ities required for each additional hot-water use should be added when sizing a single central water-heating system. Chart Type: bar 1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 16 17 18 19 20 21 22 23 24 item_01 5Hours 3Hours 2Hours 1Hours 1Hours 1Hours 10Hours 15Hours 25Hours 30Hours 20Hours 15Hours 10Hours 10Hours 15Hours 20Hours 25Hours 30Hours 35Hours 25Hours 20Hours 15Hours 10Hours 10Hours Fig. 14 Residential Average Hourly Hot-Water Use Patterns for Low and High Users Peak hourly and daily demands for various categories of commer- cial and institutional buildings are shown in Table 6. These demands for central-storage hot water represent the maximum flows metered in this 129-building study, excluding extremely high and very infre- quent peaks. Table 6 also shows average hot-water consumption fig- ures for these buildings. Averages for schools and food service establishments are based on actual days of operation; all others are based on total days. These averages can be used to estimate monthly consumption of hot water, but are not intended for sizing purposes because they do not show the time distribution of draws. Research conducted for ASHRAE (Becker et al. 1991; Thrasher and DeWerth 1994) and others (Goldner 1994a, 1994b) included a compilation and review of service hot-water use information in Inc. ASHRAE, 2019 user. single for Licensed | {}
0c2682c1-a2e3-43b6-a8c0-009e5264f1b5 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Service Water Heating 51.15 Table 6 Hot- Water Demands and Use for Various Types of Buildings* ¦ Type of Building ¦ Maximum Hourly ¦ Maximum Daily ¦ Average Daily ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Men's dormitories ¦ 14.4 L/student ¦ 83.3 L/student 100 L/student ¦ 49.7 L/student 46.6 L/student ¦ ¦ Women's dormitories Motels: Number of unitsa ¦ 19 L/student ¦ ¦ ¦ ¦ 20 or less 60 100 or more ¦ 23 L/unit 20 L/unit 15 L/unit ¦ 132.6 L/unit 94.8 L/unit 56.8 L/unit ¦ 75.8 L/unit 53.1 L/unit L/unit ¦ ¦ Nursing homes ¦ 17 L/bed ¦ 114 L/bed ¦ 37.9 69.7 L/bed ¦ ¦ Food service establishments: Type A: Full-meal restaurants and cafeterias Type B: Drive-ins, grills, luncheonettes, sandwich and snack shops ¦ ¦ 7.6 L/person 41.7 L/max meals/day ¦ 3.8 L/person ¦ ¦ Apartment houses: Number of apartments ¦ L/max meals/h 2.6 L/max meals/h ¦ 22.7 L/max meals/day ¦ 9.1 L/average meals/dayb 2.6 L/average meals/dayb ¦ ¦ ¦ ¦ ¦ ¦ ¦ Office buildings 20 or less ¦ 1.5 L/person 5.7 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 303.2 L/apartment ¦ 159.2 L/apartment ¦ ¦ ¦ 45.5 L/apartment 37.9 L/apartment 32.2 L/apartment ¦ 276.7 L/apartment 250 L/apartment ¦ 151.6 L/apartment 144 L/apartment ¦ ¦ ¦ 26.5 L/apartment 19 L/apartment ¦ 227.4 L/apartment 195 L/apartment ¦ 140.2 L/apartment 132.7 L/apartment ¦ ¦ 50 75 100 200 or more ¦ ¦ ¦ ¦ ¦ Elementary schools ¦ 2.3 L/student ¦ ¦ ¦ ¦ Junior and senior high schools ¦ 3.8 L/student ¦ 5.7 L/student 13.6 L/student ¦ 2.3 L/studentb 6.8 L/studentb ¦ *Data predate modern low-flow fixtures and appliances. commercial and multifamily structures along with new monitoring data. Some of this work found consumption comparable to those shown in Table 6; however, many of the studies showed higher consumption. Additional Data. Fast Food Restaurants. Hot water is used for food preparation, cleanup, and rest rooms. Dish washing is usually not a significant load. In most facilities, peak usage occurs during the cleanup period, typically soon after opening and immediately before closing. Hot-water consumption varies significantly among individ- ual facilities. Fast food restaurants typically consume 1000 to 2000 L per day (EPRI 1994). Supermarkets. The trend in supermarket design is to incorporate food preparation and food service functions, substantially increasing the usage of hot water. Peak usage is usually associated with cleanup periods, often at night, with a total consumption of 1100 to 3800 L per day (EPRI 1994). Apartments. Table 7 shows cumulative hot-water use over time for apartment buildings, taken from a series of field tests by Becker et al. (1991), Goldner (1994a, 1994b), Goldner and Price (1999), and Thrasher and DeWerth (1994). These data include use diversity information, and enable use of modern water-heating equipment sizing methods for this building type, making it easy to understand the variety ofheating rate and storage volume combinations that can serve a given load profile (see Example 1). Unlike Table 6, Table 7 presents low/medium/high (LMH) guidelines rather than specific singular volumes, and gives better time resolution of peak hot-water use information. The same information is shown graphically in Fig- ure 15. Note that these studies showed that occupants on average use more hot water when water-heating costs are included in the rent, than if the occupants pay directly for water-heating energy use. The low-use peak hot-water consumption profile represents the lowest peak profile seen in the tests, and is generally associated with apartment buildings having mostly a mix of the following occupant demographics: · All occupants working · One person working, while one stays at home · Seniors · Couples · Middle income aInterpolate for intermediate values. bPer day of operation. Table 7 Hot-Water Demand and Use Guidelines for Apartment Buildings (Litres per Person at 49°C Delivered to Fixtures) ¦ Guideline ¦ Peak Minutes ¦ Peak Minutes ¦ Peak Minutes ¦ Peak Minutes ¦ Peak Minutes ¦ Peak Minutes ¦ Maximum Daily ¦ Average Daily ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Guideline ¦ 5 ¦ 15 ¦ 30 ¦ 60 ¦ 120 ¦ 180 ¦ Maximum Daily ¦ Average Daily ¦ ¦ Low ¦ 1.5 ¦ 3.8 ¦ 6.4 ¦ 10.6 ¦ 17.0 ¦ 23.1 ¦ 76 ¦ 53 ¦ ¦ Medium ¦ 2.6 ¦ 6.4 ¦ 11.0 ¦ 18.2 ¦ 30.3 ¦ 41.6 ¦ 185 ¦ 114 ¦ ¦ High ¦ 4.5 ¦ 11.4 ¦ 19.3 ¦ 32.2 ¦ 54.9 ¦ 71.9 ¦ 340 ¦ 204 ¦ · Higher population density The medium-use peak hot-water consumption profile represents the overall average highest peak profile seen in the tests, and is gen- erally associated with apartment buildings having mostly a mix of the following occupant demographics: · Families · Singles · On public assistance · Single-parent households The high-use peak hot-water consumption profile represents the highest peak profile seen in the tests, and is generally associated with apartment buildings having mostly a mix of the following occupant demographics: · High percentage of children · Low income · On public assistance · No occupants working · Families · Single-parent households In applying these guidelines, the designer should note that a building may outlast its current use. This may be a reason to increase the design capacity for domestic hot water or allow space and connections for future enhancement of the service hot-water system. Building management practices, such as the explicit prohi- bition (in the lease) of apartment clothes washers or the existence of bath/kitchen hook-ups, should be factored into the design process. Inc. ASHRAE, 2019 user. single for Licensed | {}
f2774bb9-0d4c-4da4-a997-5f33dd9687b7 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 51.16 2019 ASHRAE Handbook-HVAC Applications (SI) Chart Title: HIGH-USE OCCUPANT DEMOGRAPHICS X-Axis: TIME, h Y-Axis: L/person, CUMULATIVE Chart Type: line Low Medium High-USE OCCUPANT DEMOGRAPHICS item_01 20No units specified 200No units specified 350No units specified Fig. 15 Apartment Building Cumulative Hot- Water Use Versus Time (from Table 7) A diversity factor that lowers the probability of coincident con- sumption should also be used in larger buildings. Inc. ASHRAE, 2019 user. single for Licensed The information in Table 7 and Figure 15 generates a water- heating equipment sizing method for apartment buildings. The cumulative total hot-water consumption versus time (which includes all necessary load diversity information) can be used to select a range of heating rate and storage volume options, all of which will satisfy the load. The key is that plots of cumulative total hot-water consumption versus time as shown in Figure 15 also rep- resent, by the slope of a line drawn from zero time through the cumulative volume used at any given time, the average hot-water flow rate up to that point in time. Up to any point in time, the min- imum average heating rate needed to satisfy the load is one that can heat the average hot-water flow rate through that time from the local entering cold-water temperature to the water-heating system delivery temperature. (More accurately, the heating rate needed is determined by the local slope of the hot-water use versus time curve, not the average slope. This is because storage can supply the hot water supplied up to a selected time, and the heating rate only needs to provide the additional energy after storage is depleted. Eventually, however, storage needs to be reheated, which must also be considered. See the two methods shown in Example 1.) The stor- age volume needed for that heating rate is the total cumulative flow through that time (Hiller 1998). To evaluate the range of minimum required heating rates and their corresponding minimum required storage tank volumes, it is easiest to pick various volumes in Figure 15 or Table 7, then determine the heating rate and time period that correspond to them, as shown in Example 1. Final selection of water-heating system heating rate and storage size is then made by examining the first and operating costs of the various combina- tions. Hotels. Hotel hot water uses tend to be grouped into three major categories: (1) guest room circuit, (2) laundry circuit, and (3) food service/commercial kitchen circuit. Guest room circuits tend to have the following hot water loads: (1) guest showers and baths, (2) guest room sink use, (3) guest room cleaning, and (4) common area cleaning. Bathing (showers and baths) is the largest single hotel hot- water use category, often exceeding all other hot-water uses com- bined. Research results from Hiller and Johnson (2015, 2016a, 2016b, 2016c, 2017a, 2017b) present findings on a study of a large conference hotel and a roadside travel hotel. The work provides guidance on sizing of the water heating system, including storage volumes and heating rates of water heaters, based on these two studies. ASHRAE members can obtain copies of RP-1544 reports at no cost via the ASHRAE Technology Portal (technologyportal .ashrae.org). Sizing Examples Example 1. Evaluate the range of water-heating system heating-rate and storage volume combinations that can serve a 58-unit apartment building occupied by a mix of families, singles, and middle-income couples in which most adults work. The peak expected number of building occupants is 198, based on the assortment of apartment sizes in the building. Assume a water-heating system delivery temperature of 50°C, design entering cold-water temperature of 4°C, and heating device thermal efficiency of 80%. Simplified Method. Solution: The stated occupant demographics represent a medium load. Multiplying the volume per person versus time from the medium values in Table 7 by the number of occupants gives the cumulative amount needed at any point in time and the average flow rate (and hence heat- ing rate) required through that time. At 5 min, the peak design cumulative volume is (2.6 L/person) x (198 people) = 515 L. The average flow rate over 5 min is (515 L)/(5 min)/(60 s/min) = 1.7 L/s. The required heating rate is thus, from Equation (1) and dividing by the input efficiency, 9 = (1.7 L/s)(1 kg/L)[4.1868 kJ/(kg · K) x (50 - 4°C)/0.8 = 409 kW Assuming 70% of the storage tank volume can be extracted at a useful temperature (the other 30% being degraded by mixing in the tank), the required tank volume for this heating rate is V = 515 L/0.7 = 736 L Note that, because the heating rate divided by storage capacity (555 W/L) exceeds 300 W/L, this system is considered an instantaneous water heater. At 60 min, 18.2 L/person)(198 people) = 3604 L. Average flow rate = (3604 L/60 min)/(60 s/min) = 1 L/s. 9 - (1 L/s)(1 kg/L)[4.1868 kJ/(kg· K) x (50 - 4°C)/0.8 = 240 kW V= 3604 L/0.7 = 5149 L Doing these calculations at other volumes and times yields the com- binations of heating rate and storage volume that can serve the load (Table 8). More Accurate Method. The preceding simplified method calculates the needed heating rate by computing the average water flow rate from the beginning of all draws for the day. In reality, because some storage is present, the water- heating device only needs to provide a heating rate computed from the local slope of the hot-water use curve, not the average slope. In other words for example, the flow over the first 5 min could have been pro- vided entirely from storage without any heat input at all. The water heater only needs to heat in real time the amount of hot water needed over succeeding time periods. Consequently, the simplified heating rate computational method works, but results in some degree of heating rate oversizing. Solution: Using the more accurate heating rate sizing method is similar to using the simplified method, except the local slope of the hot-water use curve versus time must be found at each time interval to determine the necessary heating rate. At 5 min, the peak design cumulative volume (Table 8) is 515 L. At 15 min, the peak design cumulative volume (Table 8) is 1267 L. The incremental flow rate (representing the local slope of the hot water use line) is hence (1267 - 515 L)/600 s =1.25 L/s. The needed heating rate is thus more accurately computed as 0 = (1.25 L/s)(1 kg/L)[4.1868 kJ/(kg· K)] (50°C - 4°C)/0.8 = 303 kW Note that heating rate divided by storage capacity (411 W/L) exceeds 300 W/L, so the more accurately sized system is still consid- ered an instantaneous water heater. From Table 8, the peak design cumulative volume at 120 min is 5999 L, and is 8237 L at 180 min. The incremental flow rate slope is thus ((8237 - 5999 L)/3600 s = 0.62 L/s. The heating rate needed when using 5999 L of storage is more accurately computed as 0 = (0.62 L/s)(1 kg/L)[4.1868 kJ/(kg · K)](50°C-4°C)/0.8 = 151 kW | {}
cee9d22f-c702-4a95-80f2-99c91d74850d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Service Water Heating 51.17 Chart Type: line USABLE STORAGE CAPACITY, Lstudent Fig. 17 Motels Fig. 18 Nursing Homes item_01 5.5mL/s per student 3.5mL/s per student 1.5mL/s per student 1.0mL/s per student 1.0mL/s per student Table 8 Example 1, Simplified Method: Heating Rate and Storage Volume Options ¦ Time, min ¦ Litres per Person ¦ Total Litres for 198 People ¦ Average Litres per Second ¦ Heating Rate, kW ¦ Storage Volume, L ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 5 ¦ 2.6 ¦ 515 ¦ 1.7 ¦ 409 ¦ 736 ¦ ¦ 15 ¦ 6.4 ¦ 1 267 ¦ 1.4 ¦ 337 ¦ 1810 ¦ ¦ 30 ¦ 11.0 ¦ 2 178 ¦ 1.2 ¦ 288 ¦ 3111 ¦ ¦ 60 ¦ 18.2 ¦ 3 604 ¦ 1.0 ¦ 240 ¦ 5149 ¦ ¦ 120 ¦ 30.3 ¦ 5 999 ¦ 0.83 ¦ 200 ¦ 8570 ¦ ¦ 180 ¦ 41.6 ¦ 8 237 ¦ 0.76 ¦ 183 ¦ 11 767 ¦ ¦ 1440 ¦ 185.5 ¦ 36 729 ¦ 0.43 ¦ 103 ¦ 52 470 ¦ From Table 8, the peak design cumulative volume at 180 min is 8237 L, and at 1440 min is 36 729 L. Consequently, the incremental flow rate slope is (36 729 - 8237 L)/75 600 s = 0.38 L/s. The heating rate needed when using 8237 L of storage is thus more accurately com- puted as Q= (0.38 L/s)(1 kg/L)[4.1868 kJ/(kg·K)](50°C - 4°C)/0.8 = 91.5 kW It is important to recognize, however, when using this more accu- rate heating rate sizing method, that storage must eventually be reheated. The minimum heating rate used should therefore not be less than that computed using the 24 h average flow rate. Doing these calculations at other volumes and times yields the more accurate combinations of heating rate and storage volume that can serve the load, as shown in Table 9. There are several techniques to size water-heating systems using the more limited draw profile information in older data. Figures 16 to 23 show relationships between recovery and storage capacity for var- ious building categories. Any combination of storage and recovery rate that falls on the proper curve satisfies building requirements. Using the minimum recovery rate and maximum storage capacity on the curves yields the smallest hot-water capacity able to satisfy the building requirement. The higher the recovery rate, the greater the 24 h heating capacity and the smaller the storage capacity required. Note that the data in Figures 16 to 23 predate modern low-flow fix- tures and appliances. These curves can be used to select recovery and storage require- ments to accommodate water heaters that have fixed storage or recovery rates. Where hot-water demands are not coincident with peak electric, steam, or gas demands, greater heater inputs can be selected ifthey do not create additional energy system demands, and the corresponding storage tank size can be selected from the curves. Ratings of gas-fired water-heating equipment are based on sea- level operation and apply up to 600 m. For operation above 600 m, and in the absence of specific recommendations from the local authority, equipment ratings should be reduced by 4% for each 300 m above sea level before selecting appropriately sized equip- ment. Recovery rates in Figures 16 to 23 represent the actual hot water required without considering system heat losses. Heat losses from storage tanks and recirculating hot-water piping should be calcu- lated and added to the recovery rates shown. Storage tanks and hot- water piping must be insulated. The storage capacities shown are net usable requirements. Assuming that 60 to 80% ofthe hot water in a storage tank is usable, the actual storage tank size should be increased by 25 to 66% to compensate for unusable hot water. Figure 24 shows hourly flow profiles for a sample building in each category, so that readers may better understand the nature of energy withdrawal rate profiles that may need to be met in such applications. These buildings were selected from actual metered tests, but are not necessarily typical of all buildings in that category. Figure 24 should not be used for sizing water heaters, because a design load profile for a real building may vary substantially from these limited test cases. Example 2. Determine the required water heater size for a 300- student women's dormitory for the following criteria: a. Storage with minimum recovery rate b. Storage with recovery rate of 2.6 mL/s per student c. With the additional requirement for a cafeteria to serve a maximum of 300 meals per hour for minimum recovery rate, com- bined with item a; and for a recovery rate of 1.9 mL/s per maxi- mum meals per hour, combined with item b Inc. ASHRAE, 2019 user. single for Licensed | {}
0ec0a58d-bf64-4ea8-8db1-b87f8f3c258c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 51.18 2019 ASHRAE Handbook-HVAC Applications (SI) Chart Type: line TYPE A TYPE B RECOVERY CAPACITY TYPE Cyan Orange Purple item_01 0.6mL/s per person 0.2mL/s per person 0.4mL/s per person 0.0mL/s per person 0.0mL/s per person 0.0mL/s per person Fig. 19 Office Buildings Chart Type: line 0 1 2 3 4 5 6 7 8 item_01 0.55mL/s per student 0.45mL/s per student 0.35mL/s per student 0.3mL/s per student 0.25mL/s per student 0.15mL/s per student 0.0mL/s per student 0.05mL/s per student 0.05mL/s per student Fig. 22 Elementary Schools Solution: a. The minimum recovery rate from Figure 16 for women's dormi- tories is 1. 1 mL/s per student, or 330 mL/s total. At this rate, storage required is 45 L per student or 13.5 m3 total. On a 70% net usable basis, the necessary tank size is 13.5/0.7 = 19.3 m3. Fig. 20 Food Service b. The same curve shows 20L storage per studentat2.6 mL/s recovery, or 300 x 19 = 5700 L storage with recovery of300 x2.6 = 780 mL/s. The tank size is 5700/0.7 = 8140 L. c. Requirements for a cafeteria can be determined from Figure 20 and added to those for the dormitory. For the case of minimum recovery rate, the cafeteria (Type A) requires 300 x 0.47 = 140 mL/s recovery rate and 300 x 26.5/0.7 = 11.4 m3 of additional storage. The entire building then requires 330 + 140 = 470 mL/s recovery and 19.3 + 11.4 = 30.7 m3 of storage. With 1.0 mL/s recovery at the maximum hourly meal output, the recovery required is 300 mL/s, with 300 x 7.5/0.7 = 3260 mL/s of addi- tional storage. Combining this with item b, the entire building requires 780 + 300 = 1080 mL/s recovery and 8140 + 3260 = 11400 L = 11.4 m3 of storage. Fig. 21 Apartments Chart Type: line 0 1 2 3 4 5 6 7 8 9 10 11 12 13 14 15 item_01 0.9mL/s per student 0.7mL/s per student 0.6mL/s per student 0.5mL/s per student 0.4mL/s per student 0.3mL/s per student 0.3mL/s per student 0.2mL/s per student 0.2mL/s per student 0.2mL/s per student 0.2mL/s per student 0.2mL/s per student 0.2mL/s per student 0.2mL/s per student 0.2mL/s per student 0.2mL/s per student Fig. 23 High Schools Note: Recovery capacities shown are for heating water only. Additional capacity must be added to offset system heat losses. Example 3. Determine the water-heater size and monthly hot-water con- sumption for an office building to be occupied by 300 people under the following conditions: a. Storage with minimum recovery rate b. Storage with 3.8 L per person storage C. Additional minimum recovery rate requirement for a luncheon- ette open 5 days a week, serving a maximum of 100 meals per hour and an average of 200 meals per day Solution: d. Monthly hot-water consumption a. With minimum recovery rate of 0.1 mL/s per person from Figure 19, 30 mL/s recovery is required; storage is 6 L per person, or Inc. ASHRAE, 2019 user. single for Licensed | {}
20c90b19-181c-4e7b-b200-a222498f63d0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Service Water Heating 51.19 Chart Type: line MEN'S DORMITORIES 6 8 10 12 2 4 item_01 1.5mL/s per student 1.4mL/s per student 1.1mL/s per student 1.0mL/s per student 5.0mL/s per student 1.4mL/s per student 1.1mL/s per student bed per mL/s Chart Type: line 12 hours 2 hours 4 hours 6 hours 8 hours 10 hours item_01 0mm Hectares (mm) 4mm Hectares (mm) 3mm Hectares (mm) 2mm Hectares (mm) 1mm Hectares (mm) 0mm Hectares (mm) X-Axis: FOOD SERVICE (TYPE B) Y-Axis: mL/s per maximum meals per h Chart Type: line 12 2 4 6 8 10 24 26 28 30 32 34 36 38 40 42 44 46 48 50 52 54 56 58 60 62 64 66 68 70 72 74 76 78 80 82 84 86 88 90 92 94 96 98 100 102 104 106 108 110 112 item_01 item_01 0.6 0.05mL/s per maximum meals per h 0.4mL/s per maximum meals per h 0.3mL/s per maximum meals per h 0.2mL/s per maximum meals per h 0.0mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h 0.05mL/s per maximum meals per h student student per mL/s mL/s X-Axis: Julian Date (JUNIOR HIGH SCHOOLS) Y-Axis: Minュ per student Chart Type: line 12 2 4 6 8 10 item_01 0Micrograms per student 4Micrograms per student 6Micrograms per student 8Micrograms per student 10Micrograms per student 12Micrograms per student Chart Type: line Week 12 Week 2 Week 4 Week 6 Week 8 Week 10 item_01 5Not specified 0Not specified 0Not specified 0Not specified 0Not specified 1Not specified unit per mL/s Chart Type: line 12 2 4 6 8 10 item_01 0.0 0.3 0.2 0.6 0.5 0.3 Chart Type: line 12 2 4 6 8 10 item_01 0.3m/s per maximum meals per t 0.4m/s per maximum meals per t 0.3m/s per maximum meals per t 0.6m/s per maximum meals per t 1.2m/s per maximum meals per t 0.9m/s per maximum meals per t X-Axis: Office buildings Y-Axis: mL/s per person Chart Type: line 12 2 4 6 8 10 item_01 0mL/s 0.2mL/s 0.0mL/s 0.0mL/s 0.0mL/s 0mL/s apartment per mL/s Chart Type: line 12 2 4 6 8 10 item_01 2Not specified 4Not specified 3Not specified 2Not specified 2Not specified 3Not specified student per mL/s student Fig. 24 Hourly Flow Profiles for Various Building Types X-Axis: Elementary Schools Y-Axis: Mass per Student Chart Type: line 12 2 4 6 8 10 item_01 0 0.5 0.2 0.0 0 0 per mL/s ![image](/image/placeholder) 12 10 8 6 4 。 2 12 2 4 6 8 10 12 2 4 6 8 10 12 SENIOR HIGH SCHOOLS DAY IN WHICH MAXIMUM HOURLY USE OCCURRED DAY IN WHICH MAXIMUM DAILY USE OCCURRED Inc. ASHRAE, 2019 Ⓒ user. single for Licensed AVERAGE OF ALL DAYS DURING TESTS | {}
7f491526-da21-43a4-aeb2-c0a8fa51b44f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 51.20 2019 ASHRAE Handbook- -HVAC Applications (SI) Table 9 Example 1, More Accurate Method: Heating Rate and Storage Volume Options ¦ Time, min ¦ Litres ¦ Total Litres ¦ Local Slope of Incremental ¦ Heating Rate, ¦ Storage Volume, ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ per Person ¦ for 198 People ¦ Litres per Minute ¦ kW ¦ L ¦ ¦ 5 ¦ 2.6 ¦ 515 ¦ 1.2 ¦ 303 ¦ 736 ¦ ¦ 15 ¦ 6.4 ¦ 1 267 ¦ 0.97 ¦ 233 ¦ 1 810 ¦ ¦ 30 ¦ 11.0 ¦ 2 178 ¦ 0.77 ¦ 191 ¦ 3 111 ¦ ¦ 60 ¦ 18.2 ¦ 3 604 ¦ 0.65 ¦ 162 ¦ 5 149 ¦ ¦ 120 ¦ 30.3 ¦ 5 999 ¦ 0.61 ¦ 151 ¦ 8 570 ¦ ¦ 180 ¦ 41.6 ¦ 8 237 ¦ 0.37 ¦ 103* ¦ 11 767 ¦ ¦ 1440 ¦ 185.5 ¦ 36 729 ¦ 0.43 ¦ 103 ¦ 52 470 ¦ *Heating rate should not be lower than that needed to satisfy load on a 24 h basis. Table 10 Hot Water Demand per Fixture for Various Types of Buildings (Litres of water per hour per fixture, calculated at a final temperature of 60°C) ¦ ¦ Apartment House ¦ Club ¦ Gymnasium ¦ Hospital ¦ Hotel ¦ Industrial Plant ¦ Office Building ¦ Private Residence ¦ School ¦ YMCA ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 1. Basin, private lavatory ¦ 7.6 ¦ 7.6 ¦ 7.6 ¦ 7.6 ¦ 7.6 ¦ 7.6 ¦ 7.6 ¦ 7.6 ¦ 7.6 ¦ 7.6 ¦ ¦ 2. Basin, public lavatory ¦ 15 ¦ 23 ¦ 30 ¦ 23 ¦ 30 ¦ 45.5 ¦ 23 ¦ ¦ 57 ¦ 30 ¦ ¦ 3. Bathtubc ¦ 76 ¦ 76 ¦ 114 ¦ 76 ¦ 76 ¦ ¦ ¦ 76 ¦ ¦ 114 ¦ ¦ 4. Dishwashera ¦ 57 ¦ 190-570 ¦ ¦ 190-570 ¦ 190-760 ¦ 76-380 ¦ ¦ 57 ¦ 76-380 ¦ 76-380 ¦ ¦ 5. Foot basin ¦ 11 ¦ 11 ¦ 46 ¦ 11 ¦ 11 ¦ 46 ¦ ¦ 11 ¦ 11 ¦ 46 ¦ ¦ 6. Kitchen sink ¦ 38 ¦ 76 ¦ ¦ 76 ¦ 114 ¦ 76 ¦ 76 ¦ 38 ¦ 76 ¦ 76 ¦ ¦ 7. Laundry, stationary tub ¦ 76 ¦ 106 ¦ ¦ 106 ¦ 106 ¦ ¦ ¦ 76 ¦ ¦ 106 ¦ ¦ 8. Pantry sink ¦ 19 ¦ 38 ¦ ¦ 38 ¦ 38 ¦ ¦ 38 ¦ 19 ¦ 38 ¦ 38 ¦ ¦ 9. Shower ¦ 114 ¦ 568 ¦ 850 ¦ 284 ¦ 284 ¦ 850 ¦ 114 ¦ 114 ¦ 850 ¦ 850 ¦ ¦ 10. Service sink ¦ 76 ¦ 76 ¦ ¦ 76 ¦ 114 ¦ 76 ¦ 76 ¦ 57 ¦ 76 ¦ 76 ¦ ¦ 11. Hydrotherapeutic shower ¦ ¦ ¦ ¦ 1520 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 12. Hubbard bath ¦ ¦ ¦ ¦ 2270 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 13. Leg bath ¦ ¦ ¦ ¦ 380 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 14. Arm bath ¦ ¦ ¦ ¦ 130 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 15. Sitz bath ¦ ¦ ¦ ¦ 114 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 16. Continuous-flow bath ¦ ¦ ¦ ¦ 625 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 17. Circular wash sink ¦ ¦ ¦ ¦ 76 ¦ 76 ¦ 114 ¦ 76 ¦ ¦ 114 ¦ ¦ ¦ 18. Semicircular wash sink ¦ ¦ ¦ ¦ 38 ¦ 38 ¦ 57 ¦ 38 ¦ ¦ 57 ¦ ¦ ¦ 19. DEMAND FACTOR ¦ 0.30 ¦ 0.30 ¦ 0.40 ¦ 0.25 ¦ 0.25 ¦ 0.40 ¦ 0.30 ¦ 0.30 ¦ 0.40 ¦ 0.40 ¦ ¦ 20. STORAGE CAPACITY FACTORb ¦ 1.25 ¦ 0.90 ¦ 1.00 ¦ 0.60 ¦ 0.80 ¦ 1.00 ¦ 2.00 ¦ 0.70 ¦ 1.00 ¦ 1.00 ¦ Note: Data sources predate low-flow fixtures and appliances. aDishwasher requirements should be taken from this table or from manufacturers' data for model to be used, ifknown. Inc. ASHRAE, 2019 user. single for Licensed 300 x 6 = 1800 L. If 70% of the hot water is usable, the tank size is 1800/0.7 = 270 L. b. The curve also shows 3.8 L storage per person at 0.18 mL/s per person recovery, or 300 x 0.18 = 54 mL/s. The tank size is 300 x 3.8/ 0.7 = 1630 L. C. Hot-water requirements for a luncheonette (Type B) are in Figure 20. With a minimum recovery capacity of 0.26 mL/s per maximum meals per hour, 100 meals per hour requires 26 mL/s recovery, and the storage is 7.6 L per maximum meals per hour, or 100 x 7.6/0.7 = 1090 L storage. The combined requirements with item a are then 56 mL/s recovery and 3660 L storage. Combined with item b, the requirement is 80 mL/s recovery and 2720 L storage. d. Average day values are found in Table 6. The office building con- sumes an average of 3.8 L per person per day x 30 days per month x 300 people = 34.2 m3 per month and the luncheonette will consume sper day x 22 days per month = 11.4 m3 per 2.6 L per meal x 200 meals month, for a total of 45.6 m per month. Note: Recovery capacities shown are for heating water only. Addi- tional capacity must be added to offset the system heat losses. Example 4. Determine the water heater size for a 200-unit apartment house under the following conditions: where unlimited supply of steam is available from central street steam system or large boiler plant. bRatio of storage tank capacity to probable maximum demand/h. Storage capacity may be reduced cWhirlpool baths require specific consideration based on capacity. They are not included in the bath- tub category. a. Storage with minimum recovery rate b. Storage with 4.2 mL/s per apartment recovery rate c. Storage for each of two 100-unit wings 1. Minimum recovery rate 2. Recovery rate of 4.2 mL/s per apartment Solution: a. The minimum recovery rate, from Figure 21, for apartment build- ings with 200 apartments is 2.2 mL/s per apartment, or a total of 440 mL/s. The storage required is 90 L per apartment, or 18 m3. If 70% of this hot water is usable, the necessary tank size is 18/0.7 = 25.7 m3. b. The same curve shows 19 L storage per apartment at a recovery rate of 4.1 mL/s per apartment, or 200 x 4.2 = 840 mL/s. The tank size is 200 x 19/0.7 = 5.43 m3. c. Solution for a 200-unit apartment house having two wings, each with its own hot-water system. 1. With minimum recovery rate of 2.6 mL/s per apartment (see Figure 21), a 260 mL/s recovery is required, and the necessary storage is 106 L per apartment, or 100 x 106 = 10.6 m3. The required tank size is 10.6/0.7 = 15.2 m3 for each wing. 2. The curve shows that, for a recovery rate of4.2 mL/s per apart- ment, storage is 50 L per apartment, or 100 x 50 = 5 m3, with recovery of 100 x 4.2 = 420 mL/s. The necessary tank size is 5/0. 7 = 7.2 m3 in a. Storage with minimum recovery rate b. each wing. Note: Recovery capacities shown are for heating water only. Addi- tional capacity must be added to offset the system heat loss. Example 5. Determine the water-heater size and monthly hot-water con- sumption for a 2000-student high school under the following conditions: a. Storage with minimum recovery rate | {}
1a27cafe-1b01-4b55-96c0-89f67c534a4c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Service Water Heating 51.21 b. Storage with 15 m3 maximum storage capacity c. Monthly hot-water consumption Solution: a. With the minimum recovery rate of 0.16 mL/s per student (from Figure 23) for high schools, 320 mL/s recovery is required. The storage required is 1 1.5 L per student, or 2000 x 11.5 = 2.3 m3. If 70% of the hot water is usable, the tank size is 2.3/0.7 = 32.9 m3. b. Net storage capacity is 0.7 x 15 = 10.5 m3, or 5.25 L per student. From the curve, a recovery capacity of 0.41 mL/s per student or 2000 x 0.41 = 820 mL/s is required. C. From Table 6, monthly hot-water consumption is 2000 students x 1.86.8 L per student per day x 22 days = 299 m3. Note: Recovery capacities shown are for heating water only. Addi- tional capacity must be added to offset the system heat loss. Table 10 can be used to determine the size of water-heating equipment from the number offixtures. However, caution is advised when using this table, because its data are very old, taken well before the introduction of modern low-flow fixtures and appliances. To obtain the probable maximum demand, multiply the total quan- tity for the fixtures by the demand factor in line 19. Note that, as the number of fixtures becomes very small (e.g., for a water heater to serve a single small apartment), the demand (diversity) factors listed in Table 10 are no longer valid. In all cases, total demand is never less than the demand for the largest single fixture. The heater or coil should have a water-heating capacity equal to this probable maxi- mum demand. The storage tank should have a capacity equal to the probable maximum demand multiplied by the storage capacity factor in line 20. Example 6. Determine heater and storage tank size for an apartment building from a number of fixtures. Solution: ¦ 60 lavatories ¦ x ¦ 7.6 ¦ = ¦ 46 L/h ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 30 bathtubs ¦ X ¦ 76 ¦ = ¦ 2280 L/h ¦ ¦ 30 showers ¦ x ¦ 114 ¦ = ¦ 3420 L/h ¦ ¦ 60 kitchen sinks ¦ x ¦ 38 ¦ = ¦ 2280 L/h ¦ ¦ 15 laundry tubs ¦ X ¦ 76 ¦ = ¦ 1140 L/h ¦ ¦ Possible maximum demand ¦ ¦ ¦ = ¦ 9576 L/h ¦ ¦ Probable maximum demand ¦ =9576 x 0.30= ¦ =9576 x 0.30= ¦ 2870 L/h ¦ 2870 L/h ¦ ¦ Heater or coil capacity ¦ =2870/3600=0.80 L/s ¦ =2870/3600=0.80 L/s ¦ =2870/3600=0.80 L/s ¦ =2870/3600=0.80 L/s ¦ ¦ Storage tank capacity ¦ =2870 x 1.25=3590 L/s ¦ =2870 x 1.25=3590 L/s ¦ =2870 x 1.25=3590 L/s ¦ =2870 x 1.25=3590 L/s ¦ Showers. In many housing installations such as motels, hotels, and dormitories, peak hot-water load is usually from shower use. Table 10 indicates the probable hourly hot-water demand and rec- ommended demand and storage capacity factors for various types of buildings. Hotels could have a 3 to 4 h peak shower load. Motels require similar volumes of hot water, but peak demand may last for only a 2 h period. In some types of housing, such as barracks, fra- ternity houses, and dormitories, all occupants may take showers within a very short period. In this case, it is best to find the peak load by determining the number of shower heads and rate of flow per head; then estimate the length of time the shower will be on. It is estimated that the average shower time per individual is 7.5 min (Meier 1985). Flow rate from a shower head varies depending on type, size, and water pressure. At 280 kPa water pressure, available shower heads have nominal flow rates of blended hot and cold water from about 160 to 380 mL/s. In multiple-shower installations, flow control valves on shower heads are recommended because they reduce flow rate and maintain it regardless of fluctuations in water pressure. Flow can usually be reduced to 50% of the manufacturer's maximum flow rating without adversely affecting the spray pattern of the shower head. Flow control valves are commonly available with capacities from 95 to 250 mL/s. If the manufacturer's flow rate for a shower head is not available and no flow control valve is used, the following average flow rates may serve as a guide for sizing the water heater: ¦ Small shower head ¦ 160 mL/s ¦ ¦ --- ¦ --- ¦ ¦ Medium shower head ¦ 280 mL/s ¦ ¦ Large shower head ¦ 380 mL/s ¦ Note that the maximum flow rate allowed by U.S. federal energy efficiency standards is 160 mL/s, as of 1992. However, higher- flowrate models are still sold. Food Service. These establishments are required to provide a sufficient supply of hot water to meet the peak hot-water demand requirements set forth by the overseeing regulatory body, usually the county health department. Cities and counties adopt or modify state or federal hot-water sizing guidelines for food service estab- lishments to meet the needs of their locality. The procedure for siz- ing water heaters for restaurants typically includes the following steps: 1. List all hot-water end-use fixtures by type and by count. 2. Characterize each fixture for maximum hot-water use per hour and per minute. 3. Calculate the peak hot-water demand for water heaters with and without storage. 4. Obtain the water heater temperature rise required for winter. 5. Calculate the minimum water heater input rate. 6. Select the water heater type, input rate, and storage capacity (in a few jurisdictions). It is important to note that the hot-water requirements for various fixtures presented in Table 1 1 are based on various resources (see the table notes), which are currently used by food service facilities and health departments to size hot-water heaters. Some equipment flow data in these guidelines predates current low-flow fixtures used in kitchens. Specifically, the flow rate requirements for prerinse spray valves have dropped from 315 mL/s to a federally mandated maximum flow rate of 100 mL/s, and, similarly, flow rate require- ments for aerators on public hand sinks have dropped from 140 mL/ s to 30 mL/s. Note that the sizing guidelines required by local mandate for commercial food service applications specify only the required heating rates; they do not address the storage volume requirements of storage water heaters. Because of this, it is not really possible to size storage water heaters with the information specified. Although for some types of storage water heaters it may be possible to provide the storage water heater heating rate specified, there is no way to know how large the tank needs to be with that information alone. More information is needed regarding the time spacing of draws throughout the day before adequate storage volume can be speci- fied. It is possible to design or select storage water heating systems that will perform adequately but do not have as high a heating rate as may be specified in local mandates, as long as adequate amounts of storage are provided. In this regard, the outdated practice of spec- ifying needed storage water heater heating requirements without regard to storage volume used is an impediment to use of newer higher efficiency technologies, such as gas- or electric heat pump water heaters and solar water heating systems. Such systems would normally be provided with lower heating rates and more storage when meeting loads, to minimize first costs. The intent ofthe heating rate sizing guidelines for storage heaters is an attempt to ensure that hot water is available during operating hours to meet the food preparation and sanitation needs of the facility for food safety reasons. Thus, the food service sizing guide- line is the minimum bar that some localities may accept for specified heating rates. However, this differs from the combination of heating rate and storage volume that may actually work for a given installa- tion. The sizing guidelines are limited in that they only focus on cal- culating the energy input rate to the water heater without providing guidance on minimum hot-water storage requirements (except for North Carolina), and hot-water delivery performance considerations Inc. ASHRAE, 2019 user. single for Licensed | {}
4c43bfa1-7bbf-4012-9da2-520da7062655 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 51.22 Table 11 Hot- w ater Requirements for Various Commercial Kitchen Uses ¦ Equipmenta ¦ Storage, mL/s ¦ Tankless, mL/s ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Hand sink or lavatory ¦ 5.3 ¦ 30 ¦ ¦ One-compartment food preparation or utility sink ¦ 5.3 ¦ 125 ¦ ¦ Two-compartment food preparation or utility sink ¦ 11 ¦ 125 ¦ ¦ Large three-compartment sanitation sink (610 x 610 x 360 mm ¦ 110b ¦ 125c ¦ ¦ Standard three-compartment sanitation sink (460 x 460 x 250 mm) ¦ 44b ¦ 125° ¦ ¦ Bar three-compartment sanitation sink (250 x 360 x 250 mm) ¦ 19b ¦ 125 ¦ ¦ Mop sink or can wash facility ¦ 16 ¦ 125c ¦ ¦ Prerinse spray valve ¦ 47 ¦ Varies ¦ ¦ Dishwasher ¦ Variesd ¦ Varies ¦ Source: CCDEH (1995), FDA (2000), NCPH (2001). aRefer to manufacturer's specifications for other end-use fixtures that use hot water. bEquation to calculate storage heater hot water demand requirements for sanitation sinks: mL/s = Sink size (mm3) x Number of compartments X 0.001 (mL/(h · mm3) + 3600 s/h Certain jurisdictions, including the FDA and North Carolina, use a compartment fill factor, which is 75% of the sink size, to calculate the hot water requirements of sani- tation sinks. °A flow rate of 320 mL/s is recommended for compartment sink or hose bibb fill oper- ations. dCertain jurisdictions, including the FDA and North Carolina, use a rack loading effi- ciency factor, which is 70% of the dishwasher manufacturer's listed hourly rinse water use, to calculate hot-water demand. (e.g., performance limitations of tankless heaters with door-type dishwashers). The food safety sizing guidelines for water heaters also do not consider after-hours cleanup, when the peak hourly hot- water use occurs in some facilities; this may cause emptying of the tank on a nightly basis. Rapidly using hot water and filling the tank with cold water can cause thermal fatiguing of the tank, greatly reducing the operating life in gas storage heaters (Fisher-Nickel 2010). There is no current method for calculating the minimum stor- age requirement for a food service facility or sizing storage heaters based on the ratio of storage capacity and energy input rate. This is a difficult task, because hot-water use on an average daily, peak hourly, or per-minute basis greatly varies between food service facil- ities, especially in larger facilities, even of equal size and type. Vari- ations in staff operating practices (e.g., after-hours store cleaning), equipment maintenance, and other operations between two identi- cal facilities can cause large differences in hot-water consump- tion. This sizing guideline and associated examples are intended to clarify the prevailing food safety sizing guidelines, which in many cases are not comprehensive and are difficult to follow. After the maximum flow rate has been calculated using Table 11, the required heater(s) may be sized using manufacturers' specifica- tion sheets that cross-reference temperature rise and flow rate, or using Equation (11): qi = Qh cp pAt/n where qi = heater input, W ( 1 1 ) Qh = flow rate, mL/s Cp = specific heat of water = 4. 1868 kJ/(kg· K) p = density of water = 1.0 kg/L At = temperature rise, K 11 = heater efficiency Sizing water heater input rate in food service may require following local food safety department water-heater sizing guide- lines, which typically provide end-use fixture flow rates, tempera- ture rise, and heater efficiency values to calculate minimum flow 2019 ASHRAE Handbook-HVAC Applications (SI) Table 12 Range in Water Heater Flow Rate Requirements to Satisfy Dishwasher Rinse Operation of Various Units ¦ Type of Dishwasher ¦ Flow Rate for Heaters Without ¦ Hourly Demand for Heaters with ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ Storage,a mL/s ¦ Storage,b mL/s ¦ ¦ Undercounter (low-temperature) ¦ 130 to 280 ¦ 23 to 68 ¦ ¦ Undercounter (high-temperature) ¦ 200 to 420 ¦ 20 to 54 ¦ ¦ Door type (low-temperature) ¦ 120 to 320 ¦ 35 to 72 ¦ ¦ Door type (high-temperature) ¦ 170 to 450 ¦ 29 to 97 ¦ ¦ Rack conveyor (low-temperature) ¦ 80 to 300 ¦ 80 to 300 ¦ ¦ Rack conveyor (high-temperature) ¦ 45 to 300 ¦ 50 to 300 ¦ ¦ Flight conveyor (high-temperature) ¦ 65 to 380 ¦ 60 to 380 ¦ aBased on flow rate during rinse operation period. bBased on dishwasher operation at 100% of mechanical capacity. rate or recovery rate. An alternative to using these input rate sizing guidelines requires the commercial kitchen to hire a professional engineer to submit for approval an alternative water-heater sizing calculation. This latter method is typically too costly and time con- suming in the build-out or renovation of most commercial kitchens. Dishwashers in food service facilities typically dictate the water heater outlet temperature required. Dishwashers generally require delivery of 60°C water for rinse operation, but inlet temperature can range from a minimum of {50°C for a low-temperature dishwasher to 82°C for a high-temperature dishwasher without a booster heater. For a typical hot-water system distribution line, heat losses require the water heater thermostat to be set at an elevated temperature (typ- ically between 63 to 66°C) to deliver 60°C water to the dishwasher or booster heater. In restaurants, bacteria are killed by rinsing washed dishes with 82 to 90°C water for several seconds. In addition, an ample supply of general-purpose hot water, usually at 60 to 65°C, is required for the wash cycle of dishwashers. Although a water temperature of 60°C is reasonable for dish washing in private dwellings, in public places, the NSF (e.g., Standard 3) or local health departments require 82 to 90°C water in the rinsing cycle. However, the NSF allows a lower temperature of 50 to 60°C when low temperature or fill and dump machines are used with the use of a chemical sanitizing rinse. The two-temperature hot-water requirements of food service estab- lishments present special problems. The lower-temperature water is distributed for general use, but the 82°C water should be confined to the equipment requiring it and should be obtained by boosting the temperature. It is dangerous to distribute 82°C water for general use. ANSI/NSF Standard 3-2001 covers the design of dishwashers and water heaters used by restaurants. The data provided in Table 12 shows the range of water heater flow rate and hourly hot-water demand requirements for various types oflow- and high-temperature sanitizing dishwashers based on 100% operating capacity of the machines. Loading a dishwasher at 100% capacity is impractical in most commercial kitchens. Some local health departments assume a 70% operating rinse capacity for sizing dishwashers' hot-water demand, except for rackless-type conveyor machines where the fresh-water rinse is continually oper- ating when the machine is in operation. Some dishwashers use only a cold-water supply for rinse and (with some models) for the tank fill, allowing them to operate without any connection to the hot- water line. These undercounter and door-type machines typically use integrated booster heaters and exhaust-air heat recovery to pre- heat the cold water for the next rinse cycle. Inc. ASHRAE, 2019 user. single for Licensed Examples 7, 8, and 9 demonstrate the use of Equation ( 1 1 ) in conjunction with Tables 1 1 and 12. Example 7. Determine the maximum hot-water flow rate demand for tankless water heaters and the maximum hourly average hot-water flow rate demand for storage water heaters for a commercial kitchen | {}
db31cf30-b39f-4ffb-9408-1cb5e719892c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Service Water Heating 51.23 with a one-compartment food preparation sink, one standard three- compartment sanitation sink, two hand sinks, two lavatories, one mop sink, one prerinse sink with a 70 mL/s spray valve, and one high- temperature door-type dishwasher (3.8 L/rack, 11 s rinse time, 57 racks/h) with a built-in 22 K temperature rise booster heater. Solution: The end-use fixtures and hot-water demand requirements for sizing the heating rate of storage or tankless water heaters are shown in the following table: ¦ Item ¦ Flow Rate Required, mL/s ¦ Recovery Rate Required, mL/s ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ One-comp. prep sink ¦ 125 ¦ 5 ¦ ¦ Three-comp. sink ¦ 125 ¦ 46 ¦ ¦ Hand sink (2) ¦ 65 ¦ 11 ¦ ¦ Lavatory (2) ¦ 65 ¦ 11 ¦ ¦ Mop sink ¦ 125 ¦ 16 ¦ ¦ Prerinse sink ¦ 70 ¦ 47 ¦ ¦ Dishwasher ¦ 340 ¦ 60 ¦ ¦ Total requirements ¦ 915 ¦ 196 ¦ The minimum flow rate for sizing the heating rate of a tankless water heater is 915 mL/s. Likewise, the minimum flow rate for sizing the heating rate of a storage water heater is 196 mL/s. Example 8. Determine the energy input requirements (heating rate) for both a tankless and a storage water heater for the commercial kitchen described in Example 7. Examine both gas and electric resistance energy source options. Assume an operating efficiency of 70% for the noncondensing gas option, 85% condensing for the condensing gas option, 90% for the electric storage option, and 99% for the electric tankless option. Assume the design entering cold-water temperature (winter) is 10°C and the water heater outlet temperature is 66°C. This is a little higher than the 60°C required by the dishwasher booster heater, to account for piping heat losses. Solution: The temperature rise required is 66 - 10 = 56 K. For a tank- less water heater, the required heating rate using Equation ( 1 1) is com- puted as qi = (0.915 L/s)(1.0 kg/L)[4.1 868 kJ/(kg·K)](56 K) = 215 kW Thus, for the 70% gas tankless option, the required energy input rate is 215/0.70 = 307 kW. It is common practice to install one or more 58 kW units in parallel in commercial facilities to meet minimum flow rate requirements. Using this approach, six standard-efficiency tankless units, each rated at 58 kW, are required to meet this load. For the 85% gas condensing tankless option, the required heating rate is 215/0.85 = 253 kW, requiring five 58 kW condensing tankless heaters. For the 99% electric tankless option, the required energy input rate is 215/0.99 = 217 kW. Four 54 kW or six 36 kW electric resistance tankless heaters are required to meet the hot-water demand. Because tankless water heaters have no storage volume, these heating rates are adequate for use in specifying appropriate water heaters. Sizing tankless heaters using manufacturers' specification sheets data on maximum flow rate at a given temperature rise is a common approach, because the data are readily provided. Flow rate data varies slightly among manufacturers of similar products at the same input rate based on the efficiency of the unit. A 58 kW standard-efficiency heater typically provides a maximum of 210 mL/s of water at a 56 K temperature rise, whereas a condensing heater provides 240 mL/s. To meet the flow requirements of 915 mL/s for this facility, five standard- efficiency 58 kW units installed in parallel for a combined input rate of 292 kW are required to meet the load by providing a maximum com- bined flow rate of 1040 mL/s. To meet the flow requirements with condensing high-efficiency tankless heaters, four 58 kW units for a combined input rate of 233 kW are required, for a maximum combined flow rate of 960 mL/s. It is important to note that using the manufac- turer's stated maximum flow rate at a given temperature rise to calcu- late the number of tankless units based on the maximum flow rate calculation of 915 mL/s is a less conservative approach, because it relies on the rated thermal efficiency of the heater instead of the typical operating efficiency. For the storage water heaters, the required heating rate is computed as qi = (0.196 L/s)(1.0 kg/L)[4.1868 kJ/(kg·K)](56 K) = 46 kW Thus, for the 70% gas storage water heater, the required heating rate is 46/0.70 = 66 kW. For the 85% gas condensing storage water heater, the required heating rate is 46/0.85 = 54 kW. For the 90% elec- tric resistance storage water heater, the required heating rate is 46/ 0.90 = 51 kW. Note that this information in insufficient to properly specify a storage water heater, because a method for calculating the minimum storage volume is needed. Moreover, once storage is incorporated, note that the loads can be met by using smaller heating rates than those com- puted here, using larger storage tanks. In this respect, the heating rates mandated by a typical health department become a barrier to using higher-efficiency equipment, such as heat pump water heaters or solar water heating, whose heating capacities are more expensive than stan- dard efficiency equipment, and whose cost-effective system designs therefore favor smaller heating rates and larger storage volumes. Although this is true, the majority of water heaters in commercial kitch- ens are specified using the food safety guidelines to calculate the mini- mum input rate of conventional gas or electric water heaters. In doing so, one or more storage heaters may be selected to meet this total requirement. Typically, one 73 kW gas storage heater (or two 37 kW units) rated at 80% thermal efficiency is chosen. An energy-efficient approach is to select a high-efficiency condensing water heater rated at 95% thermal efficiency, which is assumed to be operating at 85% oper- ating efficiency in this kitchen with continuous recirculation. A 58 kW condensing gas storage heater will meet the requirements for this facility and is a better value, because it reduces operating costs and is competi- tive on first costs. One 54 kW or two 27 kW electric resistance storage heaters could be selected from manufacturers' specification sheets to meet the hot-water demand. Example 9. For the commercial kitchen described in Example 7, what is the condensing storage water heater input rating if the facility chooses to install a dishwasher that only requires a cold-water hookup? Assume that the facility can benefit by reducing the required outlet temperature by 11 K from 66°C. Also assume that, by removing the need for contin- uous recirculation, this measure improves the operating efficiency from a nominal 85% to 90%. Solution: The total hot-water demand calculated in Example 7 drops from 196 mL/s to 136 mL/s when the hot-water demand of the dish- washer on the centralized water heater is eliminated. For the storage water heaters, the required heating rate is computed as qi = (0.136 L/s)(1.0 kg/L)[4.1868 kJ/(kg·K)](44 K) = 25 kW For the 90% gas condensing storage water heater, the required heating rate is 25/0.90 = 28 kW. One 29 kW gas condensing storage heater can be selected to meet the hot water demand using the food safety input rate sizing guidelines. Also, dishwashers that have only a cold water feed typically depend on heat recovery systems to preheat the incoming cold water from the exhaust or drainwater waste streams to a temperature of 43°C. They rely on larger secondary heating systems commonly referred to as booster heaters to heat the water to the 82°C sanitizing rinse temperature on a high-temperature machine. This requires the addition of a 39 K rise booster heater instead of a conven- tional 22 K booster heater that would be used in conjunction with entering 60°C water from the primary water heater. Schools. Service water heating in schools is needed for janitorial work, lavatories, cafeterias, shower rooms, and sometimes swim- ming pools. Hot water used in cafeterias is about 70% ofthat usually required in a commercial restaurant serving adults and can be esti- mated by the method used for restaurants. Where NSF sizing is required, follow Standard 5. Shower and food service loads are not ordinarily concurrent. Each should be determined separately, and the larger load should determine the size of the water heater(s) and the tank. Provision must be made to supply 82°C sanitizing rinse. Inc. ASHRAE, 2019 user. single for Licensed | {}
8f6351a5-ad87-4d5d-b4d2-ba0d6e612822 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 51.24 The booster must be sized according to the temperature of the supply water. If feasible, the same water can be used for both needs. If the distance between the two points of need is great, a separate water heater should be used. A separate heater system for swim- ming pools can be sized as outlined in the section on Swimming Pools/Health Clubs. Domestic Coin-Operated Laundries. Small domestic machines in coin laundries or apartment house laundry rooms have a wide range of draw rates and cycle times. Domestic machines provide a wash water temperature (normal) as low as 50°C. Some manu- facturers recommend a temperature of 70°C; however, the average appears to be 60°C. Hot-water sizing calculations must ensure a supply to both the instantaneous draw requirements of a number of machines filling at one time and the average hourly requirements. The number of machines drawing at any one time varies widely; the percentage is usually higher in smaller installations. One or two customers starting several machines at about the same time has a much sharper effect in a laundry with 15 or 20 machines than in one with 40 machines. Simultaneous draw may be esti- mated as follows: ¦ 1 to 11 machines ¦ 100% of possible draw ¦ ¦ --- ¦ --- ¦ ¦ 12 to 24 machines ¦ 80% of possible draw ¦ ¦ 25 to 35 machines ¦ 60% of possible draw ¦ ¦ 36 to 45 machines ¦ 50% of possible draw ¦ Possible peak draw can be calculated from F = 1000NPV/T where (12) F = peak draw, mL/s N = number of washers installed P = number of washers drawing hot water divided by N Vf = quantity ofhot water supplied to machine during hot-wash fill, L T = wash fill period, s Recovery rate can be calculated from R = (1000NV,)/[60(0 + 10)] = 16.7 NVf/(0 + 10) Inc. ASHRAE, 2019 user. single for Licensed where (13) R = total hot water (machines adjusted to hottest water setting), mL/s 0 = actual machine cycle time, min Note: (0 + 10) is the cycle time plus 10 min for loading and unloading. Commercial Laundries. Commercial laundries generally use a storage water heater. The water may be softened to reduce soap use and improve quality. The trend is toward installing high-capacity washer-extractor wash wheels, resulting in high peak demand. Sizing Data. Laundries can normally be divided into five catego- ries. The required hot water is determined by the mass of the mate- rial processed. Average hot-water requirements at 82°C are ¦ Institutional ¦ 4.6 mL/(kg·s) ¦ ¦ --- ¦ --- ¦ ¦ Commercial ¦ 4.6 mL/(kg·s) ¦ ¦ Linen supply ¦ 5.8 mL/(kg·s) ¦ ¦ Industrial ¦ 5.8 mL/(kg·s) ¦ ¦ Diaper ¦ 5.8 mL/(kg·s) ¦ Total mass of the material times these values give the average hourly hot-water requirements. The designer must consider peak requirements; for example, a 270 kg machine may have a 1.25 L/s average requirement, but the peak requirement could be 22 L/s. In a multiple-machine operation, it is not reasonable to fill all machines at the momentary peak rate. Diversity factors can be 2019 ASHRAE Handbook-HVAC Applications (SI) estimated by using 1.0 ofthe largest machine plus the following bal- ance: ¦ ¦ Total number of machines ¦ Total number of machines ¦ Total number of machines ¦ Total number of machines ¦ Total number of machines ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 2 ¦ 3 to 5 ¦ 6 to 8 ¦ 9 to 11 ¦ 12 and over ¦ ¦ ¦ 1.0 + ¦ 0.6 ¦ 0.45 ¦ 0.4 ¦ 0.35 ¦ 0.3 ¦ For example, four machines have a diversity factor of1.0 + 0.45 1.45. Types of Systems. Service water-heating systems for laundries are pressurized or vented. The pressurized system uses city water pressure, and the full peak flow rates are received by the softeners, reclaimer, condensate cooler, water heater, and lines to the wash wheels. Flow surges and stops at each operation in the cycle. A pres- surized system depends on an adequate water service. = The vented system uses pumps from a vented (open) hot-water heater or tank to supply hot water. The tank's water level fluctuates from about 150 mm above the heating element to a point 300 mm from the top of the tank; this fluctuation defines the working vol- ume. The level drops for each machine fill, and makeup water runs continuously at the average flow rate and water service pressure during the complete washing cycle. The tank is sized to have full working volume at the beginning of each cycle. Lines and softeners may be sized for the average flow rate from the water service to the tank, not the peak machine fill rate as with a closed, pressurized system. Waste heat exchangers have continuous flow across the heating surface at a low flow rate, with continuous heat reclamation from the wastewater and flash steam. Automatic flow-regulating valves on the inlet water manifold control this low flow rate. Rapid fill of machines increases production (i.e., more batches can be processed). Heat Recovery. Commercial laundries are ideally suited for heat recovery because 58°C wastewater is discharged to the sewer. Fresh water can be conservatively preheated to within 8 K of the waste- water temperature for the next operation in the wash cycle. Regions with an annual average temperature of 13°C can increase to 50°C the initial temperature of fresh water going into the hot-water heater. For each litre or kilogram per hour of water preheated 37 K (13 to 50°C), heat reclamation and associated energy savings is 155 kW. Flash steam from a condensate receiving tank is often wasted to the atmosphere. Heat in this flash steam can be reclaimed with a suitable heat exchanger, to preheat makeup water to the heater by 5 to 10 K above the existing makeup temperature. Swimming Pools/ Health Clubs. The desirable temperature for swimming pools is 27°C. Most manufacturers of water heaters and boilers offer specialized models for pool heating; these include a pool temperature controller and a water bypass to prevent conden- sation. The water-heating system is usually installed before the return of treated water to the pool. A circulation rate to generate a change of water every 8 h for residential pools and 6 h for com- mercial pools is acceptable. An indirect heater, in which piping is embedded in the walls or floor of the pool, has the advantage of reduced corrosion, scaling, and condensation because pool water does not flow through the pipes, but its disadvantage is the high ini- tial installation cost. The installation should have a pool temperature control and a water pressure or flow safety switch. The temperature control should be installed at the inlet to the heater; the pressure or flow switch can be installed at either the inlet or outlet, depending on the manufacturer's instructions. It affords protection against inadequate water flow. Sizing should be based on four considerations: · Conduction through the pool walls · Convection from the pool surface · Radiation from the pool surface · Evaporation from the pool surface | {}
ba804533-634f-494d-9d78-43f600d6b060 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Service Water Heating 51.25 Except in aboveground pools and in rare cases where cold groundwater flows past the pool walls, conduction losses are small and can be ignored. Because convection losses depend on tempera- ture differentials and wind speed, these losses can be greatly re- duced by installing windbreaks such as hedges, solid fences, or buildings. Radiation losses occur when the pool surface is subjected to tem- perature differentials; these frequently occur at night, when the sky temperature may be as much as 45 K below ambient air temperature. This usually occurs on clear, cool nights. During the daytime, how- ever, an unshaded pool receives a large amount of radiant energy, often as much as 30 kW. These losses and gains may offset each other. An easy method of controlling nighttime radiation losses is to use a floating pool cover; this also substantially reduces evaporative losses. Evaporative losses constitute the greatest heat loss from the pool (50 to 60% in most cases). Ifit is possible to cut evaporative losses drastically, the pool's heating requirement may be cut by as much as 50%. A floating pool cover can accomplish this. A pool heater with an input great enough to provide a heat-up time of24 h would be the ideal solution. However, it may not be the most economical system for pools that are in continuous use during an extended swimming season. In this instance, a less expensive unit providing an extended heat-up period of as much as 48 h can be used. Pool water may be heated by several methods. Fuel-fired water heaters and boilers, electric boilers, tankless electric circula- tion water heaters, air-source heat pumps, and solar heaters have all been used successfully. Air-source heat pumps and solar heating systems are often used to extend a swimming season rather than to allow intermittent use with rapid pickup. The following equations provide some assistance in determining the area and volume of pools. Elliptical Area = 3.14AB A = Short radius B = Long radius Volume = Area x Average Depth Kidney Shaped Area = 0.45L (A+B) (approximately) L = Length A = Width at one end B = Width at other end Volume = Area x Average Depth Oval (for circular, set L = 0) Area = 3.14R2 + LW L = Length of straight sides W = Width or 2R R = Radius of ends Volume = Area x Average Depth Rectangular Area = LW L = Length W = Width Volume = Area x Average Depth The following is an effective method for heating outdoor pools. Additional equations can be found in Chapter 6. 1. Obtain pool water capacity, in cubic metres. 2. Determine the desired heat pickup time in hours. 3. Determine the desired pool temperature. Ifnot known, use 27°C. 4. Determine the average temperature of the coldest month of use. The required heater output It can now be determined by the fol- lowing equations: 91 = PcpV(tf- t⌀/0 x 3600 s/h where (14) 91 = pool heat-up rate, kW p = density of water = 998 kg/m3 = specific heat of water = 4,1868 kJ/(kg· K) cp = pool volume, m3 If desired temperature (usually 27°C) [i initial temperature of pool, °C 0 = pool heat-up time, h 92 = UA(tp -ta) (15) where 92 = heat loss from pool surface, kW U = surface heat transfer coefficient = 0.060 kW/(m2. K) A = pool surface area, m2 tp = pool temperature, °C ta = ambient temperature, °C It = 91 + 92 Notes: These heat loss equations assume a wind velocity of 5 to 8 km/h. For pools sheltered by nearby fences, dense shrubbery, or buildings, an average wind velocity of less than 5.6 km/h can be assumed. In this case, use 75% of the values calculated by Equation (15). For a velocity of 8 km/h, multiply by 1.25; for 16 km/h, mul- tiply by 2.0. (16) Because Equation (15) applies to the coldest monthly tempera- tures, results calculated may not be economical. Therefore, a value of one-half the surface loss plus the heat-up value yields a more viable heater output figure. Heater input then equals output divided by fuel source efficiency. Whirlpools and Spas. Hot-water requirements for whirlpool baths and spas depend on temperature, fill rate, and total volume. Water may be stored separately at the desired temperature or, more commonly, regulated at the point of entry by blending. If rapid filling is desired, provide storage at least equal to the volume needed; fill rate can then be varied at will. An alternative is to estab- lish a maximum fill rate and provide an instantaneous water heater that can handle the flow. Industrial Plants. Hot water (potable) is used in industrial plants for cafeterias, showers, lavatories, gravity sprinkler tanks, and industrial processes. Employee cleanup load is usually heaviest and not concurrent with other uses. Other loads should be checked before sizing, however, to be certain that this is true. Employee cleanup load includes (1) wash troughs or standard lavatories, (2) multiple wash sinks, and/or (3) showers. Hot-water requirements for employees using standard wash fixtures can be estimated at 3.8 L of hot water for each clerical and light-industrial employee per work shift and 7.6 L for each heavy-industrial worker. For sizing purposes, the number of workers using multiple wash fountains is disregarded. Hot-water demand is based on full flow for the entire cleanup period. This usage over a 10 min period is indi- cated in Table 13. The shower load depends on the flow rate of the shower heads and their length of use. Table 13 may be used to esti- mate flow based on a 15 min period. Water heaters used to prevent freezing in gravity sprinkler or water storage tanks should be part of a separate system. The load depends on tank heat loss, tank capacity, and winter design tempera- ture. Process hot-water load must be determined separately. Volume and temperature vary with the specific process. If the process load occurs at the same time as the shower or cafeteria load, the system must be sized to reflect this total demand. In some cases, it may be preferable to use separate systems, depending on the various load sizes and distance between them. Inc. ASHRAE, 2019 user. single for Licensed | {}
701af03e-061f-4b3e-8f32-0f406a3334fc | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 51.26 2019 ASHRAE Handbook-HVAC Applications (SI) Table 13 Hot-Water Usage for Industrial Wash Fountains and Showers ¦ Multiple Wash Fountains ¦ Multiple Wash Fountains ¦ Showers ¦ Showers ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Type ¦ L of 60°C Water Required for 10 min Perioda ¦ Flow Rate, mL/s ¦ L of 60°C Water Required for 15 min Periodb ¦ ¦ 910 mm Circular ¦ 150 ¦ 190 ¦ 110 ¦ ¦ Semicircular ¦ 83 ¦ 250 ¦ 150 ¦ ¦ 1370 mm Circular ¦ 250 ¦ 320 ¦ 185 ¦ ¦ Semicircular ¦ 150 ¦ 380 ¦ 220 ¦ aBased on 43°C wash water and 5°C cold water at average flow rates. bBased on 40°C shower water and 5°C cold water. Table 14 Water Heater Sizing for Ready-Mix Concrete Plant (Input and Storage Tank Capacity to Supply 65°C Water at 4°C Inlet Temperature) ¦ Truck Capacity, m3 ¦ Water Heater Storage Tank Volume, L ¦ Time Interval Between Trucks, min * ¦ Time Interval Between Trucks, min * ¦ Time Interval Between Trucks, min * ¦ Time Interval Between Trucks, min * ¦ Time Interval Between Trucks, min * ¦ Time Interval Between Trucks, min * ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Truck Capacity, m3 ¦ Water Heater Storage Tank Volume, L ¦ 50 ¦ 35 ¦ 25 ¦ 10 ¦ 5 ¦ 0 ¦ ¦ Truck Capacity, m3 ¦ Water Heater Storage Tank Volume, L ¦ Water Heater Capacity, kW ¦ Water Heater Capacity, kW ¦ Water Heater Capacity, kW ¦ Water Heater Capacity, kW ¦ Water Heater Capacity, kW ¦ Water Heater Capacity, kW ¦ ¦ 4.6 ¦ 1630 ¦ 134 ¦ 179 ¦ 230 ¦ 403 ¦ 536 ¦ 809 ¦ ¦ 5.7 ¦ 1860 ¦ 154 ¦ 205 ¦ 264 ¦ 463 ¦ 615 ¦ 923 ¦ ¦ 6.9 ¦ 2130 ¦ 174 ¦ 232 ¦ 299 ¦ 524 ¦ 697 ¦ 1049 ¦ ¦ 8.4 ¦ 2430 ¦ 201 ¦ 268 ¦ 344 ¦ 604 ¦ 803 ¦ 1207 ¦ *This table assumes 10 min loading time for each truck. Thus, for a 50 min interval between trucks, it is assumed that 1 truck/h is served. For 0 min between trucks, it is assumed that one truck loads immediately after the truck ahead has pulled away. Thus, 6 trucks/h are served. It also assumes each truck carries a 450 L storage tank of hot water for washing down at the end of dumping the load. This hot water is drawn from the storage tank and must be added to the total hot water demands. This has been included in the table. Ready-Mix Concrete. In cold weather, ready-mix concrete plants need hot water to mix the concrete so that it will not be ruined by freezing before it sets. Operators prefer to keep the mix at about 21°C by adding hot water to the cold aggregate. Usually, water at about 65°C is considered proper for cold weather. If the water tem- perature is too high, some of the concrete will flash set. Generally, 150 L ofhot water per cubic metre of concrete mix is used for sizing. To obtain the total hot-water load, this number is multiplied by the number of trucks loaded each hour and the capacity of the trucks. The hot water is dumped into the mix as quickly as possible at each loading, so ample hot-water storage or large heat exchangers must be used. Table 14 shows a method of sizing water heaters for concrete plants. Sizing Boilers for Combined Space and Water Heating When service water is heated indirectly by a space heating boiler, Figure 25 may be used to determine the additional boiler capacity required to meet the recovery demands of the domestic water-heating load. Indirect heaters include immersion coils in boilers as well as heat exchangers with space-heating media. Because the boiler capacity must meet not only the water supply requirement but also the space heating loads, Figure 25 indicates the reduction of additional heat supply for water heating if the ratio of water-heating load to space-heating loadis low. This reduction is pos- sible because · Maximum space-heating requirements do not occur at the time of day when the maximum peak hot-water demands occur. · Space-heating requirements are based on the lowest outdoor design temperature, which may occur for only a few days of the total heat- ing season. · An additional heat supply or boiler capacity to compensate for pickup and radiation losses is usual. The pickup load cannot occur at the same time as the peak hot-water demand because the building must be brought to a comfortable temperature before the occupants use hot water. Chart Type: line 0.25 0.50.75 1.0 2.0 3.0 4.0 5.0 item_01 0.0Fraction 0.6Fraction 0.8Fraction 0.85Fraction 0.9Fraction 0.95Fraction 1.0Fraction Fig. 25 Sizing Factor for Combination Heating and w ater-Heating Boilers ![image](/image/placeholder) TYPICAL HEATING TZ2 ZONE HEATING SPACE Tzィ T T B T C FLOW A CHECK T3 T T2 1 BOIL ER BOILER BOILER #1 #2 #3 C G C BOILERS -D D HEATING WATER T wh CIRCULATING PUMP INDIRECT-FIRED SERVICE WATER HEATER COLD WATER HOT WATER Fig.26 Typical Modular Boiler for Combined Space and Water Heating The factor obtained from Figure 25 is multiplied by the peak water-heating load to obtain the additional boiler output capacity required. For reduced standby losses in summer and improved efficiency in winter, step-fired modular boilers may be used. Units not in operation cool down and reduce or eliminate jacket losses. Heated boiler water should not pass through an idle boiler. Figure 26 shows a typical modular boiler combination space- and water-heating arrangement. Typical Control Sequence for Indirect Water Heaters 1. Any control zone or indirectly fired water heater thermostat (e.g., In or Twh Figure 26) starts its circulating pump and supplies in power to boiler no. 1 control circuit. 2. If T1 is not satisfied, burner is turned on, boiler cycles as long as any circulating pump is on. 3. If after 5 min TA is not satisfied, V1 opens and boiler no. 2 comes on line. 4. If after 5 min TB is not satisfied, V2 opens and boiler no. 3 comes on line. 5. If Tc is satisfied and two boilers or fewer are firing for a minimum of 10 min, V2 closes. 6. If TB is satisfied and only one boiler is firing for a minimum of 10 min, V1 closes. 7. If all circulating pumps are off, boiler no. 1 shuts down. Inc. ASHRAE, 2019 user. single for Licensed | {}
909c9045-a2f1-4c00-911b-1b64e67cc175 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Service Water Heating 51.27 Table 15 Needed Tankless Water Heater Output Heat Rates, kW* ¦ Flow Rate, mL/s ¦ Temperature Rise ¦ Temperature Rise ¦ Temperature Rise ¦ Temperature Rise ¦ Temperature Rise ¦ Temperature Rise ¦ Temperature Rise ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Flow Rate, mL/s ¦ 6 K ¦ 14 K ¦ 28 K ¦ 31 K ¦ 42 K ¦ 43 K ¦ 56 K ¦ ¦ 6.3 ¦ 0.15 ¦ 0.37 ¦ 0.74 ¦ 0.81 ¦ 1.11 ¦ 1.14 ¦ 1.48 ¦ ¦ 31.5 ¦ 0.74 ¦ 1.85 ¦ 3.69 ¦ 4.06 ¦ 5.54 ¦ 5.69 ¦ 7.39 ¦ ¦ 63.1 ¦ 1.48 ¦ 3.69 ¦ 7.39 ¦ 8.12 ¦ 11.1 ¦ 11.4 ¦ 14.8 ¦ ¦ 94.6 ¦ 2.22 ¦ 5.54 ¦ 11.1 ¦ 12.2 ¦ 16.6 ¦ 17.1 ¦ 22.2 ¦ ¦ 126 ¦ 2.95 ¦ 7.39 ¦ 14.8 ¦ 16.2 ¦ 22.2 ¦ 22.8 ¦ 29.5 ¦ ¦ 158 ¦ 3.69 ¦ 9.23 ¦ 18.5 ¦ 20.3 ¦ 27.7 ¦ 28.4 ¦ 36.9 ¦ ¦ 189 ¦ 4.43 ¦ 11.1 ¦ 22.2 ¦ 24.4 ¦ 33.2 ¦ 34.1 ¦ 44.3 ¦ ¦ 221 ¦ 5.17 ¦ 12.9 ¦ 25.8 ¦ 28.4 ¦ 38.8 ¦ 39.8 ¦ 51.7 ¦ ¦ 252 ¦ 5.91 ¦ 14.8 ¦ 29.5 ¦ 32.5 ¦ 44.3 ¦ 45.5 ¦ 59.1 ¦ ¦ 284 ¦ 6.65 ¦ 16.6 ¦ 33.2 ¦ 36.6 ¦ 49.9 ¦ 51.2 ¦ 66.5 ¦ ¦ 315 ¦ 7.39 ¦ 18.5 ¦ 36.9 ¦ 40.6 ¦ 55.4 ¦ 56.9 ¦ 73.9 ¦ ¦ 379 ¦ 8.86 ¦ 22.2 ¦ 44.3 ¦ 48.7 ¦ 66.5 ¦ 68.2 ¦ 88.6 ¦ ¦ 442 ¦ 10.3 ¦ 25.8 ¦ 51.7 ¦ 56.9 ¦ 77.5 ¦ 79.6 ¦ 103.4 ¦ ¦ 505 ¦ 11.8 ¦ 29.5 ¦ 59.1 ¦ 65.0 ¦ 88.6 ¦ 91.0 ¦ 118.2 ¦ ¦ 568 ¦ 13.3 ¦ 33.2 ¦ 66.5 ¦ 73.1 ¦ 99.7 ¦ 102.4 ¦ 132.9 ¦ ¦ 631 ¦ 14.8 ¦ 36.9 ¦ 73.9 ¦ 81.2 ¦ 110.8 ¦ 113.7 ¦ 147.7 ¦ *Divide table values by input efficiency to determine required heat input rate. ASHRAE/IES Standards 90.1 and 90.2 discuss combination ser- vice water-heating/space-heating boilers and establish restrictions on their use. The ASHRAE/IES Standard 100 section on Service Water Heating also has information on this subject. Sizing Tankless Water Heaters Although tankless water heaters are sometimes also referred to as instantaneous water heaters, in this chapter the two types are dis- tinct. Larger instantaneous water heaters for bigger commercial, institutional, and industrial applications may still have some water storage tank volume, even though their ratio of heating rate divided by storage volume is large. Smaller commercial and residential sys- tems only contain a volume of water sufficient to fill the chambers or tubing where the heating is done; they do not incorporate storage tanks, and are truly tankless as the term is used here. Tankless water heaters offer potential efficiency advantages over tank-type units for several reasons. Because they do not store heated water, they have low standby energy loss (typically, only a small amount of electricity to run controls). This energy savings potential can be significant for low-use applications. Another potential ad- vantage is that the lack of a storage tank means they are much smaller than tank-type units and can more easily be located close to points of use (especially electric tankless units). Locating units close to points of use reduces energy losses in the hot-water distri- bution system, sometimes substantially. This ease of positioning may also make it easier to use more than one water heater, reducing hot-water distribution system heat losses still further by eliminating even more piping. There are many good applications of both electric and fossil- fired tankless water heaters in residences, commercial, institutional, and industrial settings. Tankless water heaters are especially useful for providing more localized heating in point-of-use or near-point- of-use applications because they do not take up much space. In gen- eral, tankless water heaters are designed to completely heat cold water in one pass through the heater. There are exceptions, however, because some models with advanced controls can also heat pre- warmed water by controllable amounts. See the discussion below about modulating heat input rates. Tankless water heaters generally have some sort of flow detection method (e.g., a flow switch or method of differential temperature measurement that indicates flow is occurring). Water heating only begins once water flow is confirmed. Outlet temperature from tank- less water heaters is determined by the flow rate, entering cold-water temperature, and applied heating rate. Simpler systems do not actively control outlet temperature, other than to turn off the heat input if exit temperature exceeds a set value. These systems are more likely to specify the use of water flow restrictors to restrict flow through the units to minimize undesirably cool water exiting the units. Systems with more advanced controls continuously monitor the exit water temperature and modulate the heat input and/or water flow rate to maintain the specified outlet temperature. Advanced electric tankless water heaters modulate power to the heating ele- ments, either in steps (multiple heating elements) or by varying the voltage and/or current supplied to the heating elements, or both. Advanced fossil-fired tankless water heaters, which are available in both natural-gas- and propane-fired versions, modulate the heating rate by either modulating heat input in steps (e.g. using multiple burners), or by modulating gas flow rate to the burner(s), or some combination of the two. These designs can be used as booster heat- ers or in recirculated heating systems (i.e., they can work well with prewarmed entering water temperatures) because they can better control exit temperature. One of the most important tankless water heater sizing consider- ations is having adequate heat input rate to heat the desired flow rate of water by a temperature rise needed to make the water warm enough to use. Table 15 shows the necessary heat input rate (not considering heat input efficiency: divide table values by heat input efficiency in decimal form [e.g., 0.8 for some fossil-fired heaters]) to determine total energy input rate required for tankless water heaters versus flow rate and needed temperature rise. The heating rates shown are computed using Equation (1). Note that 40°C is about the minimum acceptable temperature for human use at fixtures. Accounting for heat loss in piping and/or when atomizing droplets in a showerhead, 43°C is a more typical requirement. The needed temperature rise in a cold climate where the entering cold-water temperature may be 2°C would thus be 43°C -2°C = 41 K; in a warm climate where the entering cold water temperature may be 29°C, the temperature rise would be 43°C - 29°C = 14 K. For comparison, the temperature rise specified in the U.S. federal water heater testing and rating procedure is 57°C - 14°C = 43°C. For reference, typical flow rate ranges are as follows: · Hand-washing sinks: 0.01 to 0.6 L/sec · Showers: 0.05 to 0.16 L/s · Bathtub fill rates: 0.06 to 0.38 L/s · Dishwasher fill rates: 0.06 to 0.19 L/s Inc. ASHRAE, 2019 user. single for Licensed | {}
3a72a93a-7381-4bfb-b1ae-1a60ce213d0b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 51.28 2019 ASHRAE Handbook- -HVAC Applications (SI) Table 16 Hot- Water Demand in Fixture Units (60°C Water) ¦ ¦ Apartments ¦ Club ¦ Gymnasium ¦ Hospital ¦ Hotels and Dormitories ¦ Industrial Plant ¦ Office Building ¦ School ¦ YMCA ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Basin, private lavatory ¦ 0.75 ¦ 0.75 ¦ 0.75 ¦ 0.75 ¦ 0.75 ¦ 0.75 ¦ 0.75 ¦ 0.75 ¦ 0.75 ¦ ¦ Basin, public lavatory ¦ ¦ 1 ¦ 1 ¦ 1 ¦ 1 ¦ 1 ¦ 1 ¦ 1 ¦ 1 ¦ ¦ Bathtub ¦ 1.5 ¦ 1.5 ¦ ¦ 1.5 ¦ 1.5 ¦ ¦ ¦ ¦ ¦ ¦ Dishwasher* ¦ 1.5 Five fixture units per 250 seating capacity ¦ 1.5 Five fixture units per 250 seating capacity ¦ 1.5 Five fixture units per 250 seating capacity ¦ 1.5 Five fixture units per 250 seating capacity ¦ 1.5 Five fixture units per 250 seating capacity ¦ 1.5 Five fixture units per 250 seating capacity ¦ 1.5 Five fixture units per 250 seating capacity ¦ 1.5 Five fixture units per 250 seating capacity ¦ 1.5 Five fixture units per 250 seating capacity ¦ ¦ Therapeutic bath ¦ ¦ 5 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Kitchen sink ¦ 0.75 ¦ 1.5 ¦ ¦ 3 ¦ 1.5 ¦ 3 ¦ ¦ 0.75 ¦ 3 ¦ ¦ Pantry sink ¦ ¦ 2.5 ¦ ¦ 2.5 ¦ 2.5 ¦ ¦ ¦ 2.5 ¦ 2.5 ¦ ¦ Service sink ¦ 1.5 ¦ 2.5 ¦ ¦ 2.5 ¦ 2.5 ¦ 2.5 ¦ 2.5 ¦ 2.5 ¦ 2.5 ¦ ¦ Shower ¦ 1.5 ¦ 1.5 ¦ 1.5 ¦ 1.5 ¦ 1.5 ¦ 3.5 ¦ ¦ 1.5 ¦ 1.5 ¦ ¦ Circular wash fountain ¦ ¦ 2.5 ¦ 2.5 ¦ 2.5 ¦ ¦ 4 ¦ ¦ 2.5 ¦ 2.5 ¦ ¦ Semicircular wash fountain ¦ ¦ 1.5 ¦ 1.5 ¦ 1.5 ¦ ¦ 3 ¦ ¦ 1.5 ¦ 1.5 ¦ Note: Data predate modern low-flow fixtures and appliances. *See Water-Heating Terminology section for definition of fixture unit. · Clothes-washing machine fill rates: 0.06 to 0.38 L/s · Residential whole-house recurring peak rates: around 0.19 to 0.25 L/s · Residential whole-house severe-peak flow rates: 0.38 to 0.5 L/s As can be seen from Table 15, whole-house tankless water heaters need to be able to provide heating rates on the order of22 to 44 kW in all but the warmest climates. Note, however, that in single- family residential applications, users have the opportunity to learn what works and what does not, and are likely to adjust their hot- water use habits somewhat to obtain adequately hot water from whatever water-heating system is used. They could do this for ex- ample, by avoiding hot-water use from multiple fixtures simultane- ously, and reducing demanded flow rates. An important issue in the sizing of tankless water heaters is thus what peak hot-water energy rate load to design for. It is generally acceptable to design the water-heating system to meet a peak hot- water load (in terms of energy rate needed, not just water flow rate needed) that is not exceeded by 97.5% of all draws. The difficulty in sizing whole-house tankless water heaters comes in predicting how draws will coincide to create the peak energy demand rate. This peak coincident energy demand rate must be estimated by the person sizing the system, because ASHRAE does not currently have a statistically valid amount of data on peak residential water/energy flow rates with which to make recommendations. However, research (Buchberger et.al. 2015) has for the first time provided hot- water draw information from a statistically large number of residential test sites, allowing estimation of probabilities of various types of draws occurring versus time of day, probabilities of how such draws may overlap in time within and between households, and normal ranges of flow rates and total volumes for the various types of draws. Sizing recommendations are easier with storage- type water heaters because their sizing is done more based on inte- grated total energy requirements, and is not highly dependent on knowledge of peak flow rates. An issue related to proper sizing of tankless water heaters is the size of fuel piping and electrical service needed. Because gas-fired tankless water heaters must have significantly higher fuel burn rates than typical tank-types, larger gas piping may be required. The same is true for electric tankless water heaters, where a whole-house unit may require larger wiring and often additional (multiple) circuit breakers. Consequently, large tankless water heaters, both gas and electric, can in some cases require a service entrance upgrade. Nota- bly, diversified electrical demand for large numbers of electric tank- less water heaters is not much different (generally a little lower) than tank types, because of the lower number of tankless water heaters that are on at any point in time compared to tank types. However, as number of users on an electrical line decreases, demand diversity decreases, which can result in increased electrical demand com- pared to tank types as the number of users on the line decreases to fairly few. The number that "few" represents varies with size of the tankless units. Hiller (201 7) found that diversified electrical demand of 28 kW tankless water heaters in residences was similar to that of 4.5 kW storage water heaters when number of households exceeded 2 to 15, depending on averaging time interval. Sizing Instantaneous and Semi-Instantaneous Water Heaters The methods for sizing storage water-heating equipment should not be used for instantaneous and semi-instantaneous heaters. The following is based on the Hunter (1941) method for sizing hot- and cold-water piping, with diversity factors applied for hot water and various building types. Fixture units (Table 16) are assigned to each fixture using hot water and totalled. Maximum hot-water demand is obtained from Figures 27 or 28 by matching total fixture units to the curve for the type of building. Special consideration should be given to applica- tions involving periodic use of shower banks, process equipment, laundry machines, etc., as may occur in field houses, gymnasiums, factories, hospitals, and other facilities. Because these applications could have all equipment on at the same time, total hot-water capac- ity should be determined and added to the maximum hot-water demand from the modified Hunter curves. Often, the temperature of hot water arriving at fixtures is higher than is needed, and hot and cold water are mixed together at the fixture to provide the desired temperature. Equation (17), derived from a simple energy balance on mixing hot and cold water, shows the ratio of hot-water flow to desired end- use flow for any given hot, cold, and mixed end-use temperatures. Hot-water flow rate = (Mixed-temperature flow rate)( T - Tcold) mixed (T hot cold) - T Once the actual hot-water flow rate is known, the heater can then be selected for the total demand and total temperature rise required. For critical applications such as hospitals, multiple heaters with 100% reserve capacity are recommended. Consider multiple heaters for buildings in which continuity of service is important. The minimum recommended size for semi-instantaneous heaters is 0.65 L/s, except for restaurants, for which it is 0.95 L/s. When system flow is not easily determined, the heater may be sized for full flow ofthe piping system at a maximum speed of3 m/s. Heaters with low flows must be sized carefully, and care should be taken in the esti- mation of diversity factors. Unusual hot-water requirements should be analyzed to determine whether additional capacity is required. One example is a dormitory in a military school, where all showers and lavatories are used simultaneously when students return from a (17) Inc. ASHRAE, 2019 user. single for Licensed | {}
d71996ae-471f-4032-a69e-c5b8545fa055 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Service Water Heating 51.29 Chart Type: line CURVE A CURVE B CURVE C SEE ENLARGED SCALE (Figure 26) item_01 1000mL/s 1500mL/s 2000mL/s 2500mL/s 3000mL/s CURVE A: RESTAURANTS CURVE B: HOSPITALS, NURSING HOMES, NURSES' RESIDENCES, DORMITORIES, HOTELS, AND MOTELS CURVE C: APARTMENTS AND HOUSES CURVE D: OFFICE BUILDINGS, ELEMENTARY AND HIGH SCHOOLS Fig. 27 Modified Hunter Curve for Calculating Hot- Water Flow Rate (Data predate modern low-flow appliances.) Chart Type: line CURVE A CURVE B CURVE C CURVE D item_01 5L/s 3L/s 3L/s 4L/s CURVE A: RESTAURANTS CURVE B: HOSPITALS, NURSING HOMES, NURSES' RESIDENCES, DORMITORIES, HOTELS, AND MOTELS CURVE C: APARTMENTS AND HOUSES CURVE D: OFFICE BUILDINGS, ELEMENTARY AND HIGH SCHOOLS Fig. 28 Enlarged Section of Figure 27 (Modified Hunter Curve) (Data predate modern low-flow appliances.) drill. In this case, the heater and piping should be sized for full system flow. Whereas the fixture count method bases heater size of the diver- sified system on hot-water flow, hot-water piping should be sized for full flow to the fixtures. Recirculating hot-water systems are adaptable to instantaneous heaters. To make preliminary estimates of hot-water demand when the fixture count is not known, use Table 17 with Figure 27 or Figure 28. The result is usually higher than the demand determined from the actual fixture count. Actual heater size should be determined from Table 16. Hot-water consumption over time can be assumed to be the same as that in the section on Hot- Water Requirements and Storage Equipment Sizing. Example 10. A 600-student elementary school has the following fixture count: 60 public lavatories, 6 service sinks, 4 kitchen sinks, 6 showers, Table 17 Preliminary Hot-Water Demand Estimate ¦ Type of Building ¦ Fixture Units ¦ ¦ --- ¦ --- ¦ ¦ Hospital or nursing home ¦ 2.50 per bed ¦ ¦ Hotel or motel ¦ 2.50 per room ¦ ¦ Office building ¦ 0.15 per person ¦ ¦ Elementary school ¦ 0.30 per student* ¦ ¦ Junior and senior high school ¦ 0.30 per student* ¦ ¦ Apartment house ¦ 3.00 per apartment ¦ *Plus shower load (in fixture units). and 1 dishwasher at 0.5 L/s. Determine the hot-water flow rate for siz- ing a semi-instantaneous heater based on the following: a. Estimated number of fixture units b. Actual fixture count Solution: a. Use Table 17 to find the estimated fixture count: 600 students x 0.3 fix- ture units per student = 180 fixture units. As showers are not included, Table 16 shows 1.5 fixture units per shower x 6 showers = 9 additional fixture units. The basic flow is determined from curve D of Figure 28, which shows that the total flow for 189 fixture units is 1.4 L/s. b. To size the unit based on actual fixture count and Table 16, the calcu- lation is as follows: ¦ 60 ¦ public lavatories ¦ x 1.0 FU = ¦ 60 FU ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ 6 ¦ service sinks ¦ x 2.5 FU = ¦ 15 FU ¦ ¦ 4 ¦ kitchen sinks ¦ x 0.75FU = ¦ 3 FU ¦ ¦ 6 ¦ showers ¦ x 1.5 FU = ¦ 9 FU ¦ ¦ ¦ Subtotal ¦ ¦ 87 FU ¦ At 87 fixture units, curve D of Figure 28 shows 1.0 L/s, to which must be added the dishwasher requirement of 0.54 L/s. Thus, the total flow is 1.54 L/s. Comparing the flow based on actual fixture count to that obtained from the preliminary estimate shows the preliminary esti- mate to be slightly lower in this case. It is possible that the prelim- inary estimate could have been as much as twice the final fixture count. To prevent oversizing of equipment, use the actual fixture count method to select the unit. Sizing Refrigerant-Based Water Heaters Refrigerant-based heat pump water heaters (HPWHs) comprised of air-source, water-source, direct geoexchange, and sorption types of equipment are sized in a different manner than conventional sys- tems because · The variable nature ofthe heat source (air, water, and ground tem- peratures) depends on the geographic location of the application and the season of the year. HPWH manufacturers provide perfor- mance data and sizing information that take these factors into account. · To reduce first costs, heat pump water heaters benefit from a greater ratio of storage tank capacity per unit of energy input than for conventional water heaters. To achieve the lowest total system cost and the highest system efficiency, the HPWH system designer generally specifies the smallest-capacity HPWH consistent with an annual average of 12 to 18 h daily run time combined with the appropriately sized storage tank for the application. This means that part of the year the HPWH runs continuously. For air-source, water-loop, groundwater, and sorption-type HPWH systems, daily run times of up to 24 h are not uncommon. In many heat pump based systems, a conventional gas or electric commercial water heater is placed downstream in series to act as a reserve water heater. The conventional heater enables a continuous supply of hot water if the HPWHs need to be shut down for maintenance. Another strategy is to size the HPWH smaller for longer run times, thus saving on Inc. ASHRAE, 2019 user. single for Licensed | {}
6c9cee70-4cd3-4197-a490-84aaa2e267f6 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 51.30 2019 ASHRAE Handbook-HVAC Applications (SI) purchase and installation costs to meet a portion of the total daily load and use conventional heaters to meet the rest of the load and peak loads. When sizing for redundancy, the HPWH portion of the system can have multiple HPWHs and storage tanks in flow parallel, but when additional conventional water heaters are also provided (nor- mally to help serve peak hot water loads or provide back-up heating capacity) the cluster of conventional water heaters (which can be in flow parallel with each other) should be in flow series with but downstream of the cluster of HPWHs. Figure 29 shows an example HPWH system plumbing arrangement. Condensing fossil-fired water heaters can also operate more efficiently if configured in this manner, because they receive colder inlet water temperatures. 10. WATER-HEA TING ENERGY USE Energy use in water-heating systems includes the following fac- tors, not all of which apply in a given type of system (Hiller 2006c): · Qwater is energy content in water actually used, relative to entering cold-water temperature. is standby heat loss from water heater storage tank; it is · Qtank loss proportional to time and temperature difference between water in tank and surroundings. is energy loss from on/off cycling of heat input · �cycling loss device, where energy invested in mass of heating device (e.g., heat exchanger) and water in it is lost to surroundings after device turns off; loss is proportional to number ofheating cycles (e.g., in a tankless instantaneous water heater). Some fossil- fuel-fired tankless water heaters have pre- and/or postfiring combustion air blower operation to purge combustion products from combustion chamber, which can cause very rapid loss of invested energy in heat exchanger. · �piping is heat energy lost from piping while water is flowing; note that, on recirculation-loop systems, heat is lost from both supply and return piping. is heat energy lost from piping after flow ceases; note · �cooldown exhibits a large step increase once water in a pipe that Q cooldown cools to below a usable temperature, because remaining warm water in pipe must be dumped to drain before usable hot water can again be obtained at fixtures; time spacing between draws and pipe insulation levels thus strongly influence this energy loss. is energy that must be provided to reheat an amount of · �dump water equal to that dumped down the drain while waiting for hot water to arrive at fixtures; knowing the time spacing between draws in nonrecirculated piping systems is very important. · Input efficiency ni (tank-type water heater) or thermal effi- ciency 7, (tankless water heater or heating device external to tank) of heating device must be considered when calculating total water-heating system energy use. is energy used to move water within system, if · Q circulating pump done with pumps. There are often multiple circulating pumps in ![image](/image/placeholder) HOT COLD RL RETURN HPWH (TYP.) Fig. 29 Example Plumbing ofHPWH and Conventional w ater Heating System system (e.g., to circulate water from storage tanks to heating devices, recirculation-loop pumps). · �parasitics is energy to operate fans, blowers, controls, and other devices. · �supply. is energy used to deliver potable water to system and force it through system. Includes pumping energy for well pumps or city water supply pumps, and water treatment system energy. is energy used to treat and dispose of waste water, · �disposal including pumping energy and other treatment system energy. Total piping system energy use is thus Qtotal = Q water/ni + Qtank loss /mi + �cycling loss �piping/Mi + /ni + Qcirculating pump + 0 cooldown /ni + �dump + 0 parasitics �supply + �disposal + Additional energy use terms may apply in some water-heating systems. The following simple examples demonstrate how to compute water-heating system energy use for different system types and draw patterns. Assumptions for Examples 1 1 to 14 include the following: · Two fixtures 30 m apart · Six 5 min long draws per day of0.065 L/s, 40°C water at each fix- ture, spaced 3 min apart compared to 4 h apart · Water heater output temperature of 50°C · Tank-type fossil-fuel-fired water heater with input efficiency ni = 0.80 and a uniform energy factor (UEF) of 0.59, yielding UA tank W/K, including energy input efficiency (note that = 6 tank heat loss rate is a function of UEF rating, not tank size. However, for equal amounts of insulation, smaller tanks have higher UEF rating) · Tair = 20°C for both piping and tank · Tcold temperature = 14.5°C entering cold-water · Supply piping is 20 mm rigid copper with 13 mm thick foam insu- lation (Mcp)w.p.i = 1.58 kJ/(m · K), (from Table - ) pipe volume = 0.3122 L/m · Return piping is 13 mm rigid copper with 13 mm thick foam insu- lation (RL system only) · For simplicity, neglect short lengths of piping between fixture branch piping and main recirculation-loop piping (or tank if at location of fixture) · For simplicity, neglect supply and disposal energy, recirculating pump energy, and other parasitics. Example 11. Assume a continuously running hot-water recirculation-loop system with an allowed loop temperature drop to the farthest fixture of 3 K, and assuming one fixture is near the water heater. Note that because this is a continuously running recirculation-loop system, time spacing between draws is unimportant because the supply and return piping are always hot. Solution: First, compute the recirculation loop flow rate needed to prevent temperature dropping below 47°C, using Equations (1) to (4) and (9). (50-20°C)- (47-20°C) ATIm = = 28.47 K ln[(50 - 20°C)/(47-20°C)] UAflowing supply = 0.433 W/(m· K) (from Table 1) �piping supply = [0.433 W/(m·K)](30 m)(28.47 K)/0.8 = 462.28 W = (462.28 J/s)(60 s/min)(60 min/h)(24 h/day) = 39 940 kJ/day Inc. ASHRAE, 2019 user. single for Licensed | {}
79816cfa-bf86-472a-a035-f3bcabee99ee | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Service Water Heating 51.31 (462.28 W)(0.8) m circulating pump (1 kg/L)[4186.8 J/(kg·K)](3 K) = 0.029 L/s UAflowing return W/(m·K) (from Table 1 ) = 0.346 [0.346 W/(m-K)](30 m) (0.029 L/s)(1 kg/L)[4186.8 J/(kg·K)] T hot return out (47 - 20°C)e = 20°C+ = 44.8°C �piping return (0.029 L/s)(1 kg/L)[4.1868 kJ/(kg·K)] = x(47-44.8°C)/0.8 = (336 J/s)(60 s/min)(60 min/h)(24 h/day) = 28 858 kJ/day Next, determine the amount of hot water mixed with cold water to deliver the 40°C fixture delivery temperature, from Equation (24). For the fixture at the water heater, = (0.065 L/s)(40 - 14.5°C)/(50 - 14.5°C) = 0.047 L/s mhot near And for the far fixture, = (0.065 L/s)(40 - 14.5°C)/(47 - 14.5°C) = 0.051 L/s mhot far Consequently, Q water near (0.047 L/s)(1 kg/L)[4.1868 kJ/(kg·K)](50 - 14.5°C) = x (60 s/min)(5 min/draw)(6 draws/day)/0.8 = 15 692 kJ/day Q water far L/s)(1 kg/L)[4.1868 kJ/(kg-K)](47- 14.5°C) = (0.051 x (60 s/min)(5 min/draw)(6 draws/day)/0.8 = 15 589 kJ/day This is the same as for the near fixture, as it should be, because piping heat loss is separately computed. Q tank heat loss (6 W/K)(50 - 20°C)(60 s/min)(60 min/h) = x (24 h/day) = 15 552 kJ/day Thus, �total RL system = 39 940 + 28 858 + 15 692 + 15 589 + 15 552 115 631 kJ/day With the recirculation system, energy use is the same regardless of draw spacing. Example 12. Assume a nonrecirculated piping system, one fixture at water heater, draws 3 min and 4 h apart. Solution: First, determine the steady-state delivery temperature at the far fixture, and the actual hot-water flow rate to that fixture. This requires iteration: guessing an initial piping outlet temperature, calcu- lating an estimated hot-water flow rate using Equation (17), and then calculating a new piping outlet temperature based on the calculated flow rate. Guess Thot out 1 50°C. Then, = (0.065 L/s)(40 - 14.5°C) = mhot 1 (50-14.5°C) = 0.047 L/s [from Equation (17)] Thot out 2 47°C [from Equation (2), where = UAflowing = 0.433 W/(m·K), L = 30 m] (0.065 L/s)(40-14.5°C) mhot2 = = 0.051 L/s (47-14.5°C) Thot out 3 = 47.1°C (0.065 L/s)(40- 14.5°C) = = 0.0508 L/s mhot 3 14.5°C) (47.1 - Thot out 4 47.11°C = Thus, 0 water far piping + 0 = (0.0508 L/s)(1 kg/L)[4186.8 J/(kg·K)] x (50 - 14.5°C)(60 s/min)(5 min/draw) x (6 draws/day)/0.8 = 16 989 kJ/day Note that, in this computation, water energy and piping flowing heat loss energy are calculated together for simplicity. Q water near Example 11 = 15 692 kJ/day = same as in Next, compute the pipe temperature at the end ofboth the 3 min and 4 h cooldown (cd) periods, accounting for the different draw spacing scenarios. For simplicity, base the heat loss calculations on an average pipe temperature of (50 + 47.11°C)/2 = 48.6°C. Using UA zero flow W/(m·K) from Table 1, and Equation (8), = 0.26 [0.26 W/(m-K)](3 min)(60 s/min) [1,584 kJ/(m-K)](1000 J/kJ) Tpipe 3 min (48.6 - 20° C)e = 20°C + = 47.76°C $$=47.76^{\circ}\mathrm{c}$$ and Tpipe 4 h 22.67°C = The pipe does not cool below a usable temperature with the 3 min draw spacing, but it does with the 4 h draw spacing. This means that, for the 3 min draw spacing, there are five draws with small amounts of piping cooldown between draws plus one complete cooldown for the last draw of the day, whereas for the 4 h draw spacing, there are six complete cooldowns that result in dumping water in the pipe to drain at the next draw. Because pipe length to the fixture at the water heater is essentially zero under the assumptions here, only draws at the far fix- ture result in piping energy loses. From Equation (5), 2cd 3 min J/(m-K)](30 m)(48.6 -47.76°C) = [1584 x 5 cd/day/0.8 + 1 cd (lumped into �dump) = 249.48 kJ/day To estimate Qdump and the amount of water waste, assume an AF/ PV ratio of 1.5. Thus, each time the pipe cools below a usable tempera- ture, (1.5)(0.3122 L/m)(30 m) = 14.0 L of water must be dumped to drain. 2dump 3 min dump/day)(14.0 L/dump)(1 kg/L) = (1 x [4.1868 kJ/(kg·K)](50 - 14.5°C)/0.8 = 2601 kJ/day �dump 4 h (6 dumps/day)(2601 kJ/dump) = 15 606 kJ/day = and Inc. ASHRAE, 2019 user. single for Licensed Qcd4h = 0 because all cooldown energy is lumped into 2dump. Qtank heat loss kJ/day, as in Example 11 = 18 400 To simplify calculation of total water-heating system energy use, it is convenient to add the cooldown energy term computed as shown to the Qwater term calculated as if all hot water were delivered to the fix- ture at a constant flow rate and the steady-state temperature. In reality, the hot-water flow rate to the fixture varies during the initial part of a draw as the cooled but still usable water temperature increases to the | {}
460ecfe1-2117-439d-8786-df42aa917520 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 51.32 2019 ASHRAE Handbook- -HVAC Applications (SI) Table 18 Results Comparisons for Examples 11 to 14 ¦ ¦ 3 min Draw Spacing ¦ 3 min Draw Spacing ¦ 3 min Draw Spacing ¦ 4 h Draw Spacing ¦ 4 h Draw Spacing ¦ 4 h Draw Spacing ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ System Type ¦ Energy Use, kJ/day ¦ Energy Use Compared to One Tank, % ¦ Water Waste, L/day ¦ Energy Use, kJ/day ¦ Energy Use Compared to One Tank, % ¦ Water Waste, L/day ¦ ¦ Recirculation loop ¦ 118 479 ¦ 231 ¦ 0 ¦ 118 479 ¦ 184 ¦ 0 ¦ ¦ One-tank ¦ 53 930 ¦ 100 ¦ 14 ¦ 66 687 ¦ 100 ¦ 85.6 ¦ ¦ Two-tank (large) ¦ 68 184 ¦ 123 ¦ 0 ¦ 68 184 ¦ 98 ¦ 0 ¦ ¦ Two-tank (small) ¦ 58 341 ¦ 115 ¦ 0 ¦ 58 341 ¦ 92 ¦ 0 ¦ steady-state value as flow progresses. The energy use thus computed will be mathematically correct either way. Qtotal non-RL, 3 min spacing = 16 989 + 15 692 + 248 + 2601 + 18 400 = 53 930 kJ/day Qtotal non-RL, 4 h spacing = 16 989 + 15 692 + 0 + 15 606 + 18 400 = 66 687 kJ/day Note the large increase in energy use when draws are spaced far enough apart for the pipe to cool to below a usable temperature between draws. Also, the time spent waiting for hot water to arrive at the far fixture is twait L)/(0.065 L/s) = 215 s = 3.59 min = (14 Example 13. Assume two full-sized water heaters, one at each fixture; no piping. Solution: In this case, tank heat loss is doubled, but piping heat loss is eliminated. Qwater = (2)(15 692 kJ/day) = 31 384 kJ/day Qiank heat loss (2)(18 400 kJ/day) = 36 800 kJ/day = Qtotal 2-tank 36 800 = 68 184 kJ/day = 31 384 + Draw spacing is irrelevant to the two-tank system because there is no piping. Example 14. Assume two smaller water heaters, one at each fixture; no piping. Solution: When two separate water heaters are used, each can be smaller than if one water heater were used. Assuming a smaller tank- type fossil-fuel-fired water heater with input efficiency 11 = 0.80 and a UEF of 0.61, yielding UA tank = 5.2 W/K, including energy input effi- ciency, Qwater = (2)(15 692 kJ/day) = 31 384 kJ/day 0 tank heat loss (2)(5.2 W/K)(50 - 20°C)(60 s/min) = x (60 min/h)(24 h/day) = 26 957 kJ/day Qtotal 2-tank kJ/day = 31 384 + 26 957 = 58 341 Again, draw spacing is irrelevant to the two-tank system because there is no piping. Table 18 compares water and energy use of Examples 11 to 14, and shows that the continuously running recirculation-loop system uses substantially more energy than the other approaches (on the order of twice as much). This is not uncommon. Also note that, in these examples, the two-tank approach saves both water waste and energy. The multiple-water-heater approach has at worst only a small negative energy effect if done properly, and under real water draw scenarios usually uses less energy than other options. This is why multiple-water-heater design options should always be considered. In some cases, multiple-water-heater systems can have lower first costs than alternatives. Note that multiple-water-heater systems can use different types of water heaters for different parts of the system: fossil-fuel-fired or heat pump water heaters can be used to serve larger loads, whereas electric resistance water heaters may be pre- ferred for serving smaller loads. In some cases, space limitations, life and maintenance issues, and other factors may make multiple-water- heater systems unattractive. Both simplified and detailed computer models (Hiller 1992, 2000) are available to help calculate water heater energy use. These are especially useful for analyzing the energy used by heat pump water heaters, where efficiency and heating capacity vary strongly with both source (e.g., air, water) and sink (water) temperature. Computer models are also under development to compute water and energy waste associated with hot-water distribution systems. 11. HEAL TH AND SAFETY Legionellosis (Legionnaires' Disease) Legionnaires' disease (a form of severe pneumonia) is caused by inhaling aerosolized water droplets containing the bacteria Legio- nella pneumophila. Susceptibility to Legionnaire's disease varies among individuals. People with compromised immune systems (e.g., organ transplant patients or others on immunosuppressant drugs, AIDS patients, smokers, elderly, those with other chronic health conditions or injuries) are at greater risk of contracting the disease at lower exposure levels. Most water supplied to buildings contains some Legionella bac- teria (and/or other microorganisms), often at levels too low to de- tect. The concern is that organism colonies can grow (amplify) within the building hot- and cold-water systems under certain con- ditions. At high Legionella concentrations, a hazard may exist. Some examples of conditions potentially conducive to Legionella growth are temperatures within a certain range (warm, not too hot or cold), locations of flow stagnation (e.g., pipe dead legs, low flow ve- locities, other flow stagnation points, intermittent or seasonal use), and inadequate oxidant residual levels. For more specific water system design guidance, refer to ASHRAE Standard 188-2018 and ASHRAE Guideline 12-2000. Scalding Scalding is an important concern in design and operation of potable hot-water systems. Figure 30 (Moritz 1947) shows plots of exposure time versus water temperature that results in both first- degree (pain, redness, swelling, minor tissue damage) and full- thickness third-degree (permanent damage, scarring) skin burns in adults. Children burn even more rapidly. Note that, at the high tem- peratures required for some commercial and institutional operations (e.g., 60°C and above), burns can occur almost instantaneously (3 s or less exposure). Even at lower temperatures such as 51°C, found commonly in multifamily housing, hospitality, and light commer- cial facilities, burns can occur in 2 min. Safety dictates some trade- offs to limit scalding injuries (e.g., during pressure transients that may inhibit proper operation of temperature regulating valves) while minimizing risk of Legionnaire's disease. Inc. ASHRAE, 2019 user. single for Licensed | {}
78d48c4a-75f7-4a03-b8de-92f6f3c06ca6 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Service Water Heating 51.33 Chart Type: line FIRST-DEGREE BURNS THIRD-DEGREE BURNS 4.2 min at 51°C 1.5 min at 52°C 1 min at 53°C 30 s at 55°C 17 s at 55°C 5 s at 60°C 3 s at 60°C item_01 8Time (min) 8Time (min) 9Time (min) 2Time (min) 1.5Time (min) 1Time (min) 0.5Time (min) 0.2Time (min) 0.0Time (min) Fig. 30 Time for Adult Skin Burns in Hot Water Temperature Requirement Typical temperature guidelines for some services are shown in Table 19. A 60°C water temperature minimizes flue gas condensa- tion in the equipment. Other Safety Concerns Regulatory agencies differ as to the selection of protective devices and methods ofinstallation. Itis therefore essential to check and comply with the manufacturer' s instructions and the applicable local codes. In the absence of such instructions and codes, the fol- lowing recommendations may be used as a guide: · Water expands when it is heated. Although the water-heating system is initially under service pressure, the pressure rises rap- idly if backflow is prevented by devices such as a check valve, pressure-reducing valve, or backflow preventer in the cold-water line or by temporarily shutting off the cold-water valve. When backflow is prevented, the pressure rise during heating may cause the safety relief valve to weep to relieve the pressure. However, if the safety relief valve is inadequate, inoperative, or missing, pres- sure rise may rupture the tank or cause other damage. Systems having this potential problem must be protected by a properly sized expansion tank located on the cold-water line downstream of and as close as practical to the device preventing backflow. · Temperature-limiting devices (energy cutoff/high limit) prevent water temperatures from exceeding 99°C by stopping the flow of fuel or energy. These devices should be listed and labeled by a recognized certifying agency. · Safety relief valves open when pressure exceeds the valve set- ting. These valves are typically applied to water-heating and hot- water supply boilers. The set pressure should not exceed the maximum allowable working pressure of the boiler. The heat in- put pressure steam rating (in kW) should equal or exceed the maximum out-put rating for the boiler. The valves should comply with current applicable standards or the ASME Boiler and Pressure Vessel Code. · Temperature and pressure safety reliefvalves also open ifthe water temperature reaches 99°C. These valves are typically applied to water heaters and hot-water storage tanks. The heat input tempera- ture/steam rating (in kW) should equal or exceed the heat input rat- ing of the water heater. Combination temperature- and pressure- relief valves should be installed with the temperature-sensitive element located in the top 150 mm of the tank (i.e., where the water is hottest). · To reduce scald hazards, discharge temperature at fixtures acces- sible to the occupant should not exceed 50°C. Thermostatically controlled mixing valves can be used to blend hot and cold water to maintain safe service hot-water temperatures. Table 19 Representative Hot- Water Temperatures ¦ Use ¦ Temperature, °C ¦ ¦ --- ¦ --- ¦ ¦ Lavatory ¦ ¦ ¦ Hand washing ¦ 40 ¦ ¦ Shaving ¦ 45 ¦ ¦ Showers and tubs ¦ 43 ¦ ¦ Therapeutic baths ¦ 35 ¦ ¦ Commercial or institutional laundry, based on fabric ¦ up to 82 ¦ ¦ Residential dish washing and laundry ¦ 60 ¦ ¦ Surgical scrubbing ¦ 43 ¦ ¦ Commercial spray-type dish washinga ¦ ¦ ¦ Single- or multiple-tank hood or rack type ¦ ¦ ¦ Wash ¦ 65 minimum ¦ ¦ Final rinse ¦ 82 to 90 ¦ ¦ Single-tank conveyor type ¦ ¦ ¦ Wash ¦ 71 minimum ¦ ¦ Final rinse ¦ 82 to 90 ¦ ¦ Single-tank rack or door type ¦ ¦ ¦ Single-temperature wash and rinse ¦ 74 minimum ¦ ¦ Chemical sanitizing typesb ¦ 60 ¦ ¦ Multiple-tank conveyor type ¦ ¦ ¦ Wash ¦ 65 minimum ¦ ¦ Pumped rinse ¦ 71 minimum ¦ ¦ Final rinse ¦ 82 to 90 ¦ ¦ Chemical sanitizing glass washer ¦ ¦ ¦ Wash ¦ 60 ¦ ¦ Rinse ¦ 24 minimum ¦ aAs required by NSF. bSee manufacturer for actual temperature required. · A relief valve should be installed in any part of the system con- taining a heat input device that can be isolated by valves. The heat input device may be solar water-heating panels, desuperheater water heaters, heat recovery devices, or similar equipment. 12. WATER QUALITY, SCALE, AND CORROSION A complete water analysis and an understanding of system re- quirements are needed to protect water-heating systems from scale and corrosion. Analysis shows whether water is hard or soft. Hard water, unless treated, causes scaling or liming of heat transfer and water storage surfaces; soft water may aggravate corrosion prob- lems and sacrificial anode consumption (Talbert et al. 1986). Scale formation is also affected by system requirements and equipment. As shown in Figure 31, the rate of scaling increases with temperature and use because calcium carbonate and other scaling compounds lose solubility at higher temperatures. In water tube- type equipment, scaling problems can be offset by increasing water velocity over the heat transfer surfaces, which reduces the tube sur- face temperature. Also, flow turbulence, if high enough, works to keep any scale that does precipitate off the surface. When water hardness is over 140 mg/L, water softening or other water treatment is often recommended. Corrosion problems increase with temperature because corrosive oxygen and carbon dioxide gases are released from the water. Elec- trical conductivity also increases with temperature, enhancing elec- trochemical reactions such as rusting (Taborek et al. 1972). A deposit of scale provides some protection from corrosion; however, this deposit also reduces the heat transfer rate, and it is not under the control of the system designer (Talbert et al. 1986). Steel vessels can be protected to varying degrees by galvanizing or by lining with copper, glass, cement, electroless nickel-phosphorus, Inc. ASHRAE, 2019 user. single for Licensed | {}
d5459a9e-428a-49a9-ac73-8650bfe4536f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 51.34 Chart Type: line (0) (3) (6) (9) (12) (15) item_01 0kg/day 0kg/day 0kg/day 70kg/day 75kg/day 80kg/day Fig. 31 Lime Deposited Versus Temperature and Water Use (Based on data from Purdue University Bulletin No. 74) or other corrosion-resistant material. Glass-lined vessels are almost always supplied with electrochemical protection. Typically, one or more anode rods of magnesium, aluminum, or zinc alloy are in- stalled in the vessel by the manufacturer. This electrochemically ac- tive material sacrifices itself to reduce or prevent corrosion of the tank (the cathode). Higher temperature, softened water, and high water use may lead to rapid anode consumption. Manufacturers rec- ommend periodic replacement of the anode rod(s) to prolong the life of the vessel. Some waters have very little electrochemical activity. In this instance, a standard anode shows little or no activity, and the vessel is not adequately protected. If this condition is suspected, consult the equipment manufacturer on the possible need for a high- potential anode, or consider using vessels made of nonferrous ma- terial. Inc. ASHRAE, 2019 user. single for Licensed Water heaters and hot-water storage tanks constructed of stain- less steel, copper, or other nonferrous alloys are protected against oxygen corrosion. However, care must still be taken, as some stain- less steel may be adversely affected by chlorides, and copper may be attacked by ammonia or carbon dioxide. 13. SPECIAL CONCERNS Cross Flow at End-Use Fixtures Cross flow occurs when there is a connection between the hot- and cold-water lines. Cross flow is problematic because moving hot water into the cold line or, alternatively, moving cold water into the hot line, can affect the performance of end-use equipment, reduce hot-water outlet temperatures or mix hot water into the cold line used for drinking water or ice making. Ifnot resolved, cross flow in facilities can cause energy and water waste, poor water system per- formance, and facilitate growth of Legionella. One way to determine whether cross flow is occurring from the cold-water side is to turn offthe valve on the water heater cold-water inlet and let only hot water flow at a faucet. If pressure drops and water ceases to flow, then there is no cross flow, but if water continues to flow, this indicates cross flow between the hot and cold lines in the system. 2019 ASHRAE Handbook-HVAC Applications (SI) Cross flow can occur in the commercial setting at various loca- tions on the water distribution system, including at mop or utility sink faucets and at prerinse spray valve faucets. These are locations where both the hot- and cold-water valves are commonly kept in the open position for downstream tempering of water for "on-demand" sanitation tasks. Assemblies such as in-line chemical dispensers, hoses with attached spray nozzles, or downstream shutoff valves installed for filling mop buckets may promote cross flow if check valves are not installed. Similarly, in commercial kitchens, prerinse spray valve operation typically requires leaving the hot- and cold- water valves open at the faucet in advance of spray valve operation. Another place where cross flow can occur is with single-handle fau- cets at hand sinks and showers, where a worn seal in the faucet can cause a direct connection of the cold and hot line. Installing a check valve on both the hot-water and cold-water connections at end-use fixtures ensures that water only flows in a single direction, eliminating cross flow. To ensure that cross flow at the faucet is prevented, specify faucets with check valves included. Otherwise, check valves should be installed ahead of these faucets on both the hot and cold lines. Hot Water from Tanks and Storage Systems With storage systems, 60 to 80% of the hot water in a tank is assumed to be usable before dilution by cold water lowers the temperature below an acceptable level. However, better designs can exceed 90%. Thus, the maximum hot water available from a self- contained storage heater is usually Vt = Rd + MSt (18) where V1 = available hot water, L R = recovery rate at required temperature, L/s d = duration of peak hot-water demand, s M = ratio of usable water to storage tank capacity S1 = storage capacity of heater tank, L However, Equation (11) only applies ifthe water draw rate is less than the available reheat rate. Otherwise, the tank cannot heat the flowing water to a usable temperature during the draw, and Vt drops to the same as an unfired tank. For example, a fossil-fuel-fired heater with a fuel input rate of 13 kW and an input efficiency of 80% can raise the temperature of water being drawn through a storage tank at a rate of 200 mL/s by approximately 13 K. If the entering cold-water temperature is 16°C, the water will be heated to only 28°C, too cold to be useful, so the heating rate cannot contribute to effective storage tank capacity under a prolonged draw at this flow rate. In reality, draw rates are rarely constant during peak draw or other times. Computer simulation models allow equipment sizing under these more realistic conditions (Hiller 1992). Maximum usable hot water from an unfired tank is Va = MSa where Va = usable water available from unfired tank, L Sa = capacity of unfired tank, L (19) Note: Assumes tank water at required temperature. Hot water obtained from a water heater using a storage heater with an auxiliary storage tank is Vz=Vt+ Va (20) where Vz is total hot water available during one peak, in litres. | {}
a2847026-fa78-42c4-8bfe-4c12c842e7ec | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Service Water Heating 51.35 Placement of Water Heaters Many types of water heaters may be expected to leak at the end of their useful life. They should be placed where leakage will not cause damage. Alternatively, suitable drain pans piped to drains must be provided. Water heaters not requiring combustion air may generally be placed in any suitable location, as long as relief valve discharge pipes open to a safe location. Water heaters requiring ambient combustion air must be located in areas with air openings large enough to admit the required com- bustion/dilution air (see NFPA Standard 54/ANSI Z223.1). For water heaters located in areas where flammable vapors are likely to be present, precautions should be taken against ignition. For water heaters installed in residential garages, additional precau- tions should be taken. Consult local codes for additional require- ments or see sections 5.1.9 through 5.1.12 of NFPA Standard 54/ ANSI Z223.1. Outdoor models with a weather-proofed jacket are available. Direct-vent gas- and oil-fired models are also available; they are to be installed inside, but are not vented through a conventional chimney or gas vent. They use outdoor air for combustion. They must be installed with the means specified by the manufacturer for venting (typically horizontal) and for supplying air for combustion from outside the building. Air-source heat pump water heaters require access to an adequate air supply from which heat can be extracted. For residential units, a room of at least 27 m3 or ducted air is recommended. See manufac- turer's literature for more information. REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. ASHRAE. 2016. Energy standard for buildings except low-rise residential buildings. ANSI/ASHRAE/IES Standard 90. 1-2016. ASHRAE. 2018. Energy-efficient design of low-rise residential buildings. ANSI/ASHRAE/IES Standard 90.2-2018. ASHRAE. 2018. Energy conservation in existing buildings. ANSI/ ASHRAE/IES Standard 100-2018. ASHRAE. 2012. Methods of testing for rating commercial gas, electric, and oil water heaters. Standard 118.1-2012. ASHRAE. 2015. Methods of testing for rating residential water heaters. Standard 118.2-2006 (RA 2015). ASHRAE. 2016. Methods of testing for rating combination space-heating and water-heating appliances. Standard 124-2007 (RA 2016). ASHRAE. 2018. Legionellosis: Risk management for building water sys- tems. Standard 188-2018. ASHRAE. 2000. Minimizing the risk of Legionellosis associated with building water systems. Guideline 12-2000. ASME. 2019. Boiler and pressure vessel code. Section IV-19: Rules for con- struction of heating boilers; Section VIII D1-19: Rules for construction of pressure vessels. ASME International, New York. Becker, B.R., W.H. Thrasher, and D. W. DeWerth. 1991. Comparison of col- lected and compiled existing data on service hot water use patterns in res- idential and commercial establishments. ASHRAE Transactions 97(2): 231-239. Buchberger, S., T. Omaghomi, T. Wolfe, J. Hewitt, and D. Cole. 2015. Peak water demand study: Probability estimates for efficientfixtures in single and multi-family residential buildings. American Society of Plumbing Engineers, Rosemont, IL. Butcher, T. 2011. Performance of combination hydronic systems. ASHRAE Journal 53(12). CCDEH. 1995. Guidelines for sizing water heaters. California Conference of Directors of Environmental Health. www.ccdeh.com. DOE. 2001. Final rule regarding test procedures and energy conservation standards for water heaters. Code of Federal Regulations 10 CFR 430. U.S. Department of Energy, Washington, D.C. DOE. 1998. Uniform test method for measuring the consumption of energy water heaters. Code of Federal Regulations 10 CFR 430, Subpart B, Appendix E. U.S. Department of Energy, Washington, D.C. DOE. 2011. Commercial prerinse spray valves. Code ofFederal Regulations 10 CFR 431, Subject 0, Section 431.266. Energy Efficiency Program for Certain Commercial and Industrial Equipment, U.S. Department of Energy, Washington, D.C. DOE. 2014. Energy conservation program for consumer products and indus- trial equipment: Test procedures for residential and commercial water heaters. Federal Register 79(133), July 11. U.S. Department of Energy, Washington, D.C. DOE. 2017. U.S. Department of Energy 's compliance certification data- base. www.regulations.doe.gov/centication-data/ Dunn, T.Z., R.N. Spear, B.E. Twigg, and D. Williams. 1959. Water heating for commercial kitchens. Air Conditioning, Heating and Ventilating (May):70. Also published as a bulletin, Enough hot water-Hot enough. American Gas Association (1959). EPA. 2013. Summary of the Reduction of Lead in Drinking Water Act and frequently asked questions. U.S. Environmental Protection Agency, Washington, D.C. EPRI. 1990. Commercial heat pump water heaters applications handbook. CU-6666. Electric Power Research Institute, Palo Alto, CA. EPRI. 1992. Commercial water heating applications handbook. TR- 100212. Electric Power Research Institute, Palo Alto, CA. EPRI. 1994. High-efficiency electric technology fact sheet: Commercial heat pump water heaters. BR-103415. Electric Power Research Institute, Palo Alto, CA. FDA. 2000. Food establishment plan review guide. U.S. Food and Drug Administration, Silver Spring, MD. www.fda.gov/Food/Guidance Beguebon#callificenderiolantrysi Begaboy/scand TrainingResources/ucm101639.htm. Fisher-Nickel. 2010. Design guide: Improving commercial kitchen hot water system performance: Energy efficient heating, delivery, and use. Pacific Gas and Electric Company Food Service Technology Center, San Ramon, CA. caenergywise.com/design-guides/. GAMA. (Continuous Maintenance). Consumers directory of certified effi- ciency ratings for heating and water heating equipment. Gas Appliance Manufacturers Association, Arlington, VA. Glanville, P., D. Kosar, and J. Stair. 2013. Short-term performance of gas- fired tankless water heaters: Laboratory characterization. ASHRAE Transactions 119(1):248-269. Goldner, F.S. 1994a. Energy use and domestic hot water consumption: Final report-Phase 1. Report 94-19. New York State Energy Research and Development Authority, Albany, NY. Goldner, F.S. 1994b. DHW system sizing criteria for multifamily buildings. ASHRAE Transactions 100(1):963-977. Goldner, F.S., and D.C. Price. 1999. DHW modeling: System sizing and selection criteria, phase 2. Interim Project Research Report 1. New York State Energy Research and Development Authority, Albany. Hiller, C.C. 1992. WATSIMⓇ 1.0: Detailed water heating analysis code. Applied Energy Technology Co., Davis, CA. Hiller, C.C. 1998. New hot water consumption analysis and water-heating system sizing methodology. ASHRAE Transactions 104(1B):1864-1877. Hiller, C.C. 2000. WATSMPLⓇ 2.0: Simplified water heating analysis code. Applied Energy Technology Co., Davis, CA. Hiller, C. 2002. Field test comparison of a potable hot water recirculation- loop system vs point-of-use electric resistance water heaters in a high school. EPRI Report 1007022. Hiller, C.C. 2005a. Comparing water heater vs. hot water distribution system energy losses. ASHRAE Transactions 1 - 1(2):407-418. Hiller, C.C. 2005b. Hot water distribution system research-Phase I final report. California Energy Commission Report CEC-500-2005-161. Hiller, C. 2005c. School HV AC: Rethinking school potable water heating systems. ASHRAE Journal (May):48-56. Hiller, C.C. 2006a. Hot water distribution system piping time, water, and energy waste Phase I test results. ASHRAE Transactions 112(1):415- 425. Hiller, C.C. 2006b. Hot water distribution system piping heat loss factors Phase I test results. ASHRAE Transactions 112(1):436-446. Hiller, C.C. 2008. Hot water distribution system piping heat loss factors, both in air and buried- Phase II test results. ASHRAE Transactions 114(2). Inc. ASHRAE, 2019 user. single for Licensed | {}
63c94dc4-5e6e-452a-890d-f3d8f11844cf | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 54.6 2019 ASHRAE Handbook-HVAC Applications (SI) extent to which smoke leaks through such barriers depends on the size and shape of the leakage paths in the barriers and the pressure difference across the paths. Dilution Remote from Fire Smoke dilution is sometimes referred to as smoke purging, smoke removal, smoke exhaust, or smoke extraction. Dilution can be used to maintain acceptable gas and particulate concentra- tions in a compartment subject to smoke infiltration from an adja- cent space. It can be effective if the rate of smoke leakage is small compared to either the total volume of the safeguarded space or the rate of purging air supplied to and removed from the space. Also, di- lution can be beneficial to the fire service for removing smoke after a fire has been extinguished. Sometimes, when doors are opened, smoke flows into areas intended to be protected. Ideally, the doors are only open for short periods during evacuation. Smoke that has entered spaces remote from the fire can be purged by supplying out- door air to dilute the smoke. The following is a simple analysis of smoke dilution for spaces in which there is no fire. At time zero (t = 0), a compartment is con- sidered contaminated with some concentration of smoke and no more smoke flows into the compartment or is generated in it. Fur- ther, the contaminant is considered to be uniformly distributed throughout the space. The concentration of contaminant in the space can be expressed as 등 = e-at (7) and the dilution rate can be calculated from Co 1 a ln t (8) where C concentration of contaminant at time t Co initial concentration of contaminant e = base of natural logarithm (approximately 2.718) a = dilution rate, air changes per minute t = time after smoke stops entering space or smoke production has stopped, min Concentrations Co and C need to be expressed in the same units, but can be any units appropriate for the particular contaminant being considered. In reality, it is impossible to ensure that the concentration of the contaminant is uniform throughout the compartment. Because of buoyancy, it is likely that concentrations are higher near the ceiling. Therefore, exhausting smoke near the ceiling and supply- ing air near the floor probably dilutes smoke even more quickly than indicated by Equation (8). Supply air should be free or nearly free of smoke, as discussed in the Smoke Feedback section. Example 2. A space is isolated from a fire by smoke barriers and self-closing doors, so that no smoke enters the compartment when the doors are closed. When a door is opened, smoke flows through the open doorway into the space. Ifthe door is closed when the contaminant in the space is 20% of the burn room concentration, what dilution rate is required to re- duce the concentration to 1% of that in the burn room in 6 min? Solution. Time t = 6 min and ColC = 20. From Equation (8), the dilu- tion rate is about 0.5 air changes per minute, or 30 air changes per hour. Caution About Dilution near Fire: Some people have unrealis- tic expectations about what dilution can accomplish in the fire space. Neither theoretical nor experimental evidence indicates that using a building's HV AC system for smoke dilution significantly improves tenable conditions in a fire space. The exception is an unusual space where the fuel is such that fire size cannot grow above a specific limit, such as in some tunnels and underground transit situations. Because HV AC systems promote a considerable degree ofair mixing in the spaces they serve and because very large quantities of smoke can be produced by building fires, it is generally believed that smoke dilution by an HV AC system in the fire space does not improve ten- able conditions in that space. Thus, any attempt to improve hazard conditions in the fire space, orin spaces connected to the fire space by large openings, with smoke purging will be ineffective. Pressurization Many smoke control systems use mechanical fans to control smoke by pressurization. Pressure difference across a barrier can control smoke movement by preventing smoke on the low-pressure side of the barrier from migrating to the high-pressure side. Pres- surization can control smoke from a fire remote from a barrier, or from a very large fire located next to a barrier (Figure 7). Frequently, in field tests of smoke control systems, pressure dif- ferences across partitions or closed doors fluctuate by 5 Pa. These fluctuations are generally attributed to wind, although they could have been caused by the HVAC system or some other source. To control smoke movement, the pressure difference produced by a smoke control system needs to be large enough to overcome pres- sure fluctuations, stack effect, smoke buoyancy, and wind pressure, but not so large that the door is difficult to open. Pressurization of smoke control systems is discussed in the section on Pressurization System Design. Opposed Airflow Airflow can be used to control smoke flow in many applications, including buildings, rail tunnels, and highway tunnels, if the air ve- locity equals or exceeds the limiting velocity (Figure 8). For infor- mation about rail and highway tunnels, see Chapter 16. For control of smoke between an atrium and a communicating space, see NFPA Standard 92 and the limiting velocity equations in Chapter 15 ofthe Smoke Control Handbook. Airflow smoke control is not used much in buildings because of the very large amounts of airflow needed, and (more importantly) because airflow can supply oxygen to the fire, which can result in catastrophic failure. Even full sprinkler protection does not com- pletely eliminate this risk. For any application that uses the airflow approach, this failure mode needs to be addressed in the design analysis. ![image](/image/placeholder) SMOKE LAYER HIGH-PRESSURE SIDE LOW-PRESSURE SIDE CONTROLLING SMOKE FROM FIRE REMOTE FROM BARRIER HIGH-PRESSURE SIDE LOW-PRESSURE SIDE FULLY INVOLVED IN FIRE CONTROLLING SMOKE FROM FULLY INVOLVED FIRE NEXT TO BARRIER (See Note) Note: A fully involved fire is a very large fire such that all the materials in fire space that can burn are burning. Fig. 7 Smoke Flow Controlled by Pressurization Inc. ASHRAE, 2019 user. single for Licensed | {}
df715638-7319-4891-98c7-86dfe16adf3d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Fire and Smoke Control 54.7 Buoyancy (9) Buoyancy of hot combustion gases is used for smoke control in large-volume spaces such as atriums. A smoke plume rises above the fire to form a smoke layer under the ceiling of the large volume space. The smoke plume entrains air from the surroundings. The mass flow of the plume increases with height, and the plume tem- perature decreases with height. Plume flow is the basis of atrium smoke control (see the section on Atrium Smoke Control). 8. SMOKE FEEDBACK Smoke feedback occurs when smoke from an indoor fire flows outdoors and then either (1) is pulled into a smoke control supply fan or (2) flows into an atrium makeup air vent. To minimize the potential for smoke feedback, supply air intakes should be located away from the major openings from which smoke could leave a building, such as smoke control exhausts, heat and smoke vents, and open vents of elevator shafts. Smoke entering a building at a loading dock because of a large fire inside a truck should be evaluated. Con- sidering the enormous number of possible fire scenarios and build- ing designs, it is not possible to anticipate all the possible openings where smoke could leave a building. Outdoor air intakes of smoke control systems should be located such that forces of wind and buoyancy minimize the potential for smoke feedback into supply air. An understanding of airflow around buildings can be helpful in minimizing the potential for smoke feed- back. See Chapter 24 of the 2017 ASHRAE Handbook-Fundamen- tals for information about airflow around buildings. Caution: using smoke detectors to automatically shut down smoke control supply fans is not recommended, because smoke de- tectors are extremely sensitive to small amounts of smoke that would not result in an untenable environment. This high sensitivity is important to provide early warning of fires, butit could shut down a smoke control system from a puff of smoke that would not be life threatening. 9. PRESSURIZA TION SYSTEM DESIGN Door-Opening Forces The section has general information applicable to all pressuriza- tion smoke control systems. The common pressurization smoke control systems are pressurized stairwells, pressurized elevators, and zoned smoke control, which are discussed later. Supply air for pressurization smoke control systems should be free or nearly free of smoke as discussed in the section on smoke feedback. The pressure difference across a barrier must not result in door- opening forces that exceed the maximum values stipulated in codes. For example, in the NFPA Life Safety CodeⓇ (NFPA Standard 101), this maximum force is 133 N. The force required to open a side-hinged swinging door is the sum of the forces to overcome the pressure difference across the door and to overcome the door closer. This can be expressed as ![image](/image/placeholder) SMOKE AIRFLOW Note: Airflow can control smoke flow if air velocity is large enough. Fig. 8 Opposed Airflow Controlling Smoke Flow where WA△p F = Fdc 2(W - d) + F = total door-opening force, N Fdc =force to overcome door closer and other friction, N W =door width, m A =door area, m2 △p =pressure difference, Pa d =offset, m The offset d is the distance between where the door-opening force is applied and the side of the door opposite the hinges (i.e., the latch side). For a lever handle, the door-opening force can be applied where the hand grasps the lever handle. For panic hardware, the door-opening force can be applied somewhere along the panic bar. For doors that do not stick to the door frame and have properly lubri- is the force to overcome the door closer. For more cated hinges, Fdc detailed information about door-opening forces, see Klote (2018). Flow and Pressure Difference Example 3. For a side-hinged swinging door 0.914 m wide by 2.13 m high with a door closer that requires 40 N of force, and a pressure difference across it of 87 Pa. The door-opening force is applied at a lever handle such that the offset is 76 mm. The door-opening force calculated from Equation (9) is 132 N. The primary equation used for analysis of pressurization smoke control systems is the orifice equation: m = CA V2pAp Alternatively, Equation (10) can be expressed in terms of volu- metric flow: (10) 2△p V = CA p where m = mass flow through the path, kg/s C = flow coefficient A = flow area (or leakage area), m2 Ap = pressure difference across path, Pa V = volumetric flow, m3/s P = gas density in path, kg/m3 (11) Equations (10) and (1 1) are equivalent forms of the same orifice equation. Airflow paths need to be identified and evaluated in smoke control system design. Some leakage paths are obvious, such as cracks around closed doors, open doors, elevator doors, windows, and air transfer grilles. Construction cracks in building walls are less obvious but no less important. The flow area of most large openings, such as open windows, can be calculated easily. However, flow areas of cracks are more diffi- cult to evaluate. The area of these leakage paths depends on quality of work (e.g., how well a door is fitted or how weatherstripping is installed). Inc. ASHRAE, 2019 user. single for Licensed For many flow paths in buildings, a flow coefficient of 0.65 is used. The open doors of pressurized stairwells commonly have sta- tionary vortices that reduce flow significantly (Cresci 1973; Klote and Bodart 1985). These vortices are thought to be caused by asym- metric flow from the stairs, and stationary vortices can be expected at many open doors in other locations of smoke control systems. For open doors in stairwells, the geometric area of the opening should be used for the flow area, with a flow coefficient of 0.35. Typical leakage areas for walls and floors of commercial build- ings are tabulated as area ratios in Table 1. These data are based from field tests performed by the National Research Council of Canada (Shaw et al. 1993; Tamura and Shaw 1976a, 1976b, 1978; | {}
948e3409-0a6d-40bb-9060-499a951f9646 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 54.8 2019 ASHRAE Handbook-HVAC Applications (SI) Table 1 Typical Flow Areas of Walls and Floors of Commercial Buildings ¦ Construction Element ¦ Wall Tightness ¦ Area Ratio AIaw* ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Exterior building walls (includes construction cracks and cracks around windows and doors) ¦ Tight ¦ 5.0 x 10~5 ¦ ¦ Exterior building walls (includes construction cracks and cracks around windows and doors) ¦ Average ¦ 1.7 x 10-4 ¦ ¦ Exterior building walls (includes construction cracks and cracks around windows and doors) ¦ Loose ¦ 3.5 x 10-4 ¦ ¦ Exterior building walls (includes construction cracks and cracks around windows and doors) ¦ Very Loose ¦ 1.2 x 10-3 ¦ ¦ Stairwell walls (includes construction cracks but not cracks around windows or doors) ¦ Tight ¦ 1.4 X 10-5 ¦ ¦ Stairwell walls (includes construction cracks but not cracks around windows or doors) ¦ Average ¦ 1.1 X 10-4 ¦ ¦ Stairwell walls (includes construction cracks but not cracks around windows or doors) ¦ Loose ¦ 3.5 x 10-4 ¦ ¦ Elevator shaft walls (includes construction cracks but not cracks around doors) ¦ Tight ¦ 1.8 X 10-4 ¦ ¦ Elevator shaft walls (includes construction cracks but not cracks around doors) ¦ Average ¦ 8.4 x 10-4 ¦ ¦ Elevator shaft walls (includes construction cracks but not cracks around doors) ¦ Loose ¦ 1.8 x 10-3 ¦ ¦ ¦ ¦ AIAF* ¦ ¦ Floors (includes construction cracks and gaps around penetrations) ¦ Tight ¦ 6.6 x 10-6 ¦ ¦ Floors (includes construction cracks and gaps around penetrations) ¦ Average ¦ 5.2 x 10-5 ¦ ¦ Floors (includes construction cracks and gaps around penetrations) ¦ Loose ¦ 1.7 x 10-4 ¦ *A = leakage area; Aw = wall area; AF = floor area. Tamura and Wilson 1966). Considerable leakage data through building components are also provided in Chapter 3 of the Smoke Control Handbook. Both the maximum and minimum allowable pressure differences across the boundaries of smoke control should be considered. The term acceptable pressurization applies to a system that operates within the range of minimum to maximum allowable pressure differences. The maximum allowable pressure difference should not cause excessive door-opening forces. The minimum allowable pressure difference intended to prevent smoke migration across a barrier of a smoke control system is gen- erally stipulated by code. The smoke control system needs to be de- signed to maintain this minimum design pressure difference under likely conditions of wind, stack effect, or buoyancy of hot smoke. Pressure differences caused by wind and stack effect can be large in the event of a broken window or an open window or door in the fire compartment. (Windows exposed to the heat of a fire often break.) Evaluation of these pressure differences depends on evacuation time, rate of fire growth, building configuration, and the presence of a fire suppression system. The code-required minimum and maxi- mum design pressure differences need to be used. For locations with no such code requirements, the values of NFPA Standard 92 are suggested. Computer Analysis by Network Modeling CONTAM (Dols and Polidoro 2016) is the de facto standard com- puter program for analyzing pressurization smoke control systems. It is a network model that simulates airflow and contaminant flow in buildings. Network modeling for smoke control dates back to the 1960s, but these early models were subject to numerical difficulties and data input was extremely cumbersome and time consuming. CONTAM has superior numerical routines and sophisticated data input, and can be downloaded from the NIST website (www.nist .govelenegy.cod-covicommen-cinaioriotionixl.coce -modeling/download-contam) at no cost. Because CONTAM does not solve the energy equation, the user needs to input the tempera- tures of the spaces in the network. Note that, when CONTAM is discussed in this chapter, other net- work models could be used instead. Network models represent a building by a network of spaces or nodes, each at a specific pressure and temperature. The stairwells and other shafts can be modeled by a vertical series of spaces, one for each floor. Air flows through leakage paths (e.g., doors or windows that may be opened or closed, partitions, floors, exterior walls, roofs) from regions of high pres- sure to regions of low pressure. Airflow through a leakage path is a function of the pressure difference across the leakage path. In network models, air from outside the building can be intro- duced by a pressurization system into any level of a shaft or into other building spaces. This allows simulating pressurization of a stairwell, elevator shaft, stairwell vestibule, and any other building space. In addition, any building space can be exhausted. This allows analysis of zoned smoke control systems where the fire zone is exhausted and other zones are pressurized. The pressures and flows throughout the building are obtained by solving conservation equa- tions for the network. Analysis can include the driving forces of wind, the pressurization system, and indoor-to-outdoor temperature difference. The primary purpose of network simulations is to determine whether a particular smoke control system in a particular building can be balanced such that it will perform as intended. Network models can simulate pressures and flows throughout very large and complicated building networks with high accuracy, although the results are approximations. There are many flow paths in buildings, including gaps around closed doors, open doors, and construction cracks in walls, roof, and floors. These flow paths are approximated for a design analysis. However, the approximated results can be useful in identifying prob- lems with specific smoke control systems, so the smoke control system or the building can be modified appropriately. These simula- tions can also provide information to help size system components such as supply fans, exhaust fans, and vents. First-time users of CONTAM may be confused by its extensive capabilities, many of which are not usually used for smoke control analysis. Chapter 14 ofthe Smoke Control Handbook has CONTAM user information intended to help start using the software for anal- ysis of smoke control systems that rely on pressurization. This in- formation includes a section on speeding up data input. 10. SHAFT PRESSURIZA TION Stairwell pressurization and elevator pressurization are two kinds of shaft pressurization systems. Major factors that must be addressed in the design of these systems are building complexity and stack effect. Building Complexity Building complexity is a major factor in shaft pressurization, and successful shaft pressurization can be challenging in complicated buildings. A simple building has floor plans that are nearly the same from floor to floor, whereas a complicated building's floor plans dif- fer considerably from floor to floor. Figure 9 shows examples of these buildings. Air leaving a pressurized shaft flows through the building to the outdoors, and flow paths to the outdoors differ by floor in complicated buildings. This results in varying pressure dif- ferences across pressurized shafts from floor to floor in complicated buildings, and can result in challenging shaft pressurization sys- tems. Stairwell pressurization is usually straightforward for simple buildings, but elevator pressurization can be a challenge even in simple buildings. Systems that can be used to overcome these chal- lenges are discussed in the sections on Pressurized Stairwells and Pressurized Elevators. Stack Effect Sometimes engineers will say that a pressurized stairwell or ele- vator must be designed to account for stack effect. If the space is properly pressurized, there is no neutral plane, and all the flows are from the stairwell. Strictly speaking, then, there is no stack effect in the pressurized stairwell or elevator: what is meant is that the space Inc. ASHRAE, 2019 user. single for Licensed | {}
c873ae07-eab6-4621-80b7-d53b2225511b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Fire and Smoke Control 54.9 ![image](/image/placeholder) VARIABLE OFFICE OPEN PLAN FLOOR OFFICE LAYOUTS BUILDING OFFICE AND RETAIL SPACES UNDERGROUND PARKING SIMPLE BUILDING (See Note 1) COMPLICATED BUILDING (See Note 2) Notes: 1. For smoke control purposes, a simple building is one where floor plans are nearly the same from floor to floor. 2. For smoke control purposes, a complicated building is one where floor plans differ considerably from floor to floor. Fig. 9 Examples of Simple and Complicated Buildings must be designed to account for the temperature differences that cause stack effect. Caution: It is a myth that stack effect is the major factor affecting stairwell and elevator pressurization. Although stack effect can be the major factor, it often is a minor factor for pressur- ized stairwells and elevators. Pressurization air for many stairwells and elevators is untreated outdoor air that is not heated or cooled. The temperature of these shafts is often nearly the same as the out- door temperature, and the consequence of stack effect is signifi- cantly reduced as compared to shafts pressurized with air treated to the building temperature. Shaft Temperature. When pressurization air is untreated, the shaft temperature can be expressed as Ts = To + n(TB - To) where Ts temperature in stairwell, °C To temperature outdoors, °C 7 = heat transfer factor TB = temperature in building, °C There has been little research on the heat transfer factor, but it is believed to be in the range of 0.05 to 0.15. Without better data for a specific application, a heat transfer factor of 0.15 is suggested as conservative for the consequence of stack effect. For untreated supply air, it takes a few minutes for the tempera- ture in the shaft to stabilize near that ofthe outdoors. During this sta- bilization, excessive pressure differences could be produced. To prevent this, supply air can gradually be increased so that, when the shaft temperature is near that of the building, there is insufficient flow to cause excessive pressurization. If needed, temperature sta- bilization can be evaluated by a heat transfer analysis. Friction Losses in Shafts. Pressure losses from friction in stair- wells and elevator shafts can be significant when flow rates are high. CONTAM uses data from Achakji and Tamura (1988) and Tamura and Shaw (1976b) to calculate pressure loss in stairwells. 11. PRESSURIZED STAIR WELLS Many pressurized stairwells have been designed and built to pro- vide a tenable environment inside the stairwell in the event of a ![image](/image/placeholder) ROOF LEVEL DUCT SHAFT DUCT CENTRIFUGAL FAN Fig. 10 Stairwell Pressurization by Multiple Injection with Fan Located at Ground Level ![image](/image/placeholder) ROOF LEVEL CENTRIFUGAL FANS (12) Fig. 11 Stairwell Pressurization by Multiple Injection with Multiple Fans building fire. They also provide a smoke-free staging area for fire- fighters. On the fire floor, a pressurized stairwell is intended to pro- vide a positive pressure difference across a closed stairwell door to prevent smoke infiltration. For stairwells in cold climates, designers should consider treating supply air to minimize the potential of freezing water in standpipes. Supply air for pressurized stairwells should be free or nearly free of smoke, as discussed in the Smoke Feedback section. Air can be supplied to a pressurized stairwell at one or several locations. A single-injection system supplies pressurized air to the stairwell at one location, usually at the top. For tall stairwells, sin- gle-injection systems can fail when a few doors are open near the air supply injection point, especially in bottom-injection systems when a ground-level stairwell door is open. Stairwell Compartmentation Air can be supplied at multiple locations over the height of a tall stairwell. Figures 10 and 11 show two examples of multiple- injection systems that can be used to overcome the limitations of single-injection systems. Multiple-injection systems can use one or multiple fans. When one fan is used, air is supplied through a duct that is usually in a separate duct shaft. However, some systems elim- inate the expense of a separate duct shaft by locating the supply duct in the stairwell itself. In such a case, ensure that the duct does not obstruct orderly building evacuation. Stairwell compartmentation, which is not often used, consists of dividing a stairwell into several sections consisting of five to ten stories each; each compartment has at least one supply air injection point. The compartments are separated by walls with normally Inc. ASHRAE, 2019 user. single for Licensed | {}
2194ae24-34a9-4362-bc44-29dcc84a5539 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 54.10 2019 ASHRAE Handbook- -HVAC Applications (SI) closed doors. The main advantage of compartmentation is that it al- lows acceptable pressurization of stairwells that are otherwise too tall for acceptable pressurization. A disadvantage is the increase in floor area needed for the walls and doors separating the stairwell sections. When the doors between compartments are open, the ef- fect of compartmentation is lost. For this reason, compartmentation is inappropriate for densely populated buildings, where total build- ing evacuation by stairwell is planned in the event of a fire. Vestibules Pressurized stairwells with vestibules are occasionally used. The vestibules can be unpressurized, pressurized, ventilated, or both pressurized and ventilated. Vestibules provide an additional barrier around a stairwell, and can reduce the probability of an open-door connection existing between the stairwell and the building. An evacuation analysis can determine the extent to which both vestibule doors are likely to be opened simultaneously. For densely populated buildings, it is expected that on many floors both vesti- bule doors would be opened simultaneously. Therefore, vestibules may provide little benefit of an extra barrier for densely populated buildings. The algebraic equation method of analysis can be used to analyze a pressurized stairwell with an unpressurized vestibule. The pres- sure differences and flows of stairwell systems with any kind of ves- tibules, including those with openings to the outdoors and those with combinations of supply air and exhaust air, can be analyzed by CONTAM. System with Fire Floor Exhaust This system can achieve acceptable pressurization of tall stair- wells in very complicated buildings. A relatively small amount of air is supplied to the stairs, and the fire floor is exhausted such that acceptable pressurization is maintained on the fire floor where it is needed. Floors above and below the fire floor also may be exhaust- ed. These systems are discussed further in the section on Zoned Smoke Control. When a CONTAM analysis shows that the code- mandated systems cannot or are likely not to be able to achieve suc- cessful pressurization, stairwell pressurization with fire floor ex- haust could be a solution. The design analysis of these systems should include CONTAM simulations. Analysis of Pressurized Stairwells Pressure differences across a stairwell tend to vary over the height of the stairwell. Figure 12 shows pressure profiles for pres- surized stairwells in an idealized building (i.e., no vertical leakage through the floors and shafts, and leakage is the same from floor to floor) and in a more realistic building with vertical leakage through floors and an elevator shaft. This figure is for winter. When itis cold outdoors, the pressure differences tend to be less at the bottom of the stairwell than at the top. When it is hot outdoors, the trend is the opposite. For both winter and summer conditions, the pressure pro- file for an idealized building is a straight line. The pressure profiles of stairs in real buildings depend on many factors, including (1) leakage values ofthe building components, (2) building floor plans, (3) size of elevator shaft or shafts and number of elevator doors, (4) presence or absence of elevator lobbies and vents, and (5) leakage through other shafts. There are many possible shapes for such pressure profiles in real buildings, but the complex- ities of airflow in buildings are such that specific patterns for pres- sure profiles are unknown. For a building with vertical leakage, flows through the floors and shafts to some extent even out the highest and lowest pressure dif- ferences across the stairwell. The profile for a building with vertical leakage is bounded by the extremes of the pressure profile of the idealized building. This means that, other things being equal, the smallest pressure difference of the idealized analysis is less than that Chart Type: line Top of Stairwell Building with Vertical Leakage (See Note) IDEALIZED Building item_01 1 2 75 Notes: 1. The pressure difference is from the stairwell to the building across the stair door. 2. The shape of the curve for a building with vertical leakage depends on many factors, and the curve shown is only one of many possible shapes. Fig. 12 Pressure Profile of a Pressurized Stairwell in Winter Table 2 Stairwell Supply Air as Function of Leakage Classification ¦ Stairwell Leakage Classification ¦ Wall Leakage, m2/m2 ¦ Door Leakage, m2 ¦ Supply Air, m3/(s·floor) ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Low ¦ 1.4 x 10-5 ¦ 0.0075 ¦ 0.04 ¦ ¦ Average ¦ 1.1 x 10-4 ¦ 0.015 ¦ 0.11 ¦ ¦ High ¦ 3.5 X 10-4 ¦ 0.022 ¦ 0.26 ¦ Note: The supply air listed was calculated by equation method to maintain a minimum pressure difference of25 Pa. of the realistic building, and that the largest pressure difference of the idealized analysis is more than that of the realistic building. This is why the algebraic equation method discussed in the section on Equations for Steady Smoke Exhaust is conservative. An algebraic equation method of analysis pressurized stairwells is also presented in Chapter 10 ofthe Smoke Control Handbook. This algebraic equation method is based on (1) the idealized building, (2) flows calculated by the orifice equation, (3) effective areas, and (4) symmetry. It does not account for pressure losses in the stairwell from friction, but these losses tend to be small for stairwells when all stair doors are closed. CONTAM can analyze pressurized stairwells much more realistically than the algebraic equation method. Stairwell Fan Sizing Some designers size fans for pressurized stairwells using their own rules of thumb, which are generally in the range of 0.14 to 0.26 m3/s per floor. Such estimates can be appropriate for simple buildings such as those discussed previously. The primary factor regarding the amount of pressurization air needed is stairwell leak- age. Table 2 lists the supply air needed to pressurize stairwells as a function ofleakage classification. Ifthe fan is oversized, the amount of supply air can be adjusted during commissioning to achieve suc- cessful pressurization. Because of the high cost of replacing under- sized fans (including electrical wiring), rules of thumb chosen by designers usually incorporate an allowance for leakier construction than actually anticipated. Inc. ASHRAE, 2019 user. single for Licensed | {}
bc8a949d-db94-4f1e-86aa-c3902e0d5219 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Fire and Smoke Control 54.11 Chart Type: line Red Line Blue Line Green Line item_01 101.3Asp (Asoamperes) 25Asp (Asoamperes) 87Asp (Asoamperes) Fig. 13 Height Limit with Treated Supply Air in Winter Height Limit For some tall stairwells, acceptable pressurization may not be possible because ofindoor-to-outdoor temperature differences. Ac- ceptable pressurization is more likely with systems using untreated supply air than those using treated supply air. The height limit is the height above which acceptable pressur- ization is not possible for an idealized building. For the height limit to be applicable to a building, all the floors of the building must be the same or relatively similar. When using the height limit, shafts that are not pressurized are neglected. For standard atmospheric pressure at sea level, the height limit is FR(△p max △p min ) - Hm = 2.89 x 10 4 1 1 where ¦ Hm = ¦ height limit, m ¦ ¦ --- ¦ --- ¦ ¦ FR = ¦ flow area factor ¦ ¦ Ap max ¦ design pressure difference, Pa = maximum ¦ ¦ △p min = ¦ design pressure difference, Pa minimum ¦ ¦ To = ¦ absolute temperature outdoors, K ¦ ¦ Ts = ¦ absolute temperature in stairwell, K ¦ The flow area factor is A2SB(TB) F R = 1 + ABO(TS) (13) where (14) ASB = flow area between stairwell and building, m2 TB = absolute temperature in building, K ABO = flow area per stairwell between building and outdoors, m2 Ts = absolute temperature in stairwell, K Figures 13 and 14 show the height limit calculated from Equa- tions (13) and (14) for winter with treated and untreated supply air, respectively. The areas ASB and ABO are calculated using effective areas. The effective area of a system of flow areas is the area that results in the same flow as the system when it is subjected to the same pressure difference over the total system of flow paths. The effective area of any number of flow paths in parallel is Chart Type: line 0.0 0.5 1.0 1.5 2.0 2.5 3.0 item_01 200Hz 300Hz 400Hz 500Hz 600Hz 700Hz 800Hz Fig. 14 Height Limit with Untreated Supply Air in Winter n Ae = A i i=1 (15) and the effective area of any number of paths in series is -1/2 n 1 A e = i=1Ai (16) where A e effective area, m2 = Ai = flow area of path i, m2 Two examples (Figures 15 and 16) demonstrate evaluation ofASB and ABO. The areas on these figures include wall leakage through construction cracks or other paths, including gaps around doors, as appropriate for each section of wall. Figure 15 is a floor plan of a simplified open-plan office building. Because the height limit is based on symmetry, the area ABO is on a per-stairwell basis. Figure 15 shows the axis of symmetry, and flows and flow paths on one side of this axis are the mirror image of those on the other side. This fig- ure is geometrically symmetric, but the height limit also can be used for buildings where the building is only symmetric with respect to flow. In this figure, the areas between the building and the outdoors are Av, A2, andA3. These areas are in parallel, and based on Equation (15), ABO = A1 + A2 + A3. The areas between the stairwell and the building are A4 and A5, which are also in parallel. Based on Equation (15), ASB = A4 + A5. The stairwells of Figure 16 have unpressurized vestibules. As with Figure 15, ABO = A1 + A2 + A3. Calculating ASB involves flow areas both in parallel and in series. Equation (16) can only be used when no air is supplied to or exhausted from the spaces in the system of series paths. The effective area approach can be used because the only space in this path is an unpressurized vestibule. In Figure 16, the areas A5 and A6 are in parallel, so A56 = A5 + A6. The path through the vestibule is series, so from Equation (16), A456 = (1/A24 + 1/A256)-1/ 2. The paths A456 and A7 are in parallel, so ASB = A456 + A7. Example 4. For the simple building of Figure 17, (1) evaluate wind effect, (2) evaluate stack effect, and (3) determine the design capacity of the supply fans. The height of the building and stairwells is 33.5 m. The minimum and maximum design pressure differences are 25 and 87 Pa. Wind Effect. For this building, wind effect is not considered to be an issue because Inc. ASHRAE, 2019 user. single for Licensed | {}
468f05ea-da99-4f7f-b050-e0527243774b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 54.12 2019 ASHRAE Handbook-HVAC Applications (SI) · There are no windows or balcony doors that can be opened be- tween the building and the outdoors. · A centrifugal fan is used to minimize wind effect on the flow rate of pressurization air. (Wind effect can also be minimized by other kinds of fans, although this requires evaluation for the specific case.) For designs where wind effect is not minimized, CONTAM is recommended for analyzing the stair pressurization system. Stack Effect. Because the example building is only 1 1 stories tall, stack effect was not an issue. For larger buildings, the impact of stack effect should be analyzed. The winter outdoor design temperature is To = -15°C, and the building temperature is TB = 21°C. The atmospheric pressure is 101.3 kPa. Consider a heat transfer factor of n = 0.15. Because the building is simple, height limit can be used to evaluate stack effect. First, evaluate stack effect before stabilization; the first approach for this is to examine the height limit for the stairwell if pressurization air were treated. From Figure 14 with To = -15°C, the smallest value of height limit is about 45 m when ASB/ABO is near zero. The stairwell height is 33.5 m, which is less than the height limit. This means that stack effect is not an issue before temperature stabiliza- tion; consequently, it cannot be an issue after stabilization. Size Supply Fans: Because this building is simple, the rule of thumb method can be used to size the fans. Generally, rules ofthumb for pressurized stairwells are in the range of 0.14 to 0.26 m3/s per floor. The most important factor to consider in choosing a rule of thumb is the stairwell leakage, which primarily consists of the leakage of stairwell walls and stairwell doors. Construction of the stairwell is believed to be of average leaki- ness or higher. Table 2 lists supply air of0.11 m3/s per floor for aver- age leakage, and 0.26 m3/s per floor for high leakage. Because of the cost of replacing an undersized fan, the rule of thumb of 0.21 m3/s per floor is chosen. The stairwell has 1 1 floors, and fan capacity is 11(0.21) = 2.31 m3/s. Each stairwell is pressurized by one fan with capacity of 2.31 m3/s. Stairwells with Open Doors When any stair door is opened in a simple stairwell pressuriza- tion system, the pressure difference drops significantly. When all doors are closed suddenly in such a simple system, the pressure difference increases significantly. A compensated stairwell pres- surization system adjusts for changing conditions either by modu- lating supply airflow or by relieving excess pressure. The intent is to maintain acceptable pressurization when doors are opening and closing. In the United States, most codes do not require pressurized stairwells to be compensated, and such stairwells are designed to ![image](/image/placeholder) A3 STAIR A5 STAIR ] A4 I OPEN SYMMETRY PLAN OPEN OFFICE OF OFFICE PLAN AXIS I I A2 A 1 Note: This figure is geometrically symmetric, but height limit can be used for buildings where building is only symmetric with respect to flow. Fig. 15 Example for Effective Flow Areas of Building with Pressurized Stairwells maintain pressurization only when all the stair doors are closed. Traditionally, some engineers felt that pressurized stairwells needed to be compensated, but research projects by Klote (2004) and Ko and Lougheed (2016) show that noncompensated stairwell pressurization systems can maintain a tenable environment in the stairwell as long as the door on the fire floor remains closed, even if doors on other floors are opened. In computer simulations by Klote and fire experiments by Ko and Lougheed, the small amount of smoke that leaked through the gaps around a closed stair door was diluted by pressurization air and a tenable environment was maintained in the stairwell. When compensated stairwell pressurization systems are required, the systems described by Klote et al. (2017) can be used: barometric damper (BD), variable-air-volume (VAV), open exterior door (OED), and exterior vent (EV) systems. As with noncompensated stairwell pressurization systems, performance of compensated systems can be negatively affected by wind, and this needs to be taken into account during design. Compensated stairwell pressurization systems have the failure modes discussed in the following paragraphs. Barometric Damper (BD) System. This system has constant- supply airflow, which is designed to maintain acceptable pressuriza- tion with the required number of doors open. The supply air rate is not actually constant, but varies to some extent with pressure across the fan. For centrifugal fans, this flow variation is generally small. However, the term constant supply is used to differentiate this system from those where the supply air intentionally changes. When a stair door is closed, the excess supply air is relieved to the outdoors through one or more vents with barometric dampers. Barometric dampers tend to chatter because of the wind. This chatter can be so annoying that building maintenance staff some- times wire these dampers shut to stop the noise, which can lead to failure because of excessive stair pressurization. Because baromet- ric dampers are usually located on walls, wind can affect system ![image](/image/placeholder) A3 STAIR STAIR A7 I I I 4 OPEN OPEN OF A5 OFFICE OFFICE PLAN PLAN AXIS A6 I SYMMETRY VESTIBULE I I A2 I A 1 Note: This figure is geometrically symmetric, but height limit can be used for buildings where building is only symmetric with respect to flow. Fig. 16 Example for Effective Flow Areas of Building with Pressurized Stairwells and Unpressurized Vestibules ![image](/image/placeholder) 、 2 1 T T T T ~ STAIR STAIR STAIR STAIR OPEN OFFICE PLAN OPEN OFFICE PLAN FIRST FLOOR Floors 2 to 11 Symbols: Elevators Double Doors Single Door T Toilet Fig. 17 Office Building of Stairwell Examples Inc. ASHRAE, 2019 user. single for Licensed | {}
655b6672-e211-4b24-a7e3-2018202d18d4 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Fire and Smoke Control 54.13 performance more than with most other systems. If a BD compen- sated stairwell pressurization system is to be used, the design needs to mitigate damper chatter and any adverse wind effects. Variable-Air- v olume (VA V) System. In a VA v compensated stairwell system, the flow rate of supply air to the stairwell is adjusted to account for opening and closing of doors. The flow of supply air to the stairwell is controlled by multiple static pressure sensors that sense the pressure difference between the stairwell and the building. When doors are opened, the stairwell pressure drops and the flow rate of supply air is increased to achieve at least the minimum design pressurization. When all the doors are closed, stair pressure increases, and supply air is reduced to prevent excessive pressure differences. When a door is opened in the VA V system, the pressure in the stairwell drops, and it takes about 3 to 7 s for the pres- sure to recover to the initial value (Tamura 1990). When the last open door in a VA v system closes, there is a pres- sure spike that can be on the order of 250 Pa, which is extremely high compared to the usual pressure differences maintained by pres- surized stairwells. A person encountering such a peak would prob- ably not be able to open the stair door, but they could open it a minute or so later provided they knew to try. A person encountering such a peak may think the stair door was locked, and might not try to open it again. Wind can have an unusual and serious impact on VA V systems. During design analysis, engineers have encountered very high pres- sure differences during some wind conditions. For example, when an exterior door is opened during the design wind speed, there can be so much supply air that the pressure difference across some stair doors can exceed the maximum design value by as much as 100%, making it impossible or extremely difficult for occupants to enter the stairwell. A VAV compensated stairwell pressurization system design needs to deal with both the pressure spike and the effects of wind on the system. To address these potential failure modes, the design analysis needs to include simulations by network analysis computer program such as CONTAM. Open Exterior Door (OED) System. The open exterior door (OED) system has constant-supply airflow, and an exterior stairwell door that opens automatically on system activation. This system is sometimes called the Canadian system, because it originated in Canada and has been used extensively there. By eliminating opening and closing of the exterior stairwell door during system operation, the OED system eliminates the major source of pressure fluctuations. However, there can be security concerns about exterior doors that open automatically, so OED systems are suggested only for applications where this security issue is not a concern or where the concerns can be resolved with other measures. Exterior Vent (EV) System. The open exterior vent (EV) sys- tem is an alternative when security concerns prohibit using the OED system. An EV system has constant-supply airflow and an exterior vent that opens automatically upon system activation. The intent of this vent is to minimize the effect of opening and closing the exterior stair door. To minimize the effect of wind, it is suggested that the vent be near (and facing the same direction as) the exterior door. The size of the vent can be determined by CONTAM simulations. 12. PRESSURIZED ELEVATORS The elevator pressurization systems discussed in this section are intended to prevent smoke from flowing from the fire floor through an elevator shaft and threatening life on floors away from the fire floor. This section does not address smoke control for elevator evac- uation (see Chapter 12 of the Smoke Control Handbook). Usually, pressurized elevators are in buildings that have pressurized stair- wells, and this section assumes that these pressurization systems operate together. In the rare situation where pressurized elevators are the only pressurization smoke control system in a building, the information in this section may still be useful. Supply air for pres- surized elevators should be free or nearly free of smoke, as dis- cussed in the Smoke Feedback section. The information discussed in the section on Elevator Piston Effect can be used to evaluate the influence of piston effect on performance of pressurized elevator systems. The piston effect produces a pres- sure spike when a car passes a particular floor, and this happens for only a few seconds during the run of an elevator. For elevators in multiple-car shafts with car velocities less than 5 m/s, or for those in single-car shafts with car velocities less than 2.5 m/s, piston effect should not adversely affect performance of elevator pressur- ization. Design of pressurized elevators is much more complicated than design of pressurized stairwells, because (1) the building envelope often cannot effectively handle the large airflow resulting from both elevator and stairwell pressurization, and (2) open exterior doors on the ground floor can cause high pressure differences across the ele- vator shaft at the ground floor. Several systems discussed in this sec- tion can deal with this complexity, however. Usually, several exterior doors on the ground floor are open during a building fire: the fire service opens several exterior doors and keeps them open while fighting the fire. Occupants also open exterior doors during evacuation. The shaft pressurization system needs to operate as intended with these exterior doors open. Generally, a CONTAM analysis is needed to determine whether pressurized elevators and pressurized stairwells in a particular building can be balanced to perform as intended. Though it is theo- retically possible to use only a rule of thumb to design these sys- tems, a CONTAM analysis is strongly recommended. The following discussion is intended to provide an understand- ing about the elevator pressurization systems, and is based on 36 CONTAM simulations with a 14-story building (Figure 18). For a more detailed discussion of these simulations, see Chapter 1 1 of the Smoke Control Handbook. Elevator pressurization systems dis- cussed here are for use in buildings with pressurized stairwells. For these simulations, the pressure difference criteria are listed in Table 3. The leakage values and flow coefficients used for these simulations are listed in Tables 4 and 5. For the CONTAM simula- tions of the example building, supply air was injected only at the top of the elevator shafts, but for stairwells, about half the supply air was injected at the top of the stairs and the rest at the second floor. ![image](/image/placeholder) 53 m OFFICE OFFICE 2 1 SO 2 SPACE MS SPACE w S S SW T TV � I X � E X 35 OFFICE OFFICE SPACE SPACE GROUND FLOOR FLOORS 2 TO 14 SYMBOLS: MECHANICAL ELEVATOR ELEVATOR SPACE SHAFTS SO SECURITY OFFICE SW STAIRWELL SW SW 2 T TOILET SINGLE DOOR ++ DOUBLE DOOR MECHANICAL Note: Roof, elevator pits, and SPACE elevator mechanical room below ground floor are not shown. MECHANICAL PENTHOUSE (LEVEL 15) Fig. 18 Floor Plans of Example 14-Story Open Plan Office Building for Elevator Pressurization Study Inc. ASHRAE, 2019 user. single for Licensed | {}
efecba5c-0ecd-4c18-aae4-c76ae9e29cb3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 54.14 2019 ASHRAE Handbook- -HVAC Applications (SI) X-Axis: PRESSURE DIFFERENCE, Pa Y-Axis: FLOOR Chart Type: line Veny See Note 1 Vey Leaky Leaky Average item_01 2.5 3.5 4.5 2 Fig. 19 Elevator Pressure Differences for Basic Elevator Pressurization System Basic System In the basic system, each stairwell and elevator shaft has one or more dedicated fans that supply pressurization air. For reasons men- tioned previously, the basic system also includes stairwell pressur- ization, and the stair subsystems are not compensated. In most buildings, the basic system does not result in successful pressuriza- tion, so the systems discussed in this section add extra features to improve performance. For the example building with very leaky exterior walls, the CONTAM simulations showed that the basic system would perform well, but this was not so for with less leaky exterior walls. In Figure 19, for leaky exterior walls, the pressure difference across the ele- vator doors on the ground floor is about 130 Pa. For exterior walls of average leakage, the pressure difference across the elevator doors on the second floor is about 87 Pa, and at the ground floor it is about 470 Pa. These values exceed the maximum criterion used for elevator doors, which is 62 Pa (see Table 4). For average and leaky exterior walls, there is insufficient leakage in the building envelope to accommodate the large amount of pressurization air supplied to the shafts. With very leaky exteriors walls in the example building of Figure 18, Figure 19 shows that the basic system meets the pressure differ- ence criteria (Table 4). Air was supplied to each elevator shaft at 13. 1 m3/s, and to each stairwell at 3.09 m3/s. With very leaky exte- riors walls, there is enough wall leakage area to accommodate this large amount of pressurization air. For the few buildings that have very leaky building envelopes, the basic system can be a simple way to pressurize elevators and stairwells. The basic system also might work well for less leaky walls in other buildings. When a CONTAM analysis shows that the basic system does not work for a building, consider the systems discussed in the following sections. Exterior Vent (EV) System This system uses vents in the exterior walls to increase the leak- iness of the building envelope such that successful pressurization can be achieved. The vents are usually closed, but they open when the pressurization system is activated. These vents are relatively small and not intended to be a substitute for windows broken open by the fire service. Vents should be located to mitigate the potential for the wind to produce excessive pressures on the fire floor; one way to accomplish this is putting vents on each side of the floor, as shown in Figure 20. These vents may need fire dampers, depending on code requirements. Figure 20 is a typical floor of the example building with vents in the exterior walls. Vents can be sized to ensure that design criteria are met. In the example building, the vents were sized such that the amount of pressurization used for the basic system produced accept- able pressurization with the EV system in the example building. ![image](/image/placeholder) OFFICE SPACE WALL VENTS WALL VENTS OFFICE SPACE Note: Vents open when elevator and stairwell pressurization is activated. Fig. 20 Typical Floor Plan of Example Building with Exterior Vent (EV) System In Figure 20, the vents are in all four exterior walls to minimize any adverse effects of wind. The vent area should be proportional to the area of the exterior walls. If fewer vents are used, wind effects should be incorporated in the CONTAM analysis. With open exterior doors, it is not necessary to have exterior vents on the ground floor. Because the EV system may not be able to achieve acceptable pressurization with some or all the exterior doors closed, it may be necessary to have some of the exterior doors open automatically on system activation. The number of exterior doors that need to open automatically can be evaluated by CON- TAM analysis. The example building has an open office plan, but the EV system can be adapted to other buildings. Ducted flow paths can be installed from the vicinity of the unenclosed elevator lobbies to the outdoors. Such ducted paths can overcome the flow resistance of interior walls. The ducts can be located above suspended ceilings. Duct penetrations of a fire-rated wall may have fire resistance require- ments, depending on code specifications. Floor Exhaust (FE) System The FE system is a kind of zoned smoke control that reduces the amount of supply air used. In the FE system, a relatively small amount of air is supplied to the elevator shafts and the stairwells, and the fire floor is exhausted such that acceptable pressurization is maintained on that floor where it is needed. It is common to also exhaust one or two floors above and below the fire floor. As discussed in the section on Zoned Smoke Control, exhausting air from the fire floor and some floors above and below the fire floor benefits shaft pressurization. Often, this system can achieve suc- cessful pressurization in tall and very complicated buildings. Inc. ASHRAE, 2019 user. single for Licensed | {}
9bcf9e44-4076-4a76-a815-b248e7b15fb5 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Fire and Smoke Control 54.15 Table 3 Pressure Difference Criteria for Elevator Pressurization Simulations, Pa ¦ System ¦ Minimum ¦ Maximum ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Pressurized elevators ¦ 25 ¦ 62 ¦ ¦ Pressurized stairwells ¦ 25 ¦ 87 ¦ Note: Criteria are for elevator simulations discussed in this chapter, but some projects may have different criteria, depending on code requirements and requirements of spe- cific applications. Table 4 Flow Areas and Flow Coefficients of Doors Used for Elevator Pressurization Simulations ¦ Flow Path ¦ Flow Path ¦ Flow Coefficient ¦ Flow Area, m2 ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Single door, ¦ closed ¦ 0.65 ¦ 0.023 ¦ ¦ ¦ opened ¦ 0.35 ¦ 2.0 ¦ ¦ Double door, ¦ closed ¦ 0.65 ¦ 0.045 ¦ ¦ ¦ opened ¦ 0.35 ¦ 3.9 ¦ ¦ Elevator door, ¦ closed ¦ 0.65 ¦ 0.06 ¦ ¦ ¦ opened ¦ 0.65 ¦ 0.56 ¦ Note: Values were chosen for elevator simulations discussed in this chapter; flow areas and coefficients appropriate for design analysis of a specific building may be different. Table 5 Flow Areas and Flow Coefficients of Leakages Used for Elevator Pressurization Simulations ¦ Flow Path ¦ Leakage ¦ Flow ¦ Flow Area, ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ Classification ¦ Coefficient ¦ m2 per m2 of wall ¦ ¦ Exterior walls ¦ Tight ¦ 0.65 ¦ 0.50 x 10-4 ¦ ¦ ¦ Average ¦ ¦ 0.17 X 10-3 ¦ ¦ ¦ Loose ¦ ¦ 0.35 X 10-3 ¦ ¦ ¦ Very loose ¦ ¦ 0.12 x 10-2 ¦ ¦ Interior walls ¦ Loose ¦ 0.65 ¦ 0.35 x 10-3 ¦ ¦ Floor or roof ¦ Tight ¦ 0.65 ¦ 0.66 x 10-5 ¦ ¦ ¦ Average ¦ ¦ 0.52 X 10-4 ¦ ¦ ¦ Loose ¦ ¦ 0.17 x 10-3 ¦ ¦ ¦ ¦ ¦ m2 per m of wall ¦ ¦ Curtain wall gap ¦ Tight ¦ 0.65 ¦ 0.00061 ¦ ¦ ¦ Loose ¦ ¦ 0.0061 ¦ Note: Values were chosen for elevator simulations discussed in this chapter; flow areas and coefficients appropriate for design analysis of a specific building may be different. Typically, exhaust is through a shaft with a fan located in a mechanical floor or on the roof, and dampers between the shaft and the floors are closed on all floors when the system is not operating. On system activation, the dampers open on the floors to be exhausted. Where the code requires zoned smoke control, it may be necessary to pressurize one or two floors above and below the fire floor. The exhaust rates should be balanced so that the pressure differences from the elevator shaft to the building and from the stairwell to the building are acceptable. This acceptable pressuriza- tion meets the intent of the code. At floors not exhausted, pressure differences would be below the minimum design pressure differ- ence. Because the FE system only maintains acceptable pressure differences at the fire floor (and other floors that may be exhausted), use ofa FE system needs to be approved by the local code authority. As with the EV system, some of the exterior doors on the ground floor may need to open automatically upon system activation, and the number of such doors can be evaluated by the CONTAM analysis. For the example building, an FE system is shown in Figure 21. Simulations showed that each elevator shaft needed 7.14 m3/s, and each stairwell needed 1. 79 m3/s. The floor exhaust needed from the floors ranged from 2.28 to 2.55 m3/s. As with the EV system, the FE system can be adapted to other buildings. This can be done by having the exhaust draw from a space onto which the elevators and stairwells open. ![image](/image/placeholder) OFFICE EXHAUST SPACE SHAFT DAMPER OFFICE SPACE Note: Exhaust shaft has fan (not shown) located in mechanical penthouse, and dampers are closed on all floors when system is not operating. On system activation, dampers open on floors to be exhausted, and fan is activated. Fig. 21 Typical Floor Plan of Example Building with Floor Exhaust (FE) System ![image](/image/placeholder) SO ENCLOSED VENT ABOVE ELEVATOR DOORS LOBBY (See Note) Note: This vent needs fire damper and adjustable damper for balancing. Fig. 22 Ground Floor of Building with Ground-Floor Lobby (GFL) System Ground-Floor Lobby (GFL) System This system has an enclosed elevator lobby on the ground floor to reduce the tendency of open exterior doors to cause high pressure differences across the elevator shaft at the ground floor. The GFL system often has a vent between the enclosed lobby and the building to prevent excessive pressure differences across the lobby doors (i.e., the doors between the enclosed lobby and the building). The pressure difference across the lobby door and the elevator door depends on the area of the vent. There is no established criterion for the maximum pressure difference across the lobby doors, but the pressure should not be high enough to prevent the doors from remaining closed. This value depends on the specific doors and hard- ware. This discussion uses a maximum pressure difference for the lobby doors of87 Pa, but this value can be much different for specific applications. The vent should have a fire damper and a control damper in series. The control damper can be used to adjust the flow area of the vent so it can be balanced during commissioning. Figure 22 shows the ground floor of the example building with a GFL system. The intent ofthe elevator pressurization systems discussed in this chapter is to prevent smoke from flowing from the fire floor through an elevator shaft and threatening life on other floors. In the GFL system, the enclosed lobby on the ground floor protects the elevator from smoke from a fire on the ground floor. Thus, the minimum ele- vator pressure difference criterion of Table 3 does not apply to the ground floor for a GFL system. Table 6 lists the criteria used for the GFL system simulations. Successful pressurization consists of meeting these criteria. Inc. ASHRAE, 2019 user. single for Licensed | {}
7b673c0e-af1b-48a8-baaa-a497887fa1e7 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 54.16 2019 ASHRAE Handbook-HVAC Applications (SI) Table 6 Pressure Difference Criteria for GFL Elevator Pressurization Simulations, Pa ¦ Location ¦ Minimum ¦ Maximum ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Pressurized elevators on ground floor ¦ N/A ¦ 62 ¦ ¦ on other floors ¦ 25 ¦ 62 ¦ ¦ Pressurized stairwells on all floors ¦ 25 ¦ 87 ¦ ¦ Ground-floor elevator lobby door ¦ N/A ¦ 87 ¦ Note: These pressure differences are with doors to stairwell, elevator, and ground-floor lobby closed. Criteria are for GFL simulations discussed in this chapter; some proj- ects may have different criteria depending on code requirements and requirements of specific applications. For fires in high-rise buildings, the fire service frequently uses the elevators for rescue and for mobilization of firefighting equip- ment. When ground-floor lobby doors are opened, the pressure dif- ference may exceed the maximum pressure difference. If this can happen for a particular design, the fire service should be contacted to determine whether this is acceptable to them. Floor-to-floor leakage can significantly affect a GFL system's performance. This leakage consists of the leakage of the floor and that of the curtain wall gap (Table 6). 13. ZONED SMOKE CONTROL The traditional approach for HV AC systems is to shut them down during building fires, but HV AC systems can be operated in smoke control mode during building fires. Zoned smoke control consists of exhausting the zone of the fire and possibly pressurizing the sur- rounding zones. In addition to using the HV AC system, dedicated equipment can be used for zoned smoke control. Supply air for zoned smoke control systems should be free or nearly free of smoke, as discussed in the Smoke Feedback section. In zoned smoke control, a building is divided into several zones, each separated from the others by barriers. In the event of a fire, the zone with the fire is called the smoke zone, and the others are called the nonsmoke zones. Zones bordering on the smoke zone are called the surrounding zones. Either passive or pressurization smoke pro- tection is used to limit smoke spread beyond the smoke zone. Smoke control cannot make conditions tenable in the smoke zone, and occupants should evacuate the smoke zone as soon as possible. Some arrangements of smoke control zones are shown in Figure 23. In this figure, the smoke zone is indicated by a minus sign, and the surrounding zones are indicated by a plus sign. The smoke zone is often one floor of the building, but it can be the fire floor plus the floors directly above and below the fire floor. In a relatively low, sprawling building with several wings, the smoke zone can be part of a floor. When separate HVAC systems serve each zone, systems distant from the smoke zone and surrounding zones should only remain operating if the building pressurization produced by these systems does not adversely impact zoned smoke control system perfor- mance. Otherwise, they should be shut down. The traditional approach to zoned smoke control is to exhaust the smoke zone and to pressurize the surrounding zones, but other approaches have been used. Although fan-powered smoke exhaust is the most common method of treating the smoke zone, passive smoke control using smoke barriers may be satisfactory when fan- powered exhaust is not practical. Using exterior wall vents or smoke shafts to treat the smoke zone is not common, but these methods are discussed in Chapter 13 of the Smoke Control Handbook. Fan-powered pressurization or passive smoke control using smoke barriers can be used for the zones surrounding the smoke zone. Fan-powered pressurization of the surrounding zones has a negative consequence on stairwell pressurization, as discussed in the following sections. In this section, fan-powered pressurization is called pressurization, and fan-powered exhaust is called exhaust. ![image](/image/placeholder) + + SMOKE SMOKE } ZONE ZONE + + SMOKE ZONE IS ONE FLOOR SMOKE ZONE IS THREE FLOORS + SMOKE ZONE SMOKE ZONEIS ONE WING OF AFLOOR Notes: 1. In these figures, smoke zone is indicated by minus sign (一), and surrounding zones are indicated by plus sign (+). 2. Smoke zone can be treated by fan-powered exhaust or passive smoke control using smoke barriers. 3. Surrounding zones can be treated by fan-powered pressurization or passive smoke control using smoke barriers. Fig. 23 Some Arrangements of Smoke Control Zones When the floors or wings of a building are divided into many rooms with normally closed doors, these floors do not lend them- selves to the traditional concept of zoned smoke control. For such applications, a form of zoned smoke control can be used that relies on a combination of corridor exhaust and passive smoke control using smoke barriers. The passive protection tends to minimize smoke flow through the ceiling floor assembly during building fires. Some applications suitable for such an approach are hotel guest floors, apartment buildings, and some office buildings. Interaction with Pressurized Stairs The interaction ofzoned smoke control with pressurized stairwells can have a significant effect on pressure differences across the stair- well doors. The following discussion is about smoke zones that are one floor and surrounding zones consisting of one floor above and one floor below. However, the same kind of interactions can happen with smoke zones and surrounding zones that are more than one floor. The interaction between zoned smoke control and pressurized stairwells is shown in Figure 24. For zoned smoke control using both exhaust and pressurization, pressurization of the surrounding zones decreases the pressure difference △PSB across pressurized stairwell doors on these floors. This decreased pressure difference can result in failure of pressurized stairwells on the floors being pressurized. However, this failure mode is eliminated by using zoned smoke control that uses exhaust only. Ideally, exhaust and pressurization zoned smoke control should prevent smoke from reaching the floor above the smoke zone, and negative stairwell pressurization should not compromise tenability of the stairwell. The effectiveness of this depends on proper identi- fication of the fire floor. Properly maintained fire alarm systems are very good at identifying the location of a fire, but no system is per- fect. In some fires, the first smoke detector to activate was a floor or so above the fire floor. This can be attributed to any ofthe following: (1) smoke flowing through a complex route to a floor above the fire, (2) smoke detectors not working properly on the fire floor, and (3) signals from smoke detectors being misidentified. Regardless of the reason, when a fire floor is incorrectly identi- fied, the smoke zone is incorrectly chosen. In this situation, the failure mode is that inadvertent pressurization of the fire floor can Inc. ASHRAE, 2019 user. single for Licensed | {}
e11a55a1-b63e-4270-b8f2-8e4819ecfc57 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Fire and Smoke Control 54.17 ![image](/image/placeholder) PRESSURIZED STAIRWELL PRESSURIZED し SMOKE EXHAUSTED [ ZONE PRESSURIZED See Note 1 0 △p 발 0 △Psa SECTION OF BUILDING DESIRED STAIR STAIR PRESSURIZATION PRESSURIZATION WITH POTENTIAL FAILURE ZONED SMOKE CONTROL USING BOTH EXHAUST AND PRESSURIZATION ![image](/image/placeholder) PRESSURIZED STAIRWELL Notes: 1. Because of the potential for negative stairwell pressurization, zoned smoke control using both exhaust and EXHAUSTED pressurization is not recommended for tall buildings except as discussed in the Smoke See text. EXHAUSTED Zone Note 2 2. Zoned smoke control using only EXHAUSTED exhaust does not have the potential for negative stairwell pressurization that exists with zoned smoke control using both exhaust and pressurization. 0 APs 8 SECTION OF BUILDING STAIR PRESSURIZATION ZONED SMOKE CONTROL USING ONLY EXHAUST Fig. 24 Interaction Between Zoned Smoke Control and Pressurized Stairwells push smoke into the stairwells (probably into all stairwells serving the fire floor). This failure mode is more of a concern for tall build- ings, which are more difficult to pressurize acceptably, and for buildings with 10 or more stories, for which stairwell smoke pro- tection is more critical. Occupant density is another factor affecting the importance of stairwell smoke protection. Because of this failure mode, it is recommended that zoned smoke control using systems using both exhaust and pressurization not be used for tall buildings where protection ofthe stairwells is especially important. Alternatively, analyze this failure mode, including factors such as evacuation time, emergency response time, and probability ofusing the firefighter's smoke control station (FSCS) for corrective action. 14. ATRIUM SMOKE CONTROL Because ofthe lack of compartmentation in large-volume spaces, smoke protection for such spaces is important. This chapter considers a large-volume space to be at least two stories high, such as an atrium, exhibition center, enclosed shopping mall, arcade, sports arena, or airplane hangar. For simplicity, the term atrium is used generically here to mean any of these large spaces. Most atrium smoke control systems are designed to prevent exposure of occupants to smoke during evacuation; this is the approach described in this section. An alternative goal is to maintain tenable conditions even when occupants have some contact with smoke, as discussed in the section on Tenability Systems. The following approaches can be used to manage smoke in atriums: · Smoke filling. This approach allows smoke to fill the atrium space while occupants evacuate the atrium. It applies only to spaces where the smoke-filling time is sufficient for both deci- sion making and evacuation. For information about people movement and evacuation time, see Chapter 4 of the Smoke Control Handbook. The filling time can be estimated either by ![image](/image/placeholder) EXHAUST FAN SMOKE LAYER PLUME Z FIRE Fig. 25 Atrium Smoke Exhaust zone fire models or by Equations (15.1) and (15.2) in the Smoke Control Handbook. · Unsteady smoke exhaust. This approach exhausts smoke from the top of the atrium at a rate such that occupants have sufficient time for decision making and evacuation. It requires analysis of people movement and fire model analysis of smoke filling. · Steady smoke exhaust. This approach exhausts smoke from the top of the atrium to achieve a steady smoke layer height for a steady fire (Figure 25). A calculation method is given in the sec- tion on Equations for Steady Smoke Exhaust. Design Fires Analysis of the design fire is extremely important for atrium smoke control design, and an understanding of fire development is needed for such analysis. The intent of this section is to provide pre- liminary information of these topics. For more complete informa- tion, see Chapter 5 of the Smoke Control Handbook. By nature, fire is an unsteady process, but many design fires are steady fires. One ofthe most important aspects ofa design fire is the heat release rate (HRR). Other fuel properties (e.g., heat of combustion, soot yield) are not discussed here, because they are not used in the calculations in the Equation Method for Steady Smoke Exhaust section. How- ever, such fuel properties are needed for CFD simulations that include tenability analysis. A design scenario is an outline of events and conditions that are critical to determining the outcome of alternative situations or designs. In addition to the fire location and HRR, it may include many other conditions such as materials being burned, outdoor tem- perature, wind, status of the HVAC system, and doors that are opened and closed. When steady design fires are based on test data, it is accepted that the HRR of the steady fire is taken as the maximum HRR of the test data. For example, the HRR of upholstered furniture from test data is shown in Figure 26. For a sofa, the HRR grows to a maximum of about 3200 kW, then decreases as the fuel burns out. A sofa design fire could be unsteady based on the fire test data, or it could be a steady 3200 kW. A design analysis should include several design scenarios to ensure that the smoke control system will operate as intended. It is possible for an atrium project to have only one scenario, but most projects have two or three, and some complex projects require five or more. Inc. ASHRAE, 2019 user. single for Licensed | {}
1060ee43-a1ec-4333-8ff1-24806ed6b206 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 54.18 X-Axis: TIME, s Y-Axis: HEAT RELEASE RATE, kW Chart Type: line 0-200 200-300 300-400 400-600 600-900 700-1200 800-1200 900-1200 item_01 0kW 3000kW 0kW 2000kW 2500kW 2000kW 1500kW 0kW Fig. 26 HRR of Upholstered Sofa and Chair Fire Development The stages of fire development are useful when discussing fires. These stages are (1) growth, (2) flashover, (3) fully developed fire, and (4) decay. Not all fires go through all the stages, primarily because of fire suppression or a lack of fuel. The growth stage fol- lows ignition, and the early part of the growth stage is characterized by an abundance of air for the fire. During the growth stage, the fire often spreads from one object to another. The growth stage of a sofa fire is from ignition to the peak HRR of about 3200 kW. The growth stage is often characterized by the following equation: 2 (17) t 9 = 1000 g where 9 heat release rate, kW t time, s tg = growth time, s Such a growth stage is a called a t-squared fire, and typical growth times are listed in Table 7. Development of a room fire in the growth stage may seem gradual. Smoke rises above the fire to form a smoke layer under the ceiling. Typically, the fire spreads from object to object, while the temperature of the smoke layer increases. Flashover is a rapid change from a growth-stage fire to a fully de- veloped fire, and primarily occurs by thermal radiation. This radia- tion is from the flames, the smoke plume, and the hot smoke layer below the ceiling. Thin, easy-to-ignite materials (newspapers, drap- eries, etc.) near the fire are the first to burst into flame, and this is fol- lowed by ignition of the rest of the flammable materials in the room. In a room with a fully developed fire, everything that can burn is burning. A fully developed fire also is called a ventilation- controlled fire, because the HRR depends on the amount of air that reaches the fire. During a fully developed fire, flames generally ex- tend from the doorways or open windows of the fire room. A fully developed fire is characterized by inefficient combustion resulting in high carbon monoxide production. For a fully developed fire in room with one opening, the HRR within the fire room can be ex- pressed as 9 = 1260AwHw 1/2 where 9 = heat release rate of fully developed fire, kW Aw = area of ventilation opening, m2 Hw = height of ventilation opening, m (18) 2019 ASHRAE Handbook- - HVAC Applications (SI) Table 7 Typical Fire Growth Times ¦ t-Squared Fire ¦ Growth Time tg s ¦ ¦ --- ¦ --- ¦ ¦ Slow ¦ 600 ¦ ¦ Medium ¦ 300 ¦ ¦ Fast ¦ 150 ¦ ¦ Ultrafast ¦ 75 ¦ Note: Growth times from NFPA Standards 92 and 204. For example, a fully developed fire in a room with a single door 1.07 by 2.13 m has an HRR of 4190 kW. The decay stage is a decrease in the HRR, which results from either fuel consumption or fire suppression. As the fuel is consumed, the fire may change from ventilation controlled to fuel controlled. Sprinklers Sprinklers are used extensively because they effectively suppress fires. The possible responses to sprinkler spray include (1) HRR de- cay, (2) constant HRR, or (3) an increase in HRR. The first two re- sponses might be considered successful suppression, but in the third case, the sprinkler spray is overpowered by the fire. Sprinkler actuation depends on the temperature and velocity of the gases flowing by the sprinkler and on the responsiveness of the sprinkler. The responsiveness of a sprinkler is characterized by the response time index (RTI). In a fire, a ceiling jet ofhot gases flows in a radial direction from where the smoke plume contacts the ceiling. The RTI of standard-response sprinklers is greater than or equal to 80 m 1/2 · s1/2; fast-response sprinklers' RTIs are equal to or less than 50 m 1/2, s1/2. Computer programs can use the RTI and cor- relations for the ceiling jet to predict sprinkler actuation time, and some zone fire models (including CF AST, discussed in the section on Zone Fire Modeling) have this ability. In spaces with high ceilings (greater than about 8 or 1 1 m), the temperature of the smoke plume can drop so much that sprinklers may not activate, or activation may be so delayed that the spray can evaporate before it reaches the fire. Sprinklers in an atrium could have some beneficial effect, but for design purposes they are con- sidered not effective in an atrium. However, they are usually consid- ered effective for fires in communicating spaces (i.e., a space with an open pathway to an atrium, such that smoke from a fire in either the atrium or the communicating space can move from one to the other without restriction). Fires in communicating spaces are often included in design scenarios. Shielded Fires A fire can be shielded from the sprinkler spray if an obstruction is between the sprinkler and the fire. Not only does the obstruction shield the fire from the water spray, but it also prevents the usual for- mation of a smoke plume. Because the smoke plume of a shielded fire can be very different from that of an unshielded fire, the sprin- kler actuation time of shielded fires must not be calculated by the computer methods mentioned previously. Two models have been developed for the HRR of shielded fires, based on test data. At NIST, fire tests were based on a few field observations of fuel loadings in office buildings (Madrzykowski and Vettori 1992), with a peak HRR of shielded fires of 500 kW. At the National Research Council of Canada (NRCC), fire tests were based on extensive field observations of fuel loadings in many buildings (Lougheed 1997), with a peak HRR of shielded fires of 1000 kW. Inc. ASHRAE, 2019 user. single for Licensed A peak HRR of 1000 kW is suggested for most shielded fires, and an HRR of 500 kW for locations where fuel is limited, such as in a showplace office of the president of a large corporation. | {}
ce630c84-edbd-4205-acfc-17e4ea64d6e8 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Fire and Smoke Control 54.19 Transient Fuels Transient fuels are materials that are in a space temporarily. Examples include seasonal decorations, paint and solvents in stair- wells during redecorating, unpacked foam cups in cardboard boxes after delivery, cut-up cardboard boxes awaiting removal, uphol- stered furniture after delivery, stacked folding chairs, and materials from special events such as parties or dinners. Sometimes, tran- sient fuels remain in place for long periods: for instance, polyure- thane-filled mattresses delivered to a dormitory and waiting for distribution in the next school year, automobiles on display in a shopping mall, boats and campers on display in an arena, and a two-story wood frame house built for display inside a shopping mall. Transient fuel is likely to accumulate at most locations in a building, except where it would block the usual paths of heavy traf- fic. Itis unlikely that a commonly used building entrance or corridor would be blocked by transient fuel, but there could be accumula- tions next to a wall near the entrance or in the corridor. Location can play a key role in transient fuels. Consider a sofa with polyurethane foam padding that is delivered for the office of the corporate president. Because the sofa is new and clean, it is decided to temporarily leave it in the nearby atrium until it can be moved to the president's office. In a corridor of an office building, the fuel could be trash consisting of any number of things such as an old upholstered chair or cardboard boxes with packing materials. Suggested Fire Sizes In many atriums, fuel loading is severely restricted with the intent of restricting fire size. Such atriums are characterized by inte- rior finishes of metal, brick, stone, or gypsum board and furnished with objects made of similar materials, plus plants. In this chapter, a heat release rate per floor area of 225 kW/m2 is used for a fuel- restricted atrium, and 500 kW/m2 is used for atriums containing fur- niture, wood, or other combustible materials. These heat release rates per unit floor area are from Morgan (1979) and Morgan and Hansell (1987). In a fuel-restricted atrium, transient fuels must not be overlooked when selecting a design fire. The minimum fire is often considered as occupying 9.29 m2 of floor area. The HRR of the minimum transient fire is (225 kW/m2)(9.29 m2) = 2100 kW. The HRR of the minimum fire with combustibles is (500 kW/m2) (9.29 m2) = 4600 kW. However, the area involved in fire can be much greater, and large fires can easily occupy 22 to 52 m2 of floor area. This translates to large fires ranging from 1 1 000 to 26 000 kW. Table 8 lists some steady design fires, but an engineering anal- ysis as discussed in Chapter 5 of the Smoke Control Handbook can result in different fire sizes. The large fires in Table 8 are not often used for design, but they represent an atrium with a large amount of fuel such as many upholstered sofas and chairs. Atrium Smoke Filling Atrium smoke filling is only applicable to very large atriums. Atri- um smoke filling time can be calculated by empirical equations for steady fires and for t-squared fires in NFPA Standard 92 and Chapter 15 ofthe Smoke Control Handbook. These equations are based on the conventional approach of keeping smoke from coming into contact with occupants during evacuation. In very large atriums, smoke can often be diluted to the extent that a tenable environment is main- tained for some time in the smoke layer at the top of the atrium. De- sign analysis of atrium filling is usually done with CFD modeling and tenability analysis (see the section on Tenability Systems). Loss of Buoyancy in Atriums For some applications, loss of buoyancy can cause the smoke layer to descend and threaten occupants. There is little research on this event, but the geometry of the large-volume space and the fire's Table 8 Steady Design Fire Sizes for Atriums ¦ ¦ kW ¦ ¦ --- ¦ --- ¦ ¦ Minimum fire for fuel-restricted atrium ¦ 2100 ¦ ¦ Minimum fire for atrium with combustibles ¦ 4600 ¦ ¦ Large fires ¦ 11 000 to 26 000 ¦ Note: These fire sizes apply to fire in the atrium space, but not to fires in communicat- ing spaces in fully sprinklered buildings. heat release rate are major factors. Spaces that are unusually large or unusually long are of particular concern; for these cases, draft curtains can divide up the atrium into several smaller spaces. Theo- retically, CFD modeling can predict loss of buoyancy in a large- volume space, but this has not been experimentally verified. Minimum Smoke Layer Depth The ceiling jet and smoke flow under the jet each have a depth of about 10% ofthe floor-to-ceiling height. Thus, the minimum smoke layer depth should be 20% of the floor-to-ceiling height, except when an engineering analysis using full-scale data, scale modeling, or computational fluid dynamic (CFD) modeling indicates other- wise (see the section on CFD Modeling). For information about scale modeling and full-scale fire testing, see Chapters 21 and 22 of the Smoke Control Handbook. Makeup Air Makeup air needs to be provided to ensure that exhaust fans can move the design air quantities and to ensure that door-opening force requirements are not exceeded. Makeup air can be provided using fans, openings to the outdoors, or both. Supply points for makeup air need to be below the smoke layer. Makeup air should be free or nearly free of smoke, as discussed in the section on Smoke Feedback. Makeup air can be provided by mechanical fans or openings to the outdoors (e.g., opened doors or windows). When makeup air is supplied by fans, the makeup air system should be designed to pro- vide 85 to 95% of the exhaust mass flow rate (not volumetric flow rate). The remaining 5 to 15% of makeup air enters as leakage through cracks in the construction, including gaps around closed doors and windows. Evaluation of this leakage needs to take energy standards into account. Makeup air fans can be activated concurrent with smoke exhaust fans, but the flow rate of makeup air fans should always be less that of the smoke exhaust fans. When makeup air enters through openings to the outdoors, (1) the mass airflow through these openings should be considered the same as that of the smoke exhaust, and (2) the openings need to be opened automatically before the smoke exhaust fans are activated. Hadjisophocleous and Zhou (2008) and Zhou and Hadjiso- phocleous (2008) show that, for makeup air velocities exceeding 1.02 m/s, the plume can be deflected, resulting in an increase in smoke production. For even higher velocities, the plume and smoke layer can be disrupted. The maximum air velocity must not exceed 1.02 m/s if the makeup air could come into contact with the smoke plume, unless a higher velocity is supported by engineering analy- sis. A secondary reason for the 1.02 m/s restriction is that it reduces the potential for fire growth and spread caused by airflow. For sys- tems using fans, the exhaust fans should operate before the makeup air system does. A CFD study of makeup air velocity conducted at the Univer- sity of Maryland supports higher makeup air velocities higher than 1.02 m/s, provided that there is an appropriate increase in smoke exhaust flow rate and that the higher velocity does not increase fire spread or growth (ASHRAE research project RP-1600; Pongratz et al. 2016). The study examined 1, 2.5, and 5 MW fires. A method of determining the increase in smoke exhaust was developed, and one Inc. ASHRAE, 2019 user. single for Licensed | {}
82a4060f-10a2-4203-a814-8f21144c37aa | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 54.20 of the factors is the height of the makeup air supplied relative to the flame height. When makeup air is supplied through openings, the wind can affect makeup air velocity. When makeup air openings are on walls facing different directions, wind can increase the makeup air velocity. A simple approach is to have all makeup air openings on walls facing the same direction. Although many code authorities do not require it, a wind analysis is suggested to mitigate the possibil- ity of excessive makeup air velocity when makeup air openings are on walls facing different directions. Stratification and Detection A layer of hot air often forms under the ceiling of an atrium be- cause of solar radiation on the atrium roof. Although no studies have been made of this stratification layer, building designers indicate that its temperature can exceed 50°C. Temperatures below this layer are controlled by the building's heating and cooling system. When the average temperature of the plume is lower than that of the hot-air layer, a stratified smoke layer will form beneath the hot- air layer. In this situation, smoke cannot be expected to reach the atrium ceiling, and smoke detectors mounted on that ceiling cannot be expected to go into alarm. Beam smoke detectors can overcome this detection difficulty. The following approaches can provide prompt detection regardless of air temperature under the ceiling when a fire begins: Inc. ASHRAE, 2019 user. single for Licensed · Upward-Angled Beam to Detect Smoke Layer. One or more beams are aimed upward to intersect the smoke layer regardless of the level of smoke stratification. For redundancy, more than one beam smoke detector is recommended. Advantages include not needing to locate several horizontal beams, and minimized risk of false activation by sunlight (a risk with some beam smoke detectors), because the receivers are angled downward. Review the manufacturer's recommendation when using beam smoke detectors for this application, because some beam detectors are not recommended for upward-angled installation. · Horizontal Beams at Various Levels to Detect Smoke Layer. One or more beam detectors are located at roof level, with addi- tional detectors at lower levels. Exact beam positioning depends on the specific design, but should include beams at the bottom of identified unconditioned spaces and at or near the design smoke level, with several beams at intermediate positions. · Horizontal Beams to Detect Smoke Plume. Beams are arranged below the lowest expected stratification level. These beams must be close enough to each other to ensure intersection of the plume; spacing should be based on the width of the plume at the least ele- vation above a point of fire potential. All components of a beam smoke detector must be accessible for maintenance, which may require maintenance openings in walls or the roof depending on the application. Equation Method for Steady Smoke Exhaust This section describes the algebraic equation method for analy- sis of atrium smoke control systems with a steady fire. A steady atrium smoke exhaust system has a steady smoke layer interface and a fire with a constant HRR. The smoke layer interface is an ide- alized concept described in the section on Zone Fire Modeling, and the equations used here are used in some zone fire models. There is some diluted smoke below the smoke layer interface, but this diluted smoke is considered insignificant. CFD modeling can cal- culate tenability of this diluted smoke. For a case study of an engineering analysis for a three-story atrium that uses the algebraic equations of this section, see Chap- ter 16 of the Smoke Control Handbook. This case study addresses (1) the impact of wind, (2) determination of the minimum smoke layer depth, (3) system activation with a stratified hot-air layer, (4) 2019 ASHRAE Handbook- -HVAC Applications (SI) analysis of design scenarios, (5) calculation of smoke exhaust for a fire in the atrium, (5) calculation of smoke exhaust for a fire with a balcony spill plume, (6) determination of makeup air, and (7) evaluation of the number of exhaust inlets and separation between them to prevent plugholing. Readers who need to analyze atriums by the equation method may want to use AtriumCalc (Klote 2014), which uses common routines for designing atrium smoke control systems. For example, one routine calculates the smoke exhaust needed to maintain a steady smoke layer height when there is a steady design fire in the atrium with an axisymmetric plume. Each routine can be printed on a page suitable to be inserted in an engineering report. The page consists of a relevant figure, the equations used for calculation, input, and output. Other routines address balcony spill plumes, window plumes, preventing plugholing, and opposed airflow. For an atrium fire, most of the heat flows upward in the smoke plume, and practically the rest of the heat leaves the fire by radia- tion. Heat transfer from fires by conduction is negligible. The con- vective heat release rate is expressed as qc = Xc9 where (19) Xc = convective fraction qc = convective heat release rate, kW q = heat release rate, kW The convective fraction depends on the material being burned, heat conduction through the fuel, and the radiative heat transfer of the flames, but a value of0.7 is usually used. For fire reconstruction, the specific value of the fuel being burned must be used. Fire in Atrium For a fire in an atrium, the mass flow rate of the plume is usually calculated by the empirical plume equations for axisymmetric plumes. Theoretically, an axisymmetric plume has a round cross section, but the plumes of many burning objects behave like an axisymmetric plume at some distance above the fire. For a distance above the base of fire z equal to or greater than the limiting elevation Zp the mass flow of the plume is m = 0.071qc1/3z5/3 + 0.0018qc For z < ZI, the mass flow of the plume is (20) m = 0.032qc3/5z where m mass flow in axisymmetric plume at height z, kg/s qc = convective heat release rate of fire, kW z = distance above base of fire to smoke layer interface, m ZI = limiting elevation, m (21) The limiting elevation is approximately the average flame height, which is ZI = 0.166qc 2/5 (22) For a burning solid (e.g., chair, sofa, desk), the base of the fire is some distance above the floor (see Figure 25). When a flammable liquid has spilled and is burning, the base of the fire is at the floor. Figures 27 and 28 show the smoke layer temperature and the smoke exhaust rate for fires in an atrium with an axisymmetric plume. The mass flow was calculated from the preceding equa- tions, and the smoke layer temperature and volumetric flow were calculated by equations discussed in the following sections. As Z increases, the smoke layer temperature decreases (Figure 27) as a consequence of air being entrained by the plume as it rises. The | {}
1bdd7bc4-6f7d-48b2-91d0-6bf424875884 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Fire and Smoke Control 54.21 plume mass flow increases with height, and plume temperature decreases with height. Figure 28 shows that as Z increases, the smoke exhaust rate increases. Example 5. For a 2100 kW fire in an atrium with a distance from the base of the fire to the smoke layer interface of 1 1 m, what is the mass flow of the plume? The parameters are: q = 2100 kW, z = 11 m, and Xc = 0.7. 9c = Xc9 = 2100(0.7) = 1470 kW The limiting elevation is °C TEMPERATURE SMOKE Chart Type: line AMBIENT_TEMPERATURE item_01 4600kW Fig. 27 Smoke Layer Temperature for Steady Smoke Exhaust Systems Chart Type: line Q Q2 Q3 Q4 item_01 26000m3/s 21000m3/s 4600m3/s 11000m3/s Fig. 28 Smoke Exhaust Rate for Steady Smoke Exhaust Systems ZI = 0.166q2/5 = 0.166(1470)2/5 = 3.1 m Because Z is greater than Zp the mass flow of the plume is calculated with the following equation: m = 0.071ql/3z5/3 + 0.0018qc = 0.071(1470)1/3(11)5/3 + 0.0018(1470) m = 46.6 kg/s Fire in Communicating Space For a fire in a communicating space, usually the mass flow rate ofthe plume is calculated by balcony spill plume equations. The fol- lowing equations are based on extensive research, including scale model fire experiments, full-scale fire experiments, and analytical studies (Ko et al. 2008; Law 1986; Lougheed and McCartney 2008a, 2008b; Lougheed et al. 2007; McCartney et al. 2008; Morgan and Marshall 1979). The equations were developed for fire room and balcony geom- etry similar to that of Figure 29. If the geometry is different, CFD modeling is recommended. For plume height Zb less than 15 m above the balcony edge, the mass flow of the plume is m = 0.36(qW2)1/3(zb + 0.25H) (23) Note: the mass flow equations and regions of applicability for the equations listed here have been corrected. NFPA issued errata cor- recting balcony spill plume equations in NFPA Standard 92-2012. There is an erratum for the bounds of one of these equations in the Smoke Control Handbook. For Zb ≥ 15 m and plume width of less than 10 m, mass flow of the plume is m = 0.59q2/3W1/5(zb + 0.17W7/15H + 10.35W7/15 - 15) (24) For Zb ≥ 15 m and plume width between 10 and 14 m, the mass flow of the plume is m = 0.2(qcW2)1/3(zb + 0.51H + 15.75) (25) where m mass flow rate in plume, kg/s 9 = heat release rate, kW qc = convective heat release rate of fire, kW W = width of the spill, m Zb = height of plume above balcony edge, m H = height of balcony above fuel, m Physical barriers can be used to restrict the horizontal spread of smoke under the balcony. Draft curtains used for this application must extend at least 10% of the floor-to-ceiling height below the ![image](/image/placeholder) SMOKE LAYER OFFICE DOORWAY DRAFT (See Note 1) CURTAIN Zp OFFICE W VIEW OF DOOR WITH DRAFT CURTAIN H b Notes: 1. Doorway height of fire room is not more than 90% of H. SECTION VIEW 2. Atrium smoke exhaust is not shown. Inc. ASHRAE, 2019 user. single for Licensed Fig. 29 Balcony Spill Plume | {}
f11c32a7-b2e5-44ec-b1c5-44d1436eedf1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 54.22 balcony. In almost all U.S. and Canadian applications, there are no draft curtains to restrict flow as shown in Figure 29. Without draft curtains, the spill width is estimated as W = w+ b where (26) W = width of spill, m W = width of opening from area of origin, m b = distance from opening to balcony edge, m Example 6. For a 1000 kW shielded fire in a communicating space as shown in Figure 29, calculate the mass flow of the balcony spill plume. There are no draft curtains to restrict the smoke flow under the balcony. The parameters are 9 = 1000 kW, Zb = 8 m, H = 3.4 m, b = 1.8 m, and W = 4 m. The width of the spill is W = w+ b = 5.8 m Because Zb is less than 15 m, Equation (23) is used to calculate the mass flow of the balcony spill plume: m = 0.36(qW2)1/3(zb + 0.25H) = 0.36[1000(5.8)2]1/3 [8 + 0.25(3.4)] = 103 kg/s Smoke Layer Temperature The smoke layer temperature is calculated from (27) Kqc Ts = To + mCp where Ts = smoke layer temperature, °C To = ambient temperature, °C K = fraction of convective heat release contained in smoke layer qc = convective heat release rate, kW 8 = specific heat of plume gases, 1.0 kJ/(kg·K) m = mass flow rate of plume where it enters smoke layer, kg/s Equation (27) applies to both axisymmetric plumes and balcony spill plumes. For atrium smoke control systems, it is believed that K varies from 0.5 to 1.0. For calculating the volumetric flow rate of smoke exhaust with Equation (23), use K = 1.0 because it results in the highest smoke exhaust, which is conservative. For plugholing calculations (see the following section on Number of Exhaust Inlets), use K = 0.5 because it results in the largest number of exhaust inlets, which is also conservative. Other values of. K may be used for these applications if they are supported by test data or an engineering analysis. The mass flow rate is calculated from Equa- tions (20) or (21). Inc. ASHRAE, 2019 user. single for Licensed Volumetric Flow of Smoke Exhaust Volumetric flow of smoke exhaust is m V= P where (28) V = volumetric flow rate of smoke exhaust, m3/s m = mass flow rate of smoke exhaust, kg/s p = density of smoke, kg/m3 The density of smoke can be calculated from Patm p = RT S (29) where p = density of smoke, kg/m3 Patm = atmospheric pressure, Pa 2019 ASHRAE Handbook HVAC Applications (SI) R = gas constant, 287 J/(kg K) Ts = absolute temperature of smoke, K The standard atmospheric pressure Patm many locations is for provided in Chapter 2 of the Smoke Control Handbook. Example 7. What is the volumetric flow rate for the mass flow rate from Example 5? A few minutes after system activation, the air temperature in the atrium is the same as that of the outdoors, and the largest volu- metric flow rate happens during summer when it is hot outdoors. The summer outdoor design temperature is 35°C. The parameters are To = 35°C, m = 46.6 kg/s, qc = 1470 kW, Cp = 1.0, R = 287 J/(kg·K), and Patm = 101.3 kPa. For calculation of smoke exhaust, K = 1. Kqc 1(1470) Ts = To + = 35 + = 67°C (340 K) mCp 46.6(1) Patm = = 1.04 kg/m 101 300 3 p = RTs 287(340) Number of Exhaust Inlets When the flow rate of a smoke exhaust inlet is relatively large, cold air from the lower layer can be pulled through the smoke layer into the smoke exhaust. This phenomenon is called plugholing. Multiple exhaust air inlets may be needed to prevent plugholing. The maximum volumetric flow rate that can be exhausted by a sin- gle exhaust inlet without plugholing is calculated by 1/2 T T V. = 4.16yd5/2 max where (30) Vmax plugholing at Ts, m3/s maximum volumetric flow rate without Ts temperature of smoke layer, K = absolute To ambient temperature, K = absolute d = depth of smoke layer below lowest point of exhaust inlet, m Y = exhaust location factor The ratio d/Di should be greater than 2 where Diis the diameter of the exhaust inlet. For exhaust inlets centered no closer than 2Di from the nearest wall, y= 1 should be used; for less than 2Di, y=0.5 should be used. For exhaust inlets on a wall, use y= 0.5. For rectan- gular exhaust inlets, calculate Di as 2ab Di= a + b where a = length of the inlet, m b = width of the inlet, m (31) The variables a and b can be in any unit of length provided that they are both in the same units. For square inlets, Di equals the side of the square. Where multiple inlets are needed to prevent plugholing, the minimum separation between inlets should be where (32) Smin = 0.9Ve 1/2 Smin m minimum edge-to-edge separation between inlets, Ve = volumetric flow rate of one exhaust inlet, m3/s Example 8. For the fire of Example 7, determine the number of smoke exhaust inlets and the minimum separation between them to prevent plugholing. The smoke layer is 3.2 m deep. Because the inlets in the ceiling are far from walls, Y = 1. Plugholing will be calculated for an ambient temperature of 21°C. The parameters are Y = 1, d = 3.2 m, To = 21°C (294 K), m = 46.6 kg/s, qc = 1470 kW, Cp = 1.0, and V = 44.8 m3/ s. For calculating the number of exhaust inlets, K = 0.5. | {}
69da366e-a887-49cb-b6ae-615472ce7677 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Fire and Smoke Control 54.23 Kqc 0.5(1470) Ts = To + = 21 + = 36.8°F (309.8 K) mCp 46.6(1.0) 1/2 Ts- T。 V = 4. 16yd5/2 max T 1/2 309.8 - 294 = 4.16(1)(3.2)5/2 = 17.7 m3/s 294 VIVmax is 44.8/17.7 = 2.6. This means that at least three inlets are needed to prevent plugholing. Ve = 44.8/3 = 14.93 m3/s Smin = 0.9V。1/2 = 0.9(14.93)1/2= 3.48 m Ve = 44.8/3 = 14.93 m3/s Smin = 0.9Ve 1/2 = 0.9(14.93)1/2= 3.48 m An inlet velocity of 7.5 m/s is chosen. The area of each inlet is 14.93/7.5 = 1.99 m2. An inlet size of 1.3 by 1.53 m is chosen, and Di = 2ab/(a + b) = 2(1.3)(1.53)/(1.3 + 1.53) = 1.41 m. Then d/Di = 3.2/1.41 = 2.27, which meets the stipulation that this ratio has to be greater than 2. These calculations indicate that the edges of the inlets need to be at least 3.48 m apart from each other, and at least 2Di (2 X 1.41 = 2.82 m) from the nearest wall. If the edges of any inlets are closer to a wall, the calculations should be repeated with Y = 0.5. If the inlets were in the walls, Y would be 0.5. Zone Fire Modeling Zone fire modeling is a simple approach to simulating smoke transport. The idea of the zone fire model came from observations in early room fire experiments that a smoke plume rises above the fire, and a smoke layer forms under the ceiling. As the fire continues, the smoke layer descends, and smoke may flow out of doorways (a doorjet). A zone fire model considers a fire compartment to be made up of an upper smoke layer and a lower nonsmoke layer. The mass flows of the smoke plume and the doorjet are calculated from empirical equations. For the zone model idealization, temperature and con- centrations of constituents are considered to be constant throughout each layer. These properties change only as a function of time. Most zone models consider that ceilings are flat and that rooms have uniform cross-sectional areas. The height of the discontinuity between these layers (the smoke layer interface) is considered to be the same everywhere. In the idealized model at an infinitesimal distance above the interface, the temperature and contaminant con- centrations are those of the smoke layer. At an infinitesimal distance below the interface, the temperature and contaminant concentra- tions are those of the lower layer. Even with these simplifications, zone fire models have proven to be very useful tools for many appli- cations, but they must be used with care. Because different zone models use different empirical equations implemented in different ways, the predictions of different zone models vary to some extent. Many zone models were developed in the 1980s, and often had poor numerical convergence. CFAST is a multiroom zone fire model that has superior numerical convergence, many features, and a graphical interface (Peacock et al. 201 7), and has been verified with full-scale fire data. CFAST and its documentation are available from NIST at no cost from pages.nist.gov/cfast. Probably for these reasons, CFAST has become the de facto standard zone fire model. CFAST can be used to simulate atrium smoke filling, and is useful for calculating sprinkler activation time. To help new users of this model get started, Chapter 18 of the Smoke Control Handbook has general information about zone models plus some CFAST user information. CFD Modeling Atrium smoke control can be analyzed by CFD modeling. For general information about CFD modeling, see Chapter 13 of the 2017 ASHRAE Handbook-Fundamentals. For information about fire applications of CFD modeling, see Chapter 20 of the Smoke Control Handbook. The idea of CFD is to divide the space of interest into a large number of cells and to solve the governing equations for each cell. Often, millions of cells are necessary for atrium applications. The number of cells in the model should be large enough to simulate airflows around modeled obstructions faithfully, and this can be evaluated by a sensitivity analysis of cell size. Obstructions such as walls, balconies, and stairs should be taken into account, and conditions at the boundaries defined. Exhaust flow at or near the top of the atrium is specified, and makeup air conditions are also defined. This allows simulation of fluid flow in considerable detail. Although CFD modeling has significant advantages in realisti- cally simulating smoke flow, it is computationally intensive and requires a lot of computer memory and time; it is not uncommon for a CFD simulation to run for many hours and sometimes days. CFD produces so many numbers that graphical methods are needed to understand both general trends in the atrium and nuances in local- ized conditions. Several general-purpose CFD models are commercially avail- able that can be used for atrium smoke control. NIST has devel- oped the Fire Dynamics Simulator (FDS) model (McGrattan et al. 2019) with visualization software called Smokeview (Forney 2019). FDS, specifically developed and verified for fire applica- tions, can be obtained from NIST at no cost (pages.nist.gov/fds -smv/) and has become the de facto standard CFD model for fire applications. 15. TENABILITY SYSTEMS The smoke control systems previously discussed are convention- al systems intended either to keep smoke away from occupants or to allow only incidental smoke contact deemed to be negligible. Ten- ability systems are different: they are designed to allow occupants to come into contact with smoke provided that a tenable environment (i.e., one in which combustion products, including heat, are limited to a level that is not life threatening) is maintained. Analysis ofa ten- ability system consists of a smoke transport analysis and a tenability evaluation. Tenability Evaluation Toxic gas, heat, and thermal radiation exposure are direct threats to life, the severity of which depends on the intensity and duration of exposure. Tenability evaluation considers the effects of exposure to these threats, as well as reduced visibility. Reduced visibility does not directly threaten life, but it is an indi- rect hazard. It can reduce walking speed; also, when occupants and firefighters cannot see well, they can become disoriented and cannot get away from the smoke, thus prolonging their exposure. Another concern is that a disoriented person can fall from an atrium balcony, which can be fatal. Inc. ASHRAE, 2019 user. single for Licensed For information about calculating the effects of exposures to combustion gases and reduced visibility, see Chapter 6 of the Smoke Control Handbook. There is no broad consensus, but suggested vis- ibility criteria range from 4 to 14 m. When combustion products from most materials are diluted enough to meet such visibility cri- teria, the hazards to life from toxic gases, heat, and thermal radiation are also eliminated for exposures up to 20 min. This means that, for | {}
1cca11d3-afa3-4f3d-b42d-cdd009339024 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 54.24 2019 ASHRAE Handbook- -HVAC Applications (SI) most fires, tenability can be evaluated by calculating visibility, but the hazards of other exposures must also be checked. CFD Models. CFD models have been used extensively to ana- lyze smoke transport for tenability systems in atriums. In addition to analysis of smoke transport, the FDS model incorporates features that help evaluate tenability. An especially useful feature is the abil- ity of FDS to calculate visibility at user-selected points. Large Multi-Compartmented Buildings. It is not practical to use CFD to simulate smoke transport in large buildings, but CON- TAM can handle this simulation in extremely large buildings. With CONTAM, the user inputs the temperatures, and zone fire models can be used to evaluate fire produced temperatures in building spaces. Chapter 19 of the Smoke Control Handbook discusses tena- bility analysis using CONTAM, including an example. 16. COMMISSIONING AND TESTING Commissioning refers to the process of examining, comparing, testing, and documenting the installation and performance of a smoke control system to ensure that it functions according to an approved design. It demonstrates to an owner that the smoke control system installed in a project meets the project' s design goals. Special inspections are a means that an authority having juris- diction (AHJ) uses to determine that a smoke control system meets the code requirements. The International Building Code (IBC) has requirements for a special inspection and describes the qualifica- tions required for a special inspector (ICC 2012). Commissioning Process Commissioning begins at the start of the project and continues throughout the project. ASHRAE Guideline 1.5 provides methods for verifying and documenting that the performance of smoke control systems conforms with the intent of the design. For smoke control systems, an AHJ such as a building official or fire marshal typically enforces a combination of building codes, fire codes, and local standards. The intent is to determine that the system meets the owner' s project requirements (OPR), including code requirements and inspections by the AHJ throughout the delivery of the project. Witnessing and reporting are important parts of commissioning. For successful commissioning of a system, several different people typically are involved in the process. In addition to the building owner and AHJ, the system designer, general contractor, subcon- tractors, fire protection engineering consultants, and testing and balancing technicians can be involved. At the end of testing, docu- mentation is provided that the system is working properly according to the design. Commissioning activities can occur at multiple stages during the construction process. Duct inspections, duct leakage testing, and barrier inspections are activities that typically occur early in the construction process when the ducts and barriers are readily visible. Component testing, including airflow measurement, can occur at a midpoint in construction where power is provided to individual de- vices, but central monitoring and control has not yet been provided. Sequence of operations and final performance testing typically oc- curs when construction is nearly complete, often just before the building is intended to obtain its permits and open to the public. Commissioning Testing Commonly, testing and balancing (TAB) is required before for- mal acceptance testing to achieve the expected performance of all the components. TAB refers to the process where the as-built per- formance of smoke control systems is tested in the field and com- pared to the required design conditions. Adjustments to the installed system, such as refining the supply airflow rates, are made to ensure that the smoke control system is functioning as intended in the approved design documentation. System performance testing is the phase where the code- specified performance parameters appropriate to the smoke control design are measured. For example, building codes require that a minimum pressure difference exist between a pressurized stairwell and other zones in the building, and that door-opening force must not exceed a specified amount. In this case, performance testing would focus on measuring the pressure difference across stairwell doors and door-opening forces. Some common parameters mea- sured during smoke control system performance testing are (1) exhaust/supply airflow quantities, (2) airflow velocities at atrium or other large open space perimeters, (3) door-opening forces, and (4) pressure differences between zones. Caution: Smoke Bomb Tests Not Recommended. Artificial smoke from smoke bombs (also called smoke candles) or any kind of artificial smoke generator is not recommended for any performance testing, because it lacks the buoyancy ofhot smoke from a real build- ing fire. Smoke near a flaming fire has a temperature in the range of 540 to 1100°C. Heating chemical smoke to such temperatures to emulate smoke from a real fire is not recommended unless precau- tions are taken to protect life and property. Special Inspector Some building codes require special inspections and tests of smoke control systems in addition to the ordinary inspection and test requirements for buildings, structures, and parts of buildings. These special inspections and tests should verify the proper com- missioning of the smoke control design in its final, installed condi- tion. Procedures for inspection and testing should be developed by the smoke control system 's special inspector, with approval of the authorities having jurisdiction. The special inspector must under- stand the principles of smoke control, including code requirements, and should check that the system 's components are as specified and are installed as intended, as well as whether the smoke control sys- tem performs as intended. Periodic Testing After a smoke control system has been commissioned, testing must still be performed periodically over the building's life to ensure the system is in proper operating condition in the event of a fire. Periodic testing includes manual testing involving ongoing inspection and maintenance, and automatic testing to determine that integral equipment is functional and operational. Automatic testing is often performed at a higher frequency than manual testing. Con- tinued inspection and testing identifies adjustments and repairs needed to account for unforeseen changes to the building or failure of components. Until recently, smoke control system reliability has been some- what compromised because periodic testing was limited to manual testing. Inspections performed years after commissioning showed that some smoke control systems were inoperable, turned off, or made ineffective by modifications to equipment or the building. Re- liability of smoke control systems should be significantly improved by using automatic weekly self testing of system components, avail- able from Underwriters Laboratories (UL) listed equipment with the UUKL product designation. Dampers that are part of code-mandated passive smoke barriers are not included in the automatic weekly self testing. Typically, codes require testing these dampers every four years, except in hos- pitals (every six years). 17. EXTRAORDINARY INCIDENTS Most buildings are designed and built to be protected from ordi- nary incidents, but some buildings need protection from extraordi- nary incidents. Extraordinary incidents, whether caused by war, terrorism, accident, or natural disaster, can affect immediate human Inc. ASHRAE, 2019 user. single for Licensed | {}
d69e3daf-7637-450b-844b-1205da02d108 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Fire and Smoke Control 54.25 needs such as survival and safety, and also longer-term needs such as air, water, food, and shelter. Some buildings are designed with spe- cific features intended to make them less susceptible to extraordinary incidents. It is recommended that actuation of systems for fire and smoke protection be ofhigher priority than possibly conflicting auto- matic strategies designed to respond to other extraordinary condi- tions. Some acts of terrorism use fire, and those using bombs often lead to fires. Itis well known that war, terrorist attacks, and natural disas- ters have the potential to disrupt utilities and interfere with firefight- ing, and this often allows any fires that occur to grow unchecked. For these reasons, simultaneous fire and other extraordinary inci- dents should be considered likely, and any features intended to mit- igate extraordinary conditions should be designed accordingly. For more information, see ASHRAE's (2003) report, Risk Management Guidance for Health, Safety and Environmental Security under Extraordinary Incidents, and Chapter 61 of this volume. 18. SYMBOLS A = area, m2 a = dilution rate, air changes per minute; length of inlet, m Aa = free area around elevator car, m2 ABO = flow area per stairwell between building and outdoors, m2 Ae = effective area, m2 Ai = flow area of path i, m2 Air = leakage area between building and lobby, m2 As = cross-sectional area of shaft, m2 ASB = flow area between stairwell and building, m2 Aw = area of ventilation opening, m2 b = distance from opening to balcony edge, m; width of inlet, m C = flow coefficient; concentration of contaminant at time t Cc = flow coefficient for flow around car Co = initial concentration of contaminant C = specific heat of plume gases, 1.0 kJ/(kg· K) p C W = pressure coefficient d = depth of smoke layer below lowest point of exhaust inlet, m; distance from doorknob to knob side of door, m Di = diameter of exhaust inlet, m F = total door-opening force, kg Fdc kg = door closer force, FR = flow area factor H = floor-to-ceiling height, m; height of balcony above fuel, m HJ = thickness of ceiling jet, m Hm = height limit, m Hw = height of ventilation opening, m K = fraction of convective heat release contained in smoke layer m = mass flow rate, m2/s Patm = atmospheric pressure, Pa Pw = wind pressure, Pa q = heat release rate, kW/s qc = convective heat release rate, kW/s R = gas constant, 287 J/(kg· K) Smin = minimum edge-to-edge separation between inlets, m t = time, s TB = temperature in building, °C; absolute temperature in building, K TF temperature of fire compartment, K = absolute / = growth time, s g 7 = absolute temperature of air into fire compartment, K in TJ temperature of ceiling jet, K = absolute To = temperature of outdoors, °C or K To temperature, °C or K = absolute ambient Tout = absolute temperature of smoke leaving fire compartment, K Ts = temperature of shaft or stairwell, °C or K Ts = absolute temperature of smoke, K U = elevator car velocity, m/s UH = velocity at wall height H, m/s V = volumetric flow rate, m3/s Ve = volumetric flow rate of one exhaust inlet, m3/s Vin = volumetric flow rate of air into fire compartment, m3/s Vmax = maximum volumetric flow rate without plugholing at Ts, m3/s Vout = volumetric flow rate of smoke out of fire compartment, m3/s W = door width or width of spill, m w = width of opening from area of origin, m Z = distance above neutral plane or distance above base of fire, m Zb = height of plume above balcony edge, m ZI = limiting elevation, m Greek ¦ Y = exhaust location factor ¦ ¦ --- ¦ ¦ △p = pressure difference, Pa ¦ ¦ APFS = pressure difference from fire compartment to surroundings, Pa ¦ ¦ △p max maximum design pressure difference, Pa = ¦ ¦ △Pmin = minimum design pressure difference, Pa ¦ ¦ Apso = pressure difference from shaft to outdoors, Pa ¦ ¦ △p u.si = upper limit pressure difference from shaft to building, Pa ¦ ¦ 7 = heat transfer factor ¦ ¦ P = density, kg/m3 ¦ ¦ Po = outdoor air density, kg/m3 ¦ ¦ Xc = convective fraction ¦ REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. Achakji, G.Y , and G.T. Tamura. 1988. Pressure drop characteristics of typi- cal stairshafts in high-rise buildings. ASHRAE Transactions 94(1):1223- 1237. Paper DA-88-13-2. Ahrens, M. 2017. U.S. experience with sprinklers. Report, National Fire Protec- tion Association, Quincy, MA. www.nfpa.org/-imedia/Files/News-and- Besanchile-satate-andeportsSoresindintespidaspif ASHRAE. 2003. Risk management guidance for health, safety and envi- ronmental security under extraordinary incidents. Report, Presidential Ad Hoc Committee for Building Health and Safety under Extraordinary Incidents. ASHRAE. 2012. Commissioning smoke management systems. ASHRAE Guideline 1.5-2012. ASHRAE. 2013. Laboratory methods of testing fans used to exhaust smoke in smoke management systems. ANSI/ASHRAE Standard 149-2013. ASTM. 2017. Test method for fire tests of penetration firestop systems. Standard E814-13a (2017). American Society for Testing and Materi- als, West Conshohocken, PA. Cresci, R.J. 1973. Smoke and fire control in high-rise office buildings- Part II, Analysis of stair pressurization systems. Symposium on Expe- rience and Applications on Smoke and Fire Control, ASHRAE Annual Meeting, June. CSI. 2018. MasterFormat: Master list ofnumbers and titlesfor the construc- tion industry. Construction Specifications Institute, Alexandria, VA. www.masterformat.com. Dols, W.S., and B.J. Polidoro. 2016. CONTAM user guide and program documentation version 3.2. NIST Technical Note 1887. National Insti- tute of Standards and Technology, Gaithersburg, MD. Fang, J.B. 1980. Static pressures produced by room fires. NBSIR Publica- tion 80-1984. National Bureau of Standards. Available from National Institute of Standards and Technology, Gaithersburg, MD. Felker, L.G., and T.L. Felker. 2009. Dampers and airflow control. ASHRAE. Forney, G.P. 2017. User's guide for Smokeview-A tool for visualizing fire dynamics simulation data, 6th ed. NIST Special Publication 1017-1, National Institute of Standards and Technology, Gaithersburg, MD. Hadjisophocleous, G. V., and J. Zhou. 2008. Evaluation of atrium smoke ex- haust make-up air velocity (RP-1300). ASHRAE Transactions 1 14(1):147- 153. Paper NY-08-020. ICC. 2012. International Building CodeⓇ. International Code Council, Washington, DC, Section 909. Klote, J.H. 1988. Analysis of the influence of piston effect on elevator smoke control. NBSIR Publication 88-3751, National Institute of Standards and Technology, Gaithersburg, MD. Klote, J.H. 2004. Tenability and open doors in pressurized stairwells (RP- 1203). ASHRAE Transactions 110(1). Paper AN-04-11-1. Klote, J.H. 2014. AtriumCalc: Atrium smoke control calculator-Technical information and user guide, V. 1.1. ASHRAE. Inc. ASHRAE, 2019 user. single for Licensed | {}
74f583b8-4553-4eb7-ac68-911f2962a6d0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 54.26 Klote, J.H. 2018. A new look at door-opening forces and smoke control. ASHRAE Conference Paper HO-18-C033. Klote, J.H., and X. Bodart. 1985. Validation of network models for smoke control analysis. ASHRAE Transactions 91(2B):1134-1145. Paper HI- 85-23-2. Klote, J.H., and G. Tamura. 1986. Elevator piston effect and the smoke prob- lem. Fire Safety Journal 11(2):227-233. Klote, J.H., and G. Tamura. 1987. Experiments of piston effect on elevator smoke control. ASHRAE Transactions 93(2A):2217-2228. Paper NT-87- 26-1. Klote, J. H., J.A. Milke, P.G. Turnbull, A. Kashef, and M.J. Ferreira. 2012. Handbook of smoke control engineering. ASHRAE. Klote, J.H., P.G. Turnbull, and D.H. Evans. 2017. Pressurized stairwells with open doors and the IBC. ASHRAE Conference Paper LB-17-C026. Ko, Y.J., and G.D. Lougheed. 2016. Performance of stairwell pressurization system with open doors (RP-1447). ASHRAE Transactions 122(2). Paper ST-16-003. Ko, Y., G. Hadjisophocleous, and G.D. Lougheed. 2008. CFD study of the air entrainment of balcony spill plumes at the balcony edge (RP-1247). ASHRAE Transactions 114(1). Paper NY -08-040. Law, M. 1986. A note on smoke plumes from fires in multilevel shopping malls. Fire Safety Journal 10(3). Lougheed, G.D. 1997. Expected size of shielded fires in sprinklered office buildings (RP-838). ASHRAE Transactions 103(1). Paper PH-97-02-1. Lougheed, G.D., and C. McCartney. 2008a. Balcony spill plumes: Full-scale experiments, part 1 (RP-1247). ASHRAE Transactions 114(1). Paper NY-08-039. Lougheed, G.D., and C. McCartney. 2008b. Balcony spill plumes: Full-scale experiments, part 2 (RP-1247). ASHRAE Transactions 114(1). Paper NY-08-041. Lougheed, G.D., C.J. McCartney, and E. Gibbs. 2007. Balcony spill plumes. ASHRAE Research Project RP-1247, Final Report. Madrzykowski, D., and R.L. Vettori. 1992. A sprinkler fire suppression algorithm for the GSA engineering fire assessment system. NISTIR Publication 4833, National Institute of Standards and Technology, Gaith- ersburg, MD. McCartney, C., G.D. Lougheed, and E.J. Weckman. 2008. CFD investigation of balcony spill plumes in atria. ASHRAE Transactions 114(1). McGrattan, K., R. McDermott, C. Weinschenk, K. Overholt, S. Hostikka, and J. Floyd. 2017. Fire dynamics simulator user's guide. NIST Special Pub- lication 1019. 6th Edition. National Institute of Standards and Technol- ogy, Gaithersburg, MD. Morgan, H.P., and G.O. Hansell. 1987. Atrium buildings: Calculating smoke flows in atria for smoke control design. Fire Safety Journal 12:9-12. 2019 ASHRAE Handbook-HVAC Applications (SI) Morgan, H.P., and N.R. Marshall. 1979. Smoke control measures in covered two-story shopping malls having balconies and pedestrian walkways. BRE CP Publication 11/79, Borehamwood, U.K. NFPA. 2018. Standard for smoke control systems. Standard 92. National Fire Protection Association, Quincy, MA. NFPA. 2018. Life safety code�. Standard 101. National Fire Protection Association, Quincy, MA. NFPA. 2018. Standard for smoke and heat venting. Standard 204. National Fire Protection Association, Quincy, MA. Peacock, R.D., P.A. Reneke, and G.P. Forney. 2015. CFAST- Consolidated model of fire growth and smoke transport (version 7) volume 2: User's guide. NIST Technical Note 1889v2. National Institute of Standards and Technology, Gaithersburg, MD. dx.doi.org/10.6028/NIST.TN.1889v2. Pongratz, C., J.A. Milke, and A. Trouve. 2016. A CFD study to identify methods to increase maximum velocity of makeup air for atrium smoke control (RP-1600). ASHRAE Transactions 122(2). Paper ST-16-002. SFPE. 2016. SFPE Handbook offire protection engineering, 5th ed. Society of Fire Protection Engineers, Bethesda, MD. Shaw, C. Y . J.T. Reardon, and M.S. Cheung. 1993. Changes in air leakage levels of six Canadian office buildings. ASHRAE Journal 35(2):34-36. Tamura, G.T. 1990. Fire tower tests of stair pressurization systems with over- pressure relief (RP-559). ASHRAE Transactions 96(2). Paper 3426. Tamura, G.T., and C.Y. Shaw. 1976a. Studies on exterior wall air tightness and air infiltration of tall buildings. ASHRAE Transactions 83(1):122-134. Paper DA-2388. Tamura, G.T., and C. Y. Shaw. 1976b. Air leakage data for the design of ele- vator and stair shaft pressurization systems. ASHRAE Transactions 83(2): 179-190. Paper SE-2413. Tamura, G.T., and C.Y. Shaw. 1978. Experimental studies of mechanical venting for smoke control in tall office buildings. ASHRAE Transac- tions 86(1):54-71. Paper AT-2472. Tamura, G.T., and A.G. Wilson. 1966. Pressure differences for a 9-story building as a result of chimney effect and ventilation system operation. ASHRAE Transactions 72(1):180-189. UL. 2006. Fire dampers. ANSI/UL Standard 555. Underwriters Laborato- ries, Northbrook, IL. UL. 2014. Safety for ceiling dampers. ANSI/UL Standard 555C. Underwrit- ers Laboratories, Northbrook, IL. UL. 2014. Smoke dampers. ANSI/UL Standard 555S. Underwriters Labora- tories, Northbrook, IL. UL. 2015. Fire tests of penetration firestops. ANSI/UL Standard 1479-10. Underwriters Laboratories, Northbrook, IL. Zhou, J., and G.V. Hadjisophocleous. 2008. Parameters affecting fire plumes (RP-1300). ASHRAE Transactions 114(1):140-146. Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
31027a02-5bc6-4c18-aa96-20b988cb78e4 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 55 RADIANT HEATING AND COOLING ¦ Applications 55.1 ¦ Condensation Control ¦ 55.6 ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ Architecture of Radiant Ceilings 55.1 ¦ ¦ Embedded Systems 55.9 ¦ ¦ Design and Dimensioning 55.2 ¦ Fundamentals ¦ 55.11 ¦ ¦ Design Aspects of Radiant Ceiling Systems 55.2 ¦ ¦ Method to Determine Heating and Cooling Capacity 55.11 ¦ ¦ Acoustic Feature of Radiant Ceiling Panels 55.2 ¦ ¦ Thermoactive Building Systems (TABS) 55.12 ¦ ¦ Controls 55.3 ¦ ¦ Embedded Systems Controls 55.13 ¦ ¦ Design Examples 55.4 ¦ ¦ Radiant Cooling System Control 55.15 ¦ 1. APPLICATIONS B ASED on the global push towards high performance buildings, current application knowledge and readily available equip- ment, there are now few limitations for radiant heating and cooling systems. The past concern over condensation has now been success- fully addressed, with tighter enclosures to mitigate moisture infiltra- tion, dedicated outdoor air systems for dehumidification of incoming ventilation air, and current technologies capable of inte- grating and regulating all control points within radiant based HVAC systems. Additionally, radiant systems technically offer the best cou- pling with solar and geothermal energy systems, heat actuated cool- ing systems and heat pumps by enabling such systems to operate at higher efficiencies and coefficients ofperformance. They can also be applied using district energy and CHP principles to stand alone multi-story buildings. Furthermore, high performing buildings par- ticularly those with above normal sensible loads due in part to the use of electronic equipment are much better served with radiant absorption of long wave energy rather than increase recirculation of chilled air which in comparison, is neither comfortable nor efficient. 2. ARCHITECTURE OF RADIANT CEILINGS Ceiling radiant cooling panels (CRCP) and heating panels are generally built as an architectural finish product (with necessary acoustical qualities, color, and pattern), compatible with the tradi- tional drop ceiling "tee grid" system or as a free hanging element. Typically, a copper tube is embedded into an extruded aluminum saddle which is permanently affixed to the back of an architectural metal ceiling panel or is part of a built-up panel made from linear extrusions with integral tube saddles fastened together to make dif- ferent width panels. The process of how the copper coil is thermally bonded with the radiant ceiling panel is crucial especially in cooling application. Panel piping arrangements are generally in a serpentine pattern; however, parallel header arrangements are also available. Typical panel construction is illustrated in Figure 1. As installed, the "drop in" radiant panels have a mass of 7.8 to 9.7 kg/m2. A radiant ceiling panel also has an acoustic value. The acoustic signature can be achieved with a variety of perforations. In addition, a glass fiber blanket or non-woven sound-attenuating sheet is placed on the pack of the panel. The lightweight construction results in a transient response "time constant" of only about 3 to 5 minutes from ambient room tempera- ture to operating temperature once the cooling/heating fluid is applied. That means they respond rapidly to changing space sensible load conditions. Hydraulically, the ceiling panels are most fre- quently connected with flexible-push on coupling hoses for fast and safe installations, as illustrated in Figures 2 and 3. Panels can be moved aside without disconnecting the hoses, for easy access above. They can also be easily removed and reconnected ![image](/image/placeholder) Fig. 1 Typical Composition of Radiant Modular or Pan-Type Ceiling Panel ![image](/image/placeholder) G ··· Fig. 2 Cutaway View of Typical Modular Radiant Ceiling Panel for either extensive maintenance or evolving space use requirements without breaking normal threaded or sweat solder plumbing connec- tions. Radiant ceiling panels promote architectural freedom in several ways. First, radiant cooling ceilings can be designed to be visually indistinguishable from regular ceilings to maintain aesthetic appeal. Secondly, the hardware in a radiant cooling system is smaller and more flexible. The size of the ceiling panels, the arrangement of the appliances within the ceiling, and the partitioning of the room all are 55.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
bc012159-1109-4355-9e07-8207db2f738d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 55.2 2019 ASHRAE Handbook- - HVAC Applications (SI) ![image](/image/placeholder) Fig. 3 Back View of Drop Ceiling: Piping Configuration with Flexible Hose and Quick-Connect Fittings flexible. Units may also be quite large assembled from linear extru- sions which maybe be as long as 4.8 m and widths (built of several extrusions side by side) to 609 mm or even to 1219 mm wide. These are also the typical style of panels used along building perimeters for heating applications. In perimeter heating, panels are typically 152 to 609 mm wide depending on the perimeter heat loss. Due to the reduction in sensible heating and cooling loads that must be car- ried in the air, the new minimal airflow requirements often permit designs where common mechanical air distribution devices such as diffusers and ductwork are made much smaller or are eliminated altogether. 3. DESIGN AND DIMENSIONING Panels are dimensioned based on building/room loads for heat- ing or cooling and sometimes both. For heating or cooling the room design temperature and supply water temperature and flow rates determine the capacity of the panels in watts per square metre. Once this capacity is determined it is divided into the load to determine the square feet of active panels required. The design then uses this information to layout the panels in the space. Heating panels should be placed within 1 m of the exterior walls. Cooling panels should be more evenly distributed throughout the space with some heavier weighting to the highest area of heat gains (i.e., windows.) Cooling In practice, the design cooling capacity per unit panel area (W/ m2) is determined from the panel manufacturer's catalog data. The unit panel cooling capacity can be selected from the design capacity tables provided by the panel manufacturer based on the difference between the room temperature and the mean panel surface tempera- ture (or mean water temperature [MWT]). Heating In many climates, radiant cooling ceilings can also provide heat- ing. For best applications, the structure should be well insulated, and outside temperatures should not be extremely low. In these cases, radiators are not needed, saving costs and making more floor space available. Because humans sense heat from a hot ceiling more quickly than from hot air blown in from ducts, surface temperatures should not exceed 35°C. The reason the surface should not exceed 35°C is to permit humans to radiate a small amount of heat from their heads that are normally at 37°C to a slightly cooler surface. If the surface temperature exceeds 35°C, humans in the space will experience dis- comfort and may even experience headaches. This is only if the panel is right above the head sufficient separation should allow higher temperatures of 43.4 to 48.9°C max for normal ceiling heights of 2.7 to 3.3 m or even higher temperatures if placed at the perimeter walls where panels are not directly over the heads of occupants. Radiant panels radiate heat to the surrounding surfaces including people, furnishings, and the cold interior surface ofthe window. The cold window surface, loses heat via transmission to the cold outside. Without radiant heating, the cold window surface cools the air pass- ing over it, creating a significant convection down draft. Normally the baseboard radiators balance this action. With radiant heating, the interior surface of the glass is warmed through direct radiation, sig- nificantly reducing the convection down draft produced. The small down draft current produced, typically less than 0.1 to 0.15 m/s, cre- ates a vacuum effect under the radiant heat panels. The low-pressure area formed draws the warm room air at the ceiling towards this area where it is further warmed by the radiant heat panels. Thus, the air becomes even more buoyant, and it has a tendency not to convect down the outer wall. The net effect is a surface boundary layer of "dead air" created very near the window. The down draft is below the minimum threshold felt by humans. Therefore, in some cases the baseboard radiators can often be eliminated, reducing capital costs and increasing usable floor area. Another consideration in the heating mode, the convection is lower, and the ceiling's capacity is proportionally reduced. In most cases, the internal heat loads can provide sufficient heat. To prevent cold airdrop from the windows, the radiant heating portion of the ceiling needs to be installed along the perimeter of the room (typi- cally within 1 m of the exterior wall). 4. DESIGN ASPECTS OF RADIANT CEILING SYSTEMS Technically speaking, a radiant cooling ceiling is simply a large heat exchanger suspended from a room 's ceiling. It exchanges energy with the room via radiation and convection. Accordingly, cooling ceilings can be rated based on the temperature difference between the panel's MWT and the room design temperature. Heat transfer from the room to the ceiling surface (or the other way around in the case of heating) is a function of the average ceiling surface temperature and the room temperature. The objective of every radiant cooling ceiling developer is to get the ceiling surface temperature as close as possible to the water temperature. The smaller the temperature difference between chilled water and ceil- ing surface, the more efficient the system. The overall heat exchange between ceiling panels and the flow in the water piping obeys the following equation: Q = kA T (1) where T is the smallest possible temperature difference between the contact point ofthe ceiling panel and the fluid flowing in the pip- ing. This path includes the conductance between the panel and the pipe, conductance through the pipe, and the convection from the inner pipe surface to the fluid. Thus, k is the equivalent thermal con- ductivity. The removed heat by the fluid flow in the piping 0 should be as large as possible. Therefore, the overall k-value and the heat conducting areas A must be made as large as possible. Panel dimensions can be chosen freely within manufacturing and building installation constraints. The only definitive design con- straint to the architect is that active tubing attachment side must be flat. Inc. ASHRAE, 2019 user. single for Licensed | {}
e5944475-2403-4555-be80-0bfa2fff98c6 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Radiant Heating and Cooling 55.3 ![image](/image/placeholder) Dedicated outdoor air unit Dedicated outdoor air unit out t, BMS + + oWb + + t, t S 0 0 tdp 0 O ○ Heating Radiant panel Cooling Heating Radiant panel Cooling Fig. 4 Typical Control Schematic for Radiant System with Injection Control Valves in Four-Pipe/Two-Pipe System 5. ACOUSTIC FEATURE OF RADIANT CEILING PANELS Room acoustics also are handled conventionally. The following addresses commonly applied strategies for improving acoustics in rooms with cooling ceilings. Acoustic Inlay Mats Mineral fiber mats 30 mm thick and 40 kg/m3 are applied on the back of a perforated radiant ceiling tile to meet required acoustic values. Acoustic Fleece In environments such as clean rooms and hospitals where fiber rub-off is not expected under any circumstances, acoustic fleece may be used. The black fleece is bonded to the rear of the perforated ceiling panel. To prevent a decrease in the heat exchange between the heat conducting rails and the ceiling panel, the fleece is bonded between the heat-conducting rails. Acoustic fleece must have a min- imum plenum height of 300 mm to be effective. Panel Perforation The ceiling panels might feature certain perforation pattern to enhance acoustic performance or personalize the visual aspect of the ceiling. The perforation pattern is often specified with hole diameter and free area (open cross sections etc.). 6. CONTROLS The design of control system should take into account the build- ing, its intended use and the effective functioning of the heating/ cooling system, efficient use of energy and avoiding heating/cool- ing the building to full design conditions when not required. This should include keeping distribution heat losses as low as possible, e.g. reducing flow temperature when normal comfort temperature level is not required. Control and operation of the system help to handle the conditioning systems with savings of operational costs and enable the maintenance of required indoor environmental con- ditions. Hydronic radiant controls systems have two primary functions: controlling room temperature and preventing condensation on the ceiling surface. For proper operation and maximum energy savings, radiant ceiling systems require the use of precision electronic or direct digital controls. Two-Port Control Valves The two-port valve controls the heat loads by permitting more or less chilled water to flow through the valve and through the cooling ceiling (Figures 4 and 5). The supply water temperature stays con- stant. A humidity sensor closes the valve as soon as the chilled water supply temperature reaches dew point. This type of control is very affordable and simple. The only dis- advantage is dew point control. The cooling ceiling must be turned off as soon as a risk of condensation occurs. Controls are generally applied to influence both pressure (flow) and temperature. Accordingly, there are two control strategies: using (1) a two- way control valve to control water flow or (2) an injection circuit to control water temperature. Controlling Water Temperature/Injection Circuit Using an injection circuit requires a circulating pump to provide a constant flow of water through the ceiling (Figures 6, 7, and 8). Depending on the heat loads, a two- or three-way valve injects more or less chilled water to the ceiling supply. The same water quantity is sent to the system return. The supply water temperature for the ceiling is controlled by the quantity of the water injected. If risk of condensation occurs, the temperature of the supply water can be raised. The ceiling loses some of its capacity but can be kept in operation. The injection circuit ensures both effective operation and the maximum possible mean temperature difference for cooling ceil- ings. As each control zone needs a pump, a humidity sensor, and a controller (which constantly calculates dew point and compares it Inc. ASHRAE, 2019 user. single for Licensed | {}
5da77c4f-189a-43fe-92ee-8f3447824821 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 55.4 2019 ASHRAE Handbook-HVAC Applications (SI) ![image](/image/placeholder) Dedicated outdoor air unit Dedicated outdoor air unit Lout t, t2 BMS + + oWb + + vfd vfd vfd ◁ t, . ots 文古 Ma · 0 [ dp 수 HO 。 Heating Radiant panel Cooling Heating Radiant panel Cooling Fig. 5 Advanced Control System for Radiant System with Heat Exchangers in Four-Pipe/Two-Pipe System (Some Items Removed for Clarity) with the supply water temperature), this type of control is more expensive than the two-way control scheme. Energy Savings with Radiant Cooling Ceiling Systems Buildings with radiant ceiling cooling systems, Current systems almost always require 100% outdoor air systems and tight building envelopes to manage humidity. Energy saving are realized by significant reductions in air moving power (only the outdoor make- up air is distributed to the building) and the higher evaporator tem- perature of the chiller supplying cool water to the chilled ceiling panels. 7. DESIGN EXAMPLES Classroom Load calculations require that the space sensible load be 8.377 kW. The space has 30 occupants. A 9 by 9 by 3 m classroom and a maximum occupancy of30 peo- ple, is to be maintained at 23.3°C and 50% rh. From the psychomet- ric chart, this gives a dew point temperature of 12.78°C and a moisture content of 0.0081 kg/kg. Step 1. Determine the sensible and latent hourly heat gain for the room. The sensible and latent hourly heat gains are found using accepted procedures found in the ASHRAE handbooks. For this example, assume sensible hourly heat gain = 8.377 kW. Step 2. Determine the mean water temperature required for cooling. Supply water temperature = 12.78°C Assuming a temperature rise of 4 K, add half of this temperature rise to the inlet water temperature, giving 15°C. Step 3. Determine the minimum air supply required for the room. According to ASHRAE tabulated data, the recommended air supply per person is 34 m3/h per person x 30 persons = 1019 m3/h Step 4. Determine the latent load capacity of the air: NP * OCPL X 1.2 X 2500 X (HRODA2 - HRIDA) =1650 W Step Determine the sensible cooling capacity of the primary air: V x 1.2(DBIDA -DBSUP)= 4070 W where ¦ NP ¦ number of occupants in the space ¦ ¦ --- ¦ --- ¦ ¦ OCPL = ¦ latent heat produced by the occupants ¦ ¦ HRODA2 = ¦ humidity ratio of space air ¦ ¦ HRIDA = ¦ humidity ratio of space operating design condition ¦ ¦ V = ¦ volumetric flow rate of the supply air ¦ ¦ DBIDA = ¦ dry bulb temperature of space operating design condition ¦ ¦ DBSUP = ¦ dry bulb temperature of supply air ¦ 30 occupants at 65 W/pp = 1950 W/pp and the moisture gain results in = qL/(60 x hfg x Airflow) = 0.0022 kg/kg The moisture content of the space operating condition is 0.0103 kg/kg. From the psychometric chart, the dew point of the space operating tem- perature is 14°C. Inc. ASHRAE, 2019 user. single for Licensed | {}
3d27d188-665e-489c-afe6-501b1088de4c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Radiant Heating and Cooling 55.5 DOAS - Latent Loads ![image](/image/placeholder) + 12 담 Heating Radiant panel Cooling Sensible loads Fig. 6 Secondary Pumps with Mixing/Injection Control Valves on Four-Pipe/T wo-Pipe System DOAS - Latent Loads ![image](/image/placeholder) + X � �� Heating Cooling Fig. 7 Secondary Pumps with Mixing/Injection Control Valves on Four-Pipe System Dedicated outdoor air unit ![image](/image/placeholder) + N N 수 Heating Radiant panel Cooling Sensible loads Fig. 8 Two-Pipe Cooling-Only System with Heat Exchanger The space condition is calculated by including the sensible and latent loads to the space. From this condition the dew-point temperature is shown on the psychometric chart. The panel surface operating tempera- ture is selected about 2 K higher than this temperature. Step 5. Determine the sensible load capacity of the air with the fol- lowing equation: Qs = QPCp(troom tsupply)60 Qs = (1019 m3/h)(1.2 kg/m3)[1 kJ/(kg·K)](23 - 13) = 12,900 kJ/h = 3.6 kW The sensible cooling required from the panels is 4.8 kW. Step 6. Select a panel surface temperature at least 2 K higher than the space operating dew-point temperature (16.1°C) Thus, the required temperature is higher than the MWT calculated in step 2. Step 7. From the 16.1°C panel operating temperature or panel mean water temperature, derive the supply water temperature and water tem- peratures to and from the panels. Typically, the difference supply and return water temperature is 4 K, so the panel water supply temperature in this case is 13.88°C and the panel return water temperature is 18.33°C. Step 8. Figure 9 shows the panel output. Step 9. The required sensible cooling output from the panel is 4768 kW at 16.1°C MWT and therefore the required panel area is 4768 W/ 147 = 32.4 m2. The classroom has a ceiling area of 83.61 m2. The ratio of ceiling panel to ceiling is 69%. Office The office has a sensible cooling load of 2 kW, which is obtained from the load calculations. There will be two occupants in the office. A4 x 5 x 2.4 m interior office with a 0.6 X 1.2 m T-bar ceiling and a maximum occupancy of two people is to be maintained at 24°C Inc. ASHRAE, 2019 user. single for Licensed | {}
4f001024-2e21-43a0-9c5f-3dca55150dc1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 55.6 2019 ASHRAE Handbook- - HVAC Applications (SI) Chart Type: line 15 15.5 16 16.5 17 17.5 18 18.5 19 19.5 item_01 130W/m2 120W/m2 110W/m2 90W/m2 80W/m2 70W/m2 50W/m2 40W/m2 30W/m2 20W/m2 Fig. 9 Panel Output for Classroom Example: 98 W/m2 at Room Temperature of 24°C and MWT of 15°C, and 75 W/m2 at Update MWT of 16.5°C and 45% rh. From the psychometric chart, the dew-point tempera- ture is 12.7°C and moisture content is 0.009 kg/kg. Step 1. Determine the portion of the load to be provided by the radi- ant ceiling and the portion of the load to be provided by the ventilation system. As a rule of thumb, the area of radiant panels is 70% of the ceiling area of the space. For this application, the preliminary output from the radiant ceiling is 1319 W. Subtract the output of the radiant ceiling from the required sensible cooling load: 2000 - 1319 = 679 W. The required volume of supply air to meet the rest of the load can be calculated as Inc. ASHRAE, 2019 user. single for Licensed Qs = Airflow X 1.085 T Qs = 0.05 m3/s = 180 m3/h Determine the sensible load capacity of the air: Qs = QpCp(troom tsupply)60 Qs = 715 W The sensible cooling required from the panels is 2000 - 715 = 1284 W. Step 2. Determine the latent load capacity of the air: 9L = Qphfg( room supply) X 60 Two occupants = 146 W Moisture gain = 0.00091 kg/kg The moisture content of the space operating condition is 0.00991 kg/kg. The dew point of the space operating temperature from the psychometric chart is 13.8°C. Step 3. Determine the MWT required for cooling. Supply water tem- perature = 12.7°C. Assuming a temperature rise of 4 K, add half of this temperature rise to the inlet water temperature: ture of the ceiling panels is kept about 2 K higher than the space dew- point temperature. Step 4. Select a panel surface temperature at least 1.5 K higher than the operating dew temperature, which is 13.8°C +1.5 K = 15.3°C. Step 5. From the 15°C panel operating temperature or panel MWT, derive the supply water temperature and water temperatures to and from the panels. Typically, the difference between supply and return water temperature is 4 K, so the panel water supply temperature in this case is 15°C - 2 = 13°C and the panel return water temperature is 15°C + 2 = 17°C. Step 6. Figure 11 shows the panel output, the flow rate, and the cool- ing output in comparison with the air temperature MWT. Step 7. The required sensible cooling output from the panel is 1284 W; therefore, the required panel area is 13.6 m2. The office has a ceiling area of 20 m2. The ratio of ceiling panel to ceiling is 68%. 8. CONDENSATION CONTROL When the dew-point temperature of the space air has been deter- mined, the surface temperature of the radiant ceiling can be con- trolled to be above the dew point and therefore avoiding the risk of condensation. Monitoring the space air temperature and the space humidity levels will provide the space moisture content. In simple terms the supply water temperature to the panels must be controlled to avoid the possibility of condensation. The only possibility of condensation occurring is when radiant cooled ceilings are used in a space with operable windows. From practice it is known that operable windows can induce up to 6 ACH through a space. From the previous example the dew point temperature of the room condition is 13.8°C, so if this condition were to come into con- tact with a radiant panel with a surface temperature of 13.3°C and condensation would occur. The dew-point temperature of the space operating condition is shown on the psychometric chart in Figure 10. The operating surface tempera- MWT = 12.7°C + 4/2 = 14.7°C A very simple control methodology to avoid condensation is to elevate the panel surface temperature to roughly 1 to 1.5 K above the space air dew point temperature of 13.8°C, which would give a panel surface temperature of 15.5°C. | {}
d447fdc6-35ef-44b6-abc7-0e229cffe068 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Radiant Heating and Cooling 55.7 ![image](/image/placeholder) ASHRAE PSYCHROMETRIC CHART NO.1 + 、 NORMAL TEMPERATURE 55 60 BAROMETRIC PRESSURE: 29.921 INCHES OF MERCURY Copyright 1992 AMERICAN SOCIETY OF HEA TING, REFRIGERA TING AND AIR-CONDITIONING ENGINEERS, INC. SEA LEVEL 66 1.0 1.0 85 0.6 026 0000 2.0 -2000 000 6.6 SENSIBLE HEAT 이미 -1000 = 45 TOTAL HEAT t 牛奶 024 급 56 022 2 · た た e 社会 40 is 020 ENTHALPY din 二 HUMIDITY RATIO SW 35 50 016 EMP 014 45 BTU PER POUND OF DRY AIR URA 65 ENTHALPY g A 없 ) � 스 1012 UND panel surface temp panel surface temp HE 010 D dew point space condition W 化 목 supply air temperature is O 008 P� 인 15 005 40 ◀ 35 TEMPERA 월 004 a7na 002 10%,RE ATIVE HUMIDIT DR 30 2 요 활 COL 元 TO 15 <O <5 ENTHALPY - BTU PER POUND OF DRY AIR Fig. 10 Dew Point of Space Based on Operating Temperatures Primary Air Conditioning Control ofthe building humidity level is paramount when panels systems are used. Space ventilation and humidity control are solely provided by the supply air delivered from the air handling unit. The minimum supply airflow rate should be sufficient to provide both functions. The indoor dew point is determined by the latent load to the space and the condition of the supply air. To avoid the risk of condensate formation on the panels, the AHU must condition the primary air to be sufficiently dry so as to absorb the moisture gen- erated in or infiltrating into the building. Commissioning of the AHU control system must ensure that the supply air conditions are achieved without significant oscillations. A range of air conditioning technologies may be applied provided that the supply dry bulb and dew point temperature are both pre- cisely controlled. Condensation Prevention The implementation of an adequate chilled-water temperature control system, together with the supply of an adequate amount of correctly conditioned primary air, is sufficient to avoid the occur- rence of condensation on the panels. Water supply to panels should not be activated when space dew point temperatures are above the zone chilled-water supply tem- perature. It must be ensured that the panels system chilled-water supply is shut off any time the air handler is not in operation and only restored when the space dew-point temperature is safe for non- condensing panels operation. In the transition from spring to sum- mer, or from summer to winter, the outdoor air condition may result in a higher dew point and therefore the system can remain in oper- ation. In practice, a moisture sensor on the supply pipe work, or a dew point calculation warns of the possibility of condensation. The for- mation, and subsequent falling, of water droplets on the panel sur- face lags the onset of conditions that could cause condensation. Itis common for panels to operate with chilled-water temperatures below the zone dew point without significant moisture collection on the panels surface with condensation forming first on the uninsu- lated surface of the chilled-water pipework feeding the panel. Condensation prevention can be implemented with either reac- tive or proactive strategies, or a combination of both. In a proactive strategy, the control system acts to avoid or prevent the formation of condensate. In a reactive strategy, the control system acts in response to condensate that has formed. Proactive Strategies In a proactive strategy, the dew point can be monitored via con- tact humidistats by attaching the sensor to an uninsulated portion of Inc. ASHRAE, 2019 user. single for Licensed | {}
0b52f1cf-f95b-4e0b-a965-3ef4b879b59e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 55.8 2019 ASHRAE Handbook- - HVAC Applications (SI) Chart Type: line 15 15.5 16 16.5 17 17.5 18 18.5 19 19.5 item_01 120W/m2 110W/m2 90W/m2 70W/m2 50W/m2 40W/m2 30W/m2 20W/m2 10W/m2 0W/m2 Fig. 11 Panel Output for Office Example: 98 W/m2 at Room Temperature of 24°C and MWT of 15°C, and 75 W/m2 at Updated MWT of 16.5°C ![image](/image/placeholder) CONDENSATION MONITOR 4 mi XCE Fig. 12 Surface Condensation Sensor the piping, immediately prior to the supply connection to the panels' panel (Figure 12). The dew point temperature of the space airis determined by con- tinuous sensing of the space air temperature, and relative humidity. The calculated dew point must then be compared to the supply water temperature. In response to the sensor feedback, chilled water supply tempera- ture set point can be reset above the room dew point, or the supply water to the zone can be halted. Figure 13 presents a control strategy where the chilled-water supply temperature is varied in accordance with the space dew-point temperature. In this case the panel' s chilled-water temperature con- trol system maintains a minimum differential between the space dew-point temperature and its chilled-water supply. To maintain this differential, the dew-point temperature must be monitored or calcu- lated. This can be done by monitoring the humidity either in the return air duct or directly in the zone. This strategy allows the panel within the panels to continue to contribute to the space sensible cooling even during periods of elevated space moisture levels. Figure 14 shows a strategy whereby the panel's chilled-water flow is interrupted when the measured space dew-point temperature rises above the panel's chilled-water supply temperature. Reactive Strategies Condensation sensors such as those shown in Figure 12 used to detect moisture on the chilled-water supply pipe. When an indica- tion of moisture is received from the sensor, the water supply is stopped, or its supply temperature is increased. This is a reactive method that can stand alone or form part of a total strategy. Modern condensate sensors are very sensitive to the smallest amount of moisture forming. Condensation detected on the supply pipe work does not mean that the chilled panels will start to conden- sate and then drip; in fact, condensation can exist on the supply pipe for a very long period and still none present on the chilled panels. The protection provided by these devices must be weighed against the probability that more thermal complaint calls may arise when and ifthe chilled-water supply is discontinued during periods where an inconsequential amount of moisture is detected by the contact switch. Figure 15 shows a reactive control strategy that relies on surface moisture sensors affixed to the chilled-water supply pipe. In the event condensation formation has been detected, the sensors over- ride the space temperature sensor and close the chilled-water supply valve until the moisture has evaporated. Ifthe flow of water is halted in response to a moisture sensor, then a control scheme will need to be developed to address when to turn the water system back on since the stoppage of water flow would typically halt the formation of moisture on the chilled-water supply pipe, even if the differential between the zone humidity level and the chilled-water supply tem- perature has not been restored. Spaces with Operable Windows or Doors For applications in spaces with operable windows or doors, occu- pants and staff should be educated on the effect opening them can have on their thermal environment. When windows or doors are opened, the supply of chilled water should be halted to avoid risk of condensation and/or prevent loss of cooling energy. Inc. ASHRAE, 2019 user. single for Licensed | {}
b5eeada4-af98-4e4c-9c68-781193fac7dd | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Radiant Heating and Cooling 55.9 ![image](/image/placeholder) Dew Point Controller Space Humidity Sensor CHW Supply Temperature CWS 天 Mixing Valve Control Control Valve Valve temperature Chilled water supply Space dew point T T temperature temperature Zone Zone Load Load point Dew Time CWR Fig. 13 Condensation Prevention Strategy Involving Reset of Panel's Chilled- Water Supply Temperature ![image](/image/placeholder) CWS Space dew point Chilled water supply CHS Supply temperature temperature Control Temperature Valve temperature Dew Point Ⓣ Controller point Zone Zone Humidity Load Dew Sensor Water flow Water flow Waterflow on stopped resumed CWR Time Fig. 14 Condensation Prevention Strategy Where Water Flow Is Discontinued When Chilled- w ater Temperature Is Below Space Dew-Point Temperature due to Rise in Humidity in Zone or Temperature Drop Detection ofa window being opened can be accomplished by the employment of window contact switches. Alternatively, moisture sensors such as that shown in Figure 12 may be used to discontinue the chilled-water flow during periods of condensation risk. When these are applied, one sensor should be installed on the chilled water supply pipe in each room (with operable windows or doors) the sys- tem serves. It must be remembered that the chilled water flow will not be restored until the sensor determines that all moisture has been evaporated from the surface of the pipe. Figure 16 illustrates a proactive sequence where a sensor detects the opening ofa window and interrupts the chilled-water flow to the space. A surface moisture sensor is also used to ensure that the space dew-point temperature is acceptable for restoring the chilled-water flow once the window is closed. Now the control system could boost the airflow to the space to reduce the time to restoring the chilled water. 9. EMBEDDED SYSTEMS An embedded system is a surface cooling and heating system where water tubes as well as electric cables are integrated within the floor, wall, or ceiling. Radiant systems have been successfully used worldwide for heating and cooling of buildings. A radiant system provides a very good method of discharging high specific heating and cooling loads while maintaining thermal comfort at relatively low operation costs. The most popular use of radiant systems is radi- ant floor heating (Figure 17); however, ceiling as well as wall heat- ing are also used (Figure 18). Radiant systems are dimensioned in accordance to the ensuing radiant heat exchange in the space. Radiant systems usually designed as a hydronic system therefore the amount of space neces- sary for the installation is considerably smaller than a conventional air conditioning system. Because of the low plenum height neces- sary to accommodate the installations, more architectural freedom is provided. The radiant system can be installed so that both indi- vidual and zone control can be achieved. Many hospitals have radiant systems, and commercial buildings are starting to use the potential of radiant floors and ceilings. In Europe, several buildings such as the PGEM in Arnhem and the Groninger Museum have successfully used radiant systems to con- trol the indoor environment. There has also been advancement in simulation programs that allow more detailed analysis of the indoor environment. With these advanced simulation tools and the individ- ual elements necessary for the creation of a comfortable indoor cli- mate using the predicted mean vote (Fanger 1972), radiant heat exchange can be studied. Because each individual surface tempera- ture and its relationship (i.e., position to the other surfaces) can be Inc. ASHRAE, 2019 user. single for Licensed | {}
4f2be39c-a3ab-4dee-af15-db2a2d87ab59 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 55.10 2019 ASHRAE Handbook-HVAC Applications (SI) determined a solution to the comfort balance equation can easily be found. When incorporating a radiant system and a constant-volume ven- tilating system, the ventilation system may only be dimensioned to supply outdoor air for each person and to remove the latent as well as the material load if the radiant system is selected to remove the remaining cooling loads. Simmonds (1994) reported on some of these designs and how effective they are in providing an effective means of comfort climate. Because cooling surfaces make no contribution to air renewal, they may always be operated in conjunction with a ventilating or air- conditioning plant, which also ensures the probably necessary dehu- midification. However, also a combination with a natural ventilation system as well as operable windows may also be possible. Radiant cooled floors have been successfully used on many proj- ects over the past ten years and many ASHRAE and other peer- ![image](/image/placeholder) Zone Control Valve CHWS Moisture sensor switch (NC) Zoneload CHWR Yes Disable Valve Condensation Detected? No Enable Valve Fig. 15 Control Strategy Where Chilled- Water Supply Halts When Moisture Is Detected on CHWS Pipe reviewed publications have been written on these projects. How- ever, many questions still arise regarding the performance of radiant cooled floors when subjected to solar radiation. The convective cooling performance of a cooled floor has been reported by Olesen, Simmonds; Borressen (1994) reported on the solar absorption of a radiant cooled floor, this was further reported by Simmonds et al. (1996). Even with this research, many questions are still being raised regarding the performance of a radiant cooled floor when absorbing solar radiation. This section explains the performance of the floor, including some limitations of the presented calculation method, but also includes information on the controllability. This section outlines the performance of a radiant cooled floor subjected to different solar radiation intensities and will look further into the controllability of the radiant cooled floor to maintain certain conditions such as space temperatures and floor surface tempera- tures. The influence of floor coverings on radiant cooled floors will also be discussed. Previous papers by Simmonds (1994) have shown that radiant cooled floors are capable of removing 35 to 40 W/m2 from spaces. Borressen (1994) and Simmonds et al. (1996) have shown that radi- ant cooled floors are capable of removing up to 85 W/m2 of energy from a space 35 W/m2 by convection and 50 W/m2 by solar absorp- tion. This section uses a simple steady-state equation to explain the performance of a radiant cooled floor when performing at its max- imum capacity of both reducing the space air temperature and absorbing solar radiation that is reaching the floor. There are several dynamic simulation programs that accomplish the dynamic perfor- mance of a radiant floor. Many papers have been written on the per- formance of radiant floor for heating. MacCluer, Athienitis, and Simmonds. Olesen and Meirhans have reported on the performance of active concrete systems. There has been advancement in simulation programs that have permitted a more detailed analysis of the indoor environment. With these advanced simulation tools, the individual elements necessary for the creation of a comfortable indoor climate using the predicted mean vote (PMV as determined by Fanger 1972), which has been adopted in ASHRAE Standard 55-2017 and radiant heat exchange can be studied. Because each individual surface temperature and its relationship (i.e., position to the other surfaces) can be determined a solution to the comfort equation can be found. The PMV/PPD comfort equation, derived by Fanger and shown in ASHRAE Stan- dard 55-2017, can be influenced by the control or balance of the radiant heat exchange in a space. When operating a radiant heated or cooled floor correctly, the surface temperature of the floor can be regulated. Absorbing a major portion of the solar radiation entering ![image](/image/placeholder) Control Valve CWS Moisture Window Window Window Sensor closed open closed Switch (NC) uado Window Switch (NC) contact T Chilled water Chilled water Chilled water Condensation Zone flow off flow off flow off Load CWR Time Fig. 16 Condensation Prevention Strategy Involving Interruption of Water Flow After Window Opening Inc. ASHRAE, 2019 user. single for Licensed | {}
d82ecaf3-494c-49a0-8c76-999b7c20635f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Radiant Heating and Cooling 55.11 ![image](/image/placeholder) Ventilation Radiant floor panel - embedded pipes Fig. 17 Radiant Floor Heating Ventilation Radiant wall panel - embedded pipes Fig. 18 Radiant Wall Heating the space also prevents the floor from emitting thermal energy, in the form of long-wave radiation, back into the space and onto other surfaces. Because cooling surfaces make no contribution to air renewal the surfaces usually operated in conjunction with a ventilating or airconditioning plant, which also ensures the necessary dehumidifi- cation is provided. The combination of a radiant cooled system with a natural ventilation system and operable windows may also be pos- sible in certain climate conditions. 10. FUNDAMENTALS A radiant floor system exchanges thermal energy with the space by means of convection, short-wave radiation, and long-wave radi- ation. Because the understanding of the three different kinds ofheat transfer is very important to calculate and optimize a radiant floor system, this section contains a detailed narrative and mathematical description. Figure 19 shows a radiant floor with edge and back insulation. The three different types of heat transfer of the radiant floor are: · Convection: heat transfer between the floor surface and the con- duction air of the space. · Long-wave radiation: heat flux between the floor surface and the room surfaces; its quantity and wavelength are temperature dependent · Short-wave radiation: sources include high-temperature sur- faces such as the sun and electric lights. The transfer of short- wave radiation within a room does not depend on the temperature ![image](/image/placeholder) Fig. 19 Typical Radiant Floor with Edge and Back Insulation of surfaces. Short-wave radiation on the floor will be either absorbed or reflected, but the radiant floor itselfis not a source of short-wave radiation. The main source of short- radiation in a space is from the direct sunlight entering the space and from elec- trical lighting. 11. METHOD TO DETERMINE HEATING AND COOLING CAPACITY A given type of surface (floor, wall, and ceiling) delivers, at a given average surface temperature and indoor temperature (opera- tive temperature i), the same heat flow intensity (specific thermal output) in any space independent of the type of embedded system. It is therefore possible to establish a basic formula or characteristic curve for cooling and a basic formula or characteristic curve for heating, for each of the type of surfaces (floor, wall, and ceiling), independent of the type of embedded system, which is applicable to all heating and cooling surfaces. Based on the calculated average surface temperature at given combinations of medium (water) temperature and space tempera- ture, it is possible to determine the steady state heating and cooling capacity. Heat Exchange Coefficient Between Surface and Space The relationship between heat flow density and mean differential surface temperature (see Figure 20 and Equations [1] to [4]) depends on the type of surface (floor, wall, ceiling) and whether the temperature of the surface is lower (cooling) or higher (heating) than the space temperature. For floor heating and ceiling cooling in Figure 20, the heat flow density q is given by q = 8.92( S,m - )1.1 (1) For other types of surface heating and cooling systems, the heat flow intensity q is given by where is the average surface temperature and ⌀is the nominal S.m indoor operative temperature. Wall heating and wall cooling: q = 8( S,m - i D (2) Ceiling heating: q = 6( S.m D - (3) Floor cooling: 9 = 7( S.m - i D 12. THERMOACTIVE BUILDING SYSTEMS (TABS) (4) Thermoactive building systems exploit the high thermal inertia of the slab in order to perform the peak-shaving. The peak-shaving consists in reducing the peak in the required cooling power (Figure Inc. ASHRAE, 2019 user. single for Licensed | {}
8061f3f7-98ce-4f6e-82ae-70b4aef91d68 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 55.12 2019 ASHRAE Handbook-HVAC Applications (SI) 21), so that it is possible to cool the structures of the building during a period in which the occupants are absent (during nighttime, in office premises). This way the energy consumption can be reduced, and lower night time electricity rate can be used. At the same time a reduction in the size of heating/cooling system components (including the chiller) is possible. TABS may be used both with natural and mechanical ventilation (depending on weather conditions). Mechanical ventilation with Chart Type: line 1 2 5 10 20 30 item_01 10 20 30 50 100 300 Fig. 20 Basic Characteristic Curve for Floor Heating and Ceiling Cooling dehumidifying may be required depending on external climate and indoor humidity production. In the example in Figure 22, the required peak cooling power needed for dehumidifying the air during daytime is sufficient to cool the slab during night time. As regards the design ofTABS, the planner needs to know if the capacity at a given water temperature is sufficient to keep the room temperature within a given comfort range. Moreover, the planner needs also to know the heat flow on the water side to be able to dimension the heat distribution system and the chiller/boiler. The present document provides methods for both purposes. When using TABS (Figure 23), the indoor temperature changes moderately during the day and the aim of a good design ofTABS is to maintain internal conditions within the range of comfort, i.e. -0.5 < PMV < 0.5, during the day, according to ISO Standard 7730 and ASHRAE Standard 55-2017. Some detailed building-system calculation models have been developed, as for the determination of the heat exchanges under unsteady state conditions in a single room, determination of thermal and hygrometric balance of the room air, prediction of comfort con- ditions, check of condensation on surfaces, availability of control strategies and calculation ofthe incoming solar radiation. The use of such detailed calculation models is, however, limited due to the high amount of time needed for the simulations. The development of a more user-friendly tool is required. The diagrams in Figure 22 show an example of the relation between internal heat gains, water supply temperature, heat transfer on the room side, hours of operation and heat transfer on the water side. The diagrams refer to a concrete slab with raised floor (R = 0.45 [m2.K]/W) and an allowed room temperature range of 21 to 26°C. The upper diagram shows on the y axis the maximum permissible total heat gain in space (internal heat gains plus solar gains), and on the x axis the required water supply temperature. The lines in the Chart Type: line 0.00 1.00 2.00 3.00 4.00 5.00 6.00 7.00 8.00 9.00 10.00 11.00 12.00 13.00 14.00 15.00 16.00 17.00 18.00 19.00 20.00 21.00 22.00 23.00 item_01 0Watts (W) 4Watts (W) 600Watts (W) 0Watts (W) 0Watts (W) 0Watts (W) 0Watts (W) 0Watts (W) 0Watts (W) 0Watts (W) 0Watts (W) 0Watts (W) 0Watts (W) 0Watts (W) 0Watts (W) 0Watts (W) 0Watts (W) 0Watts (W) 0Watts (W) 0Watts (W) 0Watts (W) 0Watts (W) 0Watts (W) 0Watts (W) 1= HEAT GAIN 2 = COOLING POWER NEEDED FOR CONDITIONING VENTILATION AIR 3 = COOLING POWER NEEDED ON WATER SIDE 4 = REDUCTION OF REQUIRED PEAK POWER Fig. 21 Example of Peak-Shaving Effect Inc. ASHRAE, 2019 user. single for Licensed | {}
7595539e-27b6-4eb2-83ed-2da86e8175e6 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Radiant Heating and Cooling 55.13 Chart Type: line PJM B, Cyan O E, M Cr Mn L F, Mo item_01 24°C 23°C 22°C 23°C 24°C 25°C 24°C 24°C Fig. 22 Example of Temperature Profiles and PMV Values Versus Time ![image](/image/placeholder) 60 Maximum temperature- Self-regulating effect of slab areaj increase (21 °C - 26°C) 50 TIOOr 369 358 [W/M 350 Wh/m2 d 40 300 250 IN space 30 gan M aximum neat 20 total Minimum -0- 24 h Maximum SWKI 95-3: occupants and equipment - 4- 16h 10 12h 8 h SW KI 95-3: lighting 0 16 17 18 19 20 21 22 Inlet temperature tabs [°C] Chart Type: line 16 17 18 19 20 21 22 item_01 0Wh/m2 40Wh/m2 38Wh/m2 32Wh/m2 28Wh/m2 24Wh/m2 10Wh/m2 Fig. 23 Working Principle of TABS diagram correspond to different operation periods (8, 12, 16, and 24 h) and different maximum amounts of energy supplied per day. The lower diagram shows the cooling power required on the water side (to dimension the chiller) for thermoactive slabs as a function of supply water temperature and operation time. Further, the amount of energy rejected per day is indicated. The example shows that, for a maximum internal heat gain of 38 W/m2 and 8 h operation, a supply water temperature of 18.2 °C is required. If, instead, the system is in operation for 12 h, a supply water temperature of 19.3°C is required. In total, the amount of energy rejected from the room is approximately 335 Wh/m2 per day. In the same conditions, the required cooling power on the water side is 37 W/m2 (for 8 h operation) and 25 W/m2 (for 12 h operation) respectively. Thus, by 12 h operation, the chiller can be much smaller. 13. EMBEDDED SYSTEMS CONTROLS Over the years there have been many different control solutions provided for embedded systems; most of these have been for heating systems. With the advent of cooling systems different approaches have been taken; not all of these have been successful. The control systems described in this section are some of the most successful used to control an embedded system for both heating and cooling. The control system will be capable of varying heating or cooling outputs as well as maintaining predetermined surface temperatures. Control of the heating and cooling system shall enable the spec- ified designed indoor temperatures to be achieved under the speci- fied variation on internal loads and external climate and, if specified, protect buildings and equipment against frost and mois- ture damage where necessary (when normal comfort temperature level is not required). Inc. ASHRAE, 2019 user. single for Licensed | {}
01025504-865f-41f5-9fd9-bda04456499b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 55.14 2019 ASHRAE Handbook-HVAC Applications (SI) The design of control system shall take into account the building, its intend use and the effective functioning of the heating system, efficient use of energy and avoiding heating the building to full design conditions when not required. This includes keeping distribu- tion heat losses as low as possible (e.g., reducing flow temperature when normal comfort temperature level is not required). Control and operation of the system help us to handle the conditioning systems with savings of operational costs and enable the maintenance of required indoor environmental conditions. To maintain the stable thermal environment, the control system is required to keep the balance between supplied heat from the system and the losses/gains of building environment under transient condi- tions. Slowly varying energy flows in form of heat losses through the envelope are determined by indoor and outdoor temperature, and direction and speed of wind. The envelope properties of build- ing materials and windows, ventilation systems, building tightness and orientation play the key role in terms ofheat flow quantity. The thermal capacity of building envelope (when active) can remove quickly varying uncontrolled internal heat gains (occupants, artifi- cial lighting, equipment) and window shading elements eliminate quickly varying periodic and predictable external heat gains from sun radiation. These uncontrolled gains play a significant role in the fall and the spring. Principally, the control strategy depends on the design characteristics, such as building envelope, thermal inertia, the system response times and others. The heating control modes are based on three system levels: · Local (individual) control, where the heat supplied to heated space is controlled · Zone control heat supplied to a zone normally consisting of sev- eral spaces (rooms) is controlled · Central control heat supplied to the whole building is controlled by a central system The control system classification is based on performance level: · Manual: heat supply to the heated space is only controlled by a manually operated device · Automatic: a suitable system or device automatically controls heat to the heated spaces · Timing function: heat supplied to heated space is shut off or reduced during scheduled periods (e.g., night setback) · Advanced timing function Heat supply to the heated space is shut off or reduced during scheduled periods (e.g., daytime with more expensive electricity tariff). Restarting the heat supply is optimized based on various con- siderations, including reduction of energy use. Several years ago, most of the controls were manual (i.e., the user could regulate a water temperature or a water flow rate by manually adjusting a valve, or the system could be turned on or shut off). Today, automatic controls are used everywhere and have in the last decade developed significantly (fuzzy logic, wireless data transmis- sion, introduction of protocols for data communication, etc.). For a floor heating and cooling system, the control is normally split up in a central control and an individual room control. The cen- tral control will accord the outdoor climate (based on the heating curve, which is influenced by building mass, heat loss, and differ- ences in heat required by the individual rooms) to control the supply water temperature to the floor system. The room control will then control the water flow rate or water temperature individually for each room, according to the point selected by the user. Central Control (Heating Only) Instead of controlling the supply water temperature, it is recom- mended to control the average water temperature (mean value of supply and return water temperature) according to outdoor and/or indoor temperatures. This is more directly related to the heat flux into the space. If, during the heating period, for example, the inter- nal load in the space increases, the heat output of the floor system will decrease and the return temperature will increase. If the central control is controlling the average water temperature, the supply temperature will automatically decrease due to the increase in return temperature. This will result in a faster and more accurate control of the heat in put to the space and will give about 15% better energy performance than controlling the supply water temperature. If the heating system is operated intermittently (night and/or weekend set- back) the central control is also important for providing high enough water temperatures (boost effect) during the preheat period in the morning (additional 10 to 15%; the absolute heat requirement com- pared to no night setback will be lower). The energy savings by night setback in residential buildings are, however, relatively low due to the high thermal insulation standard in new houses. Individual Control Installation of individual room temperature controls is recom- mended to improve comfort and the possible energy savings. Besides the energy benefits it is essential for the thermal comfort of the occupants, that they have a possibility for individual adjustment of the room temperature set point from room to room. The influence of the individual room control strategy for floor heating and radiators have shown a 15 to 30% energy saving by using an individual room control compared to central control only. Also the effect ofnight set back and boost by reheating in the morn- ing was studied, the advantage of a boost heating (i.e., the water temperature is increased above the temperature corresponding to the heating curve during the beginning of the preheat period in the morning). This reduces the preheat time and a longer setback period is possible. Boost reheating improves the energy performance by around 8%. Room Thermostats/Sensors In case of a floor heating system, the valve on the manifold is controlled by and connected to a room sensor by wiring. In terms of comfort, it is preferable to control the room tempera- ture as a function of the operative temperature in the area occupied by the person. Besides the position, it is important to consider the shape, size, and color (important for short-wave radiation, sunlight) of the sensor in order to express convective and radiant heat exchange between sensor and space similarly as for the person. The positioning of the room temperature sensor in the area occu- pied also save energy in comparison to positioning on the wall. By positioning in the occupied area, the variations in the room tempera- ture are smaller. Time Delay, Time Response Floor mass is naturally closely linked to system time response. Unpredictable thermal gains/losses leading to reduced/increased heating load with characteristic times shorter than time constant cannot be compensated by the control system. An obvious conse- quence of the response time of a conventional floor structures is that the instant control ofthe heating power is not necessary. Hence, reg- ulating the energy supply to the floor system within a time interval correlated to the response time is not different from a continuous power control. Self-Regulating Effect Due to the high impact the quickly varying heat gains (sunshine through windows) may have on the room temperature, it is neces- sary that the heating system can control for that (i.e., reduce or increase the heat output). For a low-temperature heating system like floor heating, a significant effect is so-called self control (Figure 24), which depends partly on the temperature difference between room and floor surface and partly on the difference between room Inc. ASHRAE, 2019 user. single for Licensed | {}
6c516dba-4562-44e6-bcb3-773e000feb0f | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Radiant Heating and Cooling 55.15 X-Axis: Hour Y-Axis: Temperature Chart Type: line 0 hours 8 hours 24 hours item_01 30°C 17.5°C 18.5°C Fig. 24 Self-Regulating Effect from Radiant Floor: As Temperature Differential Between Floor Surface and Space Dry-Bulb Temperature Increases, so Does Cooling Output from Floor for both Heating and Cooling and the average temperature in the layer, where the tubes are embed- ded. It means that fast change of operative temperature will equally change of heat exchange and result in great influence of total heat exchange. 14. RADIANT COOLING SYSTEM CONTROL The cooling output of radiant heat exchange may be limited to avoid condensation on the surface and in the building structure. A central control is also essential when using floor cooling. Due to the limitation of the cooling capacity a floor system will not always be able to control the room temperature at a fixed level. Basi- cally, the control should provide the maximum cooling power tak- ing into account comfort (floor temperature, room temperature) and the risk for condensation (dew point temperature). The central con- trol for floor cooling must then take into account the dew point in the building/space, when controlling the supply water temperature. This is done by adding a humidity sensor in the building/space con- nected to the central control unit. Control of TABS In this case, individual room control is not reasonable, but a zone control (south to north), where the supply water temperature, aver- age water temperature, or flow rate may differ from zone to zone, is available. The zoning should consider the external and/or internal heat loads. Relative small temperature differences between the heated or cooled surface and the space are typical for TABS sys- tems. This matter results in a significant degree of self control in specific cases by well-designed systems with low heating/cooling load, a concrete slab can be controlled at a constant core (water) temperature year round. If, for example, the core is kept at 22°C, the system will heat at room temperature below 22°C, and cool above the room temperature of 22°C. To avoid condensation (on or under surface), the water tempera- ture or the surface temperature and the absolute humidity have to be controlled. One possibility is to set a lower limit for the supply If the supply water temperature is limited, so it will never be below the dew point, then all temperatures (water, floor surface) after the mixing valve will be higher than the dew point, and there is no risk for condensation on the pipes, in the floor construction or on the floor. Control System Components Figure 24 shows the control system components which comprise a closed circuit complete with circulating pumps. This circuit is connected to the supply and return header. The circuit is also pro- vided with all the necessary isolating and balancing valves. There are two mixing pipes installed in the circuit. One is for heating and the other is for cooling. The heating mixing pipe is connected to a heating supply which can have a variable temperature together with a return. The cooling mixing pipe is connected to a cooling supply which can have a variable temperature together with a return. This section will outline the performance of a radiant cooled floor subjected to different solar radiation intensities and will look further into the controllability of the radiant cooled floor to maintain certain conditions such as space temperatures and floor surface tem- peratures. Cooled floors with and without coverings will also be analyzed to assess the influence of floor coverings. Temperature Differences and Flow Rates Figure 25 shows an example layout for dimensioning the flow through the embedded system. The flow rate is generally deter- mined for cooling as this is more critical. Typical supply and return temperatures through the floor are 13°C and 17°C, so to provide a certain cooling output the flow rate can be determined. The flow rate through the embedded system is constant volume. Variable-volume Inc. ASHRAE, 2019 user. single for Licensed | {}
edb8e3a7-7251-4f5b-b381-785316454a91 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 55.16 2019 ASHRAE Handbook-HVAC Applications (SI) ![image](/image/placeholder) 180°F 120°F 63°F 63°F 93 = 6 gpm q2 = 19 gpm 112°F 112°F 55°F 42°F 91 = 50 gpm Heating Cooling ¦ Flow in radiant system ¦ 91 = Q, Btu/hr / ((500 x (t1-t2)) ¦ ¦ --- ¦ --- ¦ ¦ Flow in radiant system ¦ 91 = 200,000 Btu/hr / ((500 x (63°F - 55°F)) ¦ ¦ Flow in radiant system ¦ 91 = 50 gpm ¦ ¦ Cooling injection flow ¦ q2 = Q, Btu/hr / ((500 x (t1-t2)) ¦ ¦ Cooling injection flow ¦ q2 = 200,000 Btu/hr / ((500 x (63°F - 42°F)) ¦ ¦ Cooling injection flow ¦ ¦ ¦ Cooling injection flow ¦ 92 = 19 gpm ¦ ¦ Heating injection flow ¦ 93 = Q, Btu/hr / ((500 x (t1-t2)) ¦ ¦ Heating injection flow ¦ 93 = 200,000 Btu/hr / ((500 X (180°F - 112°F)) ¦ ¦ Heating injection flow ¦ 93 = 6 gpm ¦ ¦ Heating injection flow ¦ ¦ ¦ Heating injection flow ¦ Fig. 25 Heating and Cooling Connections to ¦ Radiant Floor Loop systems can also be used and these will also be described in this sec- tion. For example, assume the embedded system will have a cooling capacity of 1000 W (1 kW). Assuming a supply water temperature of 13°C and a return water temperature of 17°C, the flow rate through the embedded system will be 0.0595 kg/s. This is the constant-volume flow through the embedded system. As shown in Figure 25, there are both heating and cooling connec- tions to the control loop. Assuming that the floor is in full design cooling capacity, then the return water from the embedded system will be 17°C, and this will have to be cooled to 13°C to provide the required cooling from the embedded system. The mixing pipe is connected to a chilled- water supply and return. Again, we can assume that the chilled- water supply temperature to the mixing pipe is 6°C. The amount of cooling required from the primary chilled water is the same as the cooling output from the embedded system (1 kW). The temperature differential through the mixing pipe is 17°C return from the loop and a 6°C supply, so the t = 17 - 6 = 11 K. The flow rate through the primary chilled-water connection to the mixing pipe is 0.02 kg/s. By keeping the primary flow rate lower than the circuit flow rate, the primary connections are also smaller, which enables the two- way control valve in the chilled water connection to have an improved Cv value and authority. Another reason for this design option is that the primary chilled- water flow rate is much lower than the circuit loop flow rate and this Chart Type: line 6.0 Btu/sqft 8.0 Btu/sqft 10.0 Btu/sqft 12.0 Btu/sqft 14.0 Btu/sqft 16.0 Btu/sqft 18.0 Btu/sqft 20.0 Btu/sqft 0.0E+00 GPM/sqft item_01 70.0Fahrenheit (F) 70.0Fahrenheit (F) 68.0Fahrenheit (F) 65.0Fahrenheit (F) 63.0Fahrenheit (F) 62.0Fahrenheit (F) 64.0Fahrenheit (F) 65.0Fahrenheit (F) 80.0Fahrenheit (F) Fig. 26 Characteristics of Variable-Flow Constant- Temperature Control limits the amount of 6°C water that could be circulated through the floor. For heating, it is a very similar situation. The flow rate through the loop remains the same constant flow rate. The maximum surface temperature of an embedded system for heating is 28°C. Typical heating supply and return temperatures in the circuit are 60 to 52°C, but the maximum heating water primary supply to the mixing pipe could be 90°C. The flow rate to the mixing pipe would then be 0.0079 kg/s. This is about 1/10 ofthe loop flow rate. Again, this keeps the pri- mary connections smaller than the circulating loop, which keeps the pipe connection smaller, which in turn keeps the control valve to a small size which improves the Cv and the valve authorities. For variable-flow, constant-temperature control (Figure 26), the water supply temperature to the floor is kept at a constant 12°C, and the floor surface temperature is maintained at 20°C. As the cooling output to the space increases to maintain space set-point temperature, the water flow through the floor is increased. For this control option, the water flow rate through the floor is proportional to the cooling output from the floor. As the water flow rate increases to provide the cooling output from the floor the leaving water tem- perature from the floor decreases to a minimum of 17°C. For constant-flow, variable-temperature control (Figure 27), the water supply temperature to the floor is varied, the floor surface temperature is maintained at 20°C. As the cooling output to the space increases to maintain space set-point temperature, the water flow through the floor is constant. For this control option, the supply water temperature to the floor is varied from 16.1 to 11.1°C, which is proportional to the cooling output from the floor. As the supply water temperature decreases to provide the cooling output from the floor the leaving water temperature from the floor decreases to a minimum of 17°C. For constant-flow, constant-temperature control (Figure 28), the water supply temperature to the floor is kept at a constant 12.7°C, The floor surface temperature is varied from 16.6 to 21.6°C. As the cooling output to the space increases to maintain space set- point temperature, the water flow through the floor is constant. For this control option, the leaving water temperature from the floor is proportional to the cooling output from the floor. As the cooling out- put increases to provide the cooling output from the floor surface temperature is also increased. From these three alternatives, constant flow, variable tempera- ture provides the smoothest control. Inc. ASHRAE, 2019 user. single for Licensed | {}
1056478c-448f-439d-9c6a-55c3dbf24062 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Radiant Heating and Cooling 55.17 Chart Type: line 6.0 Btu/h self 8.0 Btu/h self 10.0 Btu/h self 12.0 Btu/h agh 14.0 Btu/h agh 16.0 Btu/h self 18.0 Btu/h agh 20.0 Btu/h self item_01 70.0Temperature (°C) 65.0Temperature (°C) 65.0Temperature (°C) 65.0Temperature (°C) 65.0Temperature (°C) 64.0Temperature (°C) 63.0Temperature (°C) 63.0Temperature (°C) Fig. 27 Constant-Flow, Variable-Temperature Control Chart Type: line 6.0 Btuth sqft 8.0 Btuth sqft 10.0 Btuh sqft 12.0 Btuh sqft 14.0 Btuh sqft 16.0 Btuh sqft 18.0 Btuh sqft 20.0 Btuth sqft item_01 60.0Degrees Fahrenheit (°F) 58.0Degrees Fahrenheit (°F) 60.0Degrees Fahrenheit (°F) 62.0Degrees Fahrenheit (°F) 64.0Degrees Fahrenheit (°F) 65.0Degrees Fahrenheit (°F) 66.0Degrees Fahrenheit (°F) 68.0Degrees Fahrenheit (°F) Fig. 28 Constant-Flow, Constant - Temperature Control Dew-Point The floor surface temperature of the radiant floor is lower than the air temperature in the space. Therefore, if the surface tempera- ture ofthe floor falls down below the space air dew point at any area, water falls out and the floor gets wet. The floor surface temperature is dependent on the water temperature at the specific area, the cool- ing load of this area and the distance between the tubes within the floor construction. Because of the distance between the tubes, the floor surface temperature is not constant. It is recommended to select a minimal EWT equal to the supposed maximal dew point temperature to avoid a condensation on the floor surface and to guarantee the selected cooling capacity of the radiant system. Addi- tional, the EWT should be controlled by a humidity control sensor. If on any reason an EWT below the supposed dew point is selected, the minimal possible surface temperature of the floor in areas with reduced loads must be calculated carefully. For example, ifthe indoor air is controlled ofa dry bulb tempera- ture of 24°C and a relative humidity of 50%, the suggested dew point is approximately 13°C. Therefore, a minimal EWT of 13°C may be selected. The combination of the radiant floor cooling sys- tem with a natural ventilation concept requires an accurate calcula- tion of the maximal suggested dew points within the space, considering the outdoor air conditions as well as the latent loads of the space. Room Control In some buildings, it may be necessary to control individual rooms separately from other rooms without adjusting the weather- Chart Type: line Supply Return Cooperative item_01 50Temperature (°C) 30Temperature (°C) 19Temperature (°C) Fig. 29 Control Strategy for Combined Radiant Heating and Cooling Floor compensation control. One way to accomplish this is with valve actuators attached to individual manifold loops that service the rooms where control is desired. 이리 moji Figure 29 shows the principles that may be applied for a space with mainly outdoor cooling and heating loads, with a combined radiant heating and cooling floor. Spaces with a high amount ofinte- rior cooling loads are quite more difficult to control if the radiant floor is used both for heating and cooling. Control Strategy for Office Buildings The control strategy for office buildings with its high number of internal loads, which are independent of outdoor conditions (weather), requires more considerations. Interior Zones. The interior zones may have only cooling loads. There, the radiant floor may provide only cooling to the zone. The EWT may be kept constant and the water flow (on or off) is con- trolled by a space thermostat. It is important to avoid an under cool- ing of the space during the night or during unoccupied periods. The water flow should switch off, if the space temperature decreases under the allowed level. It is important to consider, that there is a defined amount of cooling power stored within the construction slab, so the switch-off level should be higher than the allowed min- imal temperature level. Perimeter Zones. Perimeter zones may be equipped with a radi- ant floor system that provides both heating and cooling to the space. If the radiant floor is the only heating system, the radiant floor must be selected for the heating loads. The EWT may be controlled by a weather compensation control combined with a zone control sys- tem. In cooling mode, the EWT should be kept on a constant level. In most cases, the radiant floor cooling system for a perimeter zone is combined with either a mechanical ventilation or a natural venti- lation system to provide the remaining cooling capacity and the nec- essary fresh air and to reduce the latent loads. Itis important to avoid the cooling ofa heated floor slab or the reverse situation during nor- mal weather situations. The following strategy may be used. During periods where heating and cooling is necessary during the same day, the radiant floor should provide only heating to the space. The space cooling should be provided by the additional sys- tem (may be through operable windows). This can be designed by using a delay element of at least 1 day to switch the radiant floor sys- tem between heating and cooling mode. Outside temperatures are usually not as high during periods that require heating and cooling during the same day. So the additional air ventilation system may be used in economizer mode. During periods where usually no heating is necessary, the floor is used only for cooling as the first cooling system in a same way as in the interior zones. Inc. ASHRAE, 2019 user. single for Licensed | {}
2f4973d9-e3e9-41f7-a985-35c4cea092f2 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 55.18 2019 ASHRAE Handbook-HVAC Applications (SI) REFERENCES Athienitis, A.K., and J.G. Shou. 1991. Control of radiant heating based on the operative temperature. ASHRAE Transactions 97(2). Braun, J.E. 1990. Reducing energy costs and peak electrical demand through optimal control of building thermal storage. ASHRAE Transactions 96(2). Brunk, M.F. 1993. Cooling ceilings-An opportunity to reduce energy costs by way of radiant cooling. ASHRAE Transactions 99(2). Fanger, P.O. 1972. Thermal comfort analysis and applications in environ- mental engineering. McGraw-Hill. Harmon, J.J., and H.C. Yu. 1993. Cold air distribution and concerns about condensation. ASHRAE Journal (May). Kalisperis, L.N., M. Steinman, L.H. Summers, and B. Olesen. 1990. Auto- mated design of radiant heating systems based on thermal comfort. ASHRAE Transactions 96(1). Kochendorfer, C. 1996. Standardized testing of cooling panels and their use in system planning. ASHRAE Transactions 102(1). Leigh, S.B. 1991. An experimental study of the control of radiant floor heat- ing systems: Proportional flux modulation vs. outdoor reset control with indoor temperature offset. ASHRAE Transactions 97(2). Ling, M.D.F., and J.M. Deffenbaugh. 1990. Design strategies for low-tem- perature radiant heating systems based on thermal comfort criteria. ASHRAE Transactions 96(1). MacCluer, C.R. 1991. The response ofradiant heating systems controlled by outdoor reset with feedback. ASHRAE Transactions 97(2). MacCluer, C.R. 1989. The control of radiant slabs. ASHRAE Journal (Sep- tember). Olesen, B. W. 1994. Comparative experimental study ofperformance of radi- ant flow-heating systems and wall panel heating system under dynamic conditions. ASHRAE Transactions 100(1). ISO. 1984. Moderate thermal environments-Determination of the PMV and PPD indices and specification of the condition for thermal comfort. International Standard 7730. International Organization for Standard- ization. ROOM. [No date.] A method to predict thermal comfort at any point in space. OASYS Ltd. developed by ARUP Research and Development, London, U.K. Ruud, M.D., J.W. Mitchell, and S.A. Klein. 1990. Use of building thermal mass to offset cooling loads. ASHRAE, Transactions 96(2). Simmonds, P. 1991. A building's thermal inertia. Presented at CIBSE National Conference, Canterbury. Simmonds, P. 1991. The utilization and optimization ofa building's thermal inertia in minimizing the overall energy use. ASHRAE Transactions 97(2). Simmonds, P. 1992. The design, simulation and operation of a comfortable indoor climate for a standard office. Presented at ASHRAE/DOE/BTEC conference, Clearwater Beach, FL. Simmonds, P. 1993. Thermal comfort and optimal energy use. ASHRAE Transactions 99(1). Simmonds, P. 1993. Designing comfortable office climates. Presented ASHRAE Building Design Technology and Occupant Well-Being Temperate Climates, Brussels. Simmonds. P. 1993. Dynamic comfort control. Presented at CIBSE National Conference, Manchester. Simmonds, P. 1994. Control strategies for combined heating and cooling radiant systems. ASHRAE Transactions 100(1). Simmonds, P. 1993. Thermal comfort and optimal energy use. ASHRAE Transactions 99(1). Simmonds, P. 2003. Practical applications of designing and operating occu- pied spaces in accordance with PPD/PMV conditions. Presented ASHRAE /CIBSE Conference Edinburgh. Simmonds, P. 2003. Can the PPD/PMV be used to control the indoor thermal environment? Presented at ASHRAE /CIBSE Conference, Edinburgh. van Gerpen, J.H., and H.N. Shapiro. 1981. Analysis of slab heated buildings. ASHRAE Transactions. Welty, J.R., C.E. Wicks, and R.E. Wilson. 1969. Fundamentals of momen- tum, heat and mass transfer. John Wiley and Sons. Udagawa, M. 1993. "Simulation of panel cooling systems with linear sub- system model. ASHRAE Transactions 99(2). Zweifel, G., and M. Kochenz. 1993. Simulation of displacement ventilation and radiant cooling with DOE-2. ASHRAE Transactions 99(2). a at in at Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
2a551db6-9039-4f8a-87d5-5c0d0422ceba | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 56 SEISMIC- AND WIND-RESISTANT DESIGN ¦ SEISMIC-RESISTANT DESIGN ¦ 55.1 ¦ ¦ --- ¦ --- ¦ ¦ Terminology ¦ 55.2 ¦ ¦ Calculations ¦ 55.2 ¦ ¦ Applying Static Analysis ¦ 55.3 ¦ ¦ Computation of Loads at Building Connection ¦ 55.6 ¦ ¦ ANSI Steel Bolts ¦ 55.7 ¦ ¦ Lag Screws into Timber ¦ 55.7 ¦ ¦ Concrete Post-Installed Anchor Bolts ¦ + 55.7 ¦ ¦ Weld Capacities ¦ 55.8 ¦ ¦ Seismic Snubbers . ¦ 55.8 ¦ ALMOST all inhabited areas of the world are susceptible to the damaging effects of either earthquakes or wind. Restraints that are designed to resist one may not be adequate to resist the other. Consequently, when exposure to either earthquake or wind loading is a possibility, strength of equipment and attachments should be evaluated for all appropriate conditions. Earthquake damage to inadequately restrained HVAC&R equip- ment can be extensive. Mechanical equipment that is blown off the support structure can become a projectile, threatening life and prop- erty. The cost of properly restraining the equipment is small com- pared to the high costs of replacing or repairing damaged equipment, liability for loss oflife, or compared to the cost of building downtime due to damaged facilities. Design and installation of seismic and wind restraints have the following primary objectives: · To reduce the possibility of injury and the threat to life. · To reduce long-term costs due to equipment damage and resultant downtime. Note: The intent of building codes with respect to seismic design is not to prevent damage to property or the restrained equipment itself. This chapter covers the design of restraints to limit equipment movement and to keep the equipment captive during an earthquake or extreme wind loading. Seismic restraints and isolators do not re- duce the forces transmitted to the restrained equipment. Instead, properly designed and installed seismic restraints and isolators have the necessary strength to withstand the imposed forces. However, equipment that is to be restrained must also have the necessary strength to remain attached to the restraint. The International Building CodeⓇ (IBC) (ICC 2009) provides a prescriptive approach for applying an equivalent static force repre- senting the dynamic forces transmitted to the equipment by seismic or high-wind events. For mechanical systems, analysis of seismic and wind loading conditions can use static analysis from the pre- scriptive approach. Conservative safety factors are applied to reduce the complexity of earthquake and wind loading response analysis and evaluation. The following three aspects are considered in a prop- erly designed restraint system: · Attachment of equipment to restraint. The equipment must be pos- itively attached to the restraint, and must have sufficient strength to withstand the imposed forces and to transfer the forces to the restraint. The preparation of this chapter is assigned to TC 2.7, Seismic and Wind Resistant Design. ¦ Seismic Restraints ¦ 55.9 ¦ ¦ --- ¦ --- ¦ ¦ Restraint of Pipe and Duct Risers ¦ 55.10 ¦ ¦ Examples ¦ 55.11 ¦ ¦ Installation Problems ¦ 55.14 ¦ ¦ WIND-RESISTANT DESIGN ¦ 55.15 ¦ ¦ Terminology ¦ 55.15 ¦ ¦ Calculations ¦ 55.16 ¦ ¦ Wall-Mounted HVAC&R Component Calculations (Louvers) ¦ 55.17 ¦ ¦ Certification of HVAC&R Components for Wind ¦ 55.20 ¦ · Restraint design. The restraint also must be strong enough to with- stand the imposed forces. This should be determined by the man- ufacturer by tests and/or analysis. · Attachment of restraint to substructure. Attachment may be by bolts, lag bolts, welds, or concrete anchors. The substructure must be capable of surviving the imposed forces. 1. SEISMIC-RESISTANT DESIGN Most seismic requirements adopted by local jurisdictions in North America are based on model codes developed by the Interna- tional Code Council (ICC), such as the International Building Code (IBC). The National Building Code of Canada (NRC-IRC 2010) is Canada 's equivalent version of the IBC. Local building officials must be contacted for specific requirements that may be more strin- gent than those presented in this chapter. Other sources of seismic restraint information include · Seismic Restraint Manual: Guidelines for Mechanical Systems (SMACNA 2008), includes seismic restraint information for mechanical equipment subjected to seismic forces of up to 1.0g. · The most current National Fire Protection Association (NFPA) standards on restraint design are compliant with the IBC. · U.S. Department of Energy DOE 430. 1A and ASME AG-1 cover restraint design for nuclear facilities. · DOD (2007) provides guidance for seismic design for U.S. Department of Defense (DoD) and Department of State (DoS) facilities, and DOD (2005) provides the seismic and wind design constants. · A Practical Guide to Seismic Restraint (ASHRAE 2000) covers a broad range of seismic restraint design issues. · Federal Emergency Management Agency (FEMA) installation manuals FEMA-412, FEMA-413, and FEMA-414 are available at the FEMA Web site. They provide a step-by-step process with details for installing seismic restraint devices. In seismically active areas where governmental agencies regulate the earthquake-resistive design of buildings (e.g., California), the HVAC engineer usually does not prepare the code-required seismic restraint calculations. The HVAC engineer selects the heating and cooling equipment and, with the assistance of the acoustical engi- neer (if applicable to the project), selects the required vibration iso- lation devices. Seismic restraint calculations are performed for nonstructural components, and designs for piping, ductwork, and conduits are designed and detailed. For design-build projects, the design is reviewed by the registered design professional. Nonstruc- tural restraint components are designed and constructed to resist the aftereffects of earthquake motions as required by the applicable code 56.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
b3b1f2fd-307f-46db-a36d-07e3e4574a19 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 56.2 2019 ASHRAE Handbook-HVAC Applications (SI) and in accordance with local building officials. Reviewed designs are submitted for approval by the authority having jurisdiction. To ensure proper design factors are used, a designer should obtain information on the seismic design conditions (site class and occupancy category). The importance of the equipment and systems affected should be understood for code applications to include those items that must be functional after seismic events. The owner or building officials maintain the code-required quality control over the design by requiring construction documents, special inspection requirements, and certification requirements prepared by the registered design professional and approved by the authority having jurisdiction. Upon completion of installation, the supplier of the seismic restraints, or a qualified representative, should inspect the installation and verify that all restraints and force-resisting sys- tems are installed properly and comply with specifications. 1.1 TERMINOLOGY Base plate thickness. Thickness of the equipment bracket fas- tened to the floor. Effective shear force Veff· Maximum shear force of one seismic restraint or tie-down bolt. Effective tension force Teff. Maximum tension force or pullout force on one seismic restraint or tie-down bolt. Equipment. Any HV AC&R component that must be restrained from movement during an earthquake. Resilient support. An active seismic device (such as a spring with a bumper) to prevent equipment from moving more than a specified amount. Response spectra. Relationship between the acceleration response of the ground and the peak acceleration of the earthquake in a damped single degree of freedom at various frequencies. The ground motion response spectrum varies with soil conditions. Rigid support. Passive seismic device used to restrict any move- ment. Shear force V. Horizontal force generated at the plane of the seismic restraints, acting to cut the restraint at the base. Seismic restraint. Device designed to withstand seismic forces and hold equipment in place during an earthquake. Seismic force levels. The geographic location ofa facility deter- mines its seismic spectral response acceleration levels, as given in the International Building Code. Snubber. Device made of steel-housed resilient bushings arranged to prevent equipment from moving beyond an established gap. Tension force T. Force generated by overturning moments at the plane of the seismic restraints, acting to pull out the bolt. 1.2 CALCULA TIONS Sample calculations presented here assume that the equipment support is an integrated resilient support and restraint device. When the two functions of resilient support and motion restraint are sepa- rate or act separately, additional spring loads may need to be added to the anchor load calculation for the restraint device. Internal loads within integrated devices are not addressed in this chapter. These devices must be designed to withstand the full anchorage loads plus any internal spring loads. Both static and dynamic analyses reduce the force generated by an earthquake to an equivalent statically applied force, which acts in a horizontal or vertical direction at the component's center of grav- ity. The resulting overturning moment is resisted by shear and ten- sion (pullout) forces on the tie-down bolts. Static analysis is used for both rigidly mounted and resiliently mounted equipment. Dynamic Analysis Dynamic analysis of the isolation and snubber systems may be based on ground-level response spectra given in the IBC and reference standard ASCE 7 (ASCE 2005), which can be used as input for a dynamic analysis. Response spectra applied to nonstructural components can be developed from ICC-ES acceptance criteria AC 156 (ICC-ES 2007). Site-specific ground response spectra developed by a geotechnical or soils engineer may be used, as well. The computer analysis used must be capable of analyzing nonlinear supports and site-specific ground motions. This dynamic analysis provides the maximum seis- mic input accelerations to the equipment components, allowing com- parison to three-dimensional shock (drop) or shaker test fragility levels to determine equipment survivability. Actual drop or shaker test data for all HVAC equipment may not be available for the next several years. Using the response spectra in the code for ground-floor inputs, or the spectra in ATC 29-2 for upper floors, a dynamic analysis can yield maximum input accelerations to equipment components. Comparing them to the allowable acceleration values in the table helps the engineer assess equipment survivability. Dynamic analy- sis can also provide maximum movement at all connections and, when added to the floor-to-ceiling code-mandated movements, allows the engineer to design these flexible connections and avoid pull-out or shear failures at these locations. Under some conditions, Chapter 17 of IBC requires certificates of compliance for components and their attachments for a compo- nent importance factor Ip of 1.0 or 1.5. This is a life-safety issue as well as an essential equipment issue. Essential equipment with an Ip = 1.5 must have a certificate of compliance. Issuance of a certif- icate of compliance to the engineer of record and building official can be based on dynamic analysis. Most building officials require a stamp by a registered professional to be part of the calculations and certificate of compliance. Table 1 provides guidance on type of analysis (static or dynamic) and certificate of compliance docu- mentation is required. Sample dynamic analysis is beyond the scope of this chapter and should be provided by experienced regis- tered professionals. A common approach assumes an elastic re- sponse spectrum. The results of the dynamic analysis can then be scaled up or down as a percentage of the total lateral force obtained from the static analysis performed on the building. Dynamic analysis of piping, ductwork, and equipment reflects the response of the equipment for all earthquake-generated frequen- cies. Especially for piping and equipment, when the earthquake forcing frequencies match the natural frequencies of the system, the resulting applied forces increase. Static Analysis as Defined in the International Building Code The IBC specifies a design lateral force Fp for nonstructural com- ponents as Ip Fp = (0.4apSDS Wp) 1 + 2 름 Rp but Fp need not be greater than nor less than Fp = 1.6SDSIpWp where SDS is determined by Fp = 0.3SDSIPWP SDS = 2FaSs/3 where (1) (2) ap component amplification factor in accordance with Table 2. Inc. ASHRAE, 2019 user. single for Licensed SDS = design spectral response acceleration at short periods. Ss is the (3) (4) mapped spectral acceleration from Tables 4 and 5. (Note: More | {}
3ec035ae-cafd-46f5-bd50-038c0b6addc0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Seismic- and Wind-Resistant Design 56.3 Table 1 IBC Seismic Analysis Requirements ¦ Component Operation Required for Life Safety ¦ Building Seismic Design Category* ¦ Required Analysis Type ¦ Required Analysis Type ¦ Required Analysis Type ¦ Required Analysis Type ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Component Operation Required for Life Safety ¦ Building Seismic Design Category* ¦ Anchorage ¦ Equipment Structural Capacity ¦ Equipment Operational Capacity ¦ Certificate of Compliance ¦ ¦ No ¦ A ¦ Not required ¦ Not required ¦ Not required ¦ Not required ¦ ¦ No ¦ B, C ¦ Not required ¦ Not required ¦ Not required ¦ Not required ¦ ¦ No ¦ D ¦ Static ¦ Dynamic or test ¦ Not required ¦ For mounting only ¦ ¦ Yes ¦ C, D ¦ Static ¦ Dynamic or test ¦ Dynamic or test ¦ For continued operation ¦ ¦ No ¦ E ¦ Static ¦ Dynamic or test ¦ Dynamic or test ¦ For continued operation ¦ ¦ No ¦ C, D ¦ Static ¦ Not required ¦ Not required ¦ Not required ¦ ¦ Yes ¦ C, D ¦ Static ¦ Dynamic or test ¦ Dynamic or test ¦ For continued operation ¦ ¦ No ¦ F ¦ Static ¦ Dynamic or test ¦ Not required ¦ For mounting only ¦ ¦ Yes ¦ F ¦ Static ¦ Dynamic or test ¦ Dynamic or test ¦ For continued operation ¦ *If in question, reference structural documents. Table 2 Coefficients for Mechanical Components ¦ Mechanical and Electrical Component or Element ¦ ap ¦ Rp ¦ ¦ --- ¦ --- ¦ --- ¦ ¦ General Mechanical ¦ ¦ ¦ ¦ Boilers and furnaces ¦ 1.0 ¦ 2.5 ¦ ¦ Piping ¦ ¦ ¦ ¦ High-deformability elements and attachments ¦ 1.0 ¦ 3.5 ¦ ¦ Limited-deformability elements and attachments ¦ 1.0 ¦ 2.5 ¦ ¦ Low-deformability elements or attachments ¦ 1.0 ¦ 1.25 ¦ ¦ HVAC Equipment ¦ ¦ ¦ ¦ Vibration isolated ¦ 2.5 ¦ 2.5 ¦ ¦ Non-vibration isolated ¦ 1.0 ¦ 2.5 ¦ ¦ Mounted in-line with ductwork ¦ 1.0 ¦ 2.5 ¦ Source: IBC (2006). detailed maps for the United States are available at the U.S. Geological Survey Web site: www.usgs.gov.) Fa = function of site soil characteristics and must be determined in consultation with either project geotechnical (soils) or structural engineer. Values for Fa for different soil types are given in Table 3. (Note: Without an approved geotechnical report, the default site soil classification is assumed to be site class D.) Rp = component response modification factor in accordance with IBC. Ip = component importance factor (see the IBC for explanation and determination of Ip). 1 + 2z/h= height amplification factor where z is the height of attachment in the structure and h is the average height of the roof above grade. The value of z ≥ 0 and z/h need not exceed 1. Wp (D) = mass of equipment, which includes all items attached or contained in the equipment. The forces acting on the equipment are the lateral and vertical forces resulting from the earthquake, the force of gravity, and the forces of the restraint holding the equipment in place; these act on the center of gravity. The analysis assumes the equipment does not move during an earthquake; thus, the sum of the forces and moments must be zero. When calculating the overturning moment, including an uplift factor, the vertical component F at the center of pv gravity is typically defined (for the IBC) to be F = 0.2SDsD pv If the equipment being analyzed is isolated, the final computed force must be doubled per section 1621.3.1 of the code. Per section 1621.1.7 of the code, forces used when computing the loads for shallow (under 8 bolt diameter) embedment anchors are to be increased by a factor of 1.3R Per section 1621.3. 12.2 of the code, the only permitted expan- sion anchors for non-vibration-isolated equipment over 7.46 kW are undercut anchors. (5) Tables 4 and 5 contain brief listings of Ss factors that can be used to calculate the magnitude of the horizontal static seismic force act- ing at the equipment center of gravity. Values for IBC 2006 are Table 3 Values of Site Coefficient Fa as Function of Site Class and Spectral Response Acceleration at Short Period (S) ¦ Site Class ¦ Soil Profile Name ¦ Mapped Spectral Response Acceleration at Short Periodsa ¦ Mapped Spectral Response Acceleration at Short Periodsa ¦ Mapped Spectral Response Acceleration at Short Periodsa ¦ Mapped Spectral Response Acceleration at Short Periodsa ¦ Mapped Spectral Response Acceleration at Short Periodsa ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Site Class ¦ Soil Profile Name ¦ Ss ≤ 0.25 ¦ Ss = 0.50 ¦ Ss = 0.75 ¦ Ss = 1.00 ¦ S,≥1.25 ¦ ¦ A ¦ Hard rock ¦ 0.8 ¦ 0.8 ¦ 0.8 ¦ 0.8 ¦ 0.8 ¦ ¦ B ¦ Rock ¦ 1.0 ¦ 1.0 ¦ 1.0 ¦ 1.0 ¦ 1.0 ¦ ¦ C ¦ Very dense soil and soft rock ¦ 1.2 ¦ 1.2 ¦ 1.1 ¦ 1.0 ¦ 1.0 ¦ ¦ Dc ¦ Stiff soil profile ¦ 1.6 ¦ 1.4 ¦ 1.2 ¦ 1.1 ¦ 1.0 ¦ ¦ E ¦ Soft soil profile ¦ 2.5 ¦ 1.7 ¦ 1.2 ¦ 0.9 ¦ b ¦ F See IBC for more information aUse straight-line interpolation for intermediate values of mapped spectral accelera- tion at short period S bSite-specific geotechnical investigation and dynamic site response analyses must be performed to determine appropriate values. cD is the default Site Class unless otherwise stated in the approved geotechnical report. available on the USGS web site for U.S. locations or in Tables F-2 and G-2 of DOD (2005) for worldwide locations. 1.3 APPLYING STATIC ANALYSIS The prescriptive method in the IBC allows that an equivalent static force can be calculated that represents the dynamic motions of an earthquake. The static forces acting on a piece of equipment are vertical and lateral forces resulting from the earthquake, the force of gravity, and forces at the restraints that hold the equipment in place. The analysis assumes that the equipment does not move during the earthquake and that the relative accelerations between its center of gravity and the ground generate forces that must be balanced by reactions at the restraints. Guidance from the code bodies indicates that equipment can be analyzed as though it were a rigid component; however, a factor ap is applied in the computation to address flexi- bility issues on particular equipment types or flexible mounting arrangements. (Note: for dynamic analysis, it is common to use a 5% damping factor for equipment and a 1% damping factor for pip- ing.) Although the basic force computation is different, the details ofload distribution in the examples that follow apply independently of the code used. The forces acting on the restraints include both shear and tensile components. The application direction of the lateral seismic accel- eration can vary and is unknown. Depending on its direction, it is likely that not all of the restraints will be affected or share the load equally. It is important to determine the worst-case combination of forces at all restraint points for any possible direction that the lateral wave front can follow to ensure that the attachment is adequate. Inc. ASHRAE, 2019 user. single for Licensed | {}
1e2baa20-6fc8-4730-9c82-4c1cc7d54618 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 56.4 2019 ASHRAE Handbook- - HVAC Applications (SI) Table 4 Ss Numbers* for Selected U.S. Locations (U.S. COE 1998) ¦ State, City ¦ ZIP ¦ Ss ¦ State, City St. Louis Mississippi ¦ ZIP ¦ Ss ¦ State, City ¦ ZIP ¦ Ss 0.160 0.293 ¦ State, City ¦ ZIP ¦ Ss ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Alabama ¦ ¦ ¦ Ft. Wayne ¦ 46835 ¦ 0.162 ¦ Butte ¦ 59701 97222 ¦ 0.599 ¦ Rhode Island ¦ ¦ ¦ ¦ Birmingham ¦ 35217 ¦ 0.328 50310 ¦ Gary Tulsa ¦ 46402 ¦ 0.173 ¦ Great Falls ¦ 59404 ¦ 0.248 ¦ Providence ¦ 02907 ¦ 0.267 ¦ ¦ Mobile ¦ 36610 ¦ 0.124 ¦ Indianapolis ¦ 46260 ¦ 0.182 ¦ Nebraska Wisconsin Green Bay ¦ ¦ ¦ South Carolina ¦ ¦ ¦ ¦ Montgomery ¦ 36104 ¦ 0.170 ¦ South Bend ¦ 46637 Pocatello Springfield ¦ 0.121 ¦ Lincoln ¦ 68502 ¦ 0.177 ¦ Charleston ¦ 29406 St. Joseph ¦ 1.56 ¦ ¦ Arkansas ¦ ¦ ¦ Kansas ¦ ¦ ¦ Omaha ¦ 68144 ¦ 0.127 ¦ Columbia ¦ 29203 ¦ 0.578 ¦ ¦ Little Rock ¦ 72205 ¦ 0.461 ¦ Kansas City ¦ 66103 ¦ 0.122 ¦ Nevada ¦ ¦ ¦ South Dakota ¦ ¦ ¦ ¦ Arizona ¦ ¦ ¦ Topeka ¦ 66614 ¦ 0.184 ¦ Las Vegas ¦ 89106 ¦ 0.637 ¦ Rapid City ¦ 57703 ¦ 0.153 ¦ ¦ Phoenix ¦ 85034 ¦ 0.226 ¦ Wichita ¦ 67217 ¦ 0.142 ¦ Reno ¦ 89509 ¦ 1.29 ¦ Sioux Falls ¦ 57104 ¦ 0.113 ¦ ¦ Tuscon ¦ 85739 ¦ 0.325 ¦ Kentucky ¦ ¦ ¦ New York ¦ ¦ ¦ Tennessee ¦ ¦ ¦ ¦ California ¦ ¦ ¦ Ashland ¦ 41101 ¦ 0.221 ¦ Albany ¦ 12205 ¦ 0.275 ¦ Chattanooga ¦ 37415 ¦ 0.500 ¦ ¦ Fresno ¦ 93706 ¦ 0.592 ¦ Covington ¦ 41011 ¦ 0.186 ¦ Binghampton ¦ 13903 ¦ 0.185 ¦ Knoxville ¦ 37920 ¦ 0.589 ¦ ¦ Los Angeles Evansville ¦ 90026 ¦ 1.50 ¦ Louisville ¦ 40202 ¦ 0.247 ¦ Buffalo ¦ 14222 ¦ 0.319 ¦ Memphis ¦ 38109 ¦ 1.25 ¦ ¦ Oakland ¦ 94621 ¦ 1.55 Illinois 0.170 ¦ Louisiana ¦ ¦ ¦ Elmira ¦ 14905 ¦ 0.173 ¦ Nashville ¦ 37211 ¦ 0.305 ¦ ¦ Sacramento ¦ 95823 ¦ 0.568 Carthage 64836 54302 ¦ Baton Rouge ¦ 70807 ¦ 0.144 ¦ New York ¦ 10014 ¦ 0.425 ¦ Texas ¦ ¦ ¦ ¦ San Diego ¦ 92101 ¦ 1.54 Columbia 65202 53140 ¦ New Orleans 0.066 0.178 ¦ 70116 ¦ 0.130 ¦ Niagara Falls ¦ 14303 ¦ 0.311 Portland ¦ Amarillo ¦ 79111 ¦ 0.166 ¦ ¦ San Francisco ¦ 94114 ¦ 1.50 53714 ¦ Shreveport Des Moines ¦ 71106 ¦ 0.165 ¦ Rochester ¦ 14619 ¦ 0.248 Salem ¦ Austin ¦ 78703 ¦ 0.088 ¦ ¦ San Jose ¦ 95139 ¦ 2.05 64801 ¦ Massachusetts ¦ ¦ ¦ Schenectady ¦ 12304 ¦ 0.278 ¦ Beaumont Idaho 18104 ¦ 77705 ¦ 0.116 ¦ ¦ Colorado ¦ ¦ ¦ Boston ¦ 02127 ¦ 0.325 0.149 ¦ Syracuse ¦ 13219 ¦ 0.192 ¦ Corpus Christi Boise 18015 ¦ 78418 ¦ 0.093 ¦ ¦ Colorado Springs ¦ 80913 ¦ 0.178 0.344 ¦ Lawrence ¦ 01843 ¦ 0.376 ¦ Utica ¦ 13501 ¦ 0.250 1.04 ¦ Dallas ¦ 75233 ¦ 0.117 0.133 0.207 ¦ ¦ Denver ¦ 80239 ¦ 0.187 ¦ Lowell ¦ 01851 ¦ 0.355 ¦ North Carolina ¦ Missouri ¦ ¦ El Paso ¦ 79932 0.164 ¦ 0.358 0.114 ¦ ¦ Connecticut ¦ ¦ ¦ New Bedford Bethlehem 0.055 ¦ 02740 ¦ 0.261 ¦ Charlotte ¦ 28216 97301 ¦ 0.345 0.929 ¦ Ft. Worth 61605 Erie ¦ 76119 ¦ 0.110 ¦ ¦ Bridgeport ¦ 06606 ¦ 0.332 0.553 ¦ Springfield Joplin ¦ 01107 65109 ¦ 0.260 ¦ Greensboro Pennsylvania ¦ 27410 ¦ 0.255 Milwaukee ¦ Houston Madison ¦ 77044 53221 ¦ 0.107 0.138 0.120 ¦ ¦ Hartford Chicago ¦ 06120 60620 ¦ 0.274 0.190 ¦ Worchester ¦ 01602 ¦ 0.271 64108 ¦ Raleigh Allentown ¦ 27610 0.289 ¦ 0.211 Racine ¦ Lubbock ¦ 79424 ¦ 0.099 0.122 0.124 ¦ ¦ New Haven ¦ 06511 61265 ¦ 0.285 Kansas City 0.135 ¦ Maryland ¦ ¦ ¦ Winston-Salem ¦ 27106 0.304 ¦ 0.281 Superior ¦ San Antonio Moline ¦ 78235 53402 ¦ 0.133 0.120 ¦ ¦ Waterbury ¦ 06702 ¦ 0.287 ¦ Baltimore ¦ 21218 ¦ 0.199 65801 64501 ¦ North Dakota ¦ ¦ ¦ Waco ¦ 76704 54880 ¦ 0.095 Jefferson City 0.120 ¦ ¦ Florida Peoria ¦ ¦ ¦ Maine ¦ ¦ ¦ Fargo ¦ 58103 16511 ¦ 0.073 West Virginia ¦ Utah ¦ ¦ ¦ ¦ Ft. Lauderdale ¦ 33328 ¦ 0.070 ¦ Augusta ¦ 04330 ¦ 0.318 ¦ Grand Forks ¦ 58201 17111 ¦ 0.054 0.224 Charleston ¦ Salt Lake City ¦ 84111 25303 0.232 ¦ 1.79 0.206 ¦ ¦ Jacksonville Rock Island ¦ 32222 ¦ 0.142 0.174 0.131 ¦ Portland ¦ 04101 63166 ¦ 0.369 0.586 ¦ Ohio Harrisburg ¦ ¦ ¦ Virginia ¦ ¦ ¦ ¦ Miami ¦ 33133 61201 ¦ 0.061 83705 ¦ Michigan ¦ ¦ ¦ Akron ¦ 44312 ¦ 0.179 0.326 ¦ Norfolk Huntington ¦ 23504 ¦ 0.132 ¦ ¦ St. Petersburg Rockford ¦ 33709 61108 ¦ 0.078 0.183 ¦ Detroit ¦ 48207 ¦ 0.123 ¦ Canton Philadelphia ¦ 44702 19125 ¦ 0.316 ¦ Richmond ¦ 23233 25704 ¦ 0.300 0.221 ¦ ¦ Tampa Springfield ¦ 33635 62703 ¦ 0.083 0.263 ¦ Flint Jackson ¦ 48506 39211 ¦ 0.091 0.191 ¦ Cincinnati Pittsburgh ¦ 45245 15235 Indiana ¦ 0.191 0.129 ¦ Roanoke Wyoming ¦ 24017 ¦ 0.290 ¦ ¦ Georgia ¦ ¦ ¦ Grand Rapids Montana ¦ 49503 ¦ 0.087 ¦ Cleveland Reading ¦ 44130 19610 ¦ 0.197 ¦ Vermont Casper 82601 ¦ ¦ ¦ ¦ Atlanta ¦ 30314 ¦ 0.258 ¦ Kalamazoo ¦ 49001 ¦ 0.116 ¦ Columbus ¦ 43217 ¦ 0.164 ¦ Burlington ¦ 05401 ¦ 0.446 0.341 ¦ ¦ Augusta ¦ 30904 ¦ 0.419 ¦ Lansing ¦ 48910 ¦ 0.109 0.134 ¦ Dayton Scranton ¦ 45440 18504 ¦ 0.206 Cheyenne ¦ Washington ¦ 82001 ¦ ¦ ¦ Columbia ¦ 31907 47712 ¦ 0.169 0.754 ¦ Minnesota ¦ ¦ ¦ Springfield ¦ 45502 ¦ 0.216 ¦ Seattle ¦ 98108 ¦ 1.51 ¦ ¦ Savannah ¦ 31404 ¦ 0.402 ¦ Duluth Billings ¦ 55803 59101 ¦ 0.056 ¦ Toledo ¦ 43608 ¦ 0.171 ¦ Spokane Oregon ¦ 99201 ¦ 0.315 ¦ ¦ Iowa ¦ ¦ ¦ Minneapolis Kenosha ¦ 55422 ¦ 0.057 ¦ Youngstown ¦ 44515 ¦ 0.163 ¦ Tacoma ¦ 98402 ¦ 1.23 ¦ ¦ Council Bluffs Davenport ¦ 41011 52803 ¦ 0.186 0.130 0.073 ¦ Rochester St. Paul ¦ 55901 55111 83201 ¦ 0.055 0.056 ¦ Oklahoma Oklahoma City ¦ 73145 74120 ¦ 0.339 ¦ Washington, D.C. Washington ¦ 20002 ¦ 0.178 ¦ *Nominal values based on ZIP codes. See www.usgs.gov for calculator to check actual Ss using latitude and longitude for best results. Once the overall seismic forces Fp and Fpy have been determined (as indicated in the previous section or per the local code requirement), the loads at the restraint points can be determined. There are many different valid methods that can be used to determine these loads, but this section suggests a couple of simple approaches. Under some instances (particularly those relating to life-support issues in hospital settings), newer code requirements indicate that critical equipment must be seismically qualified to ensure its con- tinued operation during and after a seismic event. Special care must be taken in these situations to ensure that equipment has been shaker Inc. ASHRAE, 2019 user. single for Licensed | {}
647a074a-3a4f-4de4-9d2b-99c71b02c4b0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Seismic- and Wind-Resistant Design 56.5 Table 5 Ss Numbers for Selected International Locations (U.S. COE 1998) ¦ Country City ¦ Ss Country ¦ City Ss Country City ¦ Ss Country ¦ City S s ¦ ¦ ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Africa Algeria Alger · 1.24 Oran -- 1.24 Angola. Luanda ... 0.06 Benin Colonou -- 0.06 Botswana. Gaborone · 0.06 Burkina Faso Ougadougou ·· · 0.06 Burundi Bujumbura · ·· 1.24 Cameroon. Douala. ··· 0.06 Y aounde ·· 0.06 Cape Verde Praia + 0.06 Central African Republic IT Bangui. 4 0.06 Chad · 0.06 ¦ Tsingtao. 1.24 Wuhan 0.62 Cyprus Nicosia 1.24 India Bombay 1.24 Calcutta 0.62 -- 1.65 1.65 Iran ¦ Haiti Jamaica Kingston Leeward Islands. All +- 1.24 Puerto Rico -- All 0.83 Trinidad ¦ Port au Prince ++ 1.24 1.24 ¦ Serbia Belgrade. 0.62 Barcelona 0.62 Bilbao 0.62 Madrid · 0.06 Rota 0.62 Seville. · 0.62 Goteborg · 0.62 Stockholm. ++ 0.31 Bern ¦ ¦ ¦ ¦ ¦ Indonesia ¦ ¦ Spain. Sweden Switzerland. Ukraine ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 0.62 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ + - 1.24 Belmopan ... 0.62 0.62 1.24 Salvador -- - ... 1.65 Guatemala. ... 1.65 Tegucigalpa ·· 1.24 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Madras. 0.31 New Delhi 1.24 Bandung Jakarta -- Medan ···· 1.24 ··· 1.65 ···· 1.24 ¦ & Tobago All Central America Belize Canal Zone All ··· Costa Rica San Jose ... El Salvador San Guatemala Honduras. Mexico ¦ ¦ ·· Geneva ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Surabaya Isfahan Shiraz ... 1.24 Tabriz + - · 1.65 Tehran 4 1.65 ¦ Ciudad Juarez · 0.62 Guadalajara. ·· -- 1.24 Hermosillo ¦ ¦ -++ 0.31 Zurich at · 0.62 Kiev ... 0.06 Kingdom. Belfast. - -+ · 0.06 Edinburgh E 0.31 Glasgow/Renfrew 0.31 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Iraq Y ¦ Baghdad 1.24 0.31 1.65 Amman 1.24 Kimhae 0.31 ¦ -++ 1.24 Matamoros · + 0.06 Mazatlan · 0.60 0.06 ¦ United ¦ Hamilton ·· 0.31 Liverpool it ... 0.31 -- 0.62 ¦ ¦ Ndjamena. Congo Brazaville. -- 0.06 Djibouti Djibouti. ···· 1.24 -- 0.62 0.62 ¦ Basra Haifa. ··· · 1.24 Jerusalem. ···· · 1.24 Tel Aviv · -+ ···· 1.24 Fukuoka. ··· 1.24 AFB 1.24 1.24 Y 1.65 ¦ Merida - ·· Mexico City ¦ North ¦ ¦ ¦ ¦ ¦ Egypt Alexandria Cairo - ¦ Israel Itazuke Misawa AFB ···· 1.24 Naha, Okinawa. .... 1.65 Osaka/Kobe ·· 1.65 Sapporo to · 1.24 Tokyo ···· 1.65 Wakkanai ¦ ¦ ¦ London. -+ · Londonderry · ······ 0.31 Thurso i 0.31 ¦ ¦ ¦ ¦ Port Said - ·· + 0.62 Equatorial Guinea ... ¦ Japan. ¦ ¦ ¦ America All 0.31 NAS 0.62 ¦ ¦ ¦ ¦ Malabo · 0.06 Ethiopia Addis Ababa 1.24 ¦ ¦ ¦ ... 1.24 Monterrey 0.06 ¦ ¦ ¦ ¦ ¦ ·· Asmara ·· 1.24 Gabon Libreville · 0.06 Gambia. Banjul ·· 0.06 Ghana Accra.. -- 1.24 Guinea Bissau · 0.31 Conakry 0.06 Ivory Coast. Abidijan · 0.06 Kenya Nairobi ... 0.62 Lesotho. Maseru +- - 0.62 Liberia Monrovia · 0.31 Libya Tripoli 0.62 Wheelus AFB · 0.62 Madagascar Tananarive · 0.06 Malawi Blantyre .... 1.24 Lilongwe .... 1.24 Zomba .... 1.24 ¦ ¦ ¦ - Nuevo Laredo 0.06 Tijuana. 1.24 ¦ Argentia 0.31 ¦ ¦ ¦ ¦ ¦ ¦ Nicaragua ¦ Managua -- 1.65 ¦ Greenland Canada AB ¦ ¦ ¦ ¦ ¦ ¦ Panama. ¦ Colon ·· -- 1.24 Galeta 0.83 ¦ Churchill, MB 0.06 Cold Lake, AB 0.31 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Calgary, ¦ ¦ ¦ ¦ ¦ ¦ Europe ¦ - 1.24 ¦ Edmonton, AB 0.31 E. Harmon, AFB 0.62 ON 0.06 0.06 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Fort Williams, Frobisher, NT Goose Airport 0.31 ¦ ¦ ¦ ¦ ¦ ¦ Albania. ¦ Tirana Salzburg -- 0.62 ¦ ¦ ¦ ¦ ¦ ¦ ···· ¦ Austria ¦ ¦ Halifax, NS 0.31 Montreal, QC 1.24 Ottawa, ON 0.62 St. John 's, NL 1.24 ¦ ¦ ¦ ¦ ¦ Jordan ¦ Belgium ¦ · 0.62 0.31 ¦ ¦ ¦ ¦ ¦ ¦ okohama +- okota. Korea Kwangju 0.31 ¦ Bulgaria ¦ Vienna Antwerp -- Brussels · 0.62 Sofia ¦ ¦ ¦ ¦ ¦ ¦ Pusan 0.31 Seoul 0.06 Kuwait Kuwait. 0.31 Laos 0.31 ¦ Croatia ¦ ... --- 1.24 Zagreb. .... 1.24 ¦ ON. 0.31 ¦ ¦ ¦ ¦ ¦ Lebanon ¦ Republic.. ¦ Bratislava ++ 0.62 Prague...... Copenhagen ¦ Toronto, BC 1.24 ¦ ¦ ¦ ¦ ¦ - Vientiane Beirut. 1.24 Malaysia ¦ Czech Denmark Finland ¦ -- 0.31 + - 0.31 Helsinki ¦ South Argentina Brazil ¦ ¦ ¦ ¦ ¦ ¦ ¦ 0.31 Bordeaux 0.62 Lyon ++ 0.31 1.24 Nice 0.62 ¦ Vancouver, America ¦ ¦ ¦ ¦ 0.31 0.62 ¦ Kuala Lumpur --- 0.31 Myanmar Mandalay. Rangoon · E Nepal Kathmandu 1.65 Oman Muscat 0.62 Pakistan Islamabad ▲ + - Karachi 1.65 ¦ Germany ¦ 1 ·· Marseille -++ .... 1.24 Strasbourg. .. 0.06 ¦ Winnipeg, MB 0.31 Buenos Aires ·· 0.25 Belem. i 0.06 Belo Horizonte .... 0.06 Brasilia. · 0.06 Manaus ...... 0.06 Porto Alegre +- 0.06 ¦ ¦ ¦ ¦ 1.24 ¦ 0.06 0.06 ¦ France 1.24 + - 1.24 1.68 ¦ Berlin ·· Bonn -- 0.62 ¦ -- -++ Recife. ¦ ¦ ¦ ¦ ¦ ¦ ¦ Bremen 1 분 0.06 ¦ Bolivia ¦ ¦ ¦ ¦ ¦ 0.62 Lahore 0.62 Peshawar + - Qatar ¦ Frankfurt. ¦ ¦ 0.06 Rio de Janeiro ··· 0.06 Salvador. 0.06 Paulo ·· ¦ ¦ ¦ ¦ ¦ ¦ ¦ Dusseldorf · 0.31 Hamburg ¦ Paz ·· ¦ ¦ ¦ ¦ ¦ Doha 0.06 Saudi Arabia AI Badi 0.31 0.06 Dhahran. 0.31 ¦ ¦ ¦ Sao La Santa ¦ ¦ ¦ ¦ ¦ Jiddah 0.62 ¦ 1.65 ¦ 0.62 0.06 Munich 0.31 Stuttgart 0.62 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ 0.62 ¦ Cruz ... ¦ ¦ ¦ ¦ ¦ Khamis 0.31 ¦ ¦ ¦ Santiago .... ¦ ¦ ¦ ¦ Mali Bamako ·· 0.06 Mauritania Nouakchott E Mauritius Port Louis E Morocco Casablanca 0.62 Port Lyautey 4 Rabat. L Tangier ·· Mozambique Maputo. L Niger Niamey 0.06 Nigeria Ibadan E 0.06 Kaduna. 0.06 0.31 Lagos · 1.24 Rwanda Kigali L Senegal. Dakar 0.06 ¦ 1.24 ¦ ¦ Athens. ¦ ¦ ¦ ¦ ¦ 0.31 ¦ Mushayt.. Riyadh ···· 0.06 All 0.31 South Y emen Aden City 1.24 ¦ Vaihingen Greece ¦ 1.24 ¦ Chile Valparaiso ¦ ¦ ¦ ¦ Seychelles Victoria 0.06 ¦ Singapore. ¦ ¦ ¦ · Bogota · .... Quito ....... .... ¦ ¦ ¦ ¦ 1.65 Sierra Leone Freetown - 0.06 Mogadishu · ¦ ¦ ¦ ... -- ¦ ¦ ¦ ¦ ¦ -++ 1.65 0.06 Africa Cape ¦ ¦ 0.06 1.24 ¦ Kavalla Makri .... Bay. - .. ¦ Colombia Ecuador Paraquay ¦ ¦ ¦ ¦ 1.24 Somalia Town. ... ¦ Sri Lanka Colombo. Syria Aleppo. ··· Damascus .... ¦ ¦ Rhodes 1.24 Sauda Budapest 0.62 ¦ 1.65 ···· 1.24 ¦ ¦ ¦ ¦ South 1.24 Durban .... ¦ Taiwan ¦ 1.24 Thessaloniki ¦ 1.65 1.65 ¦ ·· ¦ ¦ ¦ ¦ 0.62 Johannesburg -- 0.62 1.65 Natal ¦ All 1.65 Thailand Bangkok i ¦ Hungary ¦ ¦ Asuncion. 0.06 Lima. ... ···· ¦ ¦ ¦ ¦ +- 0.31 1.65 Pretoria .... ¦ 0.62 ¦ · Iceland ¦ Keflavik ·· 1. ¦ Guayaquil 1.65 1.65 Peru Piura. ¦ ¦ ¦ ¦ ¦ 0.31 ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ ¦ Inc. ASHRAE, 2019 user. single for Licensed | {}
f3006855-e53c-4928-8253-eb11794efeb3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 56.6 Table 6 Load Combinations (Equation Numbers as Referenced in IBC) 2019 ASHRAE Handbook- -HVAC Applications (SI) ¦ ASD ¦ LRFD ¦ ¦ --- ¦ --- ¦ ¦ 5. (1.0 + 0.14SDs)D + H+F+ 0.7PQE ¦ 5.(1.2+ 0.2SDs)D + PQE + L + 0.2S ¦ ¦ 8. (0.6 + 0.14SDs)D + 0.7PQE+ H ¦ 7. (0.9 - 0.2SDs)D + PQE+ 1.6H ¦ tested or otherwise certified to meet the maximum anticipated seis- mic load. Table 6 illustrates some load combination calculations. 1.4 COMPUTATION OF LOADS AT BUILDING CONNECTION ASCE Standard 7 is based on load- and resistance-factor de- sign (LRFD). In the past, building codes have been based on allow- able stress design (ASD). Both are allowed for seismic restraint design. Load factors and load combinations that must be considered in design are defined in Chapter 2 of ASCE Standard 7. If a com- ponent is anchored with post-installed anchors, the design is usually accomplished using provisions of LRFD. The Load Combinations of Section 2.4.1 of ASCE Standard 7 must be considered in the design. Generally, for rigidly mounted components, Combination 8 is the critical combination to be con- sidered. The forces of the restraint holding the equipment in position include shear and tensile forces. It is important to determine the number of bolts that are affected by the earthquake forces. The direction of the lateral force should be evaluated in both horizontal directions, as shown in Figure 1. All bolts or as few as a single bolt may be affected. Simple Case Figure 1 shows a rigid floor-mount installation of a piece of equipment with the center of gravity at the approximate center ofthe restraint pattern. To calculate the shear force, the sum of the forces in the horizontal plane is 0 = Fp - V The equipment shown in Figure 1 has two bolts on each side, so that four bolts are in shear. Using a single-axis moment equation to calculate the tension force, the sum of the moments for overturning results in an overturning moment (OTM) and resisting moment (RM). Inc. ASHRAE, 2019 user. single for Licensed (6) For Figure 1, two bolts are in tension. See Example 1 for appli- cations of the OTM and RM. See ASCE Standard 7 for load com- binations that adjust the D (dead load) and E (earthquake load). Shear and tension forces V and T should be calculated inde- pendently for both axes, as shown in the front and side views. See the examples for complete analysis. General Case The classic method used to distribute seismic loads equally dis- tributes lateral loads among the restraints and then modifies these loads as a function of the mass eccentricity. Worst-case mass, verti- cal seismic load, and overturning components are combined to determine a maximum vertical load component. This polar method is in common use and works well for most applications. A second, lump mass method, proportions the restraint loads based on the equipment mass and distribution. When working with larger seismic forces or unstable equipment, this offers the option of more evenly distributing the seismic load, reducing anchor size and peak restraint requirements. Eccentric center of gravity (cg) loads are not required to be carried out to the corner restraints as in the polar method; this technique deemphasizes stresses in the equip- ment frame and is more suitable for nonrigid equipment types. Eccentric loads can be addressed with either the polar method or the lump mass method. ![image](/image/placeholder) Fp/3 F⌀/3 F F p p cg W h P cg W p V V I D D2 T T FRONT VIEW SIDE VIEW Fig. 1 Equipment with Rigidly Mounted Structural Bases Note: Although only two methods of computing forces for more general equipment cases are illustrated here, there are many other valid methods that can be used to distribute the restraint forces. It is important that any method used include the ability to account for equipment mass, seismic uplift forces, overturning forces, and an offset center of gravity within the equipment. Polar Method Lateral forces are equally distributed among the restraints. If the equipment's center of gravity does not coincide with its geometric center, a rotational factor is added to account for the imbalance. This factor is determined in three steps. First, compute the true chord length in the horizontal plane between the equipment's center of gravity and the restraints' geometric center. Second, multiply the equipment total seismic lateral force by this length (to obtain a rota- tional moment). Third, divide this figure by the number of moment- resisting restraints times their distance from the geometric center. (The moment-resisting restraints are those farthest and equally spaced from the geometric center.) The resulting load can then be added to the original (balanced) figure. This method transfers all imbalance loads to the corner restraints and provides a valid method ofrestraint as long as the equipment acts as a rigid body. The assump- tion that a piece of equipment can transfer these loads out to the cor- ners becomes less accurate as the equipment becomes less rigid. Calculation of the tensile/compressive forces at the restraints is more complex than that for determining the shear loads, and must include mass, vertical seismic force, overturning forces, and (ifiso- lated) the type ofisolator/restraint system used. The total tensile and compressive forces are the worst-case summation of each of these components. For clarity, each component is addressed here as a sep- arate entity. The nominal mass component at each restraint is simply the total operating mass divided by the number of restraints. The vertical seis- mic force is simply the mass component at each location multiplied by the vertical seismic force factor in terms of the total Fpv ex- load pressed in gs, the gravitational constant (Fpv/ Wp, where Fpv is the vertical seismic load component as defined by the code and Wp is the total operating mass of the equipment). This can be directed either upward or downward when summing forces. Lump Mass Method In the lump mass method, the total equipment mass is distributed among the restraints in a manner that reflects the equipment's actual mass distribution. There are many methods of determining the dis- tribution analytically or by testing, although they are not addressed in this section. Frequently, a mass distribution can be obtained from the equipment manufacturer. Once the static point loads are obtained or computed for each re- straint location, they can be multiplied by the lateral seismic accel- eration factor (Fp / Wp) to determine lateral forces at each restraint then point. Thus, if the mass at each restraint point is Ww | {}
14c8af0d-3b47-457e-ad3d-d33dfd755340 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Seismic- and Wind-Resistant Design 56.7 Veff = (Fp /Wp)Wn (7) This method considers the loads at all the restraints individually and computes the overturning forces for each in 1° increments for a full 360° of possible seismic wave front angle; it is only practical to perform using a spreadsheet. The total lateral seismic force Fp is divided into x- and y-axis components for each possible wave front approach angle. These forces are multiplied by the height of the equipment center of gravity above the point of restraint heg The resulting moments are then resolved into forces at each restraint based on the x- and y-axis moment arms associated with the partic- ular restraint location and the proportion of the load thatit will bear. Resilient Support Factors If the equipment being restrained is isolated, the following three factors must be considered: · For all forces that are not directed along the principal axes, only the corner restraints can be considered to be effective. Thus, for either distribution method, only the corner restraints can be con- sidered capable of absorbing vertical loads. · Ifthe restraints are independent (separate entities) from the spring isolation elements and if, when exposed to uplift loads, vertical spring forces are not absorbed within the housing of an integral isolator/restraint assembly, the mass factor determined in the first step of the vertical load analysis should be ignored. (This is because any effect that a mass reduction has on the attachment hardware forces is replaced by an approximately equal vertical force component from the spring.) · If the gap in the restraint element exceeds 6 mm, the final com- puted forces must be doubled per the IBC. Building Attachment The common attachment arrangements are directly bolting with steel bolts and lag bolts, welding, or anchoring to concrete using post-installed anchors. To evaluate the combined effective tensile and shear forces that act simultaneously on these connections, a sep- arate analysis is required. If allowable stress design (ASD) data are used to size hardware for through-bolted connections for the IBC codes, which are strength based, the loads may be reduced by a factor of 1.4. IfLRFD is used when selecting for the hardware, the 1.4 factor does not apply. All allowable capacities used for concrete post-installed anchor bolts selection should be drawn from ICC-ES test reports. These values reflect test data on a single anchor and should be der- ated for applications where embedment, edge distances, spacing, or location vary from the test conditions. Anchor manufacturers may have selection software to determine anchor bolt capacities that con- sider installation conditions. It should also be noted that the values published in ES reports may be either ASD or LRFD values and may need to be converted for compatibility with the (LRFD) IBC code being used. 1.5 ANSI STEEL BOLTS For direct attachment with through bolts using ASD criteria, the design capacity of the attachment hardware should be based on cri- teria established in the American Institute of Steel Construction (AISC) manual. Based on the use of A307 bolts, the basic formula for computing allowable tensile stress when shear stresses are pres- ent is Tallow - 1.8Sv = 179 where Sv is the shear stress in the bolt in megapascals. Tallow, the maximum allowable tensile stress, must not exceed 138 MPa. However, because these stresses are appropriate for dead- plus live-load combinations, they can be appropriately inflated by 1.33 when allowable stress design provisions are used and when they are used to resist wind and seismic loads as well. Peak bolt loads are based on the maximum permitted stress multiplied by the nominal bolt area. 1.6 LAG SCREWS INTO TIMBER Acceptable loads for lag screws into timber can be obtained from the National Design Specification� (NDSⓇ) for Wood Con- struction (A WC 2005). Selected fasteners must be secured to solid lumber, not to plywood or other similar material. Withdrawal force design values are a function of the screw size, penetration depth, and wood density and can be increased by a factor of 1.6 for short-term seismic or wind loads. Table 9.2A in the NDS identifies withdrawal forces on a force/embedment depth basis. Note that the values published in this table are capacities in both ASD and LRFD. In addition, NDS Table 9.4.2 introduces deration factors for reduced edge distance and bolt spacing. In timber construction, the interaction formula given in Equation (8) does not apply. Instead, per Section 9.3.5 of the NDS, the equa- tion is Za' = (W'p)Z*/[(W"p)cos2a + Z'sin2�] where (9) Z' = shear capacity drawn from Table 9.3A W = side grain withdrawal force = 1800G3/2D3/4 G = specific gravity of the timber D = diameter p = embedment depth of screw 0 = angle of composite force measured flat with surface of timber 1.7 CONCRETEPOST-INSTALLED ANCHOR BOLTS ASD Applications Capacities are manufacturer/anchor-type specific. Capacity data should be obtained from the anchor's current ES report. Where fail- ure of the steel does not govern the tensile load, strength-based de- sign (LRFD) should be used. Obtain anchor information from the anchor ICC-ES (formerly ICBO-ESR) report based on anchor and installation factors. For groups of anchors, special factors are re- quired and American Concrete Institute Standard 318-08 should be consulted. Interaction Formula. To evaluate the combined effective ten- sion and shear forces that act simultaneously on the bolt, use the either of the following equations: (Teff/Tallow ASD)5/3 + (V eff ASD) 5/3 ≤ 1.0 / Vallow or (Teff/T allow ASD) + (Veff/V allow ASD) ≤ 1.2 However, if Te⌀ ASD eff can equal Tallow ASD' ≤0.2; Tallow the full T the full V can equal Vallow ASD· ≤ 0.2; V allow ASD eff or if Veff LRFD Applications The engineer must select an anchor for use from a current eval- uation report for anchors that satisfy provisions of ACI 318 Appen- dix D or ACI 355 (the provisions are the same). From ACI 318, the capacity of the anchor must be reduced in accordance with the fol- lowing: (8) T= 0.75⌀N V = 0.75⌀V (11) Inc. ASHRAE, 2019 user. single for Licensed The interaction equation for LFRD is modified as follows: (12) (10) (13) | {}
b5682235-9646-4624-bc48-616609f23f28 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 56.8 2019 ASHRAE Handbook-HVAC Applications (SI) (Teff /Tallow) + (Veff IVallow) ≤ 1.2 (14) Types of Concrete Post-Installed Anchors Several types of anchor bolts for insertion in concrete are manu- factured. W edge and undercut anchors perform better than self- drilling, sleeve, or drop-in types. Adhesive anchors are stronger than other anchors, but lose their strength at elevated temperatures (e.g., on rooftops and in areas damaged by fire). w edge anchors have a wedge on the end with a small clip around the wedge. After a hole is drilled, the bolt is inserted and the external nut tightened. The wedge expands the small clip, which bites into the concrete. Undercut anchors expand to seat against a shoulder cut in the bottom of the anchor hole. Although these have the highest capacity of commonly available anchor types, the cost of the extra operation to cut the shoulder in the hole greatly limits the frequency of their use in the field. A self-drilling anchor is basically a hollow drill bit. The anchor is used to drill the hole and is then removed. A wedge is then inserted on the end of the anchor, and the assembly is drilled back into place; the drill twists the assembly fully in place. The self- drilling anchor is heavily affected by the skill of the craft and usu- ally not rated for seismic applications. Drop-in expansion anchors are hollow cylinders with a tapered end. After they are inserted in a hole, a small rod is driven through the hollow portion, expanding the tapered end. These anchors are only for shallow installations because they have no reserve expan- sion capacity. These anchors are usually not rated for seismic appli- cations. A sleeve anchor is a bolt covered by a threaded, thin-wall, split tube. As the bolt is tightened, the thin wall expands. Additional load tends to further expand the thin wall. The bolt must be properly pre- loaded or friction force will not develop the required holding force. These anchors are typically not used in seismic applications because of the limited reserve capacity. Large screw anchors are one-piece anchors that have a concrete cutting thread. These anchors were initially designed to be installed without a specified torque, but torque is used to ensure contact at the rated embedment Inc. ASHRAE, 2019 user. single for Licensed Adhesive anchors may be in glass capsules or installed with var- ious tools. Pure epoxy, polyester, or vinyl ester resin adhesives are used with a threaded rod supplied by the contractor or the adhesive manufacturer. Some adhesives have a problem with shrinkage; oth- ers are degraded by heat. However, some adhesives have been tested without protection to 590°C before they fail (all mechanical anchors will fail at this temperature). Where required, or if there is a con- cern, anchors should be protected with fire retardants similar to those applied to steel decks in high-rise buildings. The manufacturer's instructions for installing the anchor bolts should be followed. ES reports have further information on allow- able forces for design. Use a safety factor of 2 or as required by ES reports if the installation has not been inspected as required by the IBC Chapter 17 on special inspection. Stainless steel anchors are required for use in outdoor applica- tions noted in the latest versions of the IBC code. 1.8 WELD CAP ACITIES Weld capacities may be calculated to determine the size of welds needed to attach equipment to a steel plate or to evaluate raised sup- port legs and attachments. A static analysis provides the effective tension and shear forces. The capacity of a weld is given per unit length of weld based on the shear strength of the weld material. For steel welds, the allowable shear strength capacity is110 MPa on the throat section of the weld. The section length is 0.707 times the specified weld size. For a 1.5 mm weld, the length of shear in the weld is 0.707 x 1.5 mm. The allowable weld force (Fw)allow for a 1.5 mm weld is (Fw)allow = 1.06 x 110 = 117 N per millimetre of weld (15) For a 3 mm weld, the capacity is 233 N. The effective weld force is the sum of the vectors calculated in terms of effective shear and tension shall be reduced. Because the vectors are perpendicular, they are added by the method of the square root of the sum of the squares (SRSS), or 2 2 (Fw)eff= ( T + ( V eff) eff) (16) The length of weld required is given by the following equation: Weld length = (Fw)eff/(Fw), allow (17) 1.9 SEISMIC SNUBBERS Several types of snubbers are manufactured or field fabricated. All snubber assemblies should meet the following minimum re- quirements to avoid imparting excessive accelerations to HV AC&R equipment: · Impact surface should have a high-quality elastomeric surface that is not cemented in place. · Resilient material should be easy to inspect for damage and be replaceable. · Snubber system must provide restraint in all directions. · Snubber capacity should be verified either through test or by anal- ysis and should be certified by an independent, registered engi- neer to avoid serious design flaws. Typical snubbers are classified as Types A through J (Figure 2). Type A. Snubber built into a resilient mounting. All-directional, molded bridge-bearing quality neoprene element is a minimum of 3.2 mm thick. Type B. Isolator/restraint. Stable isolation spring bears on the base plate of the fixed restraining member. Earthquake motion of isolated equipment is restrained close to the base plate, minimizing pullout force to the base plate anchorage. Type C. Spring isolator with built-in all-directional restraints. Restraints have molded neoprene elements with a minimum thick- ness of 3 .2 mm. A neoprene sound pad should be installed between the spring and base plate. Sound pads below the base plate are not recommended for seismic installations. Type D. Integral all-directional snubber/restrained spring isola- tor with neoprene element. Type E. Fully bonded neoprene mount capable of withstanding seismic loads in all directions with no metal-to-metal contact. Type F. All-directional three-axis snubber with neoprene element. The neoprene element of bridge-bearing quality is a minimum of 4.8 mm thick. Snubber must have a minimum of two anchor bolt holes. Type G. Lateral snubber. Neoprene element is a minimum of 6.4 mm thick. Upper bracket is welded to the equipment. Type H. Restraint for floor-mounted equipment consisting of interlocking steel assemblies lined with resilient elastomer. Bolted to equipment and anchored to structure through slotted holes to allow field adjustment. After final adjustment, weld anchor to floor bracket and weld angle clip to equipment or, alternatively, fill slots with adhesive grout to prevent slip. Type I. Single-axis, single-direction lateral snubber. Neoprene element is a minimum of 6.4 mm thick. Minimum floor mounting is with two anchor bolts. Must be used with a minimum of eight, two per corner. Type J. A telescopic snubber for floor-mounted equipment, with a molded neoprene element, designed to distribute the seismic force to a larger surface area in a pipe section. This snubber is an | {}
6dc6b8d7-9bbf-4a6e-9a5c-e1d0ff30f0e5 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Seismic- and Wind-Resistant Design 56.9 ![image](/image/placeholder) TYPE D TYPE C TYPE B TYPEA ![image](/image/placeholder) TYPE E ![image](/image/placeholder) TYPE F ![image](/image/placeholder) TYPE G ![image](/image/placeholder) TYPE H TYPE I Fig. 2 Seismic Snubbers ![image](/image/placeholder) TYPE J all-directional restraint system when a minimum of four snubbers are installed. The molded neoprene element is a minimum of 6.3 mm thick and is installed with an air gap of 4.8 mm not to exceed 6.3 mm. 1.10 SEISMIC RESTRAINTS For suspended equipment, pipes, ducts, and raceways, itis neces- sary to restrain lateral movement resulting from seismic acceleration applied to the component. Unrestrained, suspended equipment and related systems will sway violently back and forth, impacting nearby building material and possibly overstressing the hanger rods. The overstressed rods will eventually break and the equipment crash down. To prevent this swaying, suspended components are restrained by one of two methods: a wire rope system, or a rigid brace using steel struts, angles, or other steel elements. Wire rope restraints are a restraint assembly for suspended equipment, piping, or ductwork consisting of high-strength, galva- nized steel aircraft cable. A typical cable restraint system is shown in Figure 3. Cable should have a certified break strength. Some models are color-coded for easy field verification. Cable must be manufactured to meet or exceed minimum materials and standard requirements. Break strengths must be per ASTM E-8 procedures. A safety factor of 2 may be used when prestretched cable is used with end connections designed to meet the cable break strength. Cables are installed to prevent excessive seismic motion and arranged so they do not engage during normal operation. Equipment suspended with vibration isolators must use cable restraints to avoid degrading the isolation. Rigid type bracing will short out the vibra- tion isolators. To prevent buckling ofthe hanger rods, add a rod stiff- ener as shown in Figure 4. · Factory-installed permanent stake eye · Field-looped through bracket and secured with cable grips · Field-looped through bracket and secured with oval sleeve · Factory brackets with integral cable clamps to secure cable Secure the cable to structure and to the braced component through a bracket or stake eye designed to meet the cable restraint rated capacity. Cables are typically secured using one of the follow- ing methods: Inc. ASHRAE, 2019 Ⓒ user. single for Licensed | {}
5e65f748-465d-46d7-9ac5-17f308576823 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 56.10 When cables are looped through a field-supplied bracket or sup- port hole, a cable thimble should be used to protect the cable. Many factory-supplied brackets are designed specifically for allowing a looped cable through without a thimble. See the manufacturer's instructions for details. Figure 5 shows typical cable restraint details with various attachment methods. Typical attachment methods to secure the rigid brace to the structure and component are shown in Figure 6. 1.11 RESTRAINT OF PIPE AND DUCT RISERS When piping and ductwork run vertically through a structure, they are identified as risers. They are subject to the same seismic and (less commonly) wind forces as are piping and ductwork oriented horizontally. The primary difference is that the forces that act along the axis of the riser are the summation of the vertical seismic forces 2019 ASHRAE Handbook- - HVAC Applications (SI) and gravity loads, whereas on horizontal systems, the axial forces are simply the horizontal seismic or wind force. It is also important to recognize, when providing restraint, that risers of any significant length and variation in temperature require support that allows thermally driven changes in the riser's overall length to be accommodated. Because the vertical seismic and wind forces are small compared to gravity forces, axial restraint for the riser can normally be provided with only minor increases in the size of the specialized components used to support the system. Because of the potential of damage to the restraint or support systems as the system grows or shrinks, it is not recommended that redundant axial restraint systems be fitted to a riser. Instead, the primary sup- port system should be designed or selected to meet the job require- ment. ![image](/image/placeholder) THREADED ROD OUTLINE OF SEISMIC CABLE QUANTITY LOCKING BOLT AND ORIENTATION PER CONTRACT DOCUMENTS NUMBER OF SEISMIC ROD CLAMPS PER MANUFACTURER'S ANGLE STIFFENER INSTRUCTIONS UNIT PLAN VIEW ANGLE OF CABLE SHALL BE 45° ± 15° CABLE REINFORCED ROD UNIT SIDE VIEW 0 STRUT STIFFENER PREINSTALLED ANGLED VIEW BRACKETS OR EQUIPMENT SUPPORT FRAMING Fig. 3 Cable Restraint Fig. 4 Rod Stiffener 0000 0000 CABLE CLAMP BOLT 5 of Connections Fig. Types Cable Inc. ASHRAE, 2019 user. single for Licensed | {}
31ef6039-8ae9-458f-b1c8-6b46afc7e3c8 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Seismic- and Wind-Resistant Design 56.11 ![image](/image/placeholder) STEEL BOLTS WITH WASHERS STEEL BOLTS WITH WASHERS STRUCTURAL WELDING LUG OPTIMUM 45° ANGLE ±15° STEEL ANGLE BRACE OPTIMUM 45° ANGLE ±15° STEEL ANGLE BRACE Fig. 6 Strut End Connections Risers of significant length are also fitted with some type of sta- bilization devices. These can be as simple as snug-fitting holes in the floors that the risers penetrate, to specialized brackets or guiding devices that maintain the alignment of the piping or duct while still allowing it to expand or contract. As is the case with the vertical forces, the components used for guidance can frequently be used to provide resistance against seismic or wind events if they are sized and attached appropriately. If, in the lateral load case, the components used to provide guid- ance are not adequate to resist the design seismic or wind load conditions, redundant, seismically qualified systems should be fit- ted to perform this task. All axial and lateral restraints fitted to risers must be effective against forces that may act in any horizontal or vertical direction as applicable. In addition, the attachment hardware used must be seis- mically qualified components (e.g., anchors), installed in accor- dance with seismically qualified procedures. 1.12 EXAMPLES The following examples are provided to assist in the design of equipment anchorage to resist seismic forces. For Examples 1 through 4, assume the provisions contained in ASCE 7-05 apply, Ip = 1.5, Ss = 0.85, site soil class is C, and the equipment is located at the top ofa 50 m building. Also include an uplift force component F = 0.2Sps D where D is the dead load for all examples. Examples pv 1 through 5 are solved using the polar method of analysis while Example 6 is solved by the lump mass method. Note: These examples assume that Ip = 1.5. This assumes that the equipment being considered is essential to the continued func- tion of the building following an earthquake or contains hazardous materials. ASCE 7-05 Section 13.2.2 requires that this equipment be certified as being operable after the design earthquake. Example 1. Anchorage design for equipment rigidly mounted to the struc- ture (see Figure 7). From Equations (1) to (4), calculate the lateral seismic force and its vertical component. Note that for post-installed, if the anchor satisfies the requirements of ASCE 7, Section 13.4.2, the value of Rp is the same as the component being considered. Post-installed anchors with current evaluation reports published by ICC or other agencies are deemed to be compliant with the provisions of ACI 355 or 318 Appendix D and thus satisfy Section 13.4.2. For rigidly mounted mechanical equipment (period < 0.06 s or > 16.7 Hz), ap from Table 2 is 1.0, otherwise ap = 2.5. ASCE 7 is based on load and resistance factor design (LRFD). In the past, building codes have been based on allowable stress design (ASD). Load factors and load combinations defined in Chapter 2 of ASCE 7 ![image](/image/placeholder) F pv PLAN d1 F cg p F P Wp og d2 h cg ANCHOR BOLT Wp d1 = 1.20 m d2 = 0.70 m = 1.00 m = 4500 N hcg Fig. 7 Equipment Rigidly Mounted to Structure (Example 1) must be considered in design. If a component is anchored with post- installed anchors, the design can only be accomplished using LRFD. The first step in the load determination process is to determine SDS using the following equation and Fa = 1.1 (from Table 3, site class C): SDS = 2FaSs/3 = 2 x 1.1 x 0.85/3 = 0.623 Using this value for SDS Equation (1) gives 0.4 x 1.0 x 0.623 x 4500 15 F 2.5 1 +2x = 2020 N P 15 1.5 Equation (2) shows that Fp need not be greater than 1.6 x 0.623 x 1.5 x 4500 = 6728 N Equation (3) shows that Fp must not be less than 0.3 x 0.623 x 1.5 x 4500 = 1262 N = 2020 N. Therefore Fp When considering provisions ofLRFD, a vertical acceleration com- ponent must be considered per ASCE 7, Section 12.4.2.2. Fpv = 0.2 x SDS x D = 0.2 x 0.623 x 4500 = 561 N For Allowable Stress Design (ASD) The load combinations of Section 2.4.1 of ASCE 7 must be consid- ered in the design. For rigidly mounted components, Combination 8 is generally the critical combination to be considered. Calculate the overturning moment OTM: OTM = Fphcg = 2020 x 1.0 = 2020 N ·m Inc. ASHRAE, 2019 user. single for Licensed (18) | {}
f8425f93-f517-4b21-b276-e91ef2818b52 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 56.12 2019 ASHRAE Handbook- - HVAC Applications (SI) Calculate the resisting moment RM: d 70 min RM = Wp = 4500 = 1575 N·m 2 2 (19) T= [2020(0.7) - 1575(0.6)]/0.70 = 670 N (20) Calculate Teff per bolt: Te⌀ = 670/2 = 335 N per through-bolt or lag screw (21) Calculate shear force per bolt: Veff= 2020/(4 x 1.4) = 361 lb per through-bolt or lag screw (22) Load and Resistance Factor Design (LRFD) The load combinations of Section 2.3.2 of ASCE 7 must be consid- ered in the design. For rigidly mounted components, Combination 7 is generally the critical combination to be considered. RM = (Wp-Fpv)dmin/2 = (4500 - 561)0.70/2 = 1379 N·m (23) Teff= [2020 - 0.9(1379)]/0.70(2) = 556 N (24) Per ASCE 7 Section 13.4.2, if post-installed anchors are used, an additional 1.3 factor is applied to all E loads. The 1.3 factor applies for projects using ASCE 7-05. This factor is not required for applications using ASCE 7-10. OTM = 2020(1.3) = 2626 N·m (25) T eff = [2626 - 1379(0.9)]/0.70(2) = 989 N (26) To convert in-lb to N·m, multiply by 0.113. Case 1. Equipment attached to a timber structure Before computing interaction forces, the computed loads must be reduced by a factor of 1.4 to make them compatible with the capacity data listed in the National Design Specification� (NDSⓇ) for Wood becomes 361/1.4 or Construction (AWC 1997). The lateral load Ve⌀ 258 N per bolt and the pullout load Te⌀ becomes 335/1.4 = 239 N per bolt. For the capacity of the connection, a resulting combined load and angle relative to the mounting surface must be computed. The com- bined load is 2 2 2 2 Ta⌀ff = N (Teff) + (Veff) = V (258) + (239) = 352 N The angle 0. = arcs in ( Teff Z', a) = 42.5°, where Za is the allowable lag screw load multiplied by applicable factors and Z'�� is the factored allowable lag screw load at angle 0. from the mounting surface. Selected fasteners must be secured to solid lumber, not to plywood or other similar material. The following calculations are made to deter- mine whether a 13 mm diameter, 100 mm long lag screw in redwood will hold the required load. For this computation, it is assumed that bolt spacing, edge distance, temperature, and other factors do not reduce the bolt capacity (see NDS for further details) and that the load allowable factor for short-term wind or seismic loads is 1.6. From Table 9.3A in the NDS, for redwood, G = 0.37, and Z perpen- dicular to the grain is 2277 N. From Table 9.2A in the NDS, for G = 0.37 and 90 mm full thread, W = 66.7 x 90 = 6003 N. Substituting into the combined load for lag bolts [Equation (9)] gives Z'a = (66.7 x 90)2277 = 3177 N 2 42.5 (66.7 x 90)42.5 + 2277 sin Therefore, a 13 mm diameter, 100 mm long lag screw can be used at each corner of the equipment. Case 2. Equipment attached to steel For equipment attached directly to a steel member, analysis is the same as that shown in case 1. Capacities for the attaching bolts are given in the Manual of Steel Construction (AISC 1989). See Chapter J of the AISC Specification for design provisions. /TASD a For this example Teff = 556/4410 = 0.126 < 0.2; therefore combined tension shear check need not be performed on the connection. Therefore, 13 mm diameter bolts can be used. Example 2. Anchorage design for equipment supported by external spring mounts (Figure 8) and attached to concrete using nonshallow post- installed anchors. A mechanical or acoustical consultant should choose the type of isolator or snubber or combination of the two. Then the product vendor should select the actual spring snubber. Using ASCE 7, the lateral force Fp must be recalculated using new factors. SDS remains as in Example 1. For expansion anchors, R p = 1.5, and for resiliently mounted mechanical equipment, ap from Table 2 is 2.5. The basic force equation is then (Note: using Rp = 1.5 is conserva- tive, because the anchors must comply with 13.4.2 of ASCE 7. The numbers could be modified) 0.4x2.5x0.623 x 4500 50 F P 1.5 1 + 2 x = 8411 N 50 1.5 Equation (2) indicates that Fp need not be greater than 1.6 x 0.623 x 1.5 x 4500 = 6728 N Equation (3) indicates that Fp must not be less than 0.3 X 0.623 x 1.5 x 4500 = 1262 N The vertical force Fpv equals Fpv= 0.2SDsD = 0.2 x 0.623 x 4500 = 561 N Because the equipment is resiliently supported, footnote b to Table 13.6-1 of ASCE 7 indicates that the computed forces may need to be doubled. Therefore, Fp is 6728 X 2 = 13.5 kN and Fpv is 561 X 2 = 1.1 kN. Assume that the center of gravity cg of the equipment coincides with the center of gravity of the isolator group. If T = maximum tension on isolator and C = maximum compression on isolator, then -Wp+ Fpv cos⌀ sin0 T, C = 土 Fphcg 2b cg 2a + Fph 4 Fphcg cose sin0 Wp+ Fpv 土 + 4 2 b a (27) To find maximum T or C, set dT/d0 = 0: ![image](/image/placeholder) F pv PLAN a F cg p 0 W h p cg b cg EXTERNAL VIBRATION ISOLATOR/SNUBBER W = 4500 N hcg = 1.00 m a = 1.20 m b = 0.70 m p Inc. ASHRAE, 2019 user. single for Licensed Fig. 8 Equipment Supported by External Spring Mounts | {}
4fe33ffc-5371-4cb2-9001-8f7a628f54f6 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Seismic- and Wind-Resistant Design dT Fphcg cose sin0 + 0 d0 2 b a 0 max tan-1(b/a) = tan-1(0.7/1.2) = 30.26° = Fphcg cos 0 sin 0 - WP + Fpv max max T = + + 4 2 b a Fphcg cos 0 sin 0 -Wp + Fpv max max C= + 4 2 b a - 4.5 + 1.12 13.5x 1 cos30.26 sin30.26 T= + + = 10.3 kN 4 2 0.7 1.2 (28) 4.5 + 1.12 13.5x 1 cos30.26 sin30.26 T = + + = -12.0 kN 4 2 0.7 1.2 (29) (30) (31) Calculate the shear force per isolator: V = (Fp/Niso) = 13 500/4 = 3375 N This shear force is applied at the operating height of the isolator. Uplift tension T on the vibration isolator is the worst condition for the design of the anchor bolts. The compression force C must be evaluated to check the adequacy of the structure to resist the loads. (32) (T1)eff per bolt = T/2 = 10 300/2 = 5150 N (33) The value of (T2)eff per bolt due to overturning on the isolator is (T2)eff = V x operating height/dNbolt (T2)eff = (3375 x 8)/(3 x2) = 4500 N where d is the distance from edge of isolator base plate to center of bolt hole. (34) (Tmax)eff = (T1)eff + (T2)eff = 5150 + 4500 = 9650 N Veff = 3375/2 = 1688 N (35) See Example 1 for the design of the connections to the structural system. (36) Anchor properties Example 3. Anchorage design for equipment with a center of gravity dif- ferent from that of the isolator group (Figure 10). (37) Ix = 4B2 Iy = 4L2 Angles: (38) Fig. 9 Spring Mount Detail (Example 2) 0 = tan-1(B/L) (39) 0. = tan-1(ex/ey) (40) B = 180 ¦�-비 (41) ![image](/image/placeholder) Tor C ANCHOR BOLT V HOLE (2) OPTIMUM 75 mm HEIGHT = 200 mm 150 mm 75 mm ▼ ELEVATION PLAN 56.13 0 = tan 1(LIx/BIy) Vertical reactions (Wn)max/min = Wp± F (43) pv (42) Vertical reaction caused by overturning moment Bh Lh cg cg Tm = ±Fp cosu + sin0 I 소 X Vertical reaction caused by eccentricity Bey Ley (Te)max/min = (Wn)max/min + I Iy Vertical reaction caused by Wp (Tw)max/min = (Wn). max/min/4 Teff Tm + (Te)max + (Tw)max (always compression) = Teff = -Tm + (Te)min + (Tw)min (tension if negative) Horizontal reactions Horizontal reaction caused by rotation 0.5 (44) 2 e2y e + Vrot = Fp 16(B2 + L ) (45) Vdir= Fp/4 V dir V = (Vrot + V dir - 2Vrot cos B)0.5 max See Example 1 for the design of the connections to the structural system. and Vmax The values of Tmin are used to design the anchorage of the isolators and/or snubbers, and Tmax is used to verify the structure's ade- quacy to resist the vertical loads. (48) (47) (46) Example 4. Anchorage design for equipment with supports and bracing for Wp suspended equipment (Figure 11). Equipment mass = 2200 N. Because post-installed anchors may not withstand published allow- able static loads when subjected to vibratory loads, vibration isolators should be used between the equipment and the structure to damp vibra- tions generated by the equipment. (49) 소 = 4L2 Ix = 4B2 (50) (51) (52) Fig. 10 Equipment with Center of Gravity Different from Isolator Group (in Plan View) ![image](/image/placeholder) F pv PLAN F P cg ○ F cg iso p B We 0 hcg x e cg B equipment ○ ○ ⌀x W = 11 000 N B= 0.51 m ex= 0.20 m p nog ey = 0.10 m = 1.0 m L = 0.76 m Anchor properties Inc. ASHRAE, 2019 user. single for Licensed | {}
5279a9bc-ea0b-415b-8154-d60ab8410dab | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 56.14 2019 ASHRAE Handbook- -HVAC Applications (SI) Angle 0 = tan 1(LIVBI) = 36.86° (53) From Equation (43), (Wn)max/min = 2200 土 548 = 2748 N or 1652 N From Equation (44), Tm = ±4934(0.132 + 0.075) = ±1021 N From Equation (45), Te = 0 From Equation (46), (Tw) max/min = 687 N or 413 N From Equation (47), (Teff) max 687 = 1708 N (downward) = 1021 + 0 + From Equation (48), (Teff)max = -1021 + 0 + 413 = -608 N (upward) Forces in the hanger rods: Maximum tensile = 1708 N Maximum compression = 608 N ![image](/image/placeholder) STRUCTURE ABOVE VIBRATION ISOLATORS 1 HANGER RODS SPLAY pv 0.30 m BRACE cg W p SECTION 45° F p 0.90 m cg 1.20 m Force in the splay brace = FpV2 = 6978 N at a 1:1 slope. Because of the force being applied at the critical angle, as in Exam- ple 2, only one splay brace is effective in resisting the lateral load Fp. Design of hanger rod/vibration isolator and connection to structure Note: Splay braces are prestretched aircraft cables with enough slack so that isolators can fully function vertically. When post-installed anchors are mounted to the underside of a con- crete beam or slab, the allowable tension loads on the anchors must be reduced to account for cracking of the concrete. A general rule is to use half the allowable load. Some manufacturers have ICC reports that pro- vide allowable values for anchors installed under the slab. Determine whether a 13 mm wedge anchor with special inspection provisions will hold the required load. Tallow Teff= 1708 N = 2600 x 0.5 x 2 = 2600 > Therefore, a 13 mm rod and post drill-in anchor should be used at each corner of the unit. For anchors installed without special inspection, Tallow Teff= 1708 N = 2600 x 0.5 = 1300 > Therefore, a larger anchor should be chosen. Determine if the 13 mm hanger rod would require a stiffener ifit is m long. 1 Design of splay brace and connection to structure Force in the slack cable = 6978 N. Because all of the load must be resisted by a single cable, the forces in the connection to the structure are Vmax = 4934 N Tmax = 4934 N = Fp Because the cable forces are relatively small, a 9.5 mm aircraft cable attached to clips with cable clamps should be used. The clips, in turn, may be attached to either the structure or the equipment. The design of a post-installed anchor installation is similar to that shown in Example 1. Anchors installed through a metal deck will have lower capacities than anchors installed in a flat slab because of limited embedment depths. Take care to ensure that the design also satisfies the requirements contained in the evaluation report for the anchor specified. Prescriptive provisions of ASCE 7 can be summarized as follows: · Formulas for relative displacement of floor and ceiling can be conservatively estimated at 1% ofthe floor-to-ceiling height. This displacement must be used to determine the required horizontal flexibility of the pipe, duct, or electrical connections at the equip- ment interface. · In ASCE 7, using all-directional snubbers with clearance of more Fp than 7 mm increases by a factor of2. · Component supports must be designed to accommodate compo- nent movement to prevent pounding on the structure or other components. This affects internal isolators and snubbers. · Equipment components exposed to seismic impact forces and using nonductile housings must be designed using 25% of mate- rial yield stresses. · Nonessential equipment, failure of which can cause essential equipment failure, must be designed as essential equipment. · If the structure's site class is not provided in the contract docu- ments, assume site class D, subject to change by the building offi- cial. · For pipe or duct on any given run, ifthe distance from the bottom of the structure to the top of the support is 305 mm or less for all supports in that run, then that run does not need sway braces. · Pipe and ducts may not be required to have sway braces, depend- ing on size, material content, and importance factor. These con- ditions are defined in Chapter 13 of ASCE 7. 1.13 INSTALLATION PROBLEMS The following should be considered when installing seismic restraints. Inc. ASHRAE, 2019 user. single for Licensed Fig. 11 Supports and Bracing for Suspended Equipment · Anchor location affects the required strengths. Concrete anchors should be located away from edges, stress joints, or existing fractures. The evaluation report for the chosen anchor should be followed as a guide for edge distances and center-to-center spac- ing. | {}
d1802b52-2410-4de5-bb00-0e567fb44c5e | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Seismic- and Wind-Resistant Design 56.15 Table 7 Definition of Exposure Categories · Supplementary steel bases and frames, concrete bases, or equip- ment modifications may void some manufacturers' warranties. Snubbers, for example, should be properly attached to a subbase. Bumpers may be used with springs. · Static analysis does not account for the effects of resonant condi- tions within a piece of equipment or its components. Because all equipment has different resonant frequencies during operation and nonoperation, the equipment itself might fail even if the restraints do not. Equipment mounted inside a housing should be seismically restrained to meet the same criteria as the exterior restraints. · Snubbers used with spring mounts should withstand motion in all directions. Some snubbers are only designed for restraint in one direction; sets of snubbers or snubbers designed for multidirec- tional purposes should be used. · Equipment must be strong enough to withstand the high deceler- ation forces developed by resilient restraints. · Flexible connections should be provided between equipment that is braced and piping and ductwork that need not be braced. · Flexible connections should be provided between isolated equip- ment and braced piping and ductwork. · Bumpers installed to limit horizontal motion should be outfitted with resilient neoprene pads to soften the potential impact loads of the equipment. · Anchor installations must be inspected (usually required for anchors resisting seismic forces); in many cases, damage occurs because bolts were not properly installed. To develop the rated restraint, bolts should be installed according to manufacturer's recommendations. · Brackets in structural steel attachments should be matched to reduce bending and internal stresses at the joint. · With the exception of heavy-duty clamps used to attach longitu- dinal restraints to piping systems, friction must not be relied on to resist any load. All connections should be positive and all holes should be tight-fitting or grouted to ensure minimal clearance at the attachment points. 2. WIND-RESISTANT DESIGN Damage done to HVAC&R equipment by both sustained and gusting wind forces has increased concern about the adequacy of equipment protection defined in design documents. Two main areas of the HV AC&R system are exposed to wind events: the HV AC&R equipment and the exterior wall-mounted cladding components, such as intake and exhaust louvers. For HV AC&R equipment, the following calculative procedure generates the same type of total design lateral force used in static analysis of the seismic restraint. The value determined for the design wind force F can be substi- W tuted for the total design lateral seismic force Fp when evaluating and choosing restraint devices. For wall-mounted components, a design wind pressure P is determined, which can be used to specify equipment performance levels and design anchors to adequately brace wall-mounted cladding components to the building structure. The American Society of Civil Engineers' (ASCE) Standard 7-05 includes design guidelines for wind, snow, rain, and earthquake loads. Note that the equations, guidelines, and data presented here only cover nonstructural components. The current standard (2005) includes more comprehensive and rigorous procedures for evaluat- ing wind forces and wind restraint. Refer to the latest version of ASCE Standard 7 adopted by the local jurisdiction. 2.1 TERMINOLOGY Classification. Buildings and other structures are classified for wind load design exposure according to Table 7. Exposure B. Urban and suburban areas, wooded areas, or other terrain with numerous closely spaced obstructions the size of single-family dwellings or larger. Use of this exposure category is limited to those areas for which terrain representative of Exposure B prevails upwind for at least 800 m or 20 times the height of the building or structure, whichever is greater. Exception: For buildings with mean roof height less than or equal to 9 m, the upwind distance may be reduced to 460 m. Exposure C. Open terrain with scattered obstructions having heights generally less than 9 m. This category includes flat open country, grasslands, and all water surfaces in hurricane-prone areas. Exposure C applies for all cases where Exposure B or D do not apply. Exposure D. Flat, unobstructed areas exposed to wind and flowing over open water outside of hurricane-prone regions for a distance of at least 1600 m. This exposure applies to structures exposed to the wind coming from over the water as well as smooth mud flats, salt flats, and unbroken ice. Reprinted with permission from ASCE (2005). Notes: 1. For a site located in a transition zone between exposure categories, the exposure resulting in the largest wind forces must be used. 2. Exposure Category D extends into downwind areas of Exposures B or C for a dis- tance of 200 m or 20 times the height of the building, whichever is greater. 3. The responsibility for determining the exposure category for a given new building project falls on the structural engineer of record. This value is documented in the structural notes drawing (the first of the structural drawings) for the project. Table 8 Wind Importance Factor I (Wind Loads) ¦ Category ¦ I ¦ ¦ --- ¦ --- ¦ ¦ I ¦ 0.87 ¦ ¦ II ¦ 1 ¦ ¦ III ¦ 1.15 ¦ ¦ IV ¦ 1.15 ¦ Note: See Table 9 for categories. Basic wind speed. The fastest m/s wind speed at 10 m above the ground of Terrain Exposure C (see Table 7) having an annual prob- ability of occurrence of 0.02. Data in ASCE Standard 7 or regional climatic data may be used to determine basic wind speeds. ASCE data do not include all special wind regions (such as mountainous terrains, gorges, and ocean promontories) where records or experi- ence indicate that the wind speeds are higher than what is shown in appropriate wind data tables. For these circumstances, regional cli- matic data may be used provided that both acceptable extreme-value statistical analysis procedures were used in reducing the data and that due regard was given to the length of record, averaging time, anemometer height, data quality, and terrain exposure. One final exclusion is that tornadoes were not considered in developing the basic wind speed distributions. Components and Cladding. Elements of the building envelope that do not qualify as part of the main wind-force resisting system. Corner Zone. Areas of building walls and roofs adjacent to building corners that experience increased external pressure from wind. Design wind force. Equivalent static force that is assumed to act on a component in a direction parallel to the wind and not necessar- ily normal to the surface area of the component. This force varies with respect to height above ground level. Importance factor I. A factor that accounts for the degree of hazard to human life and damage to HV AC components (Table 8). For hurricanes, the value of the importance factor can be linearly interpolated between the ocean line and 160 km inland because wind effects are assumed negligible at this distance inland. Inc. ASHRAE, 2019 user. single for Licensed | {}
7721e62b-db04-445d-bb31-c08985946350 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 56.16 Table 9 Exposure Category Constants ¦ Exposure Category ¦ 0 ¦ Z m g' ¦ Gust Factor G ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ B ¦ 7 ¦ 360 ¦ 0.85 ¦ ¦ C ¦ 9.5 ¦ 270 ¦ 0.85 ¦ ¦ D ¦ 11.5 ¦ 210 ¦ 0.85 ¦ Reprinted with permission from ASCE (2005). Note: See Table 7 for definitions of exposure categories. Table 10 Force Coefficients for HVAC Components, Tanks, and Similar Structures ¦ ¦ ¦ Cffor h/D Values of ¦ Cffor h/D Values of ¦ Cffor h/D Values of ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Shape ¦ Type of Surface ¦ 1 ¦ 7 ¦ 25 ¦ ¦ Square (wind normal to face) ¦ All ¦ 1.3 ¦ 1.4 ¦ 2.0 ¦ ¦ Square (wind along diagonal) ¦ All ¦ 1.0 ¦ 1.1 ¦ 1.5 ¦ ¦ Hexagonal or octagonal D N Qz > 2.5 ¦ All ¦ 1.0 ¦ 1.2 ¦ 1.4 ¦ ¦ Round D NOz > 2.5 ¦ Moderately smooth ¦ 0.5 ¦ 0.6 ¦ 0.7 ¦ ¦ ¦ Rough (D'/D = 0.02) ¦ 0.7 ¦ 0.8 ¦ 0.9 ¦ ¦ ¦ Very rough (D'/D = 0.08) ¦ 0.8 ¦ 1.0 ¦ 1.2 ¦ ¦ Round D Oz ≤2.5 ¦ All ¦ 0.7 ¦ 0.8 ¦ 1.2 ¦ Reprinted with permission from ASCE (2005). Notes: 1. Design wind force calculated based on area of structure projected on a plane normal to the wind direction. Force is assumed to act parallel to wind direction. 2. Linear interpolation may be used for h/D values other than shown. 3. Nomenclature: D = diameter or least horizontal dimension, m D' = depth of protruding elements such as ribs and spoilers, m h = structure (top of equipment) height (above ground), m Qz = velocity pressure evaluated at height z above ground level, Pa Gust response factor G. A factor that accounts for the fluctuat- ing nature of wind and the corresponding additional loading effects on HVAC components Minimum design wind load. The wind load may not be less than 0.48 kPa multiplied by the area of the HVAC component pro- jected on a vertical plane that is normal to the wind direction. Inc. ASHRAE, 2019 user. single for Licensed 2.2 CALCULATIONS Two procedures are used to determine the design wind load on HVAC components. The analytical procedure, described here, is the most common method for standard component shapes, based on the requirements in ASCE 7. The second method, the wind-tunnel procedure, is used in the analysis of complex and unusually shaped components or equipment located on sites that produce wind chan- neling or buffeting because of upwind obstructions. The analytical procedure produces design wind forces that are expected to act on HVAC components for durations of 1 to 10 s. The various factors, pressure, and force coefficients incorporated in this procedure are based on a mean wind speed that corresponds to the fastest wind speed. Analytical Procedure The design wind force is determined by the following equation: Fw = QzGCfAF where (54) F w design wind force, N Qz = velocity pressure evaluated at height z above ground level, Pa 2019 ASHRAE Handbook-HVAC Applications (SI) G = gust response factor for HVAC components evaluated at heightz above ground level Cf - force coefficient (Table 10) Af= area of HVAC component projected on a plane normal to wind direction, m2 Certain of the preceding factors must be calculated from equa- tions that incorporate site-specific conditions that are defined as fol- lows: Velocity Pressure. The design wind speed must be converted to a velocity pressure that is acting on an HVAC component at a height z above the ground. The equation is Qz = 0.613K=K21KdV21 where (55) K7 = velocity pressure exposure coefficient from Table 12 / Kd = wind directionality factor = 1.0 K = topographic factor = 1.0 V = velocity from Figure 12, m/s I = importance factor from Table 8 The force generated by the wind is calculated by (56) Fw = QzGCfAf where Fw design wind force, N Qz = velocity pressure evaluated at height Z above ground level, Pa G = gust response factor for HVAC components evaluated at heightz above ground level of area of HVAC component projected on a plane normal to wind force coefficient (Table 10) direction, m2 The following example calculations are for a 1400 kW cooling tower: Tower height h = 3 m Tower width D = 3 m Tower length 1 = 6 m Tower operating mass Wp = 8650 kg Tower diagonal dimension = V 32 + 62 = 6.71 m Area normal to wind direction Af = 3 x 6.71 = 20.1 m2 From Table 10, Cf = 1.0 for wind acting along diagonal with h/D = 3/3 = 1. Example 5. Suburban hospital in Omaha, Nebraska. The top of the cooling tower is 30 m above ground level. Building width normal to the wind B = 1000 m, and building height H = 35 m. Solution: From Figure 12, the design wind speed is found to be 40 m/s. From Table 9, use Category IV. From Table 7, use Exposure B. From Table 8, I = 1.15. From Table 12, K2 = 1.07. From Figure 13, Kd = 0.9. From Table 9, G = 0.85. Substitution into Equation (58) yields Qz = 0.613 x 1.07 x 1.0 x 0.9 x (40)2 x 1.15 = 1086 Pa = 1.1 kPa Building height is greater than 20 m; therefore, Ef= 1.0. Substitution into Equation (54) yields the design wind force as Fw = 1086 x 0.85 X 1.0 x 20.1 x 1.0 = 19 460 N Example 6. Office building in New York City. Top oftower is 200 m above ground level. Building wall normal to the wind B = 180 m and building height H = 190 m. Solution: From Figure 12, the design wind speed is 54 m/s. From Table 9, use Category II. | {}
18901b9b-d538-47b7-800a-4f4a531023a2 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Seismic- and Wind-Resistant Design 56.17 From Table 7, use Exposure B. From Table 8, I = 1.0. From Figure 13, Kd = 0.9. Because Z > 150 m, K2 must be determined from Note 2 of Table 12. From Table 9, 0. = 7.0, Zg = 1200, and G = 0.85. Substituting into the first equation in Note 2 yields K2 = 2.10(Z/Zx)2/cz = 1.72 Substituting into Equation (55) yields Qz = 0.613 x 1.72 x 1.0 x 0.9 x (54)2 x 1.15 = 3182 Pa Building height is greater than 20 m, therefore Ef = 1.0. Substituting into Equation (56) yields the design force wind as Fw = 3182 x 0.85 x 1.0 x 20.1 x 1.0 = 54 364 N Example 7. Church in Key West, Florida. The top of the tower is 15 m above ground level. Building wall normal to the wind B = 110 m and building height H = 12 m. Solution: From Figure 12, the design speed is found to be 67 m/s. From Table 9, use Category III. From Table 5, use Exposure C (as this is a hurricane-prone region). From Table 16, I = 1.15. From Table 17, G= 0.85. From Table 13, Kd = 0.9. From Table 12, K2 = 1.09 (for exp category C). From Equation (55): Q: = 0.613 x 1.09 x 1.0 x 0.9 x (67)2 x 1.15 = 3104 Pa Building height is less than 20 m, Af /(B x H) = 224/(300 x 40) = 0.02, therefore, Ef = 1.9 Substituting into Equation (56) gives the design wind force as Fw = 3104 x 0.85 x 1.0 x 20.1 x 1.9 = 100 760 N 2.3 WALL-MOUNTED HVAC&R COMPONENT CALCULATIONS (LOUVERS) For many projects, the structural engineer of record will deter- mine the components and cladding wind pressures provided on the structural notes drawing. If these wind pressures are not provided, the two following procedures (described previously) are used to determine the design wind load on HVAC cladding components. Analytical Procedure Velocity Pressure. The design wind speed must be converted to a velocity pressure that is acting on an HVAC component at height Z above the ground. This is done using Equation (54). Once the ![image](/image/placeholder) 40 45 49 54 38 58 40 58 63 ALASKA NOTE: For coastal areas and islands, use nearest contour. 54 49 67 63 45 40 63 67 58 40 LOCATION m/s Hawaii 47 40 SPECIAL WIND REGION 63 45 Puerto Rico 56 58 67 49 54 Guam 76 Virgin Islands 56 40 POPULATION CENTER American Samoa 56 58 Notes: 45 1. Values are 3 S gust speeds in m/s at 10 m above ground for Exposure C category and are associated with an annual probability of 0.02. 49 2. Linear interpolation between wind speed contours is permitted. 3. Islands and coastal areas shall use wind speed contour of coastal area. 58 54 자 4. Mountainous terrain, gorges, ocean promontories, and special wind regions 58 shall be examined for unusual wind conditions. Fig. 12 Wind Speed Data Reprinted with permission from ASCE (2005) Inc. ASHRAE, 2019 Ⓒ user. single for Licensed | {}
96d5a432-b296-479b-a4a5-a5df45373596 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 56.18 velocity pressure has been determined, the design wind pressure can be calculated. Low-Rise Buildings and Buildings with h ≤18.3 m The design wind pressure for cladding is determined by the fol- lowing equation: Pw = Qh(GCp - GCpi) (57) where P w design wind pressure, N/m2 Qh velocity pressure evaluated at mean roof height h above ground level, Pa GCp external pressure coefficient given in Figure 13 GCpi internal pressure coefficient given in Table 14 Buildings with h > 18.3 m The design wind pressure is determined by the following equa- tion: Pw = Q(GCp) - qi(GCpi) where (58) Pw design wind pressure, N/m2 Qz velocity pressure for windward walls calculated at height z above the ground of the component being examined Qh = velocity pressure for leeward walls, side walls and roofs, evaluated at height h of the roof Qi = velocity pressure for windward walls, side walls, leeward walls, and roofs, evaluated at height h of the roof GCp external pressure coefficient given in Figure 14 GCpi internal pressure coefficient given in Table 14 Example 8. Office building in Houston, Texas. The top of the building is 9.1 m above grade located in a newly developed suburban area. It is necessary to determine the wind pressures on louver 1 and louver 2 shown on the building elevation in Figure 15. ![image](/image/placeholder) h a 0 a ⑤ a a NOTES: 1. Vertical scale denotes GCp to be used with qh 2. Horizontal scale denotes effective wind area, in square metres. 3. Plus and minus signs signify pressures acting toward and away from the surfaces, respectively. 4. Each component shall be designed for maximum positive and negative pressures. 5. Values of GCp for walls shall be reduced by 10% when 0 ≤ 10°. 6. Notation: a: 10% of least horizontal dimension or 0.4h, whichever is smaller, but not less than either 4% of least horizontal dimention or 0.9 m. h: Mean roof height, in metres, except that eave height shall be used for 0 ≤ 10°, 0: Angle of plane of roof from horizontal, in degrees. Fig. 13 External Pressure Coefficient GCp for Walls for h ≤ 18.3 m Reprinted with permission from ASCE (2005) 2019 ASHRAE Handbook-HVAC Applications (SI) Solution: From Figure 12, the design speed is found to be 54 m/s. From Table 9, use Category II. From Table 7, use Exposure C. From Table 8, I = 1.0. From Table 12, K2 = 0.98, at roofheight, h = 9.1 m. From Table 13, Kd = 0.85. Kzt assumed to be 1.0. Determine GCp: Building height h is less than 18.3 m; therefore, Equation (55) is used for the pressure evaluations. GCp must be deter- mined from Figure 15 for each of the louvers. Louver 1: from the notes on Figure 15, it is necessary to determine the a dimension, which establishes the corner zone 5. The least hori- zontal dimension coming into the corner is 9.8 m from the plan view. Ten percent of this value is 1 m. The minimum value for the corner dimension is 0.9 m. Louver 1 is located 0.37 m from the corner and is therefore in corner zone 5. From Figure 15, GCp = = +0.95 or -1.3 for a 1.9 m2 wind area. A positive GCp indicates a positive pressure on the windward side of the building. A negative GCp indicates a suction pressure on the leeward side of the building. Both cases must be evaluated. Louver 2: based on the corner calculation, louver 2 is in noncorner zone 4. From Figure 15, GCp = +0.9 or -1.0 for a 2.8 m2 wind area. Determine GCpi: See Figure 14. Most buildings without significant wall openings are enclosed buildings. For the purposes of this example, an enclosed building is assumed. GCpi = +0.18 or -0.18. A positive sign indicates pressure outward on all structure walls. A negative sign indicates pressure inward on all structure walls. Determine velocity pressure at roof elevation h from Equation (55): Qh = 0.613 x 0.98 x 1.0 x 0.85 x (54)2 x 1.0 = 1489 Pa Determine design wind pressure P from Equation (56): Louver 1, case 1: positive external, positive internal P = 1489 x (0.95 - 0.18) = 1147 Pa Louver 1, case 2: positive external, negative internal GCp COEFFICIENT PRESSURE EXTERNAL Chart Type: line 0. 0.9 1.9 4.6 9.3 18.6 46.5 92.9 item_01 5 1.4 1.2 1.0 0.8 0.9 0.8 0.7 Inc. ASHRAE, 2019 user. single for Licensed EFFECTIVE WIND AREA, m2 | {}
70446908-e324-454d-b0ee-e231e1d1c501 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Seismic- and Wind-Resistant Design 56.19 ![image](/image/placeholder) 0.9 1.9 46.5 -3.6 -3.4 -3.2 -3.2 -3.0 -2.8 GCp -2.6 a a -2.4 -2.3 COEFFICIENT -2.2 2a a 2a -2.0 ⑤ -1.8 -1.8 ③ 2 3 -1.6 -1.6 2a ① -1.4 -1.4 PRESSURE -1.2 -1.0 a -1.0 4 -0.9 -0.8 -0.7 EXTERNAL h -0.6 -0.4 -0.2 0 Z +0.2 2a +0.4 ③ +0.6 +0.8 4 & +0.8 +0.9 +1.0 ROOF PLAN WALL ELEVATION 0.1 0.9 1.9 4.6 9.3 18.6 46.5 92.9 EFFECTIVE WIND AREA, m2 NOTES: 1. Vertical scale denotes GCp to be used with appropriate qz or qh- 2. Horizontal scale denotes effective wind area A. in square metres. 3. Plus and minus signs signify pressures acting toward and away from the surfaces, respectively. 4. Use qz with positive values of GCp and qh with negative values of GCp. 5. Each component shall be designed for maximum positive and negative pressures. 6. Coefficients are for roofs with angle 0 ≤ 10°, For other roof angles and geometry, use GCp values from Figure 6-11 and attendant qh based on exposure defined in 6.5.6. 7. If a parapet equal to or higher than 0.9 m is provided around the perimeter of the roof with 0 S 10°, Zone 3 shall be treated as Zone 2. 8. Notation: a: 10% of least horizontal dimension, but not less than 0.9 m. h: Mean roof height, in metres, except that eave height shall be used for 0 ≤ 10° Z: Height above ground, in metres. 0: Angle of plane of roof from horizontal, in degrees. Fig. 14 External Pressure Coefficient GCp for Walls for h > 18.3 m Reprinted with permission from ASCE (2005) ![image](/image/placeholder) 3.8 m LOUVER 2 AREA = 2.8 m2 ト 0.37 m LOUVER 1 AREA = 1.9 m2 9.8 m 9.1 m 6.2 m 10 m BUILDING FRONT ELEVATION BUILDING PLAN VIEW Fig. 15 Office Building, Example 10 P = 1489 x [0.95 - (-0.18)] = 1683 Pa P = 1489 x [(-1.3) - (-0.18)] = -1667 Pa Louver 1, case 3: negative external, positive internal The controlling values for P for louver 1 are 1683 Pa, -2204 Paand should be used to specify equipment performance levels. P = 1489 x [(-1.3) - 0.18] = -2204 Pa Louver 2, case 1: positive external, positive internal Louver 1, case 4: negative external, negative internal P = 1489 x (0.90 - 0.18) = 1072 Pa Inc. ASHRAE, 2019 user. single for Licensed | {}
6d035421-0ede-48cb-a95f-517cd5f98fa0 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 56.20 2019 ASHRAE Handbook- -HVAC Applications (SI) ![image](/image/placeholder) Santa Holmes Rosa Okalnoca Jackson Warton Washington Gadsden Leon Nouager Kadise 100 mph Duval Calhoun Liberty 110 mph Wakufa Tayor Day Frankin 120 moR 정보 52 140 mph Rachua 130 mph Putnar Levey Marion : : 100 mph Wind-borne Debris Region Clus Lake Designated areas where the basic wind speed do Orange is 120 mph or greater. Pasco Osceola 110 MPH and within 1 mile of the coast Hilsbolough Polk 110mph Hardee ghland DeSato Basic Wind Speed Charlotte Glades 1 Values are nominal design, 3- second gusts, wind-speeds in 120 mph miles per hour (mph) at 33 feet (10m) above ground for Hendry Beach Exposure C Category. 2 This map is accurate to the county. Local governments establish specific wind-speed / wind-borne debris lines Collier 130 mph using physical landmarks such as major roads, canals, rivers and shorelines. 3 Islands and Coastal areas outside the last contour shall use 140mph the last wind-speed contour of the coastal area. 150 mph Monroe Fig. 16 State of Florida Windborne Debris Regions mph x 1.609 = km/h ICC (2007) Louver 2, case 2: positive external, negative internal P = 1489 x [0.90 - (-0.18)] = 1608 Pa Louver 2, case 3: negative external, positive internal P = 1489 x [(-1.0) - 0.18] =-1757 Pa Louver 2, case 4: negative external, negative internal P = 1489 x [(-1.0) - (-0.18)] = -1221 Pa The controlling values for P for louver 2 are 1608 Pa, -1757 Pa and should be used to specify equipment performance levels. 2.4 CERTIFICA TION OF HVAC&R COMPONENTS FOR WIND Some jurisdictions require certifications of performance of HVAC&R components for wind resistance. These certifications focus on (1) the equipment's ability to remain intact and/or (2) the equipment restraints and anchors to keep the item in place during a wind event. In the United States, the State of Florida and the Building Code Compliance Office of Miami-Dade County have certification requirements that affect HVAC&R system designers. The HVAC products may have special requirements for wind performance and may need approval of the State of Florida. In addition to wind performance, the Florida Building Code (ICC 2007) requires impact resistance and wind-pressure resistance for items that protect open- ings in buildings in windborne debris regions. The windborne debris regions can be viewed in Figure 16. HVAC products provided for projects located in these regions may be required to have testing and product certification from the State of Florida before installation. Other states, such as Texas, also have requirements for wind- pressure and impact testing. To ensure that the HV AC&R equipment supplied is compliant, designers should contact the local building code official in their project location. Some of the testing protocols for the State of Florida are · TAS 201-94: Impact Testing Procedures · TAS 202-94: Criteria for Testing Impact and Non-Impact Resis- tant Building Envelope Components Using Uniform Static Air Pressure · TAS 203-94: Criteria for Testing Products Subject to Cyclic Wind Pressure Loading REFERENCES ASHRAE members can access ASHRAE Journal articles and ASHRAE research project final reports at technologyportal.ashrae .org. Articles and reports are also available for purchase by nonmem- bers in the online ASHRAE Bookstore at www.ashrae.org/bookstore. ACI. 2008. Building code requirements for structural concrete (ACI 318-08) and commentary. Standard 318-08. American Concrete Institute, Farm- ington Hills, MI. AISC. 1989. Manual ofsteel construction-Allowable stress design, 9th ed. American Institute of Steel Construction, Chicago. ASCE. 2005. Minimum design loads for buildings and other structures. Standard ASCE 7-05. American Society of Civil Engineers, Reston, VA. Inc. ASHRAE, 2019 ⊙ user. single for Licensed | {}
5637ae9f-f328-4d30-a91f-69ddceb34c66 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Seismic- and Wind-Resistant Design 56.21 Table 11 Classification of Buildings and Other Structures for Wind Loads ¦ Nature of Occupancy ¦ Category ¦ ¦ --- ¦ --- ¦ ¦ Buildings and other structures that represent a low hazard to human life in event of failure, including, but not limited to, agricultural facilities, certain temporary facilities, and minor storage facilities ¦ I ¦ ¦ All buildings and other structures except those listed in Categories I, III, and IV ¦ II ¦ ¦ Buildings and other structures that represent a substantial hazard to human life in event of failure, including, but not limited to, - Buildings and other structures where more than 300 people congregate in one area. - Buildings and other structures with elementary and secondary schools, day care facilities with capacity greater than 250 - Buildings and other structures with capacity greater than 500 for colleges or adult education facilities - Health care facilities with capacity of 50 or more resident patients, but not having surgery or emergency treatment facilities - Jails and detention centers - Power generating stations and other public utility facilities not included in Category IV - Buildings and others structures containing sufficient quantities of toxic or explosive substances to be dangerous to the public if released ¦ III ¦ ¦ Buildings and other structures designated as essential facilities including, but not limited to, - Hospitals and other health care facilities with surgery and emergency treatment facilities - Fire, rescue, and police stations and emergency vehicle garages - Designated earthquake, hurricane, or other emergency shelters - Communication center and other facilities required for emergency response - Power generating stations and other public utility facilities required in an emergency - Buildings and other structures with critical national defense functions ¦ IV ¦ ¦ Reprinted with permission from ASCE (2005). ¦ ¦ ASHRAE. 2000. A practical guide to seismic restraint. Research Project RP-812, Final Report. ASME. 2003. Nuclear air and gas treatment. Code AG-1-2003. American Society of Mechanical Engineers, New York. ASTM. 1996. Test methods for strength of anchors in concrete and masonry elements. Standard E488-96 (R2003). American Society for Testing and Materials, West Conshohocken, PA. ATC. Proceedings ofseminar on seismic design, performance, and retrofit of nonstructural components on criticalfacilities. ATC29-2. Applied Tech- nology Council, Washington, D.C. AWC. 1997. National design specification (NDSⓇ) for wood construction. American Wood Council, Washington, D.C. BOCA. 1996. The BOCA national building code, 13th ed. Building Officials & Code Administrators International, Inc., Country Club Hills, IL. Cover, L.E., et al. 1985. Handbook ofnuclear power plant seismic fragilities. Report NUREG/CR-3558. Lawrence Livermore National Laboratory and U.S. Nuclear Regulatory Commission, Washington, D.C. DOD. 1990. Structures to resist the effects of accidental explosions. Techni- cal Manual TM 5-1300. U.S. Department of Defense, Washington, D.C. DOD. 2002. Design and analysis of hardened structures to conventional weapons effects. Technical Manual TM 5-855-1. U.S. Department of Defense, Washington, D.C. Table 12 Velocity Pressure Exposure Coefficient K2 ¦ Height above ground level z, m ¦ Exposure ¦ Exposure ¦ Exposure ¦ Exposure ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Height above ground level z, m ¦ A ¦ B ¦ C ¦ D ¦ ¦ 0 to 5 ¦ 0.32 ¦ 0.57 ¦ 0.86 ¦ 1.04 ¦ ¦ 6 ¦ 0.36 ¦ 0.62 ¦ 0.89 ¦ 1.08 ¦ ¦ 8 ¦ 0.39 ¦ 0.66 ¦ 0.95 ¦ 1.13 ¦ ¦ 10 ¦ 0.42 ¦ 0.72 ¦ 1.00 ¦ 1.17 ¦ ¦ 12 ¦ 0.47 ¦ 0.76 ¦ 1.04 ¦ 1.22 ¦ ¦ 15 ¦ 0.52 ¦ 0.81 ¦ 1.09 ¦ 1.27 ¦ ¦ 20 ¦ 0.59 ¦ 0.88 ¦ 1.15 ¦ 1.33 ¦ ¦ 25 ¦ 0.62 ¦ 0.94 ¦ 1.22 ¦ 1.38 ¦ ¦ 30 ¦ 0.68 ¦ 0.98 ¦ 1.26 ¦ 1.43 ¦ ¦ 35 ¦ 0.70 ¦ 1.01 ¦ 1.28 ¦ 1.45 ¦ ¦ 40 ¦ 0.76 ¦ 1.07 ¦ 1.34 ¦ 1.50 ¦ ¦ 50 ¦ 0.83 ¦ 1.14 ¦ 1.40 ¦ 1.56 ¦ ¦ 60 ¦ 0.89 ¦ 1.19 ¦ 1.46 ¦ 1.61 ¦ ¦ 70 ¦ 0.94 ¦ 1.24 ¦ 1.49 ¦ 1.64 ¦ ¦ 80 ¦ 1.00 ¦ 1.30 ¦ 1.55 ¦ 1.69 ¦ ¦ 90 ¦ 1.05 ¦ 1.35 ¦ 1.59 ¦ 1.73 ¦ ¦ 100 ¦ 1.09 ¦ 1.39 ¦ 1.62 ¦ 1.76 ¦ ¦ 110 ¦ 1.14 ¦ 1.43 ¦ 1.65 ¦ 1.79 ¦ ¦ 120 ¦ 1.18 ¦ 1.46 ¦ 1.68 ¦ 1.82 ¦ ¦ 130 ¦ 1.21 ¦ 1.49 ¦ 1.71 ¦ 1.84 ¦ ¦ 140 ¦ 1.25 ¦ 1.53 ¦ 1.74 ¦ 1.87 ¦ ¦ 150 ¦ 1.29 ¦ 1.56 ¦ 1.77 ¦ 1.89 ¦ Reprinted with permission from ASCE (2005). Notes: 1. Linear interpolation for intermediate values of height z is acceptable. 2. For values of height z greater than 152.4 m, K2 must be calculated using the follow- ing equations: K2 =2.01(z/zx)2/cx For 4.5 m Sz≤zg or K2 = 2.01(15/zg)2/ca For z<4.5 m 3. Exposure categories are defined in Table 7. 4. Values for alpha (�) and Zg are found in Table 9. Table 13 Directionality Factor Kd ¦ Structure Type ¦ Directionality Factor Kd * ¦ ¦ --- ¦ --- ¦ ¦ Buildings ¦ ¦ ¦ Main wind-force-resisting system ¦ 0.85 ¦ ¦ Components and cladding ¦ 0.85 ¦ ¦ Arched roofs ¦ 0.85 ¦ ¦ Chimneys, tanks, and similar structures ¦ ¦ ¦ Square ¦ 0.90 ¦ ¦ Hexagonal ¦ 0.95 ¦ ¦ Round ¦ 0.95 ¦ ¦ Solid signs ¦ 0.85 ¦ ¦ Open signs and lattice framework ¦ 0.85 ¦ ¦ Trussed towers ¦ ¦ ¦ Triangular, square, rectangular ¦ 0.85 ¦ ¦ All other cross sections ¦ 0.95 ¦ Reprinted with permission from ASCE (2005). *Directionality factor Kd has been calibrated with combinations of load specified in Section 2. This factor shall only be applied when used in conjunction with load com- binations specified in 2.3 and 2.4 Inc. ASHRAE, 2019 user. single for Licensed | {}
60d115ea-5224-4b3a-8a97-48c55f380d23 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 56.22 2019 ASHRAE Handbook-HVAC Applications (SI) Table 14 Internal Pressure Coefficient GCpi ¦ Enclosure Classification ¦ GCpi ¦ ¦ --- ¦ --- ¦ ¦ Open buildings ¦ 0.00 ¦ ¦ Partially enclosed buildings ¦ +0.55 ¦ ¦ ¦ -0.55 ¦ ¦ Enclosed buildings ¦ +0.18 ¦ ¦ ¦ -0.18 ¦ Reprinted with permission from ASCE (2005). Notes: 1. Plus and minus signs signify pressures acting toward and away from the internal sur- faces, respectively. 2. Values of GCpi shall be used with 9x or 9h as specified in 6.5.12. 3. Two cases shall be considered to determine the critical load requirements for the appropriate condition: ① a positive value of GCpi applied to all internal surfaces (ii) a negative value of GCpi applied to all internal surfaces DOD. 2005. Unifiedfacilities criteria (UFC): Structural engineering. UFC 3-310-01. U.S. Department of Defense, Washington, D.C. Available at www.widg.org/cck/DOD/UFCht_3_3_301_01_pdf DOD. 2007. Unifiedfacilities criteria (UFC): Seismic design for buildings. UFC 3-310-04. U.S. Department of Defense, Washington, D.C. Avail- able at www.windg.org/cb/DOD/UFC/ufc_3_311_04.pdf ICC. 2007. Florida building code. International Code Council, Inc., Wash- ington, D.C. ICC. 2009. International building code�. International Code Council, Washington, D.C. ICC-ES. 2007. Acceptance criteria for seismic qualification by shake-table testing of nonstructural components and systems. AC156. ICC Evalua- tion Service, Inc., Whittier, CA. ICBO. 1997. Uniform building code. International Conference of Building Officials, Whittier, CA. (Now part of ICC.) NRC-IRC. 2010. National building code of Canada. National Research Council Institute for Research in Construction, Ottawa. SBCCI. 1994. Standard building code 1996. Southern Building Code Con- gress International, Inc., Birmingham, AL. SMACNA. 2008. Seismic restraint manual: Guidelines for mechanical sys- tems, 3rd ed. Sheet Metal and Air Conditioning Contractors' National Association, Chantilly, VA. U.S. Army, Navy, and Air Force. 1992. Seismic designfor buildings. TM 5- 809-10, NA VFAC P-355, AFN 88-3, Chapter 13. U.S. COE. 1998. Technical instructions: Seismic design for buildings. TI 809-04. U.S. Army Corps of Engineers, Washington, D.C. BIBLIOGRAPHY AISC. 1995. Manual of steel construction-Load and resistance factor design, 2nd ed. American Institute of Steel Construction, Chicago. Associate Committee on the National Building Code. 1985. National build- ing code of Canada 1985, 9th ed. National Research Council of Canada, Ottawa. Associate Committee on the National Building Code. 1986. Supplement to the National Building Code of Canada 1985, 2nd ed. National Research Council of Canada, Ottawa. First errata, January. ATC. Proceedings of seminar and workshop on seismic design and perfor- mance of equipment and nonstructural elements in buildings and indus- trial structures. ATC29, NCEER (New Y ork) & NSF (Washington D.C.). ATC. Seminar on seismic design, retrofit, and performance ofnonstructural components. ATC 29-1, NCEER (New York) & NSF (Washington D.C.). AWS. 2000. Structural welding code. AWS D1.1-2000. Steel American Welding Society, Miami. Ayres, J.M., and R.J. Phillips. 1998. Water damage in hospitals resulting from the Northridge earthquake. ASHRAE Transactions 104(1B):1286-1296. Batts, M.E., M.R. Cordes, L.R Russell, J.R. Shaver, and E. Simiu. 1980. Hurricane wind speeds in the United States. NBS BSS 124. National Institute of Standards and Technology, Gaithersburg, MD. Bolt, B.A. 1988. Earthquakes. W.H. Freeman, New York. DOE. 1989. Gen- eral design criteria. DOE Order 6430.1A. U.S. Department of Energy, Washington, D.C. FEMA 368 & 369. NEHRP recommended provisionsfor seismic regulations for new buildings and other structures. Part 1, Provisions; Part 2, Com- mentary. Building Seismic Safety Council, Washington, D.C. Jones, R.S. 1984. Noise and vibration control in buildings. McGraw-Hill, New York. Kennedy, R.P., S.A. Short, J.R. McDonald, M. W. McCann, and R.C. Mur- ray. 1989. Design and evaluation guidelines for the Department of Energyfacilities subjected to natural phenomena hazards. Lama, P.J. 1998. Seismic codes, HVAC pipe systems and practical solutions. ASHRAE Transactions 104(1B):1297-1304. Maley, R., A. Acosta, F. Ellis, E. Etheredge, L. Foote, D. Johnson, R. Porcella, M. Salsman, and J. Switzer. 1989. Department of the Interior, U.S. geo- logical survey. U.S. geological survey strong-motion records from the Northern California (Loma Prieta) earthquake of October 17, 1989. Open-file Report 89-568. Meisel, P. W. 2001. Static modeling of equipment acted on by seismic forces. ASHRAE Transactions 107(1):775-786. Naeim, F. 1989. The seismic design handbook. Van Nostrand Reinhold Inter- national Company Ltd., London, England. Naeim, F. 2001. The seismic design handbook, 2nd ed. Kluwer Academic, Boston. NFPA. 2002. Installation of sprinkler systems. National Fire Protection Association, Quincy, MA. Peterka, J.A., and J.E. Cermak. 1974. Wind pressures on buildings-Prob- ability densities. Journal of Structural Division, ASCE 101(6):1255- 1267. Simiu, E., M.J. Changery, and J.J. Filliben. 1979. Extreme wind speeds at 129 stations in the contiguous United States. U.S. NBS BSS 118. Na- tional Institute of Standards and Technology, Gaithersburg, MD. SMACNA. 2005. HVAC duct construction standard-metal andflexible, 3rd ed. Sheet Metal and Air Conditioning Contractors' National Association, Chantilly, VA. Wasilewski, R.J. 1998. Seismic restraints for piping systems. ASHRAE Transactions 104(1B):1273-1295. Weigels, R.L. 1970. Earthquake engineering, 10th ed. Prentice-Hall, Engle- wood Cliffs, NJ. Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
8364c3e6-c356-4628-b1bd-cedbe234c63c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 57 ELECTRICAL CONSIDERATIONS ¦ Terminology ¦ 56.1 ¦ ¦ --- ¦ --- ¦ ¦ Safety ¦ 56.1 ¦ ¦ Performance ¦ 56.2 ¦ ¦ Electrical System Components and Concepts ¦ 56.2 ¦ ¦ Power Quality Variations ¦ 56.7 ¦ ¦ Billing Rates ¦ 56.13 ¦ ¦ Codes and Standards ¦ 56.15 ¦ P RODUCTION, delivery, and use of electricity involve count- less decisions made along the way, by hundreds of people and companies. This chapter focuses on the decisions to be made about the building and equipment. Creating a building that works means including the best designs available, communicating needs and capabilities, and planning ahead. For an owner-occupied building, the benefits of a properly de- signed building return to the owner throughout the building's life. For tenant-occupied spaces, good design means fewer problems with tenant and building system interference (e.g., lighting or appli- ances in one suite disrupting computers in a neighboring suite). Because HV AC&R equipment can have a large effect on build- ings, it is necessary to address electrical issues in buildings that spe- cifically are caused by or have an effect on HVAC&R equipment. 1. TERMINOLOGY Electricity: fundamental form of energy found in positive and negative forms and expressed in terms of the movement and interac- tion of electrons. Volt (V): practical unit of electric pressure; the pressure that will produce a current of 1 A against a resistance of 1 요; equal to 1 J/s. Also called the electromotive force (emf). Current (I): movement of electrons through a conductor; mea- sured in amperes. Ampere (A): practical unit of electric current flow. Ifa 1 요 resis- tance is connected to a 1 v source, 1 A will flow. Alternating current (ac): a current that reverses at regular, recurring intervals of time and that has alternately positive and neg- ative values. The values vary over time in a sinusoidal manner. Direct current (dc): a current where electrons move steadily in one direction. Watt (W): unit ofreal electrical power, equal to the power devel- oped in a circuit by a current of 1 A flowing through a potential dif- ference of 1 V. Volt-ampere (VA): amount of apparent power in an alternating current circuit equal to a current of 1 A at an emf of1 V. It is dimen- sionally equivalent to watts. Volt-ampere is equal to watts when volt- age and current are in phase. v olt-ampere-reactive (V AR): unit for reactive power. The sym- bols Q and sometimes N are used for the quantity measured in VARs. VARs represent the power consumed by a reactive load (i.e., when there is a phase difference between applied voltage and current). Power factor: for an ac electric power system, the ratio of the real power to the apparent power, or W/VA. Three-phase power: supplied by three conductors, with the cur- rents (or voltages) of any two 120° out of phase with each other. The preparation of this chapter is assigned to TC 1.9, Electrical Systems. Y-Axis: Voltage Chart Type: line 1 2 3 item_01 0.5Voltage (t/60 s) 0.8Voltage (t/60 s) 0.2Voltage (t/60 s) Fig. 1 Fundamental v oltage Wave Y (or "wye") connection: a configuration of wiring so that each winding of a polyphase transformer (or three single-phase trans- formers) is connected to a common point, the "neutral. " Delta-connected circuit: a three-phase circuit that is mesh con- nected, so the windings of each phase of a three-phase transformer are connected in a series for a closed circuit (i.e., in a triangle or "delta" configuration). Fundamental voltage: produced by an electric ac generator and has a sinusoidal waveform with a frequency of 60 cycles per second, or 60 Hz (in the United States). Other countries may have a similar waveform but at 50 cycles per second of 50 Hz. Cycle: the part of the fundamental waveform where the electrical potential goes from zero to a maximum to zero to a minimum, and back to zero again (i.e., one complete wave; see Figure 1). At 60 Hz, there are 60 cycles in 1 second. RMS (root-mean-squared) voltage: an effective way to com- pare ac to dc value. For a pure sinusoidal waveform, RMS value is equal to 0.707 times the peak magnitude. System voltage: the RMS phase-to-phase voltage of a portion of an ac electric utility system. Each system voltage pertains to a part of the system bounded by transformers or end-use equipment. Service voltage: the voltage at the point where the electric sys- tems of the supplier and the user are connected. Utilization voltage: the voltage at the terminals of the utilization equipment. Nominal system voltage: the rated system voltage level (i.e., 480 volts) at which the electrical system normally operates. To allow for operating contingencies, utility systems generally operate at voltage levels within -5% to +5% of nominal system voltage. 2. SAFETY The greatest danger from electricity is that it is taken for granted and not taken seriously as a hazardous energy source. Electricity can produce bodily harm and property damage, and shut down entire operations. The type of damage from electricity ranges from a mild shock to the body to a major electrical fire. Electrical safety is im- portant in all occupational settings. See information on safety codes in the Electrical Codes section. Inc. ASHRAE, 2019 user. single for Licensed 57.1 | {}
10e13f2c-67bb-4790-9991-c1997e54c877 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 57.2 2019 ASHRAE Handbook-HVAC Applications (SI) In the United States, the National Electrical CodeⓇ (NEC; NFPA Standard 70) is generally accepted as the minimum safety require- ments for wiring and grounding in a structure. Other countries have similar requirements. The NEC ensures building design is safe, but may not provide the performance that a modern building requires. Rapid changes in electronic technologies have rendered many tra- ditional electrical distribution practices obsolete and must be replaced with new designs. Electrical power distribution decisions made during design affect occupants , productivity for the life of the building. Many improvements over the minimum requirements are relatively inexpensive to implement during building construction. 3. PERFORMANCE Power quality, like quality in other goods and services, is diffi- cult to define. There are standards for voltage and waveshape, but the final measure of power quality is determined by the perfor- mance and productivity of the building occupant's equipment. If the electric power is inadequate for those needs, then the quality is lacking. Specifications for electric power are set down in recognized national standards. These are voltage levels and tolerances that should be met, on the average, over a long period of time. Electric utilities and building distribution systems generally meet such spec- ifications. Voltage drop in a building is a fundamental reason for cal- culating the size of electrical conductors. Brief disturbances on the power line are not addressed in these time-averaged specifications; new standards are being developed to address these concerns. Interaction between tenants' electrical equipment is an ongoing problem. Often, a large load in one tenant's space can disrupt a small appliance or computer in another part of the building. Voltage drop along building wiring and harmonic distortion are often the causes of the problem. Dedicated circuits usually solve the voltage drop problem, but harmonic distortion must be solved at the contributing loads. By eliminating much of the wiring common to both pieces of equipment, the original performance of each is restored. With mod- ern electronic loads, the interaction might easily involve a large load that interferes with smaller, more sensitive equipment. Disturbances might travel greater distances or through nondirect paths, so diag- nostics are more difficult. Inc. ASHRAE, 2019 user. single for Licensed For tenants of a building with ordinary power distribution, lost productivity associated with power quality problems is an addi- tional operating expense. The disturbance may last only millisec- onds, but the disruption to business may require hours of recovery. This multiplication of lost time makes power quality a significant business problem. Lost productivity may be the time it takes to restart a chiller, to repair a critical piece of equipment, or to retype a document. Another aspect oflost productivity is the stress on employees whose work is lost. The building owner may suffer loss, as well. Certainly the building equipment itself may suffer from the same damage or losses as tenant equipment. Sophisticated energy management sys- tems, security systems, elevator controls, HVAC&R systems, and communications facilities are susceptible to disruption and vulner- able to damage. 4. ELECTRICAL SYSTEM COMPONENTS AND CONCEPTS Voltage differential causes electrons to flow. In a direct current (dc) electrical system, electrons flow in only one direction. In an alternating current (ac) electrical system, electrons continually alter- nate or change direction at a prescribed number of times per second. The main disadvantage of dc voltage is its inability to be boosted or attenuated easily and efficiently. The alternating magnetic fields of ac make boosting or decreasing voltage with transformers feasible, which is why ac has been widely adopted. Electrons flow more effi- ciently at lower currents because I2R losses are minimized. For the same load, raising the voltage level reduces the current while deliv- ering the same power. When long distances are involved, electric utility companies step up voltages to very high levels for transmis- sion. However, these voltages are extremely dangerous, so they must be stepped down to a safer, lower, usable voltage before use. Trans- formers offer an efficient way to change voltage levels (step-up or step-down) for an alternating current power source. Electrical Wiring (Conductors for General Wiring) Just because a conductor is insulated does not mean it is suited for a specific application. NFPA Standard 70 list designations of wires and cables that meet minimum fire, electrical, and physical requirements of relevant standards. Unless otherwise specified by codes, conductors must be aluminum, copper-clad aluminum, or copper. To find allowable ampacities for insulated conductors at vari- ous temperatures, consult Tables 3 10.15(B)(16) to 310.15(B)(20) of NFPA Standard 70-2014. Tables 310.15(B)(2)(a) and 310.15(B)(2) (b) of that standard have correction factors for ambient temperatures other than 30 or 40°C. If more than one ampacity could apply for a given circuit, use the lowest value. Transformers Transformers are used to change one voltage to another voltage, typically to step up voltage levels from generators. Power can then be transmitted at a low current (with less loss). At the end of the transmission line, a step-down transformer reduces the voltage to a usable level. A transformer consists of a ferromagnetic core wrapped with multiple coils, or windings, of wire. The input line is connected to the primary coil, and the output line is connected to the secondary coil. Alternating current 11 in the primary coil induces an alternating magnetic flux ⌀ that flows through the ferromagnetic core, changing direction during each electrical cycle. This flux in turn induces alter- nating current I2 in the secondary coil. The voltage V2 at the second- ary coil is directly related to the primary voltage by the turns ratio (i.e., the number of turns N1 in the primary coil divided by the num- ber turns N2 in the secondary coil). An ideal transformer with two windings wrapped around a magnetized core is shown in Figure 2. The ideal model for a trans- former assumes I2R losses, core losses, leakage flux, and core reluc- tance are insignificant. A practical model includes these losses. Transformer losses can be divided into core (or iron) losses, cop- per losses, and stray losses. Core losses include hysteresis losses and eddy current losses. All ferromagnetic materials tend to retain some degree of magnetization after exposure to an external magnetic field. This tendency to stay magnetized is called hysteresis, and it takes energy to overcome this opposition to change every time the mag- netic field produced by the primary winding changes polarity. Eddy current losses result from induced currents circulating in the ![image](/image/placeholder) 1, 0 0 /2 N2 V, N, V2 中 = CONSTANT Fig. 2 Ideal Transformer | {}
1ff974e1-55b5-402f-a5df-d63aca46936d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Electrical Considerations 57.3 magnetic core perpendicular to the flux. Because iron conducts both electricity and magnetic flux, eddy currents are induced in the iron just as in the secondary windings from the alternating magnetic field. Three identical single-phase, two-winding transformers may be connected to form a three-phase bank. The four possible connec- tions are Y-Y, Y-A, A-Y, and △-△. The U.S. standard for marking three-phase transformers uses H1,H2, and H3 on the high-voltage ter- minals and X1, X2, and X3 on the low-voltage terminals; A, B, and C identify phases on the high-voltage side of the transformer, and a, b, and c identify phases on the low-voltage side. Typically, three-phase voltages present the higher voltage (phase-to-phase) first, followed by the lower voltage (phase-to-neutral). Single-phase voltages typically present the lower voltage (phase-to-neutral) first, followed by the higher voltage (phase-to-phase). For example, 208/120 V is three-phase and 120/240 V is single-phase. Y-Y connections (Figure 3) are rarely used because of balancing and harmonics problems. Y-A connections (Figure 4) are typically used for stepping down from high to medium voltage. The A-Y transformer (Figure 5) is commonly used as a generator step-up transformer, where the △ winding is connected to the gen- erator terminals and the Y winding is connected to the transmission line. One advantage of the high-voltage Y winding is that a neutral point N is provided for grounding on the high-voltage side. The △-△ transformer (Figure 6) has the advantage that one phase can be removed for repair or maintenance while the remaining ![image](/image/placeholder) IA A a 0 + VAN an V IB /b B b + + Vbn VBN /c C C + VCN V cn N Fig. 3 Three-Phase Y-Y Transformer ![image](/image/placeholder) IA A a + + Vab VAN IB b B + + Vbc VBN lc C C + VCN V Fig. 4 Three-Phase Y-A Transformer phases continue to operate as a three-phase bank. The open △ con- nection allows balanced three-phase operation with the kVA rating reduced to 58% ofthe original bank. These △-△ connections are typ- ically used in distribution networks. An autotransformer has two windings connected in series (Fig- ure 7). Whereas a typical transformer's windings are only coupled magnetically via the mutual core flux, an autotransformer's wind- ings are both electrically and magnetically coupled. An autotransformer has smaller per-unit leakage impedances than a two-winding transformer; this results in both smaller series ![image](/image/placeholder) A a 0 + VAB V an lp B b + + Vbn VBC C 6 C + + VCA cn V N Fig. 5 Three-Phase A-Y Transformer ![image](/image/placeholder) A a + + VAB V ab B b + + Vbc VBC C C + + VCA Fig. 6 Three-Phase △-△ Transformer ![image](/image/placeholder) /2 1x=4 +/2 태=E1 +E2 Ex = E1 Fig. 7 Typical Autotransformer Inc. ASHRAE, 2019 user. single for Licensed | {}
ed449798-a1b7-42c1-92a9-b80ce76667b1 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 57.4 2019 ASHRAE Handbook-HVAC Applications (SI) voltage drops and higher short-circuit currents. It also has lower per- unit losses, lower excitation current, and lower cost, ifthe turns ratio is not large. An autotransformer is not isolated as well as a typical two-winding transformer; transient overvoltages pass through the autotransformer more easily because the windings are connected electrically. Transformer Coolants and Insulators. Because heat is created by the flow of electrical current through the windings, a liquid (e.g., oil or silicone) is often used as a coolant inside the transformer. Such liquids are also good electrical insulators for the wire windings and iron core. Dry transformers do not require a liquid for cooling, instead using ambient air for cooling as well as insulation. Dust, dirt, moisture, and other contaminants in the air can reduce its insu- lating capabilities and deteriorate exposed parts, and may cause pre- mature failure of the transformer. Emergency and Standby Power Systems Emergency Power Systems. IEEE Standard 446-1995 defines these systems as independent reserves of electrical power that auto- matically take over if the usual supply experiences an outage or fail- ure, and sustain mission-critical systems (i.e., those that, if inoperable, could present a danger to health and safety, or to prop- erty). Local or national codes may also mandate specific systems as required emergency power systems. Standby Power Systems. Generally, these systems provide power back-up for loads that may be critical to production or prod- uct preservation, but do not present a danger to life or safety. They allow facilities to carry on with satisfactory operation during failure or outage of the usual supply source. NFPA Standard 70 distin- guishes between those that are legally required and those that are optional. Emergency and Standby Power Supplies. Diesel generators are still the dominant source of emergency power, particularly for emergency loads such as fire pumps or elevators that require large starting currents and must meet the outage's full capacity at start-up. Some natural gas engines meet the start-up requirements for emer- gency systems, and are popular for smaller standby applications such as homes, communication towers, and other operations where diesel fuel is undesirable and/or impractical. Some turbines are also used for standby service, but most turbines are dedicated to com- bined heat and power (CHP) applications (see Chapter 7 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment). The use and constraints of emergency and standby power sys- tems must be understood to ensure proper safety and operation of the electrical equipment they support. This is especially true with emergency systems and with standby systems that are expanded to carry the full facility load, including HV AC&R systems. Starting and load step capabilities also must be understood when replacing diesel engines with natural gas engines and turbines, which have very different acceptable load step characteristics. Most codes require emergency generators used for life-safety loads to be online within 10 s. However, age, battery wear, and even improper exercising ofthe engine can cause delays and even failures to start. Even if the engine does start within 10 s, some type of ride- through device may be required to support electronic loads (includ- ing computers and energy management systems) until the generator starts and picks up the load. National mandates on emissions, and state and local implemen- tation of those mandates, also influence the generator type speci- fied. In the United States, Environmental Protection Agency (EPA) tier ratings are required for off-road engine permits, including for generators. U.S. EPA (2012) addresses emissions of oxides of nitro- gen (NOx), hydrocarbons (HC), particulate matter (PM), and carbon monoxide (CO). Earlier tier ratings limited diesel use to emergency applications in most cases, but the new tier 4 ratings allow their use for standby and CHP applications. Another variable that must be considered with all generation equipment are the potential derates caused by elevation and weather. Combustion air has a direct effect, but of varying degrees, on the energy that can be generated during combustion. W ays to overcome theses derates include precooling or humidifying the combustion air. It is important to find out from a manufacturer what the derating characteristics are and the cost in equipment and con- sumables for any correction system selected. Uninterruptible power supply (UPS) units are most com- monly used to keep computers and controls running during the tran- sition from outage to generator operation. Batteries are sized to meet the load requirement for a specified period of time (frequently about 15 min). The UPS provides power through the interruption and, if generators fail to start, provides enough time for orderly sys- tem shutdown. Flywheel technology is gaining ground where larger (e.g., whole-building) loads are supported. The flywheels are also sized for time and load, but may be cost prohibitive for orderly shutdown and even for engines that do not start until the second or third try (20 to 30 s). They are only rarely used to support a natural gas engine that may take between 1 to 3 min to start. Impedance of emergency and standby power supplies is usually higher than that of utility electric service. Thus, power quality of a circuit typically deteriorates when it is switched from regular utility power to emergency power. A key component of the emergency generator system is the auto- matic transfer switch (ATS) used to switch from the primary source (usually the utility) to the secondary source (usually the generator). The type of switch selected has important ramifications to the over- all electrical system. The types of automatic transfer switches are as follows: Standard ATS (Figure 8) · Break- (from one source) before-make (to another source) design. · Mechanically interlocked electrical contactors move loads from one power source to another. · Most can optionally be equipped for delayed transition (switch delays in the neutral position for a preset number of seconds). This allows larger (>37 kW) motors' residual voltage to decay be- fore connection to the other source. Other timers are usually avail- able to provide ride-through for one or two recloser operations (used by utilities to keep their system operational during momen- tary faults caused by falling limbs, high winds, etc.). · An in-phase monitor can be preset and used in conjunction with or in place of the delayed transition to protect large motors during the transfer process. · Can be two-, three- or four-pole, depending on phase and ground- ing scenario. · Results in at least two momentary power outages: when utility service is lost and when the system switches back to the utility. Closed-Transition ATS (Figure 9) · Provides momentary (less than six cycles) connection of load to both power sources within acceptable phase angle for seamless transfer when both sources are available. ![image](/image/placeholder) UTILITY LOAD GENERATOR Fig. 8 Break-Before-Make Design for Standard ATS Inc. ASHRAE, 2019 user. single for Licensed | {}
efd10b29-1e7b-49f3-ae21-d71c4b81d529 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Electrical Considerations 57.5 ![image](/image/placeholder) UTILITY LOAD GENERATOR Fig. 9 Closed-Transition ATS UTILITY LOAD GENERATOR Fig. 10 Parallel-Transfer Switch · Eliminates the second outage associated with a standard ATS and, in some cases, can be used to operate the generator as a peaking power source. Bypass-Isolation ATS · Same as a standard ATS except for its separate bypass mechanism to allow continuation of power to the load from either source while isolating the automatic switch device for maintenance or repair. Typically, the automatic portion of the switch can be mechanically isolated from the frame during this process. · All other features of the standard ATS apply. · Closed-transition and bypass-isolation can be combined to pro- vide the capabilities of both. Service-Entrance-Rated ATS · Transfer switch includes a circuit breaker or fused device ahead of the transfer mechanism, allowing the device to act as the service- entrance point for building load. · Fused protection can also be provided ahead of the secondary (generator) entrance point, but is normally omitted in lieu of locating the protection (circuit breaker) at the generator set. · Can include any or all of the other ATS features listed in standard, closed-transition, or bypass-isolation types. Parallel-Transfer (PT) Switch (Figure 10) · Parallel switchgear in a simple one- or two-breaker design allows for parallel connection of the load to both power sources for an indefinite time period. · Should include all protective relay devices as required by the local utility and generator supplier. · Can include some of the features of a standard ATS, because most can also be operated as an open-transfer (break-before-make) switch. Switch selection can profoundly affect the electrical system, especially if an existing back-up system is upgraded for an ex- panded role. For example, it may be necessary to completely replace the existing switchgear of a building if an original generator system with a small generator and a standard ATS is replaced with a larger generator and a closed-transition ATS. If the emergency power system is being expanded to include large motor loads, such as chillers, then · Set delay to account for chiller motor back current to dissipate. · Size the generator set large enough to handle the motor loads' starting current requirements. The electrical engineer needs to know the starting requirements and maximum allowable voltage drop that the overall electrical system can handle, especially com- puter and control loads. Most major generator manufacturers can provide sizing software. If a standard ATS is being replaced with a closed-transition or parallel-transfer switch, · Verify that the existing switchgear can handle the added potential fault current of the generator set. For instance, if the available fault current from the utility is 65 000 A and the generator fault current is 30 000 A, then the system only has to be braced for 65 000 A with a standard ATS. It has to be braced for 95 000 A with either of the other two switches because fault current is addi- tive with multiple sources connected at the same time. Ifthe emergency power system is being converted from diesel to natural gas, then · Check the acceptable load steps of the new engine: the diesel likely accepted 100% load, but the natural gas engine may be lim- ited to as low as 20% load. Chillers and other large loads fre- quently exceed the acceptable load increase. · Determine whether large-motor-load starting systems can be changed to reduce starting requirements and meet acceptable load steps. Ifthe emergency system is being modified for peaking or curtail- ment uses, then · Obtain the specific utilities' interconnection requirements; these tend to be utility-specific and may exceed normal NEC or local codes. · Check the existing system for closed-transition or parallel- transfer switch issues and compatibility. · Investigate emissions issues; standby emissions permit require- ments are almost always less stringent than peaking requirements. Ifthe emergency system includes a UPS or flywheel system, then · Size the UPS or flywheel for the maximum required load for a specific time; remember that capacity of these systems is x kW for y min. · Avoid motor loads as much as possible. Motors Motor Control and Protection. Chapter 45 ofthe 2016 ASHRAE Handbook-HVAC Systems and Equipment addresses motor control and protection in detail, but is summarized and simplified here. Motor control must be effective without damaging the motor or its associated equipment. Control must be designed to prevent inadver- tent motor starting caused by a fault in the control device. The con- trol should be able to sense motor conditions to keep the motor windings from getting too warm. Motor protection involves sensing motor current and line voltage, and can include bearing vibration, winding temperature, bearing temperature, etc. Motor temperature increase has two basic sources. Heating occurs when dirt or debris blocks airflow over or through the motor, or it comes from the motor current and is commonly referred to as I2R, where Iis motor current and R is motor winding resistance. Because the current is squared, its contribution is exponential. R is quite small and contributes a linear function to heating (and therefore temperature rise) in the motor. Motor windings can withstand tem- perature rise, depending on the motor winding temperature rating. The second source of motor temperature increase is lack of motor cooling. The primary source of cooling is moving air, usually from a shaft-driven fan. As a motor slows down, the fan runs more slowly; therefore, the less air movement, the less cooling. Because fan loads are also exponential, a small decrease in motor speed greatly reduces airflow on the motor, reducing cooling. To compound the issue, the slower the motor runs, the greater the slip, and the greater the motor current. This then becomes a vicious circle. Inc. ASHRAE, 2019 user. single for Licensed Motor Starters and Thermal Overloads. Motor starters energize (start), deenergize (stop), protect, and control the motor. They sense | {}
084ea43e-2b6a-493a-b7b1-359f1249cd3b | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 57.6 2019 ASHRAE Handbook-HVAC Applications (SI) motor current based on a time curve: the shorter the time, the more current they let through. They may also limit the number of motor starts in a given period of time so the motor does not exceed its ANSI rating. Another cause for concern is the starter's ambient tem- perature: if it is different from the ambient temperature around the motor controller, the thermal overloads need to be sized accord- ingly. Several motor starter types are available, and they can function several different ways. The across-the-line starter is the simplest but may disturb electric service because of high motor-starting current requirements. Other starters reduce and may eliminate trou- blesome electrical disturbance; for instance, the part-winding, reduced-voltage, and wye-delta starters all act by reducing the starting voltage on the motor. Fan and pump loads can usually be started this way; this reduces starting current draw and demand, but sacrifices motor starting speed. Soft-start starters also reduce the voltage and limit demand during starting, thereby easing stress on the electric system during motor starting. Variable-frequency drives (VFDs) are also used to soft-start a motor, and are designed to control acceleration during starting as well as optimize motor speed to its load. See the section Motor-Starting Methods for more information. A VFD converts ac to dc and then back to variable-frequency, variable-voltage ac. Motor speed is varied by varying the frequency of the ac output voltage, typically using pulse-width modulation (PWM). This power conversion process results in distorted input current and may contribute to building power system voltage distor- tion. When motors and other loads are supplied from a distorted voltage source, their operating temperatures may rise. Phase Loss Protection. Phase loss can be detected by sensing either voltage loss or current loss on one of the phases. Motor over- loads often are set based on the nameplate data of the motor, but the real motor current draw is less because the motor may not be fully loaded. If one of three phases is lost, the current increases in the other two phases, but not by enough to trip the overloads. However, it will overheat and possibly damage the motor. Some phase loss detectors also check phase current to be sure that it is balanced within 10%. This protects the motor and makes the operator aware of potential motor or line problems. Motor-Starting Effects. The following effects do not occur with all motors. For instance, brushless dc and inverter-driven motors, which are electronically controlled, do not have inrush currents that cause light dimming or sags. Light Dimming or Voltage Sags. Light dimming or voltage sag associated with motor starts can be more than a nuisance. Motors have the undesirable effect of drawing several times their full-load current while starting. This large current, by flowing through system impedances, may cause voltage sag that can dim lights, cause con- tactors to drop out, and disrupt sensitive equipment. The situation is worsened by an extremely poor starting displacement factor, usually in the range of 15 to 30%. If the motor-starting-induced voltage sag deepens, the time required for the motor to accelerate to rated speed increases. Excessive sag may prevent the motor from starting suc- cessfully. Motor-starting sags can persist for many seconds. The Illuminating Engineering Society ofNorth America (IESNA) is precise in describing lighting reactions. Dimming is an intentional technique to enhance the ambiance of surroundings by varying the perceived lighting levels. Itis also used to reduce the electrical power used by lamps when adequate natural lighting is available; the controller electronically follows the natural variations in a way that will not be optically perceived. Similarly, flicker is deliberately selected in some lamps to resemble a candle s flame. In contrast, this chapter discusses possible causes of undesirable, perceptible reduc- tions of a lamp's lumen output. Momentary undesirable lighting reductions from voltage sags, often caused by motor starting, were common with incandescent lamps. More efficient lamps (especially fluorescent and electronic ballasts) are now the most common for most applications. For fluo- rescent lamps, electronic ballasts convert the 60 Hz electrical ser- vice to much higher frequencies, which eliminates perception of irritating flicker, and provides greater lumens per watt than the for- mer magnetic ballasts. Similar improvements have occurred for mercury, metal halide, and sodium lamps, typically found in large stores, sports, and industrial applications. Including electronic cir- cuitry in the lamps and lighting systems makes power quality even more important for building owners: electronic components are sen- sitive to both lower and upper threshold voltages, and the building's voltage may experience momentary voltage sag as large motors start. Specific product literature for lamps, lamp ballasts, and light- ing controls should be reviewed to ensure client satisfaction with expected operations (starts, stops, and speed changes) ofthe HVAC system s motors and controls. Motor-Starting Methods. The following motor-starting meth- ods can reduce voltage sag from motor starts. An across-the-line start, energizing the motor in a single step (full-voltage starting), provides low cost and allows the most rapid acceleration. It is the preferred method unless the resulting voltage sag or mechanical stress is excessive. Autotransformer starters have two autotransformers connected to open delta (similar to a delta connection using three single-phase transformers, but with one transformer removed; carries 57.7% of a full delta load). Taps provide a motor voltage of 80, 65, or 50% of system voltage during start-up. Starting torque varies with the square of the voltage applied to the motor, so the 50% tap delivers only 25% of the full-voltage starting torque. The lowest tap that will supply the required starting torque is selected. Motor current varies as the volt- age applied to the motor, but line current varies with the square of the tap used, plus transformer losses of ~3%. Resistance and reactance starts initially insert impedance in series with the motor. After a time delay, this impedance is shorted out. Starting resistors may be shorted out over several steps; starting reactors are shorted out in a single step. Line current and starting torque vary directly with the voltage applied to the motor, so for a given starting voltage, these starters draw more current than the line with autotransformer starts, but provide higher starting torque. Reactors are typically provided with 50, 45, and 37.5% taps. Part-winding starters are attractive for use with dual-rated motors (220/440 v or 230/460 V). The stator of a dual-rated motor consists of two windings connected in parallel at the lower voltage rating, or in series at the higher voltage rating. When operated with a part-winding starter at the lower voltage rating, only one winding is energized initially, limiting starting current and torque to 50% of the values seen when both windings are energized simultaneously. Delta-wye starters connect the stator in wye for starting, then after a time delay, reconnect the windings in delta. The wye connec- tion reduces the starting voltage to 57% of the system line-line volt- age, starting current and starting torque are reduced to 33% of their values for full voltage start. Utilization Equipment Voltage Ratings Utilization equipment is electrical equipment that converts elec- tric power into some other form of energy, such as light, heat, or mechanical motion. Every item of utilization equipment should have a nameplate listing, which includes, among other things, the rated voltage for which the equipment is designed. In some cases, the nameplate also indicates the maximum and minimum voltage for proper operation. With one major exception, most utilization equip- ment carries a nameplate rating that is the same as the voltage system on which it is to be used: that is, equipment to be used on 120 V sys- tems is rated 120 V. The major exception is motors and equipment containing motors, where performance peaks in the middle of the Inc. ASHRAE, 2019 user. single for Licensed | {}
e4b5ce4b-477c-4683-8585-490a8bbeb96c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Electrical Considerations 57.7 ![image](/image/placeholder) 414 V MOTOR VOLTAGE 460 V 土 10% 506 V 456 V UTILITY VOLTAGE 480 V ± 5% 504 V 207 V MOTOR VOLTAGE 230 V ± 10% 253 V 228 V UTILITY VOLTAGE 240 V ± 5% 252 V 180 V MOTOR VOLTAGE 200 V ± 10% 220 V 198 V UTILITY VOLTAGE 208 V 土 5% 218 V Fig. 11 Utilization Voltages Versus Nameplate Ratings tolerance range of the equipment: better performance can be obtained over the tolerance range specified in ANSI Standard C84.1 by selecting a nameplate rating closer to the middle of this tolerance range. The difference between the nameplate rating of utilization equipment and the system nominal voltage is necessary because the performance guarantee for utilization equipment is based on the nameplate rating and not on the system nominal voltage. The voltage tolerance limits in ANSI Standard C84.1 are based on ANSI/NEMA Standard MG 1, Motors and Generators edition, which establishes voltage tolerance limits of the standard low- voltage induction motor at ±10% of nameplate voltage ratings of 230 and 460 V. Because motors represent the major component of utilization equipment, they were given primary consideration in the establishment of this voltage standard. Figure 11 compares utiliza- tion voltages to nameplate ratings. v oltage Level Variation Effects Whenever voltage at the terminals of utilization equipment var- ies from its nameplate rating, equipment performance and life expectancy change. The effect may be minor or serious, depending on the equipment characteristics and the amount of voltage devia- tion from the nameplate rating. NEMA standards provide tolerance limits within which performance will normally be acceptable. In precise operations, however, closer voltage control may be required. In general, a change in the applied voltage causes a proportional change in the current. Because the effect on the load equipment is proportional to the product of the voltage and the current, and because the current is proportional to the voltage, the total effect is approximately proportional to the square of the voltage. However, the change is only approximately proportional and not exact: the change in the current affects the operation of the equip- ment, so the current continues to change until a new equilibrium position is established. For example, when the load is a resistance heater, the increase in current increases the heater temperature, which increases its resistance and, in turn, reduces the current. This effect continues until a new equilibrium current and temperature are established. In the case of an induction motor, a voltage reduction reduces the current flowing to the motor, causing the motor to slow down. This reduces the impedance of the motor, increasing the cur- rent until a new equilibrium position is established between the current and motor speed. V oltage Selection Generally, the preferred utilization voltage for large commercial buildings is 480Y/277 V, three-phase. The three-phase power load is connected directly to the system at 480 V, and fluorescent ceiling lighting is connected phase-to-neutral at 277 V. Dry-type trans- formers rated 480 V/208Y/120 V are used to provide 120 V single phase for convenience outlets and 208 V three phase for other building equipment. Single-phase transformers with secondary rat- ings of 120/240 v may also be used to supply lighting and small office equipment. However, single-phase transformers should be connected in sequence on the primary phases to maintain balanced load on all phases of the primary system. Where the supplying utility furnishes the distribution transform- ers, the choice of voltages is limited to those the utility provides. For tall buildings, space will be required on upper floors for transformer installations and the primary distribution cables supplying the trans- formers. Apartment buildings generally have the option of using either 208Y/120 V three-phase/four-wire systems, or 120/240 V single-phase systems, because the major load in residential occu- pancies consists of 120 V lighting fixtures and appliances. The 208Y/120 V systems are often more economical for large apartment buildings. Single-phase 120/240 V systems should be satisfactory for small apartment buildings and other small buildings. However, large single-phase appliances, such as electric ranges and water heaters rated for use on 120/240 V single-phase systems, will not perform to the rated wattage on a 208Y/120 V systems, because the line-to-line voltage is appreciably below the rated volt- age of the appliance. 5. POWER QUALITY VARIATIONS Power quality refers to varied parameters that characterize the voltage and current for a given time and at a given point on the electric system. A power quality problem is usually any variation in the volt- age or current that actually results in failure or misoperation of equip- ment in the facility. Therefore, power quality evaluations are a function of both the power system characteristics and the sensitivity of equipment connected to the power system. This section defines the different kinds of power quality varia- tions that may affect equipment operation. Important reasons for categorizing power anomalies include the following: · Identifying the cause of the power anomalies. Understanding the characteristics of a power quality variation can often help identify the cause. · Identifying the possible effects on equipment operation. A tran- sient voltage can cause failure of equipment insulation; a sag in voltage may result in dropout of sensitive controls based on an undervoltage setting. · Determining the requirements for measurement. Some power quality variations can be characterized with simple voltmeters, ammeters, or strip chart recorders. Other conditions require special-purpose disturbance monitors or harmonic analyzers. · Identifying methods to improve the power quality. Solutions depend on the type of power quality variation. Transient distur- bances can be controlled with surge arrestors, whereas momen- tary interruptions could require an uninterruptible power supply (UPS) system for equipment protection. Harmonic distortion may require special-purpose harmonic filters. Power quality can be described in terms of disturbances and steady-state variations. Disturbances. Disturbances are one-time, momentary events. Measurement equipment can characterize these events by using thresholds and triggering when disturbance characteristics exceed specified thresholds. Examples include transients, voltage sags and swells, and interruptions. Steady-State Variations. Changes in long-term or steady-state conditions can also result in equipment misoperation. High har- monic distortion levels can cause equipment heating and failure, as can long-term overvoltages or unbalanced voltages. These are vari- ations best characterized by monitoring over a longer period oftime with periodic sampling of the voltages and currents. Steady-state variations are best analyzed by plotting trends of the important quantities (e.g., RMS voltages, currents, distortion levels). These two types ofpower quality are further defined in seven ma- jor categories and numerous subcategories. There are three primary Inc. ASHRAE, 2019 user. single for Licensed | {}
f0d2c36c-d02a-4e19-bcf2-8f5014f52936 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 57.8 attributes used to differentiate among subcategories within a power quality category: frequency components, magnitude, and duration. These attributes are not equally applicable to all categories. For in- stance, itis difficult to assign a time duration to a voltage flicker, and it is not useful to assign a spectral frequency content to variations in the fundamental frequency magnitude (sags, swells, overvoltages, undervoltages, interruptions). Each category is defined by its most important attributes for that particular power quality condition. These attributes are useful for evaluating measurement equipment requirements, system charac- teristics affecting power quality variations, and possible measures to correct problems. The terminology has been selected to agree as much as possible with existing terminology used in technical papers and standards. The following descriptions focus on causes of the power quality variations, important parameters describing the variation, and ef- fects on equipment. Inc. Transients Transients are probably the most common disturbance on distri- bution systems in buildings and can be the most damaging. Tran- sients can be classified as impulsive or oscillatory. These terms reflect the waveshape of a current or voltage transient. ASHRAE, 2019 user. Impulsive Transient. An impulsive transient (spikes or notches) is considered unidirectional; that is, the transient voltage or current wave is primarily of a single polarity (Figures 12 and 13). Impulsive transients are often characterized simply by magnitude and duration. Another important component that strongly influences the effect on many types of electronic equipment is the rate of rise, or rise time of the impulse. This rate of rise can be quite steep, and can be as fast as several nanoseconds. Repetitive subtractive transients (Figure 13), often caused by thyristors such as silicon controlled rectifiers (SCRs), are referred to as voltage notches. single The high-frequency components and high rate ofrise are import- ant considerations for monitoring impulses. Very fast sampling rates are required to characterize impulses with actual waveforms. In many power quality monitors, simple circuits are used to detect the transient's peak magnitude and duration (or volt-seconds). If for Licensed Fig. 12 Example of Spike Fig. 13 Example of Notch impulse waveshapes are recorded, they usually do not include the fundamental frequency (60 Hz) component. When evaluating these disturbances, itis important to remember that stress on equipment is based on the impulse magnitude plus the magnitude of the funda- mental component at the instant of the impulse. The voltage, current available, and pulse width determine the amount of energy available in a transient. 2019 ASHRAE Handbook- -HVAC Applications (SI) Oscillatory Transient. An oscillatory transient (Figure 14) is a voltage or current that changes polarity rapidly. Because the term "rapidly" is nebulous, the frequency content is used to divide oscillatory transients into three subcategories: high, medium, and low frequency. Frequency ranges from these classifications are chosen to coincide with common types of power system oscillatory transient phenomena. As with impulsive transients, oscillatory transients can be mea- sured with or without including the fundamental frequency. One way to trigger on transients is to continually test for deviation in the waveform from one cycle to the next. This method records any devi- ation exceeding the set threshold. When characterizing the tran- sient, it is important to indicate the magnitude with and without the 60 Hz fundamental component. Transients are generally caused by a switching event or by sys- tem response to a lightning strike or fault. The oscillations result from interactions between system capacitances and inductances, and occur at the natural frequencies of the system excited by the switching event or fault. High-frequency transients can occur at locations very close to the initiating switching event. Rise times created by closing a switch can be as fast as a few tens of nanoseconds. Short lengths of circuit have very high natural oscillation frequencies that can be excited by a step change in system conditions (e.g., operating a switch). Power electronic devices such as transistors and thyristors/SCRs can cause high-frequency transients many times during each cycle of the fun- damental frequency. The transients can be in the tens or hundreds of kilohertz, and occasionally higher. Because of the high frequencies involved, circuit resistance typi- cally damps transients out; thus, they only occur close (within tens to hundreds of metres) to the site of the switching event that generates them. Characterizing these transients with measurements is often difficult because high sampling rates are required. Medium-frequency transients are associated with switching events with somewhat longer circuit lengths (resulting in lower natural frequencies). Switching events on most 480 v distribution systems in a facility cause transient oscillations within this fre- quency range, which can propagate over a significant portion of the low-voltage system. Motor interruption (definite interruption) is a good example of a common switching event that can excite tran- sients in this frequency range. Fig. 14 Example of Oscillatory Transient Transients coupled from the primary power system (e.g., coupled through the step down transformer) can also cause medium- frequency transients. The most common cause of transients on the primary power system is capacitor switching. | {}
a83ca046-9692-4f0f-99f9-206c73b26fdb | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Electrical Considerations 57.9 Capacitor energizing results in an initial step change in the volt- age, which gets coupled through stepdown transformers by the transformer capacitance and then excites natural frequencies of the low-voltage system (typically 2 to 10 kHz). Low-frequency tran- sients are usually caused by capacitor switching, either on the primary distribution system or within the customer facility. Lower- frequency transients result from capacitance of the switched capac- itor bank oscillating with the inductance of the power system. The natural frequencies excited by these switching operations are much lower than those of the low-voltage system without the capacitor bank, because of the large capacitance of the capacitor bank itself. Capacitor switching operations are common on most distribution systems and many transmission systems. Energizing a capacitor results in an oscillatory transient with a natural frequency in the range of 300 to 2000 Hz (depending on the capacitor size and the system inductance). The peak magnitude of the transient can ap- proach twice the normal peak voltage (per unit), and lasts between 0.5 and 3 cycles, depending on system damping. Isolation transformers, voltage arresters, and/or filters can re- duce transients. Short-Duration Variations Short-duration voltage variations are momentary changes in the fundamental voltage magnitude. Common causes are faults on the power system (short circuits between phases or from phase to ground). Depending on the fault location and system conditions, the fault can cause either momentary voltage rises (swells) or momen- tary voltage drops (sags). The fault condition can be close to or remote from the point of interest. Sags. Sags (Figure 15) are often associated with system faults but can also be caused by switching heavy loads or starting large motors (usually a longer-duration variation). Figure 15 shows a typ- ical voltage sag that can be associated with a remote fault condition. For instance, a fault on a parallel feeder circuit (on the primary dis- tribution system) results in a voltage drop at the substation bus that affects all of the other feeders until the fault is cleared by opening a fuse or circuit breaker. The percent drop in the RMS voltage magnitude and duration of the low-voltage condition are used to characterize sags. Voltage sags are influenced by system characteristics, system protection practices, fault location, and system grounding. The most common problem caused by voltage sags is tripping sensitive controls (e.g., adjustable-speed drives or process controllers), relays or contactors dropping out, and failure of power supplies to ride through the sag. Many types of voltage regulators are not fast enough to provide voltage support during sags, but ferroresonant transformers and some other line conditioners can provide some ride-through capa- bility or can quickly compensate for deep sags. In practice, sags are the type of power quality variation that most frequently causes problems. Fault conditions remote from a partic- ular customer can still cause voltage sags that can cause equipment problems. Because there are no easy ways to eliminate faults on the power system, it is always necessary for customers to consider the effects of sags. Fig. 15 Example of Sag Swells. Swells or surges can also be associated with faults on the primary distribution system (Figure 16). They can occur on nonfau- lted phases when there is a single-line-to-ground fault. Swells are characterized by their magnitude (RMS value) and duration. The severity of a voltage swell is a function of fault loca- tion, system impedance, and grounding. On a three-phase un- grounded system (delta), the line-to-ground voltages on the ground phases are 1.73 per unit (i.e., 1.73 times the normal line-to-ground voltage) during a single-line-to-ground fault condition. Close to the substation on a grounded system, there is no voltage rise on the ground phases because the substation transformer is usually delta- wye, providing a low-impedance path for the fault current. Long-Duration Variations Long-duration RMS voltage deviations generally do not result from system faults. They are caused by load changes on the system and system switching operations. The duration of these voltage variations depends on the operation of voltage regulators and other types of voltage control on the power system (e.g., capacitor con- trols, generator exciter controls). The time required for these volt- age controllers to respond to system changes ranges from large fractions of a second to seconds. Long-duration variations can be overvoltages or undervoltages, depending on the cause of the vari- ation. Voltage unbalance should be considered when evaluating steady-state or long-duration voltage variations. Unbalanced volt- ages can be one of the major causes of motor overheating and failure. With increasing emphasis on energy-efficient motors, re- quirements for voltage balance (i.e., limitations on negative sequence voltage magnitudes) may become even more important. Overvoltages. Overvoltages (Figure 17) can result from load switching (e.g., switching off a large load), variations in system gen- eration, or variations in reactive compensation on the system (e.g., switching a capacitor bank on). These voltages must be evaluated against the long-duration voltage capability of loads and equipment on the system. For instance, most equipment on the power system is only rated to withstand a voltage 10% above nominal for any length of time. Many sensitive loads can have even more stringent voltage requirements. Long-duration overvoltages must also be evaluated with respect to the long-time overvoltage capability of surge arresters. Metal oxide variation (MOV) arresters in particular can overheat and fail due to high voltages for long durations (e.g., seconds). Fig. 16 Example of Swell (Surge) Fig. 17 Example of Overvoltage Inc. ASHRAE, 2019 user. single for Licensed | {}
9a33f0bf-cd01-424c-865e-9e336f77be2a | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 57.10 2019 ASHRAE Handbook HVAC Applications (SI) Fig. 18 Example of Undervoltage Overvoltages can be controlled with voltage regulation equip- ment either on the power system or in a customer's facility. This can include various tap-changing regulators, ferroresonant regulators, line power conditioners, motor-generator sets, and uninterruptible power supplies. Undervoltages. Undervoltages (Figure 18) have the opposite causes of overvoltages. Adding a load or removing a capacitor bank will cause an undervoltage until voltage regulation equipment on the system can bring the voltage back to within tolerances. Motor starting is one of the most common causes of undervolt- ages. An induction motor draws 6 to 10 times its full load current during starting. This lagging current causes voltage drops in the sys- tem impedance. If the started motor is large relative to the system strength, these voltage drops can result in a significant system un- dervoltage. The magnitude of this starting current decreases over a period ranging from 1 s to minutes, depending on the inertia of the motor and the load, until the motor reaches full speed. This type of undervoltage can be mitigated by using various starting techniques to limit the starting current and is largely self-corrected when the starting is completed. For more information, see the section on Motor-Starting Effects. Voltage Unbalance. Ideally, all phase-to-phase voltages to a three-phase motor should be equal or balanced. Unbalance be- tween the individual phase voltages is caused by unbalanced load- ing on the system and by unbalances in the system impedances. Voltage unbalance is an important parameter for customers with motors because most three-phase motors have fairly stringent lim- itations on negative-sequence voltage (a measure of voltage unbal- ance), which is generated in the motor by unbalances in supplied voltages. Negative sequence currents heat the motor significantly. Voltage unbalance limitations (and steady-state voltage require- ments in general) are discussed in ANSI Standard C84.1. The National Electrical Manufacturers Association (NEMA) developed standards and methods for evaluating and calculating voltage un- balance. Unbalance, as defined by NEMA, is calculated by the fol- lowing equation: Maximum deviation from average voltage % V oltage unbalance = 100 x Average voltage The motor derating factor caused by the unbalanced voltage curve from NEMA Standard MG 1 shows the nonlinear relationship between the percent of voltage unbalance and the associated derat- ing factor for motors (Figure 19). A balanced-voltage three-phase power supply to the motor is essential for efficient system operation. For example, a voltage unbalance of3.5% can increase motor losses by approximately 15%. Interruptions and Outages Interruptions can result from power system faults, equipment failures, generation shortages, control malfunctions, or scheduled maintenance. They are measured by their duration (because the voltage magnitude is always zero), which is affected by utility Chart Type: line (0) (1) (2) (3) (4) (5) item_01 1.0% 1.0% 0.9% 0.8% 0.8% 0.7% Fig. 19 Derating Factor Curve ![image](/image/placeholder) Fig. 20 Example of Momentary Interruption protection system design and the particular event causing the interruption. Interruptions of any significant duration can potentially cause problems with a wide variety of different loads. Computers, control- lers, relays, motors, and many other loads are sensitive to interrup- tions. The only protection for these loads during an interruption is a back-up power supply, a back-up generator (requires time to get started), or a UPS system (can constantly be online). Momentary Interruption. A typical momentary interruption (Figure 20) lasts less than 3 s and occurs during a temporary fault, when a circuit breaker successfully recloses after the fault has been cleared. Lightning-induced faults usually fall into this category un- less they cause a piece of equipment (e.g., transformer) to fail. Temporary Interruption. Temporary interruptions that last be- tween 3 s and 1 min result from faults that require multiple recloser operations to clear, or require time for back-up switching to reen- ergize portions of the interrupted circuit (e.g., automatic throwover switches). Power Failure/Blackout. Outages lasting at least 1 min (Fig- ure 21) are severe enough to be included in utility companies' reliability statistics. These failures are caused by fault conditions, maintenance operations that require repair crews, and emergency situations called blackouts. Solutions involve using either UPS systems or back-up genera- tors, depending on the critical nature of the load. UPS systems typ- ically can provide uninterrupted supply for at least 15 min (based on battery capacity). This covers all momentary and temporary inter- ruptions and provides sufficient time for an orderly shutdown. A UPS can be used in conjunction with a switching scheme involving multiple feeds from the utility to provide an even higher level ofreli- ability. Ifback-up power is required beyond the capability ofa UPS system, and multiple feeds are not realistic or adequate, then back- up generators are needed. On-site generators are typically used in these applications. Inc. ASHRAE, 2019 user. single for Licensed | {}
0589f720-ca7d-48d4-9a2f-d674d2e06c70 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Electrical Considerations 57.11 Brownout. A brownout is a long-term voltage reduction, usually of 3 to 5%. This is an intentional reduction to reduce load under emergency system conditions. Harmonic Distortion Harmonic distortion of the voltage waveform occurs because of the nonlinear characteristics of devices and loads on the power sys- tem. These nonlinear devices fall into one of three categories: · Power electronics · Ferromagnetic devices (e.g., transformers) · Arcing devices These devices usually generate harmonic currents, and voltage distortion on the system results from these harmonics interacting with the system impedance characteristics. Harmonic distortion is a growing concern for many customers and for the overall power sys- tem because of the increasing applications of power electronic equipment. In many commercial buildings, electronic (nonlinear), loads, such as variable-frequency drives, computers, and UPS sys- tems, may be dominant in the facility, especially as more buildings switch to electronic ballasts for fluorescent lighting. Harmonic distortion levels can be characterized by the complete harmonic spectrum with magnitudes and phase angles of each indi- vidual harmonic component. However, it is more common to use a single quantity, the total harmonic distortion (THD), to character- ize harmonic distortion of a particular waveform. It is important in general to distinguish between voltage distortion and current distor- tion because these quantities are handled differently in the standards and should be handled differently when performing measurements and interpreting data. Voltage distortion is caused by the harmonic current emissions of nonlinear devices interacting with the impedance characteristics of the power system. Harmonic current distortion results in elevated true RMS current, which increases I2R losses and elevated peak cur- rent. Because harmonics flow at frequencies higher than the funda- mental frequency (e.g., 180 Hz, 300 Hz, 420 Hz), additional losses are experienced because of the reduction of conductor effective cross-sectional area, a phenomenon known as skin effect. These losses are attributed to I2XL at each harmonic frequency. A particular concern is when resonance conditions on the power system magnify harmonic currents and high-voltage distortion lev- els. The natural resonance of the power system varies based on sys- tem inductance and capacitance and should be evaluated when adding nonlinear devices (equipment) or power factor capacitors to the system. Capacitors offer a low-impedance path to harmonic fre- quencies and can therefore attract harmonics, often resulting in reduced life, fuse blowing, or capacitor failure. Figure 22 illustrates the voltage waveform with harmonic content. Figures 23 and 24 illustrate distorted current waveforms. Harmonic distortion can be reduced by adding an ac line reac- tor or harmonic filter at the input of individual nonlinear loads (Figure 25). A 5% impedance line reactor typically reduces ![image](/image/placeholder) SUSTAINED INTERRUPTION Fig. 21 Example of Blackout or Power Failure Waveform Harmonic current distortion can be reduced to levels of 5 to 8% total harmonic current distortion, at the individual load, using a typ- ical low-pass harmonic filter (Figure 26). The benefit of reducing harmonics right at the contributing load is that the entire upstream power system benefits from reduced levels of current and voltage distortion. harmonic distortion for three-phase nonlinear loads to about 35% of the fundamental current. Voltage Notches. A voltage waveform with notches (see Figure 13) caused by operating power electronics, especially where SCRs are involved [e.g., adjustable-speed drives (ASDs)], can be con- sidered a special case that falls in between transients and harmonic distortion. Because notching occurs continuously (steady state), it can be characterized by the harmonic spectrum of the affected volt- age. However, frequency components associated with the notching can be quite high, and it may not be possible to characterize them with measurement equipment normally used for harmonic analy- sis. It is usually easier to measure with an oscilloscope or transient disturbance monitor. Three-phase SCR rectifiers (those typically in dc drives, UPS systems, ASDs, etc.) with continuous dc current are the most com- mon cause of voltage notching. The notches occur when the current ![image](/image/placeholder) Fig. 22 Example of Harmonic Voltage Distortion ![image](/image/placeholder) 1 0.9 0.8 0.7 0.6 0.5 0.4 0.3 0.2 0.1 0 1 5 7 11 13 17 A. THREE-PHASE INPUT WAVEFORM B. SPECTRUM Fig. 23 Example of Harmonic Current Distortion for Six-Pulse Rectifier with 5% Impedance Reactor ![image](/image/placeholder) Fig. 24 Example of Harmonic Current Distortion for One-Phase Input Current for Single Personal Computer Inc. ASHRAE, 2019 user. single for Licensed | {}
9a5b45c2-939c-4feb-9674-085c6ee9f764 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 57.12 2019 ASHRAE Handbook- HVAC Applications (SI) INPUT CURRENT WAVEFORM ![image](/image/placeholder) A M A Fig. 25 Example of VFD with ac Line Reactor ![image](/image/placeholder) INPUT CURRENT WAVEFORM Fig. 26 Example of VFD with Low-Pass Harmonic Filter Often, an isolation transformer or 3% impedance ac line reactor (inductor) can be used in the circuit to reduce the effect of notching on the source side. The additional inductance increases the severity of voltage notches at the rectifier terminals (commutation time, or width of the notch, increases with increased commutation reac- tance); however, most of the notching voltage appears across the ac inductor and notching is less severe on the source side, where other equipment shares a common voltage source. commutates from one phase to another on the ac side of the rectifier. During this period, there is a momentary short circuit between two phases. The severity of the notch at any point in the system is deter- mined by the source of inductance and the inductance between the rectifier and the point being monitored. Steep voltage changes caused by notching can also result in ring- ing (oscillation) because of capacitances and inductances in the sup- ply circuit. This oscillation can disturb sensitive controls connected to the affected circuit. The high frequencies involved can also cause noise be capacitively coupled to adjacent electrical or communica- tion circuits. Voltage Flicker Loads that vary with time, especially in the reactive component, can cause voltage flicker; the varying voltage magnitudes can affect lighting intensity. Arc furnaces are the most common cause of Fig. 27 Example of Flicker ![image](/image/placeholder) Fig. 28 Example of Electrical Noise voltage flicker. The envelope of the 60 Hz variations is defined as the flicker signal V, and its RMS magnitude is expressed as a percent- age of the fundamental. Voltage flicker is measured with respect to sensitivity of the human eye. A typical plot of the 60 Hz voltage envelope characterizing voltage flicker is shown in Figure 27. The characteristics of voltage flicker are mainly determined by load characteristics and the system short-circuit capacity. For a crit- ical load, it may be necessary to provide a dedicated feed so that it is not on the same circuit with a major load that causes voltage flicker. Using fast switching compensation, such as a static volt-ampere- reactive (V AR) system or dynamic VAR compensation system, can mitigate the problem. Another method is to effectively increase the short-circuit capacity at the point of common coupling with other loads by using a series capacitor. Protecting the series capacitor during fault conditions requires careful design. Voltage flicker appears as a modulation of the fundamental fre- quency (similar to amplitude modulation of an AM radio signal). Therefore, it is easiest to define a magnitude for voltage flicker as the RMS magnitude of the modulation signal, which can be found by demodulating the waveform to remove the fundamental fre- quency and then measuring the magnitude of the modulation. Typ- ically, magnitudes as low as 0.5% can result in perceptible light flicker if frequencies are in the range of 1 to 10 Hz. Flicker limita- tions are discussed in ANSI/IEEE Standard 146. Light dimming, another type of light flicker, is caused by starting motors. Large single- or three-phase motors, as used in air condition- ers, have the undesirable effect of drawing 6 to 10 times their full load current while starting. This large current, by flowing through system impedances, causes voltage sag that may dim lights. Noise Noise, a continuous, unwanted signal on the power circuits (Fig- ure 28), can have a wide variety of different causes (e.g., switching, arcing, electric fields, magnetic fields, radio waves) and can be cou- pled onto the power circuit in a number of different ways. The noise source and susceptible circuit can be coupled by electric or mag- netic fields or by electromagnetic interference (EMI). The frequency range and magnitude of noise depend on the source that produces the noise. A typical magnitude of noise mea- sured in the voltage is less than 1% of the RMS voltage magnitude. Inc. ASHRAE, 2019 user. single for Licensed | {}
02b52ee5-7a34-46a2-af81-ba025eafef2c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Electrical Considerations 57.13 Noise with enough amplitude disturbs electronic equipment such as microcomputers and programmable controllers. Some noise can be eliminated by using an isolation transformer with an electrostatic shield; other noise requires EMI filtering or line conditioners. Wir- ing and grounding practices also significantly affect the noise levels at particular loads. The appropriate method for controlling noise depends on the methods of coupling, frequency range of the noise, and susceptibility of the equipment being protected. Inductive (Magnetic) Coupling. Magnetic fields induce cur- rents in conductors. The magnetic fields are caused by current flow- ing in nearby power conductors, parts of circuits, data lines, or even building structure, and can be temporary or steady state. The actual coupled currents in power conductors and equipment conductors depend on exposure (length of conductor in the field), angle between conductor and field, and magnetic field strength. Conduc- tors carrying large currents and/or with large spacing between con- ductors can create strong 60 Hz magnetic fields that do not decay quickly with distance from the source. These fields can cause dis- tortion on CRT or TV screens, and may interfere with sensitive electronic (especially analog) devices such as radio-controlled equipment, energy and building automation systems, photoelectric sensors, test and measurement equipment, and data processing equipment. During building design, take steps to minimize genera- tion of strong magnetic fields, and to keep sensitive equipment well separated from these areas. Current flow in the power system ground can be an important cause of magnetic fields because the loop area between the supply conductor and the return path through the ground can be very large. Therefore, grounding techniques to minimize noise levels can help reduce magnetic field problems. To minimize interference, power conductors should always be physically separated from control cir- cuit conductors. Magnetic shielding can also help. Capacitive (Electrostatic) Coupling. Capacitive coupling between conductors results in coupling of transient voltage signals between circuits. Transient voltages with high-frequency compo- nents or high rates of rise are the most likely to be capacitively coupled between circuits (the coupling capability of a capacitor increases with frequency). Switch operations, arcing, lightning, or electrostatic discharge can cause these transients. Electric fields capacitively couple voltage between conductors. Strength is mea- sured in volts per metre and may range from very slight to many kilo- volts per metre. High magnitudes of capacitively coupled voltages can affect nor- mal operations of various types of electronic devices, or even cause discharges and damage. Possible solutions include applying shield- ing and coating, and improving design of power equipment to reduce the generation of high-transient-voltage conditions. To min- imize interference, power conductors should always be physically separated from control circuit conductors. Electromagnetic Interference (EMI). EMI refers to interfer- ence caused by electromagnetic waves over a wide range of fre- quencies. Many interference sources start out as either strongly magnetic or strongly electric, but within about half a wavelength the fields convert to a balanced ratio of electric and magnetic fields (an electromagnetic field). Transients such as electrostatic discharge, arcing, contacts, power electronic switching, fluorescent lighting, and lightning cause electromagnetic waves. Steady-state EMI can occur in the form of radio frequency interference (RFI) from micro- wave and radar transmissions, radio and TV broadcasts, corona of high-voltage transmission line, arc welding, and other sources that generate radio-frequency electromagnetic waves. Although RFI is not destructive, it can cause a variety of malfunctions of susceptible electronic equipment and can disturb microcomputers and pro- grammable controllers; the level of disturbance depends on the amount of RFI. Solutions include using appropriate shielding or fil- tering techniques. 6. BILLING RATES Equipment specifications state how much electricity is used, but the cost of that electricity is usually the determining factor in HV AC&R system design and equipment selection. Electricity tar- iffs or rates set prices for · How much electricity is used; energy (MJ) · Rate at which electricity is used; demand (kW) · Quality of electricity used; power factor (VAR or kV AR) Electric rates are contracts defining what the electricity user will pay for the amounts consumed. Rates may be based on cost, policy, market, or a combination of cost/policy and market. Additionally, rates may be based on either kW or kVA demand. Designers should not assume that the types of rates will remain the same over the life of a building, and owner/operators should review with their utility about potential rate changes that might lower cost or improve reli- ability. Cost-Based Rates Cost-based rates are designed to charge each class of consumer based on the utility's cost to serve that class. Costs depend on mega- joules used, maximum demand, and time of day at which electricity is used. A customer class is a group of electricity consumers whose use characteristics are similar; each customer class has a different rate or tariff. Typical customer classes are residential, multifamily, small commercial, large commercial, small industrial, large indus- trial, electric water heating, electric space heating, street lighting, etc. Cost-based rates are usually predicated on the following assump- tions: · The more electricity a customer uses the less it costs, per mega- joule, to serve that customer. · The higher a customer's demand, the more it costs to serve that customer. · It costs less per megajoule to serve a customer with a higher load factor. Load factor LF is defined as the customer's average demand divided by the peak demand, or the energy consumed in the billing period divided by the peak demand times the number of hours in the billing period. [LF = MJ used in the billing period/ (peak demand x hours in billing period)] · It costs less for a utility to deliver electricity at times of low sys- tem load than at times ofhigh system load. Energy Charge. The consumer pays the utility a fixed amount for every megajoule used. Small customers, especially residential, often simply pay for energy used. Certain loads may have usage pro- files that allow the utility to provide electricity at times of low pro- duction costs (e.g., street lighting) or cost less per megajoule because the customer uses significantly more than a typical cus- tomer (e.g., electric space heating). These loads are often metered separately and are charged a lower cost per megajoule than general- service usage. Fuel Adjustment Clause (FAC). A significant part of the cost of electricity is the fuel needed to generate it. In the 1970s, the price of primary energy sources (especially oil) became extremely vola- tile, and the fuel adjustment clause was designed to accommodate this without requiring frequent rate adjustments. Energy charges with FACs consist of two parts: a fixed charge per megajoule and a variable charge per megajoule that depends on the average price of fuel purchased by the power generator. During periods oflow fossil fuel prices or high hydro runoff, for example, the FAC results in lower prices to the consumer. Many utilities embed part of the fuel cost in the rate tariffs and include the remaining variable portion in the FAC. Demand Charge. "Demand" is the maximum rate of use of elec- tricity. Itis expressed in kilowatts (kW) or kilovolt-amps (kVA) and is Inc. ASHRAE, 2019 user. single for Licensed | {}
214661d8-4e4b-41ce-9aa9-6cab88835b35 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 57.14 2019 ASHRAE Handbook-HVAC Applications (SI) typically measured over 15, 30, or 60 min periods. For example, 1 kWh used in 15 min is equal to 4 kW demand (1 kWh/0.25 h). Demand charges are designed to cover the system capacity cost to deliver energy to a customer and/or the marginal generation cost to produce electricity at time of highest usage. To deliver electricity to a consumer, a utility must install wires, transformers, and meters; the higher the customer's projected demand, the larger the capacity of wires and transformers serving the customer must be. From a system- wide perspective, the utility must also build enough generation and transmission capacity to serve the system load at its highest peak level. A noncoincident demand (NCD) charge is a charge per kilo- watt for the customer's maximum demand for electricity (in any 15, 30, or 60 min period) during the billing cycle. Noncoincident demand charges are generally imposed to cover the cost to transform and deliver energy to the consumer. A coincident demand (CD) charge (also known as a peak or on-peak demand charge) is a charge per kilowatt for the customer's maximum demand for electricity in any 15, 30, or 60 min period occurring during times of high system load. For example, in a summer-peaking utility, the demand charge may be applied only to the maximum demand occurring between 11:30 AM and 6:00 PM on weekdays from May to September. CD charges are designed to pay for additional generation and other system reinforce- ment costs needed to meet peak demands. Ratcheted Demand Charge. Demand charges may be calcu- lated based on the customer's maximum demand during each bill- ing cycle, or the maximum demand during the current or previous 11 months preceding the electricity bill. A high demand in one month "ratchets" the demand charge up for some or all of the fol- lowing 1 1 months. Seasonal Rate. Some utilities' generation costs vary signifi- cantly from one season to another. For example, spring runoff may yield more low-cost hydroelectric energy, or high summer air- conditioning loads may result in more power generation by less efficient peaking plants. A seasonally adjusted rate reflects this by setting different kilowatt and/or megajoule charges for different seasons. Time of Use (TOU) Rate. A utility's average production cost for electricity usually varies with the total system load. As demand in- creases, less efficient (i.e., more costly) generators are used. Increas- ing peak loads also require that a utility invest in greater generation, transmission, and distribution capacity to meet the peak. A TOU rate is designed to recover the increased production or capacity costs during times of system peak. Electricity use is recorded by multireg- ister meters and priced at different levels, depending on whether the peak/off-peak or peak/shoulder/off-peak model is used. TOU rates are usually designed not only to "recover" time-differentiated pro- duction costs, but also to induce consumers to shift their electricity usage from peak periods to times of lower system load. In this way, TOU rates are both cost-based and policy-based. Thermal energy storage (TES) systems are one method for consumers to reduce their on-peak demand or energy charges and to consume electricity during lower-cost, off-peak times. With TES, a consumer may use the same or more total electricity but will pay less for it. Declining Block Rate. In designing cost-based rates, the cost to serve is usually inversely proportional to the amount consumed. To reflect this, energy may be priced according to a declining block rate, where the cost per megajoule decreases as usage increases. For example, a residential customer may pay $0.033/MJ for the first 3000 MJ used in a month, $0.028/MJ for the next 2000 MJ, and $0.022/MJ for all electricity above 5000 MJ. Demand-Dependent Block Rate. For larger customers, the size of the blocks of a block rate may depend on the measured demand. For example, a commercial consumer may pay $0.033/MJ for the first 300 MJ per kilowatt of billing demand, $0.028/MJ for the next 550 MJ per kilowatt of billing demand, and $0.022/MJ for every MJ above 850 MJ per kilowatt of billing demand. Load Factor Penalty. Utilities recover their fixed costs (e.g., capital cost of a transformer) as well as production costs through energy (MJ) charges as well as demand charges. If a consumer' s load factor is less than expected, then the utility's megajoule revenues may not be sufficient to recover its fixed costs. This may occur for a customer with self-owned on-site generation who relies on the utility mainly when the on-site generator is being maintained. In this case, the utility may impose a load factor penalty or sur- charge. Power Factor Penalty. A power system is more efficient and sta- ble when all three phases are equally loaded (balanced) and serving pure resistive load (100% power factor). Some inductive loads, such as most lighting and motors, require reactive power, which may be more difficult and expensive for the utility to supply. Moreover, reactive power (kV AR) is not always measured, and therefore not billed, by typical megajoule meters. Therefore, utilities often impose a power factor penalty or surcharge on customers with very reactive or inductive loads (power factor not close to 100%) to pay for the VARs that it must supply. Customer Charge. This is a monthly, usually fixed charge that a consumer must pay, regardless of whether any electricity is used, for being a customer of a utility. This charge typically covers cus- tomer services such as the costs of billing, metering, and customer support services, such as call centers. Connection Fee. When electric service is initiated, especially when construction (additional distribution lines, substations, distribution transformers, etc.) is required, the utility may charge a connection fee. For example, a utility may charge a residential customer a fixed cost per metre of distribution line that must be constructed beyond an initial 150 m of line. Some customers may require redundant facilities to ensure reliable service (e.g., a sec- ond feeder and load transfer switch for a hospital). The utility would probably include such costs in its connection fee. Policy-Based Rates Policy-based rates are designed to encourage consumers to modify their energy use to better conform with the objectives of the utility or legislative or regulatory body (e.g., using nonpollut- ing or renewable energy sources, deferring grid expansion or generator construction by shifting electricity demand from peak periods, better using waste heat from industrial processes, etc.). It can be argued that some policy-based rates are in fact cost-based, but they incorporate "externalities, or external costs that cannot be directly allocated to a consumer's electricity use. The time of use rate could fall under either category. Inverted Block Rate. The marginal cost to provide an existing customer with additional energy decreases as energy use per kilo- watt of connected load increases. However, additional energy use often hastens the need to construct new generation facilities. An inverted block rate motivates the consumer to reduce energy use by charging less for the first megajoule used. For example, a resi- dential consumer may pay $0.022 for the first 3000 MJ per month, $0.028 for the next 1800 MJ, and $0.033 for all usage above 5000 MJ. As with the declining block rate, the break points be- tween "blocks" may be based on demand for that billing cycle. Lifeline Rate. Lifeline rates are designed so lower-income consumers will still be able to afford necessary electricity (e.g., enough for refrigeration, lights, adequate heat in winter, etc.). For example, a consumer pays a subsidized price per megajoule for a minimal amount of electricity and the market rate for any usage above the minimum (e.g., $0.01/MJ for the first 2500 MJ and $0.03/MJ for usage above 2500 MJ/month). Net Metering. This is applicable for consumers who own their own on-site generation, still buy electricity from the grid, but some- times can generate more electricity than is needed in their facility. Net metering is a contract in which the customer pays the utility for Inc. ASHRAE, 2019 user. single for Licensed | {}
e9ca3fcf-9dbe-4fca-911a-77ec62ccac0d | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Electrical Considerations 57.15 the net electricity purchased (i.e., excess on-site generation is sold to the grid and offsets what the customer owes the utility for purchases from the grid). Green Power Rate. Customers may sign up for blocks of elec- tricity produced by renewable sources, such as solar photovoltaic (PV) or wind turbines. Because electricity from such sources usu- ally costs more than electricity produced by conventional genera- tion, the green energy is sold at a premium. Surcharges. Government agencies may add special surcharges to electric bills to provide funding for specific energy-related or general-purpose programs. For example, in the United States, many state governments collect public benefit funds through electric bills to provide money for energy efficiency, renewable energy, low- income weatherization, and research programs. Other surcharges may be for power plant upgrades or putting electric distribution lines underground. Surcharges can be fixed or charged on a per- kWh basis. Some surcharges may be capped at a specific dollar amount per type of customer. Taxes. Government agencies may collect sales and other specific taxes through utility bills. The taxes may be calculated as a percent- age total of the entire bill, or on a per-kWh basis (such as $0.001 per kWh). For some customers, taxes and surcharges may comprise a significant portion of the total bill. Market-Based Rates Electric utilities are restructuring to disaggregate electricity production, transmission, and distribution and open the market to competition. The theory is that a competitive electricity sector, governed by market rules, is more efficient, lower cost, and more congruent with consumer needs than regulated electric utilities. Market-based rates are not new, but they are becoming more prev- alent. Rates tend to be volatile, and are structured as a contract between the consumer and energy supplier, rather than as a tradi- tional tariff. As a result, they tend to be more customer specific than uniform over a customer class. Real-Time Pricing (RTP). Under this scheme, the cost of elec- tricity varies with each hour. The supplier sets a price for electricity based on its forecasted cost to produce or provide the electricity. Hour-by-hour prices are communicated to the customer from 1 to 24 h in advance, and the consumer decides what, if any, action to take in response to the forecasted prices. The most common RTP programs send prices to consumers each evening, to cover the next day. Some programs send prices 4 h in advance, and several also allow 1 h alerts for "surprise" prices during system emergencies or forced outages. Consumers who were on a demand (kilowatt) and energy (MJ) rate often are billed only for energy use (MJ) on RTP, because the hourly energy cost incorporates the demand charge. The RTP may only apply to the generation portion of the electric bill if transmission and distribution charges are still regulated. Fixed Pricing. Some consumers in a deregulated market may opt for fixed prices for their electric supply. In these situations, the consumer may pay a price that is higher or lower than the RTP or spot prices. With this type of pricing, the burden of price risk goes to the supplier, who may charge a risk premium to the cus- tomer. Spot Pricing. Consumers in some regions may purchase some or all of their electricity on the spot market, based on the current mar- ginal cost of electricity. This is done through a power exchange, with the consumer either contracting directly with the exchange or going through a third-party electricity broker. Consumers may also purchase electricity through a combination of long-term contracts and spot market purchases. Interruptible Rates and Responsive Loads. At times of high marginal electricity costs, it may be more cost effective for a util- ity to pay its customers to reduce electricity consumption than to contract for additional electricity supplies. With interruptible rates, a consumer agrees to reduce power consumption to or below an agreed-upon level (or go off-line) when requested to do so by the utility, in return for a lower price. The utility's requests may be limited in number of times per year (or month) the consumer can be asked to reduce load, maximum duration of the load reduction, and minimum notice required (typically 1 to 4 h) before electric load is reduced. In other cases, there is no limit to the number or length of utility requests. Direct Load Control. This is similar to interruptible load, but instead of the consumer's complying with the utility's request, the utility can exercise direct control over the consumer's appliances. Appliances commonly contracted for load control programs are water heaters, swimming pool pumps, air conditioners, heat pumps, resistance space heat, and controllable thermostats for HVAC&R systems. The tariff usually is in the form of a monthly rebate or fixed bill credit for each controllable appliance. Performance-Based Rates. These are designed to ensure that the consumer receives acceptable quality and reliability of electric supply. The utility and consumer agree on a minimum standard for service quality in terms of number and duration of outages, voltage sags and swells, harmonic levels, or other transient phenomena. If these minimum service quality levels are not met, the utility must rebate money to the consumer; the amount rapidly increases as per- formance or service quality declines. In some cases, the rate, or type of rate charged, may not change, but customers receive bill credits or rebates based on a reduction in the electric company's rate of return. Performance Contracting. In performance contracting, a con- sumer contracts with a third party to pay for the end-use applica- tions of electricity. This usually involves an agreement where the performance contractor [often called an energy service company (ESCO)] installs and sometimes operates and maintains improved equipment for HVAC&R systems, lighting, building or process energy management, etc. The consumer's payments are indexed to successful equipment performance, which is often evaluated in terms of the facility's utility bills and calculated cost savings com- paring the actual energy costs with estimates of what the costs would have been without the ESCO' s intervention. A more detailed explanation of performance contracting is presented in ASHRAE Guideline 14-2002. 7. CODES AND STANDARDS NECⓇ The National Electrical CodeⓇ (NEC; NFPA Standard 70) is devised and published by the National Fire Protection Association, a consensus standards writing industry group. It is revised every three years. The code exists in several versions: the full text, an abridged edition, and the NEC Handbook (which contains the authorized commentary on the code, as well as the full text). It sets minimum electrical safety standards, and is widely adopted. UL Listing Underwriters Laboratories (UL), formerly an insurance industry organization, is now independent and nonprofit. It tests electrical components and equipment for potential hazards. When a device is UL-listed, UL has tested the device, and it meets their requirements for safety (i.e., fire or shock hazard). It does not necessarily mean that the device actually does what it is supposed to do. The UL does not have power of law in the United States; non-UL-listed devices are legal to install. However, insurance policies may have clauses that limit their liability in a claim related to failure of a non-UL-listed device. The NEC requires that a wiring component used for a spe- cific purpose is UL-listed for that purpose. Thus, certain components must be UL-listed before inspector approval and/or issuance of occu- pancy permits. Inc. ASHRAE, 2019 user. single for Licensed | {}
8bdc5bfb-fb03-4f3c-9ead-21380f6c492c | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 57.16 2019 ASHRAE Handbook- -HVAC Applications (SI) CSA Approved The Canadian Standards Association (CSA) is made up of various government agencies, power utilities, insurance companies, electrical manufacturers, and other organizations. They update CSA Standard C22.1, the Canadian Electrical Code (CEC), every two or three years. The Canadian Standards Association (or recognized equivalent) must certify every electrical device or component before it can be sold in Canada. Implicit in this is that all wiring must be done with CSA- approved materials. Testing is similar to UL testing (a bit more strin- gent), except that CSA approval is required by law. Like the UL, ifa fire is caused by non-CSA-approved equipment, the insurance com- pany may not pay the claim. ULC Underwriters Laboratory of Canada (ULC) is an independent organization that undertakes the quarterly inspection ofmanufactur- ers to ensure continued compliance of UL listed/recognized prod- ucts to agency reports and safety standards. This work is done under contract to UL, Inc.; they are not a branch or subsidiary of UL. NAFTA Wiring Standards Since the North America Free Trade Agreement (NAFTA) came into effect on January 1, 1994, CSA approval of a device is legally considered equivalent to UL approval in the United States, and UL listing is accepted as equivalent to CSA approval in Canada. De- vices marked only with UL approval are acceptable in the CEC, and CSA approval by itself of a device is accepted by the NEC. This allows much freer trade in electrical materials between the two countries. This does not affect the electrical codes themselves, so differences in practice between the NEC and CEC remain. IEEE The Institute of Electrical and Electronic Engineers' Standard 519 suggests limits for both harmonic current and voltage distor- tion, based on electrical system conditions. BIBLIOGRAPHY ANSI. 2011. Electric power systems and equipment-Voltage ratings (60 Hz). Standard C84.1-2011. American National Standards Institute, Washington, D.C. ASHRAE. 2002. Measurement of energy and demand savings. Guideline 14-2002. CSA. 2006. Canadian electrical code, part I, 20th ed.: Safety standard for electrical installations. Standard C22.1-06. Canadian Standards Associ- ation, Toronto. IEEE. 1980. Definitions of fundamental waveguide terms. ANSI/IEEE Standard 146-1980. Institute of Electrical and Electronics Engineers, Piscataway, NJ. IEEE. 1995. Recommended practice for emergency and standby power sys- tems for industrial and commercial applications. Standard 446-1995. Institute of Electrical and Electronics Engineers, Piscataway, NJ. IEEE. 1992. Recommended practices and requirements for harmonic con- trol in electrical power systems. ANSI/IEEE Standard 519-1992. Insti- tute of Electrical and Electronics Engineers, Piscataway, NJ. NEMA. 2007. Condensed information guide for general purpose industrial ac small and medium squirrel-cage induction motor standards. ANSI/ NEMA Standard MG 1-2007. National Electrical Manufacturers Asso- ciation, Rosslyn, VA. NFPA. 2011. National electrical codeⓇ. Standard 70-2011. National Fire Protection Association, Quincy, MA. U.S. EPA. 2012. Frequently asked questions from owners and operators of nonroad engines, vehicles, and equipment certified to EPA standards. EPA-420-F-12-053. U.S. Environmental Protection Agency, Office of Transportation and Air Quality, Washington, D.C. Available at http:// www.epa.gow.nnshinghway-hissa//egs/42063.pdf Related Commercial Resources Inc. ASHRAE, 2019 user. single for Licensed | {}
a39fe8b0-7504-433e-a1f9-db967ed5b129 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Related Commercial Resources CHAPTER 58 ROOM AIR DISTRIBUTION ¦ Application Guidelines ¦ 58.1 ¦ ¦ --- ¦ --- ¦ ¦ Fully Mixed Air Distribution ¦ 58.2 ¦ ¦ Fully Stratified Air Distribution ¦ 58.9 ¦ ¦ Partially Mixed Air Distribution ¦ 58.13 ¦ ¦ Air Dispersion Systems ¦ 58.15 ¦ ROOMair distribution systems, like other HVAC systems, are air to achieve required thermal comfort and ventilation for space occupants and processes. Although air terminals (inlets and outlets), terminal units, local ducts, and the rooms themselves may affect room air distribution, this chapter addresses only air ter- minals and their effect on occupant comfort. This chapter is intended to help HVAC designers apply air distribution systems to occupied spaces, providing information on characteristics of various air dis- tribution strategies, and tools and guidelines for applications and system design. Naturally ventilated spaces are not addressed; see Chapter 16 of the 2017 ASHRAE Handbook-Fundamentals for de- tails. Also see Chapter 20 of the 2017 ASHRAE Handbook-Funda- mentals for more information on space air diffusion; Chapter 19 of the 2016 ASHRAE Handbook-HVAC Systems and Equipment for information on room air distribution equipment; and Chapter 49 of this volume for sound and vibration control guidance. Room air distribution systems can be classified by (1) their pri- mary objective and (2) the method by which they attempt to accom- plish that objective. The objective of any air distribution system can be classified as one of the following: · Conditioning and/or ventilation of the space for occupant thermal comfort · Conditioning and/or ventilation to support processes within the space · A combination of these As a general guideline, the occupied zone of a space is any loca- tion where occupants normally reside, and may differ from project to project; it is application-specific, and should be carefully defined by the designer. The occupied zone is generally considered to be the room volume between the floor level and 1.8 m above the floor. Stan- dards and guidelines, such as ASHRAE Standards 55 and 62.1, fur- ther define the occupied zone (e.g., Standard 55 exempts areas near walls). Occupant comfort is defined in detail in ASHRAE Standard 55- 2017. Figure 5.3.1 of the standard shows acceptable ranges of tem- perature and humidity for spaces. As a general guide, a majority of occupants in typical office spaces can be satisfied with thermal envi- ronments over a wide range of temperatures and relative humidities. Designers often target indoor dry-bulb temperatures between 73 and 22 and 25°C, relative humidities between 25 and 60%, and occupied zone air velocities below 0.25 m/s. ASHRAE Standard 113 describes a method for evaluating effec- tiveness of various room air distribution systems in achieving ther- mal comfort. Room air distribution methods can be classified as one of the fol- lowing: · Fully mixed systems (e.g., overhead distribution) have little or no thermal stratification of air in the occupied and/or process space. The preparation of this chapter is assigned to TC 5.3, Room Air Distribu- tion. ¦ Air Terminal Units (ATUs) ¦ 58.19 ¦ ¦ --- ¦ --- ¦ ¦ Room Fan-Coil Units ¦ 58.26 ¦ ¦ Heating and Cooling Coil Selection ¦ 58.30 ¦ ¦ Chilled Beams ¦ 58.31 ¦ ¦ Air Curtain Units ¦ 58.34 ¦ · Full thermal stratification systems (e.g., thermal displacement ventilation) have little or no air mixing in the occupied and/or pro- cess space. · Partially mixed systems (e.g., most underfloor air distribution designs) provide limited air mixing in the occupied and/or process space. · Task/ambient air distribution (e.g., personally controlled desk outlets, spot conditioning systems) focuses on conditioning only part of the space for thermal comfort and/or process control. Because task/ambient design requires a high degree of individual control, it is not covered in this chapter; see Chapter 20 of the 2017 ASHRAE Handbook-Fundamentals for details. Guidance is also provided by ASHRAE (2013). Figure 1 shows the spectrum between the two extremes (full mix- ing and full stratification) of room air distribution strategies. 1. APPLICATION GUIDELINES Design Considerations Architectural and Spatial Constraints. Air distribution prod- ucts must fulfill both the functional requirement of conditioning space and the visual aesthetic determined by the architect. Architec- tural constraints may limit placement of air outlets and ductwork. Heat Gain and Loss Characteristics. Large sensible heat loads can drive air movement in a space. Warm air is more buoyant and rises; cooler air is denser and descends to the ground. A zone may experience different heat loads depending on the season or time of day. The air distribution system must meet the varying heating and cooling needs throughout the building's operation. Care should be taken to ensure cool surfaces, such as exterior windows, do not reach temperatures below dew point, or condensation will occur. Thermal Comfort. Occupant thermal comfort depends on sev- eral variables, including air velocity, air temperature, thermal radia- tion, humidity, occupant metabolic rate, and occupant clothing. Air distribution systems that use higher air velocities and temperature differentials may create a greater risk of draft. Likewise, exterior windows with warm or cold surfaces can produce undesired thermal radiation to nearby occupants. For more information, see ASHRAE Standard 55-2017 and its user' s manual (ASHRAE 2016). Acoustical Requirements. Sound emitted from inlets and outlets is directly related to the airflow quantity and free area velocity. The airflow sound intensity in a space also depends on the room 's acous- tical absorption and the observer's distance from air distribution devices. For more information, see Chapter 49 of this volume and Chapter 8 in the 2017 ASHRAE Handbook-Fundamentals. Available Locations for Air Inlets and Outlets. Inlet and outlet characteristics are discussed in Chapter 20 of the 2016 ASHRAE Handbook- -HVAC Systems and Equipment. This chapter discusses more specific application considerations for air inlets and outlets. Code Requirements. Some applications (e.g., operating rooms) may require compliance with special or local codes that limit the selection and placement of certain types of air outlets. 58.1 Inc. ASHRAE, 2019 user. single for Licensed | {}
39d1ba0e-8589-496c-9e2e-760e02916049 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 58.2 2019 ASHRAE Handbook-HVAC Applications (SI) ![image](/image/placeholder) MIXED MIXED FULLY STRATIFIED STRATIFIED STRATIFIED ELEVATION ELEVATION ELEVATION ELEVATION FULLY MIXED MIXED MIXED LOCAL TEMPERATURE LOCAL TEMPERATURE LOCAL TEMPERATURE LOCAL TEMPERATURE PARTIALLY MIXED ROOM AIR DIFFUSION METHODS FULLY STRATIFIED ROOM AIR FULLY MIXED ROOM AIR DISTRIBUTION SYSTEMS DISTRIBUTION SYSTEMS EXAMPLES: · Thermal displacement using low-velocity cool air · Natural ventilation EXAMPLES: · Underfloor air distribution (using room air induction) in cooling operation · Underseat air distribution (using room air induction) in cooling operation · Task/ambient cooling (using furniture-based outlets) · Task/ambient (spot) cooling or heating (industrial applications) EXAMPLES: Fig. 1 Classification of Air Distribution Strategies · Overhead mixed air supply in cooling operation · Fan-coil units and unit ventilators · High-velocity floor-based supply in heating operation Indoor Air Quality and Sustainability Air distribution systems affect not only indoor air quality (IAQ) and thermal comfort, but also energy consumption over the entire life of the project. Choices made early in the design process are important. ASHRAE Standard 90. 1 provides energy efficiency re- quirements that affect supply air characteristics. U.S. Green Building Council's (USGBC) Leadership in Energy and Environmental Design (LEEDⓇ) Green Building Rating Sys- tem TM was originally created in response to indoor air quality con- cerns, and has evolved to include prerequisites and credits for increasing ventilation effectiveness and improving thermal comfort (new.usgbc.org/leed). These requirements and optional points are relatively easy to achieve if good room air distribution design prin- ciples, methods, and standards are followed. Environmental tobacco smoke (ETS) control is a LEED prereq- uisite. Banning indoor smoking is a common approach, but ifindoor smoking is to be allowed, ASHRAE Standard 62.1 requires that more than the base non-ETS ventilation air be provided where ETS is present in all or part of a building. Rock (2006) provides addi- tional advice on dealing with ETS. Ventilation effectiveness is affected directly by the room air dis- tribution system' s design, construction, and operation, but is very difficult to predict. Many attempts have been made to quantify ven- tilation effectiveness, including ASHRAE Standard 129. However, this standard is only for experimental tests in well-controlled labo- ratories and should not be applied directly to real buildings. Because of the difficulty in predicting ventilation effectiveness, ASHRAE Standard 62.1 provides a table of typical values that were determined through the experiences of its Standard Project Com- mittee and reviewers or extracted from research literature; for exam- ple, well-designed ceiling-based air diffusion systems produce near- perfect air mixing in cooling mode, and yield an air change effec- tiveness of almost 1.0. More information on ASHRAE Standard 62.1 is available in its user's manual (ASHRAE 2011). Displacement and underfloor air distribution (UF AD) systems have the potential for values greater than 1.0. More information on ceiling- and wall-mounted air inlets and outlets can be found in Rock and Zhu (2002). Performance of displacement systems is described by Chen and Glicksman (2003), and UFAD is discussed in detail by ASHRAE (2013). Table 1 Recommended Return Inlet Face Velocities ¦ Inlet Location ¦ Velocity Across Gross Area, m/s ¦ ¦ --- ¦ --- ¦ ¦ Above occupied zone ¦ >4 ¦ ¦ In occupied zone, not near sedentary occupants ¦ 3 to 4 ¦ ¦ near sedentary occupants ¦ 2 to 3 ¦ ¦ Door or wall louvers ¦ 1 to 1.5 ¦ ¦ Through undercut area of doors ¦ 1 to 1.5 ¦ Air terminals, such as diffusers or grilles, may become unsightly over time because of accumulation of dirt on their faces (smudging). Instead of replacing air terminals, and thus requiring new materials and energy for manufacturing, they can often be cleaned in place to restore their appearance. Those that cannot be cleaned and must be replaced should be recycled, not discarded, to recover the various metals and other desirable materials of construction. Return Air Inlets The success of a mixed air distribution system depends primarily on supply diffuser location. Return grille location is far less critical than the location of air outlets. In fact, the return air intake affects room air motion only in the area immediately around the grille. Mea- surements of velocity near a return air grille show a rapid decrease in magnitude as the measuring device is moved away from the grille face. Table 1 shows recommended maximum (to avoid excessive noise) return inlet face velocities as a function of grille location. Every enclosed space should have return/transfer inlets of adequate size per this table. For stratified and partially mixed air distribution systems, it can be advantageous to place the return air inlet in the ceiling. ASHRAE Standard 62. 1 allows ventilation effectiveness greater than 1.0 for some stratified and partially mixed air distribution systems in cool- ing mode if the return air inlet is located in the ceiling. Supply air short circuiting is normally not a problem if the outlet is selected to provide adequate throw and directed away from returns or exhausts. The success ofthis practice is confirmed by the availability and use of combination supply and return diffusers. 2. FULLY MIXED AIR DISTRIBUTION In mixed air systems, high-velocity supply jets from air outlets maintain comfort by mixing room air with supply air. This air Inc. ASHRAE, 2019 user. single for Licensed | {}
0691eab1-d7af-44e5-9262-70e59b449b62 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Room Air Distribution 58.3 mixing, heat transfer, and resultant velocity reduction should occur outside the occupied zone. Occupant comfort is maintained not directly by motion of air from outlets, but from secondary air motion from mixing in the unoccupied zone. Comfort is maximized when uniform temperature distribution and average room air veloc- ities of less than 0.25 m/s are maintained in the occupied zone. Maintaining average velocities less than 0.25 m/s in the occupied zone is often overlooked by designers, but is critical to maintaining comfort. The outlet's selection, location, supply air volume, dis- charge velocity, and air temperature differential determine the resulting air motion in the occupied zone. Principles of Operation Mixed systems generally provide comfort by entraining room air into discharge jets located outside occupied zones, mixing supply and room air. Ideally, these systems generate low-velocity air motion (less than 0.25 m/s) throughout the occupied zone to provide uniform temperature gradients and velocities. Proper selection of an air outlet is critical for proper air distribution; improper selection can result in room air stagnation, unacceptable temperature gradi- ents, and unacceptable velocities in the occupied zone, possibly leading to occupant discomfort or poor air quality. The location of a discharge jet relative to surrounding surfaces is important. Discharge jets attach to parallel surfaces, given sufficient velocity and proximity. When a jet is attached, the throw increases by about 30% over a jet discharged in an open area. This difference is important when selecting an air outlet. For detailed discussion of the surface effect on discharge jets, see Chapter 20 of the 2017 ASHRAE Handbook-Fundamentals. Space Ventilation and Contaminant Removal These systems are intended to maintain acceptable indoor air quality by mixing supply and room air (dilution ventilation). Supply air is typically a conditioned mixture of ventilation and recirculated air. Outlet type and discharge velocity determine the mixing rate of the space and should be a design consideration. The room ' s return or exhaust air carries away diluted air contaminants. Space air ventila- tion rates are mandated under ASHRAE Standard 62.1, but supply airflow rates are often higher because of thermal loads. Benefits and Limitations Benefits of fully mixed systems include the following: · Most office applications can use lower supply dry-bulb tempera- tures, for smaller ductwork and lower supply air quantities. · Air can be supplied at a lower moisture content, possibly elimi- nating the need for a more complex humidity control system. · Vertical temperature gradients are lower for cooling applications with high internal heat gains, which may improve thermal comfort. · Mixed systems are the most common design for air distribution systems, because designers and installers are familiar with the required system components and installation. Limitations of mixed systems include the following: · Partial-load operation in variable-air-volume (V A V) systems may reduce outlet velocities, reducing room air mixing and compro- mising thermal comfort. Designers should consider this when selecting outlets. · Cooling and heating with the same ceiling or high-sidewall dif- fuser may cause inadequate performance in heating mode and/or excessive velocity in cooling mode. · Ceilings more than 4 m high may require special design consid- erations to provide acceptable comfort in the occupied zone. Care should be taken to select the proper outlet for these applications. · Because mixed systems typically use high-velocity jets of air, any obstructions in the space (e.g., bookshelves, wall partitions, fur- niture) can reduce comfort. Chart Type: line 100 200 300 400 500 600 item_01 0dB INCREASE 5dB INCREASE 10dB INCREASE 15dB INCREASE 20dB INCREASE 25dB INCREASE *Ratio of air pressure before and after damper. Fig. 2 Effects of Neck-Mounted Damper on Air Outlet · Lighter-than-air contaminants are uniformly mixed in the space and typically result in higher contaminant concentrations, which may compromise indoor air quality. Mixed air systems typically use either ceiling or sidewall outlets discharging air horizontally, or floor- or sill-mounted outlets dis- charging air vertically. They are the most common method of air distribution in North America. Inlet Conditions to Air Outlets The way an airstream approaches an outlet is important. For good air diffusion, the inlet configuration should create a uniform discharge velocity profile from the outlet, or the outlet may not per- form as intended. The outlet usually cannot correct effects of improper duct ap- proach. Many sidewall outlets are installed either at the end of ver- tical ducts or in the side of horizontal ducts, and most ceiling outlets are attached either directly to the bottom of horizontal ducts or to special vertical takeoff ducts that connect the outlet with the hori- zontal duct. In all these cases, devices for directing and equalizing the airflow may be necessary for proper direction and diffusion of the air. ASHRAE research project RP-1335 (Landsberger et al. 2011) determined that a wide-open damper installed in the neck of a dif- fuser could add up to 8 NC to the cataloged NC value, depending on diffuser and damper types. Significantly closed balancing dampers can add more than 10 NC, depending on duct pressure and how far upstream it is installed. Table 2 gives forward throw asymmetries for various diffuser types, and Figure 2 compares the total pressure ratio of a diffuser with no damper versus a neck-mounted damper that is increasingly throttled. Effects of Typical Field Installations on Common Ceiling Diffusers. Ceiling air outlets are tested using ideal installation conditions described in ASHRAE Standard 70: a minimum of three vertical, straight duct diameters before the diffuser inlet. Field installations are often not ideal because of ceiling plenum limitations, architectural design, structural supports of the building, etc. ASHRAE research project RP-1335 (Landsberger et al. 2011) developed some useful application data that can be used by design engineers to predict throw, pressure drop, and sound caused by non- ideal installations. Tables 2, 3, and 4 give a general summary of application data from RP-1335. The multipliers provided in these tables may be applied to diffuser performance data measured from tests compliant with ASHRAE Standard 70-2006. Space Temperature Gradients and Airflow Rates Inc. ASHRAE, 2019 user. single for Licensed A fully mixed system creates homogeneous thermal conditions throughout the space. As such, thermal gradients should not exist in the occupied zone. Improper selection, sizing, or placement may | {}
65507bb0-7b6e-4907-b8d8-ac512c49bb42 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 58.4 2019 ASHRAE Handbook-HVAC Applications (SI) Table 2 Forward Throw Asymmetry Vertical Inlet Duct Height ¦ Diffuser Type ¦ 0 Duct Diameter ¦ 0 Duct Diameter ¦ 1.5 Duct Diameters ¦ 1.5 Duct Diameters ¦ 3 Duct Diameters ¦ 3 Duct Diameters ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ No Damper ¦ Damper ¦ No Damper ¦ Damper ¦ No Damper ¦ Damper ¦ ¦ Square ¦ 1.4 ¦ 1.2-1.4 ¦ 1.1 ¦ 1.0-1.1 ¦ 1.0 ¦ 1.2 ¦ ¦ Round ¦ 1.4 ¦ 1.2-1.4 ¦ 1.1 ¦ 1.0-1.1 ¦ 1.0 ¦ 1.2 ¦ ¦ Plaque ¦ 1.2-1.3 ¦ 1.1-1.3 ¦ 1.1 ¦ 1.0-1.1 ¦ 1.0 ¦ 1.1 ¦ ¦ Perforated ¦ 1.3 ¦ 1.2-1.3 ¦ 1.1 ¦ 1.0-1.1 ¦ 1.0 ¦ 1.1-1.2 ¦ ¦ Modular core ¦ 1.4 ¦ 1.2-1.4 ¦ 1.1 ¦ 1.0-1.1 ¦ 1.0 ¦ 1.0 ¦ ¦ Louvered ¦ 1.4 ¦ 1.2-1.4 ¦ 1.1 ¦ 1.0-1.1 ¦ 1.0 ¦ 1.0 ¦ Source: data from Landsberger et al. (2011). Note: Multipliers valid for round hard duct and flex duct. Multipliers represent proportional increase of throw distance in forward direction of ducted air motion. Table 3 Total Pressure Increase Vertical Inlet Duct Height ¦ Diffuser Type ¦ 0 Duct Diameter ¦ 0 Duct Diameter ¦ 1.5 Duct Diameters ¦ 1.5 Duct Diameters ¦ 3 Duct Diameters ¦ 3 Duct Diameters ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ ¦ No Dampera ¦ Damperb ¦ No Dampera ¦ Damperb ¦ No Dampera ¦ Damperb ¦ ¦ Square ¦ 1.4-1.7 ¦ 1.7-2.2 ¦ 1.3-1.5 ¦ 1.7-2.1 ¦ 1.1-1.2 ¦ 1.5-1.8 ¦ ¦ Round ¦ 1.4-1.6 ¦ 1.6-2.0 ¦ 1.2-1.4 ¦ 1.5-1.9 ¦ 1.1-1.2 ¦ 1.2-1.7 ¦ ¦ Plaque ¦ 1.4-1.7 ¦ 1.7-2.2 ¦ 1.3-1.5 ¦ 1.7-2.1 ¦ 1.1-1.2 ¦ 1.5-1.8 ¦ ¦ Perforated ¦ 1.4-1.6 ¦ 1.6-2.0 ¦ 1.2-1.4 ¦ 1.5-1.9 ¦ 1.1-1.2 ¦ 1.2-1.7 ¦ ¦ Modular core ¦ 1.2-1.4 ¦ 1.4-1.6 ¦ 1.1-1.2 ¦ 1.3-1.5 ¦ 1.1 ¦ 1.3-1.4 ¦ ¦ Louvered ¦ 1.5-1.8 ¦ 1.8-2.4 ¦ 1.3-1.6 ¦ 1.8-2.3 ¦ 1.2-1.3 ¦ 1.6-2.0 ¦ Source: data from Landsberger et al. 2011. aMultipliers based on round hard duct; for flex duct, add 0.2-0.4. bMultipliers based on round sliding damper; if round OBD, subtract 0.3. Table 4 NC Increase Vertical Inlet Duct Height ¦ ¦ 0 Duct Diameter ¦ 0 Duct Diameter ¦ 1.5 Duct Diameters ¦ 1.5 Duct Diameters ¦ 3 Duct Diameters ¦ 3 Duct Diameters ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Diffuser Type ¦ No Dampera ¦ Damperb ¦ No Dampera ¦ Damperb ¦ No Dampera ¦ Damperb ¦ ¦ Square ¦ 7 ¦ 8 ¦ 3 ¦ 10 ¦ 0 ¦ 7 ¦ ¦ Round ¦ 9 ¦ 10 ¦ 4 ¦ 12 ¦ 0 ¦ 8 ¦ ¦ Plaque ¦ 7 ¦ 8 ¦ 3 ¦ 10 ¦ 0 ¦ 7 ¦ ¦ Perforated ¦ 5 ¦ 5 ¦ 2 ¦ 7 ¦ 0 ¦ 5 ¦ ¦ Modular core ¦ 3 ¦ 3 ¦ 1 ¦ 3 ¦ 0 ¦ 2 ¦ ¦ Louvered ¦ 8 ¦ 8 ¦ 3 ¦ 9 ¦ 0 ¦ 6 ¦ Source: data from Landsberger et al. 2011. aNC based on round hard duct; for flex duct, add 1 NC. bNC based on round sliding damper; if round OBD, -2 NC (except for 0 duct diame- ter). prevent full mixing and can result in stagnant areas, or having high- velocity air entering the occupied zone. Supply airflow requirements to satisfy space sensible heat gains or losses are inversely proportional to the temperature difference between supply and return air. The following equation can be used to calculate space airflow requirements (at standard conditions): qs 0 = 1.2(tr - t⌀ where (1) Q = required supply airflow rate to meet sensible load, L/s Is net sensible heat gain in the space, W 5 = return or exhaust air temperature, °C ts = supply air temperature, °C For fully mixed systems with conventional ceiling heights, the return (or exhaust) and room air temperatures are the same; for example, a room with a set-point temperature of 24°C has, on average, a 24°C return or exhaust air temperature. Methods for Evaluation The objective of air diffusion is to create the proper combination of room air temperature, humidity, and air motion to provide ther- mal comfort and acceptable indoor environmental quality in the occupied zone. There are three recommended methods of selecting outlets for mixed air systems using manufacturers' data: · By appearance, flow rate, and sound data · By isovels (lines of constant velocity) and mapping · By comfort criteria These selection methods are not meant to be independent. It is the designer's choice as to which to start with, but it is recom- mended that at least two methods be used for any design. Variation from accepted thermal limits (ASHRAE Standard 55), lack of uniform thermal conditions in the space, or excessive fluc- tuation of conditions in one part of the space may produce discom- fort. Thermal discomfort can also arise from any of the following conditions: · Excessive air motion (draft) · Excessive room air temperature stratification (horizontal, verti- cal, or both) · Failure to deliver or distribute air according to load requirements at different locations · Rapid fluctuation of room temperature Design Procedures By Appearance, Flow Rate, and Sound Data. For a given ap- pearance, flow rate, pressure drop, and sound level criteria, designers can select outlets from manufacturers' catalogs, using the following steps: 1. Determine air volumetric flow requirements based on load and room size. For VAV systems, evaluation should include the range of flow rates from minimum occupied to design load. Consider both cooling and heating mode requirements. 2. Determine acceptable outlet noise criterion (NC); consult Chapter 49 of this volume, or Chapter 8 in the 2017 ASHRAE Handbook-Fundamentals. 3. Locate a range of products from manufacturers' catalogs that meet the airflow and NC requirements. Multiple outlets in a space at the same cataloged NC, and other design considerations, may result in actual sound levels greater than cataloged values. Manufacturers' data are obtained using ideal inlet conditions, and may vary from field installations. From experience, · For identical outlets 3 m or more apart, the cataloged NC rating applies. · Identical outlets within 3 m of each other add no more than 3 dB to the sound pressure level. · For continuous linear outlets, only the sound produced by the closest 3 m need be considered. 4. Select air terminals from manufacturers' catalogs that meet aes- thetic and physical needs. Although these selections may meet the sound requirements for a project, the results do not fully address occupant comfort. Without evaluating the throw of the outlets or room air mixing, this selection method may result in excessive air velocities in the occupied zone, or limited mixing and resultant stagnation. It is recommended that the designer consider selection by isovel mapping or by comfort cri- teria in addition to selection by appearance, flow rate, and sound Inc. ASHRAE, 2019 user. single for Licensed | {}
4d699526-2f44-4401-a7a7-6085065d98dd | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Room Air Distribution 58.5 ![image](/image/placeholder) 0.5 m/s ISOVEL 3 m DIFFUSER 0.25 m/s 3 m 3 m 0.75 m/s OUTLET OUTLET THROW Fig. 4 Schematic for Example 1 Fig. 3 Throw Isovels at Different Terminal Velocities (Adapted from ASHRAE Standard 70-2006) data. Either of these methods addresses resulting air motion in the occupied zone and occupant comfort. Selection by Isovels and Mapping. Using manufacturers' catalog throw data, a designer can predict the path of an outlet's dis- charge jet. Most manufacturers' catalogs list the distance a jet trav- els to reach a terminal velocity of 0.75 to 0.25 m/s. With this information, the designer can map the path of the discharge jet for a given outlet. This evaluation can prevent problems such as exces- sively high air velocities in the occupied zone, or stagnation in a given area. Note that most manufacturers' throw data are based on isothermal supply air; the supply jet temperature is equal to the room air temperature. When using this mapping method, consider the positive or negative buoyancy of nonisothermal (heated or cooled) supply air. In both heating and cooling, a discharge jet should travel the distance shown in the catalog to a terminal velocity of 0.75 m/s without much influence from buoyancy. When evaluat- ing a jet at lower terminal velocities (e.g., 0.5 to 0.25 m/s), consider buoyancy's effect on the distance the jet will travel. Horizontal Throw. A cooled confined air jet projecting along a horizontal surface travels a shorter distance than the equivalent vol- umetric isothermal air jet traveling the same path. If an outlet is selected so that the cooled horizontal jet does not have enough velocity to reach a vertical surface, the jet can separate from the hor- izontal surface and project down into the occupied zone, causing drafts and discomfort. A heated confined air jet projecting along a horizontal surface travels farther than the equivalent volumetric isothermal jet traveling the same path. If an outlet is selected so that the heated, horizontal jet does not have enough velocity to reach a vertical sur- face, the jet can pool at the ceiling level, causing stagnation (no mix- ing) within the occupied space and resulting in high levels of contaminants, thermal stratification, and discomfort. In a free jet scenario, expect similar results as for a confined jet, but if isothermal performance is based on confined jet installation, a 30% reduction in throw length from isothermal performance will occur, along with buoyancy effects. Vertical Throw. A cooled air jet projecting vertically upward travels a shorter distance than the equivalent volumetric isothermal air jet traveling the same path. A heated air jet projecting upward travels farther than the equivalent volumetric isothermal air jet trav- eling the same path. For both cooled and heated air jets, the opposite is true for downward projection. Combining selection by isovels and mapping with acoustical selection allows discharge jet location and intensity in a space to be predicted. Outlet selection should be evaluated at the space's typical operating points (i.e., maximum heating and cooling, and minimum heating and cooling). The following steps may be used: 1. Identify the occupied zone for the space, as defined by ASHRAE Standard 55-2017. 2. Select outlet(s) that meet design NC, pressure drop, and flow rate requirements. Identify the supply jet location using cataloged throw data. 3. Evaluate air jet mapping to ensure terminal velocities in the occupied zone do not exceed 0.25 m/s. 4. For overhead heating applications, △t x 8.5 K (see Chapter 20 of the 2017 ASHRAE Handbook-Fundamentals), evaluate the dia- gram to ensure thatjet velocities 1.4 m from the floor are at least 0.75 m/s. Other design considerations include the following: · In multiple-outlet applications, jets should not collide to cause a downward projection of air resulting in velocities greater than 0.25 m/s in the occupied zone. · For VAV applications, consider both minimum and maximum flow conditions. Example 1. For a 6 by 12 m zone, with a 2.7 m ceiling, with uniform loading of 31.5 W/m2 or 700 W, and air volumetric flow of 5 L/s per square metre or 378 L/s for a dual-outlet configuration, use isovel map- ping to select an appropriate diffuser option that meets a sound criteria of NC 35. Solution: 1. The occupied zone is defined as a height of 1.8 m off the floor, 0.3 m from interior walls, and 1 m from exterior walls. See ASHRAE Standard 55 for the most current definition of occupied zone. 2. One manufacturer suggests that a single 0.6 x 0.6 m plaque diffuser with a 0.2 m inlet at 189 L/s yields an NC 30 and an isothermal throw of 3.6 m at a terminal velocity of 0.25 m/s. 3. With an air jet characteristic length of3 m, and 0.9 m between ceiling and start of the occupied zone, the velocity of the colliding jets can be assumed to not exceed 0.25 m/s in the occupied zone. Verify that resulting diffuser pressure drop and aesthetics meet requirements. 4. If one or more of the walls are exterior in this example, even with additional throw length due to warmer supply air, additional air vol- ume may be required to meet 1.4 m above the floor at 0.75 m/s. Evaluate other diffuser types for similar or better performance criteria. Selection by Comfort Criteria T0.25/L. Selection by isovels and mapping is effective at predicting the path of the discharge jet from an outlet and evaluating resultant occupant comfort. However, there is an established method to quantify occupant comfort for both cool- ing and heating conditions, based on space dimensions and isother- mal catalog throw data. This method can be used to predict a space's resulting air diffusion performance index (ADPI). Inc. ASHRAE, 2019 user. single for Licensed | {}
5cfdedcf-7357-42f6-b709-e957d0f2214a | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 58.6 The comfort criteria T0.25/L method was developed to predict occupant comfort using manufacturers' isothermal catalog throw data (T, usually for 0.25 m/s terminal velocity) and the dimensions available for throw L on the plan view of a mechanical drawing. By using the ratio of T0.25/L, the designer can predict the level of com- fort with a single rating number, ADPI, which can provide further information about the comfort level in a space for results obtained from the NC and mapping selection methods. The effective draft temperature provides a quantifiable indica- tion of comfort at a discrete point in a space by combining the phys- iological effects of air temperature and air motion on a human body. The effective draft temperature ted (the difference in temperature between any point in the occupied zone and the control condition) can be calculated using the following equation for the cooling con- dition, proposed by Rydberg and Norback (1949) and modified by Straub (Straub and Chen 1957; Straub et al. 1956) in discussion of a paper by Koestel and Tuve (1955): Air Distribution Performance Index (ADPI). The air distribution performance index was developed as a way to quantify the comfort level in heating and cooling for a space conditioned by a mixed air system. ADPI uses the effective draft temperature collected at an array of points taken within the occupied zone to predict comfort. ADPIis the percentage of points in a space where the effective draft temperature is between -1.7 and +1.1 K for cooling and -2.2 and +2 K for heating. The acceptable air velocity is less than 0.36 m/s for heating and cooling. In addition, the acceptable vertical temperature gradient should be less than 3 K/m. High ADPI values generally correlate to high space thermal comfort levels with the maximum obtainable value of 100. Selecting outlets to provide a minimum ADPI value of 80 generally results in a well-mixed space. ted=(tx-tc)-8.0(Vx -0.15) [Cooling Only] where effective draft temperature, K ted (2) tx = local airstream dry-bulb temperature, °C tc = average (control) room dry-bulb temperature, °C Vx velocity, m/s = local airstream centerline Inc. ASHRAE, 2019 user. single for Licensed Liu and Novoselac (2015) developed an effective draft tempera- ture ted for the heating condition based on predicted mean vote (PMV) model specified in ASHRAE Standard 55. A high vertical temperature gradient occurs during heating when throws are insuf- ficient, resulting in stagnation of supply air and unacceptable venti- lation to the breathing zone. ted=(tx-t)-9.1(Vx - 0.15) [Heating Only] where (3) ted = effective draft temperature, K tx = local airstream dry-bulb temperature, °C tc = average (control) room dry-bulb temperature, °C Vx velocity, m/s = local airstream centerline T0.25/L Selection Method. This method uses the ratio of cata- loged isothermal throw data at 0.25 m/s to the characteristic length for a given device (Table 5). Each type of diffuser has different performance characteristics and therefore may provide a different ADPI value for the same con- ditions. Calculating T0.25/L for a given outlet can predict the level of comfort for a space. Using Tables 6A and 6B, the designer can opti- mize not only the type of diffuser to select but also the size and capacity for both cooling and heating. Using T0.25/L helps designers maximize space cooling comfort; however, this method is not meant to, nor may it be practical to, eval- uate T0.25/L values for each outlet on a project. The design guidelines in Tables 6A and 6B were developed from laboratory experiments in chambers lower than 3 m, with test diffusers symmetrically distrib- uted (Liu and Novoselac 2014; Liu et al. 2016; Miller and Nash 2019 ASHRAE Handbook-HVAC Applications (SI) Table 5 Characteristic Room Length for Several Diffusers (Measured from Center of Air Outlet) ¦ Diffuser Type ¦ Characteristic Length L ¦ ¦ --- ¦ --- ¦ ¦ High sidewall grille ¦ Distance to wall perpendicular to jet ¦ ¦ Adjustable blade ¦ ¦ ¦ Fixed blade ¦ ¦ ¦ Linear bar ¦ ¦ ¦ Nozzle ¦ ¦ ¦ Horizontal-throw ceiling diffuser ¦ Distance to closest wall, midplane between outlets or intersecting air jet ¦ ¦ Round ¦ ¦ ¦ Square ¦ ¦ ¦ Perforated ¦ ¦ ¦ Louvered ¦ ¦ ¦ Plaque ¦ ¦ ¦ Swirl ¦ ¦ ¦ Sill grille ¦ Length of room in direction ofjet flow ¦ ¦ Ceiling slot diffuser ¦ Distance to wall perpendicular to jet or midplane between outlets ¦ ¦ Light troffer diffusers ¦ Distance to midplane between outlets plus distance from ceiling to top of occupied zone ¦ 1971). Therefore, attention should be paid to ceiling height of build- ings (e.g., airport terminals) or highly asymmetric diffuser layouts. Previously published T0.25/L values at higher cooling loads (60 to 250 W/m2) are available in previous versions of this chapter and available in the ASHRAE Handbook Online version of this chapter. Design Procedures. T0.25/L can be used as a general tool to eval- uate cooling comfort levels in a space, at the beginning of design to optimize outlet selection (as shown in the following steps), or at the end of the process to predict comfort levels in spaces designed using NC and mapping methods: 1. Determine air volumetric flow requirements based on load and room size. For VAV systems, evaluation should include both minimum occupied and maximum design flow rates. 2. Select tentative diffuser type and location in room. 3. Determine room ' s characteristic length L (Table 5). 4. Select recommended T0.25/L ratio from Tables 6A and 6B. 5. Calculate throw distance T0.25 by multiplying recommended T0.25/L ratio from Tables 6A and 6B by available length L. 6. Locate appropriate outlet size from manufacturer's catalog. 7. Ensure that this outlet meets other imposed specifications (e.g., noise, static pressure loss). Example 2. For a 6 by 3.7 m room, with 2.7 m ceiling, with uniform load- ing of 31.5 W/m2 or 700 W and air volumetric flow of 5 L/s per square metre or 110 L/s for one outlet, find the size for a 0° deflection horizon- tal blade, high sidewall grille located at center of 3.7 m end wall, 225 mm from ceiling. Solution: 1. Constant-volume system, 110 L/s, high sidewall grille, located at center of 3.7 m end wall, 225 mm from ceiling 2. Characteristic length L = 6 m (length of room: Table 5) 3. Recommended maximum, T0.25/L = 1.8 in cooling mode (Table 6A) T0.25/L = 1.6 in heating mode (Table 6B) 4. Throw to 0.25 m/s, T0.25 = 1.8 x 6 = 10.8 m in cooling mode To.25 = 1.6 x 6 = 9.6 m in heating mode To satisfy both modes of operation, choose one or find a com- mon throw distance that resides within the overall ADPI range of both modes and base product selection off chosen criteria. Further | {}
5ef1b930-7353-4141-b2bc-d0ed37cb300a | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Room Air Distribution 58.7 Table 6A Air Diffusion Performance Index (ADPI) Selection Guide for Typical Cooling Loads ¦ Terminal Device in Cooling Mode ¦ Installation ¦ Load, W/m2 ¦ Max. ADPI T0.25/L ¦ Max. ADPI ¦ T/L Low Limit for ADPI > 80% ¦ T/L High Limit for ADPI > 80% ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Adjustable-blade grilles ¦ 45° upward blades, High sidewall ¦ 25 ¦ 0.8 ¦ 98 ¦ 0.4 ¦ 1.3 ¦ ¦ Adjustable-blade grilles ¦ 45° upward blades, High sidewall ¦ 50 ¦ 0.9 ¦ 96 ¦ 0.5 ¦ 1.2 ¦ ¦ Adjustable-blade grilles ¦ 0° horizontal blades, High sidewall ¦ 25 ¦ 1.7 ¦ 94 ¦ 1.2 ¦ 2.2 ¦ ¦ Adjustable-blade grilles ¦ 0° horizontal blades, High sidewall ¦ 50 ¦ 1.8 ¦ 88 ¦ 1.4 ¦ 2.2 ¦ ¦ Adjustable-blade grilles ¦ 45° downward blades, High sidewall ¦ 25 ¦ 0.9 ¦ 76 ¦ NA ¦ NA ¦ ¦ Adjustable-blade grilles ¦ 45° downward blades, High sidewall ¦ 50 ¦ 1 ¦ 70 ¦ NA ¦ NA ¦ ¦ Fixed-blade grilles (high sidewall installation) ¦ 15° upward blades, High sidewall ¦ 25 ¦ 1.4 ¦ 96 ¦ 0.5 ¦ 2.4 ¦ ¦ Fixed-blade grilles (high sidewall installation) ¦ 15° upward blades, High sidewall ¦ 50 ¦ 2.1 ¦ 94 ¦ 1.2 ¦ 2.9 ¦ ¦ Fixed-blade grilles (high sidewall installation) ¦ 15° downward blades, High sidewall ¦ 25 ¦ 1.9 ¦ 85 ¦ 1.5 ¦ 2.2 ¦ ¦ Fixed-blade grilles (high sidewall installation) ¦ 15° downward blades, High sidewall ¦ 50 ¦ 2 ¦ 82 ¦ 1.8 ¦ 2.2 ¦ ¦ Linear-bar grilles (high sidewall installation) ¦ High sidewall ¦ 25 ¦ 1.3 ¦ 92 ¦ 0.7 ¦ 1.8 ¦ ¦ Linear-bar grilles (high sidewall installation) ¦ High sidewall ¦ 50 ¦ 1.3 ¦ 88 ¦ 1.0 ¦ 1.6 ¦ ¦ Linear-bar grilles (high sidewall installation) ¦ Sill ¦ 25 ¦ 1.3 ¦ 94 ¦ 0.9 ¦ 1.7 ¦ ¦ Linear-bar grilles (high sidewall installation) ¦ Sill ¦ 50 ¦ 1.3 ¦ 90 ¦ 1.0 ¦ 1.6 ¦ ¦ Nozzles (high sidewall installation) ¦ High sidewall ¦ 25 ¦ 0.7 ¦ 96 ¦ 0.4 ¦ 2.0 ¦ ¦ Nozzles (high sidewall installation) ¦ High sidewall ¦ 50 ¦ 1 ¦ 89 ¦ 0.4 ¦ 1.9 ¦ ¦ Round ceiling diffuser ¦ Ceiling ¦ 25 ¦ 1.6 ¦ 99 ¦ 0.4 ¦ 3.2 ¦ ¦ Round ceiling diffuser ¦ Ceiling ¦ 50 ¦ 1.9 ¦ 98 ¦ 0.5 ¦ 3.2 ¦ ¦ Square ceiling diffuser ¦ Ceiling ¦ 25 ¦ 1.8 ¦ 100 ¦ 0.8 ¦ 2.8 ¦ ¦ Square ceiling diffuser ¦ Ceiling ¦ 50 ¦ 1.8 ¦ 100 ¦ 0.6 ¦ 3.1 ¦ ¦ Perforated diffusers, round pattern ¦ Ceiling ¦ 25 ¦ 1.9 ¦ 95 ¦ 0.5 ¦ 3.3 ¦ ¦ Perforated diffusers, round pattern ¦ Ceiling ¦ 50 ¦ 2.1 ¦ 95 ¦ 0.9 ¦ 3.4 ¦ ¦ Perforated diffusers, directional pattern (4-way) ¦ Ceiling ¦ 25 ¦ 2.1 ¦ 100 ¦ 1.2 ¦ 3.1 ¦ ¦ Perforated diffusers, directional pattern (4-way) ¦ Ceiling ¦ 50 ¦ 2 ¦ 95 ¦ 1.0 ¦ 2.9 ¦ ¦ Louvered face diffusers, with lip on deflector blade ¦ Ceiling ¦ 25 ¦ 2.5 ¦ 100 ¦ 0.5 ¦ 4.4 ¦ ¦ Louvered face diffusers, with lip on deflector blade ¦ Ceiling ¦ 50 ¦ 2.6 ¦ 100 ¦ 0.6 ¦ 4.5 ¦ ¦ Louvered face diffusers, without lip on deflector blade ¦ Ceiling ¦ 25 ¦ 2 ¦ 100 ¦ 0.5 ¦ 3.6 ¦ ¦ Louvered face diffusers, without lip on deflector blade ¦ Ceiling ¦ 50 ¦ 1.8 ¦ 100 ¦ 0.4 ¦ 3.4 ¦ ¦ Plaque face diffusers ¦ Ceiling ¦ 25 ¦ 1.6 ¦ 100 ¦ 0.3 ¦ 3.0 ¦ ¦ Plaque face diffusers ¦ Ceiling ¦ 50 ¦ 1.6 ¦ 100 ¦ 0.4 ¦ 3.2 ¦ ¦ Linear-slot diffusers ¦ Ceiling ¦ 25 ¦ 1.8 ¦ 100 ¦ 0.5 ¦ 3.0 ¦ ¦ Linear-slot diffusers ¦ Ceiling ¦ 50 ¦ 1.8 ¦ 100 ¦ 0.5 ¦ 3.1 ¦ ¦ T-bar slot diffusers ¦ Ceiling, periphery of a wall ¦ 25 ¦ 1.3 ¦ 96 ¦ 0.7 ¦ 1.9 ¦ ¦ T-bar slot diffusers ¦ Ceiling, periphery of a wall ¦ 50 ¦ 1.5 ¦ 90 ¦ 1.1 ¦ 1.9 ¦ ¦ Swirl diffusers ¦ Ceiling ¦ 25 ¦ 1.3 ¦ 100 ¦ 0.4 ¦ 2.4 ¦ ¦ Swirl diffusers ¦ Ceiling ¦ 50 ¦ 1.3 ¦ 98 ¦ 0.4 ¦ 2.4 ¦ ¦ N-slot diffusers ¦ Ceiling ¦ 25 ¦ 1.8 ¦ 100 ¦ 1.3 ¦ 2.4 ¦ ¦ N-slot diffusers ¦ Ceiling ¦ 50 ¦ 1.8 ¦ 95 ¦ 1.3 ¦ 2.3 ¦ Source: Data developed by Liu et al. (2016) for this chapter from ASHRAE research project RP-1546 (Liu 2016), and air speed limit (0.36 m/s) extrapolated from data. Additional data point used to create new regressions for ADPI curves to better represent current diffusers/grilles. Table applies to spaces with maximum 3.7 m ceiling. evaluation may be required if air volumetric flow changes based on mode of operation. 5. Refer to the manufacturer's catalog for a size that gives this isother- mal throw to 0.25 m/s. One manufacturer recommends the following sizes, when vanes are straight, discharging at 110 L/s: 400 by 100 mm, 300 by 125 mm, or 250 by 150 mm. There are many considerations to be made when designing a fully mixed system. For more information, see Rock and Zhu (2002). Typical Applications Horizontal Discharge Cooling with Ceiling-Mounted Out- lets. Ceiling-mounted outlets typically use the surface effect to transport supply air in the unoccupied zone. The supply air projects across the ceiling and, with sufficient velocity, can continue down wall surfaces and across floors, as shown in Figure 5. In this appli- cation, supply air should remain outside the occupied zone until it is adequately mixed and tempered with room air. Air motion in the occupied zone is generated by room air entrainment into the supply air (Nevins 1976). ![image](/image/placeholder) SUPPLY AIR ROOM AIR Fig. 5 Air Supplied at Ceiling Induces Room Air into Supply Jet Overhead outlets may also be installed on exposed ducts, in which case the surface effect does not apply. Typically, ifthe outlet is mounted 300 mm or more below a ceiling surface, discharge air will not attach to the surface. The unattached supply air has a shorter throw and can project downward, resulting in high air velocities in Inc. ASHRAE, 2019 user. single for Licensed | {}
456005a5-2af8-4617-9c44-669107d37950 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 58.8 2019 ASHRAE Handbook-HVAC Applications (SI) Table 6B Air Diffusion Performance Index (ADPI) Selection Guide for Typical Heating Loads ¦ Terminal Device in Heating Mode ¦ Installation ¦ Load, W/m2 ¦ Max. ADPI T0.25/L ¦ Max. ADPI ¦ T/L Low Limit for ADPI > 80% ¦ T/L High Limit for ADPI > 80% ¦ ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ --- ¦ ¦ Adjustable-blade grilles ¦ 45° upward blades, High sidewall ¦ 30 to 40 ¦ 1.1 ¦ 95 ¦ 0.6 ¦ 1.9 ¦ ¦ ¦ 0° horizontal blades, High sidewall ¦ 30 to 40 ¦ 1.6 ¦ 94 ¦ 1.1 ¦ 2.4 ¦ ¦ ¦ 45° downward blades, High sidewall ¦ 30 to 40 ¦ 0.7 ¦ 84 ¦ 0.6 ¦ 0.8 ¦ ¦ Fixed-blade grilles ¦ 15° upward blades, High sidewall ¦ 30 to 40 ¦ 1.8 ¦ 96 ¦ 1.2 ¦ 2.8 ¦ ¦ ¦ 15° downward blades, High sidewall ¦ 30 to 40 ¦ 1.4 ¦ 88 ¦ 0.6 ¦ 2.2 ¦ ¦ Linear-bar grilles ¦ High sidewall ¦ 30 to 40 ¦ 1.2 ¦ 94 ¦ 0.6 ¦ 1.7 ¦ ¦ ¦ Sill ¦ 30 to 40 ¦ 1.2 ¦ 100 ¦ 0.7 ¦ 1.8 ¦ ¦ Nozzles (high sidewall installation) ¦ High sidewall ¦ 30 to 40 ¦ 1.5 ¦ 92 ¦ 1.0 ¦ 2.0 ¦ ¦ Round ceiling diffuser ¦ Ceiling ¦ 30 to 40 ¦ 1.4 ¦ 93 ¦ 1.0 ¦ 2.3 ¦ ¦ Square ceiling diffuser ¦ Ceiling ¦ 30 to 40 ¦ 1.7 ¦ 91 ¦ 2.5 ¦ 3.4 ¦ ¦ Perforated diffusers, round pattern ¦ Ceiling ¦ 30 to 40 ¦ 2.1 ¦ 90 ¦ 2.0 ¦ 2.8 ¦ ¦ Perforated diffusers, directional pattern (4-way) ¦ Ceiling ¦ 30 to 40 ¦ 2.5 ¦ 87 ¦ 2.5 ¦ 3.4 ¦ ¦ Louvered face diffusers, with lip on deflector blade ¦ Ceiling ¦ 30 to 40 ¦ 2.6 ¦ 88 ¦ 2.5 ¦ 4.4 ¦ ¦ Louvered face diffusers, without lip on deflector blade ¦ Ceiling ¦ 30 to 40 ¦ 2.1 ¦ 88 ¦ 2.1 ¦ 3.2 ¦ ¦ Plaque face diffusers ¦ Ceiling ¦ 30 to 40 ¦ 2.1 ¦ 93 ¦ 2.1 ¦ 3.0 ¦ ¦ Linear-slot diffusers ¦ Ceiling ¦ 30 to 40 ¦ 1.7 ¦ 90 ¦ 1.7 ¦ 3.1 ¦ ¦ T-bar slot diffusers ¦ Ceiling, periphery of a wall ¦ 30 to 40 ¦ 1.6 ¦ 91 ¦ 1.3 ¦ 2.0 ¦ ¦ Swirl diffusers ¦ Ceiling ¦ 30 to 40 ¦ 1.4 ¦ 100 ¦ 1.4 ¦ 2.1 ¦ ¦ N-slot diffusers ¦ Ceiling ¦ 30 to 40 ¦ 1.9 ¦ 100 ¦ 1.5 ¦ 2.4 ¦ Source: Data developed by Liu and Novoselac (2015) for this chapter from ASHRAE research project RP-1546 (Liu 2016), and air speed limit (0.36 m/s) extrapolated from data. Additional data point used to create new regressions for ADPI curves to better represent current diffusers/grilles. Table applies to spaces with maximum 3.7 m ceiling. the occupied zone. Some outlets are designed for use in exposed duct applications. Typical outlet performance data presented by manufacturers are for outlets with surface effect; consult manufac- turers for information on exposed duct applications. Vertical-Discharge Cooling or Heating with Ceil- ing-Mounted Outlets. Vertically projected outlets are typically selected for high-ceiling applications that require forcing supply air down to the occupied zone. It is important to keep cooling supply air velocity below 0.25 m/s in the occupied zone. For heating, supply air should reach the floor. There are outlets specifically designed for vertical projection, and it is important to review the manufacturer's performance data notes to understand how to apply catalog data. Throws for heating and cooling differ and also vary depending on the difference be- tween supply and room air temperatures. Cooling with Sidewall Outlets. Sidewall outlets are usually selected when access to the ceiling plenum is restricted. Sidewall outlets that are within 300 mm of a ceiling and set for horizontal or a slightly upward projection provide a discharge pattern that attaches to the ceiling and travels in the unoccupied zone. This pat- tern entrains air from the occupied zone to provide mixing. In some applications, the outlet must be located 0.5 to 1.25 m below the ceiling. When set for horizontal projection, the discharge at some distance from the outlet may drop into the occupied zone. Most devices used for sidewall application can be adjusted to project the air pattern upwards toward the ceiling. This allows the discharge air to attach to the ceiling, increasing throw distance and minimizing drop. This application provides occupant comfort by inducing air from the occupied zone into the supply air. Some outlets may be more than 1.25 m below the ceiling (e.g., in high-ceiling applications, the outlet may be located closer to the occupied zone to minimize the volume of the conditioned space). Most devices used for sidewall applications can be adjusted to project the air pattern upward or downward, which allows the device's throw distance to be adjusted to maximize performance. When selecting sidewall outlets, it is important to understand the manufacturer's data. Most manufacturers offer data for outlets tested with surface effect, so they only apply if the device is set to direct supply air toward the ceiling. When the device is 1.25 m or more below a ceiling, or supply air is directed horizontally or down- ward, the actual throw distance of the device is typically shorter. Many sidewall outlets can be adjusted to change the spread of sup- ply air, which can significantly change throw distance. Manufactur- ers usually publish throw distances based on specific spread angles. Cooling with Floor-Mounted Air Outlets. Although not typi- cally selected for nonresidential buildings, floor-mounted outlets can be used for mixed-system cooling applications. In this configu- ration, room air from the occupied zone is induced into the supply air, providing mixing. When cooling, the device should be selected to discharge vertically along windows, walls, or other vertical sur- faces. Typical nonresidential applications include lobbies, long cor- ridors, and houses of worship. It is important to select a device that is specially designed for floor applications. It must be able to withstand both the required dy- namic and static structural loads (e.g., people walking, loaded carts rolling across). Also, many manufacturers offer devices designed to reduce the possibility of objects falling into the device. It is strongly recommended that obstructions are not located above these in-floor air terminals, to avoid restricting their air jets. Long floor-mounted grilles generally have both functioning and nonfunctioning segments. When selecting air outlets for floor mounting, it is important to note that the throw distance and sound generated depend on the length of the active section. Most manufac- turers' catalog data include correction factors for length 's effects on both throw and sound. These corrections can be significant and should be evaluated. Understanding manufacturers' performance data and corresponding notes is imperative. Cooling with Sill-Mounted Air Outlets. Sill-mounted air out- lets are commonly used in applications that include unit ventila- tors and fan-coil units. The outlet should be selected to discharge Inc. ASHRAE, 2019 user. single for Licensed | {}
6513e263-2462-4822-9d3f-617fa4077173 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Room Air Distribution 58.9 vertically along windows, walls, or other vertical surfaces, and project supply air above the occupied zone. As with floor-mounted grilles, when selecting and locating sill grilles, consider selecting devices designed to reduce the nuisance of objects falling inside them. It is also recommended that sills be designed in a way that prevents their use as shelves. Perimeter Control Techniques. In many cases, it is advanta- geous to decouple perimeter and interior supply air sources, espe- cially as new buildings trend toward full glazing exteriors. Often, interior spaces require cooling all year round due to personnel, elec- tronic equipment, and lighting load requirements. Perimeter spaces, however, are more susceptible to the outside environmental condi- tions and can have major effects on interior space loads if not prop- erly managed. Heating and Cooling with Perimeter Ceiling-Mounted Outlets. When air outlets are used at the perimeter with vertical projection for heating and/or cooling, they should be located near the perimeter surface, and selected so that the published 0.75 m/s isothermal throw extends at least halfway down the surface or 1.4 m above the floor, whichever is lower. In this manner, during heating, warm air mixes with the cool downdraft on the perimeter surface, to reduce or even eliminate drafts in the occupied space. Ifa ceiling-mounted air outlet is located away from the perimeter wall, in cooling mode, the high-velocity cool air reduces or over- comes the thermal updrafts on the perimeter surface. To accomplish this, the outlet should be selected for horizontal discharge toward the wall. Outlet selection should be such that isothermal throw with terminal velocity of 0.75 m/s should include the distance from the outlet to the perimeter surface. For heating, the supply air tempera- ture should not exceed 8.5 K above the room air temperature. Be conscious of room design. Ifthere are shelves or desks against or near the perimeter surface the high velocity air jet could disturb items on the surfaces or result in drafts. Perimeter Heating with Floor/Sill-Mounted Outlets. The outlets used in this configuration must be located near the perimeter sur- face. In heating mode, it is important to select a vertical throws such that it overcomes the down draft produced by a cold perimeter surface. The amount of heat generated from the outlet must be enough to overcome or mix with this down draft airstream to avoid ankle-level draft issues in the occupied space. 3. FULLY STRA TIFIED AIR DISTRIBUTION Fully stratified air distribution systems are characterized by a vertical temperature gradient throughout the space, where the coolest temperature is at the floor level, and the warmest tempera- ture is at the ceiling height. Displacement ventilation (DV) systems are the most common example of a fully stratified air distribution system. DV systems typically use floor or low sidewall (sometimes ceiling-mounted) diffusers delivering low-velocity, cool air across the floor. The low-velocity air, in conjunction with room loads and buoyancy effects, creates the characteristic vertical thermal stratifi- cation. Principles of Operation DV systems (Figure 6) use very low discharge velocities, with diffusers typically sized to provide outlet velocities between 0.20 and 0.35 m/s. In addition to the low velocity discharge, the tempera- ture of the supply air is also different from a fully mixed system, with temperatures generally above 16°C; lower temperatures may be used in industrial applications, exercise or sports facilities, and transient areas where comfort concerns are minimal. This cool supply air is more dense than the ambient air and drops to the floor after discharge, whether from floor, low sidewall, or ceiling mounted locations, spreading across the lower level of the space (typically less than 0.2 m in height). As convective heat sources (Figure 6) in the space transfer heat to the cooler air around them, natural convection currents form and rise along the heat transfer boundary. Without significant room air movement, these currents rise to form a convective heat plume (thermal plume) around and above the heat source; as the plume rises, it expands by entraining surrounding air. Its growth and veloc- ity are proportional to the heat source's size and sensible load, as well as the temperature of the ambient air above it. As the plume rises, ambient air from below and around the heat source fills the void. An occupant in a DV system entrains the cool, conditioned air directly into their breathing zone. As the occupant exhales, the spent air, being warmer and more humid than the ambient air, is pulled out of the breathing zone by the rising plume. Convective heat from sources located above the occupied zone has little effect on occupied-zone air temperature. At a certain height, where plume temperature equals ambient temperature, the plume dissipates and spills horizontally. Two dis- tinct zones are thus formed in the room: a lower occupied zone with little or no recirculation flow (close to displacement flow), and an upper zone with recirculation flow. The boundary between these two zones is often called the shift zone (or stratification height). The height of this boundary layer between the upper and lower zones is determined based on the convection flow rates of the ther- mal plumes in relation to the airflow rate supplied by the diffusers. In a DV system, increasing the airflow rate limits stratification and lowers the boundary layer height, with a decrease in airflow provid- ing the opposite effect Actual and simplified representations of the temperature gradient in the space are shown in Figure 6. DV systems can be modeled as shown in Figure 7. A thin layer of conditioned supply air (typically between 100 and 200 mm) lies adjacent to the floor. Directly above this layer of conditioned air is the lower zone, in which both ambient air temperature and contam- inant concentration levels increase with height; this relationship is mostly linear. As the air transitions through the boundary layer, the upper, unoccupied zone contains a pool of warm, used, and/or con- taminated air. This upper zone may or may not form, depending on the supplied airflow rate in proportion to the volume of thermal plumes rising through the space. Space Ventilation and Contaminant Removal Thermal plumes created by heat sources, in conjunction with thermal stratification within the space, allow DV to be very effective at removing airborne contaminants that are equal to or lighter than the ambient air (e.g., respiratory-produced contaminants, tobacco smoke). The upward momentum of room air created by thermal plumes from heat sources drive an overall upward momentum of air, which displace contaminants out of the breathing zone. This typi- cally results in a concentration of contaminants above the occupied ![image](/image/placeholder) RETURN UPPER UNOCCUPIED ZONE SHIFT ZONE CONVECTIVE PLUME LOWER OCCUPIED SUPPLY ZONE Fig. 6 Displacement Ventilation System Inc. ASHRAE, 2019 user. single for Licensed | {}
26d4315f-9efe-4796-9f1b-d6eb098adaa3 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 58.10 2019 ASHRAE Handbook-HVAC Applications (SI) Chart Type: line 0 0.5 1 item_01 0.0 0.2 0.3 Fig. 7 Temperature Profile of Displacement Ventilation System zone greater than that in the breathing zone. This has been recog- nized in ASHRAE Standard 62.1-2016, which allows DV systems to have a zone air distribution effectiveness Ez value of 1.2, compared to maximum values of 1.0 for mixed air systems. Thus, the designer can decrease the required outdoor air by 17% when using a DV sys- tem, which may result in energy savings for the system. Care should be taken when selecting DV systems when it is known that there will be airborne contaminants that are heavier than the ambient air. In these systems, a fully mixed system is typically recommended. Figure 8 shows thermal temperature gradients that might be expected for a classroom with a 3 m ceiling, served by DV. If loads are typical to the application and proper space airflow is supplied, Skistad et al. (2002) indicate that approximately 50% of the total temperature difference between supply air and return or exhaust air is dissipated in clear zone(s) next to the outlet(s). The other half of the temperature gradient is the space temperature gradient (STG), assumed to be linear with air temperature, increasing grad- ually from floor to ceiling. For stationary, low-activity occupants, keep supply air tempera- tures above 16°C. When occupants are very near outlets (e.g., in underseat delivery), it is recommended to keep supply air tempera- tures at or above 18°C. Outlet Characteristics Displacement outlets are designed for average outlet velocities between 0.20 to 0.35 m/s, and are typically mounted in a low side- wall or floor location. Yuan et al. (1999) recommend 0.2 m/s to maintain thermal comfort in the space. Returns or exhausts should be located at a minimum height of 2.75 m to ensure temperature stratification control. Returns or exhausts should be located as high as possible in the space to promote upward momentum of the air, and should efficiently remove as much of the stratified zone as pos- sible; they also should be equally distributed throughout the space to encourage equal air movement and discourage cross flow in the stratified zone. Intensive heat sources may benefit from having returns located directly above them to quickly remove generated heat from the room. Displacement outlets are available in a number of configurations and sizes. Some models are designed to fit in corners or along side- walls, or stand freely as columns. It is important to consider the Chart Type: line 0. 0.2 0.3 0.4 0.5 0.6 0.7 0.8 0.9 1.0 item_01 0% 0% 0% 0% 10% 20% 30% 60% 90% 100% Fig. 8 Temperature Gradient Relationships for Thermal Displacement Ventilation System in Typical Classroom or Office with 3 m Ceiling degree of flow equalization the outlet achieves, because use of the entire outlet surface for air discharge is paramount to minimizing clear zones and maintaining acceptable temperatures at the lower levels of the space. Stationary occupants should not be subjected to discharge veloc- ities exceeding around 0.25 m/s because air at the ankle level within this velocity envelope tends to be quite cool. As such, most outlet manufacturers define an adjacent zone (also called a clear zone) in which locating stationary, low-activity occupants is strongly dis- couraged, but transient occupancy, such as in corridors or aisles, is allowed. Occupants with high activity levels may also find the clear zone acceptable. For a typical space, a single displacement diffuser can penetrate around 8 to 9 m. Spaces that are wider than this or have high load densities should look at providing displacement diffusers on multi- ple walls, or free standing (e.g., around columns) for even airflow distribution. A computational fluid analysis (CFD) may be war- ranted for more complex spaces to validate the design. Contact the diffuser manufacturer for further diffuser selection assistance. Benefits and Limitations Benefits of displacement ventilation systems include the follow- ing: · Flexibility: as load distribution changes in the space, the buoy- ancy forces drive/pull where the conditioned air will go. Thus, a DV system can work effectively in an evenly distributed load space, as well as a space with concentrated loads. A mixing sys- tem may cause drafts, or have stagnant zones in similar loading circumstances. · Low noise: due to the low velocities associated with DV diffus- ers, the generated noise is typically very low (<20 NC for most applications). · Fewer drafts: lower turbulence intensity can reduce draft-related complaints. · Indoor air quality improvements: properly designed DV sys- tems displace higher concentrations of contaminants above the occupied zone than in the breathing zone. · Energy savings: due to a supply air temperature typically above 16°C (more typically 18°C), significantly less energy may be used Inc. ASHRAE, 2019 user. single for Licensed | {}
ecd1200c-0a4a-41c7-a15c-8f2931e93260 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | Room Air Distribution 58.11 in certain climates due to an increase in free cooling hours. Less outdoor air is required to meet ASHRAE Standard 62.1 require- ments, meaning less outdoor air needs to be conditioned. Some applications do not favor use ofDV systems. Small offices, especially with perimeter exposures, often do not have room for the large outlets that may be required. The following types of areas may be better served by a mixed system: · Spaces with ceiling heights less than 2.7 m · Some spaces with exceptionally high occupied zone heat loads. · Spaces in hot and humid climates that may result in higher dehu- midification and reheat energy usage · Spaces with ceiling heights below 3 m that are subjected to sig- nificant room air disturbances · Applications where contaminants are heavier and/or colder than ambient air. Methods of Evaluation Unlike mixed systems, outlets in thermal displacement systems discharge air at very low velocities, resulting in very little mixing. As such, design of these systems primarily involves determining a supply airflow rate to manage the thermal gradients in the space in accordance with ASHRAE comfort guidelines. ASHRAE Standard 55 recommends that the vertical temperature difference between the ankle and head levels of standing occupants be no more than 3 K to maintain a high degree (>95%) of occupant satisfaction. Inlet Conditions Similar to mixing system diffusers, inlet conditions (including presence of dampers, elbows, flex duct, etc.) can have a negative effect on performance, primarily noise (NC) and pressure drop. Inlet conditions should match ASHRAE Standard 70 testing condi- tions as closely as possible to mimic catalogue performance data. DV diffusers are typically designed with internal baffles or nozzles, which should not be affected by inlet conditions at relatively low plenum velocities. Design Procedures DV system design is somewhat different than for mixing venti- lation. For mixing ventilation systems, where air is mixed relatively evenly throughout the space, the return/exhaust air temperature is assumed to equal the space temperature. In displacement ventilation systems, the space is divided into two vertical zones. The desired space air temperature is maintained only in the lower zone and is always higher in the upper zone because of the temperature stratifi- cation created by natural convection. ASHRAE research project RP-949 (Chen et al. 1999) developed a calculation method for determining supply air volume, air tem- perature, and other design parameters specifically for DV systems. Using these calculations, the maximum temperature stratification, as outlined in ASHRAE Standard 55, is not exceeded. Example 4 uses the calculations outlined in RP-949 and the procedure pre- sented by Chen & Glicksman (2003). This research project is intended for use with typical office and classroom spaces; for larger spaces such as atriums and theaters, careful consideration is neces- sary, and a computational fluid dynamic (CFD) analysis is recom- mended to verify design. The Federation of European Heating and Air Conditioning Associations (REHVA) also developed two pro- cedures for calculation of air volume in DV systems; see the REHVA design guide for further information on these methods. Example 4. Determine the supply air temperature, supply air flow rate, and face area for a displacement diffuser for a small office room (3 x 4 x 3 m) with the following characteristics: 9⌀ occupant load, 150 W qe computer/equipment load, 90 W qoe 90 + qe = 240 W ql lighting load, 250 W qex exterior load, 130 W tset point = 22°C Step 1. Determine total cooling load: It = qoe + ql + 9ex = 240 + 250 + 130 = 620 W Step 2. Determine airflow rate to meet cooling load. ASHRAE RP- 949 (Chen et al. 1999) allows applying factors to each heat load based on how much they contribute to room stratification: 0.295qoe + 0.132q1+ 0.185qex QDV = 1000pcpAthf (4) 0.295(240) + 0.132(250) + 0.185(130) QDV = = 0.035 m3/s = 35 L/s 1000(1.005)(1.225)(3) cp = specific heat, 1.005 kJ/kg· K P = density of air, 1.225 kg/m3 where Athf = maximum head-to-foot temperature differential for a standing occupant, 3 °C (per ASHRAE Standard 55-2017) Step 3. Determine minimum outdoor air requirement per ASHRAE Standard 62.1-2013: ⑤ R p Pz+RAAz Qoz = Ez (2.5)(2) + (0.3)(3x4) = 7.2 L/s Qoz = 1.2 where Rp = outdoor air rate per person, 2.5 L/s-person per ASHRAE Stan- dard 62.1-2013 Pz = zone population (number of people in zone during typical us- age), 2 Ra = area outdoor air rate, 0.3 (L/s)·m2 per Standard 62.1 Az = zone floor area, 12 m2 Ez = ventilation effectiveness, 1.2 (per Standard 62.1 for DV systems) Therefore, the total supply air volume Qs for cooling is determined by the cooling load and is 35 L/s. Step 4. Calculate supply air temperature. The following formula assumes thermostat is located 1 m from the floor: Azqr ts = tsp - Athf- 0.584Q2DV + 1.208A 2s (12)(620) ts = 22 - 3 - + 12.9°C 2 (0.584)(35) + (1.208)(12)(35) 620 tr = 12.9°C + + 27.6°C (1.208)(35) Step 5. Determine return air temperature: 9T tr = ts + 1.208Qs Step 6. Adjust airflow for new supply temperature. DV systems typi- cally use warmer supply air temperatures than mixing systems. The supply air temperature should be at least 17°C, or 5.5 K less than the room set point, whichever is higher. Supply airflow should maintain the same return temperature: ts = 17°C It Qs = 60pcp(tr-ts) Inc. ASHRAE, 2019 user. single for Licensed (7) ⑥ (8) | {}
f55d167f-f5d8-4f76-b44b-febf09352267 | 2019 ASHRAE Handbook - HVAC Applications (SI) by Ashrae (z-lib.org) (2).pdf | 58.12 2019 ASHRAE Handbook-HVAC Applications (SI) 620 2s = 0.0343 m3/s = 34 L/s 1000(1.005)(1.225)(27.6- 12.9) Therefore, in order to condition this particular office using a DV system, it is necessary to deliver 17°C, air at an airflow rate of 34 L/s. Step 7. Size diffuser. Yuan et al. (1999) recommend a maximum dif- fuser face velocity of 0.2 m/s to obtain acceptable thermal comfort. This recommendation is based on the nominal diffuser size. Qs A diffuser 0.2 (9) 34 A diffuser = 0.170 m2 0.2 x 1000 A single diffuser that is 300 x 600 mm will meet this minimum area requirement to maintain comfort. Check with the manufacturer's per- formance data to ensure diffuser selection meets noise and comfort requirements. Space temperature gradient (STG) is affected by the strength and location of heat sources in the space, heat exchange by radiation between surfaces in the space, and supply airflow. The design pro- cedure presented in this section is based on Skistad et al. 's (2002) simplified method of estimating temperature gradient (Figure 8). This method is applicable for typical spaces with a ceiling height up to 3.7 m, such as classrooms, office spaces, and meeting rooms. When designing more complex spaces, computational fluid dynamics (CFD) software programs may be used (see Chapter 13 of the 2017 ASHRAE Handbook-Fundamentals for more informa- tion). The thermal gradient relationships illustrated in Figure 8 can be used to establish an acceptable supply-to-return air temperature differential AtSR from which the supply airflow rate is calculated. Because the space temperature gradient is assumed to be linear, the occupied gradient in the occupied zone is proportional to the vol- ume of the space it represents. For example, if return height is 3 m and the occupied zone is 1.5 m high, its gradient comprises 50% of the space temperature gradient, or 25% of AtSR· The temperature difference between room air at the top of the occupied zone and the supply air is therefore 75% of △ISR· Determining an acceptable AtSR should consider both the room- to-supply temperature differential and the occupied zone tempera- ture gradient (as limited to 3 K by ASHRAE Standard 55). Inc. ASHRAE, 2019 user. single for Licensed In general, high-ceiling applications allow larger supply-to- return air temperature differentials, because the occupied zone is a smaller percentage of total room air volume. However, the differen- tial may be reduced by limitations on supply air temperature, as shown in Example 5. The supply airflow rate 0 to achieve AtSR is calculated from Equation (1). Example 5. A classroom with a 3 m ceiling is to be cooled by displacement ventilation. The supply air temperature is 16.5°C and room temperature is maintained at 24°C at 1.5 m level. The total sensible heat gain of the space is 8200 W. Calculate the (1) overall temperature differential between supply and return airflow and (2) required space airflow. Identify return air temperature and temperature at occupants' ankle level. Solution: Using the relationships in Figure 8, the supply-to-return tem- perature differential AISR and return air temperature can be predicted as follows: AtSR = (troom - tsupply)/0.75 = (24 - 16.5)/0.75 = 10 K + AISR = 16.5 + 10 = 26.5°C treturn tsupply = To ensure a high level of thermal comfort, the occupied-zone tem- perature gradient △toz should not exceed 3 K. For this application, the occupied zone gradient is acceptable: At⌀z = AISR x 0.25 = 10 x 0.25 = 2.5°C From Equation (1), the airflow required to maintain this gradient is 0 = 8200/(1.2 x 10) = 683 L/s Typical Applications Thermal displacement ventilation systems typically have higher return air temperatures than mixed systems. Thus, they may allow extended periods of air- or water-side economizer operation, espe- cially in mild, relatively dry climates. Thermal displacement ventilation systems are commonly used in applications such as · Restaurants · Casinos · Classrooms/education facilities · Large open-plan offices, classrooms, lecture halls, and meeting rooms · Theaters and auditoriums · Industrial spaces · Hospitals and cleanrooms · Other spaces with high ceilings Perimeter Control DV systems rely on buoyancy of the cool supply air and thermal plumes of the heat sources to drive stratification in the space. Due to this, DV is typically a cooling-only method of room air distribution. When heating is required, the warmer (more buoyant) air, in con- junction with the low discharge velocity, can mean that the air may not effectively condition the occupied zone, or may completely bypass the occupied zone to the returns. This can have a negative effect on both the thermal comfort and indoor air quality in the space. Limited heating differentials may be acceptable depending on a number of factors. ASHRAE research project RP-1373 (Jiang and Chen 2009) explores the ventilation effectiveness of DV sys- tems in heating and cooling scenarios. For heating, either a displacement diffuser with integrated heat- ing or a separate system is generally recommended. Displacement ventilation can be used successfully in combination with perimeter fan coils, hydronic systems, or radiators and convectors installed at exterior walls to offset space heat losses. Radiant heating panels and heated floors can also be used. Using this hybrid approach, the DV diffusers can provide isothermal ventilation air, with the auxiliary devices handling the heating load. Displacement diffusers with integrated heat typically have a sep- arate heating plenum featuring a heating coil and are often used for perimeter applications. Heat/cool changeover diffusers can also be used. For this design, the heating portion of the diffuser may not provide a displacement pattern, so care should be taken to ensure proper ventilation effectiveness. Care is also needed when using DV systems in high perimeter cooling load applications. DV diffuser mounting locations should be carefully considered to minimize the risk of conditioned air being drawn toward the strong thermal plume of the exterior surface. It may be better to place diffusers along an interior surface to ensure that the conditioned air reaches interior occupants before conditioning the exterior envelope loads. Considerations Unique to Displacement Ventilation Systems (10) It is often beneficial to couple DV systems with hydronic prod- ucts. As Yuan et al. (1999) state, a maximum of 120 W/m2 hydronic products can be used to increase capacity of the system. Another (11) | {}